## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | FD Installation Checklist |  |  |  |  | Yes | FD Installation Checklist | 260d6e74-00c1-4d7a-9018-edded8e73172
checkpoint-status |  |  | checkpoint | FD Dimensions
label | 675be665-2e9f-5a81-96a0-7a10edcd1b08 |  | note | Min Penetration = (1.01W + 10mm) x (1.01H + 10mm)
label | 511497eb-050c-5dbb-a4e7-b891c82b799f |  | note | Max Penetration = (W+F) x (H+F)
label | 192c64a0-7e60-5156-9ab9-8d208a1f5304 |  | note | F= Side of the angle against Fire Wall (mm)
label | 74858ab3-2298-510e-bee5-98dff6ea6d06 |  | note | AS.1682.2:2015
text | 996f6694-a4cc-560e-8014-20e1ad21d71c |  | textbox | FD Size (W X H):
text | de4c5181-a030-5406-be56-ff07106bb8a4 |  | textbox | Flange Size (F):
text | 76328958-87c1-5c6c-a4e9-f6e32940ed3a |  | textbox | Minimum Peno Size (W X H):
text | 3db064f8-29b2-56e6-96e4-25ea85994a94 |  | textbox | Maximum Peno Size (W X H):
text | f11946e5-472c-563f-b08f-2646289f45e7 |  | textbox | Current Peno Size (W x H)
checkpoint-status |  |  | checkpoint | FD fully open; blades free to close and latch
checkpoint-status |  |  | checkpoint | FD orientation and air flow direction is correct
checkpoint-status |  |  | checkpoint | FD wholly within wall/ Slab; case is square
checkpoint-status |  |  | checkpoint | FD and Duct attached correctly/ Breakaway
checkpoint-status |  |  | checkpoint | Packing/expansion metal installed around casing
checkpoint-status |  |  | checkpoint | Opening in fire rated structure is correct
checkpoint-status |  |  | checkpoint | FD Flanges attached correctly
checkpoint-status |  |  | checkpoint | FD # corresponds to the one detailed on drawing
checkpoint-status |  |  | checkpoint | FD location corresponds to the one detailed on drawing
checkpoint-status |  |  | checkpoint | FD accessible for maintenance and service purposes
checkpoint-status |  |  | checkpoint | FD Installer Label complete
checkpoint-status |  |  | checkpoint | Fusible Link Fitted
checkpoint-status |  |  | checkpoint | Floor Mounted-2000 mm of Duct insulated above FD
checkpoint-status |  |  | checkpoint | Installation is approved
checkpoint-status |  |  | checkpoint | Corrective actions have been undertaken
checklist-flat |  |  | checklist | FD Installation Photos |  |  |  |  | Yes | FD Installation Photos Checklist | 3c08390e-d335-4b55-bfa9-df6f2fd3aae4
checkpoint-status |  |  | checkpoint | Penetration Width
checkpoint-status |  |  | checkpoint | Penetration Height
checkpoint-status |  |  | checkpoint | Left and/or Rigth Gap
checkpoint-status |  |  | checkpoint | Top and/or Bottom Gap
checkpoint-status |  |  | checkpoint | FD c/w Retention Angles
checkpoint-status |  |  | checkpoint | FD Open
checkpoint-status |  |  | checkpoint | FD Close
checkpoint-status |  |  | checkpoint | FD Break Away Joint
checkpoint-status |  |  | checkpoint | FD with AP
checkpoint-status |  |  | checkpoint | Gaps Around FD Sealed
checkpoint-status |  |  | checkpoint | Sticker