## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | FD Installation Checklist |  |  |  |  | Yes | FD Installation Checklist | b35d74de-4a43-44ab-b63f-a0a7078d2dcc
checkpoint-status |  |  | checkpoint | FD Dimensions
label | 3e860684-41ba-5f8a-8d5b-8d7500b621c6 |  | note | Min Penetration = (1.01W + 10mm) x (1.01H + 10mm)
label | 99bcb281-7c28-54c7-b116-aba9568a11cb |  | note | Max Penetration = (W+F) x (H+F)
label | 56f1b0ef-0108-5d7f-bab8-28980a83bae3 |  | note | F= Side of the angle against Fire Wall (mm)
label | 255ce387-b80e-52da-a504-c82f31daaf9f |  | note | AS.1682.2:2015
text | 52055e0d-740a-5d6c-9fb4-ed0d3b0476bb |  | textbox | FD Size (W X H):
text | 4c38c0d3-1d65-538c-882e-b95480935b55 |  | textbox | Flange Size (F):
text | 9fef491d-016f-5ba0-9caf-750651190013 |  | textbox | Minimum Peno Size (W X H):
text | 147d3a79-a882-5ce9-b9da-2a6f85352ce5 |  | textbox | Maximum Peno Size (W X H):
text | d6bcf8b9-440f-574f-9577-be397349b59e |  | textbox | Current Peno Size (W x H)
checkpoint-status |  |  | checkpoint | FD fully open; blades free to close and latch
checkpoint-status |  |  | checkpoint | FD orientation and air flow direction is correct
checkpoint-status |  |  | checkpoint | FD wholly within wall/ Slab; case is square
checkpoint-status |  |  | checkpoint | FD and Duct attached correctly/ Breakaway
checkpoint-status |  |  | checkpoint | Packing/expansion metal installed around casing
checkpoint-status |  |  | checkpoint | Opening in fire rated structure is correct
checkpoint-status |  |  | checkpoint | FD Flanges attached correctly
checkpoint-status |  |  | checkpoint | FD # corresponds to the one detailed on drawing
checkpoint-status |  |  | checkpoint | FD location corresponds to the one detailed on drawing
checkpoint-status |  |  | checkpoint | FD accessible for maintenance and service purposes
checkpoint-status |  |  | checkpoint | FD Installer Label complete
checkpoint-status |  |  | checkpoint | Fusible Link Fitted
checkpoint-status |  |  | checkpoint | Floor Mounted-2000 mm of Duct insulated above FD
checkpoint-status |  |  | checkpoint | Installation is approved
checkpoint-status |  |  | checkpoint | Corrective actions have been undertaken
checklist-flat |  |  | checklist | FD Installation Photos Checklist |  |  |  |  | Yes | FD Installation Photos Checklist | bb4559e4-3fbd-4cc0-8b0b-ad7934619fb8
checkpoint-status |  |  | checkpoint | Penetration Width
checkpoint-status |  |  | checkpoint | Penetration Height
checkpoint-status |  |  | checkpoint | Left and/or Rigth Gap
checkpoint-status |  |  | checkpoint | Top and/or Bottom Gap
checkpoint-status |  |  | checkpoint | FD c/w Retention Angles
checkpoint-status |  |  | checkpoint | FD Open
checkpoint-status |  |  | checkpoint | FD Close
checkpoint-status |  |  | checkpoint | FD Break Away Joint
checkpoint-status |  |  | checkpoint | FD with AP
checkpoint-status |  |  | checkpoint | Gaps Around FD Sealed
checkpoint-status |  |  | checkpoint | Sticker