## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | RR-SEPD-BESS-FIC-010-01 - Footings Subgrade | [5 empty] | RR-SEPD-BESS-FIC-010-01 - Footings Subgrade
section | Part 1 – Subgrade Preparation
checkpoint | Survey set out
label | Survey set out for excavation to latest IFC drawings
label | Specifications/Drawings Reference - IFC drawings
checkpoint | Excavation completed to subgrade design heights
label | Subgrade trimmed to correct heights for construction of footing
label | Tolerance = +0mm, -50mm
label | Specifications/Drawings Reference - IFC drawings
checkpoint | Subgrade compacted
label | Subgrade compacted with heaviest equipment suitable to be used in the area.
label | Minimum of 6x passes
label | — 700kg DPU
label | — 350kg DPU
label | — 100-150kg plate compactor
label | — Legrammer (60-80kgs)
label | — Trench roller (eg. BMP 8500)
label | Specifications/Drawings Reference - AS 1289, WBS-SS-CI-SPC-0006
checkpoint | Surface cleaned of loose material/debris/rubbish
label | Surface is even and clean of materials
label | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
checkpoint | Subgrade inspection & proof roll
label | Subgrade verified, compacted and trimmed.
label | Subgrade proof rolled and no excessive deformation found (refer to Proof Roll FIC where applicable).
label | Specifications/Drawings Reference - AS 1289, WBS-SS-CI-SPC-0006
checkpoint | Soft Spots remediation
label | Any soft spots identified and rectified as per the Engineer’s instruction
label | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
checkpoint | Compaction testing
label | 95% MMDD
label | 1x test per footing (or every 5m where applicable)
label | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
section | Document Sign-off
checkpoint | Prepared by:
textbox | ROBAR - Name:
textbox | ROBAR - Position:
date | Date:
signoff | Add Signature