## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP-001 CONDUITS IN SLABS | itp |  |  |  |  | ITP-001 CONDUITS IN SLABS Rev 1
section | PREPARATION
checkpoint | DETERMINE ORIGIN AND DESTINATION
label | INSPECTION FUNCTION - CHECK ALL RELEVANT DRAWINGS
label | APPLICABLE STANDARD - ELECTRICAL DRAWINGS
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CHECK CLEAR OF OTHER SERVICES, PENETRATIONS ETC
label | INSPECTION FUNCTION - CO-ORDINATE WITH OTHER SERVICES
label | APPLICABLE STANDARD - ALL RELEVANT DRAWINGS
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CHECK CABLE SIZE TO VERIFY CONDUIT SIZE
label | INSPECTION FUNCTION - CHECK DIMENSIONS
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CHECK IF EXPANSION JOINTS ARE REQUIRED
label | INSPECTION FUNCTION - CHECK ALL RELEVANT DRAWINGS
label | APPLICABLE STANDARD - STRUCTURE DRAWINGS
label | ACCEPTANCE CRITERIA - COMPLIES
section | INSTALLATION
checkpoint | MARK OUT POSITIONS OF JUNCTION BOXES AND PENETRATIONS WHERE NECESSARY
label | INSPECTION FUNCTION - CHECK ALL RELEVANT DRAWINGS
label | APPLICABLE STANDARD - ELEC/DRWG
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL BAR CHAIRS WHERE NECESSARY
label | INSPECTION FUNCTION - ENSURE IN STRAIGHT LINES
label | APPLICABLE STANDARD - ELEC/DRWG
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL JUNCTION BOXES AND CONDUITS AND GLUE
label | INSPECTION FUNCTION - CHECK ALL RELEVANT DRAWINGS
label | APPLICABLE STANDARD - ELEC/DRWG
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | TIE CONDUITS SECURELY AT ALL JOINTS AND MIDPOINTS
label | INSPECTION FUNCTION - CHECK AND OBSERVE
label | APPLICABLE STANDARD - TIED SECURELY
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | ENSURE ALL CONDUITS ARE 50MM ABOVE DECK
label | INSPECTION FUNCTION - CHECK AND OBSERVE
label | APPLICABLE STANDARD - MINIMUM 50MM ABOVE DECK
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | MARK UP DRAWING OF CONDUIT RUNS (IF REQUIRED)
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS PER INSTALLATION
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | OBSERVE CONDUITS WHEN CONCRETE IS BEING POURED
label | INSPECTION FUNCTION - OBSERVE
label | APPLICABLE STANDARD - NO BROKEN CONDUITS
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-002 CIRCUIT CONTROL WIRING ROUGH IN | itp |  |  |  |  | ITP-002 CIRCUIT CONTROL WIRING ROUGH IN Rev 1
section | CIRCUIT CONTROL WIRING ROUGH IN
checkpoint | REFER TO DRAWING TO DETERMINE CABLE SUPPORT ROUTE AND CHECK SEPARATION FROM DATA/COMMS SERVICES
label | INSPECTION FUNCTION - CO-ORDINATE WITH OTHER SERVICES
label | APPLICABLE STANDARD - DRAWINGS & REGULATIONS REFER ATTACHED
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | DETERMINE CABLE SIZE AS PER ITP 30 SELECTION OF CABLES FOR SUBCIRCUIT WIRING ETC.
label | INSPECTION FUNCTION - CALCULATION
label | APPLICABLE STANDARD - AS/ANZ 3000:2007, AS/ANZ 3008:1998
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CABLE SIZES / MAX LENGTH
textbox | CABLE SIZES
textbox | MAX LENGTH
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS/ANZ 3000:2007, AS/ANZ 3008:1998
checkpoint | DETERMINE CABLE SUPPORT SYSTEM ie. CATINARY, CABLE TRAY, FIX TO STRUCTURE, DUCTING
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS/ANZ 3000:2007 SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL CABLE SUPPORT SYSTEM
label | INSPECTION FUNCTION - SELECT APPROPRIATE FIXINGS
label | APPLICABLE STANDARD - MAX CENTRES
label | ○ CABLE TRAY: 2 METRES
label | ○ CATINARY: 20 METRES
label | (Support to prevent sagging if necessary.)
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint-no-status | ALL CABLES ARE TO BE IDENTIFIED AS FOLLOWS: DB NO. FOLLOWED BY CIRCUIT NO. THEN FEED OR ACTIVE, WHITE CABLE MARK WITH BLACK TEXTA, BLACK CABLE WHITE TAPE THEN MARK WITH BLACK TEXTA. WHEN ROUGHING IN POWER CIRCUITS IN STUD WALL ETC. THE LOOP IN LOOP OUT AT THE GPO LOCATION SHALL BE TAPED TOGETHER. IF THE CABLES ARE TAPED TOGETHER IT WILL ENSURE THAT THE TRADESMEN FITTING OFF THE GPO WILL CONNECT ALL CABLES. AS TRADESMEN COMPLETE THE ROUGH IN THEY SHOULD MARK UP THE DRAWINGS THE LOCATIONS OF THE FEEDS AND RUNS ETC. THIS WILL ASSIST WHERE ANOTHER TRADESMAN COMPLETES THE JOB AND FIT OFF.
checkpoint | CHECK CABLE SIZE/TYPE, BLACK SHEATH FOR POWER, WHITE SHEATH FOR LIGHT: 4MM TO BE USED FOR RUNS OVER 90 METRES (UNLESS SPECIFIED DIFFERENTLY)
label | INSPECTION FUNCTION - CHECK SIZE TYPE & COLOUR
label | APPLICABLE STANDARD - AS 3008, AS/NZS 3000:2007AS SPECIFIED
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL AND IDENTIFY CABLES. ANY CABLE NOT TERMINATED IMMEDIATELY MUST HAVE THE ENDS TAPED COVERING THE BARE COPPER.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS DETAILED & TAPED ENDS
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | FIX CABLES TO SUPPORT SYSTEM
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS/NZS 3000:2007 / SPEC.
label | ACCEPTANCE CRITERIA - MAX. 900 CENTRES
checkpoint | FIT-OFF OUTLETS, PLUG BASES ETC. (IF NECESSARY), EACH CIRCUIT TO BE FITTED OFF COMPLETELY & CLEAN UP AREA
label | INSPECTION FUNCTION - CHECK CONNECTIONS, ALL OUTLETS ON CIRCUIT FITTED/ MADE SAFE.
label | APPLICABLE STANDARD - AS/NZS 3000:2007.
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-003 MAINS AND SUBMAINS INSTALLATION | itp |  |  |  |  | ITP-003 MAINS AND SUBMAINS INSTALLATION Rev 1
section | CABLE INSTALLATION
checkpoint | MEASURE CABLE RUNS WITH APPROPRIATE ACCURATE MEASURING INSTRUMENT EG TAPE MEASURE, WHEEL, ROPE IN CONDUIT
label | INSPECTION FUNCTION - MEASURE
label | APPLICABLE STANDARD - AS ELEC. DRAWINGS
label | ACCEPTANCE CRITERIA - AS INSTALLED CONDUITS, CABLE TRAYS
checkpoint | CHECK CABLE SIZES. RESISTANCE OF PROTECTIVE EARTH CONDUCTOR SHALL BE LOW ENOUGH TO PERMIT PASSAGE OF CURRENT NECESSARY TO OPERATE PROTECTIVE DEVICE.
label | *RULE 1.11.2.2. *RULE 1.7.4.3.4.
label | INSPECTION FUNCTION - CHECK ELECTRICAL DRAWINGS OR SPECS.
label | APPLICABLE STANDARD - AS/NZS 3000:2007 AS 3008
label | ACCEPTANCE CRITERIA - COMPLIES WITH REGULATIONS
checkpoint | CONFIRM LENGTH OF CABLE
label | INSPECTION FUNCTION - CORRECT SIZE. LENGTH
label | APPLICABLE STANDARD - N.A.
label | ACCEPTANCE CRITERIA - N.A.
checkpoint | INSTALL CABLE IN APPLICABLE METHOD EG. CABLE STANDS, ELECTRIC WINCH, PULLEYS ETC. ANY CABLE NOT TERMINATED IMMEDIATELY MUST HAVE THE ENDS TAPED COVERING THE BARE COPPER.
label | INSPECTION FUNCTION - MOST APPROPRIATE METHOD
label | APPLICABLE STANDARD - OH & S GUIDELINES & TAPED ENDS
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | TREFOIL (REFER TO DETAILS ON BACK FOR ALL OPTIONS) CABLES AND TIE CABLES TO SUPPORT SYSTEM
label | INSPECTION FUNCTION - ENSURE SPACING
label | APPLICABLE STANDARD - AS/ NZS 3000:2007
label | ACCEPTANCE CRITERIA - COMPLIES WITH REGULATIONS
checkpoint | CHECK REQUIREMENTS FOR CABLE IDENTIFICATION AND INSTALL
label | INSPECTION FUNCTION - CHECK METHOD
label | APPLICABLE STANDARD - AS PER SPEC
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-004 CONDUIT CABLE TRAY | itp |  |  |  |  | ITP-004 CONDUIT CABLE TRAY Rev 1
section | CONDUIT INSTALLATION
checkpoint | CO-ORDINATE WITH OTHER SERVICES, ENSURE SEGREGATION FROM COMMS / DATA SERVICES
label | INSPECTION FUNCTION - CHECK OTHER TRADES DRAWINGS
label | APPLICABLE STANDARD - AS/NZS 3000/1000 REFER ATTACHED
label | ACCEPTANCE CRITERIA - COMPLIES WITH REGUL.
checkpoint | SIZE AND TYPE OF CONDUIT
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - AS SPEC. & REGULATION
label | ACCEPTANCE CRITERIA - AS/NZS 3000:2007
checkpoint | INSTALL CONDUIT
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - LEVEL AND STRAIGHT
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | FIXINGS
label | INSPECTION FUNCTION - CHECK CORRECT SADDLES
label | APPLICABLE STANDARD - AS SPEC.
label | ACCEPTANCE CRITERIA - MAX. 1000 CENTRES
section | CABLE TRAY INSTALLATION
checkpoint | CO-ORDINATE WITH OTHER SERVICES
label | INSPECTION FUNCTION - CHECK OTHER TRADES DRAWINGS
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - COMPLIES WITH REGUL.
checkpoint | SIZE OF CABLE TRAY
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - AS SPEC. & REGULATION
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL FIXINGS
label | INSPECTION FUNCTION - SELECT APPROPRIATE FIXING
label | APPLICABLE STANDARD - MAX 2000 CENTRES
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL CABLE TRAY
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - LEVEL & STRAIGHT.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | DO SKETCH OR MARK UP DRAWING FOR FUTURE AS BUILTS
label | INSPECTION FUNCTION - ACCURATE DRAWINGS
label | APPLICABLE STANDARD - AS SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-005 SWITCHBOARD DELIVERY | itp |  |  |  |  | ITP-005 SWITCHBOARD DELIVERY Rev 7
section | DELIVERY CO-ORDINATION
checkpoint | PRIOR TO DELIVERY VISUAL INSPECTION BY FOREMAN TO CO-ORDINATE DELIVERY ON SITE
label | INSPECTION FUNCTION - VISUAL CHECK DIMENSIONS & WEIGHT
label | APPLICABLE STANDARD - OHS.
label | ACCEPTANCE CRITERIA - COMPLIES
section | SITE DELIVERY
checkpoint | DETERMINE METHOD OF UNLOADING EG. CRANE, FORKLIFT, MAN POWER, SPECIALIST SUB CONTRACTOR & ARRANGE
label | INSPECTION FUNCTION - SAFE WORK PRACTICE ARRANGE SUPPORT SPECIALIST
label | APPLICABLE STANDARD - O.H.S.
checkpoint | CO-ORDINATE TIME OF DELIVERY
label | INSPECTION FUNCTION - CONFIRM TIME
label | ACCEPTANCE CRITERIA - AS CONFIRMED
checkpoint | POSITIONING INTO PLACE EG. CRANE, FORKLIFT, ROLLERS, MANUAL, SPECIALIST SUB CONTRACTOR. IF PSG VIC ARE POSITIONING MAIN SWITCHBOARD, MANOUVERING KIT IS TO BE DELIVERED WITH THE MAIN SWITCHBOARD. DISTRIBUTION BOARDS REQUIRE LIFTING TROLLEY.
label | INSPECTION FUNCTION - SAFE WORK PRACTICE
label | APPLICABLE STANDARD - O.H.S.
checklist | ITP-006 SOFT WIRING | itp |  |  |  |  | ITP-006 SOFT WIRING Rev 1
section | SOFT WIRING
checkpoint | DELIVERY CHECK FOR DAMAGE
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - NO DAMAGE
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL HARD WIRING TERMINATION POINT
label | INSPECTION FUNCTION - CHECK FIXINGS
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - MANUFACT. RECOMMEND-ATIONS
checkpoint | TERMINATE CABLE AT TERMINATION BOX
label | INSPECTION FUNCTION - CORRECT TERMINATION POINT CONNECTIONS TIGHT
label | APPLICABLE STANDARD - AS SPEC
label | ACCEPTANCE CRITERIA - CONNECTION CORRECT HAND TIGHT
checkpoint | LOOP FLEXIBLE LEAD FROM TERMINATION BOX TO LIGHT SWITCH, SENSOR OR OUTLET AS REQUIRED
label | INSPECTION FUNCTION - CHECK CONNECTORS
label | APPLICABLE STANDARD - AS/NZS 3000:2007 ELEC/DRWG
label | ACCEPTANCE CRITERIA - CHECK CONNECTOR MATED CORRECTLY
checkpoint | TEST AND COMMISSION
label | INSPECTION FUNCTION - INSPECTION
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - COMPLIES WITH REGS
checklist | ITP-007 COMMS-BACKBONE, CABLING, TERMINATION & TESTING | itp |  |  |  |  | ITP-007 COMMS-BACKBONE, CABLING, TERMINATION & TESTING Rev 1
section | COMMS-BACKBONE, CABLING, TERMINATION & TESTING
checkpoint | OBTAIN THE MOST RECENT DRAWINGS AND SPECIFICATIONS.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - DRAWING REGISTER
label | ACCEPTANCE CRITERIA - CORRECT DRAWINGS
checkpoint | INSTALL CABLE SUPPORT OR CONDUIT WHERE REQUIRED.
label | INSPECTION FUNCTION - CHECK FIXING
label | APPLICABLE STANDARD - SPEC. & DRAWING AS/ACIF 3009:2006, AS/ZS 3080, AS/NZS 3034
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | DRESS CABLES TO FINAL LOCATION. ENSURE VELCRO STRAPS FOR CAT 6 CABLING
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - DRAWINGS & SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | TERMINATE CABLING ENSURING CORRECT COLOUR CODE. ENSURE CORRECT TERMINATION TOOL USED AS PER VENDOR RECOMMENDATION
label | INSPECTION FUNCTION - CHECK TERMINATIONS
label | APPLICABLE STANDARD - AS/ACIF 3009:2006, AS/ZS 3080, AS/NZS 3034
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | TEST TERMINATIONS USING WIZARD TESTER FOR KRONE BLOCK TERMINATIONS AND MOD TAP TESTER FOR PATCH PANEL TERMINATIONS.
textbox | DEVICE NUMBER:
label | INSPECTION FUNCTION - TEST
label | APPLICABLE STANDARD - AS/ACIF 3009:2006, AS/ZS 3080, AS/NZS 3034
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | LABEL FRAMES AND COMPLETE RECORD BOOKS
label | INSPECTION FUNCTION - LABELLING
label | APPLICABLE STANDARD - AS/NZS 3085.1 : 2004
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | RECORD RESULT
label | INSPECTION FUNCTION - RESULTS
label | APPLICABLE STANDARD - AS/ACIF 3009:2006, AS/ZS 3080, AS/NZS 3034
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | COMPLETE TELECOMMUNICATIONS CABLING ADVICE FORM AND ATTACHMENT IF REQUIRED
label | INSPECTION FUNCTION - TELECOMMUNICATIONS ADVICE
label | APPLICABLE STANDARD - AS/ACIF S009:2006
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-008 COMMS-DATA & VOICE TERMINATION | itp |  |  |  |  | ITP-008 COMMS-DATA & VOICE TERMINATION Rev 1
section | COMMS-DATA & VOICE TERMINATION
checkpoint | VISUAL CHECK ENSURING CABLE TO BE FITTED OFF IN CORRECT POSITION.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - DRAWING & SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | SELECTION OF CORRECT TOOL TO BE USED FOR TERMINATION TYPE.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - MANUFACT. RECOMMEN.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | ENSURE CABLES ARE STRIPPED NO MORE THAN THE SPECIFIED DISTANCE. CHECK TERMINATIONS AT COMPLETION FOR COLOUR CODE AND SEQUENCE.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - AS 3080 & MANUFACT. REQUIREMENTS
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | LABEL OUTLETS
label | INSPECTION FUNCTION - ENSURE CORRECT LABEL TYPE AND DESCRIPTION.
label | APPLICABLE STANDARD - DRAWINGS & SEPC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | PATCH OUTLETS TO HARDWARE DEVICES WHERE APPLICABLE AND CHECK FOR CORRECT OPERATION.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS PER CLIENTS REQUIREMENTS
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | COMPLETE CERTIFICATION IF REQUIRED
label | INSPECTION FUNCTION - DOCUMENT COMPLETED
label | APPLICABLE STANDARD - MANUFACT. RECOMMEN.
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-009 COMMS-DATA AND VOICE CABLING | itp |  |  |  |  | ITP-009 COMMS-DATA AND VOICE CABLING
section | COMMS-DATA AND VOICE CABLING
checkpoint | OBTAIN THE RELEVANT AND MOST RECENT DRAWINGS AND SPECIFICATION.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - DRAWING REGISTER
label | ACCEPTANCE CRITERIA - DRAWING REGISTER
checkpoint | INSTALL CABLE SUPPORT OR CONDUIT WHERE REQUIRED.
label | INSPECTION FUNCTION - CHECK FIXINGS
label | APPLICABLE STANDARD - AS 3080, SPEC. & DRAWING AS 3000
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | VERIFY CORRECT CABLE TYPE.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - DRAWINGS & SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | DECIDE APPROPRIATE CABLE NUMBERING SEQUENCE RELEVANT TO FINAL FIT OFF SEQUENCE.
label | INSPECTION FUNCTION - RECORD DETAILS
label | APPLICABLE STANDARD - LEGIBLE & CAN BE FOLLOWED BY OTHERS.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL CABLE WITHIN OR ON CABLE SUPPORT SYSTEM AS APPROPRIATE.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS 3080, SPEC. & DRAWING AS 3000
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | FORM CABLES INTO RELEVANT FIT-OFF GROUPS AT THE CABINET END.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - NEAT & TIDY
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-010 COMMS-DATA JACK TERMINATION | itp |  |  |  |  | ITP-010 COMMS-DATA JACK TERMINATION Rev 1
section | COMMS-DATA JACK TERMINATION
checkpoint | VISUAL CHECK ENSURING CABLE TO BE FITTED OFF IN CORRECT POSITION.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - DRAWING & SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | SELECTION OF CORRECT TOOL TO BE USED FOR TERMINATION TYPE.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - MANUFACT. RECOMMEN.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | ENSURE CABLES ARE STRIPPED NO MORE THAN THE SPECIFIED DISTANCE. CHECK TERMINATIONS AT COMPLETION FOR COLOUR CODE AND SEQUENCE. PUT STUFFER CAP ONTO JACK
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - AS 3080 & MANUFACT. REQUIREMENTS
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | ATTACH WRAP AROUND LABEL TO CABLE NO MORE THAN 60MM FROM THE JACK. ENSURING CORRECT NUMBER SEQUENCE.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - DRAWINGS & SEPC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL JACK INTO WORKSTATION OR WALL OUTLET.
label | INSPECTION FUNCTION - CHECK.
label | APPLICABLE STANDARD - DRAWINGS & SEPC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | LABEL OUTLET ENSURING CORRECT NUMBER SEQUENCE
label | INSPECTION FUNCTION - ENSURE CORRECT LABEL TYPE.
label | APPLICABLE STANDARD - DRAWINGS & SEPC.
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-011 DATA AND PATCH PANEL TERMINATION | itp |  |  |  |  | ITP-011 DATA AND PATCH PANEL TERMINATION
section | DATA AND PATCH PANEL TERMINATION
checkpoint | VISUAL CHECK ENSURING CABLE TO BE FITTED OFF IN CORRECT POSITION.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - DRAWING & SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | SELECTION OF CORRECT TOOL TO BE USED FOR TERMINATION TYPE.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - MANUFACTURER RECOMMENDATION
checkpoint | INSTALL PATCH PANEL INTO CABINET LOOM CABLES TO THE BACK OF THE PATCH PANEL. TIE INTO POSITION USING VELCRO STRIP AND/OR CABLE TIES SUPPLIED.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - AS 3080 & MANUFACT. REQUIREMENTS
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | ENSURE CABLES ARE STRIPPED NO MORE THAN THE SPECIFIED DISTANCE. CHECK TERMINATIONS AT COMPLETION FOR COLOUR CODE AND SEQUENCE.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - AS 3080 & MANUFACT. REQUIREMENTS
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | ATTACH WRAP AROUND LABEL TO CABLE NO MORE THAN 60MM FROM THE JACK. ENSURING CORRECT NUMBER SEQUENCE.
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - DRAWINGS & SEPC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL PATCH PANEL INTO EQUIPMENT RACK OR CABINET.
label | INSPECTION FUNCTION - CHECK.
label | APPLICABLE STANDARD - DRAWINGS & SEPC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | LABEL OUTLET ENSURING CORRECT NUMBER SEQUENCE
label | INSPECTION FUNCTION - ENSURE CORRECT LABEL TYPE.
label | APPLICABLE STANDARD - DRAWINGS & SEPC.
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-012 INSTALL DISTRIBUTION BOARDS - TERMINATE SUBMAINS CABLES | itp |  |  |  |  | ITP-012 INSTALL DISTRIBUTION BOARDS - TERMINATE SUBMAINS CABLES Rev 1
section | DISTRIBUTION BOARD
checkpoint | DELIVERY CHECK FOR DAMAGE, PAINT FINISH, DIMENSIONS AND DOORS AGAINST APPROVED SHOP DRAWING
label | INSPECTION FUNCTION - VISUAL CHECK
label | APPLICABLE STANDARD - AS SPEC.
checkpoint | LOCATE & FIX INTO POSITION
label | INSPECTION FUNCTION - CHECK FOR CLEARANCE, CHECK FIXING METHOD
label | APPLICABLE STANDARD - AS/NZS 3000:2007AS SPEC. ELECTRICAL DRAWINGS
checkpoint | INSTALL SUBMAINS CABLING AS APPROPRIATE EG. GLANDS, TRAY, DUCT
label | INSPECTION FUNCTION - INSTALLED CORRECTLY
label | APPLICABLE STANDARD - AS/NZS 3000:2007
checkpoint | INSTALL LUGS AND TERMINATE
label | INSPECTION FUNCTION - CHECK LUG SIZES, CHECK CONNECTIONS
label | APPLICABLE STANDARD - AS/NZS 3000:2007
checkpoint | ANY CABLES NOT TERMINATED PRIOR TO ENERGISATION MUST BE REMOVED FROM CUBICLE AT ORIGIN AND HAVE ENDS COVERED IN HEATSHRINK. AT DESTINATION CABLES MUST BE COVERED IN HEATSHRINK AND BE CONTAINED IN A JUNCTION BOX
label | INSPECTION FUNCTION - CHECK CONNECTIONS BOTH LINE AND LOAD
label | APPLICABLE STANDARD - AS/NZS 3000:2007
checkpoint | CLEAN & VACUUM
label | INSPECTION FUNCTION - VISUAL CHECK
label | APPLICABLE STANDARD - FREE OF FOREIGN MATERIAL
checkpoint | ORGANISE INPECTION BY INSPECTOR. LODGE PRESCRIBED / NON PRESCRIBED (AS APPLICABLE) CERTIFICATE OF ELECTRICAL SAFETY (IF REQUIRED).
label | INSPECTION FUNCTION - INSPECT
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CLEARLY IDENTIFY SERVICES
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - CLEARLY VISIBLE
section | WHEN READY TO ENERGISE PROCEED IN ACCORDANCE WITH ENERGISATION PROCEDURE
checkpoint | ENERGIZE & RECORD RESULTS ON ITP 116
label | INSPECTION FUNCTION - TEST
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CHECK SWITCHBOARD AS INSTALLED MATCHES SHOP DRAWING. IF NECCESARY MODIFY SHOP DRAWING TO MATCH INSTALLED & RETURN TO OFFICE
label | INSPECTION FUNCTION - VISUAL CHECK
label | APPLICABLE STANDARD - SHOP DRAWING
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CLEAN SWITCHBOARD CUPBOARD
label | INSPECTION FUNCTION - VISUAL CHECK
label | APPLICABLE STANDARD - CLEAN & TIDY
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-013 COMMISSIONING OF DISTRIBUTION BOARDS | itp |  |  |  |  | ITP-013 COMMISSIONING OF DISTRIBUTION BOARDS Rev 1
section | COMMISSIONING OF DISTRIBUTION BOARDS
checkpoint | PRIOR TO ENERGISING ALL PERSONNEL INVOLVED TO BE INDUCTED INTO ENERGISATION PROCEDURE AND ALL STEPS UNDERTAKEN TO ENSURE COMPLIANCE WITH THIS PROCEDURE
label | INSPECTION FUNCTION - INDUCT INTO SITE SPECIFIC ENERGISATION PROCEDURE
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | OBTAIN FRESH COPIES OF CURRENT LIGHT AND POWER DRAWINGS AND MARK UP ANY CHANGES FROM THE WORKING DRAWINGS
label | INSPECTION FUNCTION - VISUAL CHECK
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - IS CURRENT REVISION
checkpoint | OBTAIN COPY OF DISTRIBUTION BOARD SCHEDULE TO MARK UP ANY ADDITIONS OR DELETIONS FOUND WHILST COMMISSIONING
label | INSPECTION FUNCTION - VISUAL CHECK
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | COLLECT MATERIAL FROM OFFICE AND HAVE CORRECT DB STRUCTURE DOWNLOADED.
label | INSPECTION FUNCTION - ENSURE ACCURACY
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | COMMENCE COMMISSIONING
label | INSPECTION FUNCTION - TEST
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | UPDATE COPIES OF DISTRIBUTION BOARD SCHEDULE WITH ANY ADDITIONS/DELETIONS
label | INSPECTION FUNCTION - VISUAL CHECK
checkpoint | RETURN DB SCHEDULE TO OFFICE FOR TYPING OF SWITCHBOARD SCHEDULE, LEAVE COPY IN SWITCHBOARD
label | INSPECTION FUNCTION - COPY RETAINED
label | APPLICABLE STANDARD - INSTALLED
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CHECK TYPED SCHEDULE FOR ACCURACY AND INSTALL IN SCHEDULE HOLDER
label | INSPECTION FUNCTION - VISUAL CHECK
label | APPLICABLE STANDARD - SAME AS DB SCHEDULE
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CLEAN SWITCHBOARD CUPBOARD
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - CLEAN & TIDY
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-014 DISTRIBUTION BOARD TEST RESULTS | itp |  |  |  |  | ITP-014 DISTRIBUTION BOARD TEST RESULTS Rev 1
section | DISTRIBUTION BOARD TEST RESULTS
checkpoint-no-status | Details
textbox | VAST TESTING DEVICE EQUIPMENT NUMBER:
textbox | CERTIFICATE OF ELECTRICAL SAFETY NUMBER:
checkpoint | VISUAL INSPECTION
textbox | C/B NO.
textbox | CIRCUIT No.
textbox | NO. OF GPO’S SWITCHES
textbox | NO. OF LIGHTS
textbox | EARTH CONTINUITY & RESISTANCE: PASS RESULT |  |  | Ω
textbox | INSULATION RESISTANCE: PASS RESULT |  |  | Ω
checkpoint | POLARITY / CORRECT CONNECTIONS
textbox | EARTH LOOP IMPENDENCE: PASS |  |  | Ω
checkpoint | RCD TESTING CONTRACTUAL REQUIREMENT
textbox | QUANTITY LABELS REQUIRED: TRAFOLYTE
textbox | QUANTITY LABELS REQUIRED: PAPER
checkpoint-no-status | SCHEDULE: DESCRIPTION INCLUDE ROOM NO. / OR AREAS
textbox | SCHEDULE:
checklist | ITP-016 TERMINATE SUB CIRCUIT CABLING | itp |  |  |  |  | ITP-016 TERMINATE SUB CIRCUIT CABLING Rev 1
section | TERMINATE SUB CIRCUIT CABLING
checkpoint | INSTALL SUB CIRCUIT CABLING IN ACCORDANCE WITH DB SCHEDULE AND TERMINATE. IF CIRCUIT NOT COMPLETE AT THE OTHER END, IT MUST NOT BE TERMINATED BUT PLACED IN A JUNCTION BOX AT FIELD END AND IN CONNECTORS AT DISTRIBUTION BOARD END.
label | INSPECTION FUNCTION - CHECK CONNECTIONS, BOTH LINE & LOAD
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CLEAN & VACUUM
label | INSPECTION FUNCTION - VISUAL CHECK
label | APPLICABLE STANDARD - FREE OF FOREIGN MATERIAL
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | RECORD RELEVANT INFORMATION AND ANY CHANGES ON DB SCHEDULE. AND RETURN TO ADMINISTRATOR/OFFICE FOR COMMISSIONING TEAM
label | INSPECTION FUNCTION - ENSURE ACCURACY
label | APPLICABLE STANDARD - AS/NZS 3017-2001
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-017 CONSTRUCTION WIRING INSTALLATION, TEST & INSPECTION AND REMOVAL | itp |  |  |  |  | ITP-017 CONSTRUCTION WIRING INSTALLATION, TEST & INSPECTION AND REMOVAL Rev 1
section | CONSTRUCTION WIRING INSTALLATION, TEST & INSPECTION AND REMOVAL
checkpoint-no-status | Note: Tradespersons performing Construction Wiring must be holders of a current Electrical Installations on Construction and Demolition Site card.
checkpoint | PREPARE SINGLE LINE DIAGRAM OF PROPOSED DISTRIBUTION SYSTEM.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS 3000
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | REQUEST POWER DISTRIBUTION TO CONDUCT FAULT DISCRIMINATION STUDY TO VERIFY CORRECT FUNCTIONALITY.
label | INSPECTION FUNCTION - VISUAL SOFTWARE MODELING
label | APPLICABLE STANDARD - AS 3000 MANUFACT.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | ADJUST CIRCUIT BREAKER SIZES IF REQUIRED, MODIFY SINGLE LINE DIAGRAM. FILE COPY OF STUDY ON SITE. 6 MONTH TEST DATES TO BE ACTIVATED.
label | INSPECTION FUNCTION - VISUAL
section | SWITCHBOARDS - SWITCHBOARD CONNECITON CHECKLIST
checkpoint | POSITION AND FIX SWITCHBOARD.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS 3012, AS 300, Electrical Installations on Construction Sites
label | ACCEPTANCE CRITERIA - COMPLIES
section | INSTALLATION OF CABLING
checkpoint | CABLING MUST BE SUPPORTED AND PROTECTED FROM DAMAGE. CONSTRUCTION WIRING TAPE MUST BE FITTED AT EVERY 5 METRES.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS 3012, AS 300, Electrical Installations on Construction Sites
label | ACCEPTANCE CRITERIA - COMPLIES
section | CABLE TERMINATION
checkpoint | TERMINATE SUB CIRCUITS AND SUBMAINS.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS 3012, AS 300, Electrical Installations on Construction Sites
label | ACCEPTANCE CRITERIA - COMPLIES
section | COMMISSIONING
checkpoint | TEST AND COMMISSION.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS 3012, AS 300, Electrical Installations on Construction Sites
label | ACCEPTANCE CRITERIA - COMPLIES
section | CERTIFICATES OF ELECTRICAL SAFETY
checkpoint | LODGE PRESCRIBED/NON PRESCRIBED (AS APPLICABLE) CERTIFICATE OF ELECTRICAL SAFETY. ORGANISE INSPECTOR (IF REQUIRED). PERIODICAL CERTIFICATE TO BE ACTIVATED AND CORRESPONDING NUMEBR ATTACHED.
label | APPLICABLE STANDARD - Electricity Safety Act 1998. Electricity Safety (Installations) Regulations.
label | ACCEPTANCE CRITERIA - COMPLIES
section | CIRCUIT PROTECTION
checkpoint | EARTH LEAKAGE CIRCUIT BREAKERS ARE TO BE USED FOR CIRCUIT PROTECTION LIGHTS AND SHEDS, 30 MA, MAXIMUM OUTLETS: 30MA MAXIMUM
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS 3012, AS/NZS 3000:2007, Electrical Installations on Construction Sites
label | ACCEPTANCE CRITERIA - COMPLIES
section | ELCB TESTING
checkpoint | ELCB’S MUST BE FULLY TESTED INITIALLY AND THEN TESTED EVERY MONTH WITH RESULTS RECORDED AND C/B’S TAGGED.
label | INSPECTION FUNCTION - COMPLETION OF F 82, TESTING
label | APPLICABLE STANDARD - AS 3012, AS 300, Electrical Installations on Construction Sites
label | ACCEPTANCE CRITERIA - COMPLIES
section | INSPECTION OF PLANT & EQUIPMENT
checkpoint | THE INSTALLATION RESISTANCE OF ALL EQUIPMENT AND FLEXIBLE CORDS SHOULD BE CONDUCTED 3 MONTHLY. TEST AND TAG AS REQUIRED BY INDIVIDUAL SITE
textbox | TEST EQUIPMENT NO.
textbox | CALIBRATION DUE DATE.
label | APPLICABLE STANDARD - AS 3012, AS/NZS 3000:2007, Electrical Installations on Construction Sites
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | SIX MONTHLY RE-TESTING OF CONSTRUCTION WIRING INSTALLATION TO BE COMPLETED FOLLOWING INITIAL INSTALLATION.
label | APPLICABLE STANDARD - AS 3012, AS 3017, AS/NZS 3000:2007, Electrical Installations on Construction Sites
section | REMOVAL
checkpoint | REMOVE REDUNDANT MAINS, SUBMAINS, SUBCIRCUITS AND SWITCHBOARDS. MUST USE INSULATED TOOLS. CONSTRUCTION a A CLASS ELECTRICIAN ONLY ALLOWED TO REMOVE WIRING
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS 3012, AS 3017, AS/NZS 3000:2007, Electrical Installations on Construction Sites
checklist | ITP-018 LIGHT FITTING INSTALLATION | itp |  |  |  |  | ITP-018 LIGHT FITTING INSTALLATION Rev 1
section | LIGHT FITTING INSTALLATION
checkpoint | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS PER ORDER/ DRAWING NO. DAMAGE
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | LOCATIONS CO ORDINATE WITH OTHER SERVICES
label | INSPECTION FUNCTION - ENSURE NO CONFLICT WITH OTHER SERVICES ON SITE
label | APPLICABLE STANDARD - ADEQUATE CLEARANCE
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | MARKING OUT IF REQUIRED - REFER TO REFLECTED CEILING PLAN FOR SET OUT
label | INSPECTION FUNCTION - ENSURE CORRECT CUT OUT SIZE
label | APPLICABLE STANDARD - MANUFACT. DIMENSIONS
label | ACCEPTANCE CRITERIA - FITS TO NEW CEILING
checkpoint | PLUG IN OR FIT OFF LIGHT / PLUG BASE
label | INSPECTION FUNCTION - CHECK CONNECTIONS
label | APPLICABLE STANDARD - RE SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL LIGHT FITTING
label | INSPECTION FUNCTION - CHECK TYPE
label | APPLICABLE STANDARD - ELEC DRWG
label | ACCEPTANCE CRITERIA - CORRECT TYPE
checkpoint | INSTALL LAMPS AND DIFFUSER
label | INSPECTION FUNCTION - DO NOT TOUCH DIFFUSER
label | APPLICABLE STANDARD - RE SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CLEAN FITTING, LAMP DIFFUSER
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - CLEAN & WORKING
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-019 COPPER DATA & VOICE TESTING | itp |  |  |  |  | ITP-019 COPPER DATA & VOICE TESTING Rev 1
section | COPPER DATA & VOICE TESTING
checkpoint | VISUAL CHECK OF OUTLETS FOR COMPLETION.
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS/NZS 3080:2003
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | SELECTION OF CORRECT TESTING INSTRUMENT.
textbox | TEST DEVICE NUMBER:
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS/NZS 3080:2003:
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | SELECTION OF CORRECT SETTINGS FOR TEST INSTRUMENTS.
label | — CABLE TYPE
label | — OUTLET TYPE
label | — TERMINATION SEQUENCE
label | — VENDOR CABLING SPECIFICATIONS
label | — CORRECT AND SEQUENTIAL PROJECT DETAILS
label | INSPECTION FUNCTION - CHECK SETTINGS
label | APPLICABLE STANDARD - AS/NZS 3080:2003:
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | TEST OUTLETS AND RECORD TEST RESULTS AS SPECIFIED AND/OR REQUESTED
label | INSPECTION FUNCTION - TEST & RECORD
label | APPLICABLE STANDARD - AS/NZS 3080:2003
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | COMPLETE TELECOMMUNICATIONS CABLING ADVICE FORM AND ATTACHMENT IF REQUIRED
label | INSPECTION FUNCTION - TELECOMMUNICATIONS ADVICE
label | APPLICABLE STANDARD - AS/ACIF S009:2006
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-022 BAKELITE AND POWER INSTALLATION | itp |  |  |  |  | ITP-022 BAKELITE AND POWER INSTALLATION Rev 1
section | BAKELITE AND POWER INSTALLATION
checkpoint | CHECK DRAWINGS FOR QUANTITY, BRAND TYPE AND COLOUR
label | INSPECTION FUNCTION - CHECK MAKE & COLOUR
label | APPLICABLE STANDARD - AS SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | LOCATION/COMPLIANCE WET AREAS, HAZARDS ETC. MOUNTING HEIGHTS
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - AS/NZS 3000:2007 ELEC/DRWG
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | FIT OFF AND FIX SWITCHES, WHERE MULTI GANG SWITCHES WITH MULTI CIRCUITS ARE INVOLVED USE SHROUDS ON EACH SWITCH. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
label | INSPECTION FUNCTION - CORRECT TERMINATION POINT AND CONNECTIONS TIGHT. ALL SWITCHES ON CIRCUIT FITTED OR MADE SAFE.
label | APPLICABLE STANDARD - ELECTRICAL DRAWING. AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - CONNECTION CORRECT. HAND TIGHT. OUTLETS STRAIGHT AND LEVEL.
checkpoint | FIT OFF AND FIX GPO’S, WHERE A GPO IS LOCATED WITHIN 150mm OF A METAL STUD, USE SHROUD. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
label | INSPECTION FUNCTION - CORRECT TERMINATION POINT & CONNECTIONS TIGHT. ALL OUTLETS ON CIRCUIT FITTED OR MADE SAFE.
label | APPLICABLE STANDARD - ELECTRCIAL DRAWINGS AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - CONNECTION CORRECT HAND TIGHT. OUTLETS STRAIGHT AND LEVEL.
checkpoint | FIT OFF FINAL APPLIANCES
label | INSPECTION FUNCTION - CORRECT TERMINATION POINT & CONNECTIONS TIGHT
label | APPLICABLE STANDARD - ELECTRCIAL DRAWINGS AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - CONNECTION CORRECT HAND TIGHT
checkpoint | COVER PLATES (IF REQUIRED)
label | INSPECTION FUNCTION - CHECK & INSTALL
label | APPLICABLE STANDARD - AS SPEC.
label | ACCEPTANCE CRITERIA - INSTALLED
checkpoint | INSTALL LABEL (IF A SPECIFIED REQUIREMENT)
label | INSPECTION FUNCTION - ENSURE CORRECT TYPE, LABEL. ENSURE CORRECT CIRCUIT I.D
label | APPLICABLE STANDARD - AS SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-023 EXIT & EMERGENCY LIGHT INSTALLATION | itp |  |  |  |  | ITP-023 EXIT & EMERGENCY LIGHT INSTALLATION Rev 1
section | EXIT & EMERGENCY LIGHT INSTALLATION
checkpoint | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS PER ORDER/ DRAWING, NO DAMAGE
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | LOCATIONS CO ORDINATE WITH OTHER SERVICES
label | INSPECTION FUNCTION - ENSURE NO CONFLICT WITH OTHER SERVICES ON SITE
label | APPLICABLE STANDARD - ADEQUATE CLEARANCE
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint-no-status | Note – THE SEQUENCE OF STEPS 4 & 5 MAY ALTER, DEPENDANT ON THE LIGHT.
checkpoint | MARKING OUT (IF REQUIRED)- REFER TO REFLECTED CEILING PLAN FOR LOCATIONS
label | INSPECTION FUNCTION - ENSURE CORRECT CUT OUT SIZE
label | APPLICABLE STANDARD - MANUFACT. DIMENSIONS.
label | ACCEPTANCE CRITERIA - FITS WITH NO GAPS
checkpoint | PLUG IN OR FIT OFF LIGHT, FIT-OFF DATA CABLE IF APPLICABLE
label | INSPECTION FUNCTION - CHECK CONNECTIONS
label | APPLICABLE STANDARD - MANUFACTURERS SPEC.
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | NUMBER AND INSTALL LIGHT FITTING AND AS BUILT DRAWING
label | INSPECTION FUNCTION - CHECK TYPE
label | APPLICABLE STANDARD - ELEC. DRWGS
label | ACCEPTANCE CRITERIA - CORRECT TYPE
checkpoint | INSTALL LAMP & DIFFUSER AND CLEAN FITTING
label | INSPECTION FUNCTION - CHECK CORRECT TYPE, EXIT ARROW DIRECTIONS
label | APPLICABLE STANDARD - DRAWINGS
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | MARK UP LIGHTING DRAWING, DATA LOOP INCLUDED, NUMBERING ALL EXIT AND EMERGENCY LIGHTS (IF APPLICABLE)
label | INSPECTION FUNCTION - DRAWINGS MARKED UP
label | ACCEPTANCE CRITERIA - COMPLETE
checkpoint | RECORD INFORMATION ON DATABASE SHEET
label | INSPECTION FUNCTION - RECORD ON ITP 114
label | ACCEPTANCE CRITERIA - COMPLETE
checkpoint | COMPLETE LOG BOOK AND RECORD RESULTS IF APPLICABLE
label | INSPECTION FUNCTION - CHECK
label | APPLICABLE STANDARD - AS 2293-1
label | ACCEPTANCE CRITERIA - COMPLETE
checklist | ITP-025 SELECTION OF CABLES FOR SUBCIRCUIT WIRING TO MEET RQMNTS ETC | itp |  |  |  |  | ITP-025 SELECTION OF CABLES FOR SUBCIRCUIT WIRING TO MEET RQMNTS ETC Rev 1
section | SELECTION OF CABLES FOR SUBCIRCUIT WIRING TO MEET RQMNTS ETC
checkpoint | ASCERTAIN REQUIREMENTS OF SPECIFICATION FOR: CURRENT CARRYING CAPACITY VOLTAGE DROP LIMITATIONS FAULT LOOP IMPEDENCE.
section | CURRENT CARRYING CAPACITY
checkpoint | DETERMINE A MINIMUM SIZE CABLE TO SATISFY THE CURRENT CARRYING CAPACITY REQUIREMENTS. REFER TO TABLE 2 IN AS/NZS 3008:1. APPLY DERATIVE / RATING FACTOR.
label | APPLICABLE STANDARD - AS/NZS 3000:2007; AS/NZS 3008:1998
label | ACCEPTANCE CRITERIA - COMPLIES
section | VOLTAGE DROP LIMITATION
checkpoint | VOLTAGE DROP LIMITATION:
label | A) DETERMINE BY CALCULATION VOLTAGE DROP % IN CONSUMER AND SUBMAINS CABLE.
label | B) CALCULATE MAX. LENGTH OF SUBCIRCUIT UTILISING THE FOLLOWING INPUTS;
label | i) 5% LESS % CALCULATED IN A) UNLESS SPECIFIED OTHERWISE.
label | ii) CURRENT 50% OF C/B RATING.
label | APPLICABLE STANDARD - AS/NZS 3000:2007; AS/NZS 3008:1998
label | ACCEPTANCE CRITERIA - COMPLIES
section | FAULT LOOP IMPEDENCE
checkpoint | CALCULATE MAXIMUM CIRCUIT LENGTH IN METRES THAT WILL ENSURE CORRECT OPERATION OF PROTECTIVE DEVICES TO PROVIDE PROTECTION AGAINST INDIRECT CONTACT. TABLE B5.1 MAY BE UTILISED. HOWEVER THE TABLE DOES NOT PROVIDE DETAILS ON ALL POSSIBLE CONFIGURATIONS.
label | APPLICABLE STANDARD - AS/NZS 3000:2007; AS/NZS 3008:1998
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | MAXIMUM LENGTH OF CIRCUIT WILL BE DETERMINED BY THE SHORTEST MAXIMUM LENGHTH CALCULATED IN EITHER OF VOLTAGE DROP OR FAULT LOOP IMPEDENCE CALCULATION.
label | APPLICABLE STANDARD - AS/NZS 3000:2007; AS/NZS 3008:1998
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | A COPY OF ALL CALCULATIONS AND ASSUMPTIONS MADE IN DETERMINING CURRENT CARRYING CAPACITY AND MAXIMUM LENGTHS OF CIRCUIT IS TO BE ATTACHED TO THIS ITP.
label | APPLICABLE STANDARD - AS/NZS 3000:2007; AS/NZS 3008:1998
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | OBTAIN APPROVAL FROM CONSULTING ENGINEER IF ANY OF THE ABOVE CONFLICT WITH THE SPECIFICATIONS.
label | APPLICABLE STANDARD - AS/NZS 3000:2007; AS/NZS 3008:1998
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CABLE SIZES AND LENGTHS OF CIRCUIT DETERMINED BY THE ABOVE PROCESS ARE TO BE INPUT TO STEP 3 OF ITP 02.
checklist | ITP-026 INSTALLATION OF TEMPORARY POWER BOARD | itp |  |  |  |  | ITP-026 INSTALLATION OF TEMPORARY POWER BOARD Rev 1
section | INSTALLATION OF TEMPORARY POWER BOARD
checkpoint | LOCATE & FIX INTO POSITION BOLT TEMPORARY BOARD DOWN WITH AT LEAST 2 FIXINGS
label | INSPECTION FUNCTION - CHECK FOR CLEARANCE, CHECK FIXING METHOD
label | APPLICABLE STANDARD - AS/NZS 3000:2018, 3012:2010
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL SUBMAINS CABLING AS APPROPRIATE EG. GLANDS, TRAY, DUCT
label | INSPECTION FUNCTION - INSTALLED CORRECTLY
label | APPLICABLE STANDARD - AS/NZS 3000:2018, 3012:2010
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL LUGS AND TERMINATE
label | INSPECTION FUNCTION - CHECK LUG SIZES, CHECK CONNECTIONS
label | APPLICABLE STANDARD - AS/NZS 3000:2018, 3012:2010
checkpoint | ANY CABLES NOT TERMINATED PRIOR TO ENERGISATION MUST BE REMOVED FROM CUBICLE AT ORIGIN AND HAVE ENDS COVERED IN HEATSHRINK. AT DESTINATION CABLES MUST BE COVERED IN HEATSHRINK AND BE CONTAINED IN A JUNCTION BOX
label | INSPECTION FUNCTION - CHECK CONNECTIONS BOTH LINE AND LOAD
label | APPLICABLE STANDARD - AS/NZS 3000:2018, 3012:2010
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CLEARLY IDENTIFY SERVICES
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - CLEARLY VISIBLE
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | WHEN READY TO ENERGISE PROCEED IN ACCORDANCE WITH ENERGISATION PROCEDURE
label | APPLICABLE STANDARD - AS/NZS 3000:2018, 3012:2010
checkpoint | ENERGIZE & RECORD RESULTS ON ITP 14
label | INSPECTION FUNCTION - TEST
label | APPLICABLE STANDARD - AS/NZS 3000:2007
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | UPDATE TEMPORARY POWER BOARD REGISTER
label | APPLICABLE STANDARD - AS/NZS 3000:2018, 3012:2010
checklist | ITP-027 DECOMMISSION TEMPORARY POWER BOARD | itp |  |  |  |  | ITP-027 DECOMMISSION TEMPORARY POWER BOARD Rev 1
section | DECOMMISSION TEMPORARY POWER BOARD
checkpoint | Determine what the temporary board is controlling and confirm what action is required before board can be de-Commissioned.
label | INSPECTION FUNCTION - VISUAL, DUAL SIGN OFF
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | BUILDER INSPECTION - De-commission form issued to builder, 48hours notice to be given, Sign off builders checklist, Safety Committee Inspection, Final approval to be given by builder
label | INSPECTION FUNCTION - FORM TO BE COMPLETED
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | Perform voltage test to ensure power supply has been isolated, Disconnect supply cables, Fire sealing of penetrations
label | INSPECTION FUNCTION - TESTING, SEALING
checkpoint | Remove temporary board
label | INSPECTION FUNCTION - VISUAL
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | Update temporary power board register
label | INSPECTION FUNCTION - SIGN OFF
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-028 DE-COMMISSION ELECTRICAL EQUIPMENT | itp |  |  |  |  | ITP-028 DE-COMMISSION ELECTRICAL EQUIPMENT Rev 1
section | DE-COMMISSION ELECTRICAL EQUIPMENT
checkpoint | Determine what the Electrical Equipment is controlling and confirm what action is required before Equipment can be de-Commissioned.
label | INSPECTION FUNCTION - VISUAL, DUAL SIGN OFF
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | BUILDER INSPECTION - De-commission form (RISC Form) issued to builder, 48hours notice to be given, Sign off builders checklist, Safety Committee Inspection, Final approval to be given by builder
label | INSPECTION FUNCTION - FORM TO BE COMPLETED
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | Perform voltage test to ensure power supply has been isolated, Disconnect supply cables, Fire sealing of penetrations
label | INSPECTION FUNCTION - TESTING, SEALING
checkpoint | Remove Electrical Equipment
label | INSPECTION FUNCTION - VISUAL
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | Update any Switch board registers and labelling
label | INSPECTION FUNCTION - SIGN OFF
label | ACCEPTANCE CRITERIA - COMPLIES
checklist | ITP-028 LAYING U.GROUND ELECTRICAL CONDUITS UP TO DEPTH OF 1.5M | itp |  |  |  |  | ITP-028 LAYING U.GROUND ELECTRICAL CONDUITS UP TO DEPTH OF 1.5M Rev 1
section | LAYING U.GROUND ELECTRICAL CONDUITS UP TO DEPTH OF 1.5M
checkpoint | INSPECT CONDUIT MATERIAL TO CHECK THAT IT MEETS MATERIAL SPECIFICATIONS
label | INSPECTION FUNCTION - VISUAL, MEASURE KEY DIMENSIONS
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CHECK CONDUIT ALIGNMENT AS PER PLANS
label | INSPECTION FUNCTION - MEASURE
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | SET OUT MARKED, AND ALL SERVICES LOCATED
label | INSPECTION FUNCTION - VISUAL, MEASURE & LOCATE WHERE NECESSARY
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | ERECT PEDESTRIAN BARRICADING AS PER PLAN
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CHECK EXCAVTION DEPTH AGAINST PROPOSED ROAD LEVEL
label | INSPECTION FUNCTION - DRAWINGS & TECH STANDARDS
label | ○ *VEDN TECHNICAL STANDARDS
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | EXCAVATE TO THE TRENCH AS PER PLAN
label | INSPECTION FUNCTION - MINIMUM COVER AND WIDTH AS PER SPECIFICATION
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | PLACE SPECIFIED BEDDING MATERIAL IN TRENCH
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | PLACEMENT OF CONDUIT OF SPECIFIED SIZE IN ACCORDANCE WITH SPECIFICATIONS/DRAWINGS
label | INSPECTION FUNCTION - DRAWINGS & TECH STANDARDS
label | ○ *VEDN TECHNICAL STANDARDS
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | BACKFILL OVER CONDUIT TO 300MM
label | INSPECTION FUNCTION - VISUAL AND MEASURE
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL COVER SLABS ABOVE CONDUIT
label | INSPECTION FUNCTION - DEPTH AS PER TECH STANDARDS & MEASURE
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | INSTALL MARKER TAPE ABOVE CONDUIT
label | INSPECTION FUNCTION - DEPTH AS PER TECH STANDARDS & MEASURE
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | BACK FILL AND REINSTATEMENT OF GROUND
label | INSPECTION FUNCTION - DRAWINGS & TECH STANDARDS*
label | ○ *VEDN TECHNICAL STANDARDS
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES
checkpoint | CHECK STABILISED FCR BACKFILL 200MM BELOW PROPOSED ROAD LEVEL, COMPACTED FCR ABOVE THAT
label | INSPECTION FUNCTION - VISUAL
label | APPLICABLE STANDARD - AS3000 SERVICE INSTALLATION RULES 2014
label | ACCEPTANCE CRITERIA - COMPLIES