## ITP Cover Page
Wastewater PE Inspection Test Plan
Project: Peacocke Whatukooruru Drive
Number and Revision: DN1205 - 111 - Rev C
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | Peacocke Whatukooruru Drive |  |  |  |  | ITP Number: |  |  | 111
Project Number: |  |  | DN1205 |  |  |  |  | ITP Status: |  |  | Draft For Approval
ITP Description: |  |  | Wastewater PE |  |  |  |  | Revision: | 1000 |  | C
Contract Number: |  |  | Peacocke Whatukooruru Drive |  |  |  |  | Drawing Sets: |  |  | 146000-002A-2301 to 146000-002A-2396
Customer: |  |  | Hamilton City Council |  |  |  |  | Specification: |  |  | Project Specification and Appendices.
Quality Specified: |  |  | NZTA Z/1
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  |  | Responsibilities Key
A | Draft for Review | 2023-02-08 |  | Nicola Turner |  | First revision for review & approval |  |  |  | A | Action |  |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  |  | CR | Customer Rep
B | Draft for Review | 13/09.2024 |  | Nicola Turner |  | Second revision ammendments made per BBO advice via InEight (DN1205-DOW-RFI-0268.01) |  |  |  | C | Check |  |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  |  | PM | Project Manager
C | Draft for Review | 2024-10-23 |  | Nicola Turner |  | Third revision ammended to include manhole constructionper BBO request via InEight (DN1205-DOW-RFI-0268.03) |  |  |  | E | Examine |  |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) |  |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) |  |  | QM | QA Manager / Rep
[10 empty] | I | Inspection |  |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  |  | SE | Site Engineer
[10 empty] | O | Operation |  |  | QE | Quality Engineer
[10 empty] | R | Review |  |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  |  | SV | Surveyor
[10 empty] | V | Visual Verification |  |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point |  |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  |  | Signature: |  |  | Date:
Downer PM | [7 empty] | Downer PM
Downer QM | [7 empty] | Downer QM
Client (If Applicable) | [7 empty] | Client (If Applicable)

## ITP Master Body
Wastewater PE Inspection Test Plan
Project: Peacocke Whatukooruru Drive
Number and Revision: DN1205 - 111 - Rev C
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity
[6 empty] | Activity | By
SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
1.1 | Extent of Line Setout | Ensure line and level of wastewater has been marked out and agreed with Engineer in accordance with the drawings. Identify any clashes before construction. | Design Drawings | ITP Sign Off | Prior to Construction & Every Revision of IFC Drgs / Data | M | PE
1.2 | Environmental Protection | Install Erosion Sediment Control measures in line with PWRBSS ESCP plans Inspect, monitor, and maintain ESCP measures weekly and immediately before & after significant weather events | Project ESCP Plans | ITP Sign Off | Prior to Construction Inspect, Monitor, and Maintain Weekly and immediately before and after significant weather events | M | PE
1.3 | Stakeholder | Inform stakeholders of upcoming works Agree plans for maintaining access to properties during construction with landowners | Project Stakeholder Management Plan | ITP Sign Off | Prior to Construction with continue updates throughout the works | M | PE
1.4 | Permits | Permit to Dig must be in place before any ground breaking activity commences, incl. trenching, driving waratahs or survey pegs, and topsoil strip. Permit to Dig will be based on BBO existing Services Drawings, Before U Dig Plans , potholing by the project, CAT & Genny survey, and visual inspections. All known services must be clearly marked on site and briefed to the workforce . | Section 2.2.10 Project Specification | Ground Disturbance Permit DN-ZH-FM043.1 | Prior to Construction Reviewed and Reissued weekly or when site conditions change | H | PE
SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
2.1 | Pipes/Fittings/precast Units | Confirm pipes diameter and class as shown on the drawings. Pipe dimensions given on the drawings are nominal outside diameters. Manufacturer verification/records of compliance of PE pipe (i.e. pipe resin data) | Project Specification | Visual Check Manufacturer's Verification | Each Delivery to Site | S | PE
2.2 | Undercut Backfill/Bedding/Side/Haunch/Overlay/Backfill Material Compliance | Confirm material grading and density of pit sand | AS/NZS2566 G1 (or otherwise) | IANZ Lab Test Reports | 1 Test per 1000m3 | H | PE
SECTION 3 – CONSTRUCTION ACTIVITY
3.1 PIPELINE
3.1.1 | Foundation Compliance | Scala 3 blows/100mm Vane Shear Strength 70kPa | Project Specification 4.3 | Scala test result | Every 20m along trench 1 test every 5m² at driveways and footpaths | H | QE
3.1.2 | Undercut Backfill Compliance | NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 95%(Average98%) of MDD | Non cohesive material - Minimum Density Index (DI) of 60 or 95% of MDD AS/NZs 3725:2007 | IANZ Lab Test Report | Based on Undercut Section | H | QE
3.1.3 | Bedding Compaction Testing | NDM Back Scatter Minimum Compaction 95%(Average98%) of MDD | Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002 | IANZ Lab Test Report | Every 20m along trench 1 test every 5m² at driveways and footpaths | H | QE
3.1.5 | Overlay Compaction Testing Overlay zone shall extend from top of Side Zone to 600mm above the top of the pipe. 2 lifts of 300mm should be placed. | NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 92% of MDD | Non cohesive material - Minimum Density Index (DI) of 60 or 92% of MDD AS/NZS 3725:2007 | IANZ Lab Test Report | Every 20m along trench 1 test every 5m² at driveways and footpaths | H | QE
3.1.6 | Collection of Waipa ITPs | ITP 04 Butt Welding | PWRBSS Quality Management Plan | Document Review | Once | HP | ENG
3.1.7 | Backfill Inspection | Inspection of pipes prior to backfilling to ensure correct installation. No damages caused to the pipeline. | Project Specification 4.3 | Photographs | Continous | S | PE
3.1.8 | Survey | All wastewater lines shall be laid per design layout. The deviation from approved design alignment permitted either in plan or elevation shall be: Vertical tolerance ± 50mm on straight and 100mm in curves | Vertical tolerance +/- 50mm Horizontal +/- 100mm | Survey Data | Continous | C | SV
3.1.9 | Backfill Compaction Testing | NDM Direct Transmission with a probe depth of 300mm Testing to be completed on 500mm lifts of backfill - 95% of MDD at OMC | Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002 | IANZ Lab Test Report | Every 20m along trench 1 test every 5m² at driveways and footpaths | H | QE
3.1.10 | End Caps | Red-painted sealed end per RITS D5.4. | RITS D5.4 | Photographs | Each End Cap | S | PE
3.2 ROMOLD MANHOLE
3.2.1 | Manhole Foundation Compliance | Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa | Project Specification 4.3 | IANZ Scala test result | 1 Test/Manhole | H | QE
3.2.2 | Undercut Backfill Compliance | NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 95% of MDD | HS2 backfil Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 3725:2012 | IANZ Lab Test Report | 1 Test/Manhole if Undercut required | H | QE
3.2.3 | Bedding Compaction Testing | NDM Back Scatter Minimum Compaction 95% of MDD | HS2 backfil Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 3725:2012 | IANZ Lab Test Report | 1 Test/Manhole | H | QE
3.2.4 | Backfill Inspection | Inspection of pipes prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the manhole | Project Specification 4.3 | Photographs | Continous | S | PE
3.2.5 | Backfill Testing | NDM Direct Transmission with a probe depth of 300mm Testing to be completed on 500mm lifts of backfill - 95% of MDD at OMC. Minimum Compaction 95%(Average98%) of MDD | MDD Average of 98% with minimum of 95% PS 4.5 | IANZ Lab Test Report | 4 Density tests per layer at Quarter Points Around Structure | H | QE
3.2.6 | Concrete Load Distribution Ring | Installed per manufacturers requirements. | BBO Request | Photographs | Each romold manhole | S | PE
3.3 TESTING & REINSTATEMENT
3.3.1 | Pressure Testing Methodology | Subcontractor to submit to method statement prior to testing. | PS Appendix L 3.10 | Engineer's confirmation of witness test | Notification required 2 working days prior to testing | H | ENG
3.3.2 | Pressure Testing Qualification | Confirmation of qualification of personnel supervising the test. | PS Appendix L 3.10.3 | Qualification | Once per supervisor | S | PE
3.3.3 | PE Pipeline Pressure Test | Unless otherwise specified and approved with line-specific methodolfy (i.e. Pressuremain 04 and 03). Testing to be undertaken on completion of invasive/major works. M5 per NZS 2566.2, test pressure 1.25x lowest rated component. | PS Appendix L 3.10.10 (RFI-0268) | Pressure Test Report incl. data log in .csv or .xls format | Per methodology | H | ENG
3.3.4 | Romold Manhole
SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
4.1 | Unforeseen Items | Upload items which may not be captured appropriately above (i.e. EF Coupler Installation) | BBO Request | Misc. | Once per lot | C | PE
4.2 | Survey As-Builts | Quality Check on New Works | Project Specification | Survey Data As Built Drawings Photographs Red Pen As-Builts including Undercuts | Post Works Completion | H | SV