## Resources
Type | Id | Name | Values | Prompting Name
checklist | b1832b7a-a98e-4f92-936f-06626789fef8 | Communications - Copper |  | Copper
checkpoint | 76c3fe8f-3ddc-4a5e-a05c-ba977ab9a969 | Cabling is not susceptible to mechanical damage.
checkpoint | e18f9918-2b47-40e2-91f9-5482c3f7b9ec | Cable is dressed on the cable pathways with velcro.
checkpoint | eee317b7-8f5b-4eb2-883e-61d2e1a00f59 | Apply a plastic wrap printed label to each end of the cable.
checkpoint | 2f3a1f84-388b-47df-90de-dde96ff660f7 | Cable is terminated into a faceplate or surface mount block.
checkpoint | 78caadc4-7dd4-4b82-a55a-b5670488ad92 | Cable is terminated into the correct patch panel reflected in the communication cabinet elevations.
checkpoint | fe7c9542-22b6-49bb-8910-c5e9721757f7 | The patch panel, faceplate/surface mount block are labelled correctly with a traffolyte.
signoff | dfbecaf3-200a-4be9-8412-b04a17a436d1 | Checked By (Heyday/MDE):
checklist | 443eca7d-a2e8-4c87-9677-f00b0242b663 | Quality - Light Pole Installation |  | Quality - Light Pole Installation
section | b332fb7b-427d-414c-b5cb-8e86f4847882 | Details
checkpoint | ab2d546b-f890-4fc1-81ae-7bc52acf70ba | Receipt of Pole Lights to site & storage. (ITP Reference Item 1)
checkpoint | 1f8e819f-a4c7-406e-825d-37a9e6f5c53a | Select correct Pole Light Type for location. (ITP Reference Item 2) HOLD POINT
checkpoint | d7ce0c2f-d79b-4f14-817d-8498cb0cc100 | Install to the location as per Heyday IFC Drawings (ITP Reference Item 3)
checkpoint | 0e2a6517-9ab1-4b35-85b0-3ce2f0bd3a56 | Connection to footing and levelling (ITP Reference Item 4)
checkpoint | 2370bfe8-a969-4806-8e87-158d373a1720 | Base Plate Grouting (ITP Reference Item 5)
checkpoint | 767d3422-cd9a-4ace-abe0-d8e0cf04d7e7 | Termination of Light Pole (ITP Reference Item 6)
checkpoint | e3fca214-7759-443c-952c-8c2daf00b1b9 | Photo evidence captured of Light Pole Installation. (ITP Reference Item 7)
signoff | eb807203-b6aa-40ce-bc9c-3a9203c55658 | Signoff Required from Heyday & Multiplex
checklist | 2e96ad2c-caef-477a-9068-962baf335263 | Testing & Commissioning - Solar Photovoltaic System (Pre-energisation) |  | Solar Photovoltaic System (Pre-energisation)
checkpoint | a03a5368-d0b8-481b-9289-debec47e63ce | SCS Commissioning Checklist Section 5 (System Measurements – Inverter)
checklist | a906754c-d403-475f-ad3b-c70a140dc0bc | zSYS - Testing & Commissioning - Low Voltage Cables (Mains/Submains) (old version) |  | Low Voltage Cables (Mains/Submains)
section | b418aaab-9b06-44b0-94e1-3ede97d477ce | WSA20-MPX-04000-EL-ITC-31052000 Construction Tests (Pre-energisation)
checkpoint | d188b021-c32b-41f7-87bb-11f766286f2e | Pre-requisite Works
checkpoint | 81489160-48f7-46d0-a24e-949ea95b267f | Insulation Damage
checkpoint | 3b51b38e-15d0-405b-bb07-6d92793c3096 | Correct Type of Termination
checkpoint | d745f718-f2d9-4418-9af8-482a8be6b609 | Correct Cable Size and Labelling
signoff | add92717-6d4d-42c9-a6fb-ee5a9a64abac | Checked By (Heyday):
checkpoint-no-value | d76b7d3e-7893-4898-abc4-7856524a63d9 | Insulation Resistance
checkpoint | 56eb7263-d352-4540-82b1-504626d33d1d | R-W
button | ffa14fb8-15fd-51d3-9959-4f7d19cde905 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 242417f9-5a72-5339-bb58-a99423be5f8b | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 5b556e62-d9b7-4870-83b4-50bcbfac5b7b | R-B
button | d264b0c7-b7b7-5cf2-b6bb-3b5c00524887 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 0c066d3c-ad99-5a06-acf6-19a238b6f102 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | b894838a-385c-40e9-8bec-73c371bac414 | W-B
button | a32e441a-079d-5043-a3bc-415f3864e642 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 40ad8e62-206b-5705-8b53-ce6ece09e0f8 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 0f550083-67ea-4967-83dc-d3339a498887 | R-N
button | a39f5898-cb63-5d41-a52f-5373c95efa9d | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | da8fc1d5-493b-538b-8d0e-e94a4bdaa36e | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 1ca94486-039c-4892-b3cf-8b780e2b858b | W-N
button | b731a9ca-d585-5762-b127-5a2ed792318a | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 76375cf2-58cd-5a2c-a86c-3a8f4bc01d66 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 55fb3f15-268b-4b3d-be21-064d7b8bec24 | B-N
button | 1ef2a404-1241-5090-bd5f-a20e3b80ed3d | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | b98d8928-132f-5007-acd0-fd77fd7d66e6 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 19d841c7-986a-4238-b259-17523fb3bb5f | R-E
button | 24e3b97c-0376-56ee-ab9d-492b702ecd5f | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | cbb384d6-87cc-5bd0-80c9-5cd5ec350f34 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 35f93450-7f45-4b73-9c65-e31af3dbe3de | W-E
button | 214f0871-62cd-5860-a5ec-4d96a351d1e7 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 044f765f-8df4-5d3e-9f4c-7e54ac782b40 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 46bac21d-9f13-4a6d-8a04-6d46873a27d0 | B-E
button | 5291d96c-05bc-5957-b448-f1e5a03bc9db | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 3062c198-f593-5c2b-843f-b8abef93aced | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 006f4405-0150-4aac-86ae-fa57737e7f32 | N-E
button | 0058342c-260a-5ef7-9873-946cd8aa6e80 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 9695a55b-bc10-527e-bfc7-bc4b29254b29 | Actual Reading if <500MΩ/<1000MΩ
signoff | 0cbd4359-3351-4abc-abb2-88817f7234e2 | Checked By (Heyday):
checkpoint-no-value | 69e479e3-25e8-4b7d-ae31-c19a2b1f1683 | Continuity Testing
checkpoint | 14b261e0-1977-4da5-a31a-8f1226ba7306 | Red Phase
textbox | 1daee8fc-c745-5e9f-bab2-360139c10f57 | Resistance (Ω)
textbox | c761c802-992a-5093-9e69-1a799880a4ef | Target Resistance (Ω)
checkpoint | a16308e0-bc73-4098-a838-b7578c171046 | White Phase
textbox | 7ac1f684-4f70-58b9-99b1-4ee70b94823e | Resistance (Ω)
textbox | 057a6a73-b8d3-575a-8851-bcc2fd7532b1 | Target Resistance (Ω)
checkpoint | b31431ac-ddb0-4902-b913-4e5629a26318 | Blue Phase
textbox | f5b1e39e-3fe7-562c-80a6-86c9c4053244 | Resistance (Ω)
textbox | 08dfa819-d9a2-5b7d-a54d-d64641fe62ca | Target Resistance (Ω)
checkpoint | 2626f720-b759-48cc-b13a-655b28d109e3 | Neutral
textbox | 1e3b691f-5fec-538c-9b80-691e6cf151ef | Resistance (Ω)
textbox | 394687c1-f09d-5872-abcb-eb9386c50309 | Target Resistance (Ω)
checkpoint | 48d0ec5e-d841-4f36-8bd6-7ba123ce2bd4 | Earth
textbox | d447ed02-2ed7-577b-a490-c9b653ca4175 | Resistance (Ω)
textbox | 3e11c70b-d516-52bc-b417-39a4e2b3ca8f | Target Resistance (Ω)
signoff | db751fa8-560a-4f0b-ab49-64a991b9aca7 | Checked By (Heyday):
section | 3d441328-ff3d-4850-9693-19a85fa9c3fe | WSA20-MPX-04000-EL-ITC-31053000 Component (Energised)
checkpoint-no-value | 77fc7e3f-a00d-4e51-856b-ff185d4f06fa | Phase Rotation
button | 8ffdb850-aed3-5361-a6a8-5313f2b948ef | Direction | Clockwise,Anti-Clockwise
signoff | e126b328-38f6-42d6-9218-6e1cd2d45b2e | Checked By (Heyday):
checkpoint-no-value | af343016-3efe-4d7a-a4ae-ed3e650a7add | Voltage
checkpoint | 1ab20a6f-41d1-4fb4-abef-9f9e77bff94a | Red - White
textbox | a3188b29-a1c9-563d-a1c6-40ae982fca5a | Voltage (V)
checkpoint | 77c308c5-7443-40cd-b1c3-e691ea6f7e3a | Red - Blue
textbox | 087bfc0f-94ac-52b8-876b-9aedf3296b15 | Voltage (V)
checkpoint | 2384e992-b276-4ebb-847a-e56f7367de81 | White - Blue
textbox | 13994845-428f-544a-9577-7317f84f3a4d | Voltage (V)
checkpoint | b51e7cb2-4cf8-4edf-831c-d56ca03649dd | Red - Neutral
textbox | 7b8ec0c2-8698-51c4-bad0-630a1daf392e | Voltage (V)
checkpoint | 3c14003b-2c46-4bf4-b41c-d33d24eb1f36 | White - Neutral
textbox | 11339380-881a-5e02-a87f-f0749e268f6e | Voltage (V)
checkpoint | fa91cc59-fd27-44f4-90a8-d6816bf0b33d | Blue - Neutral
textbox | 9efc517a-8f9e-579a-8113-9446da70c6fb | Voltage (V)
checkpoint | 0703d3fd-5af2-4732-b261-3d3ed41c126b | Red - Earth
textbox | 231229c4-d448-5b42-90e9-9c8e3d4274c6 | Voltage (V)
checkpoint | b6908b13-b575-47d7-94a0-5f69900ee350 | White - Earth
textbox | 12d987c2-e738-5d10-9e6d-d60a60fc0c2d | Voltage (V)
checkpoint | 7755019a-58ab-4d7b-939c-577677253e59 | Blue - Earth
textbox | c30baabc-8880-5c44-8d99-29366cbceaa8 | Voltage (V)
signoff | 744591f0-83c0-42bd-8996-f7a302ecc020 | Checked By (Heyday):
checklist | 264c3934-9552-474e-a440-07c77ad73347 | Testing & Commissioning - UPS (System Commissioning) |  | UPS (System Commissioning)
checkpoint | 57bc2b37-cbf2-41b6-be97-f08b875fd4cc | UPS – Functional Performance Test Report
note | 66cfeccd-867d-5d84-b88f-b0e6be08bdd0 | The following tests are conducted (see Schneider Electric - Site Acceptance test protocol for results and trends):
note | 248e2182-3c88-548a-9d16-83cbfe1cffe2 | ○ Load Transfer test
note | 3165be1c-67e3-513d-ba2d-739729acf2db | ○ Inverter to bypass transition on NO LOAD
note | ba06c38d-84b0-57ab-bb2f-af01b1a45b9e | ○ Inverter to bypass transition on FULL LOAD
note | 4ad73757-b2d1-5e11-93d0-de966663e293 | ○ Load step test (0%-50%-0%)
note | 6abf185b-84cd-59af-a6a5-7d2db2ef381f | ○ Load step test (25%-75%-25%)
note | af8c85e8-d471-58c9-95fd-2b7d7aa46aa1 | ○ Load step test (50%-100%-50%)
note | 8b7ebabc-e30a-5299-a59e-03185a8dd2c9 | ○ Load step test (75%-100%-75%)
note | 1869e058-9c4b-5cda-9106-e67d703976e6 | ○ Load step test (0%-100%-0%)
note | cc904bb5-37bd-559e-8661-48790dccc0b4 | ○ THDi and THDv measurements (0%, 25%, 50%,75%, 100%)
note | 10f48170-9c16-5cb5-b41d-534c75ee3fd1 | ○ Expected Results: Total Harmonic Distortion (THD) is to be under 5%
note | 36eb3717-5cff-57d2-b2b6-e013a4b9f1ac | ○ UPS efficiency calculation (Unity PF@0%, 25%, 50%, 75%, 100%)
note | a6c23fcf-6893-5fce-a12b-7cb207ee50e1 | ○ UPS battery discharge test (15min EOL)
signoff | 293955cf-2d1d-4d00-b4c9-a555503de06c | Checked By (Heyday):
checklist | 0768c84e-b3bd-4c6a-aa09-13255ac65d50 | Quality - Busduct |  | Quality - Busduct
checkpoint | b5e3fe26-c783-40f9-bcd4-eaf2b88586e1 | Receipt of busduct/ busway & take off box's delivery to site
checkpoint | a3ff3953-176a-4f1f-aa7e-1986d652eda6 | Set out - Ensure correct size, type and spare capacity
checkpoint | d6a046bc-7068-4c9b-9b6c-f8328e22b064 | Accessories to be factory made items
checkpoint | 65db417e-1f27-4f5e-819c-78b92e4a29e3 | Hangers installed as per the drawings
checkpoint | 299dea92-5f16-4433-a952-cfa942e266da | IR Test of Busduct - Separate - Test Result Above 1M Ω
checkpoint | 8454a122-48a5-4d58-aebe-c3d8bdefcfe4 | Busduct Piece are installed safely
checkpoint | c87d056a-92e3-4209-8b5a-28c6bf6d1ea5 | Busduct Torqued to 95Nm
checkpoint | 29e3b00e-cad7-45d1-917f-5c5cf497b715 | IR Test of Busduct - Joined - Test Result Above 1M Ω
checkpoint | ac33c530-7829-4181-9de4-04f2f3f3f53c | Photos attached of installed piece
checklist | cd19afae-43c1-494e-97bd-9a30d61e02a9 | Quality - Light Fitting Installation |  | Quality - Light Fitting Installation
section | fad17488-ad94-4b71-80cd-90db66bcd739 | Quality - Light Fitting Installation
checkpoint | 89ecbeb9-1176-423a-a888-6e80c6c51b71 | Installed to the correct location as per drawings
checkpoint | 0168e49d-c352-4cae-8363-eed09392b39c | Installed correct size and light fitting type
checkpoint | c53357d7-708d-4ff4-8f0b-7f960ca71412 | Correct Operation
checkpoint | 04d30ae1-e08f-42ea-8806-db9349c16e3d | Installed to the correct Circuit & DB Destination
checkpoint | 5b70a775-2872-4c45-919a-788a71d64678 | Correct labelling of light fitting (if required)
signoff | eb0747c8-65ab-474a-930b-ad1bca04f6de | Signoff Required from Heyday
checklist | ff0e237c-dd3c-4bd6-9493-b3cb341861c7 | Testing & Commissioning - Load Bank |  | Load Bank
section | 536dda0e-5101-4baf-9bdf-b0735aff5fb9 | WSA20-MPX-04000-EL-ITC-31143000 - Component Tests (Pre-commissioning)
checkpoint | 7bdbd1de-9025-4189-85e4-2fcb1213e2e6 | Sephco Commissioning Checklist
signoff | f3d07a75-f318-4c18-bc0e-9b2acceba9c5 | Checked By (Heyday):
checklist | 3ca3689f-77c0-48c2-ab24-e1d735cf09e7 | Testing & Commissioning - 3 Phase Subcircuit |  | 3 Phase Subcircuit
section | 861fd99c-dca8-43d2-8e4b-f8409081293a | Pre-requisite Works
checkpoint | 6da69891-19bb-46f6-a2d4-9b9cf3d8e4bc | Insulation Damage
checkpoint | 7225f360-ac04-4778-95db-9dbcc07e76ac | Correct Type of Termination
checkpoint | 3971722c-baa9-43a9-aa06-c86c6056edfb | Correct Colour Code
checkpoint | 9708cbf1-ec02-4027-9710-1f71e383629d | Correct Outlet Rating and Size
checkpoint | e327169b-3ebd-4006-adbb-d344cb7384ca | Earth Continuity
textbox | d1fad654-d6b7-5aaa-ad18-5ced852d1212 | Resistance (Ω)
checkpoint | 21706f16-3e14-4132-869a-39878965623e | Polarity Check
button | a878f000-c1ad-5c8c-917d-0e62e1a0e5c2 | No Transposition | YES,NO
button | b8ec0463-70f4-5599-97fb-21e80b4abc49 | Switch in Active | YES,NO
section | 9cac9730-f4a3-4380-b5fb-b44eee12d42e | Insulation Resistance
checkpoint | 96dd6692-f9e5-4dbd-8b51-64a37deb1e6e | R-W
button | 2b39491a-1d6a-511a-82f4-71cfabd13a8c | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | d348ccc8-6968-5dae-a021-9c9ceffa5e6f | Actual Reading if <200MΩ/<500MΩ
checkpoint | f206d7ac-521d-4be4-8f41-eea8e2e1e3bf | R-B
button | 52a2c584-84aa-5609-880b-8300f96e8f5e | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | f9cb7812-44c5-52af-a9b2-3ffb8d4e72a6 | Actual Reading if <200MΩ/<500MΩ
checkpoint | 882b4c0f-8dcb-4d8c-8881-b4c7b13c157a | W-B
button | c6af3168-67a5-5e0e-935f-deba5b39563d | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 92fa960a-d385-55d2-a305-6489a079a3f0 | Actual Reading if <200MΩ/<500MΩ
checkpoint | 8ed72945-9322-49ab-879b-2450c3ad8f68 | R-N
button | f3510836-c94f-5348-bc00-0fe3bd323739 | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 8f7cadda-8d23-53d8-af25-7ee29ed9e6e2 | Actual Reading if <200MΩ/<500MΩ
checkpoint | 3ce7661c-5fca-41d4-a5a5-790a3a4b01c6 | W-N
button | 4037876f-d6e5-5dbc-9a61-0e8ea3923279 | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | d477f3c7-aa58-5755-aa05-0b066a1b7cef | Actual Reading if <200MΩ/<500MΩ
checkpoint | 9651f12e-c9a4-442d-bc8c-f11c854fa56e | B-N
button | 4605fcfd-7b25-5173-a9e7-a07339fd902c | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | a0128354-5305-5bf4-8282-5f7a8295fc7f | Actual Reading if <200MΩ/<500MΩ
checkpoint | 6e4631a7-7c3b-405e-ab1b-9f82b89f9fd9 | R-E
button | c64a6297-5d59-5b92-87a9-d2b62a3fbf04 | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 144b208d-ae23-5be7-9e51-128cf9d3dcc2 | Actual Reading if <200MΩ/<500MΩ
checkpoint | 0fccc83f-b50d-4cc0-a288-d4c98f56d0fd | W-E
button | a0b931b0-76eb-54d1-bfa0-459efcda5dcf | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 84054121-9153-5416-93f7-c6d93908d8d6 | Actual Reading if <200MΩ/<500MΩ
checkpoint | fc799b05-5f47-4321-a8db-0c227ad69d10 | B-E
button | 729c09c8-067e-5ce3-8113-46aaef757ae0 | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | f51bf965-727e-5964-8a37-3fb5928b1a41 | Actual Reading if <200MΩ/<500MΩ
checkpoint | 827f6e60-be17-4eca-9c30-2c54ef6f95c4 | N-E
button | 977a6a16-6d9e-51d3-9adc-0d181d6c3fed | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 22efc18d-777c-5ae2-9787-29ab2333ca6e | Actual Reading if <200MΩ/<500MΩ
section | e60f69f2-5a59-44f0-8566-b462615f9a6b | Voltage
checkpoint | cac5f44a-a6bc-43b1-bc53-f27a0da64f14 | Red - White
textbox | d4f6e39a-cf4b-52ba-bdcb-be3fcffe2da4 | Voltage (V)
checkpoint | 04166c8d-957b-4eff-8864-5075cad5d374 | Red - Blue
textbox | c2419cc4-d59c-522d-bc84-c1b9e086ff6d | Voltage (V)
checkpoint | 8d39a288-efcc-46a4-94b9-e7db2c44ff87 | White - Blue
textbox | b6a6b526-117f-5e79-8caf-03a2f65b3c2c | Voltage (V)
checkpoint | 37f3f198-3fa3-4e3c-8adc-2d6c6cbb04a1 | Red - Neutral
textbox | 84e20906-51b7-5586-ba8a-2d4a0116eb57 | Voltage (V)
checkpoint | ba9cca36-b89a-4d4e-91ec-08c54b9d4d4d | White - Neutral
textbox | 5b8dd4b2-2a55-5141-8932-7780c4377448 | Voltage (V)
checkpoint | 105d0dae-3ddb-45ad-8b9a-83a2318b7f89 | Blue - Neutral
textbox | d043e074-431b-5586-a349-5e7e8b33c605 | Voltage (V)
checkpoint | f2f49762-0dc4-40de-95b0-61b04776d6e4 | Red - Earth
textbox | d88e464b-bed5-5f0c-af21-50d796bb2403 | Voltage (V)
checkpoint | 2d1255f8-a0dd-4086-9488-3b81ccfe8362 | White - Earth
textbox | 525be556-c6cd-5964-97e9-9b8c22e9604b | Voltage (V)
checkpoint | f436332f-ea9d-4c26-baaf-6498f0980e05 | Blue - Earth
textbox | a12e795b-46a0-5ee2-be31-e824ee9c758c | Voltage (V)
section | 4bb0e1c9-4368-4df3-bb6e-c9fb61376ee0 | Earth Fault Loop Impedance Test / RCD-RCBO Tripping Test
checkpoint | b0df5f2e-1ff1-49a7-8eba-c133f962acfe | Impedance - (N/A if the circuit is RCD Protected)
textbox | b044fe0b-852f-5b44-844f-169a2ebc699d | Record Inpedance (Ω)
textbox | b93650ce-1006-567a-bce0-c07128c7e1cf | Target Impedance (Ω)
checkpoint | 79eb7072-a04e-4b6a-85e5-30b4b5f2109d | RCD-RCBO Tripping Test
textbox | abf38619-a914-59e4-97ed-521a8167c7c6 | Trip Current (mA)
textbox | 273439a4-eb3c-5eaa-b343-12c237a4b61d | Trip Time (ms)
signoff | 6aa7fba7-6aac-4dd5-a301-11e58a52dfb3 | Checked By (Heyday):
checklist | f5b959a8-9496-4502-9f36-3c5ce66f64bc | Testing & Commissioning - Low Voltage Cables - Mains/Submains (Pre-Energisation) |  | Low Voltage Cables - Mains/Submains (Pre-Energisation)
section | 018edeaf-369d-4f29-b1bf-c91bde4328eb | Pre-requisite Works
checkpoint | 23f86157-f72b-4ffa-a768-98665b79837f | Insulation Damage
checkpoint | 57bacc0d-557a-45ca-93e7-ece22f64ffd4 | Correct Type of Termination
checkpoint | 9684c7b9-19a0-48c9-b01a-cccbab0659ff | Correct Cable Size and Labelling
section | 57d6eede-c12c-4a00-be4c-750031f4f70e | Insulation Resistance
checkpoint | 0cf19de5-79a4-4ab0-8d41-dc57fd701299 | R-W
button | 9a8a942c-c760-54ab-8156-7f923929fb81 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | ce678e18-59f2-501b-974a-b76616a2e263 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | d4ef7fc9-293d-4bb1-a821-0d89ceace40b | R-B
button | 1c60b3a6-1e7b-5679-9483-48e4dd4f3da1 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | dd511f61-20d5-518f-81f4-fc71cc02430e | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 88eebd9e-2491-41ab-8bc2-7495c59d63f0 | W-B
button | 00092a90-1d66-57c2-9ac1-af0166a8fdba | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | ccd93f11-247b-50bb-8940-faffeea99973 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 0dbda30a-d146-4689-8032-1a754f027c24 | R-N
button | c2567637-4493-5346-b1b1-6608d53e6dbe | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | f42ca530-cdd3-5eec-9abc-41f8a9593ad3 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 30776b3e-d58f-4dc9-bb62-41c38d10f98d | W-N
button | 9e43d7f4-0af4-5ba6-96d7-5ca6707f7408 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | d3ac676d-4354-5beb-9005-912a85b0d966 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 2970f94b-cb79-43a9-9ea1-b18274f0ac88 | B-N
button | 591d006c-3ed7-56f8-8464-c575b772c723 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 4cc71dfc-b209-54b8-bc83-e89b7f48d10d | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 3d6923be-a1f5-449f-a6e0-8f4ed98390f2 | R-E
button | c2fab04d-bf8f-581c-b555-5ed80cce206e | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 55cce7c7-7810-582e-8a6b-369795d3b0c6 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | c9c38127-6fdd-48a2-9520-4253554c02e0 | W-E
button | 06e4a05b-ae5f-5741-8393-5b16751588c6 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 2282f52b-da13-536e-ac5b-4cba786a817b | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 256e178d-ee3e-4d6a-b835-ea77f714c7d4 | B-E
button | 4e9f2bd5-abdc-5f0e-87ca-b8c4ecf750c6 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 75306665-e77b-5cf6-8ce6-a29309f9b014 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 90b33d64-3d90-45ba-8441-9a370fc4ba0d | N-E
button | 7d47d5a8-e5e5-54b1-bf15-f8deabff2b62 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 71eef9c5-5789-5d90-89ea-0b68c00ea9b5 | Actual Reading if <500MΩ/<1000MΩ
section | 52006caf-6350-4285-8d32-6a0561fdbfed | Continuity Testing
checkpoint | 904dd9ec-4232-4529-a23d-9924bf54ff18 | Red Phase
textbox | cf4db43d-bd8a-5d5d-8efe-a99fe73bd4d0 | Resistance (Ω)
textbox | bbc273bf-6757-59b2-b065-7b79be06a427 | Target Resistance (Ω)
checkpoint | 8a010c34-ad3f-44f6-b612-187c1b52df72 | White Phase
textbox | c53816fc-336b-5f0c-82dc-5a69b57952ab | Resistance (Ω)
textbox | 96675194-8fbd-56aa-93d5-0408c0aa5faf | Target Resistance (Ω)
checkpoint | b3d56b96-05a0-4893-95d7-00bf5811b4fe | Blue Phase
textbox | c1062c2d-c386-55f0-99cd-12016163d1ee | Resistance (Ω)
textbox | 88f65101-39fd-5748-b7cf-2b25ec17919b | Target Resistance (Ω)
checkpoint | b5e9a7d4-309f-452f-b5fb-5b1bdeb93dae | Neutral
textbox | 736f3782-a7c4-588c-acd2-268a4a03e69f | Resistance (Ω)
textbox | 615464c5-2962-5723-9c3e-de0d1a961057 | Target Resistance (Ω)
checkpoint | fbe6cce2-e362-42d8-ac3c-ed5f1e81b0a9 | Earth
textbox | 2ee539aa-933f-56c0-9220-1db1e740fc7b | Resistance (Ω)
textbox | 17f9b7f0-2c20-5abe-a210-21c0556a83fd | Target Resistance (Ω)
signoff | 0963f175-9fe2-4d9e-a431-045b23711916 | Checked By (Heyday):
checklist | d80c0715-f329-4661-9a44-68e4b5a51855 | Communications - Fibre |  | Fibre
checkpoint | e2737053-d94a-48c5-b40d-ea6cb9f0e5d8 | Cabling is not susceptible to mechanical damage.
checkpoint | c283b042-76d5-463a-8cca-eae28e34775a | Cable is dressed on the cable pathways with velcro.
checkpoint | 0f151bed-084f-43d3-bbb6-d3158693983c | Apply a plastic traffolyte label to each end of the cable.
checkpoint | 434d0ada-b213-43de-a343-48e2bdb3bafb | Fibre optic reticulates into cabinet correctly and is terminated into fobot.
checkpoint | 361e5676-c9be-450d-b966-9efe3d620a60 | Fobots is labelled correctly with traffolyte.
signoff | 716f9a14-a9e5-4c50-ad9f-89cc55535c35 | Checked By (Heyday/MDE):
checklist | 67c04e62-9a16-4ad6-bff1-f850ca353df4 | Substation Earthing Inspection |  | Substation Earthing Inspection
section | 62a898b2-f6e0-4591-bc14-0522ba8a9ad1 | Details:
checkpoint | cc096a5a-a547-4918-8c51-0dae4ac1849d | Visual Inspection of Pit
note | 2ccf85d8-44ed-5696-a9fe-27b45edd008a | Photo Required of Pit
checkpoint | cfa7a13d-7bee-4cbd-b8da-81dedcf3f58d | Earth Resistance from Pit Earth Rod to Earth Bar
note | 67446d85-d979-5751-a367-9cbdd434a363 | Earth Resistance to be <0.5Ω
note | 7d3aed57-4013-5bac-931e-5a7f90003aa0 | Photo of Multimeter with results from Earth Rod to Earth Bar
signoff | 6a32d84d-266b-4ff3-9e8f-293b4d104a9f | Checked By (Heyday):
checklist | 6c383b39-f825-4304-9fd9-14040470c7da | Testing & Commissioning - PMCS - (Pre-Energisation) |  | PMCS - (Pre-Energisation)
section | 80cb1efa-9413-4588-bbd4-416d894354f7 | WSA20-MPX-04000-EL-ITC-31183000 - Component Tests
checkpoint | 0bc2971f-c935-4b69-be54-5aed9a755752 | Schneider Point to Point Validation ITP - RIOM
checkpoint | 64746830-809f-4404-a799-04603a3e90e9 | Schneider Point to Point Validation ITP - PAC
checkpoint | 3711391c-514f-4938-9967-a2538ffa1220 | Schneider Point to Point Validation ITP - EPS
checkpoint | 007fcd38-df52-4f21-b06c-149e50cb0e72 | Schneider Point to Point Validation ITP - PFC
checkpoint | f61dbfe3-d3f0-4a24-bfd3-13f971c6385d | Schneider Point to Point Validation ITP - UPS
checkpoint | 8a8b9076-eb21-4099-9cc0-ec74a028bc5f | Schneider Point to Point Validation ITP - EV
checkpoint | ca18920f-89c7-4222-8b3a-f7735b3a43bf | Schneider Point to Point Validation ITP - IEM
checkpoint | 691ce5d3-7b5e-40f8-9a3e-b54ef81e8ac9 | Schneider Point to Point Validation ITP - eGSE
checkpoint | f03a126f-5637-4d04-af33-7b8030637f22 | Schneider Point to Point Validation ITP - GEN
checkpoint | aad1bf93-4560-481f-9bb8-940ce1c9a995 | Schneider Point to Point Validation ITP - LCS
checkpoint | 75178553-dde5-47ef-9dbb-d4d130d134b8 | Schneider Point to Point Validation ITP - EML
checkpoint | c0da70a4-fe4c-4380-a6f9-7184ad3bf353 | Schneider Point to Point Validation ITP - PV
signoff | ac3afc66-f236-4331-9cfd-25ccb6c4835a | Checked By (Heyday):
checklist | 040342f5-daf6-4418-aa6a-1b082a38f63d | zSYS - Testing & Commissioning - Distribution Boards (Energised) (old version) |  | Distribution Boards (Energised)
section | b032e628-606e-4000-bbbb-d0d62e221806 | Phase Voltage Reading
checkpoint | 25cd4117-cbf6-4345-ab67-bb1968727612 | Red- Earth
textbox | 34e9aeec-597f-5189-ab44-01363240ca69 | Voltage (V)
checkpoint | 300c9e68-151a-48e5-803c-97e5444eff43 | White - Earth
textbox | b567a645-857f-5bdb-aca9-ae4e0411db36 | Voltage (V)
checkpoint | 0b7272c1-f2e6-4bd3-9343-a48778530121 | Blue - Earth
textbox | 963b41ea-0cfd-51e2-97e2-cb271cf50b09 | Voltage (V)
checkpoint | 0abe01fd-b56e-48d6-a408-e8ad14bbc663 | Neutral - Earth
textbox | e74a8fbc-740f-5f14-a471-792ad68f9fcc | Voltage (V)
checkpoint | 7f96d7fb-8c43-4f71-b7b7-6b9ca50aca12 | Red- White
textbox | e421da73-271d-56a2-81f4-2d7051c6eb6a | Voltage (V)
checkpoint | 66e4a52a-bd60-44b5-8908-85b019e24a5c | Red - Blue
textbox | c4ad7d72-86dd-50ac-8ab5-2eb970370af8 | Voltage (V)
checkpoint | 558bad05-a42e-4fc8-a641-bed24775dcaa | Red - Neutral
textbox | a151468c-19a8-5bec-a83f-a09899690743 | Voltage (V)
checkpoint | 0b858f23-7214-486e-a656-2ced2a8d0c70 | White - Blue
textbox | b5261aff-621c-5d9d-b230-73ec46f29d0d | Voltage (V)
checkpoint | 6b50fbc2-d1cc-4add-8f05-7a7b5346e16d | White - Neutral
textbox | 3f4beb3f-2274-5ecb-89c5-b4edb4aa3467 | Voltage (V)
checkpoint | abbc0971-bcee-4f15-a8a5-08965349ecff | Blue - Neutral
textbox | db82d5b7-8194-54c4-b7bb-1f726fd8463f | Voltage (V)
section | c72524f2-27f4-407c-aaf3-8983b5dad92e | Phase Rotation
checkpoint | 4e7f16e1-abda-4354-8ea6-f416faea4dbc | Direction
button | 7df95ddb-312c-57e0-919a-96eca9084fa4 | Direction | Clockwise,Anti-Clockwise
signoff | 2d77651c-8e1c-4733-b114-b9e33d17dbbe | Checked By (Heyday):
checklist | fdead114-deb8-44bc-b55d-be88024af9f4 | zSYS - Testing & Commissioning - Subcircuits (Energised) (deprecated) |  | Subcircuits (Energised)
section | c3037dc6-5437-4d3a-b0e8-e43b354e9e31 | Voltage
checkpoint | fb6e4570-b4cb-43ab-9082-051d819f2387 | Red - White
textbox | cc1852b5-a858-5622-a499-3f6f7a5ecf0c | Voltage (V)
checkpoint | 9b24a948-75c0-422d-ac9d-8b597617acad | Red - Blue
textbox | 907067cd-77b3-58fa-b9df-fa4d5dc2626a | Voltage (V)
checkpoint | 716ace7e-cce9-4389-8bf2-0852ecf28ed9 | White - Blue
textbox | 0c0a9199-cf09-571e-a421-0e9413ed7efb | Voltage (V)
checkpoint | 00955b7e-5a72-498e-b9b9-44d726b1737b | Red - Neutral
textbox | 7cb95a8c-b08d-53bb-9f92-c42b900dd157 | Voltage (V)
checkpoint | 7d03839b-63b6-432a-80a9-184c0e4f8de6 | White - Neutral
textbox | 1d76cae3-8545-5350-8895-f5dfbba90860 | Voltage (V)
checkpoint | 046f1ac1-9e92-4f8f-9792-f9b78602f279 | Blue - Neutral
textbox | 04f6bb60-9d27-5a2b-abf6-5c0fc9f7bca1 | Voltage (V)
checkpoint | 85ee5f16-6867-4227-8168-4abf62726adb | Red - Earth
textbox | 558df863-72c1-5a49-a741-d97bb562cae1 | Voltage (V)
checkpoint | 92d818e7-0134-4120-8c38-5989b5693ba4 | White - Earth
textbox | 6f194aae-c3d4-543a-8770-022b84d0a96e | Voltage (V)
checkpoint | 11027c91-4c93-48f9-8748-342c95cb2978 | Blue - Earth
textbox | 49ce1391-484c-5415-9c72-afa45c4c7b32 | Voltage (V)
section | 1395c343-7cad-4eac-b2ef-0e94635c4b64 | Earth Fault Loop Impedance Test - (N/A if the circuit is RCD Protected)
checkpoint | 3b5353b1-0122-40f9-bdef-a7d49ee87f9a | Impedance
textbox | 6fe7d82f-84cb-53e9-af32-5b53073c1c82 | Record Inpedance (Ω)
textbox | 0280d8cc-33c9-558c-8058-c3e02dc3acd8 | Target Impedance (Ω)
checkpoint | 62ce819a-2a7d-4c5a-b870-7e3b02d2a275 | RCD/RCBO Tripping Test
textbox | 508af3fc-b279-5a1b-8447-ce5b88e6c620 | Trip Current (mA)
textbox | 298fdfb3-9ea0-51aa-b3da-88668aff353b | Trip Time (ms)
signoff | 94e2fe6c-163e-4db7-ab76-95e5fccaa1fa | Checked By (Heyday):
checklist | 7b246d4f-d493-4a96-a703-880733961745 | Testing & Commissioning - Distribution Boards (Pre-Energisation) |  | Distribution Boards (Pre-Energisation)
section | fa47f1b8-3e3e-41d9-aee5-0bffb1dbde39 | Physical Checks
checkpoint | a2a38f2b-b83f-465d-ac18-666b79851309 | Confirm board's dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | d0173fb1-b7a4-4fe5-b3f3-4957b1dc6e13 | Confirm correct circuit identification and labelling
checkpoint | 6243f1fe-f6bc-4eea-a876-16ce0b57d2a0 | Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in the Comment section
checkpoint | 8a876eef-445e-4401-8c23-c44c3fcec414 | Confirm correct phase identification of busbars and cables inside the board
checkpoint | 88d1391b-398e-49b0-9508-aa54e90129a9 | Confirm correct size of earthing conductors
checkpoint | 3f2d8c61-6a2e-4740-b89f-ff93ece3113f | Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
section | 2c0bf394-bd1e-4bcb-8578-a8b30fd3dfd5 | Mechanical Checks
checkpoint | 7a4ad267-5e5a-45cc-ba9a-4fca8fc3c8be | Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint | 8fe2ae1d-ef63-45c3-8916-3225e6d58cd6 | Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint | 9b5d1b54-b746-4f41-b9cd-488012d1f123 | Repeat mounting and dismounting of power fuses for 1 time
checkpoint | 69405970-b174-4627-887b-65e175daf287 | Repeat mounting and dismounting of control fuses 1 time
checkpoint | 39b4ee49-8ded-4508-9e04-f8e8a13bc0d2 | Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards.
checkpoint | 7d0559f9-1c49-4555-a760-b7da62822cab | Conduct pull test for all cables connected to MCBs and Termination blocks
section | 0bc81f3d-9c90-42d2-8754-8265b04bfded | Preliminary Checks
checkpoint | 59041ea2-5897-4760-b195-d5508458ef02 | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint | eec1440e-9167-4118-a5c3-a83ac50f3f2e | 2. Confirm Main Breaker Closed
checkpoint | 1d346d53-673c-4751-bd19-cc1494becd27 | 3. Confirm Outgoing Breakers Closed
section | 0c680e07-b577-4aa0-a117-6498cc2d2a18 | Insulation Resistance (500V)
checkpoint | 19cde899-93ff-4446-8319-29f3df80c43b | 1. Between L1 Phase and Neutral
button | 8d5137fe-f9ad-53f2-bd0e-3b78b4ac100f | >10MΩ | YES,NO
textbox | d3514873-d980-580e-a9b3-e3d6768388da | Actual Reading if <10MΩ
checkpoint | 27ba78cb-cc6a-4486-9060-04449287e31e | 2. Between L2 Phase and Neutral
button | 96cdbdc4-a3b3-50d4-a4e9-24c58da4d7ed | >10MΩ | YES,NO
textbox | c893bc4b-7942-5666-a387-d37e84acd413 | Actual Reading if <10MΩ
checkpoint | 3067f610-0cdc-40d4-9a94-a38a87ad84c6 | 3. Between L3 Phase and Neutral
button | 591b519d-97e7-55c5-a0c1-4f4205e18e70 | >10MΩ | YES,NO
textbox | 40e1ad66-d1b0-530d-9c48-7c0490f0c9f0 | Actual Reading if <10MΩ
checkpoint | 2425cfa0-d441-439a-aa0a-b3212293fbd5 | 4. Between Neutral and Earth
button | d89ced1e-58d9-5d29-bc08-1f547426c277 | >10MΩ | YES,NO
textbox | dda844a8-c676-5038-b8bb-94d5a66da629 | Actual Reading if <10MΩ
checkpoint | 91811b40-2fae-4cc8-a3ed-f90d5e99daa7 | 5. Between L1 Phase and Earth
button | 5f6a6117-6456-50e3-84ab-abf2bee73138 | >10MΩ | YES,NO
textbox | ccc22a7a-9a96-553a-b6a0-f4df0fa7b6aa | Actual Reading if <10MΩ
checkpoint | 8b72189a-04d6-4285-be93-763670b8ebe4 | 6. Between L2 Phase and Earth
button | fb74e74a-2e7a-52d3-9084-17d88add7ebb | >10MΩ | YES,NO
textbox | 6bb70748-b114-5c79-ba02-b3967f854f88 | Actual Reading if <10MΩ
checkpoint | 5cf9e886-3040-49e4-94f9-878470d6486a | 7. Between L3 Phase and Earth
button | f8b5bf4a-5ba6-5c60-9660-24e935f0e336 | >10MΩ | YES,NO
textbox | bc001e99-f2bc-53da-8c13-954427272a66 | Actual Reading if <10MΩ
checkpoint | 1d9918f8-3252-4b80-b891-80573f9e0942 | 8. Between L1 Phase and L2 Phase
button | 5fde54df-8e06-5008-9320-1d04a65f1079 | >10MΩ | YES,NO
textbox | 3799590b-09c6-5a2c-b35e-df93781c3769 | Actual Reading if <10MΩ
checkpoint | 5fa8127b-f62f-4825-84e2-44fd7ea37b94 | 9. Between L1 Phase and L3 Phase
button | 27efbce9-eafc-534c-9385-3c4351e3faf3 | >10MΩ | YES,NO
textbox | cee17755-0e21-5240-995e-f3d505967592 | Actual Reading if <10MΩ
checkpoint | 6621d964-67ab-40ee-8881-d55718bbdebf | 10. Between L2 Phase and L3 Phase
button | eb372be4-3b3a-5104-bb15-30a5499e166d | >10MΩ | YES,NO
textbox | e0be4235-3074-5e18-81f5-a1fa6f1f7a80 | Actual Reading if <10MΩ
section | ff744fd6-409b-4128-8678-d95b35cadb4c | Earth Continuity Test
checkpoint | 33bdaa69-8a6c-404f-a18d-cca8372bb5c5 | Earth Continuity
textbox | 346af0cb-2812-5550-8210-bea371afd6ac | Resistance (Ω) - [Target: <0.5Ω]
signoff | 0f95add1-bb04-4201-9a4a-ff76b13d207e | Checked By (Heyday):
checklist | c4fab001-6d7f-4e61-9514-e45467024253 | Testing & Commissioning - Communications Cabling |  | Communications Cabling
checkpoint | 55d94b5c-3689-4cb2-8f73-9160690a51be | Cable installed to Manufacturers requirements
checkpoint | f4a63d89-7085-4de9-a646-9ff3b5e2c2b7 | Cable Labelled
checkpoint | 57b1b891-a26a-4284-b199-006ddec485d7 | Cable Terminated
checkpoint | 0b118d6f-2240-4905-9767-72c4a3c64569 | Cable Tested
checkpoint | 61d91b88-697a-4bdc-a7a3-1d7e495d395f | As-Builts reflects installed Cable Number and Location
signoff | 86dbe344-1f18-4c57-9799-284e4f4985ac | Checked By (Heyday):
checklist | 36c84e5b-0495-4dfc-b941-3b128d44482c | Testing & Commissioning - Earthing Systems - Construction Tests (Earth System Reticulation) |  | Earthing Systems - Construction Tests (Earth System Reticulation)
checkpoint | 5d791298-49e3-4116-b523-c359d010f8b6 | Correct Cable Size and Labelling
checkpoint | 3124bc43-3fc7-4493-9eea-108a575e2ae1 | Earth Continuity
textbox | c5ad7585-699d-581b-8267-c3d24da56d0e | Resistance (Ω)
textbox | e8f761bb-2760-541e-b5ec-9156d4f317ce | Target Resistance (Ω)
signoff | 5c7272eb-5012-417d-9440-1e7547cbd7b6 | Checked By (Heyday):
checklist | adf41567-33c7-4edd-a2e3-b2eb8e5ca8a8 | Testing & Commissioning - Low Voltage Cables - Mains/Submains (Energised) |  | Low Voltage Cables - Mains/Submains (Energised)
section | 2b0dd3a0-2840-4fd7-838c-e64206f9de3f | Phase Rotation
checkpoint | a6e4ad7e-ec83-4416-8528-d65f1ab998b5 | Direction
button | 28ea72d6-4a91-5a15-94c5-2854db45b57b | Direction | Clockwise,Anti-Clockwise
signoff | c26a325e-78ba-45d6-91e6-5860806890c3 | Checked By (Heyday):
section | e88e7031-561f-46cd-bbb9-0199c3ac78cb | Voltage
checkpoint | 86f8e276-da9e-4b97-ba69-9d5b6f4dd122 | Red - White
textbox | 93653f00-3b32-5550-844e-7b7cf8710501 | Voltage (V)
checkpoint | 6ed9be45-6b56-4b49-87da-ea502410a2e4 | Red - Blue
textbox | b368877c-44f2-56ed-8d65-302019e35b3e | Voltage (V)
checkpoint | db14faf0-0b83-49f8-b05e-3ed90cd33602 | White - Blue
textbox | 71305fd4-cd21-5a08-90d9-04d103c384bf | Voltage (V)
checkpoint | b2cb4bf8-69b4-4225-a2f7-6c2d237fc507 | Red - Neutral
textbox | 50f8d9fd-9169-58b7-8c5c-2ad5568d5af6 | Voltage (V)
checkpoint | 0eb3a0b2-9ab2-43bb-98b4-86a8a5174f99 | White - Neutral
textbox | 15d9f414-9e57-5b37-8804-20266311e4d0 | Voltage (V)
checkpoint | b70d7c3e-3add-4007-ad5d-b1ca733190b5 | Blue - Neutral
textbox | 69e62051-5aa3-5258-8375-5880247be8a5 | Voltage (V)
checkpoint | 8d2bbccf-f4e9-4131-99ab-030da4b330d2 | Red - Earth
textbox | 85db411d-c77e-5ae5-9482-8871a3b373c5 | Voltage (V)
checkpoint | 0725d234-197f-4880-b767-b9be6da1b33c | White - Earth
textbox | 58452f28-615b-5268-8df2-6aa3d6bad2f7 | Voltage (V)
checkpoint | 1cfb0202-de30-4657-b8ff-6952e850a957 | Blue - Earth
textbox | 45e1a898-8aef-5fe6-a258-43e9f2f26db6 | Voltage (V)
signoff | 8982ac97-a732-4e66-a639-4970c71168cf | Checked By (Heyday):
checklist | 1e831a00-d7dd-47a8-8c1a-3adb421c1401 | Testing & Commissioning - UPS (Pre-Energistation) |  | UPS (Pre-Energistation)
checkpoint | 9fce7efb-00fa-4dbe-8da7-cb82428781d1 | Commissioning & Installation / Start-up Report - System Room Check – Page 6
checkpoint | 76622146-1a89-4937-b3b6-b3b6251e014f | Commissioning & Installation / Start-up Report - System Check – Page 6.
checklist | 942ddc73-90e7-4113-b188-d0d2bd40f2b6 | Quality - Earthing & Lightning protection |  | Quality - Earthing & Lightning protection
checkpoint | 1479e842-cca4-487c-ab4e-fbc4bbd640de | Receipt of Cable & test point delivery to site
checkpoint | 39de632f-40ed-467a-b184-4cb1d361cc72 | Correct cable size and Cable type installed per the shop drawing
checkpoint | 949d0a9c-6e76-4913-a8b1-243717cdd555 | Installed and Terminated to final locations
signoff | 6d5b64a1-3d75-444a-b7b6-bd7a5fc618ad | Signoff Required from Heyday & Multiplex
checkpoint | 232b8310-ad90-42ac-8360-ffb23fe6a001 | Photos of test piont and bonds attached
checklist | 8d60bbbe-1ea3-4ffc-acc6-cc9659a95a68 | Testing & Commissioning - Emergency Lighting |  | Emergency Lighting
checkpoint | c2dfcdbf-2955-419d-b108-ffede429bf4f | Pre-requisite Works
checkpoint | 22880dd4-2579-4d39-b8c9-957b8934c66f | Correct Location & Labelling
checkpoint | 919b553b-f5f3-4c09-8f17-9d5c2b61169a | Correct Software Mapping
checkpoint | bc6f4cea-40bb-4efd-b470-b4392c182cc9 | Discharge Autonomy Test
signoff | e7af81ef-61e0-4cde-9f0b-c1aae177aa04 | Checked By (Heyday):
checklist | 4bb6e476-8bbc-4e45-a973-63a140bfa3f8 | Testing & Commissioning - UPS (Energised) |  | UPS (Energised)
checkpoint | fdfaaa2d-ff73-42fa-a03d-542a79ed959a | Commissioning & Installation / Start-up Report - Unit pre start-up check – Page 7
checkpoint | e799e765-75f6-4b34-9a13-8ca4acee5b53 | Commissioning & Installation / Start-up Report - Unit Functional Check – Page 7
checkpoint | 0a01ea4f-cb67-4be8-b374-02ed1def6419 | Commissioning & Installation / Start-up Report - Unit Final Inspection – Page 8
checklist | befeb558-5dff-408c-be76-d2ce72f1844a | Quality - In Ground conduit install - HV ONLY |  | Quality - In Ground conduit install.
checkpoint | 73a71ac9-bed4-4633-9d29-21efd7bbd825 | Receipt of conduit delivery to site & storage. (ITP Reference Item 1)
checkpoint | 2622f687-370d-4ad8-902e-5f73f0b589b6 | Set out. (ITP Reference Item 2)
checkpoint | 6259a244-bbfe-42b5-b5fd-9ed8c0ad949c | Excavation - Correct trenching alignment & depth. (ITP Reference Item 3)
signoff | 90fc07f1-12f8-4be1-896f-b45f3eac4701 | Signoff Required from Heyday & Multiplex
checkpoint | dd02b98f-0593-48ef-95db-8b6cc4b7ab98 | Conduit Installation. (ITP Reference Item 4)
checkpoint | c0e3dd45-3837-42c7-bee2-80fed1e7f336 | Spacer Frame Installation. (ITP Reference Item 5)
checkpoint | 5761ad7f-9073-4e10-8201-47d52ca32c93 | Change of direction/bend Installation, correct bending radius used as per drawing. (ITP Reference Item 6)
checkpoint | d08685d6-ed34-483b-89b9-269076cad5c8 | Bellmouths installed within Insitu Pits. (ITP Reference Item 7)
checkpoint | b3c19a1d-81eb-4263-999c-3a3a7b5c1c09 | Glue Conduits together. (ITP Reference Item 8)
checkpoint | 67b70002-92b4-4565-bbe6-d9c23f5fe188 | TSB Installation around & above conduits. (ITP Reference Item 9)
signoff | 367f0d61-a448-4b6f-9362-f1c6a51d7b09 | Signoff Required from Heyday & Multiplex
checkpoint | 5aba8eea-2b46-4f4a-96b5-2272371c28af | 150mm cover of backfill above TSB. (ITP Reference Item 10)
checkpoint | cd6b3534-56e2-435e-b73b-aa9fcc6bee01 | Warning tape installation above 150mm cover. (ITP Reference Item 11)
checkpoint | f70d4a64-90e6-489b-9c09-8c9e5f9b1ce5 | Back fill & compact. (ITP Reference Item 12)
checkpoint | 8162eec1-3d56-4a82-bde2-8d1f7d768500 | Rope & pathway test. (ITP Reference Item 13)
checkpoint | 54eb1e84-db3e-4c93-95e4-fbc4fb10d586 | Sealing of conduits. (ITP Reference Item 14) HOLD POINT
signoff | 53bfa6af-a21d-4791-91fd-86ad581731fa | Signoff Required from Heyday & Multiplex
checklist | ab447333-a299-4292-8db0-7bf6f22c0c5a | zSYS - Testing & Commissioning - Distribution Boards (Pre-Energisation) (old version) |  | Distribution Boards (Pre-Energisation)
section | 8977fb2d-d688-4cf3-ba87-cb3b8fa58f11 | Physical Checks
checkpoint | 53931865-a78a-45ab-97ba-c708723ce19b | Confirm board's dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | 406cc207-1337-4249-b626-ad3c99a32f08 | Confirm correct circuit identification and labelling
checkpoint | 9fe77cb5-17a2-4cbd-986f-6b77e11a3212 | Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in the Comment section
checkpoint | 803faee4-c37d-40fe-9c85-2e74fc369c5b | Confirm correct phase identification of busbars and cables inside the board
checkpoint | 47ec17c8-ae92-4b4d-866c-ff0d9ea6aee2 | Confirm correct size of earthing conductors
checkpoint | 63b54de8-ad3b-41d3-a0f3-fc5241186aa9 | Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
section | 64c1c2c8-43ed-4fd4-bb5b-5d012ed1db54 | Mechanical Checks
checkpoint | cf8b9aa7-08fd-4c0e-91c8-cbb9f004a809 | Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint | 49cfc303-218e-487c-81da-99c451f007b0 | Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint | bcb84516-3183-41b4-96f5-4fce85c25419 | Repeat mounting and dismounting of power fuses for 1 time
checkpoint | aa08c339-65f9-48dd-bb4c-bcb7bb3ecc17 | Repeat mounting and dismounting of control fuses 1 time
checkpoint | bc551d4c-f188-4b41-92fa-cc1e5bb9ac39 | Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards.
checkpoint | 48adfc55-5257-4635-a37d-8aaa1cdb361a | Conduct pull test for all cables connected to MCBs and Termination blocks
section | 21404c63-9e24-472c-9e6b-fcff18e7f796 | Preliminary Checks
checkpoint | 28c77213-b2ae-49b2-8713-4e8526be9db4 | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint | 8dfbd3cf-e1f3-4186-92f7-84d6786be3cd | 2. Confirm Main Breaker Closed
checkpoint | 19f52456-4a04-4556-af92-67733c2ddd7c | 3. Confirm Outgoing Breakers Closed
section | bdf6c1bc-a00d-4ab5-9aff-1bbba6598c13 | Insulation Resistance (500V)
checkpoint | 95780f93-e76b-4d2f-9976-285f8da63ae6 | 1. Between L1 Phase and Neutral
button | d13d1e56-7dcb-5e3a-9b5c-a0177a9b705e | >10MΩ | YES,NO
textbox | acb50fa4-ec67-553a-ac17-a3c84289aef3 | Actual Reading if <10MΩ
checkpoint | 97429c4d-a75b-43ac-b3d6-8e93dea59342 | 2. Between L2 Phase and Neutral
button | b536bc25-10c9-5f2b-b54e-2d017764b346 | >10MΩ | YES,NO
textbox | fbc00ebb-87e0-5b6b-b6ea-a7b87cda5dde | Actual Reading if <10MΩ
checkpoint | 56504dc8-adab-47d4-b32b-f0ef6bf26930 | 3. Between L3 Phase and Neutral
button | bf84e43c-e7a0-5de6-8d9d-eaaa028eb099 | >10MΩ | YES,NO
textbox | 21adcd4d-6cbf-5f5e-b8a8-b96d7ba516f5 | Actual Reading if <10MΩ
checkpoint | 59e61667-dcdb-4fdf-a339-2e207b35bcbb | 4. Between Neutral and Earth
button | a7c183bc-5dac-5983-b295-3010e75cbb96 | >10MΩ | YES,NO
textbox | a7e77f7f-29c5-518c-9001-05d65d66e0fa | Actual Reading if <10MΩ
checkpoint | 555ad5dc-50ed-4de6-bb8e-e1c1569a6e90 | 5. Between L1 Phase and Earth
button | baf66c08-1e2a-5e9b-92bf-4c4497f8506c | >10MΩ | YES,NO
textbox | a613c700-5f1c-5268-b5ff-dd5877585430 | Actual Reading if <10MΩ
checkpoint | 758028f6-f6fa-43eb-906b-ad9ba25d281f | 6. Between L2 Phase and Earth
button | 1429255c-7841-56ad-8697-2c6d159d4785 | >10MΩ | YES,NO
textbox | 3cb29882-53f7-571c-a986-60f07c038d4a | Actual Reading if <10MΩ
checkpoint | 7d0031ee-ffd7-418b-8ad9-32353aca2e22 | 7. Between L3 Phase and Earth
button | 6b34d913-698f-543f-acbd-b15ce2393323 | >10MΩ | YES,NO
textbox | eca5e2f2-4f96-54a4-bd9c-d773ef32d661 | Actual Reading if <10MΩ
checkpoint | 95d05598-ce63-4609-bc1e-50944d2c5aac | 8. Between L1 Phase and L2 Phase
button | f2d0ded0-11dc-5ed7-b174-7ae1e1f2de7f | >10MΩ | YES,NO
textbox | 409049d8-bf8e-5277-b9d3-092b1ed58bf4 | Actual Reading if <10MΩ
checkpoint | f5ff6e4a-a62f-4e95-aea1-04b18472b68c | 9. Between L1 Phase and L3 Phase
button | 062ccca4-0713-55fd-a25e-95a99c06db87 | >10MΩ | YES,NO
textbox | 94d30298-de90-5b38-bbbd-e6d83151d789 | Actual Reading if <10MΩ
checkpoint | bb98cdd5-869c-44eb-8f53-98f3bc74dcc8 | 10. Between L2 Phase and L3 Phase
button | bb2650ae-08aa-536f-bfd8-7ae3895db90c | >10MΩ | YES,NO
textbox | eabaa815-6458-54b1-aa8c-0d477e6c4d97 | Actual Reading if <10MΩ
section | 7ce3d526-d0f2-46a6-919a-831e9e8f6dd5 | Earth Continuity Test
checkpoint | f3e1e57e-5bd1-4798-b4c6-f29e27628b90 | Earth Continuity
textbox | 2a6ea1f6-c5ff-500e-9214-32679eb3c7c6 | Resistance (Ω) - [Target: <0.5Ω]
checklist | 4fa4fbf4-42a3-4393-b3f3-b3449cbe025c | zSYS - Testing & Commissioning - Main Switchboards (Energised) (old version) |  | Main Switchboards (Energised)
section | ac0e86aa-8433-435d-99f0-ee31dee7d83a | Phase Voltage Reading
checkpoint | 24106199-b416-4225-9d08-100917b946cd | Red - Earth
textbox | c443a7c0-6aba-543f-82e5-1170cbc71f4a | Voltage (V)
checkpoint | e3980818-60e0-4b1b-ab2c-81724d8f83d1 | White - Earth
textbox | eef0209b-e0b9-523b-8d28-9f9340dc3729 | Voltage (V)
checkpoint | 18896dac-fc9f-46de-b007-79aeef2b0f90 | Blue - Earth
textbox | 2f39fda3-89eb-5730-adaf-57ef629f4a16 | Voltage (V)
checkpoint | 37cecaf8-dd25-4fa0-88b0-67aeb76f8251 | Neutral - Earth
textbox | d9ab42fc-3e57-59f4-9227-22a83acd2a34 | Voltage (V)
checkpoint | 1ab16c1a-4ccb-4083-9814-f592ea23ebf5 | Red - White
textbox | faf84b07-2bca-5974-ac1b-59db0a83d6d7 | Voltage (V)
checkpoint | 83ba6965-4ced-4f86-967f-af18081b752d | Red - Blue
textbox | c9bf26ff-c861-5cc4-ba8e-e92005fbe46e | Voltage (V)
checkpoint | 101036c5-4d49-417e-9273-22589dd9d669 | Red - Neutral
textbox | 130a2510-3cbd-5ac6-b383-6f1ce4e81e05 | Voltage (V)
checkpoint | 7bdcb278-4f06-4a4d-b354-23a8b3a31689 | White - Blue
textbox | 62ab94a7-c532-5e3f-b61c-750942b36bf9 | Voltage (V)
checkpoint | 83173e6a-8ca4-46ac-a28a-57ac2ba143c5 | White - Neutral
textbox | 06feaf21-f1e7-5548-8341-e2b5fcfc3809 | Voltage (V)
checkpoint | a8540f30-6054-4949-875f-3153f51ab8d9 | Blue - Neutral
textbox | d7baeed0-5f98-54f2-a730-e0d7b4d47bba | Voltage (V)
section | d602f38d-cb2d-47df-af96-38ea7789a0dc | Phase Rotation
checkpoint-no-value | cc20153b-ce79-445c-86cd-57ab49ea7a6a | Direction
button | 12292019-ba2f-5220-a323-2186e95666e1 | Direction: | Clockwise,Anti-Clockwise
signoff | 3da7e379-2ead-4d3d-8087-3dda4c33f598 | Checked By (Heyday):
checklist | f8f7170d-7d95-45ff-a33e-8660a43544f1 | Testing & Commissioning - HV/LV Transformers |  | HV/LV Transformers
checkpoint | 0969b89b-13b4-4408-9f80-44764c16f940 | Schneider Electric Transformer QA/QC Test Report – Installation Configuration Page 3.
checkpoint | 71e45806-0bf8-420a-9058-dc8022588864 | Schneider Electric Transformer QA/QC Test Report – Pre-Testing inspection Page 4.
checkpoint | 3db19474-7cc3-4bc9-96d7-b8a25713e7af | Schneider Electric Transformer QA/QC Test Report – Transformer Test - Page 4:
note | f8c6c0e2-0485-509a-931b-46c872a5edc9 | Continuity test on HV and LV Windings
note | 3faf0bd7-0a5a-5492-be65-9c05fe1f5766 | ○ Insulation Resistance Test LV Winding to Earth
note | a9a2e7ec-06f4-5b0c-89c3-d73ab8bec5d5 | ○ Winding Resistance
note | d5f48f7a-6630-5728-8eb8-e0783cbc2636 | ○ Winding Ration verification (taps: +2.5%, +1.25%, 0, -1.25%, -2.5% )
note | 07063b97-3ec1-52e0-b91d-4ecb899353d4 | ○ Vector Groups
note | b63500bd-c421-55e0-9a61-593f3e871930 | ○ Check bushings
note | bb642782-7878-5cb6-a87d-4afc54389d15 | ○ Control cubicle visual inspection
note | 8d2f3627-9622-502b-9733-5ad37a7f6000 | ○ Control Cabling within the control cubicle visual inspection and connection verification against approved schematics
note | c61de0f1-9a75-591c-8fd3-a5716389ee98 | ○ Confirm opening of LV door operates “normally open contact when doors are closed”
signoff | 5c13a156-5bca-4154-a40f-5738c1d988f4 | Checked By (Heyday):
checklist | bc06466f-09e0-4844-adac-aec4b5269f76 | Quality - LV and Communication - Pit and Pipe Inspection |  | LV and Communication - Pit and Pipe Inspection
checkpoint | 8014076b-6fd0-4f39-92bc-06436c30abbd | Cover Slab and correct Pit installed per shop drawing.
checkpoint | 7f8c709e-47a2-46a9-97f3-9530310e73c8 | Pit Lid installed to correct FSL
checkpoint | 7392339a-0e99-4210-9eee-1c4acde014c7 | Conduits from pit out have been mandueled using correct size.
checkpoint | 2762682b-f76d-4347-b346-e128b9f353ef | Ropes installed in conduits
signoff | 4a19f46c-9fca-48f7-87c8-9ef56fa500f7 | Signoff Required from Heyday
checkpoint | e9793bd1-f449-4e14-bf49-ad1a79f8ff50 | Photo of pits installed.
checklist | 6ef4f278-b682-4732-b309-dda39a361785 | Quality - Light & Power Circuit Rough-In |  | Quality - Light & Power Circuit Rough-In
checkpoint | 01f55dbc-9321-42c9-8588-c4faba57d6e3 | Receipt of cable delivery to site & storage. (ITP Reference Item 1)
checkpoint | 3779156b-7aa8-4293-98fc-e9c4a61a862d | Correct size & cable type. (ITP Reference Item 2) HOLD POINT
checkpoint | 02fd3b3d-fed5-4ef9-a1eb-73eddf8ff184 | Installed to correct cable routing arrangements & circuit number. (ITP Reference Item 3)
checkpoint | 3ce64644-d2fd-44a9-acc1-15989cddc134 | Installed to final location. (ITP Reference Item 4)
checkpoint | 1db46d67-0d00-48c0-bd70-c109140314f1 | Photo evidence captured of cable installation. (ITP Reference Item 5)
signoff | da9add73-c80d-4e8d-a6a0-086057f02b00 | Signoff Required from Heyday & Multiplex
checklist | 50866f89-092f-4410-b11b-5e2c0f371df3 | Testing & Commissioning - Main Switchboards (Pre-Energisation) |  | Main Switchboards (Pre-Energisation)
section | 8fae24b8-93ff-44e4-9f3e-3d4d4fd11b95 | Physical Checks
checkpoint | e709c7be-8e7d-4169-9abe-3cb7607e04ab | 1. Confirm boards dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | f12a6ef1-c025-4c3f-8e3c-aabbcbac8a65 | 2. Confirm correct MSB Form of Separation, Provide actual Form of Separation in Comments section
checkpoint | 4bacf871-43d7-44b1-9ca7-931eb3d5c73e | 3. Confirm the Layout of fitted components (ACBs, MCCBs, MEN, ATS) is in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | 5acd8e26-1e16-488f-bf1f-2688b05a237b | 4. Confirm that Brand of fitted components is in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | c3e92977-4409-4e3c-b8a0-114bf210be9f | 5. Confirm meters location, types and labels are in accordance with approved shop drawings
checkpoint | 134840f7-5341-470d-a375-90551e836a99 | 6. Confirm the circuit breakers rating is in accordance with discrimination study (provide discrimination study reference in the Comments section)
checkpoint | 0763de31-405b-4e72-857d-2ced3f82e9c9 | 7. Confirm Trip units and protection relay settings are set in accordance with discrimination study
checkpoint | 109d65e8-a0df-42f4-8a18-a6457d59aadf | 8. Confirm correct circuit identification and labelling
checkpoint | f10e2dcb-9875-47f0-b4d8-958e1fd394ee | 9. Confirm easy access to controls termination
checkpoint | 9a611db2-39d4-4660-b50b-1fcb1452706a | 10. Confirm correct location, access and sufficient support for incoming cables
checkpoint | 8083287d-4ea4-4e47-8888-070a7be1c4f8 | 11. Confirm correct location, access and sufficient support for outgoing cables
checkpoint | dd201025-c906-4ded-af65-32c021351bff | 12. Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in a Comment section
checkpoint | a596d58c-b005-485b-9c07-51013801b5a8 | 13. Confirm correct phase identification of busbars and cables inside the board
checkpoint | bc2f44c9-0e12-4027-9ac0-857eef3646d5 | 14. Confirm correct size of incoming power cables as per approved cable schedule
checkpoint | 5db9f0ed-1af7-439a-be14-ef8d2771c4d1 | 15. Confirm correct size of earthing conductors
checkpoint | 3039bea8-eb57-44dd-beda-50bce13c367b | 16. Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
section | 1e94d923-98c2-4cf3-83f4-8e81fb3f9ed2 | Mechanical Checks
checkpoint | ed460c2b-4e25-45f6-a336-77a8cc25c8ae | 1. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
checkpoint | 0e70d6de-0d05-46e6-a482-c5df4089c862 | 2. Repeat racking of air circuit breaker in and out of chassis for 2 times to verify correct functionality of sliding mechanism
checkpoint | 33e985fc-0800-4089-ac92-b78eaf79d6fb | 3. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
checkpoint | 7606501e-6b84-4d59-bf66-647360d4245e | 4. Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint | 8365c25d-b9eb-4b26-a107-e3ec28f0ca3f | 5. Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint | cfa73a8c-32bd-498f-92f4-6645a8c83db8 | 6. Repeat mounting and dismounting of control fuses 1 time
checkpoint | 1bbac3cf-816d-429e-8593-6f95117b09fa | 7. Repeat mounting and dismounting of control fuses 1 time
checkpoint | 4df04b50-8603-4e17-a06d-09346cb9d6c6 | 8. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 1 Breaker and confirm that Source 2 Breaker is mechanically interlocked
checkpoint | ba24e470-4526-445c-8da5-7f158e4f0fa9 | 9. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 2 Breaker and confirm that Source 1 Breaker is mechanically interlocked
checkpoint | a9a85573-39a3-48ad-acb5-79c2bccd745e | 10. Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards
section | 722dc086-3965-41eb-8544-d40f6e036103 | Switch Gear Busbar - Preliminary Checks
checkpoint | 7f37c3cd-7b41-49b4-8dd7-d0952e802c69 | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint | 420447a3-a867-4e5e-b379-dad0ffae8c6d | 2. Confirm Main Incomers ACBs/MCCBs are Closed
checkpoint | 0cad5f1a-3ffc-4c5c-b91f-9a473d0f7771 | 3. Confirm Bus-coupler is Closed (if exist)
checkpoint | 216adc9a-95a4-48a8-822a-97fe489b05c1 | 4. Confirm Outgoing Feeders is Closed
checkpoint | 31e36a40-14f8-4cbe-9a16-a63c06e2e646 | 5. Confirm Main Panel Neutral to Earth Link(s) was Removed
checkpoint | 3521c02c-fa2e-4164-9e0a-e2a75858c4bd | 6. Confirm Neutral link on Transient Voltage Surge Suppressor is Opened
checkpoint | f4d3a76f-555b-4d08-b1d6-4d5b74b52e15 | 7. Confirm All Long Time rating Plugs From ACB's are Removed (if applicable)
section | b93d32c8-fa8d-49b1-9124-61c88bd8b5a1 | Switch Gear Busbar - Insulation Resistance (1000V)
checkpoint | fce186ff-8fe9-420b-baa6-25a24b2687eb | 1. Between L1 Phase and Neutral
button | 5d0fa9d4-3057-5f7b-95f7-ee58f147495d | >10MΩ | YES,NO
textbox | 80a0e736-fd6c-580a-9dfe-e4566efffaa5 | Actual Reading if <10MΩ
checkpoint | f51eb97c-857c-41ad-8a95-47625b23dfba | 2. Between L2 Phase and Neutral
button | 67010062-53c3-58b0-aaf0-1fce18f8b9f5 | >10MΩ | YES,NO
textbox | ce4e99d7-d9b1-56ef-8de3-f1adc0c6dea7 | Actual Reading if <10MΩ
checkpoint | 90fd0fcf-c627-4718-8cc7-77d1c29a1fed | 3. Between L3 Phase and Neutral
button | 4411ae80-a470-52a3-8e98-2e78a4fd4846 | >10MΩ | YES,NO
textbox | bd565b3f-87dd-59b9-8dbb-46149c449d56 | Actual Reading if <10MΩ
checkpoint | 13d3855a-a1b4-46e7-8ccc-b27564e8a236 | 4. Between Neutral and Earth
button | 91779843-aadc-5e9e-8df5-c8484ba1da16 | >10MΩ | YES,NO
textbox | 0d181df8-1b98-5f4c-ba7b-187a701c47b8 | Actual Reading if <10MΩ
checkpoint | f95ee146-bbb8-4e2f-a4df-c8e5d3f26450 | 5. Between L1 Phase and Earth
button | 4c632dfa-483b-5787-adb5-28360c6c913f | >10MΩ | YES,NO
textbox | 39b1bc1e-1c12-50dd-8316-88afe5fca0cf | Actual Reading if <10MΩ
checkpoint | d30595f0-a3f8-4402-b31c-336b98e222bb | 6. Between L2 Phase and Earth
button | 46836438-d796-5460-aa13-7cae26b1fd97 | >10MΩ | YES,NO
textbox | 9e6f285d-66fd-56cf-b709-4c5083cc1e73 | Actual Reading if <10MΩ
checkpoint | fe251e3b-f2e0-47da-a196-2c7bede637f4 | 7. Between L3 Phase and Earth
button | 6120150e-b479-5ebb-b823-3d0597e4012d | >10MΩ | YES,NO
textbox | 371fa103-6b1b-5a1d-a8ff-22b0a9a90fe0 | Actual Reading if <10MΩ
checkpoint | 6b83d718-c6ab-4eae-9a93-cbf60e348f7f | 8. Between L1 Phase and L2 Phase
button | 6c31f4b8-d3b5-5a40-aec8-1cace3e40112 | >10MΩ | YES,NO
textbox | e6e64b91-a4fa-503d-a906-c38b723cab43 | Actual Reading if <10MΩ
checkpoint | 322c5bc1-a6a4-468a-90e9-2fbb787585a4 | 9. Between L1 Phase and L3 Phase
button | acae8a88-5a0b-5a84-932f-bd9473732356 | >10MΩ | YES,NO
textbox | c3ac8128-d9c4-5287-a16f-68a7a4233fc7 | Actual Reading if <10MΩ
checkpoint | 5467d427-0bfe-4a76-93c0-dafb6762aab2 | 10. Between L2 Phase and L3 Phase
button | c32f53a4-5b47-5025-8e58-dd468a5b1ae8 | >10MΩ | YES,NO
textbox | c60a138e-3cbd-5d99-a5d7-e1830a41f33d | Actual Reading if <10MΩ
section | 1101a10d-756f-4e13-8fda-4961a22ab017 | Current Transformer Checks
checkpoint | 6e28df17-fe33-4990-b850-65e3962369b9 | Current Transformer Checks
textbox | 2ca59f02-67a2-5beb-b332-0c51245ac3ca | CT ID | YES,NO
button | a0a82070-b7f4-5def-a4e8-ed1406108b82 | CT Polarity is Correct | YES,NO
button | a6f07223-c23c-528e-8fc1-033de1f54bd3 | No crossed phase CT connections | YES,NO
button | ef0bddc3-f045-565f-8180-9f59cbbe3652 | No phase sequence CT connection errors | YES,NO
signoff | 63bf9fa9-ae18-4cdd-93aa-59a4170eb7de | Checked By (Heyday):
checklist | 8007dcfc-3ab6-4e51-b178-76b596a74764 | zSYS - Testing & Commissioning - Subcircuits (Pre-Energisation) (deprecated) |  | Subcircuits (Pre-Energisation)
section | 22ad59a6-cf64-407d-8f90-5890e12e2bfe | Pre-requisite Works
checkpoint | b034e671-5464-480c-b898-4c0b89db9eb5 | Insulation Damage
checkpoint | 13a23277-0fe8-4374-aaef-aa7b3bdea9b0 | Correct Type of Termination
checkpoint | 7d2acd0a-24f3-41f1-8549-e0698682b9c2 | Correct Colour Code
checkpoint | 4919545e-b812-4b77-8115-4ff5721c7d27 | Correct Outlet Rating and Size
checkpoint | 8e34e536-54ec-4939-8934-3f3d3f7f4d4a | Earth Continuity
textbox | e48a685a-85d6-54ef-b8a5-009f1248d667 | Resistance (Ω)
textbox | c60c77ee-1713-51d3-a35f-5f17b87af27b | Target Resistance (Ω)
checkpoint | 25bc796b-0c2c-4d75-b91c-136cda9c846e | Polarity Check
button | 6cc45da1-047c-5b14-889c-43bb3bc119b7 | No Transposition | YES,NO
button | 26306414-0fa5-5acb-b63b-66c528b70448 | Switch in Active | YES,NO
section | d305aeea-8fea-4098-a7dc-afe9deff4cac | Insulation Resistance
checkpoint | 5ee7f7ee-54b7-45c5-b7e2-fe4ee37eba30 | R-W
button | 9a5cb2d1-5579-5a1d-9b00-9e4805b0f7da | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 83ef69cd-1925-58cc-9adc-7a97c9360e5b | Actual Reading if <200MΩ/<500MΩ
checkpoint | 3dea09e1-3881-45ef-a781-85a5a88bdc6a | R-B
button | 2f711467-3548-5a70-a738-dbe6cf167542 | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | a9de846a-1cbb-541d-bedc-8a41e4f24ce2 | Actual Reading if <200MΩ/<500MΩ
checkpoint | 2eb786e6-ef15-4e2b-97b7-eecdb2e097a7 | W-B
button | d41ed56f-5193-5bba-93eb-44438fc6873d | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 12bdb9a2-bf23-546e-a4ec-6cf6665c5f2e | Actual Reading if <200MΩ/<500MΩ
checkpoint | 4ea2dc4b-195a-4c12-9876-230d5ac2040c | R-N
button | f05704aa-afd2-5e64-9910-56add5f5e59d | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 707778f0-646b-5a67-906a-34920889dd38 | Actual Reading if <200MΩ/<500MΩ
checkpoint | ec507b52-7f69-4bbc-b10d-2c56e359c3bb | W-N
button | 9c6102a6-6af6-582f-b34c-d0eb93785a4f | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | b720d213-3f51-53b6-a5a5-14d9b877255c | Actual Reading if <200MΩ/<500MΩ
checkpoint | 3ff57f6f-7d61-4328-ae9a-889cc6d2ee6c | B-N
button | a2c3311f-319b-5340-a658-d46d17c2bd77 | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 4877c8c8-eef6-5ecd-8bfb-b83bbd4b904a | Actual Reading if <200MΩ/<500MΩ
checkpoint | cac2b1f3-b411-4ec9-8814-87c194603224 | R-E
button | ccbea4e6-80ce-5526-a285-93b56c1384df | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 96871594-a87a-5d28-8a5b-cfc2b9dc9d0b | Actual Reading if <200MΩ/<500MΩ
checkpoint | 3ffd3ec4-dbde-4082-b569-5d08acbec281 | W-E
button | 8965c822-04f9-55cf-951f-5ba61123f22c | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 0d686dc2-1a52-5be8-b36d-6909a37f2c4f | Actual Reading if <200MΩ/<500MΩ
checkpoint | e9083a50-4c3b-4382-9700-a8de9e654525 | B-E
button | 820de140-0575-5936-9d37-3b64d320489a | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 213182a6-0653-5767-9dc0-31a947da6ceb | Actual Reading if <200MΩ/<500MΩ
checkpoint | e64ac7ba-1607-4ff5-8cb6-d0567d4db251 | N-E
button | 5be7cda6-dacf-5b45-9a4c-09f61f5c2f3b | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 4e5f42a4-56dd-5ff3-ac48-cc3a42e72347 | Actual Reading if <200MΩ/<500MΩ
signoff | 101aba1c-8202-4327-9a19-cdc1f43535a6 | Checked By (Heyday):
checklist | 0ab4814e-ddcd-49f8-8d06-d7ee539439a5 | Testing & Commissioning - Low Voltage Busduct (Energised) |  | Low Voltage Busduct (Energised)
section | 56b517ed-d914-41f2-96a7-965ae9efdff1 | Phase Rotation
checkpoint | 4c6ab7d8-e371-4454-b5bd-85d1fc9e87e2 | Direction
button | a30d2ede-1096-5c42-975d-8a1be371ca17 | Direction | Clockwise,Anti-Clockwise
signoff | fa9a7ff6-7c7a-431a-983e-756bb25dea55 | Checked By (Heyday):
section | 8e265440-c473-440d-a516-0359dd4e6393 | Voltage
checkpoint | 94d46092-4876-4725-b9f8-5d7434200652 | Red - White
textbox | 4acfc2d5-d4cd-5a9e-a48e-4556de77b138 | Voltage (V)
checkpoint | cea9d429-b75d-431a-85a7-aa3358f67df3 | Red - Blue
textbox | 33b3e158-b999-558b-8219-4378cabaf116 | Voltage (V)
checkpoint | f78d8e9d-64fb-4a16-9fee-f2eae06c45c3 | White - Blue
textbox | 3aa40e1d-b21a-5f71-8fac-e8968bdbf5e1 | Voltage (V)
checkpoint | 1898309a-844d-4694-b4ce-867734163b9e | Red - Neutral
textbox | f5241f11-686a-59f5-9ff4-cfdbe0b920e4 | Voltage (V)
checkpoint | 9fe0a72a-67fd-4f6d-b4bc-657002c5487f | White - Neutral
textbox | 1e87b879-5ba3-5d4b-825b-a059e4ff959c | Voltage (V)
checkpoint | d5eb50a9-bf63-4c23-82f2-2807888f24dd | Blue - Neutral
textbox | bf6b7655-9c2e-5ff2-9973-938cf3c6aaf6 | Voltage (V)
checkpoint | 5659b85a-684e-49c6-9618-92a793aea502 | Red - Earth
textbox | 2b3b47e3-65cb-5550-b872-92b0c10c686f | Voltage (V)
checkpoint | 747676ca-124e-403e-9c65-c5ba6e57922d | White - Earth
textbox | 1f5ad7ba-1296-50a3-8a73-943d46b0379a | Voltage (V)
checkpoint | a24327c9-3e70-4ccc-bb76-6fd489037fda | Blue - Earth
textbox | b045f50e-7da0-5ed0-af29-d3fad1980b0c | Voltage (V)
signoff | 4d8d5f35-7891-47d0-8ebd-e1cb5724390f | Checked By (Heyday):
checklist | 6074ec10-56f3-4474-abae-aef805bb6293 | ITP |  | ITP
checkpoint | 652e967d-7a17-434c-bf03-94f23854ac39 | Please attach copy of ITP
checklist | 3197a15c-fb25-4da8-93c2-1071feb4a30a | Quality - Mains and Sub Mains |  | Quality Mains and Sub Mains
checkpoint | 5995aabe-eb0b-4f72-bd17-b11af3d003ea | Receipt of cable containment delivery to site & storage. (ITP Reference Item 1)
checkpoint | 454354e1-cd28-4ebc-a495-5ba71e40b723 | Cable storage & handling. (ITP Reference Item 2)
checkpoint | f84e2ad5-6f64-4be4-992c-2b0d33e84078 | Correct cable size & type. (ITP Reference Item 3)
signoff | 355beeb6-9c31-4d23-b970-601bca7f4c7c | Signoff Required from Heyday & Multiplex
checkpoint | f1021e10-0d78-4abb-a08a-31619a07b4b0 | Cable pulling tension to not exceed manufacturer's recommendations. (ITP Reference Item 4)
checkpoint | 260eca92-0c0f-4aab-a131-bc516cea6278 | Cable lubrication if required. (ITP Reference Item 5)
checkpoint | 90df3d73-26f0-4bd0-82b7-0e057a263b0f | Installed to latest drawings – schematics/single line diagram & cable containment drawings. (ITP Reference Item 6)
checkpoint | 92eb3322-198d-4c8d-b841-6b7ca9b79fbb | Correct cable tag installed. (ITP Reference Item 7)
checkpoint | 526951e3-3236-44db-8c32-95480e8172d6 | Photo evidence captured for cable containment install. (ITP Reference Item 8)
signoff | cd03cf1f-383d-4515-970e-26c0bb9ee7b3 | Signoff Required from Heyday & Multiplex
checklist | f008c625-0eb2-41be-bb21-70905f27afe1 | Quality - Pole Light Pier Installation ITC |  | Quality - Pole Light Pier Installation ITC
checkpoint | 150bb9b1-6ff3-4517-a999-29c791e0df61 | Receipt of foundation cages delivery to site & storage. (ITP Reference Item 1)
checkpoint | 40a15249-fc25-438a-a714-c3ec4f9948c6 | Set out (Correct pier locations as per approved shop drawings). (ITP Reference Item 2)
checkpoint | 70c1d0ea-0b23-418f-af30-df6a3e39d09c | Correct trenching alignment & depth with excavator and auger. (ITP Reference Item 3)
checkpoint | a554b496-d39e-49df-ada2-7b544e3a5299 | Install cage and rag bolts to correct finish level. (ITP Reference Item 4)
checkpoint | df47fdc0-37ca-4661-9466-466795668e86 | Install conduits and formatube. (ITP Reference Item 5)
signoff | adbead86-a352-4716-ae61-5a3fcb4bca6c | HOLD POINT inspection prior to concrete
checkpoint | eef05d75-6bdd-4963-a418-fea84d40db8f | Concrete installation with tremie pipe. (ITP Reference Item 6)
checkpoint | ecb7f41c-9222-488e-a9dc-2ae0d04db3fa | Photo evidence captured for cable containment install. (ITP Reference Item 7)
signoff | 755b64e9-dc2a-4a45-92c7-18cf070d7538 | Signoff Required from Heyday & Multiplex
checklist | 55687e49-7ac5-41c7-95bb-08c0e7c58654 | Testing & Commissioning - PMCS |  | PMCS
section | 6d39116f-93ac-4c31-b733-b41891044e4a | WSA20-MPX-04000-EL-ITC-31183000 - Component Tests (Pre-commissioning)
checkpoint | 0f3e7711-e0b9-4442-9cde-9544fac38446 | Schneider Point to Point Validation ITP - RIOM
checkpoint | 363f12e9-42ca-4ebd-9f72-465cb421c246 | Schneider Point to Point Validation ITP - PAC
checkpoint | 909ed226-bacd-4172-948f-6bb3a9774ffe | Schneider Point to Point Validation ITP - EPS
checkpoint | 4170b671-0120-496a-950c-fc6c643c72a1 | Schneider Point to Point Validation ITP - PFC
checkpoint | 4bce19cd-c9e5-44b5-8633-e57edd635592 | Schneider Point to Point Validation ITP - UPS
checkpoint | 512c4451-1ea2-4d4c-92e5-aa9bedb5a86f | Schneider Point to Point Validation ITP - EV
checkpoint | fb8cc9f5-9762-4676-8db2-7fb9a4072ff9 | Schneider Point to Point Validation ITP - IEM
checkpoint | fef1adbb-cd17-4792-83f6-ddad180e93d7 | Schneider Point to Point Validation ITP - eGSE
checkpoint | e0760722-56ae-4c39-9758-f4ad831a7800 | Schneider Point to Point Validation ITP - GEN
checkpoint | 0d4a2136-bbf3-4120-9af8-aa4ee417b934 | Schneider Point to Point Validation ITP - LCS
checkpoint | f2e4baf3-db16-42c1-856b-c5d1ea2af0dc | Schneider Point to Point Validation ITP - EML
checkpoint | 32ac393c-b449-49c8-8c01-4537449c011d | Schneider Point to Point Validation ITP - PV
signoff | 2aaa59e8-f9a9-40e8-95e6-eb37298f6b25 | Checked By (Heyday):
section | ff22da6d-3cf0-4ac7-84a6-1401d58129f9 | WSA20-MPX-04000-EL-ITC-31184000 - System Acceptance Tests (Commissioning)
checkpoint | 42e63be9-0b4d-45fa-a96c-67f05aaa6664 | Schneider WSA LV PMCS Cx ITP - RIOM
checkpoint | b1cacbf7-ed0f-4b96-9a82-abceea0421a7 | Schneider WSA LV PMCS Cx ITP - PAC
checkpoint | 8c03faf9-2e4c-4ef7-9741-bad9b0bbc42d | Schneider WSA LV PMCS Cx ITP - EPS
checkpoint | d1aca762-82b0-4fa7-9cd5-d65258b3be37 | Schneider WSA LV PMCS Cx ITP - PFC
checkpoint | d5f5901f-5e6f-4899-b397-55aa27f163eb | Schneider WSA LV PMCS Cx ITP - UPS
checkpoint | c0daf05b-b0eb-4b4e-8f71-b97e9dc4a6e4 | Schneider WSA LV PMCS Cx ITP - EV
checkpoint | 8ace8b4e-3b9a-43be-9525-4151be7b76cc | Schneider WSA LV PMCS Cx ITP - IEM
checkpoint | 559e5a9a-153d-4f70-9936-accb5ef23056 | Schneider WSA LV PMCS Cx ITP - eGSE
checkpoint | e76c6a77-eb82-4ce1-b0ab-43b760b35fd1 | Schneider WSA LV PMCS Cx ITP - GEN
checkpoint | d50a52b4-a611-4608-996c-f6ed4059e72b | Schneider WSA LV PMCS Cx ITP - LCS
checkpoint | 04659ead-350e-4522-adac-90c797c5c308 | Schneider WSA LV PMCS Cx ITP - EML
checkpoint | f983179a-9ad1-4eb9-a581-a3b64af3d443 | Schneider WSA LV PMCS Cx ITP - PV
signoff | 5575884b-b5f1-4f3a-bcf7-d8139b45eee7 | Checked By (Heyday):
checklist | 13cf0cf9-c3da-4e9c-bb52-18cc0215eece | Testing & Commissioning - Low Voltage Busduct (Pre-Energisation) |  | Low Voltage Busduct (Pre-Energisation)
section | 2683ac7d-d83d-434f-86db-4bc68ec544c8 | Pre-requisite Works
checkpoint | 6f6e2026-e685-47f6-96eb-26aab5f17835 | Insulation Damage
checkpoint | fbb93c2b-c852-4a57-b3e1-c9ab11a568fc | Correct Type of Termination
checkpoint | cfc0e5d9-f976-494b-9421-9032e5ad627c | Correct Colour Code
checkpoint | 4478576e-9436-47da-943e-dbc0c0770867 | Correct Size and Labelling
checkpoint | 0af3d548-923b-45c1-9792-4072fb23bf3a | Correct Routing
section | 52688ba0-c53b-4ecf-9ceb-ed2c6bea4ef1 | Continuity Testing
checkpoint | 2bbbeb81-d76f-4ab7-9b37-4af81c15d03e | Red Phase
textbox | bccf9913-d1d2-56f3-a607-88c92ed9ccab | Resistance (Ω)
textbox | f6644a85-f277-584c-b823-e4aabc9fe3fa | Target Resistance (Ω)
checkpoint | fb88138b-a601-468d-a400-b241f2a7d8f1 | White Phase
textbox | 0b7948c2-7d82-5100-8f1b-4cea01b30f18 | Resistance (Ω)
textbox | 66424b14-26aa-5233-a73e-8fa6cc8050f6 | Target Resistance (Ω)
checkpoint | 9c311428-b330-40eb-b40c-1dd67b1725aa | Blue Phase
textbox | 52743c86-7a1e-5846-9ed4-16d922e5a47a | Resistance (Ω)
textbox | 5f38758d-f8b6-51ab-a26e-c74dd36d841b | Target Resistance (Ω)
checkpoint | b34c5bdc-1be4-4637-b9d2-444cd99281de | Neutral
textbox | f370275e-68f7-5955-8861-2dcb1588eb3e | Resistance (Ω)
textbox | 585a13f3-7590-5d8a-bbc8-95d5275da47a | Target Resistance (Ω)
checkpoint | 30c50d31-0f05-4055-a918-1ca7a5211171 | Earth
textbox | 3b368092-9571-5aa2-a2a7-e0730ef000fd | Resistance (Ω)
textbox | b7961f1e-bd19-544e-968b-da79a8efb990 | Target Resistance (Ω)
section | fb07be62-3a2f-4f9c-b77d-500cab4e5db9 | Insulation Resistance
checkpoint | 4b1c9924-2f9e-4a2f-9e95-666cf0fe70da | R-W
button | 71e52e0f-a926-568d-a8cd-a92f6c639b94 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 236615dc-9f7f-5d83-b480-8f4a2ee5b083 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 40e123b4-db69-43d8-9785-4b395c22ffc5 | R-B
button | 970d468e-6b01-5be9-b3b6-05d5078c0aab | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 33641d8f-e337-533a-a805-87211cbf3a91 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 8d09ae7e-c911-4b43-af36-414ea08fcce7 | W-B
button | b3b8d3a8-65a5-5c5d-aeec-ccbf4ea127a9 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | ee127d77-1bf2-5c44-b48e-7269a34edaeb | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 160b2c93-6069-4671-95ba-e72256df6f8b | R-N
button | bd4e072d-3fcf-52ff-82b9-294e57745273 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 7ec26620-539d-538d-ba0d-db4f4d700f79 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 2218ed7b-c321-493c-b1f1-41861b0b0a42 | W-N
button | f2522ff5-f858-50ac-afa5-d36327eba8b7 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | a8e1d7e2-1f9d-5fae-a962-5a9ff4b7e50e | Actual Reading if <500MΩ/<1000MΩ
checkpoint | a13a077c-4e34-4816-acfd-d56ca034e416 | B-N
button | e6c30564-7894-53de-84e1-27f305aa7aee | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 53ed9870-e3ff-5a45-9d16-70ec0141be7e | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 55c6628d-118f-484b-8659-a501d45e9040 | R-E
button | b0dfed67-2b0a-5d94-afbf-b0695936573b | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 1dd8bfc4-1c23-5ce6-8bd8-e776a7524c53 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | b868133f-b4b3-4beb-a629-a4b3ae5e6ccf | W-E
button | 8f12b33d-2867-5720-809f-451dd09a8a35 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 11d0aeb0-8c74-5805-8a27-3c9ffc096d80 | Actual Reading if <500MΩ/<1000MΩ
checkpoint | 2f1e5474-67ca-4290-a4c0-d0c00ab0fa5f | B-E
button | 91374eda-c96c-52e7-8d39-0ea32572ab8c | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 14a493d0-eeb2-5290-9728-f1b86a8b0eba | Actual Reading if <500MΩ/<1000MΩ
checkpoint | c9a0cae2-b286-4106-845c-1cc0f3a2c670 | N-E
button | 5c0881ea-f11e-5a26-9ea2-899b372ad1a0 | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | 9ec664f6-3127-5687-85f9-817771475f51 | Actual Reading if <500MΩ/<1000MΩ
signoff | 475fb419-ba6d-4392-acf5-3dc809c6e54a | Checked By (Heyday):
checklist | fdca44a3-a610-4a4a-a0ea-7da07a734c72 | zSYS - Communications - Cabinet (old version, 15-03-24) |  | Cabinet
checkpoint | a6b5c039-9104-4d59-ab1d-6bfb5762edd5 | Confirm rack has been earthed
checkpoint | 83c98af0-89bb-42b3-871e-fe93cc9cd729 | Confirm cabinet has seismic fixings and bayed together.
checkpoint | 0a237f42-78de-4a32-b6a8-8d1d0024fc3d | Confirm cable management installed
checkpoint | c1084f6e-3980-4a5c-8269-2e82fcc13c33 | Confirm cabinet has asset managed label on front and rear
checkpoint | cc59b323-0b74-425c-8606-50e8f1820b7c | Confirm Cabinet is correct orientation
checkpoint | 7ea45823-f0f0-4797-a3d6-e4ef97ffaa13 | Confirm PDU-A and PDU-B are on correct side and plugged into correct power supply
signoff | 2ff22c34-eb26-4df6-afa8-2ad76c2cc4a7 | Checked By (Heyday/MDE & Multiplex):
checklist | beabc3c1-d91c-4682-8f40-36c8a2a82b21 | Communications - Cabinet |  | Cabinet
checkpoint | 41f7b111-03de-4550-8d87-5c1e6cb2c7f4 | Confirm rack has been earthed
checkpoint | d69dbbde-2831-4f20-a233-c9500bca8943 | Confirm cabinet has seismic fixings and bayed together.
checkpoint | e0513bfd-d7c9-4a3c-9249-3b9bbcefba5d | Confirm cable management installed
checkpoint | 1d5dc9f3-e563-4f3b-a2d5-c8343f3db3c3 | Confirm cabinet has asset managed label on front and rear
checkpoint | 553c8be5-5cae-4441-a886-0bdbfa7e5068 | Confirm Cabinet is correct orientation
checkpoint | 042b9b80-7f34-4164-9730-3e77da608a83 | Confirm PDU-A and PDU-B are on correct side and plugged into correct power supply
checkpoint | b1a466ed-7739-4389-9eb4-13bc7fdc884f | All copper and fibre cabling has been terminated as per rack elevation
signoff | 68fc4045-c8b9-4435-81ce-c4cafa93074a | Checked By (Heyday/MDE & Multiplex):
checklist | 2a7a5575-2a12-47c2-a292-10a24024510d | Quality - Power and Lighting Subcircuits |  | Quality - Power and Lighting Subcircuits
checkpoint | 70aa64d9-0d08-47a5-8647-185834a86644 | Receipt of cable containment delivery to site & storage. (ITP Reference Item 1)
checkpoint | 84059ae9-7244-4dd8-9a39-ebc63fff828d | Correct size & cable type. (ITP Reference Item 2)
signoff | 4a470d59-f780-42db-bffe-6da8cc16b798 | Signoff Required from Heyday & Multiplex
checkpoint | db00ad9e-a369-4a3c-bd2f-9ccd89e5e646 | Installed to correct cable routing arrangements & circuit number. (ITP Reference Item 3)
checkpoint | 4219368a-1076-4619-8929-abca8707cfec | Installed to final location. (ITP Reference Item 4)
checkpoint | 20a0c556-952f-4aa0-bd5d-f94f701bcb09 | Photo evidence captured for cable containment install. (ITP Reference Item 5)
signoff | 1edfb0b5-9856-4905-aedf-671e3f5cee52 | Signoff Required from Heyday & Multiplex
checklist | 649a71d7-064d-465e-ba05-320512b949a3 | Quality - Electrical Equipment/Accessory Installation |  | Quality - Electrical Equipment/Accessory Installation
section | d18315df-1b72-43cc-9143-5c9bc3430f85 | Quality - Electrical Equipment/Accessory Installation
checkpoint | 585c5f70-3264-4601-aca9-9f6dc7a514ed | Installed Correct Type/Colour of Equipment or Accessory
checkpoint | cac01609-7c33-4cab-af93-fbd489f9fe06 | Installed to the correct location as per drawings
checkpoint | 912552dd-470f-4970-90de-7ef32e3bc3fa | Installed with correct fixings and made safe
checkpoint | 3c9b09ea-59d1-4090-b937-0a7ad38b7c63 | Installed to the correct Circuit & DB Destination
checkpoint | 47fca860-7d93-449d-8125-dc0d57e93b9d | Installed correct labelling
checkpoint | 03dffa92-dc6d-46f4-a357-8a4226f1f897 | Final Check and No Damage to item
signoff | 8cad35c9-294a-40ec-9219-3986eeb6d95b | Signoff Required from Heyday
checklist | 54731133-f18a-4d97-95e6-64aee3d66a70 | Testing & Commissioning - PMCS - Energised |  | PMCS - Energised
section | b70035bd-c922-47e0-9f91-0f5759ee6df6 | WSA20-MPX-04000-EL-ITC-31184000 - System Acceptance Tests
checkpoint | 7ccf45df-e107-415e-9a6d-9245237e61b7 | Schneider WSA LV PMCS Cx ITP - RIOM
checkpoint | 35fe0e6a-d70a-45f6-b5a0-9076eb4e528f | Schneider WSA LV PMCS Cx ITP - PAC
checkpoint | e0f9faba-82f3-4bde-aeea-b94722c0dd90 | Schneider WSA LV PMCS Cx ITP - EPS
checkpoint | b4961f39-3aa9-4694-9dc6-de81d5c81979 | Schneider WSA LV PMCS Cx ITP - PFC
checkpoint | 86227350-4ca3-4fa3-b4b7-31f467675a19 | Schneider WSA LV PMCS Cx ITP - UPS
checkpoint | afe2194c-92fd-4db9-b886-e7adbef9c63c | Schneider WSA LV PMCS Cx ITP - EV
checkpoint | aa8f5b05-c914-45f0-85ac-f98ad2a0887a | Schneider WSA LV PMCS Cx ITP - IEM
checkpoint | 8ad6dd46-99e8-4ea3-86e9-acb9990841c3 | Schneider WSA LV PMCS Cx ITP - eGSE
checkpoint | d330c9ca-c23a-4890-8100-15367f9d3983 | Schneider WSA LV PMCS Cx ITP - GEN
checkpoint | e8108dda-ac8d-427e-ac1a-b770391d63df | Schneider WSA LV PMCS Cx ITP - LCS
checkpoint | 68acecc8-1749-4a90-a9db-d88123034461 | Schneider WSA LV PMCS Cx ITP - EML
checkpoint | 13681449-c97e-47ca-83d4-503418a2b151 | Schneider WSA LV PMCS Cx ITP - PV
signoff | eba7d451-5aae-4829-a17e-b3335210cf9c | Checked By (Heyday):
checklist | 86aa87a6-b5d4-4b51-9765-f9fe0fc446b6 | Quality - Pole Light Footings Installation ITC |  | Pole Light Footings Installation ITC
checkpoint | 93472ed9-c576-4bed-b079-e12233246175 | Receipt of foundation cages delivery to site & storage. (ITP Reference Item 1)
checkpoint | 791b4fb7-fecc-41d7-ba76-cc69cb27162e | Set out (Correct pier locations as per approved shop drawings). (ITP Reference Item 2)
checkpoint | 19e95f7b-a15c-46ca-a66e-1812cf73670b | Correct trenching alignment & depth with excavator and auger. (ITP Reference Item 3)
checkpoint | 22f2ae71-60be-47d2-a9f0-112b19deee8c | Install cage and rag bolts to correct finish level. (ITP Reference Item 4)
checkpoint | 13281cde-694f-4b1e-9787-09b3d6d65227 | Install conduits and formatube. (ITP Reference Item 5)
signoff | 23fa6f29-6099-4518-9c9d-54ac3c86a3d9 | HOLD POINT inspection prior to concrete
checkpoint | cd81f109-9a77-4b22-a318-90a67a3acbd7 | Concrete installation with tremie pipe. (ITP Reference Item 6)
checkpoint | 17ea0ec2-33b1-4fee-be15-8539fba8033e | Photo evidence captured for cable containment install. (ITP Reference Item 7)
signoff | 1d223f93-c353-40b4-95bf-e85ae1de063a | Signoff Required from Heyday & Multiplex
checklist | 74ef4895-c901-4195-b1e6-568fa108d3a6 | Quality - Pole Light Pier Installation ITP |  | Quality - Pole Light Pier Installation ITP
checkpoint | d141cdf8-2c92-468d-981a-8d40874001e6 | Approved IFC Drawings
note | 6d19f8f7-788c-5e0d-bc33-76dd10f80676 | Review drawings and revision status with Heyday drawing register, ensuring to only work to AFC drawings, and approved documents:
note | 6537a2f2-5fc0-5d31-ad24-477d3b5fdbe7 | WSA50-MPX-02702-EL-DRG-000321[05]
note | 50142c21-8e58-54b0-a011-450d0a00704e | WSA50-MPX-02702-EL-DRG-000324[01]
note | 5ede2959-a4a4-5661-90b8-2e133bcd7ac8 | WSA50-MPX-02702-EL-DRG-000304[03]
note | 1b604985-bcd6-5249-b8dc-453724b876b5 | WSA50-MPX-02702-ST-DRG-001202[04]
checkpoint | b906b77c-0024-4d28-b9bf-a934707889b0 | Material
note | 4d042522-c3ed-59c0-98b3-e389f0bc615a | Only use material approved by MPX through the required sample process listed on Heyday samples register as approved:
checkpoint | 9dcf734f-1498-43bc-b595-e006ecacecff | Receipt of foundation cages delivery to site& storage.
note | e5fb6037-18c8-5625-b350-5b308891b02a | Review all delivered against approved product submission and confirm conformance. Components parts list, as stated on the purchase order/invoice, to be validated against received items
checkpoint | 42000244-686e-4421-a8cb-59ed88c7b67a | Set out (Correct location set out as per approved shop drawings) .
note | 641e1bda-b6cf-535c-a749-bdfc8f2a4302 | Set out to be confirmed with latest AFC drawings. WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
checkpoint | 3ce17901-8e6a-45aa-9285-07af72c9dff6 | Correct trenching alignment & depth with Excavator and Auger. If rock is struck, geotech will be required to confirm socket depth
note | f446e29a-1c71-5f6e-b685-f90d8b55d83d | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
checkpoint | c8b8768d-7078-4443-93fd-a29b58825976 | Install cage and Ragbolts to correct finish level.
note | 42cae0c5-c6c2-59c4-b958-c38b9208aedf | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
checkpoint | 39ce1519-db25-4e34-adba-82c81eb82cb3 | Install conduits & Formatube.
note | 9432e873-9bf2-5eee-998a-29466ac400f9 | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
checkpoint | 03299ee3-8868-4dd6-97a4-ed326639b3b9 | Concrete installation using Tremie Pipe
note | 0f27ed9f-3b54-5939-ac39-1a396cf37601 | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
checkpoint | aff63e29-d37a-430a-b815-0b2ac0cb1d1c | Photo evidence captured for asset install
note | 5f6419e0-e42e-5b67-978e-8347f3b8d982 | Photo evidence to be captured, stored and provided for formal submission where applicable/outlined within ITP
checkpoint | 2401931c-f442-410d-a3b9-fdbcc09f344c | Completion of installation
note | bc61b16b-a422-592b-a8e3-872930dbfdba | Heyday supervisor to ensure that all work has been completed to relevant standards & approved drawings
checkpoint | 1ffd0d95-180e-4ef8-8820-4b993ed022ab | Photo Evidence
note | 44f4be71-9bd2-5438-9773-100944729e64 | Heyday supervisor to capture & submit photo evidence as part of completed works specified within ITC
checkpoint | d3dd1b34-8145-42d8-945f-de334445dffa | As-built survey & report
note | e1c38bfd-eb43-5e6e-a058-5a000c373a09 | Heyday supervisor to submit As-built drawings as part of completed works
signoff | c39d730b-b3ac-4805-bcfa-347c07a5600f | Signoff Required from Heyday & Multiplex
checklist | 1d378708-99dd-41cd-983b-c8c2d8a87dfb | Quality - Cable tray/Ladder |  | Quality - Cable tray/Ladder
checkpoint | f7304667-4e24-48f5-86d3-64ffdb1e21d2 | Receipt of Cable Tray delivery to site & storage
checkpoint | 2bd9f9cf-263c-476d-95d4-0a08b088bef3 | Set out to be confirmed with latest AFC Drawings
checkpoint | e64772dd-b6dd-4bf5-8a12-dc36b7263180 | Accessories to be factory made items
checkpoint | fc0f799c-8b1b-4379-bc47-2f292f97907c | Correct Levelling & Alignment
checkpoint | b080b835-d7b7-432f-a0c0-8ab4fe9b2f95 | correct bracket and safe fixing
checkpoint | 4a33f2d3-208c-4b01-be48-6274464e9497 | Correct Bends used (Cable Ladder)
checkpoint | 3928498c-2649-4de9-8894-ce6451f89040 | Cable Tray Checked For Sharp Edges
checkpoint | 818b9572-aaf8-4143-80ad-91e2dbb47f32 | Containment Earthing - As Per the Standards
signoff | ec96a558-76fa-48dd-91b2-bf90d58d063c | Signoff Required from Heyday & Multiplex
checkpoint | 2d94ecbf-4577-48d4-8ae1-f2e0f5ca54ef | Photos attached.
checklist | df71fccc-889f-4250-bc86-4df129d6a8ae | LOT BREAK UP |  | LOT BREAK UP
checkpoint | dcdf5328-e886-4cde-95f0-59dde8dc5444 | Attached Mark up of Lot Breakup
checklist | f5d4527b-a4f5-4f85-a73d-8bb4269b0fe5 | Quality - Distribution boards |  | Quality - Distribution boards
checkpoint | d6119b14-f47e-46ad-9c3d-1dfc2d7431d3 | Receipt of switchboard delivery to site
checkpoint | bce8f233-f43b-4bb6-a305-e9445debc197 | set out to be confirmed with latest Switchboards Shop drawings
checkpoint | 3fed3a41-f5ad-4054-adc2-0c781a13ca4d | Correct alignment to set out drawings
signoff | d3ccabc7-63ba-425b-ba90-8961928abe68 | Signoff Required from Heyday & Multiplex
checkpoint | 0b755a50-7baf-4f0c-8830-94a475ae7592 | Correct bracket and safe fixing
checkpoint | aa1624e4-fda7-4b38-9962-42d72de05b34 | Photos of boards attached
checklist | acb2f3e9-3777-4399-b35b-cd82a51e0bc9 | Quality - Inground LV & Communication Conduits |  | Quality - Inground LV & Communication Conduits
checkpoint | 9b2fffc9-270e-40a7-8705-dc47b2e2fc93 | Receipt of conduit delivery to site & storage. (ITP Reference Item 1)
checkpoint | 70b2b64d-0827-4bee-80ee-6c7a6b30714b | Set out. (ITP Reference Item 2)
checkpoint | 0a679e76-8055-432b-9110-4815fb67c9bc | Excavation - Correct trenching alignment & depth. (ITP Reference Item 3) HOLD POINT
signoff | 59074d54-8fd4-43b0-a5b8-4cdfea916d9c | Signoff Required from Heyday & Multiplex
checkpoint | 357831f8-c75f-46be-9596-87d215933f06 | Conduit Installation. (ITP Reference Item 4)
checkpoint | 9e6699ed-e0b0-4dd0-b3a0-700451229f5f | Spacer Frame Installation if required. (ITP Reference Item 5)
checkpoint | a87979ac-06d4-4e99-82f7-e6aaefb00a8f | Change of direction/bend Installation, correct bending radius used as per drawing. (ITP Reference Item 6)
checkpoint | 333936bd-24ef-4be2-9e99-69381801f33f | Glue Conduits together. (ITP Reference Item 7)
checkpoint | 6987a898-3ce5-4f8a-a5de-6ab949600aeb | 300mm cover of backfill above conduits. (ITP Reference Item 9)
checkpoint | 8f0fea9b-58bd-4345-9e8a-4aa51bceb2c8 | Warning tape installation above 300mm cover. (ITP Reference Item 10)
checkpoint | dec68183-4c9b-4ee1-9342-effcea72e79a | Back fill & compact. (ITP Reference Item 11)
signoff | 96c28ed0-6797-4ae4-b00d-b769a9c6d3bb | Signoff Required from Heyday & Multiplex
checkpoint | 3d9dc89b-30c6-419b-a47d-9320633a0ebf | Record photo evidence. (ITP Reference Item 14)
checklist | 4f516721-9264-4603-a113-5d0c70e71377 | Testing & Commissioning - Lighting Control |  | Lighting Control
checkpoint | 8c82fdbe-8112-4b24-8d84-0462942894a2 | Pre-requisite Works
checkpoint | f6adb625-199d-424f-91ee-be65f1df8ba3 | Correct Location & Labelling
checkpoint | 857c855a-81e6-4de5-a16a-74858e79f3c5 | Manual Control
checkpoint | e0ecd3a3-ac7c-4d58-81db-b765f2d3fefa | Occupancy Sensor or PE Cell Control
signoff | 420e3ac5-6120-45c2-9561-ce56de03204b | Checked By (Heyday):
checklist | eb8a49ae-7f4d-4e38-9f02-6cdfbf19ebe8 | Testing & Commissioning - Solar Photovoltaic System (Energised) |  | Solar Photovoltaic System (Energised)
checkpoint | c81c44e5-267c-40b2-a310-23bc182cb8ef | SCS Commissioning Checklist Section 5 (System Measurements – AC Measurements)
signoff | a426b55b-f3e5-4f30-8dd8-13ee8bc08ab1 | Checked By (Heyday):
checklist | 10d56c3d-cdad-465f-b948-220f28af9777 | Testing & Commissioning - Single Phase Subcircuit |  | Single Phase Subcircuit
section | 99fcf775-d9d9-45aa-bc40-72ea8e95beac | Pre-requisite Works
checkpoint | b6245e80-1e48-4375-9cfc-b3295cba6b21 | Insulation Damage
checkpoint | c960e5b7-636f-44eb-8b9e-1acc1f6c3372 | Correct Type of Termination
checkpoint | 830d7519-7adc-4fe4-990f-97619c9fa743 | Correct Colour Code
checkpoint | 6623d9a4-6615-4c48-a1c0-4c32931da7b4 | Correct Outlet Rating and Size
checkpoint | 6af80b46-6884-4add-b7f2-b4eb130de2b9 | Earth Continuity
textbox | 060aa90b-811f-5ad5-a5da-76c27b44531f | Resistance (Ω)
checkpoint | 7eec440f-bc3f-455d-bf19-55fc824a350a | Polarity Check
button | 440b6016-299e-5394-867f-385fa07202af | No Transposition | YES,NO
button | 053b0de7-0eb6-5547-9d2d-46e1f3bf95e9 | Switch in Active | YES,NO
section | f4a80d27-97cd-4a26-b498-168f68df6e9a | Insulation Resistance
checkpoint | 8ba76168-4007-4b84-a280-12de7c138cd0 | R-N
button | 537274d1-6646-5c85-9b27-ebf56328087c | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 6dafc51c-6de6-5824-870b-a7a7a90a7265 | Actual Reading if <200MΩ/<500MΩ
checkpoint | db4bc454-6f5c-491f-a3a3-dfaca4127ad2 | R-E
button | 8982dd66-b9fb-5b80-853e-77054ede7db5 | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | ae800fe7-c015-5255-b809-77f63aec3189 | Actual Reading if <200MΩ/<500MΩ
checkpoint | 40c2ab33-5545-4ccd-9b21-54406f15e189 | N-E
button | b6de9cfe-c2d0-5ae3-97a9-4ecc322b1504 | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | 7eaa26a2-e6bf-5dbe-bc66-803628eeb184 | Actual Reading if <200MΩ/<500MΩ
section | 28c42bf5-375b-4323-800e-8f7333eb5598 | Voltage
checkpoint | c4eb594f-a5e8-4bda-ad37-025dc2ed4b10 | Red - Neutral
textbox | 40d5203f-80a5-5632-8e29-135176de772d | Voltage (V)
checkpoint | 23234cdd-c1ec-4a2d-a172-b8a9451f300a | Red - Earth
textbox | fb73a258-9d7e-5f99-b38f-64a76c6df601 | Voltage (V)
section | b0eba347-4d78-4768-a547-43d5a8d27339 | Earth Fault Loop Impedance Test / RCD-RCBO Tripping Test
checkpoint | 9af5b6e3-ad80-4327-acd6-fd1c0042d1b4 | Impedance - (N/A if the circuit is RCD Protected)
textbox | ca658463-6c9b-535c-9f84-e77a01da0d98 | Record Inpedance (Ω)
textbox | 35a29d49-1248-5728-ad7c-5f968884a5b1 | Target Impedance (Ω)
checkpoint | 4429efd3-4f70-4c1d-b68e-8e99ef5835f9 | RCD/RCBO Tripping Test
textbox | e3ba2339-b613-58ff-83a6-2095d2667dcd | Trip Current (mA)
textbox | e0ca11a2-eb7e-51dd-ad53-5839c860a2f7 | Trip Time (ms)
signoff | 858b7cb6-6ac1-489a-b2ee-fa203eaa4510 | Checked By (Heyday):
checklist | 9fab4365-0c7c-4272-bb80-5b9faa529583 | zSYS - Testing & Commissioning - Main Switchboards (Pre-Energisation) (old version) |  | Main Switchboards (Pre-Energisation)
section | 22eb7f7e-8c59-4487-a47e-66dfb2a8e4d9 | Physical Checks
checkpoint | 5c2ce6ee-2a07-4eb2-9732-1425352814d4 | 1. Confirm boards dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | 5be2bd0b-1025-4ae4-ab50-3f0c711f4972 | 2. Confirm correct MSB Form of Separation, Provide actual Form of Separation in Comments section
checkpoint | 996b0331-5238-44f9-8e27-1af654b0136a | 3. Confirm the Layout of fitted components (ACBs, MCCBs, MEN, ATS) is in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | d34f0ac7-b294-4054-a440-b05145502ed7 | 4. Confirm that Brand of fitted components is in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | d13c1f9f-6f12-45a5-abe1-069a42001d25 | 5. Confirm meters location, types and labels are in accordance with approved shop drawings
checkpoint | fed66c04-a281-4226-85d2-cc1308b854d6 | 6. Confirm the circuit breakers rating is in accordance with discrimination study (provide discrimination study reference in the Comments section)
checkpoint | 166bb322-d628-43ec-9bf8-041b5379fdf0 | 7. Confirm Trip units and protection relay settings are set in accordance with discrimination study
checkpoint | 93ac2995-c7cb-4cc3-a23d-7aeb233d2f0d | 8. Confirm correct circuit identification and labelling
checkpoint | 33c244aa-637a-4c9c-a3bd-f3f0a27832bc | 9. Confirm easy access to controls termination
checkpoint | d5c43a96-4cd9-4b7e-b730-d86ffd31a364 | 10. Confirm correct location, access and sufficient support for incoming cables
checkpoint | f6c1526b-8bd8-47df-910e-4c30ff239067 | 11. Confirm correct location, access and sufficient support for outgoing cables
checkpoint | efb34131-9aba-4536-afc2-5a1ba1c41ba4 | 12. Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in a Comment section
checkpoint | c7e0b75b-2b88-486c-8aea-193fa85a6473 | 13. Confirm correct phase identification of busbars and cables inside the board
checkpoint | b6b186e7-a394-432b-b4c3-1c546efb7c33 | 14. Confirm correct size of incoming power cables as per approved cable schedule
checkpoint | 25682894-a13e-4c7e-b5d2-1ed03bbe5ca8 | 15. Confirm correct size of earthing conductors
checkpoint | a63f9ab9-3c0d-4360-a0b2-a829b7bfa713 | 16. Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
signoff | 529e41ad-b85c-4e77-a03f-21cbf978f9af | Checked By (Heyday):
section | 6ce9011f-c18e-49cb-8b51-cbc6ca09e827 | Mechanical Checks
checkpoint | d3d3fa2f-dbd4-48a9-a297-191ccc66a30a | 1. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
checkpoint | cd7f5d77-c10b-4355-bdc9-48df1eeb1747 | 2. Repeat racking of air circuit breaker in and out of chassis for 2 times to verify correct functionality of sliding mechanism
checkpoint | a02c43de-d823-4815-9245-9b73bf7a7185 | 3. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
checkpoint | 293c2a5e-d8a8-44c8-9185-207501f06af8 | 4. Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint | 2afb0689-63c5-4f33-af11-123463e55789 | 5. Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint | e16b21ae-358f-422a-839c-288ffec3b935 | 6. Repeat mounting and dismounting of control fuses 1 time
checkpoint | a8b903c9-d1e9-473c-b6c1-f629e9a99da3 | 7. Repeat mounting and dismounting of control fuses 1 time
checkpoint | 288f2a71-998d-4c75-beb6-0deb9499782e | 8. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 1 Breaker and confirm that Source 2 Breaker is mechanically interlocked
checkpoint | 8c1eaf4e-3fa3-4791-be7e-e1e6ef8c795c | 9. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 2 Breaker and confirm that Source 1 Breaker is mechanically interlocked
checkpoint | 0d8aaa41-c502-4bba-a980-96764f1df1d1 | 10. Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards
signoff | c87d02e9-828c-4db6-9932-1072e3b506bc | Checked By (Heyday):
section | 1f491dfa-7337-4563-bc46-34746bb3c48c | Switch Gear Busbar - Preliminary Checks
checkpoint | c5631ed0-e566-4ae8-a020-7b6d4211b82e | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint | 4eb807d2-5bca-4540-a6de-0dfec00a7205 | 2. Confirm Main Incomers ACBs/MCCBs are Closed
checkpoint | b5b90f91-02f1-494a-91fd-5e26a35e8f42 | 3. Confirm Bus-coupler is Closed (if exist)
checkpoint | ca1b94e1-2e86-4ed2-b45f-3aa6b6454048 | 4. Confirm Outgoing Feeders is Closed
checkpoint | 2cb37458-00bc-44c1-8295-797f0992e483 | 5. Confirm Main Panel Neutral to Earth Link(s) was Removed
checkpoint | 8b6c5b34-5b0a-4375-a758-2d56372f3092 | 6. Confirm Neutral link on Transient Voltage Surge Suppressor is Opened
checkpoint | 297782fc-ca5d-450f-a8d4-348b269dd1bf | 7. Confirm All Long Time rating Plugs From ACB's are Removed (if applicable)
section | 0e3b566a-5543-4de4-95da-6e4ccb73147b | Switch Gear Busbar - Insulation Resistance (1000V)
checkpoint | e79c8a67-e5e7-4a7e-a99b-af1abab22fb3 | 1. Between L1 Phase and Neutral
button | da47e5a7-0c2b-5bec-a1d1-4cb02286f697 | >10MΩ | YES,NO
textbox | db7be619-6a72-502a-a4ad-711cf96f67d4 | Actual Reading if <10MΩ
checkpoint | 71a0f318-66af-4cc8-b487-4df4c9dc029a | 2. Between L2 Phase and Neutral
button | 59432468-bda3-564d-92dc-f4e2bee5c3db | >10MΩ | YES,NO
textbox | aba78d31-3e23-55a6-9766-d251b6434bdb | Actual Reading if <10MΩ
checkpoint | 673eae18-143e-4e9a-8ae1-0a45252a041c | 3. Between L3 Phase and Neutral
button | 0f2b13e8-1769-58bf-8094-2321c28b4b65 | >10MΩ | YES,NO
textbox | e07c2df7-beb2-56f8-871c-1eef6ab7088f | Actual Reading if <10MΩ
checkpoint | ce6fad98-6bb5-4fb7-9f88-ee00befb1116 | 4. Between Neutral and Earth
button | 9fdcde1a-167f-5d39-a0e5-1cb4f6b03e16 | >10MΩ | YES,NO
textbox | 0aae33fc-1f86-56cf-bcaa-7c9683e5ced3 | Actual Reading if <10MΩ
checkpoint | 596b3c56-7ea2-4ff0-8354-eacef1be0c8f | 5. Between L1 Phase and Earth
button | 0e5eadb1-159e-5316-8ed3-ba7569aa068a | >10MΩ | YES,NO
textbox | 3af4c9b7-17ee-509a-a86a-e44dbb922e4f | Actual Reading if <10MΩ
checkpoint | 75ea76a2-5def-436e-9cf8-f0c5b020c21e | 6. Between L2 Phase and Earth
button | ff324f1f-1245-5080-b81b-6adf91084997 | >10MΩ | YES,NO
textbox | 5a4fc6a7-81e0-5134-99ea-ee44034c6aea | Actual Reading if <10MΩ
checkpoint | f37dec3d-c4f3-4751-a50c-2eb1a3b0b25f | 7. Between L3 Phase and Earth
button | 57077747-e456-51dc-95f8-16862262daf8 | >10MΩ | YES,NO
textbox | e07fb00e-674c-51f5-870d-14d2e9b4849f | Actual Reading if <10MΩ
checkpoint | 5cc50f0b-a7f2-4c30-bb36-d5194b192585 | 8. Between L1 Phase and L2 Phase
button | 401458f6-879f-53f3-8d18-10efab680a77 | >10MΩ | YES,NO
textbox | 705676ed-5793-5579-9cde-bc18e438a4ab | Actual Reading if <10MΩ
checkpoint | 349c44dd-d60c-47bb-8322-bf4b839fe071 | 9. Between L1 Phase and L3 Phase
button | 99997557-a1cf-561c-9d88-77517f0475ee | >10MΩ | YES,NO
textbox | c6dabda2-3ff5-580c-98b5-aa61ee7a6bbe | Actual Reading if <10MΩ
checkpoint | cd0086bf-ad8b-4954-92a3-fa574f86657a | 10. Between L2 Phase and L3 Phase
button | a9563b29-b822-560b-894a-19a8b0711f65 | >10MΩ | YES,NO
textbox | 357f59da-ed5f-59e7-b57e-96b1702845dd | Actual Reading if <10MΩ
signoff | 67310bca-10fe-4882-a17f-e4b101ed6794 | Checked By (Heyday):
section | 617ac783-deeb-4d2c-a6fc-cf19e94add7c | Circuit Breaker Settings Check
checkpoint | 19a2969e-dbcc-41c8-a3f0-9159857e3e9b | Circuit Breaker Settings Check
textbox | 835eb5c1-5f2d-5710-aadb-36394bf4654d | Cubicle ID
textbox | 91a2b2b3-4cfa-5af5-9722-386cba31835c | Feeder Name
button | 55199d04-18f2-511c-9854-a369d11a7e1c | Setup as per Discrimiation settings (YES/NO) | YES,NO
signoff | caf1447e-4504-4012-b446-7880ab6823df | Checked By (Heyday):
section | 4a519bd4-1653-4c30-85a8-b02ff8273204 | Current Transformer Checks
checkpoint | 2f8f8b1b-7c5b-4126-93f6-d396977b82ad | Current Transformer Checks
textbox | 30d835de-637a-5822-afca-b2eec318553c | CT ID | YES,NO
button | 8f0d1368-938d-5dac-9eea-61880c8a1aa7 | CT Polarity is Correct | YES,NO
button | bbfc2853-d078-5953-9199-36455cb8f00f | No crossed phase CT connections | YES,NO
button | 3ba6c161-79a1-5a17-b798-3ff025d6af66 | No phase sequence CT connection errors | YES,NO
signoff | cd34c750-45f8-4686-ad16-80ed235bc4fa | Checked By (Heyday):
checklist | 14710401-9c29-4f39-b42b-46d1e98b2241 | Quality - Precast Pit Install |  | Quality - Precast Pit Install
checkpoint | 086a6b84-79c1-498b-8fd5-7a0d0772c2d7 | Receipt of Precast pit delivery to site & storage
checkpoint | b14f26fa-c956-42c1-b0eb-9aff33b5c57e | Pit is built to approved shop drawings (photos attached)
checkpoint | 130f2cdf-1e80-4855-95c0-2cd47b51596c | correct trenching and alignment & depth
checkpoint | 9aded11b-2e7c-4a43-8a19-631766a35474 | installed to correct finish level
checkpoint | c15d1211-1381-4840-9688-999120feaeba | correct back fill installed around pit
signoff | 81f8fe16-d331-4056-87d5-6661de7afbed | Signoff Required from Heyday & Multiplex
checkpoint | cb7ac338-822e-4947-bc3d-0bac0e0bc5a9 | Install correct pit lid
checkpoint | 8de1c1e5-d080-4a8f-9755-8cb1dff3eead | Photo of pit installed attached.
checklist | 98f3e20c-7459-44a1-acf3-d606bbabcc8c | Add Heyday On-site Penetration Register |  | Heyday On-site Penetration Register
checkpoint-no-value | 59c53197-7f17-4c08-bf34-cbdecd6a2185 | Fire Stopping System No.
dropdown | 672e6ca0-d27f-5ade-be47-cadc764e3fd6 | Select System No. | FAS190329 - Conduits within concrete,27912900 - Conduit through FRL
checkpoint-no-value | e82129a9-505d-4e71-b755-ee0177a1c10c | Penetration Type
dropdown | cc41d543-a0b2-5338-bccb-350edabe3c42 | Select Type | Floor,Wall,Ceiling
checkpoint-no-value | 131473b5-4685-4902-9704-23cc5b0c0dad | Location
textbox | faf0f92a-b611-5142-9cc5-1997de933838 | Location:
checkpoint-no-value | 0c4e0a22-6611-460c-a28a-e063b47bc23b | FRL
dropdown | ff51926a-ed3a-538f-be24-62136736cc0a | Select FRL | ~ / 120 / 120
checkpoint-no-value | 9f625aa4-64a1-4726-aa04-9e338bb01d63 | Service Description
dropdown | 964bec46-4098-5d46-8d97-65a3ffddbac9 | Select Description | Conduits within concrete,Concrete through FR compartment
checkpoint | 3ce1e2b8-4527-4c0f-8dfd-51303366e887 | Photo of Fire Sealing & Label
checklist | cae18be9-29d2-43c5-a730-ba3a912fa0c5 | Testing & Commissioning - Earthing Systems - Construction Tests (Main Earth System) |  | Earthing Systems - Construction Tests (Main Earth System)
checkpoint | d269a52a-29a7-45f0-ade5-97796ceae758 | RWV Industries – Earthing Test Report. Steel Reinforcement Continuity
checkpoint | aa286d59-6b01-4cdd-895a-a4bae9404a65 | RWV Industries – Earthing Test Report. Footing Earthing
checklist | 075cbb8f-7395-4215-990a-36ee8f123766 | Testing & Commissioning - Distribution Boards (Energised) |  | Distribution Boards (Energised)
section | ac8d2b3a-1062-4805-9ee2-f6ed983b5857 | Phase Voltage Reading
checkpoint | a53ff1c6-2797-40a2-a2f8-f7d38489ecdc | Red - White
textbox | 41085b71-2ea6-5b63-a473-f908e40c84db | Voltage (V)
checkpoint | 16a098d4-cc95-4d40-b7f2-5a6f971a8dae | Red - Blue
textbox | 196e18ef-44d6-5e0c-a2a1-3e123df518ec | Voltage (V)
checkpoint | 5f5f3b6a-f863-41d2-b2f2-ae73ae753490 | White - Blue
textbox | dd4fb89a-49d2-5cb5-81f7-9353800034b4 | Voltage (V)
checkpoint | 2c7982e1-caca-49f5-b608-0d810e12fc87 | Red - Neutral
textbox | 84ea402e-0a70-5ef7-875a-b3d7242e3e72 | Voltage (V)
checkpoint | 23082f5e-1a0c-4b41-87eb-0d83fd061e60 | White - Neutral
textbox | 3559dc80-e4b9-529a-b961-94b338fdf2a5 | Voltage (V)
checkpoint | d20cf236-03c4-48ec-bb3d-a76d4c0a7931 | Blue - Neutral
textbox | b5c0d298-c429-55a3-b066-19c0ef1adec4 | Voltage (V)
checkpoint | 828bffa7-26e3-4c1a-9bae-5901fdb6fa71 | Red - Earth
textbox | 5e97d0e2-e2ab-5fd5-b47a-2336dfd51118 | Voltage (V)
checkpoint | 1258b1f5-490b-4bed-a1f2-aa12c5f28b2c | White - Earth
textbox | ac623e8d-cf6b-505d-bb88-361d6a1997e1 | Voltage (V)
checkpoint | 5b1ac89f-0558-43f0-863a-940529d8515e | Blue - Earth
textbox | 3970221d-9189-52b1-8a60-1654c34deea7 | Voltage (V)
section | 2817d947-17af-4959-86d2-ad261376d5c6 | Phase Rotation
checkpoint | b88f8ba0-5ca0-416a-833c-5540c7146713 | Direction
button | ae1d7739-bc6e-5e73-89bd-a6284a3ee7fb | Direction | Clockwise,Anti-Clockwise
signoff | 60203d98-7d92-49d7-941d-68aecd92f89d | Checked By (Heyday):
checklist | 3e42762d-bf31-4d36-829b-e5be308b1a59 | Testing & Commissioning - Main Switchboards (Energised) |  | Main Switchboards (Energised)
section | f9aa158d-c33c-45ef-8941-ff151efe3e40 | Phase Voltage Reading
checkpoint | f96731dc-15c4-4ade-b71a-c95e9777c215 | Red - White
textbox | f4a3c1c8-4e6c-58fe-92a1-38c60f07d84d | Voltage (V)
checkpoint | 46972991-0c7b-473b-9eaf-8a516c8c437a | Red - Blue
textbox | 9012a56a-eb3f-549c-a99e-4ab59a18706f | Voltage (V)
checkpoint | eb36847c-ed6d-4567-9d58-f3b164fd3df1 | White - Blue
textbox | 7730bb55-8399-5410-a6d8-9e321f2c3b55 | Voltage (V)
checkpoint | a1f0e0e5-888d-439a-b021-188f1611623e | Red - Neutral
textbox | 1b9de252-2bcb-50f7-a8a4-21296a1917d1 | Voltage (V)
checkpoint | 5982f28f-419b-436a-a8c8-e8c3a795f156 | White - Neutral
textbox | fd5ad721-6b4d-581b-98cd-16572b17c288 | Voltage (V)
checkpoint | c968da2a-b6d4-4aef-b161-053f68e23df1 | Blue - Neutral
textbox | 5e1fa804-47a1-5108-b5c5-98b30ca5c998 | Voltage (V)
checkpoint | 3be6019e-bce6-494d-9680-40f2b59f2946 | Red - Earth
textbox | 27a4ef16-3301-50ce-998e-8dc1a2448f00 | Voltage (V)
checkpoint | 264f3f81-f0b1-451c-98da-05ef1aedaaff | White - Earth
textbox | 1dee7dae-4540-58c6-980a-81266bf5e66f | Voltage (V)
checkpoint | eb645a35-eaac-4c73-a941-28e7662351d0 | Blue - Earth
textbox | fef4a341-e45a-5d94-b3d8-5d6cc06e2ce8 | Voltage (V)
section | 03d24af3-4139-436a-b530-ee2eb31b26b6 | Phase Rotation
checkpoint-no-value | 0983e440-0629-44a5-acde-f06ac1b4807b | Direction
button | 53223924-832f-5e8b-9414-bec236d33ab5 | Direction: | Clockwise,Anti-Clockwise
signoff | 06501d42-3386-43fb-b9da-0d8237b6d947 | Checked By (Heyday):
checklist | 62d202b1-8c66-4e1e-8901-ccb27238b552 | Testing & Commissioning - PFC |  | PFC
checkpoint | 1944b174-f008-4363-8bdf-1c008fa2b047 | WSA20-MPX-04000-EL-ITC-31102000 - Construction Tests (Pre-energisation)
checkpoint | f68e9d2d-b76e-4654-afa5-0ea82486de02 | WSA20-MPX-04000-EL-ITC-31073000 - Component Test (Energised)
checkpoint | 9b9b1768-ae07-4672-ae74-d1727c05c53a | CT Ratio Verification (V,A,kVA) L1/L2/L3 - Component Test (Energised)
checkpoint | c057c646-daba-4f37-a524-666f830967de | Power Factor Correction Controller Configuration as per manufacturers recommendations - Component Test (Energised)
signoff | 7b4885d9-2b6b-4d72-93c7-cb464dd5b560 | Checked By (Heyday):
checklist | a51aecd7-4888-4ee4-90eb-9c6e39fa4e6f | Quality Mains and Sub Mains |  | Quality Mains and Sub Mains
checkpoint | 481c366a-fe5f-4bf9-b08e-3fe618e39573 | Receipt of cable containment delivery to site & storage. (ITP Reference Item 1)
checkpoint | c1f2e221-dde5-4dad-9b44-c6afb6999b40 | Cable storage & handling. (ITP Reference Item 2)
checkpoint | a952b6d5-c1b0-4efa-bc98-18fecdf45664 | Correct cable size & type. (ITP Reference Item 3)
signoff | 2e077f6e-060a-4e49-a276-969004145f0b | Signoff Required from Heyday & Multiplex
checkpoint | dd8f2a5e-5bac-4622-9945-985f7020ddc9 | Cable pulling tension to not exceed manufacturer's recommendations. (ITP Reference Item 4)
checkpoint | 7199c90a-99f7-4c2e-ad30-b8eb856528f1 | Cable lubrication if required. (ITP Reference Item 5)
checkpoint | cc57e662-d195-4557-b8fc-88991a964bdd | Installed to latest drawings – schematics/single line diagram & cable containment drawings. (ITP Reference Item 6)
checkpoint | 3700b49e-c745-4dde-9bf2-634c32593cff | Correct cable tag installed. (ITP Reference Item 7)
checkpoint | 89bedb52-fb10-432d-9c5e-92594ea32e40 | Photo evidence captured for cable containment install. (ITP Reference Item 8)
signoff | 2007734c-08ee-4ea7-bd50-d84c77daae1f | Signoff Required from Heyday & Multiplex
checklist | ba235e82-281b-4be6-86a7-99b15884cf5b | Quality - Main switchboard Install |  | Quality - Main switchboard Install
checkpoint | 4e2cdcce-3851-423a-a541-3b034abfec6f | Receipt of switchboard delivery to site
checkpoint | af37baef-ea2c-4d09-9044-e0784b0f5248 | set out to be confirmed with latest Switchboards Shop drawings
checkpoint | 716a9f94-20d4-4671-948f-dc7edc48366e | Correct alignment to set out drawings
signoff | b2e7b34e-3d88-4de2-b56b-a13cac0dbf56 | Signoff Required from Heyday & Multiplex
checkpoint | 4592a97d-1ffe-468f-9314-db6d31bb43bc | Correct bracket and safe fixing
checkpoint | e1732cfa-bc3c-438f-99ff-b6c05049e4c7 | Photos of boards attached