## Sheet1
Homi Train Station - Inspection and Test Plan
Project Area |  | Homai Train Station |  |  |  | Rev | 4 |  | Inspection and Test Codes:
Activity Title |  | Electrical Ducting Installation |  |  |  | Date | 2025-01-30 |  | [R] Review | Review of reports, records or other evidence of compliance.
Location | [5 empty] | Lot No. |  |  | [I] Inspection | In process check, work proceeds. Record the check if required.
Ref # |  | DN1212-ITP-006 | [6 empty] | [W] Witness | Inspection to be witnessed on site and recorded. Record to be filed.
DNZ Project Manager: |  | Dan Trotman | [6 empty] | [H] Hold | No work to proceed past Hold Point until this is completed, recorded and released
AT Project Manager: |  | Werner Nel
DNZ Project Engineer: |  | Grant Wallace
Drawings/Reference Documents: |  | Drawing Key Notes & Luminaire Schedule: 3235599-SP03-BE-1000 Electrical Schematics: 3235599-SP03-BE-1001 Electrical Scope of Works: 3235599-SP03-BE-1002 Lighting Layout Sheet 1: 3235599-SP03-BE-1011 Lighting Layout Sheet 2: 3235599-SP03-BE-1012 Lighting Layout Sheet 3: 3235599-SP03-BE-1013
Specifications: |  | 746-24-874-AC 746-22-052-PS Auckland Transport Design Manual (TDM) - Street Lighting Appendix L-Electrical Cable Specification AS/NZS 3000 Wiring Rules AS/NZS 2053 Conduits and Fittings for Electrical Installations AS/NZS 2648 Underground Marking Tape NZTA M/4 Basecourse Aggregates AS4702-2000 Polymeric Cable Protection Covers
ITP Item # | Construction Activity or Material Element |  | Standard, Drawing or Specification Reference | Construction Activity Description, Test Type and Acceptance Criteria |  | Test Frequency |  | QA Record | Verification Method and On Site Responsibilities |  |  | DNZ Rep Sign and Date
[9 empty] | DNZ Engineer | Engineer's Rep | Designer Rep
1 | PRELIMINARY AND GENERAL
1.1 | IFC Drawings and Specification |  | ACC | A minimum of two weeks prior to construction: document review. DWG’s are for construction or as per instruction Works done in accordance with Project specification |  | Once |  | N/A | R |  | H | Sign | Date
1.2 | Method Statement & JSEA Development |  | The Downer Standards (TDS) | Prior to construction: document review. |  | Once |  | Method Statement & JSEA Completed & signed by relevant authority | H | R | R | Sign | Date
1.3 | Permit to Dig |  | DN-ZH-ST043 Ground Disturbance | Prior to construction. Permit in work package |  | Permit issued each week |  | Permit number ....................... | H |  |  | Sign | Date
1.4 | Survey Model |  | N/A | Model Review. |  | Once |  | Visual Inspection & measurement Survey Check set out as per design | H |  |  | Sign | Date
1.5 | Corridor Access Requests (CAR) |  | N/A | Corridor Access Requests (CARs) is required before any work is carried out on public roads. |  | Once |  | Approved CAR | H |  |  | Sign | Date
1.6 | Temporary Traffic Management Plan (TTMP) |  | COPTTM | Prior to works commencing: Review Approved TTMP. Required before any work is carried out on public roads. |  | Once |  | Approved TTMP | H |  |  | Sign | Date
2 | MATERIAL APPROVALS
2.1 | Electrical Ducts: 100mm or 50mm nominal bore Orange Skin PVC Duct |  | AS/NZS 3000 | Telecom Standard SN9 rating. All bends to be swept bends. |  | Once |  | Delivery Dockets | I |  | R | Sign | Date
2.2 | GAP 7 or Sand |  | AS/NZS 3000 Figure 3.14 Page 201 | Gap7 or Sand to be used for bedding. Maximum particle size 7mm. |  | Once |  | Delivery Dockets | R |  | R | Sign | Date
2.3 | Electrical Warning Tape |  | AS/NZS 2648.1 AS/NZS 3000-Section 3.11.4.5 Page 198 | 150mm Wide Plastic Orange warning tape with black lettering stating: "WARNING ELECTRICAL CABLE BELOW". Complying with AS/NZS 2648.1. |  | Once |  | Delivery Dockets | I |  | R | Sign | Date
2.4 | Epoxy Mortar |  | MDS | Hybond Two Part Epoxy Mortar or similar approved product. |  | Once |  | MDS | R |  | R | Sign | Date
2.5 | PVC Solvent Cement |  | MDS | Marley clear solvent cement or similar approved product. |  | Once |  | MDS | I |  | R | Sign | Date
2.6 | GAP65 |  | TNZ M/4: 2006 - 3 NZS 4407 : 1991 NZS 4402 : 1986 | The basecourse aggregate shall be sampled and tested by an IANZ accredited laboratory for crushing resistance, wethering quality Index and California bearing ratio ( Class 3 & 4). |  | Once Per Year Or Every 10 000 m³ |  | Test Report | R |  | R | Sign | Date
2.7 | Mechanical Protection (Mag Slab) |  | AS/NZS 3000 Figure 3.14 Page 201 AS4702-2000 AS/NZS 2648 | Polymeric cable protection cover 150mm Wide Mag Slab or similar approved product. |  | If required |  | Delivery Docket | I |  | R | Sign | Date
2.8 | Blue Building Strap (Draw-Wire) |  | AS/NZS 3000 | 19mm x 300mm or 25mm x 250m Blue Polythene Strapping. |  | Once |  | Delivery Dockets | I
CONSTRUCTION ACTIVITIES
3.1 | Use of Existing Ducting |  | 3235599-SP03-BE-1011 3235599-SP03-BE-1012 3235599-SP03-BE-1013 Note 3 & 4 | Confirm space for new wirring within existing ducting route prior to the installation. If there is no space available, DNZ to size and run a new duct from MSB-E to Existing Electrical Pit. |  | Where required |  | As-Built | I
3.2 | Survey Set-Out |  | IFC Drawings | Before works commencement. Set out by Surveyor. Alignment as per IFC drawings. |  | Once |  | As-Built | H
3.3 | Trench Excavation to Depth |  | 3235599-SP03-BE-1011 3235599-SP03-BE-1012 3235599-SP03-BE-1013 AS/NZS 3000 Figure 3.14 Page 201 Auckland Transport Design Manual (TDM) - Street Lighting Appendix L-Electrical Cable Specification Section 6.2 | Ensure excavation depth achieves the minimum cover of 600mm from ground level to top of installed duct. |  | Once |  | Checklist Photos | I |  |  | Sign | Date
3.4 | Place Bedding |  | AS/NZS 3000 Figure 3.14 Page 201 | Ensure bedding thickness is a minimum of 50mm of GAP7 or Sand. |  | Once |  | Checklist Photos | I |  | R | Sign | Date
3.5 | Lay Ducting |  | 3235599-SP03-BE-1011 3235599-SP03-BE-1012 3235599-SP03-BE-1013 | Minimum cover 600mm from ground level to top of installed duct. Lay ducting and back fill with GAP7 or Sand ensuring to have a minimum of 50mm on top of duct. Ensure 50mm separation between electrical ducts running parallel. Ducts to extend 50mm inside the pit. |  | Once |  | Checklist Photos | R |  | H | Sign | Date
3.6 | Draw-wire Installation |  | N/A | Draw-wire to be installed with 2.0m of slack on both ends of duct. |  | Each Duct |  | Checklist Photos | I |  | H | Sign | Date
3.7 | Mag Slab Installation |  | AS/NZS 3000 Figure 3.14 Page 201 Auckland Transport Design Manual (TDM) - Street Lighting Appendix L-Electrical Cable Specification Section 6.4 | If required mag slab to be placed 75mm approximatly from top of ducts. |  | Each Trench |  | Checklist Photos | I |  | H | Sign | Date
3.8 | Marker Tape Installation |  | AS/NZS 3000 Figure 3.14 Page 201 Auckland Transport Design Manual (TDM) - Street Lighting Appendix L-Electrical Cable Specification Section 6.5 | Plastic warning tape to be placed 250mm below ground level prior to GAP65 backfill. |  | Each Trench |  | Checklist Photos | I |  | H | Sign | Date
3.9 | Backfill in Layers |  | Auckland Transport Design Manual (TDM) - Street Lighting Appendix L-Electrical Cable Specification Section 6.3 | Ensure trench is backfilled with GAP65. Backfill in 100mm layers, hand ramming the first two layers followed by power compaction. Clegg test each backfill layer to achieve CIV: 12 |  | Each Layer |  | Photos Clegg Results Checklist | I |  | R | Sign | Date
3.1 | End caps or electrical tape |  | N/A | Ensure all ends to have capping or tape cover. |  | Where required |  | Photos | I |  |  | Sign | Date
4 | FINAL RECORDS
4.1 | Construction Record Compilation |  | N/A | Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted. |  | Once |  | QA Records | H |  | R | Sign | Date
4.2 | Survey Records |  | N/A | Ensure all items have been surveyed. |  | Once |  | Survey Data | H |  | R | Sign | Date
4.3 | Redline Drawings |  | IFC Drawings | Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen. |  | Once |  | IFC Mark-Up | H |  | R
4.4 | As-Built |  | Contract Specifications - General Section 2 Page 21 | Complete final as-built 2D drawings to be handed over with the CAD files. |  | Once |  | As-Builts | H |  | R
4.5 | Non-conformances |  | DN1212-DOW-PLA-PM-0005 QMP | Non-conformances reports to be raised when specification not met. All non-conformances within the area under review need to be listed on the NCR report. NCR Reference ….................. |  | When Required |  | NCR Forms on InEight | H |  | R | Sign | Date
Comments:
ITP APPROVAL PROCESS
Prepared By: Site Engineer |  |  | Moses Kaufanga |  | Signed: |  | Date:
Reviewed By: Quality Mgr./Eng. |  |  | Nas Matar |  | Signed: |  | Date:
Reviewed By: Project Manager |  |  | Dan Trotman |  | Signed: |  | Date:
Reviewed By: Design Engineer |  |  | Daniel Cvitanich |  | Signed: |  | Date:
Reviewed By: AT Project Manager |  |  | Werner Nel |  | Signed: |  | Date:
Reviewed By: AT Engineer to Contract |  |  | Mike Robertson |  | Signed: |  | Date:
FINAL ITP CLOSE-OUT
Downer Project/Site Engineer |  |  |  |  | Signed: |  | Date:
QA Mgr./Engineer |  |  |  |  | Signed: |  | Date:
Designers Rep(Assistant) |  |  |  |  | Signed: |  | Date:
Note on A52: Kelsey Wong: ITP Revision to be signed and approved the Project Lead prior to construction. Final version issued to Quality Engineer / Engineer's Rep for Comment and Acceptance of ITP.