## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1212-ITP-006 Ducting | itp |  |  |  |  | DN1212-ITP-006 Ducting Rev4
section | 1 - PRELIMINARY AND GENERAL
checkpoint | 1.1 - IFC Drawings and Specification
label | Standard, Drawing or Specification Reference - ACC
label | Construction Activity Description, Test Type and Acceptance Criteria - A minimum of two weeks prior to construction: document review. DWG’s are for construction or as per instruction
label | ○ Works done in accordance with Project specification
label | Test Frequency - Once
label | QA Record - N/A
label | DNZ Engineer - R
label | Designer Rep - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.2 - Method Statement & JSEA Development
label | Standard, Drawing or Specification Reference - The Downer Standards (TDS)
label | Construction Activity Description, Test Type and Acceptance Criteria - Prior to construction: document review.
label | Test Frequency - Once
label | QA Record - Method Statement & JSEA Completed & signed by relevant authority
label | DNZ Engineer - H
label | Engineer's Rep - R
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.3 - Permit to Dig
label | Standard, Drawing or Specification Reference - DN-ZH-ST043 Ground Disturbance
label | Construction Activity Description, Test Type and Acceptance Criteria - Prior to construction. Permit in work package
label | Test Frequency - Permit issued each week
textbox | QA Record - Permit number
label | DNZ Engineer - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.4 - Survey Model
label | Standard, Drawing or Specification Reference - N/A
label | Construction Activity Description, Test Type and Acceptance Criteria - Model Review.
label | Test Frequency - Once
label | QA Record - Visual Inspection & measurement Survey Check set out as per design
label | DNZ Engineer - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.5 - Corridor Access Requests (CAR)
label | Standard, Drawing or Specification Reference - N/A
label | Construction Activity Description, Test Type and Acceptance Criteria - Corridor Access Requests (CARs) is required before any work is carried out on public roads.
label | Test Frequency - Once
label | QA Record - Approved CAR
label | DNZ Engineer - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.6 - Temporary Traffic Management Plan (TTMP)
label | Standard, Drawing or Specification Reference - COPTTM
label | Construction Activity Description, Test Type and Acceptance Criteria - Prior to works commencing: Review Approved TTMP.
label | ○ Required before any work is carried out on public roads.
label | Test Frequency - Once
label | QA Record - Approved TTMP
label | DNZ Engineer - H
holdpoint | AUTHORITY HOLDPOINT
section | 2 - MATERIAL APPROVALS
checkpoint | 2.1 - Electrical Ducts: 100mm or 50mm nominal bore Orange Skin PVC Duct
label | Standard, Drawing or Specification Reference - AS/NZS 3000
label | Construction Activity Description, Test Type and Acceptance Criteria - Telecom Standard SN9 rating.
label | ○ All bends to be swept bends.
label | Test Frequency - Once
label | QA Record - Delivery Dockets
label | DNZ Engineer - I
label | Designer Rep - R
checkpoint | 2.2 - GAP 7 or Sand
label | Standard, Drawing or Specification Reference - AS/NZS 3000 Figure 3.14 Page 201
label | Construction Activity Description, Test Type and Acceptance Criteria - Gap7 or Sand to be used for bedding.
label | ○ Maximum particle size 7mm.
label | Test Frequency - Once
label | QA Record - Delivery Dockets
label | DNZ Engineer - R
label | Designer Rep - R
checkpoint | 2.3 - Electrical Warning Tape
label | Standard, Drawing or Specification Reference - AS/NZS 2648.1, AS/NZS 3000-Section 3.11.4.5 Page 198
label | Construction Activity Description, Test Type and Acceptance Criteria - 150mm Wide Plastic Orange warning tape with black lettering stating: "WARNING ELECTRICAL CABLE BELOW".
label | ○ Complying with AS/NZS 2648.1.
label | Test Frequency - Once
label | QA Record - Delivery Dockets
label | DNZ Engineer - I
label | Designer Rep - R
checkpoint | 2.4 - Epoxy Mortar
label | Standard, Drawing or Specification Reference - MDS
label | Construction Activity Description, Test Type and Acceptance Criteria - Hybond Two Part Epoxy Mortar or similar approved product.
label | Test Frequency - Once
label | QA Record - MDS
label | DNZ Engineer - R
label | Designer Rep - R
checkpoint | 2.5 - PVC Solvent Cement
label | Standard, Drawing or Specification Reference - MDS
label | Construction Activity Description, Test Type and Acceptance Criteria - Marley clear solvent cement or similar approved product.
label | Test Frequency - Once
label | QA Record - MDS
label | DNZ Engineer - I
label | Designer Rep - R
checkpoint | 2.6 - GAP65
label | Standard, Drawing or Specification Reference - TNZ M/4: 2006 - 3, NZS 4407 : 1991, NZS 4402 : 1986
label | Construction Activity Description, Test Type and Acceptance Criteria - The basecourse aggregate shall be sampled and tested by an IANZ accredited laboratory for crushing resistance, wethering quality Index and California bearing ratio ( Class 3 & 4).
label | Test Frequency - Once Per Year
label | Or
label | ○ Every 10 000 m³
label | QA Record - Test Report
label | DNZ Engineer - R
label | Designer Rep - R
checkpoint | 2.7 - Mechanical Protection (Mag Slab)
label | Standard, Drawing or Specification Reference - AS/NZS 3000 Figure 3.14 Page 201, AS4702-2000, AS/NZS 2648
label | Construction Activity Description, Test Type and Acceptance Criteria - Polymeric cable protection cover 150mm Wide Mag Slab or similar approved product.
label | Test Frequency - If required
label | QA Record - Delivery Docket
label | DNZ Engineer - I
label | Designer Rep - R
checkpoint | 2.8 - Blue Building Strap (Draw-Wire)
label | Standard, Drawing or Specification Reference - AS/NZS 3000
label | Construction Activity Description, Test Type and Acceptance Criteria - 19mm x 300mm or 25mm x 250m Blue Polythene Strapping.
label | Test Frequency - Once
label | QA Record - Delivery Dockets
label | DNZ Engineer - I
section | 3 - CONSTRUCTION ACTIVITIES
checkpoint | 3.1 - Use of Existing Ducting
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1011, 3235599-SP03-BE-1012, 3235599-SP03-BE-1013 Note 3 & 4
label | Construction Activity Description, Test Type and Acceptance Criteria - Confirm space for new wirring within existing ducting route prior to the installation. If there is no space available, DNZ to size and run a new duct from MSB-E to Existing Electrical Pit.
label | Test Frequency - Where required
label | QA Record - As-Built
label | DNZ Engineer - I
checkpoint | 3.2 - Survey Set-Out
label | Standard, Drawing or Specification Reference - IFC Drawings
label | Construction Activity Description, Test Type and Acceptance Criteria - Before works commencement.
label | ○ Set out by Surveyor.
label | ○ Alignment as per IFC drawings.
label | Test Frequency - Once
label | QA Record - As-Built
label | DNZ Engineer - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Trench Excavation to Depth
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1011, 3235599-SP03-BE-1012, 3235599-SP03-BE-1013, AS/NZS 3000 Figure 3.14 Page 201
label | ○ Auckland Transport Design Manual (TDM) - Street Lighting Appendix L-Electrical Cable Specification Section 6.2
label | Construction Activity Description, Test Type and Acceptance Criteria - Ensure excavation depth achieves the minimum cover of 600mm from ground level to top of installed duct.
label | Test Frequency - Once
label | QA Record - Checklist, Photos
label | DNZ Engineer - I
checkpoint | 3.4 - Place Bedding
label | Standard, Drawing or Specification Reference - AS/NZS 3000 Figure 3.14 Page 201
label | Construction Activity Description, Test Type and Acceptance Criteria - Ensure bedding thickness is a minimum of 50mm of GAP7 or Sand.
label | Test Frequency - Once
label | QA Record - Checklist, Photos
label | DNZ Engineer - I
label | Designer Rep - R
checkpoint | 3.5 - Lay Ducting
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1011, 3235599-SP03-BE-1012, 3235599-SP03-BE-1013
label | Construction Activity Description, Test Type and Acceptance Criteria - Minimum cover 600mm from ground level to top of installed duct.
label | ○ Lay ducting and back fill with GAP7 or Sand ensuring to have a minimum of 50mm on top of duct.
label | ○ Ensure 50mm separation between electrical ducts running parallel.
label | ○ Ducts to extend 50mm inside the pit.
label | Test Frequency - Once
label | QA Record - Checklist, Photos
label | DNZ Engineer - R
label | Designer Rep - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.6 - Draw-wire Installation
label | Standard, Drawing or Specification Reference - N/A
label | Construction Activity Description, Test Type and Acceptance Criteria - Draw-wire to be installed with 2.0m of slack on both ends of duct.
label | Test Frequency - Each Duct
label | QA Record - Checklist, Photos
label | DNZ Engineer - I
label | Designer Rep - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.7 - Mag Slab Installation
label | Standard, Drawing or Specification Reference - AS/NZS 3000 Figure 3.14 Page 201
label | ○ Auckland Transport Design Manual (TDM) - Street Lighting Appendix L-Electrical Cable Specification Section 6.4
label | Construction Activity Description, Test Type and Acceptance Criteria - If required mag slab to be placed 75mm approximatly from top of ducts.
label | Test Frequency - Each Trench
label | QA Record - Checklist, Photos
label | DNZ Engineer - I
label | Designer Rep - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.8 - Marker Tape Installation
label | Standard, Drawing or Specification Reference - AS/NZS 3000 Figure 3.14 Page 201
label | ○ Auckland Transport Design Manual (TDM) - Street Lighting Appendix L-Electrical Cable Specification Section 6.5
label | Construction Activity Description, Test Type and Acceptance Criteria - Plastic warning tape to be placed 250mm below ground level prior to GAP65 backfill.
label | Test Frequency - Each Trench
label | QA Record - Checklist, Photos
label | DNZ Engineer - I
label | Designer Rep - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.9 - Backfill in Layers
label | Standard, Drawing or Specification Reference - Auckland Transport Design Manual (TDM) - Street Lighting Appendix L-Electrical Cable Specification Section 6.3
label | Construction Activity Description, Test Type and Acceptance Criteria - Ensure trench is backfilled with GAP65.
label | ○ Backfill in 100mm layers, hand ramming the first two layers followed by power compaction.
label | ○ Clegg test each backfill layer to achieve CIV: 12
label | Test Frequency - Each Layer
label | QA Record - Photos, Clegg Results, Checklist
label | DNZ Engineer - I
label | Designer Rep - R
checkpoint | 3.10 - End caps or electrical tape
label | Standard, Drawing or Specification Reference - N/A
label | Construction Activity Description, Test Type and Acceptance Criteria - Ensure all ends to have capping or tape cover.
label | Test Frequency - Where required
label | QA Record - Photos
label | DNZ Engineer - I
section | 4 - FINAL RECORDS
checkpoint | 4.1 - Construction Record Compilation
label | Standard, Drawing or Specification Reference - N/A
label | Construction Activity Description, Test Type and Acceptance Criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
label | Test Frequency - Once
label | QA Record - QA Records
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Survey Records
label | Standard, Drawing or Specification Reference - N/A
label | Construction Activity Description, Test Type and Acceptance Criteria - Ensure all items have been surveyed.
label | Test Frequency - Once
label | QA Record - Survey Data
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3 - Redline Drawings
label | Standard, Drawing or Specification Reference - IFC Drawings
label | Construction Activity Description, Test Type and Acceptance Criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen.
label | Test Frequency - Once
label | QA Record - IFC Mark-Up
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4 - As-Built
label | Standard, Drawing or Specification Reference - Contract Specifications - General Section 2 Page 21
label | Construction Activity Description, Test Type and Acceptance Criteria - Complete final as-built 2D drawings to be handed over with the CAD files.
label | Test Frequency - Once
label | QA Record - As-Builts
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.5 - Non-conformances
label | Standard, Drawing or Specification Reference - DN1212-DOW-PLA-PM-0005 QMP
label | Construction Activity Description, Test Type and Acceptance Criteria - Non-conformances reports to be raised when specification not met. All non-conformances within the area under review need to be listed on the NCR report.
textbox | NCR Reference
label | Test Frequency - When Required
label | QA Record - NCR Forms on InEight
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
section | ITP APPROVAL PROCESS
checkpoint-no-status | ITP APPROVAL PROCESS
label | Prepared By: Site Engineer - Moses Kaufanga
label | Reviewed By: Quality Mgr./Eng. - Nas Matar
label | Reviewed By: Project Manager - Dan Trotman
label | Reviewed By: Design Engineer - Daniel Cvitanich
label | Reviewed By: AT Project Manager - Werner Nel
label | Reviewed By: AT Engineer to Contract - Mike Robertson
date | Date:
section | FINAL ITP CLOSE-OUT
checkpoint | FINAL ITP CLOSE-OUT
textbox | Downer Project/Site Engineer:
textbox | QA Mgr./Engineer:
textbox | Designers Rep(Assistant):
date | Date:
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature