## Table 1
[7 empty] | Inspection and Test Plan - Control and Supervision of the Works | [14 empty] | Doc ID: FH-ZU2-QU-ITP034 REV: 0
Client: Melbourne Airport | [7 empty] | Contract No: CP14038-01 | [10 empty] | Prepared By: Jihad Barbar
Project: Taxiway Zulu | [14 empty] | Reviewed By: Jamal Khodr | [6 empty] | Date: 06/01/2025
Construction Process: ALER 3 Electrical | [14 empty] | Approved By: Marco Poggenberg | [6 empty] | Date: 06/01/2025
Specifications: ZULU-BECA-001-SPC-00005, Drawings
Structure / Component: Electrical Switchboards, DBs, LV Cabling, Containment, Lighting, Lighting Control, Emergency Lighting, Access Control Systems and CCTV Installation.
Lot No: |  |  |  |  | Lot Details: | [7 empty] | Lot size/Quantity: |  |  |  |  | Date:
Item No. |  |  | Task/Activity Description | Inspection/Test | [14 empty] | HP/ WP/ AP/ IP/ TP SCP | Responsibility | Checked by:
|  |  |  | Frequency |  | Acceptance Criteria |  |  | Reference Documents |  |  |  |  | Inspection/ Test Method |  | Record of conformity |  |  |  | Project Engineer / Site Engineer | Principal’s Rep. |  | FH | Date
1 |  |  | Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
1.1 |  |  | Check for correct documentation | Prior to commencing activity |  | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings. - all drawings are the latest revision. |  |  | Drawings / Aconex Register |  |  |  |  | Verify |  | Drawings and drawing registers |  |  | HP* | Project Engineer / Site Engineer
1.2 |  |  | Implementation of all measures and controls | Prior to commencing activity |  | All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP. |  |  | PSP, EMP, TMP, JSEA, SWMS, WP |  |  |  |  | Visual Inspection |  | This ITP signed |  |  | HP* | Project Engineer / Site Engineer
1.3 |  |  | Survey Checks | Prior to commencing activity |  | Survey set out to be completed for all assets |  |  | Drawings |  |  |  |  | Verify |  | This ITP signed |  |  | HP* | Project Engineer / Site Engineer
1.4 |  |  | Submission & approval of shop drawings | Prior to commencing activity |  | HOLD POINT Submit shop drawings to the principal’s representative for approval prior to fabrication commencement. Items to include but not limited to: MSB, DB-A, DB-C, DB-L&P, DB-EX1, DB-EX2, MSSB, DB-MGC, DB-GCP, DB-LBC, Luminaires, Light Control Systems, Lightning Protection and Earthing |  |  | ZULU-BECA- 001-SPC-00005 C2100 Page 8, Drawings 030- 3100 set, Approved Shop drawings |  |  |  |  | Verify |  | Aconex Reference |  |  | HP | Project Engineer / Site Engineer /Principal’s Representative
1.5 |  |  | Material Submissions | Prior to commencing activity |  | HOLD POINT Items to include but not limited to: - Cables, control panels, luminaires, lighting control, switches, isolators, contactors, circuit breakers, earthing system, cable trays, ladders, etc. (all containment) |  |  | ZULU-BECA- 001-SPC-00005 AS/NZS 3000 Drawings 030- 3100 set, |  |  |  |  | Verify |  | Aconex Reference |  |  | HP | Project Engineer / Site Engineer /Principal’s Representative
1.6 |  |  | Temporary Works (if applicable) | Prior to commencing activity |  | Submission and approval of the following documentation based on the Temporary Works Design Process Matrix. |  |  | ZULU-BECA- 001-SPC-00005 Temporary Works Design Process Matrix Drawings 030- 3100 set, |  |  |  |  | Verify |  | As defined by the Temporary Works Design Process Matrix (where applicable) |  |  | HP* | Project Engineer / Site Engineer
1.7 |  |  | Off-site Inspections | Each Lot |  | WITNESS POINT Inspection and attendance on site for Factory Acceptance Testing for: - Switchboards - Distribution Boards Following these inspections FAT testing shall be submitted. |  |  | ZULU-BECA- 001-SPC-00005 C2121.20, AS/NZS 3000, Drawings 030- 3100 set |  |  |  |  | Verify |  | This ITP Signed Factory Acceptance Tests |  |  | WP TP | Project Engineer / Site Engineer /Principal’s Representative
1.8 |  |  | Certificates of Compliance (prior to delivery to onsite) | Each Lot |  | Provide Suppliers Certificate of Compliance and Spatial Certificate of Compliance for  Switchboards  Distribution Boards  Control Systems  Power Control  Switchgear  Cables |  |  | ZULU-BECA-001-SPC-00005 C2100.3, AS/NZS 3000, Drawings 030- 3100 set |  |  |  |  | Verify |  | Supplier’s Certificate of Compliance Spatial Certificate of Compliance (where required) |  |  | HP | Project Engineer / Site Engineer /Principal’s Representative
2 |  |  | Construction
2.01 |  |  | Delivery of Materials to site | Each Lot |  | Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site. Identify any damage/defects prior to unloading of the material. |  |  | ZULU-BECA- 001-SPC-00005 Drawings |  |  |  |  | Visual Inspection |  | This ITP Signed Materials Inspection Checklist on ConQA |  |  | IP | Project Engineer / Site Engineer
2.2 |  |  | Conduit / Containment Installation – Walls and Ceilings | Each Lot |  | Confirm the following items are constructed in accordance with IFC design and specification.  Fixings secured in walls/ceilings.  Conduits, bends, and junction boxes  Draw wires installed  Fire-stopping and fire protection |  |  | ZULU-BECA- 001-SPC-00005 AS/NZS 3000, Drawings 030- 3100 set |  |  |  |  | Visual Inspection |  | This ITP Signed Building Eng ITC |  |  | IP | Project Engineer / Site Engineer
2.3 |  |  | MSB, LV Distribution Boards, and Control Panels | Each Lot |  | Confirm the following items are constructed in accordance with IFC design and specification.  Size, colour, location  Plinth (if required)  Secure and anchored.  Labels  Switchgear and M.E.N Link  Tightness & alignment  All wiring tidy and neat Verify and confirm the following tests (not limited to):  Polarity Check  Cable Loop Resistance (Ohms)  Insulation Resistance (Core-Core& Core to Earth) |  |  | ZULU-BECA- 001-SPC-00005 AS/NZS 3000, Drawings 030- 3100 set |  |  |  |  | Visual Inspection |  | This ITP Signed Building Engineering ITP |  |  | IP | Project Engineer / Site Engineer
2.4 |  |  | Cable Tray & Cable Tray Support Post Installation (Comms, Electrical and AGL) | Each Lot |  | Confirm the following items are constructed in accordance with IFC design and specification.  (i) Provide cable support system throughout, including cable trays (both power and Comms/ELV), cable ladders, trunking, conduits and catenary wire system.  (ii) External ducts and draw pits for the incoming LV supply shall be provided by the Civils Trade. Ducts connected between building and external pits to be of flexible type and be able to withstand building movement.  (iii) Provide cast-in conduits with draw wires as required.  (iv) All safety services shall be installed on fire rated containment. Where fire rated cable share containment with general services reticulation, all containment and fixings shall be selected and installed to suit the requirements of the safety services installation. |  |  | ZULU-BECA- 001-SPC-00005 -C2100, C2112 AS/NZS 3000 Drawings 030- 3100 set |  |  |  |  | Visual Inspection |  | This ITP Signed Building Eng ITC |  |  | IP | Project Engineer / Site Engineer
2.5 |  |  | Cabling – Mains, Submains, | Each Lot |  | Confirm cabling is constructed in accordance with IFC design and AS/NZS 3000. Verify and confirm the following tests (not limited to):  Polarity Check  Cable Loop Resistance (Ohms)  Insulation Resistance (Core-Core& Core to Earth) |  |  | ZULU-BECA- 001-SPC-00005 C2111.5 AS/NZS 3000 Drawings 030- 3100 set |  |  |  |  | Visual Inspection |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.6 |  |  | Emergency Lighting and Illuminated Exit Sign Installation | Each Lot |  | Confirm cabling is constructed in accordance with IFC design and AS/NZS 3000 & AS/NZS 2293 Verify and confirm the following tests (not limited to):  Polarity Check  Cable Loop Resistance (Ohms)  Insulation Resistance (Core-Core& Core to Earth) All Emergency luminaires, signs and exits labelled as per ALER 3 Emergency Lighting Schedule. |  |  | ZULU-BECA- 001-SPC-00005 C2132 Drawings 030- 3100 set AS/NZS 3000 |  |  |  |  | Visual Inspection |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.7 |  |  | Light Fitting and Light Control Installation. (External/Internal Luminaires, PIRs) | Each Lot |  | Confirm the following items are constructed in accordance with IFC design and specification.  Type, size, colour, quantities, location  Secure Verify and confirm the following tests (not limited to):  Polarity Check  Cable Loop Resistance (Ohms)  Insulation Resistance (Core-Core& Core to Earth) DALI control and lighting devices has been provided where dimming or time scheduling is required. External lighting must meet spill requirements of Part 139 (Aerodromes) MOS 2019 (i.e. downward facing so no spill light above the horizontal) and must not cause glare or distraction to pilots during aircraft movements. |  |  | ZULU-BECA- 001-SPC-00005 C2133 C2130 Drawings 030- 3100 set AS/NZS 1680.3 AS/NZS 3000 MOS 2019 – Part 139 |  |  |  |  | Visual Inspection |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.8 |  |  | GPOs / Data / Antenna outlets & WAPs | Each Lot |  | Confirm the following items are constructed in accordance with IFC design and specification.  Quantities& location  Secure  Fitted off and level. Confirm mounting height of outlets on site with the Superintendent. Generally, and unless otherwise shown on the drawings, outlets shall be mounted at:  300 mm above floor level or 200mm above benches in commercial areas.  1400 mm above floor level in plant and industrial areas. |  |  | ZULU-BECA- 001-SPC-00005- C2141 Drawings 030- 3100 set AS/NZS 3000 AS/ACIF S009:2006 |  |  |  |  | Visual Inspection |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.9 |  |  | Access Control systems Installation (Security Panel, Card Readers, Mag locks, Reed switches, REX, UPS) | Each Lot |  | Confirm the following items are constructed in accordance with IFC design and specification.  Size, colour, quantities, location  Secure  Fitted off and level. Check that the card reader is installed: a) at 1000mm above floor level; and b) on the access side of the door, on the mullion or within 600mm of the door / egress area as applicable. Verify battery and/or UPS capacity can operate normally for a duration of Eight (8) hours. |  |  | ZULU-BECA- 001-SPC-00005 C2701/C2703, Drawings 030- 3100 set, AS/NZS 3000 AS/NZS 2293 AS/ACIF S009:2006 |  |  |  |  | Visual Inspection |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.1 |  |  | CCTV Systems (CCTV Racks, CCTV Cameras, Archivers & Monitors) | Each Lot |  | Verify that CCTV rack installation quality are satisfactory as follows:  Equipment layout per IFC layout drawing.  Equipment are securely fastened.  Connection & terminations are securely fastened.  Racks (internal and external surfaces) are clean and free from any drilling dust, cable tie or cable off cuts and other debris.  Verify that all cables, patch cords, terminations and equipment are correctly labelled in accordance with the Cable Schedule, Patch Record and Label Schedules as well as the IFC Drawings. Verify that all cameras and mounting brackets are installed as per the camera coverage plans and camera schedule. |  |  | ZULU-BECA- 001-SPC-00005 C2705, Drawings 030- 3100 set, AS/NZS 3000 AS/ACIF S009:2006 |  |  |  |  | Visual Inspection |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.11 |  |  | Lightning Protection and Earthing Installation | Each Lot |  | The external lighting protection system shall be constructed as per AS/NZS 1768 and APAM standards Structural steelwork, cable trunking, metallic cable support systems, metal equipment and pipework shall be bonded as required by the regulations, AS/NZS 3000. Provide a main earth bar in the main switch room in a convenient location at 300 mm above finished floor level. Each bar shall be copper and be bonded to two local building earth plates using single core 70 mm2 green PVC sheathed stranded copper cable. |  |  | ZULU-BECA- 001-SPC-00005 C2160 / C2161 Drawings 030- 3100 set AS/NZS 1768 APAM standards AS/NZS 3000 |  |  |  |  | Visual Inspection |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.12 |  |  | Existing LV Services Migration | Each Lot |  | The following existing services have been migrated to the new ALER3 MSB: • Building 18 LV Supply • MISC LV supply • VOR LV supply • IWDI-1 and IWDI-2 LV supply • SFAL LV supply • RAF LV supply • DME LV supply |  |  | ZULU-BECA- 001-SPC-00005 C2160 / C2100 Drawings 030- 3100 set APAM standards AS/NZS 3000 |  |  |  | Visual Inspection |  |  | This ITP Signed Building Eng ITP |  |  | HP* | Project Engineer / Site Engineer
2.13 |  |  | Survey As Built | Prior to Covering Services |  | Survey to pick up services prior to covering |  |  | FH QMP |  |  |  | Verify |  |  | Survey |  |  | HP* | Project Engineer / Site Engineer /Surveyor
Final Inspection The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications. Print Name: Position: Signature: Date: / /
Legend:
| HP |  | Hold Point |  | Work shall not proceed past the HP until released by the Principal’s Representative | [5 empty] | IP |  | Inspection point |  |  |  |  | Formal Inspection to be done and recorded
[7 empty] | Inspection and Test Plan - Control and Supervision of the Works | [14 empty] | Doc ID: FH-ZU2-QU-ITP034 REV: 0
Client: Melbourne Airport | [7 empty] | Contract No: CP14038-01 | [10 empty] | Prepared By: Jihad Barbar
Project: Taxiway Zulu | [14 empty] | Reviewed By: Jamal Khodr | [6 empty] | Date: 06/01/2025
Construction Process: ALER 3 Electrical | [14 empty] | Approved By: Marco Poggenberg | [6 empty] | Date: 06/01/2025
Specifications: ZULU-BECA-001-SPC-00005, Drawings
Structure / Component: Electrical Switchboards, DBs, LV Cabling, Containment, Lighting, Lighting Control, Emergency Lighting, Access Control Systems and CCTV Installation.
HP* |  | Fulton Hogan Hold Point |  | Work shall not proceed past the HP* until released by Fulton Hogan | [5 empty] | TP |  | Test Point |  |  |  |  | Product compliance test to be undertaken and recorded/reported
WP |  | Witness Point |  | An inspection which must be witnessed by the Principal’s Representative | [5 empty] | SCP |  | Survey conformance point |  |  |  |  | A qualified surveyor to check product/section/structure and report
AP |  | Approval Point |  | Written or verbal approval given by the Principal’s Representative
Notes