## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP034 - ALER 3 Electrical | itp |  |  |  |  | FH-ZU2-QU-ITP034 - ALER 3 Electrical - Rev 0
section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
checkpoint | 1.1 - Check for correct documentation
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | – using the correct and complete set of drawings.
label | – all drawings are the latest revision.
label | Reference Documents - Drawings / Aconex Register
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings and drawing registers
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 1.3 - Survey Checks
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Survey set out to be completed for all assets
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 1.4 - Submission & approval of shop drawings
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - HOLD POINT
label | ○ Submit shop drawings to the principal’s representative for approval prior to fabrication commencement. Items to include but not limited to:
label | – MSB, DB-A, DB-C, DB-L&P, DB-EX1, DB-EX2, MSSB, DB-MGC, DB-GCP, DB-LBC, Luminaires, Light Control Systems, Lightning Protection and Earthing
label | Reference Documents - ZULU-BECA- 001-SPC-00005 C2100 Page 8, Drawings 030-3100 set, Approved Shop drawings
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - Project Engineer / Site Engineer /Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.5 - Material Submissions
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - HOLD POINT
label | ○ Items to include but not limited to:
label | – Cables, control panels, luminaires, lighting control, switches, isolators, contactors, circuit breakers, earthing system, cable trays, ladders, etc. (all containment)
label | Reference Documents - ZULU-BECA- 001-SPC-00005, AS/NZS 3000, Drawings 030-3100 set
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - Project Engineer / Site Engineer /Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.6 - Temporary Works (if applicable)
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Submission and approval of the following documentation based on the Temporary Works Design Process Matrix.
label | Reference Documents - ZULU-BECA- 001-SPC-00005, Temporary Works Design Process Matrix, Drawings 030-3100 set
label | Inspection/Test Method - Verify
label | Record of conformity - As defined by the Temporary Works Design Process Matrix (where applicable)
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 1.7 - Off-site Inspections
label | Frequency - Each Lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Inspection and attendance on site for Factory Acceptance Testing for:
label | – Switchboards
label | – Distribution Boards
label | ○ Following these inspections FAT testing shall be submitted.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 C2121.20, AS/NZS 3000, Drawings 030-3100 set
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Factory Acceptance Tests
label | WP TP
label | Responsibility - Project Engineer / Site Engineer /Principal’s Representative
date | Date Completed:
checkpoint | 1.8 - Certificates of Compliance (prior to delivery to onsite)
label | Frequency - Each Lot
label | Acceptance Criteria - Provide Suppliers Certificate of Compliance and Spatial Certificate of Compliance for
label | ○ Switchboards
label | ○ Distribution Boards
label | ○ Control Systems
label | ○ Power Control
label | ○ Switchgear
label | ○ Cables
label | Reference Documents - ZULU-BECA-001-SPC-00005 C2100.3, AS/NZS 3000, Drawings 030-3100 set
label | Inspection/Test Method - Verify
label | Record of conformity - Supplier’s Certificate of Compliance, Spatial Certificate of Compliance (where required)
label | HP
label | Responsibility - Project Engineer / Site Engineer /Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 - Construction
checkpoint | 2.01 - Delivery of Materials to site
label | Frequency - Each Lot
label | Acceptance Criteria - Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site.
label | ○ Identify any damage/defects prior to unloading of the material.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, Materials Inspection Checklist on ConQA
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.2 - Conduit / Containment Installation – Walls and Ceilings
label | Frequency - Each Lot
label | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
label | ○ Fixings secured in walls/ceilings.
label | ○ Conduits, bends, and junction boxes
label | ○ Draw wires installed
label | ○ Fire-stopping and fire protection
label | Reference Documents - ZULU-BECA-001-SPC-00005, AS/NZS 3000, Drawings 030-3100 set
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Building Eng ITC
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.3 - MSB, LV Distribution Boards, and Control Panels
label | Frequency - Each Lot
label | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
label | ○ Size, colour, location
label | ○ Plinth (if required)
label | ○ Secure and anchored.
label | ○ Labels
label | ○ Switchgear and M.E.N Link
label | ○ Tightness & alignment
label | ○ All wiring tidy and neat
label | Verify and confirm the following tests (not limited to):
label | ○ Polarity Check
label | ○ Cable Loop Resistance (Ohms)
label | ○ Insulation Resistance (Core-Core& Core to Earth)
label | Reference Documents - ZULU-BECA- 001-SPC-00005, AS/NZS 3000, Drawings 030-3100 set
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, Building Engineering ITP
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.4 - Cable Tray & Cable Tray Support Post Installation (Comms, Electrical and AGL)
label | Frequency - Each Lot
label | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
label | ○ (i) Provide cable support system throughout, including cable trays (both power and Comms/ELV), cable ladders, trunking, conduits and catenary wire system.
label | ○ (ii) External ducts and draw pits for the incoming LV supply shall be provided by the Civils Trade. Ducts connected between building and external pits to be of flexible type and be able to withstand building movement.
label | ○ (iii) Provide cast-in conduits with draw wires as required.
label | ○ (iv) All safety services shall be installed on fire rated containment. Where fire rated cable share containment with general services reticulation, all containment and fixings shall be selected and installed to suit the requirements of the safety services installation.
label | Reference Documents - ZULU-BECA- 001-SPC-00005-C2100, C2112 AS/NZS 3000, Drawings 030-3100 set
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Building Eng ITC
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.5 - Cabling – Mains, Submains,
label | Frequency - Each Lot
label | Acceptance Criteria - Confirm cabling is constructed in accordance with IFC design and AS/NZS 3000.
label | Verify and confirm the following tests (not limited to):
label | ○ Polarity Check
label | ○ Cable Loop Resistance (Ohms)
label | ○ Insulation Resistance (Core-Core& Core to Earth)
label | Reference Documents - ZULU-BECA- 001-SPC-00005 C2111.5, AS/NZS 3000, Drawings 030-3100 set
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Building Eng ITP
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.6 - Emergency Lighting and Illuminated Exit Sign Installation
label | Frequency - Each Lot
label | Acceptance Criteria - Confirm cabling is constructed in accordance with IFC design and AS/NZS 3000 & AS/NZS 2293
label | Verify and confirm the following tests (not limited to):
label | ○ Polarity Check
label | ○ Cable Loop Resistance (Ohms)
label | ○ Insulation Resistance (Core-Core& Core to Earth)
label | All Emergency luminaires, signs and exits labelled as per ALER 3 Emergency Lighting Schedule.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 C2132, Drawings 030-3100 set, AS/NZS 3000
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Building Eng ITP
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.7 - Light Fitting and Light Control Installation. (External/Internal Luminaires, PIRs)
label | Frequency - Each Lot
label | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
label | – Type, size, colour, quantities, location
label | – Secure
label | ○ Verify and confirm the following tests (not limited to):
label | – Polarity Check
label | – Cable Loop Resistance (Ohms)
label | – Insulation Resistance (Core-Core& Core to Earth)
label | ○ DALI control and lighting devices has been provided where dimming or time scheduling is required.
label | ○ External lighting must meet spill requirements of Part 139 (Aerodromes) MOS 2019 (i.e. downward facing so no spill light above the horizontal) and must not cause glare or distraction to pilots during aircraft movements.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 C2133 C2130, Drawings 030-3100 set, AS/NZS 1680.3, AS/NZS 3000 MOS 2019 – Part 139
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Building Eng ITP
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.8 - GPOs / Data / Antenna outlets & WAPs
label | Frequency - Each Lot
label | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
label | ○ Quantities& location
label | ○ Secure
label | ○ Fitted off and level.
label | Confirm mounting height of outlets on site with the Superintendent. Generally, and unless otherwise shown on the drawings, outlets shall be mounted at:
label | ○ 300 mm above floor level or 200mm above benches in commercial areas.
label | ○ 1400 mm above floor level in plant and industrial areas.
label | Reference Documents - ZULU-BECA- 001-SPC-00005- C2141, Drawings 030-3100 set, AS/NZS 3000, AS/ACIF S009:2006
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Building Eng ITP
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.9 - Access Control systems Installation (Security Panel, Card Readers, Mag locks, Reed switches, REX, UPS)
label | Frequency - Each Lot
label | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
label | – Size, colour, quantities, location
label | – Secure
label | – Fitted off and level.
label | ○ Check that the card reader is installed:
label | a) at 1000mm above floor level; and
label | b) on the access side of the door, on the mullion or within 600mm of the door / egress area as applicable.
label | ○ Verify battery and/or UPS capacity can operate normally for a duration of Eight (8) hours.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 C2701/C2703, Drawings 030-3100 set, AS/NZS 3000, AS/NZS 2293 AS/ACIF S009:2006
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Building Eng ITP
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.10 - CCTV Systems (CCTV Racks, CCTV Cameras, Archivers & Monitors)
label | Frequency - Each Lot
label | Acceptance Criteria - Verify that CCTV rack installation quality are satisfactory as follows:
label | – Equipment layout per IFC layout drawing.
label | – Equipment are securely fastened.
label | – Connection & terminations are securely fastened.
label | – Racks (internal and external surfaces) are clean and free from any drilling dust, cable tie or cable off cuts and other debris.
label | – Verify that all cables, patch cords, terminations and equipment are correctly labelled in accordance with the Cable Schedule, Patch Record and Label Schedules as well as the IFC Drawings.
label | ○ Verify that all cameras and mounting brackets are installed as per the camera coverage plans and camera schedule.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 C2705, Drawings 030-3100 set, AS/NZS 3000 AS/ACIF S009:2006
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Building Eng ITP
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.11 - Lightning Protection and Earthing Installation
label | Frequency - Each Lot
label | Acceptance Criteria - The external lighting protection system shall be constructed as per AS/NZS 1768 and APAM standards
label | ○ Structural steelwork, cable trunking, metallic cable support systems, metal equipment and pipework shall be bonded as required by the regulations, AS/NZS 3000.
label | ○ Provide a main earth bar in the main switch room in a convenient location at 300 mm above finished floor level. Each bar shall be copper and be bonded to two local building earth plates using single core 70 mm2 green PVC sheathed stranded copper cable.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 C2160 / C2161, Drawings 030-3100 set, AS/NZS 1768, APAM standards, AS/NZS 3000
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Building Eng ITP
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.12 - Existing LV Services Migration
label | Frequency - Each Lot
label | Acceptance Criteria - The following existing services have been migrated to the new ALER3 MSB:
label | ○ Building 18 LV Supply
label | ○ MISC LV supply
label | ○ VOR LV supply
label | ○ IWDI-1 and IWDI-2 LV supply
label | ○ SFAL LV supply
label | ○ RAF LV supply
label | ○ DME LV supply
label | Reference Documents - ZULU-BECA- 001-SPC-00005 C2160 / C2100, Drawings 030-3100 set, APAM standards, AS/NZS 3000
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Building Eng ITP
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.13 - Survey As Built
label | Frequency - Prior to Covering Services
label | Acceptance Criteria - Survey to pick up services prior to covering
label | Reference Documents - FH QMP
label | Inspection/Test Method - Verify
label | Record of conformity - Survey
label | HP*
label | Responsibility - Project Engineer / Site Engineer /Surveyor
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: