## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - Wastewater Drainage Lines | itp |  |  |  |  | ITP - Wastewater Drainage Lines
section | WW 1.0 - Wastewater Line Setout
checkpoint | 1.1 - Ensure that the latest revision of the relevant drawing is being used.
label | Acceptance Criteria - CI
label | Verifying Document - Current Plan and Longsection revisions being used to install
checkpoint | 1.2 - Confirm Datum for Survey Setout
label | Acceptance Criteria - CI
label | Verifying Document - Correspondence of Datum to use
checkpoint | 1.3 - Confirm existing and proposed drainage locations
label | Acceptance Criteria - CI
label | Verifying Document - Asbuilt of Existing Manholes
checkpoint | 1.4 - All wastewater pipes and manholes shall be placed in accordance with Engineer's model and locations given in design drawings.
label | Spec Reference/Special Conditions - Prelet
label | Acceptance Criteria - CI
label | Verifying Document - Drainage Models provided by Engineer
checkpoint | 1.5 - Wastewater Connection Authorisation approval from Veolia for Tie-ins into existing
label | Spec Reference/Special Conditions - Veolia Requirements
label | Acceptance Criteria - HP
label | Verifying Document - Signed Wastewater Connection Authorsiation form from Veolia
holdpoint | HOLD POINT
checkpoint | 1.6 - Complete council Kick-off meeting
label | Spec Reference/Special Conditions - Building Consent
label | Acceptance Criteria - HP
label | Verifying Document - Council inspection report
holdpoint | HOLD - Continue only if the above is signed off.
section | WW 2.0 - Wastewater Line Excavation
checkpoint | 2.1 - Wastewater trench should be excavated to design levels given in drawings. Tolerances given are -0mm, +50mm for line and -50mm, +0mm for level. Trench to be benched or battered when depth exceed 1.2m. Trench width to be dependant on pipe diameter and trench depth. Use trench shield if battered cannot be achieve.
label | Spec Reference/Special Conditions - NZS 4404:2010, AS/NZS 2566.2 WorkSafe NZ – Good Practice Guidelines: Excavation Safety
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 2.2 - IF rock is encountered levels and photos are to be taken. Geotech must inspect rock prior to any break out. Levels and photos must be taken post-breakout.
label | Acceptance Criteria - HP
label | Verifying Document - Geotech signoff
holdpoint | HOLD POINT
checkpoint | 2.3 - Breakout to commence only once Client have issued a site instruction
label | Acceptance Criteria - WP
label | Verifying Document - H&R Site Instruction
holdpoint | HOLD - Continue only if the above is signed off.
section | WW 3.0 - Wastewater Line Installation
checkpoint | 3.1 - The position tolerance for pipe laying at any point along the length of the installation shall be within ±30 mm from the specified design.
label | Spec Reference/Special Conditions - Watercare C3.1.1
label | Acceptance Criteria - CI
label | Verifying Document - M&P longsection sheet
checkpoint | 3.2 - Ensure grade with digital spirit level matches design grade along pipe alignment
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Photos along alignment
checkpoint | 3.3 - Asbuilt of pipe invert levels prior to Auckland Council Inspection
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Asbuilt Drawing
checkpoint | 3.4 - Allow Auckland Council opportunity to inspect pipeline prior to backfill
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Council inspection report
checkpoint | 3.6 - Allow Veolia opportunity to inspect Tie-in prior to backfill
label | Spec Reference/Special Conditions - Veolia Requirements
label | Acceptance Criteria - CI
label | Verifying Document - Correspondence from Veolia
checkpoint | 3.7 - Backfill line in 200mm layers and conduct Clegg Hammer Impact Tests for Hardfill achieving CIV 25
label | Spec Reference/Special Conditions - Watercare C2.21 row 12
label | Acceptance Criteria - CI
label | Verifying Document - Clegg Hammer Results Sheet
checkpoint | 3.8 - Backfill line in 300mm layers and conduct Shearvanes for clay fill achieving average value not less than 150KPA
label | Spec Reference/Special Conditions - Engenium Excavation and Hardfil Spec. Item 2.4
label | Acceptance Criteria - CI
label | Verifying Document - Shear Vane Results Sheet
checkpoint | 3.9 - Pipework shall be CCTV inspected for defects, in particular pipe joints and to identify ponding areas for correction in gravity systems
label | Spec Reference/Special Conditions - Watercare General Civil Construction Standard C3.1j
label | Acceptance Criteria - CI
label | Verifying Document - CCTV Footage and Reports
checkpoint | 3.10 - Watertightness Testing in presence of Auckland Council and Engineer
label | Spec Reference/Special Conditions - Watercare General Civil Construction Standard C10.5.1
label | Acceptance Criteria - CI
label | Verifying Document - Council inspection report and Engineer Correspondence
section | WW 4.0 - Handover to client with PS3
checkpoint | 4.1 - Complete Council final drainage inspection
label | Acceptance Criteria - HP
label | Verifying Document - Council inspection report
holdpoint | HOLD POINT
checkpoint | 4.2 - Complete Engineer final drainage inspection
label | Acceptance Criteria - HP
label | Verifying Document - Correspondence Engineer
holdpoint | HOLD POINT
checkpoint | 4.2 - As built all pipe invert levels in manholes and CP and lid levels
label | Acceptance Criteria - HP
label | Verifying Document - As built report
holdpoint | HOLD POINT
checkpoint | 4.4 - Handover to client with CS3
label | Spec Reference/Special Conditions - CS3 Drainage
label | Acceptance Criteria - HP
label | Verifying Document - Handover documents
holdpoint | HOLD POINT
checkpoint | Comments / Required Actions:
textbox | Rev. Status
date | Date
textbox | Reason for Rev.
checkpoint | Signed by:
note | Contractors Representative
textbox | Print:
date | Date:
note | Clients Representative
textbox | Print:
date | Date:
signoff | Signatures:
checklist | ITP - Drainage Manholes | itp |  |  |  |  | ITP - Drainage Manholes
section | WW 1.0 - Wastewater Manhole Setout
checkpoint | 1.1 - Ensure that the latest revision of the relevant drawing is being used.
label | Acceptance Criteria - CI
label | Verifying Document - Current Plan and Longsection revisions being used to install
checkpoint | 1.2 - Confirm Datum for Survey Setout
label | Acceptance Criteria - CI
label | Verifying Document - Correspondence of Datum to use
checkpoint | 1.3 - Confirm existing and proposed drainage locations
label | Acceptance Criteria - CI
label | Verifying Document - Asbuilt of Existing Manholes
checkpoint | 1.4 - All wastewater pipes and manholes shall be placed in accordance with Engineer's model and locations given in design drawings.
label | Spec Reference/Special Conditions - Prelet
label | Acceptance Criteria - CI
label | Verifying Document - Drainage Models provided by Engineer
checkpoint | 1.5 - Wastewater Connection Authorisation approval from Veolia for Tie-ins into existing
label | Spec Reference/Special Conditions - Veolia Requirements
label | Acceptance Criteria - HP
label | Verifying Document - Signed Wastewater Connection Authorsiation form from Veolia
holdpoint | HOLD POINT
checkpoint | 1.6 - Complete council Kick-off meeting
label | Spec Reference/Special Conditions - Building Consent
label | Acceptance Criteria - HP
label | Verifying Document - Council inspection report
holdpoint | HOLD - Continue only if the above is signed off.
section | WW 2.0 - Wastewater Manhole Excavation
checkpoint | 2.1 - Manhole shall be placed on firm natural ground
label | Spec Reference/Special Conditions - Watercare WW 9
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 2.2 - IF rock is encountered levels and photos are to be taken. Geotech must inspect rock prior to any break out. Levels and photos must be taken post-breakout.
label | Acceptance Criteria - HP
label | Verifying Document - Geotech signoff
holdpoint | HOLD POINT
checkpoint | 2.3 - Breakout to commence only once Client have issued a site instruction
label | Acceptance Criteria - WP
label | Verifying Document - H&R Site Instruction
holdpoint | HOLD - Continue only if the above is signed off.
section | WW 3.0 - Wastewater Manhole Installation
checkpoint | 3.1 - Manhole Base to be laid on minimum 100mm bed of Gap20
label | Spec Reference/Special Conditions - Watercare WW 9
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.2 - Hydrophilic Seal Starters to be used to connnect into manhole
label | Spec Reference/Special Conditions - Watercare WW 5
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.3 - Haunching to be done on all lines entering manhole
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Photos of Haunching outside manhole
checkpoint | 3.4 - Asbuilt of Manhole invert levels prior to Auckland Council Inspection
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Asbuilt Drawing
checkpoint | 3.5 - The position tolerance for pipe laying at any point along the length of the installation shall be within ±30 mm from the specified design.
label | Spec Reference/Special Conditions - Watercare C3.1.1
label | Acceptance Criteria - CI
label | Verifying Document - M&P manhole sheet
checkpoint | 3.5 - Allow Auckland Council opportunity to inspect manhole Haunching prior to backfill
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Council inspection report
checkpoint | 3.6 - Allow Veolia opportunity to inspect Tie-in prior to backfill
label | Spec Reference/Special Conditions - Veolia Requirements
label | Acceptance Criteria - CI
label | Verifying Document - Correspondence from Veolia
checkpoint | 3.7 - Backfill Manhole in 200mm layers and conduct Clegg Hammer Impact Tests for Hardfill achieving CIV 25
label | Spec Reference/Special Conditions - Watercare C2.21 row 12
label | Acceptance Criteria - CI
label | Verifying Document - Clegg Hammer Results Sheet
checkpoint | 3.8 - Backfill Manhole in 300mm layers and conduct Shearvanes for clay fill achieving average value not less than 150KPA
label | Spec Reference/Special Conditions - Engenium Excavation and Hardfil Spec. Item 2.4
label | Acceptance Criteria - CI
label | Verifying Document - Shear Vane Results Sheet
checkpoint | 3.9 - Benching to be done with Half Round Channel pipe earthenware
label | Spec Reference/Special Conditions - Watercare WW5, Watercare WW9
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.10 - Steps to be installed, ensure that lid opening is orientated on sthe location of steps.
label | Spec Reference/Special Conditions - Watercare WW 5
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.11 - Ensure full entry depth of throat is not greater than 450mm and that the finishing around it is complete.
label | Spec Reference/Special Conditions - Watercare WW 6
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.12 - Manhole covers in the road shall be constructed so that the cover hinge is facing the oncoming traffic, for all other covers the orientation should be so that the cover hinge is at 90 degrees from the ladder, either side.
label | Spec Reference/Special Conditions - Watercare WW 6
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.13 - Safety Grille to be installed
label | Spec Reference/Special Conditions - Watercare WW 7
label | Acceptance Criteria - CI
label | Verifying Document - Photos
holdpoint | HOLD - Continue only if the above is signed off.
section | WW 4.0 - Handover to client with PS3
checkpoint | 4.1 - Complete Council final drainage inspection
label | Acceptance Criteria - HP
label | Verifying Document - Council inspection report
holdpoint | HOLD POINT
checkpoint | 4.2 - Complete Engineer final drainage inspection
label | Acceptance Criteria - HP
label | Verifying Document - Correspondence Engineer
holdpoint | HOLD POINT
checkpoint | 4.2 - As built all pipe invert levels in manholes and CP and lid levels
label | Acceptance Criteria - HP
label | Verifying Document - As built report
holdpoint | HOLD POINT
checkpoint | 4.4 - Handover to client with CS3
label | Spec Reference/Special Conditions - CS3 Drainage
label | Acceptance Criteria - HP
label | Verifying Document - Handover documents
holdpoint | HOLD POINT
checkpoint | Comments / Required Actions:
textbox | Rev. Status
date | Date
textbox | Reason for Rev.
checkpoint | Signed by:
note | Contractors Representative
textbox | Print:
date | Date:
note | Clients Representative
textbox | Print:
date | Date:
signoff | Signatures:
checklist | ITP - Stormwater Manholes | itp |  |  |  |  | ITP - Stormwater Manholes
section | SW 1.0 - Stormwater Manhole Setout
checkpoint | 1.1 - Ensure that the latest revision of the relevant drawing is being used.
label | Acceptance Criteria - CI
label | Verifying Document - Current Plan and Longsection revisions being used to install
checkpoint | 1.2 - Confirm Datum for Survey Setout
label | Acceptance Criteria - CI
label | Verifying Document - Correspondence of Datum to use
checkpoint | 1.3 - Confirm existing and proposed drainage locations
label | Acceptance Criteria - CI
label | Verifying Document - Asbuilt of Existing Manholes
checkpoint | 1.4 - All wastewater pipes and manholes shall be placed in accordance with Engineer's model and locations given in design drawings.
label | Spec Reference/Special Conditions - Prelet
label | Acceptance Criteria - CI
label | Verifying Document - Drainage Models provided by Engineer
checkpoint | 1.5 - Complete council Kick-off meeting
label | Spec Reference/Special Conditions - Building Consent
label | Acceptance Criteria - HP
label | Verifying Document - Council inspection report
holdpoint | HOLD - Continue only if the above is signed off.
section | SW 2.0 - Stormwater Manhole Excavation
checkpoint | 2.1 - Manhole shall be placed on firm natural ground
label | Spec Reference/Special Conditions - SWCOP SW06
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 2.2 - IF rock is encountered levels and photos are to be taken. Geotech must inspect rock prior to any break out. Levels and photos must be taken post-breakout.
label | Acceptance Criteria - HP
label | Verifying Document - Geotech signoff
holdpoint | HOLD POINT
checkpoint | 2.3 - Breakout to commence only once Client have issued a site instruction
label | Acceptance Criteria - WP
label | Verifying Document - H&R Site Instruction
holdpoint | HOLD - Continue only if the above is signed off.
section | SW 3.0 - Stormwater Manhole Installation
checkpoint | 3.1 - Manhole Base to be laid on minimum 100mm bed of Gap20
label | Spec Reference/Special Conditions - SWCOP SW05
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.2 - 600mm max Starters to be used to connnect into manhole
label | Spec Reference/Special Conditions - SWCOP SW04
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.3 - Haunching to be done on all lines entering manhole
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Photos of Haunching outside manhole
checkpoint | 3.4 - Asbuilt of Manhole invert levels prior to Auckland Council Inspection
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Asbuilt Drawing
checkpoint | 3.5 - The position tolerance for pipe laying at any point along the length of the installation shall be within ±30 mm from the specified design.
label | Spec Reference/Special Conditions - Watercare C3.1.1
label | Acceptance Criteria - CI
label | Verifying Document - M&P manhole sheet
checkpoint | 3.5 - Allow Auckland Council opportunity to inspect manhole Haunching prior to backfill
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Council inspection report
checkpoint | 3.6 - Allow Veolia opportunity to inspect Tie-in prior to backfill
label | Spec Reference/Special Conditions - Veolia Requirements
label | Acceptance Criteria - CI
label | Verifying Document - Correspondence from Veolia
checkpoint | 3.7 - Backfill Manhole in 200mm layers and conduct Clegg Hammer Impact Tests for Hardfill achieving CIV 25
label | Spec Reference/Special Conditions - Watercare C2.21 row 12
label | Acceptance Criteria - CI
label | Verifying Document - Clegg Hammer Results Sheet
checkpoint | 3.8 - Backfill Manhole in 300mm layers and conduct Shearvanes for clay fill achieving average value not less than 150KPA
label | Spec Reference/Special Conditions - Engenium Excavation and Hardfil Spec. Item 2.4
label | Acceptance Criteria - CI
label | Verifying Document - Shear Vane Results Sheet
checkpoint | 3.9 - Benching to be done with Half Round Channel pipe concrete
label | Spec Reference/Special Conditions - SWCOP SW05
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.10 - Steps to be installed, ensure that lid opening is orientated on sthe location of steps.
label | Spec Reference/Special Conditions - SWCOP SW05
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.11 - Ensure full entry depth of throat is not greater than 450mm and that the finishing around it is complete.
label | Spec Reference/Special Conditions - SWCOP SW05
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 3.12 - Manhole covers in the road shall be constructed so that the cover hinge is facing the oncoming traffic, for all other covers the orientation should be so that the cover hinge is at 90 degrees from the ladder, either side.
label | Spec Reference/Special Conditions - Watercare WW 6
label | Acceptance Criteria - CI
label | Verifying Document - Photos
holdpoint | HOLD - Continue only if the above is signed off.
section | SW 4.0 - Handover to client with PS3
checkpoint | 4.1 - Complete Auckland Council final drainage inspection
label | Acceptance Criteria - HP
label | Verifying Document - Council inspection report
holdpoint | HOLD POINT
checkpoint | 4.2 - Complete Engineer final drainage inspection
label | Acceptance Criteria - HP
label | Verifying Document - Correspondence Engineer
holdpoint | HOLD POINT
checkpoint | 4.2 - As built all pipe invert levels in manholes and CP and lid levels
label | Acceptance Criteria - HP
label | Verifying Document - As built report
holdpoint | HOLD POINT
checkpoint | 4.4 - Handover to client with CS3
label | Spec Reference/Special Conditions - CS3 Drainage
label | Acceptance Criteria - HP
label | Verifying Document - Handover documents
holdpoint | HOLD POINT
checkpoint | Comments / Required Actions:
textbox | Rev. Status
date | Date
textbox | Reason for Rev.
checkpoint | Signed by:
note | Contractors Representative
textbox | Print:
date | Date:
note | Clients Representative
textbox | Print:
date | Date:
signoff | Signatures:
checklist | ITP - Stormwater Drainage Lines | itp |  |  |  |  | ITP - Stormwater Drainage Lines
section | SW 1.0 - Stormwater Line Setout
checkpoint | 1.1 - Ensure that the latest revision of the relevant drawing is being used.
label | Acceptance Criteria - CI
label | Verifying Document - Current Plan and Longsection revisions being used to install
checkpoint | 1.2 - Confirm Datum for Survey Setout
label | Acceptance Criteria - CI
label | Verifying Document - Correspondence of Datum to use
checkpoint | 1.3 - Confirm existing and proposed drainage locations
label | Acceptance Criteria - CI
label | Verifying Document - Asbuilt of Existing Manholes
checkpoint | 1.4 - All wastewater pipes and manholes shall be placed in accordance with Engineer's model and locations given in design drawings.
label | Spec Reference/Special Conditions - Prelet
label | Acceptance Criteria - CI
label | Verifying Document - Drainage Models provided by Engineer
checkpoint | 1.5 - Complete council Kick-off meeting
label | Spec Reference/Special Conditions - Building Consent
label | Acceptance Criteria - HP
label | Verifying Document - Council inspection report
holdpoint | HOLD - Continue only if the above is signed off.
section | 2.0 - Stormwater Line Excavation
checkpoint | 2.1 - Wastewater trench should be excavated to design levels given in drawings. Tolerances given are -0mm, +50mm for line and -50mm, +0mm for level. Trench to be benched or battered when depth exceed 1.2m. Trench width to be dependant on pipe diameter and trench depth. Use trench shield if battered cannot be achieve.
label | Spec Reference/Special Conditions - NZS 4404:2010, AS/NZS 2566.2, WorkSafe NZ – Good Practice Guidelines: Excavation Safety
label | Acceptance Criteria - CI
label | Verifying Document - Photos
checkpoint | 2.2 - IF rock is encountered levels and photos are to be taken. Geotech must inspect rock prior to any break out. Levels and photos must be taken post-breakout.
label | Acceptance Criteria - HP
label | Verifying Document - Geotech signoff
holdpoint | HOLD POINT
checkpoint | 2.3 - Breakout to commence only once Client have issued a site instruction
label | Acceptance Criteria - WP
label | Verifying Document - H&R Site Instruction
holdpoint | HOLD - Continue only if the above is signed off.
section | SW 3.0 - Stormwater Line Installation
checkpoint | 3.1 - The position tolerance for pipe laying at any point along the length of the installation shall be within ±30 mm from the specified design.
label | Spec Reference/Special Conditions - Watercare C3.1.1
label | Acceptance Criteria - CI
label | Verifying Document - M&P longsection sheet
checkpoint | 3.2 - Ensure grade with digital spirit level matches design grade along pipe alignment
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Photos along alignment
checkpoint | 3.3 - Asbuilt of pipe invert levels prior to Auckland Council Inspection
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Asbuilt Drawing
checkpoint | 3.4 - Allow Auckland Council opportunity to inspect pipeline prior to backfill
label | Spec Reference/Special Conditions - Auckland Council Requirement
label | Acceptance Criteria - CI
label | Verifying Document - Council inspection report
checkpoint | 3.7 - Backfill line in 200mm layers and conduct Clegg Hammer Impact Tests for Hardfill achieving CIV 25
label | Spec Reference/Special Conditions - Watercare C2.21 row 12
label | Acceptance Criteria - CI
label | Verifying Document - Clegg Hammer Results Sheet
checkpoint | 3.8 - Backfill line in 300mm layers and conduct Shearvanes for clay fill achieving average value not less than 150KPA
label | Spec Reference/Special Conditions - Engenium Excavation and Hardfil Spec. Item 2.4
label | Acceptance Criteria - CI
label | Verifying Document - Shear Vane Results Sheet
checkpoint | 3.9 - Pipework shall be CCTV inspected for defects, in particular pipe joints and to identify ponding areas for correction in gravity systems
label | Spec Reference/Special Conditions - SWCOP
label | Acceptance Criteria - CI
label | Verifying Document - CCTV Footage and Reports
holdpoint | HOLD - Continue only if the above is signed off.
section | SW 4.0 - Handover to client with PS3
checkpoint | 4.1 - Complete Council final drainage inspection
label | Acceptance Criteria - HP
label | Verifying Document - Council inspection report
holdpoint | HOLD POINT
checkpoint | 4.2 - Complete Engineer final drainage inspection
label | Acceptance Criteria - HP
label | Verifying Document - Correspondence Engineer
holdpoint | HOLD POINT
checkpoint | 4.2 - As built all pipe invert levels in manholes and CP and lid levels
label | Acceptance Criteria - HP
label | Verifying Document - As built report
holdpoint | HOLD POINT
checkpoint | 4.4 - Handover to client with CS3
label | Spec Reference/Special Conditions - CS3 Drainage
label | Acceptance Criteria - HP
label | Verifying Document - Handover documents
holdpoint | HOLD POINT
checkpoint | Comments / Required Actions:
textbox | Rev. Status
date | Date
textbox | Reason for Rev.
checkpoint | Signed by:
note | Contractors Representative
textbox | Print:
date | Date:
note | Clients Representative
textbox | Print:
date | Date:
signoff | Signatures: