## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | e5e05ec3-b5e7-4ea7-bcf8-b7b860580bca |  | checklist | QA - Main Water Reticulation |  |  |  |  | Yes | QA - Main Water Reticulation | 049ddd78-5519-4668-9ade-5a675e2ebe5f
checkpoint-group | becb69e6-643f-42e8-9eab-e0960bb0e6b2 |  | section | Cold Water Main
checkpoint-no-status | 60c65f23-6f04-432c-a89f-aa1dc6a7f0f4 |  | checkpoint | Zone / Area
text | e6d3ca1c-1add-5b32-a550-48d33cbc5e3f |  | textbox | Zone / Area
checkpoint-status | 1143ca37-b60d-4a51-9327-697321dc5678 |  | checkpoint | Connections welded/crimped correctly
checkpoint-status | d2159fbb-04ff-478e-8caa-1e50b678e6e8 |  | checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
checkpoint-status | 837bacab-b42d-4a31-af82-8356fa2a9389 |  | checkpoint | Lagging installed and neat
checkpoint-status | 5587f44e-1242-4b7e-8c64-5e69750b3798 |  | checkpoint | Labels installed
checkpoint-status | 132e52b9-5c3d-40b7-bb7c-5fe46956e453 |  | checkpoint | Correct valves fitted correctly
checkpoint-status | b86a64b3-3c85-43e0-922e-ed1892d59242 |  | checkpoint | Seismic bracing completed
checkpoint-status | 13396721-92ff-473f-a72a-a2f4ef6f3e59 |  | checkpoint | Tested
checkpoint-group | de80f719-2e76-495d-9285-4a7e0c6d89da |  | section | Hot Water Main
checkpoint-no-status | 9b5240c0-e721-4543-abc5-cb6956c62275 |  | checkpoint | Zone / Area
text | 42ad0cf1-33fa-5951-a97c-0f457edf2048 |  | textbox | Zone / Area
checkpoint-status | 02915715-41a6-4465-83ed-0d4cc11e3a3a |  | checkpoint | Connections welded/crimped correctly
checkpoint-status | aeaa95d5-3ced-45ed-9e54-6b1bf7fb1b11 |  | checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
checkpoint-status | 6b266bcb-315d-4ba1-a3ab-409bf60beaef |  | checkpoint | Lagging installed and neat
checkpoint-status | e2146b91-d1bd-418d-9007-67edae83584b |  | checkpoint | Labels installed
checkpoint-status | 11c031fd-aec6-48ee-a7c0-254567bdd0f2 |  | checkpoint | Correct valves fitted correctly
checkpoint-status | 9377286a-025d-49a3-9f1d-e16f89b14a61 |  | checkpoint | Seismic bracing completed
checkpoint-status | ca3f3b37-0c86-4018-ade2-e0db296f87d8 |  | checkpoint | Tested
checklist-flat | 3010756a-b0dc-49d1-b919-6cfa33db2997 |  | checklist | Pre-line Inspection |  |  |  |  | Yes | SYS QA - Pre-line Inspection | 0a5b4c20-04c2-4fed-8688-9dd259ffe9c7
checkpoint-status | 732731e1-3086-4a1e-a28a-12e7510d4354 |  | checkpoint | Nogs in correct Location
checkpoint-status | 4fa6e126-26da-4290-bf19-7841abcf4d19 |  | checkpoint | Cylinder seismic nogs in place
checkpoint-status | 9eea4ac3-8529-43b3-aeba-6da00b12a933 |  | checkpoint | Vanity, shower, toilet nogs
checkpoint-status | 4579f3cb-978c-477a-bbfa-c985f1de8cb4 |  | checkpoint | Shower mixer - Depths allowance for tiles, nogs square to wall
checkpoint-status | f15a2d61-b232-4ae9-8406-3dfe586acdc9 |  | checkpoint | Mixers straight
checkpoint-status | efc239d6-6c57-4510-a6fb-9cbd5e8e3cb9 |  | checkpoint | Vanity Wingbacks
checkpoint-status | 43b59bad-ff04-4638-8c3e-b2901c09fa47 |  | checkpoint | Outlets straight
checkpoint-status | 58ae99ea-3343-4a32-90b6-dceea3d449fb |  | checkpoint | Outlets correct length
checkpoint-status | 4da3e67f-d133-4322-9f99-b462ff0aac49 |  | checkpoint | HWC water feeds
checkpoint-status | 6bfda8f0-796e-482a-9192-ddc010f60a0d |  | checkpoint | Capped Off
checkpoint-status | 026bc1ea-25c6-4185-8af2-196bd1f713d2 |  | checkpoint | Rubbish removed
checkpoint-status | 8b3e51c2-adad-408d-9e29-00e2143fa396 |  | checkpoint | Protective covers in place
label | b1038ee6-f12a-599c-ad74-dc57d93388c9 |  | note | Attach photos of completed area
checkpoint-status | 403deac7-c60c-4f0d-b259-420efa879791 |  | checkpoint | Pre Line Inspection Passed - Foreman
holdpoint | 77a2e51f-c428-4b98-aac8-16dc2f2ffde7 |  | signoff | Add Signature
checkpoint-status | e262a3f2-fcab-44f2-85c4-410110cf087f |  | checkpoint | Pre Line Inspection Passed - Witness
holdpoint | 93cd0fca-c01b-4a70-98b7-fcd8641bc568 |  | signoff | Add Signature
checklist-sectioned | 424ba421-8203-4040-b74b-6de90e2f86e8 |  | checklist | QA - Basement Underslab |  |  |  |  | Yes | QA - Basement Underslab | 1cf13880-f235-463f-ac0a-382ba770d710
checkpoint-group | d4b2d9dc-3b6b-4ef8-b35a-05d65ee8faeb |  | section | Area Prestart / Acceptance & Drawings
checkpoint-status | b55346b9-266e-4110-8f60-c64778b82a50 |  | checkpoint | Area ready for works (grids setout, area accessible and approval to start)
text | fe971271-d59b-51d9-a047-f51bd3297a41 |  | textbox | Zone / Area
checkpoint-status | 260cb85b-583a-4ef6-aadf-eb1ad83a829d |  | checkpoint | Current Dimensioned Slab Set Out Drawings numbers and revisions recorded
checkpoint-group | 93fcbf85-fd0a-4443-83a2-e733b7974a72 |  | section | Under Slab Pipe install
checkpoint-status | 375c5757-1681-418f-b4ec-23d06b42ec0a |  | checkpoint | Correct pipe laid to specified level and grade (all joints sealed correctly as specified)
text | f2c4784d-7950-53db-aa65-e84274055b64 |  | textbox | Zone / Area
text | 179f051a-61b0-5b5f-b0e0-52511edbca73 |  | textbox | Start Invert
text | 813ba7ee-5381-5597-a64a-e814d829845d |  | textbox | Finish Invert
text | 3073de31-c9e5-551c-8080-4f183306262b |  | textbox | Grade of Pre-Line %
text | a2a88a48-c37d-5912-821b-e8d5009333ee |  | textbox | Product Type
checkpoint-status | 776dd2a6-e4c4-4eb5-9d1a-a6a1bed0307d |  | checkpoint | Pipe supported
checkpoint-status | 534a4487-87bb-4aac-8a78-5d8de62bd5b3 |  | checkpoint | Install Tests completed, reviewed & approved
text | c729e1a1-e9a8-5f77-8180-1a26e21c8705 |  | textbox | Test method used
text | 44e49fb2-2e38-5cf9-be2f-6d85df223849 |  | textbox | Duration
checkpoint-status | 5b12e29b-5b02-4e74-b94a-52e480864477 |  | checkpoint | Local Authority Inspection Passed
text | 9022100f-a588-5197-b4de-ce3206ba1a14 |  | textbox | Witnessed by
text | 28918296-fcb9-5bfb-9260-a9b8a1099328 |  | textbox | Representing (Company)
text | d441291b-c955-5904-9ab2-cb526376540e |  | textbox | Date
holdpoint | 7381a86b-da22-4c0d-ae59-40ddf340ef13 |  | signoff | Signoff required
checkpoint-status | eac979ee-8d3b-4aab-a301-461060db1ed4 |  | checkpoint | All relevant test plugs removed where applicable
checkpoint-status | c94b73f4-df91-410e-96f7-aab29d5fe2d3 |  | checkpoint | Open ends sealed
checkpoint-status | 89fce0ff-9a00-4b36-ae7c-302a54de138a |  | checkpoint | General photos, comments and observations
checkpoint-status | c74cbd42-6c71-4292-94eb-53eeb206cc7e |  | checkpoint | Pipe Laying Completed
text | 2c18e22a-780c-5a4f-8d6b-efca62c15b0a |  | textbox | Laid by
boolean | f5daecaa-6efb-5ba0-a005-247b9cb094e6 |  | tickbox | Bedding Sound
boolean | d332f559-eede-5708-9fb8-7d1ac01072e9 |  | tickbox | Soil Removed
boolean | c58550a6-2865-5b4e-9462-21dd1f940d53 |  | tickbox | Trench Compacted
boolean | e6218213-1ad4-511b-b808-20afc20ff764 |  | tickbox | Hard Filled
checkpoint-group | 60de64d5-2ca9-433d-9d50-ba6ed045fccb |  | section | Area Completion/Signoff
checkpoint-status | 34d3714d-f97b-42c4-bfd7-4ce800615ee9 |  | checkpoint | Specified Protection Around All feeds/pipes penetrating slab
checkpoint-status | 4f259aa2-8ee5-4bb0-a0a3-f76d1eafea56 |  | checkpoint | All Measurements Double Checked
checkpoint-status | 1fa6a279-5827-4264-8515-a4576845ca9b |  | checkpoint | As-Built Drawings recorded (drawing & revision number(s)
checkpoint-status | 9728a59d-3505-4bd3-8780-9a5ba6f637a6 |  | checkpoint | All relevant under slab works completed, reviewed and approved
text | 22dcced0-a05c-5b51-a72a-0f213acc20e1 |  | textbox | Completion Date
checklist-flat | c36a3052-b1b9-4f28-869a-0bf32c654ecf |  | checklist | Testing - Waste / Stacks |  |  |  |  | Yes | Testing - Waste / Stacks | 26fad855-cac6-4100-a384-112f715aa8cf
checkpoint-no-status | b9bc5a36-59bb-42d9-bceb-9a356bf8f827 |  | checkpoint | Details
text | 7f015a7b-6af4-5bea-8ff1-fdd5423fee4b |  | textbox | Zone / Area
text | c9cfe8fc-d559-5652-91a1-418d08a230e7 |  | textbox | Area / Stack
checkpoint-status | 1704e3a5-d31b-40fe-83a3-d32e5e63dbf3 |  | checkpoint | Flood Test in accordance with ASNZ 3500 (15.2)
text | 90eee7f3-8245-5db9-a052-9b6b45ece6f8 |  | textbox | Duration
text | dd645640-cb65-526d-b29a-ab60ed8daee3 |  | textbox | Notes
checkpoint-status | 974a3827-e96e-4f87-9a8c-18c68729c09b |  | checkpoint | Install Tests completed, reviewed & approved
checkpoint-status | 615a62df-5b22-442a-92aa-9bfe59b34f4d |  | checkpoint | Local Authority Inspection Passed
text | 55505fc4-00d2-545c-8d71-f1570d39a130 |  | textbox | Witnessed by
text | 8386b781-8985-5e4f-b2a0-23ba4ace0e6e |  | textbox | Representing (Company)
text | 7757a3a4-b4c0-59cc-8148-23333e1bd7c2 |  | textbox | Date
checklist-sectioned | 51bcc71c-6e0b-4795-bf8c-7452c533d5c7 |  | checklist | Basement Underslab |  |  |  |  | Yes | SYS QA - Basement Underslab | 3cba7a74-d9b0-49b3-a7e8-0c96f0341227
checkpoint-group | ab020846-d081-4a24-9249-c826fe0d4b1a |  | section | Area Prestart / Acceptance & Drawings
checkpoint-status | 8b198ca9-bc71-4a21-a05a-628b9bd6a888 |  | checkpoint | Area Prestart / Acceptance & Drawings
text | ed4e56f7-77b5-5e66-aa8b-6c3f759521e6 |  | textbox | Zone / Area
checkpoint-status | 75cf252c-53b5-4eea-aa4a-284224f6c84b |  | checkpoint | Area ready for works (grids setout, area accessible and approval to start)
checkpoint-status | 971ff774-22cd-47c4-ad91-f8da8817a3b2 |  | checkpoint | Current Dimensioned Slab Set Out Drawings numbers and revisions recorded
checkpoint-group | 1973fc76-9068-4c82-b3a7-85e183025c71 |  | section | Under Slab Pipe install
checkpoint-status | fde7bd53-0e9e-40b9-9e18-5d5c9353705e |  | checkpoint | Correct pipe laid to specified level and grade (all joints sealed correctly as specified)
text | 22616ec6-4444-5dee-b790-e645c9791fa5 |  | textbox | Start Invert
text | 73217ffa-076e-5801-a646-d3045abcf15b |  | textbox | Finish Invert
text | a9370626-7d8b-5fb5-81f9-b3dab3af39fb |  | textbox | Grade of Pre-Line %
text | 862ab7bd-0769-5439-b2d8-89f76facb138 |  | textbox | Product Type
checkpoint-status | f9403331-c7ed-41ae-85cf-b0a260d997d5 |  | checkpoint | Pipe supported
checkpoint-status | 133b959a-b263-4e0e-9789-e3117feb0abb |  | checkpoint | Install Tests completed, reviewed & approved
text | 81ad1883-3298-56e8-b502-23f89ba20ab7 |  | textbox | Test method used
text | 04df1b75-80f6-55c2-89fd-62f0c471fc25 |  | textbox | Duration
checkpoint-status | d974dc98-f739-48ab-8999-7243b83a9f06 |  | checkpoint | Local Authority Inspection Passed
text | 761394e7-27a3-5e35-8462-498938cbb3d0 |  | textbox | Witnessed by
text | 831c74a4-e265-5a2b-909e-87bcc1df6378 |  | textbox | Representing (Company)
text | 1110655e-5765-5ace-8732-d5f444408be8 |  | textbox | Date
checkpoint-status | efbddd73-4c33-4a12-814f-82f2f02ad25d |  | checkpoint | All relevant test plugs removed where applicable
checkpoint-status | 631f1bb2-bf20-488e-94c2-84e928632737 |  | checkpoint | Open ends sealed
checkpoint-status | fbb01af4-d03c-4462-9186-dc1e6036575d |  | checkpoint | General photos, comments and observations
checkpoint-status | 842c5a37-705a-4572-9abc-f6b5360a9250 |  | checkpoint | Pipe Laying Completed
text | 5e2949ae-6bc3-510c-ab3d-8ef04ef5f987 |  | textbox | Laid by
boolean | 70bcc76a-1bc1-5923-bcff-957046124718 |  | tickbox | Bedding Sound
boolean | 9a830648-8b2a-585a-a1e1-ae1d7be35859 |  | tickbox | Soil Removed
boolean | f0feb51d-34a7-556a-b19d-5326c89ee677 |  | tickbox | Trench Compacted
boolean | 1f0457b3-b762-512f-976a-ef2af13284c3 |  | tickbox | Hard Filled
checkpoint-group | 99bf0c29-e6cf-4d8d-a58b-91448c44351e |  | section | Area Completion/Signoff
checkpoint-status | 8055ac12-e201-4970-a84a-9a52e759b30d |  | checkpoint | Specified Protection Around All feeds/pipes penetrating slab
checkpoint-status | 62a19c9a-7dd2-4150-993c-de4101983636 |  | checkpoint | All Measurements Double Checked
checkpoint-status | e41370f1-6a03-449b-80ed-5e087d4d63eb |  | checkpoint | As-Built Drawings recorded (drawing & revision number(s)
checkpoint-status | 4bd1ee7b-eab5-4608-bca2-5ebf996d4a16 |  | checkpoint | All relevant under slab works completed, reviewed and approved
text | 40fcf283-3878-5d38-aa1a-f5e5111af5e0 |  | textbox | Completion Date
checklist-sectioned | 660e1cf1-78a6-41cd-9683-2ae465676935 |  | checklist | QA - Cold Water Booster Pump |  |  |  |  | Yes | QA - Cold Water Booster Pump | 59762f5b-a700-4d52-a100-abe5ca09d0aa
checkpoint-group | ac522fe8-af70-4b2f-abfc-31d4cc5ea5fe |  | section | Zone / Area
checkpoint-no-status | c6cfa678-9ce5-460d-9340-3b7e2b0b6885 |  | checkpoint | Details
text | 2c7cc425-a1ee-5ee1-a66c-fd7c74e27178 |  | textbox | Zone / Area
checkpoint-group | 176d107d-6c2e-40f3-a88c-273fe52aadad |  | section | Pumpset manifold
checkpoint-status | 42d58baa-3f50-48b3-b3d9-faa9ea6bb441 |  | checkpoint | Connections welded correctly
checkpoint-status | 5a406584-0553-4019-931d-7f61de949883 |  | checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
checkpoint-status | 8b9215ea-625e-42a8-b4f3-b943d8fa4d8e |  | checkpoint | Valves fitted correctly
checkpoint-status | d93790c6-16c7-4441-bec0-b6c66d9eb8df |  | checkpoint | Line strainer fitted between pump & tank
checkpoint-group | 1ae81dc2-a63d-4bbb-9fcd-76fa7dc4e74f |  | section | Pumps
checkpoint-status | 71f2d33b-b515-47ef-953b-7b72621f1e37 |  | checkpoint | Pump 1 Startup KPA
checkpoint-status | e7343096-18ef-439f-ba67-3cd5f959b946 |  | checkpoint | Pump 1 kick out pressure KPA
checkpoint-status | 336b0f55-82d7-45fc-89a5-be04e4f820cf |  | checkpoint | Pump 2 Startup KPA
checkpoint-status | 5a3ffc3b-24e7-428c-853b-f6f572175ada |  | checkpoint | Pump 2 kick out pressure KPA
checkpoint-status | c4e8bbbd-7ed6-46c9-82e3-12783d62caa8 |  | checkpoint | Pressure vessel pressure
checkpoint-group | ab73e294-fbe6-420d-8973-a19c33838176 |  | section | General
checkpoint-status | 8818378b-1892-4baf-ab63-8bf136002368 |  | checkpoint | Mains water change over
checkpoint-status | 7bfbc366-cf3e-49b3-b15f-7d3ec0f67467 |  | checkpoint | Flow test pump
checkpoint-status | 25753812-522e-4384-a91b-73e04f517e3a |  | checkpoint | Pressure tests pipework
checkpoint-status | 1dece72f-03b6-400e-95c1-7e5ae7e792a1 |  | checkpoint | Visual check (for leaks form valves, tees, saddles, etc)
checkpoint-status | 1fb6e68d-0367-409b-8229-b8d6706eb3bc |  | checkpoint | Non return valves fitted
checkpoint-status | e7534321-284b-4f6d-8f7e-183196186a1d |  | checkpoint | Installers name & date works completed
text | f332bd58-ac3a-5111-98b3-e323f14d52f2 |  | textbox | Installers name
text | 92eff766-75b5-5332-9911-f2232ad12b2d |  | textbox | Date:
checkpoint-status | 2bccd6d0-e50f-49e8-a8ca-bd73b4e4d34b |  | checkpoint | Tested by & date
text | cbafc0c4-704c-529b-81d3-a77eb43992e2 |  | textbox | Tested by:
text | 98dd32a4-5bf5-5ef4-9587-a27547d19f76 |  | textbox | Date tested:
checkpoint-status | 0ec103d9-2a37-45ed-8c67-d86bc997ad75 |  | checkpoint | Council inspector sign off and date
checklist-sectioned | da481583-a777-42fc-9bd4-c682d6f439b3 |  | checklist | QA - Sump Pump |  |  |  |  | Yes | QA - Sump Pump | 643fc55a-c93e-4157-9077-0088d064f67c
checkpoint-group | 4e187d02-5679-45d7-b201-8b0dcdb4e65c |  | section | Unit check
checkpoint-status | db9e486d-27b2-4fdc-86b1-cd1bd14583d1 |  | checkpoint | Area acceptable and ready for work to begin
checkpoint-status | ced0ff8d-e4b7-4105-b54f-8b5076f43619 |  | checkpoint | Pump mounted on base, & housing condition good - no leaks
checkpoint-status | f811127f-abea-4f26-992c-ce80597bf31e |  | checkpoint | Alignment checked (field alignment performed where required)
checkpoint-status | e3213841-4218-4e14-8d1a-3e1e8d97edc9 |  | checkpoint | Pump impeller works correctly
checkpoint-group | a8294046-9b95-461f-bd96-6b8221fa5013 |  | section | Pipework
checkpoint-status | 1a25c4b6-1e02-484d-a50e-5f37193701e6 |  | checkpoint | Strainer installed & cleaned
checkpoint-status | 711144d8-622c-4c6e-8e23-8a2f320418e0 |  | checkpoint | All isolation valves set correctly - non return valve, isolation valve
checkpoint-group | dc9a84b9-0574-4372-996d-3ef97d1a1359 |  | section | Electrical
checkpoint-status | 405ba3b1-192d-465b-8817-76557e9cc365 |  | checkpoint | Local isolator located
checkpoint-status | c4be4b3a-b29a-4471-9076-1ca5eec279fc |  | checkpoint | All power and control wiring correctly installed
checkpoint-status | 4f539931-0cc2-453c-a189-7bbb9221dd23 |  | checkpoint | All electrical connections correct and tight
checkpoint-status | bc76df6c-7702-4cec-8b61-da250225d0d5 |  | checkpoint | Controls point to point check completed
checkpoint-group | 200b050a-5246-4174-a4ff-75b82a3626c8 |  | section | Float levels
checkpoint-status | c3856818-54e3-4236-9552-f1937acca2f6 |  | checkpoint | invert - low level alarm
checkpoint-status | 4d54101b-ab0a-42e9-ab57-1525fabb9e7b |  | checkpoint | invert - mid level for dual pump operation
checkpoint-status | f9b33284-102f-43aa-a84f-0b4f7ce937b4 |  | checkpoint | invert - high level alarm
checkpoint-status | df1bb515-d6b1-4f7d-a8ce-771287715fcd |  | checkpoint | Rail / lifting chains installation
checklist-flat | d2780388-ec9b-4614-9a8b-ef24d562c162 |  | checklist | Hotwater Plant, Pumps & Tempering Valves |  |  |  |  | Yes | SYS QA - Hotwater Plant, Pumps & Tempering Valves | 64867fbb-eb46-4078-8cc7-8aae1152a21e
checkpoint-status | 5f103dfc-b661-4d68-9ae6-5c55ed314a00 |  | checkpoint | Flush all lines and strainer including rinnais
checkpoint-status | 0491497f-620b-4663-9ca6-ec5970526732 |  | checkpoint | All safety valves installed
checkpoint-status | 6dff967e-5d60-4feb-bf07-38b9773bd064 |  | checkpoint | Seismic restraint fitted
checkpoint-status | e3f4d1c8-e7e2-48a0-afa3-73e6ea29f448 |  | checkpoint | Check condensate drains from Rheem gas boilers
checkpoint-status | eebd10b3-a9da-4f95-95e4-e4a0f36e4a16 |  | checkpoint | Check All Connectors For Leaks
checkpoint-status | 8b0948e9-49cf-45ed-8c8a-66a402d8a4aa |  | checkpoint | Check all valves and connections for leaks
checkpoint-status | 88d93ef2-c27b-4e63-a54f-fc755620a633 |  | checkpoint | Operate cold water expansion valves / check operation
checkpoint-status | afaa3a4b-9208-4445-961c-00c660228264 |  | checkpoint | Set limiting valve
checkpoint-status | 63ded34c-97cd-49b7-afff-5a67328a4643 |  | checkpoint | Test TPR valve
checkpoint-status | 6960542a-438e-464f-9670-c771b053e333 |  | checkpoint | Check for crossovers
checkpoint-status | c3d289e0-c6c7-4889-a8fb-1dabddc9e034 |  | checkpoint | Check HWC For Correct Valve Installation
checkpoint-status | 1ced6cda-ee5e-4579-bdcc-4e786c55a96d |  | checkpoint | Lagging completed
checkpoint-status | 6808ca1d-145d-438d-882d-ec0c441e3510 |  | checkpoint | Check All Hot/Cold Pipes For Correct Position
checkpoint-status | 4eb03123-3b8a-4971-ad22-f46498ce4b0e |  | checkpoint | Set tempering valve temperature
checkpoint-status | e83ba6f5-1287-4039-ab98-b2aa5a9c8f5b |  | checkpoint | Set Rheem gas water heaters
checkpoint-status | d914d962-2acb-4da4-8cd0-71aca970234e |  | checkpoint | Set thermostat temperature
checkpoint-status | 830d1bd6-2503-4bdf-ac18-40d1b1795d83 |  | checkpoint | Set Bleed air from primary pumps
checkpoint-status | 1337c778-7a2f-4057-8edc-d3a047a09a1d |  | checkpoint | Bleed air from circulating pump
checkpoint-status | 8472f4b3-89b4-4195-bd7b-7767f54807e7 |  | checkpoint | Set all return thermostatic balancing valves
checkpoint-status | d017bff7-22a6-4c07-9a6b-c28ad0731ef6 |  | checkpoint | Test gas for soundness & check working pressure
checkpoint-status | c6021ee9-6318-493d-94e7-62cb8ce626e4 |  | checkpoint | Water temperature in Hot water cylinders
checkpoint-status | ed9e5eda-e134-499e-9e0c-3821961dae20 |  | checkpoint | Installers name & date works completed
holdpoint | 6aa6b3fd-5392-4d75-a2d1-10e14a8cd03d |  | signoff | Request Signoff
checklist-flat | fbfadf14-fd0d-4772-9a3e-bb02429e601e |  | checklist | Testing - Cold Water Main |  |  |  |  | Yes | Testing - Cold Water Main | 6b054c7d-e84b-41d6-81cb-b3dd7b5e3a0d
checkpoint-no-status | 1a57f22c-0858-4b1b-a477-7ec3cdf03222 |  | checkpoint | Details
text | 8f1508c8-4d9e-5e3e-b0fa-7edc1acedf28 |  | textbox | Zone / Area
checkpoint-status | e715a14c-4e4e-4137-9339-46a95ff5c38a |  | checkpoint | Pressure 1500 kpa or as per spec
text | f5a11110-6196-5412-aa78-0c2aaded07de |  | textbox | Duration
checkpoint-status | b46f5a6f-6aba-4293-8db8-bd724a1543ad |  | checkpoint | Visual check (for leeks form valves, tees, saddles, etc)
label | d16cf25e-3453-5e80-89f5-e63e91e8905b |  | note | Attach photos of completed area
checkpoint-status | 3c31b0f5-f15a-4314-b2f8-65598310b9af |  | checkpoint | Pre Line Inspection Passed - Foreman
checkpoint-status | a6b2800d-d9bd-442f-b3e2-6e6593df5f13 |  | checkpoint | Pre Line Inspection Passed - Inspector
checklist-flat | 43dd81a0-6262-43b4-a7c8-06e26e38d09c |  | checklist | Test and Comission Waste |  |  |  |  | Yes | SYS QA - Test and Comission Waste | 6fb612af-8360-422a-8e6b-079075e3d4fa
checkpoint-status | 30a2467d-2c9c-4e08-bcc0-f870a4563ead |  | checkpoint | First Fix
checkpoint-status | 81087f9c-9ce5-4239-b59c-22ae2ca264de |  | checkpoint | Waste Pipeout complete
checkpoint-status | f8865e82-dc30-4805-b58e-89fe581188d0 |  | checkpoint | Vent installed
checkpoint-status | fc9c2fb0-3d3b-4ef6-8edb-597c2135606a |  | checkpoint | Correct Fall
checkpoint-status | 2c2a9a96-1653-4707-bc34-ee58e5e092fe |  | checkpoint | Correct Clipping
checkpoint-status | 7b90d651-50fb-4871-9fe7-f1e04b389982 |  | checkpoint | Flood Test in accordance with ASNZ 3500
checkpoint-status | 4312bd3a-204b-4914-bf40-dfec78ae38be |  | checkpoint | Hydrostatic test Plug Removed
checkpoint-status | bf4138aa-fe96-4671-96f7-e5f777af6396 |  | checkpoint | Inspection Cover Replaced
checkpoint-status | d5f5ab16-3b75-422a-b394-253a20bd43f0 |  | checkpoint | All pipe stubs & FWG's covered
checkpoint-status | 97d52e80-9e6e-44d4-b8c7-05b0155e0904 |  | checkpoint | Visual check & photos attached
label | 0e163a2e-84a7-5a80-8b51-c7004b67f7a5 |  | note | Attach photos of completed area
checkpoint-status | a7ec07b2-bc20-4e9c-885d-7c5b99ba4f92 |  | checkpoint | Pre Line Inspection Passed - Foreman
holdpoint | 23021423-6698-4b72-aad4-afc13553c3fd |  | signoff | Add Signature
checkpoint-status | def54814-cf39-44b6-920c-7a176b3ee6cd |  | checkpoint | Pre Line Inspection Passed - Witness
holdpoint | 7d07bc16-137d-4d10-bab7-19dcc9f5a4d9 |  | signoff | Add Signature
checklist-flat | 1ffae3a2-796c-438d-a1a9-93cd3ec7755f |  | checklist | Gas |  |  |  |  | Yes | SYS QA - Gas | 8500c7ba-f45e-4ca1-985f-e2c58476e8f5
checkpoint-status | 7a6a379c-8b0f-4598-831d-32bc0b8e8bd6 |  | checkpoint | All fittings scrapped correctly
checkpoint-status | 01415b23-714f-4150-a980-266f1a7181c9 |  | checkpoint | Iso used on fittings
checkpoint-status | 7bce014a-8b94-463a-b960-8451bac8de4e |  | checkpoint | Valves fitted correctly
checkpoint-status | adb5a224-773f-4419-9104-338057471179 |  | checkpoint | Fititngs welded & weld indicator has popped out
checkpoint-status | b9c44f1d-d5a7-4070-b366-62aaa70c8558 |  | checkpoint | Trace wire and ID tape installed
checklist-sectioned | b1b34a84-6781-4d60-87fc-e9dfd09b2fe0 |  | checklist | Waste / Stacks |  |  |  |  | Yes | QA - Waste / Stacks | 8806a1d5-212d-4aff-883f-014fb83949fd
checkpoint-group | 9640aedf-c3cb-4ff4-bed5-ac57b2ecd390 |  | section | Area Prestart / Acceptance & Drawings
checkpoint-status | 95f62047-a266-433c-ace1-61e57ac1ea64 |  | checkpoint | Area Prestart / Acceptance & Drawings
text | 6a93b62a-82e2-5702-b3dd-729b69b91a28 |  | textbox | Zone / Area
checkpoint-status | 7c7f8cc6-ab25-4c75-b483-52d93031088f |  | checkpoint | Area ready for works
checkpoint-status | 43ba8f6a-bed0-4275-a80c-5c136f805975 |  | checkpoint | Current Dimensioned Slab Set Out Drawings numbers and revisions recorded
checkpoint-group | ec152346-08ac-4e44-beba-0851198190fe |  | section | Pipe install
checkpoint-status | 7f99b52d-a19d-4ca0-b47f-1042f9b48494 |  | checkpoint | IE's - Test points installed correct locations (ASNZS 3500)
checkpoint-status | 8745e4a5-a1c6-4965-a44e-c1396583b2a6 |  | checkpoint | Pipeout completed
checkpoint-status | 3cfa0eb3-d187-4dd3-918f-86e98a016ec8 |  | checkpoint | Correct labels
checkpoint-status | 4c940b8c-1d80-43ca-8546-441c8c405718 |  | checkpoint | Acoustic lagging
text | b0f4d7fa-0ce7-55eb-a5f7-1e6bf49bc478 |  | textbox | Product Type
checkpoint-status | 33b180f4-2298-4e0e-84f2-e7f2d53edb70 |  | checkpoint | Correct Pipe supports completed
checkpoint-status | 6add2362-ed3f-4709-9454-bdc740ebaed2 |  | checkpoint | Seismic bracing completed
checkpoint-status | 72195271-7a5c-4e78-b27f-add0e444a465 |  | checkpoint | Vent installed
checkpoint-status | f6fa8e6f-d9ee-4c0f-adfe-fcf520005320 |  | checkpoint | Correct fall
checkpoint-status | ed5f2229-053e-48f0-b49b-6023b3c15967 |  | checkpoint | Flood Test in accordance with ASNZ 3500
text | e140adfd-b7f2-5d3e-aa5f-569b1c3cc208 |  | textbox | Witnessed by
text | bcd9e8b9-8131-5171-995e-3f0b398b39f7 |  | textbox | Representing (Company)
text | ba0d7846-7b70-5872-acb4-668baab7f96a |  | textbox | Date
holdpoint | 9abaf43c-d1e5-40b9-8048-d4daf5d1b375 |  | signoff | Request sign off
checkpoint-status | a1ca6039-2e13-4c36-87ed-1e2ac75b9f17 |  | checkpoint | All relevant test plugs removed where applicable
checkpoint-status | efc0c9d5-8e2c-44ee-b98b-1f1fc8bc76e1 |  | checkpoint | Open ends sealed
checkpoint-status | 08f96971-5aba-4f1f-ab04-8dfbf7efddde |  | checkpoint | General photos, comments and observations
checkpoint-status | f3b2ca5b-1973-4339-8678-9b2aaafff154 |  | checkpoint | Pipe Install Completed
text | 9a23741a-036e-52a3-aa33-32a48a614101 |  | textbox | Installed by
holdpoint | a5ac6bc7-a488-413b-b811-8b4c8ae71175 |  | signoff | Add Signature
checklist-sectioned | 5894eb5c-9637-4b5f-ad15-9e7830f5a4d5 |  | checklist | Test and Comission Water Supply |  |  |  |  | Yes | SYS QA - Test and Comission Water Supply | 91895969-6561-4062-8154-6155dbf5d18e
checkpoint-group | 4e5ef6d9-e1b8-451a-a5ac-30252ea50789 |  | section | Water Suppy
checkpoint-status | 9504a35d-6e86-41e1-b158-1a0adb57cbd3 |  | checkpoint | Pipe Work Secured in ceiling
checkpoint-status | e767df9d-4fa9-42d4-bd58-4b58765dfdc4 |  | checkpoint | Pipe Work Secured in wall
checkpoint-status | 7abf7f65-2efc-4ff1-83eb-9c9c9f6d4fd0 |  | checkpoint | Pipe Work Siliconed
checkpoint-status | 0fe1b868-ab40-4203-8374-3e9d47c8e88d |  | checkpoint | Check for Crossovers
checkpoint-status | 706673eb-57de-4e0d-993e-787a81d10ea8 |  | checkpoint | Pressure Test 1500 KPA or product/job spec
checkpoint-status | 8aab60c0-082d-4a08-9e72-1c085527069d |  | checkpoint | Visual check & photos attached
checkpoint-status | 1c950e3b-7528-4b58-92e2-a84535134e78 |  | checkpoint | Check all joints
checkpoint-status | 5b514d5f-798c-414d-9215-137f2ec3adb5 |  | checkpoint | Shower/bath outlet Crimp
boolean | 9c4d884d-e5c7-5bba-be92-31de8fc4bb3c |  | tickbox | photo uploaded
holdpoint | dfd7feb8-852f-43be-bcf1-3cee50614e85 |  | signoff | Request Signoff
checklist-flat | 3bbafe88-bf8f-420a-9d78-5c7ff78bbbd9 |  | checklist | First Fix Apartments |  |  |  |  | Yes | SYS QA - First Fix Apartments | 98a9e451-5d4a-4a8c-b175-74280d6fdb62
checkpoint-status | 6795ddbb-3339-4810-bd58-b1d27beb0217 |  | checkpoint | PVC stack complete
checkpoint-status | d5257225-cc24-4a02-8ac6-9330cf293001 |  | checkpoint | Toilet, shower and basin waste connected to stack
checkpoint-status | f7abcd93-c009-4036-898e-0de5c39ef0b2 |  | checkpoint | A/C drain connected
checkpoint-status | 8699c283-518c-48c9-a1ff-3e6de0943c27 |  | checkpoint | Shower flange installed
checkpoint-status | ed34dd7d-7688-4d6e-827c-9e2a8c9d5641 |  | checkpoint | PVC stack flood tested
checkpoint-status | 585c3511-0f4f-450c-b119-f1a941089ced |  | checkpoint | Water to toilet
checkpoint-status | 921c1e44-6053-415d-b81e-0dffe74bee21 |  | checkpoint | Water run to toilet and basin mixer installed
checkpoint-status | bc22f166-0a92-41f2-a42b-fb248ab81fe3 |  | checkpoint | Water run to shower and shower mixer installed
checkpoint-status | e3804b50-f2aa-44ab-b902-f2ed75af4f05 |  | checkpoint | water supply run to slide shower - Outlet crimp photo loaded
checkpoint-status | 11d67dc9-9c04-4505-9bcf-df11dc8443d9 |  | checkpoint | All pipework clipped and siliconed where it runs through walls
checkpoint-status | 2c6786a7-dd87-4faf-978b-1e0cfcee22e8 |  | checkpoint | Check All Hot/Cold Pipes For Correct Position
checkpoint-status | 813057d2-35c3-4f5d-8021-8085123cad32 |  | checkpoint | Acoustic lagging where required
checkpoint-status | 42d5b5af-7116-44bb-86ef-5a89fbf610aa |  | checkpoint | Thermal lagging to hotpipes where required
checkpoint-status | 30b59334-ada7-4083-a374-0f1063c22803 |  | checkpoint | All rubbish removed and and material back in storage
checkpoint-status | f66426d6-8db2-427f-83d6-74ff7ab7874d |  | checkpoint | Check no 1st fix clashes with 2nd fix fixing screws
checkpoint-status | a8467a68-d373-4c3d-bd61-627e07dcc317 |  | checkpoint | Check all nogs are installed
checkpoint-status | ce07d5d8-5b0f-43e4-9c74-58b1cbf255a3 |  | checkpoint | Installers name & date works completed
holdpoint | 7dbcc9e8-1557-4816-b5d6-3da81e10d317 |  | signoff | Request Signoff
checklist-sectioned | dc7915a2-077d-454b-9d73-0c9f9d73b754 |  | checklist | First Fix Plumbing - Water & Waste |  |  |  |  | Yes | SYS QA - First Fix Plumbing - Water & Waste | 9c5bc559-cd4b-45df-8aab-ab984634f5d0
checkpoint-group | 24e62dc9-e698-412f-8d1b-6bb0ae8f6dd1 |  | section | Bathroom
checkpoint-status | 901ceca1-1be6-4c69-9e83-f68c578685ac |  | checkpoint | W.C Supply
checkpoint-status | dd700d2b-d172-4bf1-9b3b-0d5c93e2428f |  | checkpoint | Shower waste
checkpoint-status | dc290834-2459-46e7-ac2a-2409ebdf7a91 |  | checkpoint | Shower mixer/check depth
checkpoint-status | 7f560592-cfa0-4963-9abd-20717cca7575 |  | checkpoint | Toilet waste
checkpoint-status | e02e0a2f-ab9f-4d43-9308-bda789d551b1 |  | checkpoint | Vanity Waste
checkpoint-status | f2ede6a5-deb3-48df-873d-ee4097a595ad |  | checkpoint | Vanity Wingbacks
checkpoint-status | 6802aa23-cacc-459d-b333-2894ac00f9d4 |  | checkpoint | Vanity, shower, toilet nogs
checkpoint-status | 4f772ab6-9290-4426-bf5d-b780f07c77f0 |  | checkpoint | Bath mixer where applicable
checkpoint-group | 5fbbd9f9-de2f-4444-863c-5d75dc98afdc |  | section | Laundry
checkpoint-status | fe2e9f43-2e78-4ed2-8822-5aa07175bbd6 |  | checkpoint | Hot and cold water
checkpoint-status | 6617f16d-aff9-462a-b0e0-1c53342e8354 |  | checkpoint | Waste pipe
checkpoint-group | 51bda0f3-de0f-4ed6-a896-6f75c3178dd4 |  | section | Kitchen
checkpoint-status | fdb4335a-abb0-4bd3-829d-844b86145866 |  | checkpoint | Hot and cold water
checkpoint-status | a0c9a895-a9c6-4eb7-89c0-68bdc5c99824 |  | checkpoint | Waste pipe
checkpoint-group | a6d3c8e0-d99b-4e69-a374-30f2cd424149 |  | section | Balcony
checkpoint-status | 64bb0d96-7c12-427e-992b-8ac14646aed4 |  | checkpoint | Balcony drains & pipework installed/correct screws in flange
checkpoint-status | 8d009185-1bb2-4a8d-8ac2-08ef9f8ce092 |  | checkpoint | Correct screws in flange
checkpoint-group | 8331a835-1c80-4b3e-8f66-2369bfd2cbf0 |  | section | General
checkpoint-status | 139c5476-fe8b-467e-b539-39f1ecc0401d |  | checkpoint | Pipe Work Clipped
checkpoint-status | e96e2be7-ff06-4ab6-85a3-932606592223 |  | checkpoint | HWC water feeds
checkpoint-status | 21071ced-a976-4c9e-837d-fb931649d20c |  | checkpoint | HWC waste
checkpoint-status | 3f867510-ce28-42f9-a62f-bf0b62422696 |  | checkpoint | HWC nogs for strapping
checkpoint-status | a15213fe-5012-4c97-9ff6-7bd21a0ba4eb |  | checkpoint | Pipe Work Siliconed
checkpoint-status | 009bd25e-884f-46cd-9fa3-294a94f7c917 |  | checkpoint | Capped Off
checkpoint-status | 22a0d4d4-15a8-4152-b06d-6ae33e2f99d0 |  | checkpoint | Check for Crossovers
checkpoint-status | d5b7b97d-71e9-4402-aa85-c7ca10e2ccf5 |  | checkpoint | Double check all sefont of fixtures
checkpoint-status | ec413d46-e535-42ed-a4ce-b4ac11254406 |  | checkpoint | Acoustic lagging where required
checkpoint-status | 7d46728c-5415-4767-a48b-b28c72e5cb75 |  | checkpoint | Thermal lagging to hotpipes where required
checkpoint-status | 3867ef86-dffb-489b-8ba9-72d4f81b20d6 |  | checkpoint | Floor waste flange fitted
checkpoint-status | 7792a94a-2a1c-4387-b682-47ee4136970f |  | checkpoint | Pressure Test 1500 KPA
checkpoint-status | 505886ac-cf9b-4be8-801e-352eb5412157 |  | checkpoint | Installers name & date works completed
holdpoint | 0fd68a51-bc87-45d3-b404-c5ba150ae460 |  | signoff | Request Signoff
checklist-sectioned | b01e60c1-9a25-4ed2-9bcb-481bc04fdda8 |  | checklist | QA - Manhole |  |  |  |  | Yes | QA - Manhole | ab69b988-d324-434c-96de-a51739c7c011
checkpoint-group | cd2d0f23-0313-4f69-92b1-25b57ad723be |  | section | Manhole Install
checkpoint-status | 9a9ad95e-babe-4589-8af0-197600a6d29a |  | checkpoint | Latest consented drawings
text | ac5d452c-831f-55e5-90fb-aa5db08a9778 |  | textbox | Drawing Ref No.
checkpoint-status | 673e8fce-b79b-439b-9783-6b2f5b3d883e |  | checkpoint | Setout Completed checked and accurate
checkpoint-status | fb252221-6eca-43c9-9ee6-9d6f29080156 |  | checkpoint | Excavation Accurate - Location & Depth
checkpoint-status | a9f60bba-d1a3-44fb-a5e4-5cb749168a36 |  | checkpoint | Ground conditions checked & acceptable
checkpoint-status | 41bfe6d7-d700-4f73-a603-84c0aec4ab64 |  | checkpoint | Bedding depth and material correct & compacted
checkpoint-status | 726482fc-2f3b-46d4-a7eb-3252a16a0300 |  | checkpoint | Correct manhole installed to specified height and sitting level
checkpoint-status | b3dbd258-8f05-47a7-9d28-932cf94338ba |  | checkpoint | Manhole Risers Installed (if applicable)
checkpoint-status | 22fc2a2a-ee2c-4371-9208-3cb1aa6f3f9c |  | checkpoint | Joints & connections correctly sealed as specified
checkpoint-status | 5b8dbef9-0c68-44b1-a726-32e9205acc96 |  | checkpoint | Manhole benching completed and acceptable
checkpoint-status | 8a01bda9-8459-4b01-b216-90e91f598eec |  | checkpoint | Concrete Lid Installed and sitting appropriately
checkpoint-status | 85cda6ac-e34c-4f5f-becd-ac83499a5367 |  | checkpoint | Cast Iron Lid Installed and sitting flush
checkpoint-status | e1385bf5-a474-4083-9c58-62679e4a11f4 |  | checkpoint | Signoff on Completed Work (Council etc)
checkpoint-group | 841a941a-06fa-4a97-9e21-b280f7cba024 |  | section | Backfill
checkpoint-status | 5abd5e59-bd34-4911-a79f-1ac7642dc1b5 |  | checkpoint | Backfill methodology and material confirmed
checkpoint-status | bfa94407-370e-4b88-a9f3-affef85184ea |  | checkpoint | Any formwork/ debris removed from area
checkpoint-status | d5c93936-5eca-432d-bd97-de38fc8d6598 |  | checkpoint | Any waterproofing/ drainage / service requirements completed and inspected
checkpoint-status | 45868c17-de55-41a2-bede-e5f99094ceef |  | checkpoint | Approval given to commence backfill - attach any other relevant inspections and observations closed out
checkpoint-status | 0bc6c6b5-c9dc-4e80-8df0-05dc63d19ef9 |  | checkpoint | General photos and observations during backfill
checkpoint-status | fccca367-f228-4953-b936-b12908c54ac6 |  | checkpoint | Backfill completed correctly and heights checked/ correct
checklist-sectioned | bc6c1b70-9b71-486a-88e7-dc8e5f0fc24f |  | checklist | Core Water |  |  |  |  | Yes | SYS QA - Core Water | bcba7dc2-1d22-4b11-a179-c675cf39bd49
checkpoint-group | 0e1ba3f1-b3a5-4325-a063-91fb682bd298 |  | section | Cold water main
checkpoint-status | 5871ff1e-da15-48e3-b281-1294a95c1097 |  | checkpoint | Connections brazed correctly
checkpoint-status | 0b317c77-8eb4-4b30-b908-81a8591f50dc |  | checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
checkpoint-status | 3fca531f-dc2f-4c96-a0d7-df3e4be3c2a6 |  | checkpoint | Valves fitted correctly
checkpoint-group | c4af4c78-70cf-4315-a806-8444cdc7a95a |  | section | Hot water main
checkpoint-status | 2e11d3fa-60b9-4d2f-b286-02b7e7536340 |  | checkpoint | Connections welded correctly
checkpoint-status | 1adfd2be-bbd4-4ae5-8323-e07fd6d7853f |  | checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
checkpoint-status | fcf91a68-4672-4bba-a0f3-ddc580d46101 |  | checkpoint | Expansion allowed for
checkpoint-status | 666b1a80-3473-4c72-ae9b-131cf91ef888 |  | checkpoint | Lagging installed and neat
checkpoint-status | 0b06ba6c-1cfa-45d2-be8e-85363c3e2c01 |  | checkpoint | Valves fitted correctly
checkpoint-group | 3221494d-2ce8-4304-b4be-330cf3f28552 |  | section | General
checkpoint-status | 8bbeec3e-999d-4638-99e6-7aa1c879dec7 |  | checkpoint | Open ends of riser capped for testing
checkpoint-status | c5148c95-9890-4e4b-9f61-cc057053a310 |  | checkpoint | Checked for cross over's
checkpoint-status | 930d5234-bce7-45da-b836-51b67ab77e00 |  | checkpoint | Tidy work areas
checkpoint-status | aae50757-c203-4c60-bd30-2134181744ae |  | checkpoint | Pressure test to 1500kpa for 30mins
checkpoint-status | 30f8f34b-4178-4d9d-a6dd-af347cd80cb4 |  | checkpoint | Visual check (for leeks form valves, tees, saddles, etc)
checkpoint-status | 394a84d8-8d72-4c01-9048-574c7f4e4123 |  | checkpoint | Seismic bracing for pipework longitude and latitude
checkpoint-status | 58b17371-e91b-4257-ab64-8cb12103b737 |  | checkpoint | Lateral labelling of pipework backflow devices fitted
checkpoint-status | 8578c590-6598-4e95-83df-1ff56c473d2c |  | checkpoint | Pre Line Inspection Passed
checkpoint-status | 18ff8293-5b36-4974-952c-6b9f0e56d7fb |  | checkpoint | Installers name & date works completed
holdpoint | 0b3340b5-d95e-4ce9-9d4e-170fd7f793df |  | signoff | Request Signoff
checklist-flat | 43193c4e-8d8f-4376-9084-d2a349921764 |  | checklist | Testing - Hot Water Main |  |  |  |  | Yes | Testing - Hot Water Main | c0ab9acd-25cc-4fb3-b129-7b1c4909ff15
checkpoint-no-status | 3f4bfce1-407b-426f-9c37-b4da54c53ea8 |  | checkpoint | Details
text | 2f28a8b6-2764-512f-bb88-571efb233540 |  | textbox | Zone / Area
checkpoint-status | 1f5449ea-5cec-4360-8e20-aa685c6e12e0 |  | checkpoint | Pressure 1500 kpa or as per spec
text | 245773bc-a76f-5b60-b18a-a2fec8c283e6 |  | textbox | Duration
checkpoint-status | d1a1939e-1630-440e-916c-45e3b05edf5a |  | checkpoint | Visual check (for leeks form valves, tees, saddles, etc)
label | b59af80c-985c-5adf-9dc4-fa79865780eb |  | note | Attach photos of completed area
checkpoint-status | 7703d739-6662-498c-a234-5f0c4336aa1c |  | checkpoint | Pre Line Inspection Passed - Foreman
checkpoint-status | 4dcd7b31-82fa-4b6a-9972-9338df400ec8 |  | checkpoint | Pre Line Inspection Passed - Inspector
checklist-flat | 36868f9c-2b19-4b93-b44e-8b367bddf23d |  | checklist | Second Fix Plumbing - Water & Waste |  |  |  |  | Yes | SYS QA - Second Fix Plumbing - Water & Waste | e2ee9b4e-2440-4f76-b64d-4f54c0533ea7
checkpoint-status | 1e842138-da68-49e3-9ad0-42e90e1ada7b |  | checkpoint | Flush all water pipes before connecting fittings
checkpoint-status | 3006aed8-b288-4e7b-9218-d89f40c0207d |  | checkpoint | Correct Taps And Fittings Provided
checkpoint-status | 8508fb36-5f24-45c6-9c00-c22c1539c183 |  | checkpoint | Silicone Applied To Fixtures Where Required
checkpoint-status | 2492f00b-b87d-41de-aa55-416dc8dc4ffa |  | checkpoint | Check All Tap Connectors For Leaks
checkpoint-status | b91dcbad-315d-41c2-880b-dfac89be839c |  | checkpoint | Check Screwed Nippling In Walls For Leaks
checkpoint-status | ddde70b6-c45f-4967-b9fe-648785d0ea76 |  | checkpoint | Check Traps For Leaks
checkpoint-status | 80a612d8-6cdf-46a4-bdbc-f971db6e7584 |  | checkpoint | Check Cisterns For Leaks
checkpoint-status | 222c8f52-7529-412c-98cf-8559e680d36a |  | checkpoint | Check cisterns flushing correctly
checkpoint-status | d0810dba-f52d-4168-ad8e-4a00a8d18ad3 |  | checkpoint | Check All Fixtures Function Correctly
checkpoint-status | dd508fac-89c7-4476-b118-940c08b8185a |  | checkpoint | Test TPR on HWC and safetray drains away & airgap
checkpoint-status | f7b02c27-009e-4aed-b3da-af2bd3022b46 |  | checkpoint | Check HWC For Correct Valve Installation
checkpoint-status | 8a1d9c18-8fe5-4a2e-b8f6-a12a8b59d9d6 |  | checkpoint | Check Restraints & Timber chooks are installed on HWC
checkpoint-status | 3152445e-b1a4-47e0-b55b-eccf49165d6b |  | checkpoint | Element Position on HWC Is In A Serviceable Position
checkpoint-status | bd5b54eb-764d-481b-9004-b3def9cd0fa6 |  | checkpoint | Check FWG & Shower wastes are clean & clear
checkpoint-status | 5277c400-8911-4dd6-8f4e-cd437980a5f7 |  | checkpoint | Check Flanges Have Been Installed Where Required
checkpoint-status | 053c17e3-95fd-4495-9d5b-c75fff750fdc |  | checkpoint | Check All Soll Pipe Connections Are Connected To Drain
checkpoint-status | 4afe4752-3222-4246-ae48-287e75dd58d1 |  | checkpoint | Kitchen overflow working and no leaks
checkpoint-status | cf5dc38e-ef77-4633-90b8-82de8b54a4a3 |  | checkpoint | Picked Up All Left Over Material & Retumed to Office
checkpoint-status | 340b9e6d-40c2-4b81-955e-3ba034f94d4c |  | checkpoint | All your rubbish removed or in bins provided
checkpoint-status | 2485942a-14d6-4e18-bdb9-2293a3e43a7c |  | checkpoint | Check All Hot/Cold Pipes For Correct Position
checkpoint-status | aef4b887-de55-49b9-be5c-8d07fa232608 |  | checkpoint | Temperature set point
checkpoint-status | 6487f4d3-a0a1-44d0-9f13-fac613c80efc |  | checkpoint | Downpipe & overflow cover installed on balcony
checkpoint-status | bb48c9e4-8cf0-4d3b-86c3-7bac375b18da |  | checkpoint | Correct screws on balcony drain
checkpoint-status | afc10910-2307-4291-865c-bf40dcf2d08d |  | checkpoint | Installers name & date works completed
holdpoint | 7e019337-de4e-47af-ae1e-c0eb2ce056e7 |  | signoff | Request Signoff
checklist-flat | 42b54b00-ab75-462c-908a-9a3c8223da17 |  | checklist | Hot Water Cylinders |  |  |  |  | Yes | SYS QA - Hot Water Cylinders | ea10072e-a92e-47bc-b291-1e44bc9f0342
checkpoint-status | 6dd0ef6d-1153-429c-a25c-2d51539c2d86 |  | checkpoint | All safety valves installed
checkpoint-status | a82e357b-db46-4e28-8394-d150fe2886b5 |  | checkpoint | Seismic restraint fitted & wooden chochs installed
checkpoint-status | efb339f3-32a1-486d-8465-f170b444097c |  | checkpoint | Check all tap connectors for leaks
checkpoint-status | ce130d74-ff9d-4e82-bf41-c40b67059ace |  | checkpoint | Operate cold water expansion valves / check operation
checkpoint-status | c4d11b47-0fed-4340-a5ce-c043c459f5b9 |  | checkpoint | Test TPR valve
checkpoint-status | c496c50d-1792-4d8b-963d-febe553abd99 |  | checkpoint | Check for cross overs
checkpoint-status | 447e4cb3-7120-4a0c-8796-dead79249825 |  | checkpoint | Check HWC For Correct Valve Installation
checkpoint-status | 34b8b120-9b80-4b53-9663-d1626590dcdd |  | checkpoint | Test overflow & safe tray
checkpoint-status | 514a0c12-5aa9-45a8-aa13-91ddf5044c06 |  | checkpoint | Check Element Position on HWC Is In A Serviceable Position
checkpoint-status | 0f9461fc-b9b2-4da3-9a5f-bc653101051c |  | checkpoint | Check All Hot/Cold Pipes For Correct Position
checkpoint-status | 92c8cf48-45ed-48e7-a26a-6327e5f7df15 |  | checkpoint | Cylinder filled before turning on
checkpoint-status | 9bd795a9-a43c-4f71-a1bb-1ca2b38149be |  | checkpoint | Set tempering valve temperature 55deg C
checkpoint-status | 9188c08d-7df6-455a-bea5-86c2720a499d |  | checkpoint | Thermal lagging installed
checkpoint-status | 1ac722ec-ae9b-498e-8a71-4837f558ad13 |  | checkpoint | Installers name & date works completed
holdpoint | 19fd2e72-75b5-4602-8bfd-020ace03753d |  | signoff | Request Signoff
checklist-sectioned | 112f16e0-70e5-44d7-acfb-a8c608ca53c6 |  | checklist | Water Pump Commissioning |  |  |  |  | Yes | SYS QA - Water Pump Commissioning | f63f9078-dd79-41be-b6f6-e0bca879a7cd
checkpoint-group | f6f9ee4f-d47c-452b-9f8f-42f4b83357e7 |  | section | Pumpset mainfold
checkpoint-status | 25927c33-4233-4eef-b3ef-71e14225e289 |  | checkpoint | Connections welded correctly
checkpoint-status | 64acf82c-4eb3-4d00-860b-685e085c9d79 |  | checkpoint | Clip Spacing to manufactures specs horizontal/ vertical
checkpoint-status | c2e2bb6d-34be-4a55-8430-7a86cb8fc00c |  | checkpoint | Valves fitted correctly
checkpoint-status | d6c9b706-a96d-49d1-88cf-2691eac4029c |  | checkpoint | Line strainer fitted between pump & tank
checkpoint-group | 5d044a81-889e-4286-af2f-68fb7e098b77 |  | section | Pumps
checkpoint-status | 50707348-b874-4182-a03e-0c5e30fe3496 |  | checkpoint | Pump 1 Startup KPA
checkpoint-status | 7b50825a-6bc2-436f-82bf-d9a11a475ccf |  | checkpoint | Pump 1 kick out pressure KPA
checkpoint-status | 8a93540a-063c-4961-b20e-ae2d770b0505 |  | checkpoint | Pump 2 Startup KPA
checkpoint-status | 19c25e73-9ca2-4013-8718-8110acd2ec6c |  | checkpoint | Pump 2 kick out pressure KPA
checkpoint-status | 36a73ef3-d859-4aee-ab38-14565190adce |  | checkpoint | Pressure vessell pressure
checkpoint-group | 11d9228f-bde0-42ae-8f05-abbcfeed8714 |  | section | General
checkpoint-status | a97586ad-3f53-4446-b970-48d95acba44e |  | checkpoint | Mains water change over
checkpoint-status | ce330e1e-d3c0-4ce9-9499-15a561212bae |  | checkpoint | Flow test pump
checkpoint-status | b31a7d71-0a08-49f5-8d6f-8c00f92d4cfb |  | checkpoint | Pressure tests pipework
checkpoint-status | 3c22fefd-a24e-4f3f-a24c-3106697e0ab5 |  | checkpoint | Visual check (for leaks form valves, tees, saddles, etc)
checkpoint-status | 24eb9cce-cf09-4f4f-9ba8-3beff788d179 |  | checkpoint | Non return valves fitted
checkpoint-status | 34e04ecb-32f8-437a-bc07-bf0bc38aa549 |  | checkpoint | Installers name & date works completed
holdpoint | 0b289068-be5a-4916-9a7e-8555d2efe513 |  | signoff | Request Signoff
checklist-flat | 08ee5ce6-cd62-4acf-8b4d-89ab0b94bd32 |  | checklist | Testing - Sump Pump |  |  |  |  | Yes | Testing - Sump Pump | f984c158-d7fd-4fb6-b4c1-48e13e077dd1
checkpoint-no-status | 6754a3fc-1f25-4005-ad77-37f8b28c9548 |  | checkpoint | Installer Details
text | 10adcf9c-05ec-5bf4-b224-ef37d39c2342 |  | textbox | Installers name
text | bf9a9727-fb43-5d4c-9927-fd06a4ef983f |  | textbox | Date:
checkpoint-status | 763194c2-7939-463d-be3f-a89bb181413a |  | checkpoint | Tested by & date
text | 2b7e5f3e-1e5c-58d7-ba24-7e82cb5569e5 |  | textbox | Tested by:
text | 68b7e2d7-3fc5-5bee-9f45-2a88a62f0f5a |  | textbox | Date tested:
checkpoint-status | 4b210c36-c9c5-4579-b934-402c5478b7e5 |  | checkpoint | Council inspector sign off and date
checklist-flat | cbe11001-f598-4a1d-82d2-22d918c9c78b |  | checklist | Testing - Cold Water Booster Pump |  |  |  |  | Yes | Testing - Cold Water Booster Pump | fd557763-7626-4acf-8ad9-f1d60249d9b3
checkpoint-no-status | 177db684-e191-49ea-a27c-4ccaa6436c2a |  | checkpoint | Installer Details
text | 307c75d6-6c2d-5690-9116-b77088ddb8d8 |  | textbox | Installers name
text | 5266857b-80e4-5ea6-ae3c-4c32ebe3d63f |  | textbox | Date:
checkpoint-status | fdbe188b-c33b-46ec-887d-a6b37e1e35a8 |  | checkpoint | Tested by & date
text | ce665d6b-81cd-5154-b39f-ec16701d00b4 |  | textbox | Tested by:
text | b4213eb9-50f6-560e-be8d-68c609a3b366 |  | textbox | Date tested:
checkpoint-status | 5ef43964-8aba-41f1-8b9c-6db37976bab3 |  | checkpoint | Council inspector sign off and date