## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
QA - Sprinkler Pipe Installation Rough In
| Scope |  |  | Sprinkler Pipe Installation Rough In
Rows
|  | Sprinkler Pipe Installation Rough In | dynamic | Sprinkler Pipe Installation Rough In | Site QA
Columns
|  | Check sprinkler heads for dmg./scratches to paint |  | Check sprinkler heads for damage/scratches to paint finish | Initial Installation
|  | Flexi compliant to AS2118 & FM approved |  | Flexi compliant to AS2118 and FM approved | Initial Installation
|  | Sprinklers neatly hemped & soaped |  | Sprinklers neatly hemped and soaped (with inner escutcheon plates installed, if required) | Initial Installation
|  | Grid lines marked out/confirmed w/ asst. of bldg. team |  | Grid lines marked out and confirmed with the assistance of building team | Initial Installation
|  | Pipework installed as per ISSUED FOR CONST. drawings |  | Pipework installed as per the ISSUED FOR CONSTRUCTION drawings? (correct heights, measurements off grid lines) | Initial Installation
|  | Pipework hangers/supports installed correctly |  | Pipework hangers/supports installed correctly | Initial Installation
|  | Concealed space sprinklers installed as per AS2118 |  | Concealed space sprinklers installed as per AS2118 with no obstructions | Initial Installation
|  | Flexi installed to manufact. specs & tied up from dmg. |  | Flexi installed to manufacturers specs and tied up away from possible damage | Initial Installation
|  | Have the correct sprinklers been installed? |  | Have the correct sprinklers been installed? (Temperature rating, Fast Response, Finish) | Initial Installation
|  | Riser pipework installed as per ISSUED FOR CONST. drawings |  | Riser pipework installed as per the ISSUED FOR CONSTRUCTION drawings? | Initial Installation
|  | Riser hangers/supports installed correctly |  | Riser hangers/supports installed correctly? | Initial Installation
|  | Fire sprinkler control valve installed & connected to system |  | Fire sprinkler control valve installed and connected to system, riser and drain pipework? (t | Initial Installation
|  | Fire Rating/acoustic sealing of pens. prior to ceiling sheeting |  | Fire Rating/acoustic sealing of penetrations completed prior to ceiling sheeting? | Initial Installation
|  | Fire Rating/acoustic sealing of riser penetrations |  | Fire Rating/acoustic sealing of riser penetrations completed? | Initial Installation
|  | Exposed fire sprinkler pipework completely painted to colour |  | Exposed fire sprinkler pipework completely painted to required colour? | Initial Installation
|  | Any changes to installation recorded for AS BUILT DRAWINGS |  | Any changes to installation recorded for AS BUILT DRAWINGS | Initial Installation
|  | 1.6MPa/400 kpa in excess of maximum static working pressure |  | 1.6MPa or 400 kpa in excess of the maximum static working pressure (whichever is greater) for a period of 2 hours, with no loss of pressure duration the 2 hour duration. | Hydrostatic Pressure Test
|  | Pipework Joints/connections/position/spacing correct |  | Are the pipework Joints, connections, position & spacing correct? | Hydrostatic Pressure Test
|  | All open ends plugged off to close up piping network |  | Are all open ends plugged off to close up the piping network? | Hydrostatic Pressure Test
|  | Start Time: | Start Time: | Are all open ends plugged off to close up the piping network? | Hydrostatic Pressure Test
|  | Test Pressure: | Test Pressure: | Are all open ends plugged off to close up the piping network? | Hydrostatic Pressure Test
|  | Attach picture of pressure test gauge: |  | Attach picture of pressure test gauge: | Hydrostatic Pressure Test
|  | Finish Time: | Finish Time: | Attach picture of pressure test gauge: | Hydrostatic Pressure Test
|  | Test Pressure: | Test Pressure: | Attach picture of pressure test gauge: | Hydrostatic Pressure Test
|  | Attach picture of pressure test gauge: |  | Attach picture of pressure test gauge: | Hydrostatic Pressure Test
|  | Any pressure loss during test? |  | Any pressure loss during test? | Hydrostatic Pressure Test
QA - Sprinkler Pipe Installation Fit Off
| Scope |  |  | Sprinkler Pipe Installation Fit Off
Rows
|  | Sprinkler Pipe Installation Fit Off | dynamic | Sprinkler Pipe Installation Fit Off | Site QA
Columns
|  | Check Sprinkler Heads for dmg./scratches to paint |  | Check Sprinkler Heads for damage/scratches to paint finish | Fit Off - Part 1
|  | Check Flexi for damage/kinks |  | Check Flexi for damage/kinks (take a photo of any damaged Flexi with room/area reference) | Fit Off - Part 1
|  | Water is drained the water out of the system |  | Check the water is drained the water out of the system | Fit Off - Part 1
|  | Installation drawings are the most recent revision |  | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION? | Fit Off - Part 1
|  | Laser used to fit off to accurate measurements |  | Laser used to fit off to accurate measurements? | Fit Off - Part 1
|  | Sprinklers installed as per AS2118 |  | Sprinklers installed as per AS2118 with no obstructions? | Fit Off - Part 1
|  | Correct sprinklers been installed |  | Have the correct sprinklers been installed? (Temperature rating, Fast Response, Finish) | Fit Off - Part 1
|  | Water is reinstated into the system at completion |  | Check the water is reinstated into the system at the completion of fit off | Fit Off - Part 1
|  | Check sprinkler heads for dmg./scratches to paint |  | Check sprinkler heads for damage/scratches to paint finish | Fit Off - Part 2
|  | Check sprinkler heads are straight/parallel to surface |  | Check sprinkler heads are straight and parallel to finished surface | Fit Off - Part 2
|  | No paint or gyprock setting on sprinkler head |  | Check there is no paint or gyprock setting on sprinkler head | Fit Off - Part 2
|  | Outer escutcheon plates installed |  | Outer escutcheon plates installed | Fit Off - Part 2
|  | No gaps between outer escutcheon plate/ceiling |  | Check there is no gaps between the outer escutcheon plate and the finished ceiling | Fit Off - Part 2
|  | Sprinklers installed as per AS2118 |  | Sprinklers installed as per AS2118 with no obstructions? | Fit Off - Part 2
|  | 1.6MPa/400 kpa in excess of max. static working pressure |  | 1.6MPa or 400 kpa in excess of the maximum static working pressure (whichever is greater) for a period of 2 hours, with no loss of pressure duration the 2 hour duration. | Hydrostatic Pressure Test
|  | Pipework Joints/connections/position/spacing correct |  | Are the pipework Joints, connections, position & spacing correct? | Hydrostatic Pressure Test
|  | All open ends plugged off to close up piping network |  | Are all open ends plugged off to close up the piping network? | Hydrostatic Pressure Test
|  | Start Time: | Start Time: | Are all open ends plugged off to close up the piping network? | Hydrostatic Pressure Test
|  | Test Pressure: | Test Pressure: | Are all open ends plugged off to close up the piping network? | Hydrostatic Pressure Test
|  | Attach picture of pressure test gauge |  | Attach picture of pressure test gauge: | Hydrostatic Pressure Test
|  | Finish Time: | Finish Time: | Attach picture of pressure test gauge: | Hydrostatic Pressure Test
|  | Test Pressure: | Test Pressure: | Attach picture of pressure test gauge: | Hydrostatic Pressure Test
|  | Attach picture of pressure test gauge |  | Attach picture of pressure test gauge: | Hydrostatic Pressure Test
|  | Any pressure loss during test? |  | Any pressure loss during test? | Hydrostatic Pressure Test
QA - Sprinkler System Commissioning
| Scope |  |  | Sprinkler System Commissioning
Rows
|  | Sprinkler System Commissioning | dynamic | Sprinkler System Commissioning | Site QA
Columns
|  | Check operation of monitored isolation valve |  | Check operation of the monitored isolation valve and record FIP interface
|  | Inspect & test gauge operation |  | Inspect and test gauge operation (record a video of the drop in pressure and the pressure re-stabilising to static working pressure)
|  | Check operation of manual test drain confirm flow switch |  | Check operation of manual test drain confirm flow switch activation to FIP
|  | Check operation of the water pressure switch |  | Check operation of the water pressure switch activation to FIP
|  | Check operation of solenoid test drain confirm FSW activation |  | Check operation of solenoid test drain confirm FSW activation to FIP
|  | Check operation of water motor alarm |  | Check the operation of the water motor alarm
QA - Fire Detection Installation Rough In
| Scope |  |  | Fire Detection Installation Rough In
Rows
|  | Fire Detection Installation Rough In | dynamic | Fire Detection Installation Rough In | Site QA
Columns
|  | Installation drawings are the most recent revision |  | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION?
|  | Room/area layout set out & confirmed |  | Room/area layout set out and confirmed with the assistance of building team?
|  | Cable installed to device locations |  | Cable installed to device locations as per the most recent ISSUED FOR CONSTRUCTION drawings?
|  | Cable supports installed correctly |  | Cable supports installed correctly?
|  | Sufficient slack in cable to reach req. fit off loc. |  | Sufficient slack in cable to reach required fit off location?
|  | Cable tray installed as per AS 3000 |  | Cable tray installed as per AS 3000?
|  | Fire Detection cable has compliant spacing |  | Fire Detection cable has compliant spacing between Detection, EWIS/OWS and electrical power cable?
|  | Fire Rating/acoustic sealing of penetrations |  | Fire Rating/acoustic sealing of penetrations completed prior to ceiling sheeting?
|  | Wires clearly drawn & submitted |  | Are wires clearly drawn and submitted for AS BUILTS/AS CONSTRUCTED drawings
|  | All devices numbered on drawing |  | Are all devices numbered on drawing for AS BUILTS/AS CONSTRUCTED drawings?
|  | Riser Cable Tray Installation |  | Riser Cable Tray Installation & cables installed in a neat order?
|  | Cable supported to tray |  | Cable supported to tray
|  | Fire Rating/acoustic sealing of penetrations |  | Fire Rating/acoustic sealing of penetrations completed prior to ceiling sheeting?
QA - Fire Detection Installation Fit Off
| Scope |  |  | Fire Detection Installation Fit Off
Rows
|  | Fire Detection Installation Fit Off | dynamic | Fire Detection Installation Fit Off | Site QA
Columns
|  | Installation drawings are the most recent revision |  | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION?
|  | Excess slack in cable removed |  | Excess slack in cable removed?
|  | Smoke and Thermal Detectors installed |  | Smoke and Thermal Detectors are installed in correct dimensioned locations as per the ISSUED FOR CONSTRUCTION drawings?
|  | Thermal & Smoke Detectors installed in accordance with AS1670, AS1668, BCA |  | Check Thermal and Smoke Detectors installed in accordance with AS1670, AS1668, BCA (take photo of data sheet for devices being installed)
|  | EWIS/OWS speaker installed in correct locations |  | EWIS/OWS speaker are installed in the correct dimensioned locations as per the ISSUED FOR CONSTRUCTION drawings?
|  | Laser used to fit off to accurate measurements |  | Laser used to fit off to accurate measurements?
|  | WIP/MCP installed as per AS1670 & BCA |  | WIP/MCP installed as per AS1670 & BCA
|  | All devices are numbered correctly using labels |  | All devices are numbered correctly using labels (NO MARKERS) and in correct location as per the AS BUILT DEVICE numbering markup?
|  | All devices are fit off as per ISSUED FOR CONSTRUCTION drawings |  | All devices are fit off as per ISSUED FOR CONSTRUCTION drawings and clear of any obstructions?
|  | Cable joints & terminations correctly completed |  | Cable joints and terminations correctly completed with no tension on the terminals?
|  | All traffolyte labels installed to each WIP/MCP |  | All traffolyte labels are installed to each WIP/MCP and field module?
QA - Fire Detection System Commissioning
| Scope |  |  | Fire Detection System Commissioning
Rows
|  | Fire Detection System Commissioning | dynamic | Fire Detection System Commissioning | Site QA
Columns
|  | Test each Smoke Detector |  | Test each Smoke Detector in accordance with AS1670, AS1668, BCA using smoke can and record FIP alarm.
|  | Test each thermal Detector |  | Test each thermal Detector in accordance with AS1670, AS1668, BCA using a heat detector tester kit can and record FIP alarm.
|  | Test Speakers |  | Test Speakers in accordance with AS1670 & BCA under general fire alarm and record results using a sound probe meter
|  | Test Visual Alarm Devices |  | Test Visual Alarm Devices in accordance with AS1670 & BCA under general fire alarm
|  | Test WIP phones |  | Test WIP phones in accordance AS1670, BCA
|  | Test Manual Call Points |  | Test Manual Call Points in accordance with AS1670, BCA and record FIP/EWIS alarm
|  | Test Field Module Interfaces |  | Test Field Module Interfaces in accordance with AS1670, AS1668, BCA and record FIP alarm (take a photo of the Interface and FIP the the same time)
|  | Test activation of smoke/fire door magnetic hold open devices |  | Test the activation of smoke/fire door magnetic hold open devices under local fire alarm
|  | Test activation of mechanical fire trips |  | test the activation of mechanical fire trips under general fire alarm
|  | Test activation of security fire trips |  | Test the activation of security fire trips under general fire alarm
|  | Test EWIS/OWS time delay for cascading |  | Test the EWIS/OWS time delay for cascading and changing from ALERT to EVAC (record a video of the EWIS/OWS Panel)
|  | Test activation of network monitoring |  | Test the activation of network monitoring during latching FIP alarm
|  | Test activation of external bell under fire trip mode |  | Test the activation of the external bell under fire trip mode in accordance AS1670, BCA
|  | Test activation of external strobe under fire trip mode |  | Test the activation of the external strobe under fire trip mode in accordance AS1670, BCA