## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP031 - Blinding, Pile Caps and Slab Footings Rev 3 | itp |  |  |  |  | ITP031 - Blinding, Pile Caps and Slab Footings Rev 3
section | 1.0 General
checkpoint | 1.1 - Material Submission / Approval
label | Ref docs - AS 3600 235929-000- CV-SP-00007
label | Acceptance criteria - Has the mix design to be approved prior to placement. Material properties meet project specification, AS 3600, AS 1379?
label | ○ Do Structural Elements meet: Minimum Concrete strength 40 MPa or as specified in Drawings?
label | ○ Do Non-Structural Elements meet: Minimum Concrete strength 15 MPa or as specified in Drawings?
label | ○ Has Steel Reinforcement schedule provided to MDR for review and approved?
label | ○ Do admixtures shall conform with AS 1478.1 and are permitted if used in accordance with manufacturers instructions?
label | ○ Mixtures containing calcium chloride shall not be used.
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Mix Design Number, Bar Bending Schedules, Material compliance certificates
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.2 - Determine lot size
label | Acceptance criteria -
textbox | Lot Size = Each pour section per day (location or m2) or each structural (Pilecap)
label | Key - S
label | MDR/VIVA Key - S
checkpoint | 1.3 - Permits
label | Acceptance criteria - The following are relevant, in place and signed onto:
label | – Penetration permit
label | – Hot works permit
label | – Temporary work permit
label | – Working at heights permit
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - H
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 Blinding/Lean Concrete
checkpoint | 2.1 - Set out
label | Ref docs - IFC drawings
label | Acceptance criteria - Extents, grades and levels correct to relevant drawings. All services have been marked out.
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA Key - W
checkpoint | 2.2 - Pre-Pour Inspection
label | Ref docs - Bulk Earthworks ITP 02
textbox | Underlying lot number:
label | Acceptance criteria - Has a pre-pour inspection been completed with the client, and they have verified in writing that the pour is able to commence?
label | ○ The foundation base excavation shall be tested, surface compacted and approved prior to placement of the blinding.
label | ○ The foundation location, depth and dimensions shall also be checked and confirmed prior. to placing the blinding.
label | ○ Approval shall be provided, in writing, by McDermott to the foundation. subcontractor before commencing with concrete placement.
label | ○ Has this been completed?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Pre-Pour Checklist
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 - Lean Mix Concrete
label | Ref docs - Section 5.1.2 of document 235929-000- CV-SP-00007
label | Acceptance criteria - Approved Concrete Mix Design.
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Dockets
checkpoint | 2.4 - Placement of Lean Mix
label | Ref docs - 235929-000- CV-SP-00007
label | Acceptance criteria - Has the blinding been poured to the correct level? The following are acceptable:
label | – Minimum Thickness = 50mm
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - As-built Survey
section | 3.0 Formwork
checkpoint | 3.1 - Temporary works requirements
label | Ref docs - SYM-INF-Temporary Work Procedure IFU 05122
label | Acceptance criteria - Formwork above 1.0m to be designed by temporary works engineer.
label | ○ Has design to be undertaken by external consultant complying with AS1170 and AS3610 plus any project specification requirements?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - S
checkpoint | 3.2 - Pile Penetration
label | Ref docs - Civil Drawings IFC
label | Acceptance criteria - Pile C.O.L to penetrate 50mm above blinding of pile cap (+/- 25mm).
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Report
checkpoint | 3.3 - Formwork Setout and positioning correct
label | Ref docs - Civil drawings 235929-000- CV-SP-00008; Section 6
label | Acceptance criteria - Is formwork checked for potential loose sections, ensuring no movement upon placement of concrete?
label | ○ Is formwork in line with survey markings?
label | ○ Have chamfers (if required) been attached to formwork in level manner?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA Key - W
checkpoint | 3.4 - Concrete jointing
label | Ref docs - Civil drawings
label | Acceptance criteria - Have construction joints to be installed as detailed on Drawings and notes using correct materials?
button | Acceptance | Yes,No,N/A
label | Key - W
section | 4.0 Reinforcement
checkpoint | 4.1 - Steel reinforcement supply
label | Acceptance criteria - Have steel tags checked against supply schedule prior to installation?
label | ○ Does the manufacturer hold a valid ACRS certificate?
label | ○ Is reinforcement is free from rust and other contaminates that may affect bonding?
button | Acceptance | Yes,No,N/A
label | Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Delivery Dockets / certificates / product tags, Incoming material checklist Photo’s
checkpoint | 4.2 - Steel reinforcement installation
label | Ref docs - 235929-000- CV-SP-00009, AS3600 17.5.3, 235929-000- CV-01-92002- 010002
label | Acceptance criteria - Is steel installed as per the latest IFC drawings?
label | ○ Does steel reinforcement conform with Steel Reinforcement Specification?
label | ○ Has minimum cover to inside face of wall must be maintained? All reinforcement shall be in accordance with AS 3600 & Civil drawings.
label | – – – – – – – – – – – – – –
label | 17.5.3 Tolerance on position of reinforcement and tendons
label | The deviation from the specified position of reinforcement and tendons shall not exceed the following:
label | (a) For positions controlled by cover –
label | (i) in beams, slabs, columns and walls: -5, +10 mm;
label | (ii) in slabs-on-ground: -10, +20 mm; and
label | (iii) in footings cast in the ground: -10, +40 mm,
label | where a positive value indicates the amount the cover increases and a negative value indicates the amount the cover decreases.
label | (b) For positions not controlled by cover, namely –
label | (i) the location of tendons on a profile: 5 mm;
label | (ii) the position of the ends of reinforcement: 50 mm; and
label | (iii) the spacing of bars in walls and slabs and of fitments in beams and columns: 10% of the specified spacing or 15 mm, whichever is greater.
label | – – – – – – – – – – – – – –
label | 8.1 CONCRETE COVER SHALL BE IN ACCORDANCE WITH AUSTRALIAN STANDARD AS 3600 OR THE VALUES STATED BELOW, WHICHEVER IS GREATER.
label | ○ PAVING (TOP) = 30 mm
label | ○ PAVING (BOTTOM - AGAINST GROUND) = 50 mm
label | ○ FOUNDATIONS CAST AGAINST FORMWORK (INCL. EXPOSED WEATHER FACE) = 45 mm
label | ○ FOUNDATIONS CAST AGAINST GROUND = 65 mm
label | ○ EXPOSED TO WASH DOWN WATER AND/OR PROCESS SPILLAGE = 50 mm
label | ○ CAST ON LEAN CONCRETE = 45 mm
label | ○ CFA PILES = 70 mm
label | – – – – – – – – – – – – – –
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - IFC Drawing Number and Revision
holdpoint | AUTHORITY HOLDPOINT
section | 5.0 Structural Concrete Pour
checkpoint | 5.1 - Pre-pour Inspection
label | Ref docs - Appendix 7.1 Pre-Concrete Placement Checklist
label | Acceptance criteria - Has a pre-pour inspection checklist completed prior to placement?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Appendix 7.1 Pre-Concrete Placement Checklist
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Placement
label | Ref docs - 235929-000- CV-SP-00007 Appendix 7.3 Concrete Truck Record
label | Acceptance criteria - Concrete shall not be placed when temperature is less the 5°C or greater than 36°C. Between 32°C and 36°C admixtures and placing requirements must be met.
label | ○ Concrete shall be transported, handled and placed to prevent segregation, loss or leakage of materials.
label | ○ Concrete shall not be dropped from a height greater than 2m.
label | ○ Concrete shall be discharge within 90 minutes of dispatch from plant.
label | ○ For continuous pours, the maximum time lag between truck loads shall not exceed 25 minutes.
label | ○ Concrete shall be thoroughly vibrated to ensure no honey combing, voids or surface defects occurs and compaction is achieve throughout structure.
label | ○ Water shall not be added to achieve slump greater than that specified. Slump test to be completed after water is added.
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Appendix 7.3 Concrete Truck Pour Record/Dockets
checkpoint | 5.3 - Slump Test
label | Ref docs - Section 5.1.1 235929-000- CV-SP-00007
label | Acceptance criteria - Slump must be 100mm as per the specification.
label | ○ Otherwise refer to approved slump (80mm). Testing shall be +- 15% of stated.
label | ○ Approved mix design slump
button | Acceptance | Yes,No,N/A
label | Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test docket
checkpoint | 5.4 - Strength Testing
label | Ref docs - 235929-000- CV-SP-00007 Section 6.8
label | Acceptance criteria - Samples to be taken from chute. 5 cylinders collected per sample – 1x 7day, 3x 28day, 1x reserve.
label | ○ 1 test for the first 20m3
label | ○ 1 test per 40n3 thereafter
label | ○ Frequency reduce to 1 test per 80m3 for pours over 400m3
label | Acceptance
label | – – – – – – – – – – – – – –
label | No. of samples ¦¦ Volume of concrete (m3)
label | – – – – – – – – – – – – – –
label | 1 ¦¦ <20
label | 2 ¦¦ 20-60
label | 3 ¦¦ 60-100
label | 4 ¦¦ 100-140
label | – – – – – – – – – – – – – –
label | Key - H
label | MDR/VIVA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.6 - Curing of Concrete
label | Ref docs - 235929-000- CV-SP-00007 Section 6.5
label | Acceptance criteria - As per the approved Curing Methodology.
label | ○ Has curing been conducted as per approved curing methodology?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Approved Curing Technical Data Sheet
checkpoint | 5.7 - Concrete Finishing
label | Ref docs - 235929-000- CV-SP-00007 Section 6.4
label | Acceptance criteria - Finish concrete per schedule below:
label | ○ Interior walls or columns exposed: smooth form/rubbed finish.
label | ○ Exterior walls or columns exposed: smooth form/rubbed finish.
label | ○ Walls below grade: rough form finish.
label | ○ Exterior slabs for spill containment: float finish.
label | ○ Other exterior slabs (i.e. foot traffic): broom finish.
label | ○ Interior slabs: steel trowel.
label | ○ Interior slabs to accept additional finish: steel trowel.
label | ○ Surfaces to be grouted: rough [6 mm amplitude] but even finish with laitance removed to provide good bond between grout and concrete.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Concrete Pour Record
checkpoint | 5.8 - Formwork Stripping
label | Ref docs - 235929-000-CV-SP-00007, AS1510, AS1509, Section 6.6 of 235929-000-CV SP-00008 CONC FORMWORK
label | Acceptance criteria - Has Remove formwork progressively so no unbalanced loads are applied to the structure, or concrete is damaged?
label | ○ Has the formwork been removed in the same sequence as concrete placement to achieve similar concrete surface coloration?
label | ○ In accordance with AS3600 Table 4.4 and Section 17.1.5, removal of forms before 7 days would require a curing membrane conforming to AS3799 to be applied immediately or any other approved acceptable method of water retention in the concrete.
label | ○ Has this been completed?
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA Key - S
section | 6.0 Completion
checkpoint | 6.1 - As Built
label | Acceptance criteria - As built to be submitted after pour, showing set out, RLs, grades, extents, bolts, grout tubes, starter bars, etc.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Conformance report
checkpoint | 6.2 - Concrete Test Results
label | Ref docs - 235929-000-CV-SP-00007 AS3600, AS1379, AS3610 IFC drawings
label | Acceptance criteria - Submission of 28 days results. Results meet requirements.
button | Acceptance | Yes,No,N/A
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - NATA endorsed test report
checkpoint | 6.3 - Concrete cracking approval
label | Acceptance criteria - Contractor is to submit a concrete crack repair methodology to MDR prior to commencing any crack repair. Has this been approved?
label | – – – – – – – – – – – – – –
label | Maximum Allowable Crack Widths in New Concrete
label | – – – – – – – – – – – – – –
label | Service Exposure Condition ¦¦ Crack Width, μm
label | – – – – – – – – – – – – – –
label | Interior ¦¦ 300
label | Exterior air (or soil) ¦¦ 200
label | Water-retaining structures ¦¦ 100
label | – – – – – – – – – – – – – –
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Concrete Repair Method Document Approval
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.4 - Concrete cracking repair
label | Acceptance criteria - Has concrete crack repair been undertaken as per the approved method?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photo’s
holdpoint | AUTHORITY HOLDPOINT