## ITP-xxx
|  |  | Inspection and Test Plan - Control and Supervision of the Works | [7 empty] | Document # ITP-003
[11 empty] | Revision : 00 | Date : 08/09/25
Client: |  | Yarra Trams |  | Construction Process: |  | Prepared by: |  | Reviewed by : |  |  | Approved by :
Project: |  | Vic & Eliz St Stage 2 |  | Electrical and Communication Conduit |  | Name: | Jake Cardillo | Name: | Patrick Fagan |  | Name: Shaun Kent
Contract No: |  | 8B5600 |  | Specifications: Yarra Trams Infrastructure - Tram Track Construction Standard (CE-019-ST-0033)
|  |  |  | Structure / Component: Tram Tracks (Electrolysis, Platform Conduits) |  | Signed : |  | Signed : |  |  | Signed :
|  |  |  | Location: Vic & Elizabeth St |  | Date : 08/09/25 |  | Date : 08/09/25 |  |  | Date : 08/09/25
Lot No: |  |  | Lot Details: | [5 empty] | Lot Size/ Quantity:
Item | Task/Activity Description |  | Inspection / Controls and Verification Detail |  |  |  |  | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
No. |  |  | Frequency | Acceptance Criteria | Reference Documents | Inspection / Test Method | Record of conformity |  | Project Engineer Site Engineer Superintendent Surveyor Foreman | Client | Fulton Hogan | FH's Sub-contractor | Date
1 | Preliminary Works
1.1 | Check for correct documentation |  | Prior to commencing any activity | Employees and sub contractors shall be issued with the most current and complete construction drawings | Drawings and drawing registers | Visual inspection | This ITP signed off | HP* | Fulton Hogan Engineer | N/A |  | N/A
1.2 | Implementation of all measures and controls |  | Prior to commencing any activity | All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP | PSP, EMP, TMP, JSEA, SWMS, WP | Visual Inspection | This ITP signed off | HP* | Fulton Hogan Engineer | N/A |  | N/A
1.3 | Materials |  | Per Batch | • Electrical supply conduit to be Orange and rigid HD UPVC of sizes as required. • Communications conduit to be White and rigid UPVC of either 32 or 50mm size or larger as required as outlined in the drawings. | CE-019-ST-0033 cl 4.4.1 AS 2053 | Verify | This ITP signed | HP* | Fulton Hogan Engineer | N/A |  | N/A
2 | Construction Works
2.1 | Survey set-out |  | As required | • Work is set out in accordance with drawings. | Work procedure | Verify | This ITP signed | HP* | Fulton Hogan Engineer | N/A |  | N/A
2.2 | Excavation and Trenching |  | Prior to Installation | • Minimum cover for underground conduits shall be 600mm • Open trenching only permitted in unpaved areas, line of trench to be at right angle to the track • Trench shall maintain a minimum clearance of 300mm from all existing services where possible | CE-019-ST-0033 cl 4.2.5 & 4.2.8 | Verify | This ITP signed | WP | Fulton Hogan Engineer | N/A |  | N/A
2.3 | Installation of Conduits and pits |  | Each Lot | • Conduits in the same run shall be spaced 50mm by using clean sand to pack voids Conduit shall be embedded in not less than 50mm sand and covered by >50mm - 75mm< sand • Mechanical protection shall be provided by installation of polymeric cable or cover strip of thickness not less than 3mm, and of a material equivalent of UPVC conduit complying to AS 2053. Protective material shall be placed not less than 100mm above the conduit, and shall not be less than 150mm wide. • Conduits shall be joined male to female ends and sealed with approved adhesive immediately prior to joining. • Conduits shall not be subject to construction loadings • Bottom of lowest conduit shall maintain a minimum 100mm above pit floor • Conduits shall be capped with UPVC electrical caps | CE-019-ST-0033 cl 4.4 | Visual inspection | This ITP signed | WP | Fulton Hogan Engineer/ YT | N/A |  | N/A
2.4 | Inspection of conduit installation |  | Each Lot | Laying of conduits and installation of pits shall be inspection by superintendent and conform to design drawings before any backfilling procedure is to commence | Work procedure | Visual Inspection | This ITP Signed | HP | Fulton Hogan Engineer/YT |  |  | N/A
2.5 | Back Fill of Trenches |  | Each Lot | • Backfilling (for trenching or road crossings) - Conduit trench shall be backfilled above marker tape with crushed rock or suitable excavated material and compacted to 90% standard compaction 150mm-200mm below sub base level, the last 150mm-200mm shall be compacted to 100% standard compaction using handheld mechanical plant | CE-019-ST-0033 cl 4.2.5 | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A |  | N/A
2.6 | Installation of Draw Cords |  | Each Lot | Draw wire shall be provided for each conduit, with extra 3m length at each pit, material to be used shall be 6mm 'telstra rope' | CE-019-ST-0033 cl 4.4.6.2 | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A |  | N/A
2.7 | Compaction |  | Each Lot | During compaction optimum moisture content of bedding and select fill is within 85% to 115% as provided by suppliers | CE-019-ST-0033 cl 4.2.8 | Verify | This ITP signed | HP* | Fulton Hogan Engineer | N/A |  | N/A
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
| Print Name: |  | Position: |  | Signature: |  |  |  |  | Date: / /
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FHDB |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
WP | Witness Point | An inspection which must be witnessed by the Superintendent |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
AP | Approval Point | Written or verbal approval given by the Superintendent
Note on K16: Rodrigo Anchico: Write "N/A" to disable the cell.