## ITP - Bisset Road Wastewater
INSPECTION & TEST PLAN
ITP 01 - Bisset Road - Wastewater Reticulation Upgrade |  | Contract Name: |  |  |  | Hold Point (H) |  | Review | Prepared By | Signature | Date
[6 empty] | Witness (W) |  | Prepared By | Josh Welch |  | 2025-08-01
United Civil Project Number - 7067 |  | Kaikohe Wastewater Reticulation Upgrade |  |  |  | Submit (S) |  | Reviewed By | Gerrie van der Linde |  | 2025-08-01
[6 empty] | Perform (P) |  | Approved by
Accept (A)
TASK | SPECIFICATION REFERENCE | TEST/TASK REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL | Client | COMMENTS
Preconstruction
Precondition Survey | Wastewater Specification B.2.11.2.2 | Visual inspection. | UCCL | Prior to starting on site. Survey conducted of all surfaces, footpaths, kerbs, driveways and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works. | Survey documents submitted to Engineer. | P | S
Materials Quality | FNDC Approved Materials List - Wastewater and Stormwater | Visual check for approved materials, quality and condition. | UCCL | On arrival to site, prior to using materials. | Materials meet specifications or otherwise approved by Engineer. Delivery dockets. Photos. | W | W
Survey Setout | Wastewater Specification B.2.11.2.4 | Survey set out. | UCCL | Prior to commencing each stage of work. | Survey set out as per IFC drawings. | P | W | Check all MHs for levels, prior to constructing drainage lines, they must verify the inverts and locations of existing manholes as part of the inspection and testing process
Service Location | Wastewater Specification B.2.11.4.2 | Locate underground services within work area. | UCCL | Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services. |  | P | W
Installation
Material Properties (Bedding) | Wastewater Specification B.7.5.1.9 | AP20 Grading curve to be submitted to Engineer for approval. | UCCL Haigh Workman | Prior to using bedding material on site. PE bedding, pipe surround and haunching shall be AP20 in accordance with AS/NZS 2566. | Bedding grading curve accepted by Engineer. | S | A
Material Properties (Subbase - AP65) | FNDC Engineering Standards 3.3.2 | Subbase material meets FNDC Engineering Standards | UCCL Haigh Workman | Prior to using subbase material on site. | Subbase material test certificates accepted by Engineer. | S | A
Material Properties (Basecourse - AP40) | FNDC Engineering Standards 3.3.2 | Bascourse material meets FNDC Engineering Standards | UCCL Haigh Workman | Prior to using basecourse material on site. | Basecourse material test certificates accepted by Engineer. | S | A
Pipe and Rubber Rings | Wastewater Specification B.7.8.3 | Visual inspection | UCCL | Visual inspection prior to use (clean and free from defects). | Photographs. | W | W
Pipeline Installation (PVC) | Wastewater Specification B.7.8 and B.7.9 FNDC Engineering Standards Sheet 31 | Visual inspection Pipeline installed to correct alignment, grade and level | UCCL | On completion of installation of each length of pipe, prior to backfilling. Throughout installation of pipeline. Horizontal alignment +100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe. | As-built drawings. Photographs. | P | W
Stainless Steel Pipe Bridge | Wastewater Specification 'Package 3 - Bisset - Pipe Bridges Specification | Visual inspection Pipe installed as per specification to correct alignment, grade and level | UCCL | On completion of installation of each pipe bridge. Horizontal alignment + 100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe. | As-built drawings. Photographs. | P | W
Manhole Installation and Backfill | Wastewater specification B.7.9 | Visual inspection. Manhole checks including position, haunching, steps and sealed joints. | UCCL | On completion of manhole installation. | Falls through manholes are to be within +5mm of design levels. Maximum deviation from vertical (manholes/chambers) shall be 10mm per metre. | P | W
Pipe Bedding | Wastewater Specification B.3.4.1 FNDC Engineering Standards Sheet 31 | Visual inspection. Compaction test on top of bedding. | UCCL | Bedding installed as per specifications. | Photographs. Compaction test results. | P | W
Pipe Backfill (Outside of Carriageway) | Wastewater Specification B.3.6.3 FNDC Engineering Standards Sheet 31 | Visual inspection. Compaction test on top of GAP65. | UCCL | On completion of GAP65 layer. On completion of ordinary backfill. | Photographs. Compaction test results. | P | W
Subbase | Wastewater Specification B.3.6 and B.3.7 FNDC Engineering Standards 3.3.3.3 and Sheet 31 | Visual inspection NDM testing | UCCL | NDM testing on completion of subbase layer, prior to installing basecourse. Backfill and compaction completed as per specifications. | Compaction records. Photographs. | P | W
Basecourse | Wastewater Specification B.3.6.2 FNDC Engineering Standards 3.3.3.4 and Sheet 31 | Visual inspection NDM testing | UCCL Haigh Workman | NDM testing on completion of basecourse layer, prior to sealing. Basecourse installed as per FNDC Engineering Standards, and NZTA B/02. | Compaction records. Photographs. | H | H
Detection Tape | Wastewater Specification B.7.5.1.6 FNDC Engineering Standards 5.3.3.1.2 | Visual inspection | UCCL | "Sewerage" detection tape laid directly above all wastewater pipelines. | Photographs. | P | W
Pipeline Testing | Wastewater Specification B.7.9.1 | Air test | UCCL Haigh Workman | Each section of pipeline is to be tested by 'Air Test', including Lunden junctions. | Drop in pressure shall not exceed 25mm over a period of 5 minutes. | H | H
Manhole Testing | Wastewater Specification B.7.9.1 | Visual inspection. Water test. | UCCL | Visual inspection of each manhole prior to backfilling. Water test after backfill. | Drop in level shall not exceed 5mm in 10 minutes. | H | H
Wastewater House Connections | Wastewater Specification B.7.8.10 | Visual inspection. Survey. | UCCL | On completion of each connection. | Photographs. As-built drawings. | P | W
Reinstate Driveways | Wastewater Specification B.3.8.5 | Visual inspection | UCCL | On completion of wastewater installation. Driveways reinstated in the same material and to the same standard as existing prior to works. | Photographs. | P | W
Reinstate Footpaths | Wastewater Specification B.3.8.5 | Visual inspection | UCCL | On completion of wastewater installation. Footpaths reinstated in the same material and dimensions as existing footpath, and constructed to FNDC Standards. | Photographs. | P | W
Reinstate Kerb and Channel | Wastewater Specification B.8.5 | Visual inspection | UCCL | Kerb and channel profiles match existing. Concrete has minimum 28-day strength of 25MPa. | Photographs. | P | W
Concrete Pour | Wastewater Specification B.4.4.2 | Prepour inspection | UCCL Haigh Workman | Prior to pouring concrete. | Pre-pour inspection checklist. Photographs. | P | W
Asphaltic Concrete Layer (DG10) | NZTA M10 Specification | As per NZTA M10 Specification | UCCL | On completion of the pavement surface. | Test results submitted to Engineer. Photographs. | P | W
Post Construction
As-Built Drawings | Wastewater Specification B.2.18.1 | As-built records and coordinate data | UCCL | Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion. Final as-builts issued prior to Final Completion. | As-builts submitted to the Engineer for approval. | S | A
CCTV | Wastewater Specification B.2.18.2 | CCTV video survey to the National Standards | UCCL | On completion of the installation of each pipeline with backfill to the top of the pipe. | CCTV results submitted to Engineer for approval. | S | A
RAMM Information | Wastewater Specifcation B.2.18.3 | RAMM information | UCCL | RAMM information submitted to the Engineer on completion of works. | RAMM information submitted to the Engineer. | S | A

## ITP - WW ConQA
INSPECTION & TEST PLAN
ITP - Wastewater Reticulation Upgrade
Location & Contract Details |  | SPECIFICATION REFERENCE | TEST/TASK REQUIRED
| Contract Details | Contract Name | Text Box
|  | Contract Number | Text Box
| Location | Location of Works | Text Box
Preconstruction
| Precondition Survey | Specification Reference: Wastewater Specification B.2.11.2.2 Test/Task Required: Visual inspection. Inspection By: UCCL Task Timing or Frequency: Prior to starting on site. Survey conducted of all surfaces, footpaths, kerbs, driveways and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works. Acceptance Criteria: Survey documents submitted to Engineer. | P, F, NA, Attachment
| Materials Quality | Specification Reference: FNDC Approved Materials List - Wastewater and Stormwater Test/Task Required: Visual Inspection. Task Timing or Frequency: Visual check for approved materials, quality and condition. Acceptance Criteria: Materials meet specifications or otherwise approved by Engineer. - Delivery dockets/Photos. | P, F, NA, Attachment
| Survey Setout | Specification Reference: Wastewater Specification B.2.11.2.4 Test/Task Required: Survey Setout Inspection By: UCCL Task Timing or Frequency: Prior to commencing each stage of work Acceptance Criteria: Survey setout as per IFC drawings. Check all MHs for levels, prior to constructing drainage lines, they must verify the inverts and locations of existing manholes as part of the inspection and testing process | P, F, NA, Attachment
| Service Location | Specification Reference: Wastewater Specification B.2.11.4.2 Test/Task Required: Locate underground services within work area. Inspection By: UCCL Task Timing or Frequency: Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services. | P, F, NA, Attachment
Installation
| Material Properties (Bedding) | Specification Reference: Wastewater Specification B.7.5.1.9 Test/Task Required: AP20 Grading curve to be submitted to Engineer for approval. Inspection By: UCCL, Accepted by Haigh Workman Task Timing or Task Frequency: Prior to using bedding material on site. PE bedding, pipe surround and haunching shall be AP20 in accordance with AS/NZS 2566. Acceptance Criteria: Bedding grading curve accepted by Engineer. | P, F, NA, Attachment
| Material Properties (Subbase - AP65) | Specification Reference: FNDC Engineering Standards 3.3.2 Test/Task Required: Subbase material meets FNDC Engineering Standards Inspection By: UCCL, Accepted by Haigh Workman Task Timing or Task Frequency: Prior to using subbase material on site. Acceptance Criteria: Subbase material test certificates accepted by Engineer. | P, F, NA, Attachment
| Material Properties (Basecourse - AP40) | Specification Reference:FNDC Engineering Standards 3.3.2 Test/Task Required: Bascourse material meets FNDC Engineering Standards Inspection By: UCCL Haigh Workman Task Timing or Task Frequency: Prior to using basecourse material on site. Acceptance Criteria: Basecourse material test certificates accepted by Engineer | P, F, NA, Attachment
| Pipe and Rubber Rings | Specification Reference: Wastewater Specification B.7.8.3 Test/Task Required: Visual inspection Inspection By: UCCL Task Timing or Task Frequency: Visual inspection prior to use (clean and free from defects). Acceptance Criteria: Photographs | P, F, NA, Attachment
| Pipeline Installation (PVC) | Wastewater Specification B.7.8 and B.7.9 FNDC Engineering Standards Sheet 31 Specification Reference: Wastewater Specification B.7.8 and B.7.9 FNDC Engineering Standards Sheet 31 Test/Task Required: Visual inspection Pipeline installed to correct alignment, grade and level Inspection By: UCCL Task Timing or Task Frequency: On completion of installation of each length of pipe, prior to backfilling. Throughout installation of pipeline. Horizontal alignment +100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe. Acceptance Criteria: As-built drawings. Photographs. | P, F, NA, Attachment
| Stainless Steel Pipe Bridge | Specification Reference: Wastewater Specification 'Package 3 - Bisset - Pipe Bridges Specification Test/Task Required: Visual inspection Pipe installed as per specification to correct alignment, grade and level Inspection By: UCCL Task Timing or Task Frequency: On completion of installation of each pipe bridge. Horizontal alignment + 100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe. Acceptance Criteria: As-built drawings. Photographs. | P, F, NA, Attachment
| Manhole Installation and Backfill | Specification Reference: Wastewater specification B.7.9 Test/Task Required: Visual inspection. Manhole checks including position, haunching, steps and sealed joints. Inspection By: UCCL Task Timing or Task Frequency: On completion of manhole installation. Acceptance Criteria: Falls through manholes are to be within +5mm of design levels. Maximum deviation from vertical (manholes/chambers) shall be 10mm per metre. | P, F, NA, Attachment
| Pipe Bedding | Specification Reference: Wastewater Specification B.3.4.1 FNDC Engineering Standards Sheet 31 Test/Task Required: Visual inspection. Compaction test on top of bedding. Inspection By: UCCL Task Timing or Task Frequency: Bedding installed as per specifications. Acceptance Criteria: Photographs/Compaction test results. | P, F, NA, Attachment
| Pipe Backfill (Outside of Carriageway) | Specification Reference: Wastewater Specification B.3.6.3 FNDC Engineering Standards Sheet 31 Test/Task Required: Visual inspection. Compaction test on top of GAP65. Inspection By: UCCL Task Timing or Task Frequency: On completion of GAP65 layer. On completion of ordinary backfill. Acceptance Criteria: Photographs. Compaction test results. | P, F, NA, Attachment
| Subbase | Specification Reference: Wastewater Specification B.3.6 and B.3.7 FNDC Engineering Standards 3.3.3.3 and Sheet 31 Test/Task Required: Visual inspection NDM testing Inspection By: UCCL Task Timing or Task Frequency: NDM testing on completion of subbase layer, prior to installing basecourse. Backfill and compaction completed as per specifications. Acceptance Criteria: Compaction records. Photographs. | P, F, NA, Attachment
| Basecourse | Specification Reference: Wastewater Specification B.3.6.2 FNDC Engineering Standards 3.3.3.4 and Sheet 31 Test/Task Required: Visual inspection NDM testing Inspection By: UCCL, Hold Point Haigh Workman Task Timing or Task Frequency: NDM testing on completion of basecourse layer, prior to sealing. Basecourse installed as per FNDC Engineering Standards, and NZTA B/02. Acceptance Criteria: Compaction records. Photographs. | Hold Point P, F, NA, Attachment
| Detection Tape | Specification Reference: Wastewater Specification B.7.5.1.6 FNDC Engineering Standards 5.3.3.1.2 Test/Task Required: Visual inspection Inspection By: UCCL Task Timing or Task Frequency: '"Sewerage" detection tape laid directly above all wastewater pipelines. Acceptance Criteria: Photographs. | P, F, NA, Attachment
| Pipeline Testing | Specification Reference: Wastewater Specification B.7.9.1 Test/Task Required: Air test Inspection By: Hold Point UCCL & Haigh Workman Task Timing or Task Frequency: Each section of pipeline is to be tested by 'Air Test', including Lunden junctions. Acceptance Criteria: Drop in pressure shall not exceed 25mm over a period of 5 minutes. | Hold Point P, F, NA, Attachment
| Manhole Testing | Wastewater Specification B.7.9.1 Specification Reference: Visual inspection. Water test. Test/Task Required: Visual Inspection & Water Test Inspection By: Hold Point UCCL & Haigh Workman Task Timing or Task Frequency: Visual inspection of each manhole prior to backfilling. Water test after backfill. Acceptance Criteria: Drop in level shall not exceed 5mm in 10 minutes. | Hold Point P, F, NA, Attachment
| Wastewater House Connections | Specification Reference: Wastewater Specification B.7.8.10 Test/Task Required: Visual inspection. Survey. Inspection By: UCCL Task Timing or Task Frequency: On completion of each connection. Acceptance Criteria: Photographs. As-built drawings. | P, F, NA, Attachment
| Reinstate Driveways | Specification Reference: Wastewater Specification B.3.8.5 Test/Task Required: Visual inspection Inspection By: UCCL Task Timing or Task Frequency: On completion of wastewater installation. Driveways reinstated in the same material and to the same standard as existing prior to works. Acceptance Criteria: Photographs. | P, F, NA, Attachment
| Reinstate Footpaths | Specification Reference: Wastewater Specification B.3.8.5 Test/Task Required: Visual inspection Inspection By: UCCL Task Timing or Task Frequency: On completion of wastewater installation. Footpaths reinstated in the same material and dimensions as existing footpath, and constructed to FNDC Standards. Acceptance Criteria: Photographs. | P, F, NA, Attachment
| Reinstate Kerb and Channel | Specification Reference: Wastewater Specification B.8.5 Test/Task Required: Visual inspection Inspection By: UCCL Task Timing or Task Frequency: Kerb and channel profiles match existing. Concrete has minimum 28-day strength of 25MPa. Acceptance Criteria: Photographs. | P, F, NA, Attachment
| Concrete Pour | Specification Reference: Wastewater Specification B.4.4.2 Test/Task Required: Prepour inspection Inspection By: UCCL/Haigh Workman Task Timing or Task Frequency: Prior to pouring concrete. Acceptance Criteria: Pre-pour inspection checklist. Photographs. | P, F, NA, Attachment
| Asphaltic Concrete Layer (DG10) | Specification Reference: NZTA M10 Specification Test/Task Required: As per NZTA M10 Specification Inspection By: UCCL Task Timing or Task Frequency: On completion of the pavement surface. Acceptance Criteria: Test results submitted to Engineer. Photographs. | P, F, NA, Attachment
Post Construction
| As-Built Drawings | Specification Reference: Wastewater Specification B.2.18.1 Test/Task Required: As-built records and coordinate data Inspection By: UCCL Task Timing or Task Frequency: Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion. Final as-builts issued prior to Final Completion. Acceptance Criteria: As-builts submitted to the Engineer for approval. | P, F, NA, Attachment
| CCTV | Specification Reference: Wastewater Specification B.2.18.2 Test/Task Required: CCTV video survey to the National Standards Inspection By: UCCL Task Timing or Task Frequency: On completion of the installation of each pipeline with backfill to the top of the pipe. Acceptance Criteria: CCTV results submitted to Engineer for approval. | P, F, NA, Attachment
| RAMM Information | Specification Reference: Wastewater Specifcation B.2.18.3 Test/Task Required: RAMM information Inspection By: UCCL Task Timing or Task Frequency: RAMM information submitted to the Engineer on completion of works. Acceptance Criteria: RAMM information submitted to the Engineer. | P, F, NA, Attachment