## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - Wastewater Reticulation Upgrade | itp
section | Location & Contract Details
checkpoint-no-status | Contract Details
textbox | Contract Name
textbox | Contract Number
checkpoint-no-status | Location
textbox | Location of Works
section | Preconstruction
checkpoint | Precondition Survey
label | Specification Reference: Wastewater Specification B.2.11.2.2
label | Test/Task Required: Visual inspection.
label | Inspection By: UCCL
label | Task Timing or Frequency: Prior to starting on site.
label | ○ Survey conducted of all surfaces, footpaths, kerbs, driveways and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works.
label | Acceptance Criteria: Survey documents submitted to Engineer.
checkpoint | Materials Quality
label | Specification Reference: FNDC Approved Materials List - Wastewater and Stormwater
label | Test/Task Required: Visual Inspection.
label | Task Timing or Frequency: Visual check for approved materials, quality and condition.
label | Acceptance Criteria: Materials meet specifications or otherwise approved by Engineer. - Delivery dockets/Photos.
checkpoint | Survey Setout
label | Specification Reference: Wastewater Specification B.2.11.2.4
label | Test/Task Required: Survey Setout
label | Inspection By: UCCL
label | Task Timing or Frequency: Prior to commencing each stage of work
label | Acceptance Criteria: Survey setout as per IFC drawings.
label | ○ Check all MHs for levels, prior to constructing drainage lines, they must verify the inverts and locations of existing manholes as part of the inspection and testing process
checkpoint | Service Location
label | Specification Reference: Wastewater Specification B.2.11.4.2
label | Test/Task Required: Locate underground services within work area.
label | Inspection By: UCCL
label | Task Timing or Frequency: Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services.
section | Installation
checkpoint | Material Properties (Bedding)
label | Specification Reference: Wastewater Specification B.7.5.1.9
label | Test/Task Required: AP20 Grading curve to be submitted to Engineer for approval.
label | Inspection By: UCCL, Accepted by Haigh Workman
label | Task Timing or Task Frequency: Prior to using bedding material on site.
label | ○ PE bedding, pipe surround and haunching shall be AP20 in accordance with AS/NZS 2566.
label | Acceptance Criteria: Bedding grading curve accepted by Engineer.
checkpoint | Material Properties (Subbase - AP65)
label | Specification Reference: FNDC Engineering Standards 3.3.2
label | Test/Task Required: Subbase material meets FNDC Engineering Standards
label | Inspection By: UCCL, Accepted by Haigh Workman
label | Task Timing or Task Frequency: Prior to using subbase material on site.
label | Acceptance Criteria: Subbase material test certificates accepted by Engineer.
checkpoint | Material Properties (Basecourse - AP40)
label | Specification Reference:FNDC Engineering Standards 3.3.2
label | Test/Task Required: Bascourse material meets FNDC Engineering Standards
label | Inspection By: UCCL
label | ○ Haigh Workman
label | Task Timing or Task Frequency: Prior to using basecourse material on site.
label | Acceptance Criteria: Basecourse material test certificates accepted by Engineer
checkpoint | Pipe and Rubber Rings
label | Specification Reference: Wastewater Specification B.7.8.3
label | Test/Task Required: Visual inspection
label | Inspection By: UCCL
label | Task Timing or Task Frequency: Visual inspection prior to use (clean and free from defects).
label | Acceptance Criteria: Photographs
checkpoint | Pipeline Installation (PVC)
label | ○ Wastewater Specification B.7.8 and B.7.9
label | ○ FNDC Engineering Standards Sheet 31
label | Specification Reference: Wastewater Specification B.7.8 and B.7.9
label | ○ FNDC Engineering Standards Sheet 31
label | Test/Task Required: Visual inspection
label | Pipeline installed to correct alignment, grade and level
label | Inspection By: UCCL
label | Task Timing or Task Frequency: On completion of installation of each length of pipe, prior to backfilling.
label | ○ Throughout installation of pipeline.
label | ○ Horizontal alignment +100mm.
label | ○ Vertical tolerance +/- 10% of the design grade for each section of pipe.
label | Acceptance Criteria: As-built drawings.
label | Photographs.
checkpoint | Stainless Steel Pipe Bridge
label | Specification Reference: Wastewater Specification 'Package 3 - Bisset - Pipe Bridges Specification
label | Test/Task Required: Visual inspection
label | ○ Pipe installed as per specification to correct alignment, grade and level
label | Inspection By: UCCL
label | Task Timing or Task Frequency: On completion of installation of each pipe bridge.
label | ○ Horizontal alignment + 100mm.
label | ○ Vertical tolerance +/- 10% of the design grade for each section of pipe.
label | Acceptance Criteria: As-built drawings.
label | ○ Photographs.
checkpoint | Manhole Installation and Backfill
label | Specification Reference: Wastewater specification B.7.9
label | Test/Task Required: Visual inspection.
label | ○ Manhole checks including position, haunching, steps and sealed joints.
label | Inspection By: UCCL
label | Task Timing or Task Frequency: On completion of manhole installation.
label | Acceptance Criteria: Falls through manholes are to be within +5mm of design levels.
label | ○ Maximum deviation from vertical (manholes/chambers) shall be 10mm per metre.
checkpoint | Pipe Bedding
label | Specification Reference: Wastewater Specification B.3.4.1
label | ○ FNDC Engineering Standards Sheet 31
label | Test/Task Required: Visual inspection.
label | ○ Compaction test on top of bedding.
label | Inspection By: UCCL
label | Task Timing or Task Frequency: Bedding installed as per specifications.
label | Acceptance Criteria: Photographs/Compaction test results.
checkpoint | Pipe Backfill (Outside of Carriageway)
label | Specification Reference: Wastewater Specification B.3.6.3
label | ○ FNDC Engineering Standards Sheet 31
label | Test/Task Required: Visual inspection.
label | ○ Compaction test on top of GAP65.
label | Inspection By: UCCL
label | Task Timing or Task Frequency: On completion of GAP65 layer.
label | ○ On completion of ordinary backfill.
label | Acceptance Criteria: Photographs.
label | ○ Compaction test results.
checkpoint | Subbase
label | Specification Reference: Wastewater Specification B.3.6 and B.3.7
label | ○ FNDC Engineering Standards 3.3.3.3 and Sheet 31
label | Test/Task Required: Visual inspection
label | ○ NDM testing
label | Inspection By: UCCL
label | Task Timing or Task Frequency: NDM testing on completion of subbase layer, prior to installing basecourse.
label | ○ Backfill and compaction completed as per specifications.
label | Acceptance Criteria: Compaction records.
label | ○ Photographs.
checkpoint | Basecourse
label | Specification Reference: Wastewater Specification B.3.6.2
label | ○ FNDC Engineering Standards 3.3.3.4 and Sheet 31
label | Test/Task Required: Visual inspection
label | ○ NDM testing
label | Inspection By: UCCL, Hold Point Haigh Workman
label | Task Timing or Task Frequency: NDM testing on completion of basecourse layer, prior to sealing.
label | ○ Basecourse installed as per FNDC Engineering Standards, and NZTA B/02.
label | Acceptance Criteria: Compaction records.
label | ○ Photographs.
holdpoint | HOLD POINT
checkpoint | Detection Tape
label | Specification Reference: Wastewater Specification B.7.5.1.6
label | ○ FNDC Engineering Standards 5.3.3.1.2
label | Test/Task Required: Visual inspection
label | Inspection By: UCCL
label | Task Timing or Task Frequency: '"Sewerage" detection tape laid directly above all wastewater pipelines.
label | Acceptance Criteria: Photographs.
checkpoint | Pipeline Testing
label | Specification Reference: Wastewater Specification B.7.9.1
label | Test/Task Required: Air test
label | Inspection By: Hold Point UCCL & Haigh Workman
label | Task Timing or Task Frequency: Each section of pipeline is to be tested by 'Air Test', including Lunden junctions.
label | Acceptance Criteria: Drop in pressure shall not exceed 25mm over a period of 5 minutes.
holdpoint | HOLD POINT
checkpoint | Manhole Testing
label | ○ Wastewater Specification B.7.9.1
label | Specification Reference: Visual inspection.
label | ○ Water test.
label | Test/Task Required: Visual Inspection & Water Test
label | Inspection By: Hold Point UCCL & Haigh Workman
label | Task Timing or Task Frequency: Visual inspection of each manhole prior to backfilling.
label | ○ Water test after backfill.
label | Acceptance Criteria: Drop in level shall not exceed 5mm in 10 minutes.
holdpoint | HOLD POINT
checkpoint | Wastewater House Connections
label | Specification Reference: Wastewater Specification B.7.8.10
label | Test/Task Required: Visual inspection.
label | ○ Survey.
label | Inspection By: UCCL
label | Task Timing or Task Frequency: On completion of each connection.
label | Acceptance Criteria: Photographs.
label | ○ As-built drawings.
checkpoint | Reinstate Driveways
label | Specification Reference: Wastewater Specification B.3.8.5
label | Test/Task Required: Visual inspection
label | Inspection By: UCCL
label | Task Timing or Task Frequency: On completion of wastewater installation.
label | ○ Driveways reinstated in the same material and to the same standard as existing prior to works.
label | Acceptance Criteria: Photographs.
checkpoint | Reinstate Footpaths
label | Specification Reference: Wastewater Specification B.3.8.5
label | Test/Task Required: Visual inspection
label | Inspection By: UCCL
label | Task Timing or Task Frequency: On completion of wastewater installation.
label | ○ Footpaths reinstated in the same material and dimensions as existing footpath, and constructed to FNDC Standards.
label | Acceptance Criteria: Photographs.
checkpoint | Reinstate Kerb and Channel
label | Specification Reference: Wastewater Specification B.8.5
label | Test/Task Required: Visual inspection
label | Inspection By: UCCL
label | Task Timing or Task Frequency: Kerb and channel profiles match existing.
label | ○ Concrete has minimum 28-day strength of 25MPa.
label | Acceptance Criteria: Photographs.
checkpoint | Concrete Pour
label | Specification Reference: Wastewater Specification B.4.4.2
label | Test/Task Required: Prepour inspection
label | Inspection By: UCCL/Haigh Workman
label | Task Timing or Task Frequency: Prior to pouring concrete.
label | Acceptance Criteria: Pre-pour inspection checklist.
label | ○ Photographs.
checkpoint | Asphaltic Concrete Layer (DG10)
label | Specification Reference: NZTA M10 Specification
label | Test/Task Required: As per NZTA M10 Specification
label | Inspection By: UCCL
label | Task Timing or Task Frequency: On completion of the pavement surface.
label | Acceptance Criteria: Test results submitted to Engineer.
label | ○ Photographs.
section | Post Construction
checkpoint | As-Built Drawings
label | Specification Reference: Wastewater Specification B.2.18.1
label | Test/Task Required: As-built records and coordinate data
label | Inspection By: UCCL
label | Task Timing or Task Frequency: Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion.
label | ○ Final as-builts issued prior to Final Completion.
label | Acceptance Criteria: As-builts submitted to the Engineer for approval.
checkpoint | CCTV
label | Specification Reference: Wastewater Specification B.2.18.2
label | Test/Task Required: CCTV video survey to the National Standards
label | Inspection By: UCCL
label | Task Timing or Task Frequency: On completion of the installation of each pipeline with backfill to the top of the pipe.
label | Acceptance Criteria: CCTV results submitted to Engineer for approval.
checkpoint | RAMM Information
label | Specification Reference: Wastewater Specifcation B.2.18.3
label | Test/Task Required: RAMM information
label | Inspection By: UCCL
label | Task Timing or Task Frequency: RAMM information submitted to the Engineer on completion of works.
label | Acceptance Criteria: RAMM information submitted to the Engineer.
checklist | ITP 01 - Bisset Road - Wastewater Reticulation Upgrade | itp
section | Preconstruction
checkpoint | Precondition Survey
label | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.2.2
label | TEST/TASK REQUIRED: Visual inspection.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Prior to starting on site.
label | ○ Survey conducted of all surfaces, footpaths, kerbs, driveways and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works.
label | ACCEPTANCE CRITERIA: Survey documents submitted to Engineer.
label | UCCL: P
label | Client: S
checkpoint | Materials Quality
label | SPECIFICATION REFERENCE: FNDC Approved Materials List - Wastewater and Stormwater
label | TEST/TASK REQUIRED: Visual check for approved materials, quality and condition.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On arrival to site, prior to using materials.
label | ACCEPTANCE CRITERIA: Materials meet specifications or otherwise approved by Engineer.
label | ○ Delivery dockets.
label | ○ Photos.
label | UCCL: W
label | Client: W
checkpoint | Survey Setout
label | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.2.4
label | TEST/TASK REQUIRED: Survey set out.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Prior to commencing each stage of work.
label | ACCEPTANCE CRITERIA: Survey set out as per IFC drawings.
label | UCCL: P
label | Client: W
label | COMMENTS: Check all MHs for levels, prior to constructing drainage lines, they must verify the inverts and locations of existing manholes as part of the inspection and testing process
checkpoint | Service Location
label | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.4.2
label | TEST/TASK REQUIRED: Locate underground services within work area.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services.
label | UCCL: P
label | Client: W
checkpoint | Material Properties (Bedding)
label | SPECIFICATION REFERENCE: Wastewater Specification B.7.5.1.9
label | TEST/TASK REQUIRED: AP20 Grading curve to be submitted to Engineer for approval.
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Prior to using bedding material on site.
label | ○ PE bedding, pipe surround and haunching shall be AP20 in accordance with AS/NZS 2566.
label | ACCEPTANCE CRITERIA: Bedding grading curve accepted by Engineer.
label | UCCL: S
label | Client: A
checkpoint | Material Properties (Subbase - AP65)
label | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
label | TEST/TASK REQUIRED: Subbase material meets FNDC Engineering Standards
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Prior to using subbase material on site.
label | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
label | UCCL: S
label | Client: A
checkpoint | Material Properties (Basecourse - AP40)
label | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
label | TEST/TASK REQUIRED: Bascourse material meets FNDC Engineering Standards
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Prior to using basecourse material on site.
label | ACCEPTANCE CRITERIA: Basecourse material test certificates accepted by Engineer.
label | UCCL: S
label | Client: A
checkpoint | Pipe and Rubber Rings
label | SPECIFICATION REFERENCE: Wastewater Specification B.7.8.3
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Visual inspection prior to use (clean and free from defects).
label | ACCEPTANCE CRITERIA: Photographs.
label | UCCL: W
label | Client: W
checkpoint | Pipeline Installation (PVC)
label | SPECIFICATION REFERENCE: Wastewater Specification B.7.8 and B.7.9
label | ○ FNDC Engineering Standards Sheet 31
label | TEST/TASK REQUIRED: Visual inspection
label | ○ Pipeline installed to correct alignment, grade and level
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of installation of each length of pipe, prior to backfilling.
label | ○ Throughout installation of pipeline.
label | ○ Horizontal alignment +100mm.
label | ○ Vertical tolerance +/- 10% of the design grade for each section of pipe.
label | ACCEPTANCE CRITERIA: As-built drawings.
label | ○ Photographs.
label | UCCL: P
label | Client: W
checkpoint | Stainless Steel Pipe Bridge
label | SPECIFICATION REFERENCE: Wastewater Specification 'Package 3 - Bisset - Pipe Bridges Specification
label | TEST/TASK REQUIRED: Visual inspection
label | ○ Pipe installed as per specification to correct alignment, grade and level
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of installation of each pipe bridge.
label | ○ Horizontal alignment + 100mm.
label | ○ Vertical tolerance +/- 10% of the design grade for each section of pipe.
label | ACCEPTANCE CRITERIA: As-built drawings.
label | ○ Photographs.
label | UCCL: P
label | Client: W
checkpoint | Manhole Installation and Backfill
label | SPECIFICATION REFERENCE: Wastewater specification B.7.9
label | TEST/TASK REQUIRED: Visual inspection.
label | ○ Manhole checks including position, haunching, steps and sealed joints.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of manhole installation.
label | ACCEPTANCE CRITERIA: Falls through manholes are to be within +5mm of design levels.
label | ○ Maximum deviation from vertical (manholes/chambers) shall be 10mm per metre.
label | UCCL: P
label | Client: W
checkpoint | Pipe Bedding
label | SPECIFICATION REFERENCE: Wastewater Specification B.3.4.1
label | ○ FNDC Engineering Standards Sheet 31
label | TEST/TASK REQUIRED: Visual inspection.
label | ○ Compaction test on top of bedding.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Bedding installed as per specifications.
label | ACCEPTANCE CRITERIA: Photographs.
label | ○ Compaction test results.
label | UCCL: P
label | Client: W
checkpoint | Pipe Backfill (Outside of Carriageway)
label | SPECIFICATION REFERENCE: Wastewater Specification B.3.6.3
label | ○ FNDC Engineering Standards Sheet 31
label | TEST/TASK REQUIRED: Visual inspection.
label | ○ Compaction test on top of GAP65.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of GAP65 layer.
label | ○ On completion of ordinary backfill.
label | ACCEPTANCE CRITERIA: Photographs.
label | ○ Compaction test results.
label | UCCL: P
label | Client: W
checkpoint | Subbase
label | SPECIFICATION REFERENCE: Wastewater Specification B.3.6 and B.3.7
label | ○ FNDC Engineering Standards 3.3.3.3 and Sheet 31
label | TEST/TASK REQUIRED: Visual inspection
label | ○ NDM testing
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of subbase layer, prior to installing basecourse.
label | ○ Backfill and compaction completed as per specifications.
label | ACCEPTANCE CRITERIA: Compaction records.
label | ○ Photographs.
label | UCCL: P
label | Client: W
checkpoint | Basecourse
label | SPECIFICATION REFERENCE: Wastewater Specification B.3.6.2
label | ○ FNDC Engineering Standards 3.3.3.4 and Sheet 31
label | TEST/TASK REQUIRED: Visual inspection
label | ○ NDM testing
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of basecourse layer, prior to sealing.
label | ○ Basecourse installed as per FNDC Engineering Standards, and NZTA B/02.
label | ACCEPTANCE CRITERIA: Compaction records.
label | ○ Photographs.
label | UCCL: H
label | Client: H
holdpoint | HOLD POINT
checkpoint | Detection Tape
label | SPECIFICATION REFERENCE: Wastewater Specification B.7.5.1.6
label | ○ FNDC Engineering Standards 5.3.3.1.2
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : "Sewerage" detection tape laid directly above all wastewater pipelines.
label | ACCEPTANCE CRITERIA: Photographs.
label | UCCL: P
label | Client: W
checkpoint | Pipeline Testing
label | SPECIFICATION REFERENCE: Wastewater Specification B.7.9.1
label | TEST/TASK REQUIRED: Air test
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Each section of pipeline is to be tested by 'Air Test', including Lunden junctions.
label | ACCEPTANCE CRITERIA: Drop in pressure shall not exceed 25mm over a period of 5 minutes.
label | UCCL: H
label | Client: H
holdpoint | HOLD POINT
checkpoint | Manhole Testing
label | SPECIFICATION REFERENCE: Wastewater Specification B.7.9.1
label | TEST/TASK REQUIRED: Visual inspection.
label | ○ Water test.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Visual inspection of each manhole prior to backfilling.
label | ○ Water test after backfill.
label | ACCEPTANCE CRITERIA: Drop in level shall not exceed 5mm in 10 minutes.
label | UCCL: H
label | Client: H
holdpoint | HOLD POINT
checkpoint | Wastewater House Connections
label | SPECIFICATION REFERENCE: Wastewater Specification B.7.8.10
label | TEST/TASK REQUIRED: Visual inspection.
label | ○ Survey.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of each connection.
label | ACCEPTANCE CRITERIA: Photographs.
label | ○ As-built drawings.
label | UCCL: P
label | Client: W
checkpoint | Reinstate Driveways
label | SPECIFICATION REFERENCE: Wastewater Specification B.3.8.5
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
label | ○ Driveways reinstated in the same material and to the same standard as existing prior to works.
label | ACCEPTANCE CRITERIA: Photographs.
label | UCCL: P
label | Client: W
checkpoint | Reinstate Footpaths
label | SPECIFICATION REFERENCE: Wastewater Specification B.3.8.5
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
label | ○ Footpaths reinstated in the same material and dimensions as existing footpath, and constructed to FNDC Standards.
label | ACCEPTANCE CRITERIA: Photographs.
label | UCCL: P
label | Client: W
checkpoint | Reinstate Kerb and Channel
label | SPECIFICATION REFERENCE: Wastewater Specification B.8.5
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Kerb and channel profiles match existing.
label | ○ Concrete has minimum 28-day strength of 25MPa.
label | ACCEPTANCE CRITERIA: Photographs.
label | UCCL: P
label | Client: W
checkpoint | Concrete Pour
label | SPECIFICATION REFERENCE: Wastewater Specification B.4.4.2
label | TEST/TASK REQUIRED: Prepour inspection
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete.
label | ACCEPTANCE CRITERIA: Pre-pour inspection checklist.
label | ○ Photographs.
label | UCCL: P
label | Client: W
checkpoint | Asphaltic Concrete Layer (DG10)
label | SPECIFICATION REFERENCE: NZTA M10 Specification
label | TEST/TASK REQUIRED: As per NZTA M10 Specification
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of the pavement surface.
label | ACCEPTANCE CRITERIA: Test results submitted to Engineer.
label | ○ Photographs.
label | UCCL: P
label | Client: W
checkpoint | As-Built Drawings
label | SPECIFICATION REFERENCE: Wastewater Specification B.2.18.1
label | TEST/TASK REQUIRED: As-built records and coordinate data
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion.
label | ○ Final as-builts issued prior to Final Completion.
label | ACCEPTANCE CRITERIA: As-builts submitted to the Engineer for approval.
label | UCCL: S
label | Client: A
checkpoint | CCTV
label | SPECIFICATION REFERENCE: Wastewater Specification B.2.18.2
label | TEST/TASK REQUIRED: CCTV video survey to the National Standards
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of the installation of each pipeline with backfill to the top of the pipe.
label | ACCEPTANCE CRITERIA: CCTV results submitted to Engineer for approval.
label | UCCL: S
label | Client: A
checkpoint | RAMM Information
label | SPECIFICATION REFERENCE: Wastewater Specifcation B.2.18.3
label | TEST/TASK REQUIRED: RAMM information
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : RAMM information submitted to the Engineer on completion of works.
label | ACCEPTANCE CRITERIA: RAMM information submitted to the Engineer.
label | UCCL: S
label | Client: A