## Sheet1
Precondition Survey | Wastewater Specification B.2.11.2.2 | Visual inspection. | UCCL | Prior to starting on site. Survey conducted of all surfaces, footpaths, kerbs, driveways and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works. | Survey documents submitted to Engineer. | P | S |  | Precondition Survey | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.2.2 | TEST/TASK REQUIRED: Visual inspection. | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : Prior to starting on site. Survey conducted of all surfaces, footpaths, kerbs, driveways and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works. | ACCEPTANCE CRITERIA: Survey documents submitted to Engineer. | UCCL: P | Client: S | COMMENTS: | Precondition Survey
Materials Quality | FNDC Approved Materials List - Wastewater and Stormwater | Visual check for approved materials, quality and condition. | UCCL | On arrival to site, prior to using materials. | Materials meet specifications or otherwise approved by Engineer. Delivery dockets. Photos. | W | W |  | Materials Quality | SPECIFICATION REFERENCE: FNDC Approved Materials List - Wastewater and Stormwater | TEST/TASK REQUIRED: Visual check for approved materials, quality and condition. | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : On arrival to site, prior to using materials. | ACCEPTANCE CRITERIA: Materials meet specifications or otherwise approved by Engineer. Delivery dockets. Photos. | UCCL: W | Client: W | COMMENTS: | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.2.2
Survey Setout | Wastewater Specification B.2.11.2.4 | Survey set out. | UCCL | Prior to commencing each stage of work. | Survey set out as per IFC drawings. | P | W | Check all MHs for levels, prior to constructing drainage lines, they must verify the inverts and locations of existing manholes as part of the inspection and testing process | Survey Setout | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.2.4 | TEST/TASK REQUIRED: Survey set out. | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : Prior to commencing each stage of work. | ACCEPTANCE CRITERIA: Survey set out as per IFC drawings. | UCCL: P | Client: W | COMMENTS: Check all MHs for levels, prior to constructing drainage lines, they must verify the inverts and locations of existing manholes as part of the inspection and testing process | TEST/TASK REQUIRED: Visual inspection.
Service Location | Wastewater Specification B.2.11.4.2 | Locate underground services within work area. | UCCL | Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services. |  | P | W |  | Service Location | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.4.2 | TEST/TASK REQUIRED: Locate underground services within work area. | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services. | ACCEPTANCE CRITERIA: | UCCL: P | Client: W | COMMENTS: | INSPECTION BY: UCCL
Material Properties (Bedding) | Wastewater Specification B.7.5.1.9 | AP20 Grading curve to be submitted to Engineer for approval. | UCCL Haigh Workman | Prior to using bedding material on site. PE bedding, pipe surround and haunching shall be AP20 in accordance with AS/NZS 2566. | Bedding grading curve accepted by Engineer. | S | A |  | Material Properties (Bedding) | SPECIFICATION REFERENCE: Wastewater Specification B.7.5.1.9 | TEST/TASK REQUIRED: AP20 Grading curve to be submitted to Engineer for approval. | INSPECTION BY: UCCL Haigh Workman | TASK TIMING OR TASK FREQUENCY : Prior to using bedding material on site. PE bedding, pipe surround and haunching shall be AP20 in accordance with AS/NZS 2566. | ACCEPTANCE CRITERIA: Bedding grading curve accepted by Engineer. | UCCL: S | Client: A | COMMENTS: | TASK TIMING OR TASK FREQUENCY : Prior to starting on site. Survey conducted of all surfaces, footpaths, kerbs, driveways and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works.
Material Properties (Subbase - AP65) | FNDC Engineering Standards 3.3.2 | Subbase material meets FNDC Engineering Standards | UCCL Haigh Workman | Prior to using subbase material on site. | Subbase material test certificates accepted by Engineer. | S | A |  | Material Properties (Subbase - AP65) | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2 | TEST/TASK REQUIRED: Subbase material meets FNDC Engineering Standards | INSPECTION BY: UCCL Haigh Workman | TASK TIMING OR TASK FREQUENCY : Prior to using subbase material on site. | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer. | UCCL: S | Client: A | COMMENTS: | ACCEPTANCE CRITERIA: Survey documents submitted to Engineer.
Material Properties (Basecourse - AP40) | FNDC Engineering Standards 3.3.2 | Bascourse material meets FNDC Engineering Standards | UCCL Haigh Workman | Prior to using basecourse material on site. | Basecourse material test certificates accepted by Engineer. | S | A |  | Material Properties (Basecourse - AP40) | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2 | TEST/TASK REQUIRED: Bascourse material meets FNDC Engineering Standards | INSPECTION BY: UCCL Haigh Workman | TASK TIMING OR TASK FREQUENCY : Prior to using basecourse material on site. | ACCEPTANCE CRITERIA: Basecourse material test certificates accepted by Engineer. | UCCL: S | Client: A | COMMENTS: | UCCL: P
Pipe and Rubber Rings | Wastewater Specification B.7.8.3 | Visual inspection | UCCL | Visual inspection prior to use (clean and free from defects). | Photographs. | W | W |  | Pipe and Rubber Rings | SPECIFICATION REFERENCE: Wastewater Specification B.7.8.3 | TEST/TASK REQUIRED: Visual inspection | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : Visual inspection prior to use (clean and free from defects). | ACCEPTANCE CRITERIA: Photographs. | UCCL: W | Client: W | COMMENTS: | Client: S
Pipeline Installation (PVC) | Wastewater Specification B.7.8 and B.7.9 FNDC Engineering Standards Sheet 31 | Visual inspection Pipeline installed to correct alignment, grade and level | UCCL | On completion of installation of each length of pipe, prior to backfilling. Throughout installation of pipeline. Horizontal alignment +100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe. | As-built drawings. Photographs. | P | W |  | Pipeline Installation (PVC) | SPECIFICATION REFERENCE: Wastewater Specification B.7.8 and B.7.9 FNDC Engineering Standards Sheet 31 | TEST/TASK REQUIRED: Visual inspection Pipeline installed to correct alignment, grade and level | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : On completion of installation of each length of pipe, prior to backfilling. Throughout installation of pipeline. Horizontal alignment +100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe. | ACCEPTANCE CRITERIA: As-built drawings. Photographs. | UCCL: P | Client: W | COMMENTS: | COMMENTS:
Stainless Steel Pipe Bridge | Wastewater Specification 'Package 3 - Bisset - Pipe Bridges Specification | Visual inspection Pipe installed as per specification to correct alignment, grade and level | UCCL | On completion of installation of each pipe bridge. Horizontal alignment + 100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe. | As-built drawings. Photographs. | P | W |  | Stainless Steel Pipe Bridge | SPECIFICATION REFERENCE: Wastewater Specification 'Package 3 - Bisset - Pipe Bridges Specification | TEST/TASK REQUIRED: Visual inspection Pipe installed as per specification to correct alignment, grade and level | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : On completion of installation of each pipe bridge. Horizontal alignment + 100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe. | ACCEPTANCE CRITERIA: As-built drawings. Photographs. | UCCL: P | Client: W | COMMENTS: | Materials Quality
Manhole Installation and Backfill | Wastewater specification B.7.9 | Visual inspection. Manhole checks including position, haunching, steps and sealed joints. | UCCL | On completion of manhole installation. | Falls through manholes are to be within +5mm of design levels. Maximum deviation from vertical (manholes/chambers) shall be 10mm per metre. | P | W |  | Manhole Installation and Backfill | SPECIFICATION REFERENCE: Wastewater specification B.7.9 | TEST/TASK REQUIRED: Visual inspection. Manhole checks including position, haunching, steps and sealed joints. | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : On completion of manhole installation. | ACCEPTANCE CRITERIA: Falls through manholes are to be within +5mm of design levels. Maximum deviation from vertical (manholes/chambers) shall be 10mm per metre. | UCCL: P | Client: W | COMMENTS: | SPECIFICATION REFERENCE: FNDC Approved Materials List - Wastewater and Stormwater
Pipe Bedding | Wastewater Specification B.3.4.1 FNDC Engineering Standards Sheet 31 | Visual inspection. Compaction test on top of bedding. | UCCL | Bedding installed as per specifications. | Photographs. Compaction test results. | P | W |  | Pipe Bedding | SPECIFICATION REFERENCE: Wastewater Specification B.3.4.1 FNDC Engineering Standards Sheet 31 | TEST/TASK REQUIRED: Visual inspection. Compaction test on top of bedding. | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : Bedding installed as per specifications. | ACCEPTANCE CRITERIA: Photographs. Compaction test results. | UCCL: P | Client: W | COMMENTS: | TEST/TASK REQUIRED: Visual check for approved materials, quality and condition.
Pipe Backfill (Outside of Carriageway) | Wastewater Specification B.3.6.3 FNDC Engineering Standards Sheet 31 | Visual inspection. Compaction test on top of GAP65. | UCCL | On completion of GAP65 layer. On completion of ordinary backfill. | Photographs. Compaction test results. | P | W |  | Pipe Backfill (Outside of Carriageway) | SPECIFICATION REFERENCE: Wastewater Specification B.3.6.3 FNDC Engineering Standards Sheet 31 | TEST/TASK REQUIRED: Visual inspection. Compaction test on top of GAP65. | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : On completion of GAP65 layer. On completion of ordinary backfill. | ACCEPTANCE CRITERIA: Photographs. Compaction test results. | UCCL: P | Client: W | COMMENTS: | INSPECTION BY: UCCL
Subbase | Wastewater Specification B.3.6 and B.3.7 FNDC Engineering Standards 3.3.3.3 and Sheet 31 | Visual inspection NDM testing | UCCL | NDM testing on completion of subbase layer, prior to installing basecourse. Backfill and compaction completed as per specifications. | Compaction records. Photographs. | P | W |  | Subbase | SPECIFICATION REFERENCE: Wastewater Specification B.3.6 and B.3.7 FNDC Engineering Standards 3.3.3.3 and Sheet 31 | TEST/TASK REQUIRED: Visual inspection NDM testing | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of subbase layer, prior to installing basecourse. Backfill and compaction completed as per specifications. | ACCEPTANCE CRITERIA: Compaction records. Photographs. | UCCL: P | Client: W | COMMENTS: | TASK TIMING OR TASK FREQUENCY : On arrival to site, prior to using materials.
Basecourse | Wastewater Specification B.3.6.2 FNDC Engineering Standards 3.3.3.4 and Sheet 31 | Visual inspection NDM testing | UCCL Haigh Workman | NDM testing on completion of basecourse layer, prior to sealing. Basecourse installed as per FNDC Engineering Standards, and NZTA B/02. | Compaction records. Photographs. | H | H |  | Basecourse | SPECIFICATION REFERENCE: Wastewater Specification B.3.6.2 FNDC Engineering Standards 3.3.3.4 and Sheet 31 | TEST/TASK REQUIRED: Visual inspection NDM testing | INSPECTION BY: UCCL Haigh Workman | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of basecourse layer, prior to sealing. Basecourse installed as per FNDC Engineering Standards, and NZTA B/02. | ACCEPTANCE CRITERIA: Compaction records. Photographs. | UCCL: H | Client: H | COMMENTS: | ACCEPTANCE CRITERIA: Materials meet specifications or otherwise approved by Engineer. Delivery dockets. Photos.
Detection Tape | Wastewater Specification B.7.5.1.6 FNDC Engineering Standards 5.3.3.1.2 | Visual inspection | UCCL | "Sewerage" detection tape laid directly above all wastewater pipelines. | Photographs. | P | W |  | Detection Tape | SPECIFICATION REFERENCE: Wastewater Specification B.7.5.1.6 FNDC Engineering Standards 5.3.3.1.2 | TEST/TASK REQUIRED: Visual inspection | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : "Sewerage" detection tape laid directly above all wastewater pipelines. | ACCEPTANCE CRITERIA: Photographs. | UCCL: P | Client: W | COMMENTS: | UCCL: W
Pipeline Testing | Wastewater Specification B.7.9.1 | Air test | UCCL Haigh Workman | Each section of pipeline is to be tested by 'Air Test', including Lunden junctions. | Drop in pressure shall not exceed 25mm over a period of 5 minutes. | H | H |  | Pipeline Testing | SPECIFICATION REFERENCE: Wastewater Specification B.7.9.1 | TEST/TASK REQUIRED: Air test | INSPECTION BY: UCCL Haigh Workman | TASK TIMING OR TASK FREQUENCY : Each section of pipeline is to be tested by 'Air Test', including Lunden junctions. | ACCEPTANCE CRITERIA: Drop in pressure shall not exceed 25mm over a period of 5 minutes. | UCCL: H | Client: H | COMMENTS: | Client: W
Manhole Testing | Wastewater Specification B.7.9.1 | Visual inspection. Water test. | UCCL | Visual inspection of each manhole prior to backfilling. Water test after backfill. | Drop in level shall not exceed 5mm in 10 minutes. | H | H |  | Manhole Testing | SPECIFICATION REFERENCE: Wastewater Specification B.7.9.1 | TEST/TASK REQUIRED: Visual inspection. Water test. | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : Visual inspection of each manhole prior to backfilling. Water test after backfill. | ACCEPTANCE CRITERIA: Drop in level shall not exceed 5mm in 10 minutes. | UCCL: H | Client: H | COMMENTS: | COMMENTS:
Wastewater House Connections | Wastewater Specification B.7.8.10 | Visual inspection. Survey. | UCCL | On completion of each connection. | Photographs. As-built drawings. | P | W |  | Wastewater House Connections | SPECIFICATION REFERENCE: Wastewater Specification B.7.8.10 | TEST/TASK REQUIRED: Visual inspection. Survey. | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : On completion of each connection. | ACCEPTANCE CRITERIA: Photographs. As-built drawings. | UCCL: P | Client: W | COMMENTS: | Survey Setout
Reinstate Driveways | Wastewater Specification B.3.8.5 | Visual inspection | UCCL | On completion of wastewater installation. Driveways reinstated in the same material and to the same standard as existing prior to works. | Photographs. | P | W |  | Reinstate Driveways | SPECIFICATION REFERENCE: Wastewater Specification B.3.8.5 | TEST/TASK REQUIRED: Visual inspection | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation. Driveways reinstated in the same material and to the same standard as existing prior to works. | ACCEPTANCE CRITERIA: Photographs. | UCCL: P | Client: W | COMMENTS: | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.2.4
Reinstate Footpaths | Wastewater Specification B.3.8.5 | Visual inspection | UCCL | On completion of wastewater installation. Footpaths reinstated in the same material and dimensions as existing footpath, and constructed to FNDC Standards. | Photographs. | P | W |  | Reinstate Footpaths | SPECIFICATION REFERENCE: Wastewater Specification B.3.8.5 | TEST/TASK REQUIRED: Visual inspection | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation. Footpaths reinstated in the same material and dimensions as existing footpath, and constructed to FNDC Standards. | ACCEPTANCE CRITERIA: Photographs. | UCCL: P | Client: W | COMMENTS: | TEST/TASK REQUIRED: Survey set out.
Reinstate Kerb and Channel | Wastewater Specification B.8.5 | Visual inspection | UCCL | Kerb and channel profiles match existing. Concrete has minimum 28-day strength of 25MPa. | Photographs. | P | W |  | Reinstate Kerb and Channel | SPECIFICATION REFERENCE: Wastewater Specification B.8.5 | TEST/TASK REQUIRED: Visual inspection | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : Kerb and channel profiles match existing. Concrete has minimum 28-day strength of 25MPa. | ACCEPTANCE CRITERIA: Photographs. | UCCL: P | Client: W | COMMENTS: | INSPECTION BY: UCCL
Concrete Pour | Wastewater Specification B.4.4.2 | Prepour inspection | UCCL Haigh Workman | Prior to pouring concrete. | Pre-pour inspection checklist. Photographs. | P | W |  | Concrete Pour | SPECIFICATION REFERENCE: Wastewater Specification B.4.4.2 | TEST/TASK REQUIRED: Prepour inspection | INSPECTION BY: UCCL Haigh Workman | TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete. | ACCEPTANCE CRITERIA: Pre-pour inspection checklist. Photographs. | UCCL: P | Client: W | COMMENTS: | TASK TIMING OR TASK FREQUENCY : Prior to commencing each stage of work.
Asphaltic Concrete Layer (DG10) | NZTA M10 Specification | As per NZTA M10 Specification | UCCL | On completion of the pavement surface. | Test results submitted to Engineer. Photographs. | P | W |  | Asphaltic Concrete Layer (DG10) | SPECIFICATION REFERENCE: NZTA M10 Specification | TEST/TASK REQUIRED: As per NZTA M10 Specification | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : On completion of the pavement surface. | ACCEPTANCE CRITERIA: Test results submitted to Engineer. Photographs. | UCCL: P | Client: W | COMMENTS: | ACCEPTANCE CRITERIA: Survey set out as per IFC drawings.
As-Built Drawings | Wastewater Specification B.2.18.1 | As-built records and coordinate data | UCCL | Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion. Final as-builts issued prior to Final Completion. | As-builts submitted to the Engineer for approval. | S | A |  | As-Built Drawings | SPECIFICATION REFERENCE: Wastewater Specification B.2.18.1 | TEST/TASK REQUIRED: As-built records and coordinate data | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion. Final as-builts issued prior to Final Completion. | ACCEPTANCE CRITERIA: As-builts submitted to the Engineer for approval. | UCCL: S | Client: A | COMMENTS: | UCCL: P
CCTV | Wastewater Specification B.2.18.2 | CCTV video survey to the National Standards | UCCL | On completion of the installation of each pipeline with backfill to the top of the pipe. | CCTV results submitted to Engineer for approval. | S | A |  | CCTV | SPECIFICATION REFERENCE: Wastewater Specification B.2.18.2 | TEST/TASK REQUIRED: CCTV video survey to the National Standards | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : On completion of the installation of each pipeline with backfill to the top of the pipe. | ACCEPTANCE CRITERIA: CCTV results submitted to Engineer for approval. | UCCL: S | Client: A | COMMENTS: | Client: W
RAMM Information | Wastewater Specifcation B.2.18.3 | RAMM information | UCCL | RAMM information submitted to the Engineer on completion of works. | RAMM information submitted to the Engineer. | S | A |  | RAMM Information | SPECIFICATION REFERENCE: Wastewater Specifcation B.2.18.3 | TEST/TASK REQUIRED: RAMM information | INSPECTION BY: UCCL | TASK TIMING OR TASK FREQUENCY : RAMM information submitted to the Engineer on completion of works. | ACCEPTANCE CRITERIA: RAMM information submitted to the Engineer. | UCCL: S | Client: A | COMMENTS: | COMMENTS: Check all MHs for levels, prior to constructing drainage lines, they must verify the inverts and locations of existing manholes as part of the inspection and testing process
Service Location
SPECIFICATION REFERENCE: Wastewater Specification B.2.11.4.2
TEST/TASK REQUIRED: Locate underground services within work area.
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services.
ACCEPTANCE CRITERIA:
UCCL: P
Client: W
COMMENTS:
Material Properties (Bedding)
SPECIFICATION REFERENCE: Wastewater Specification B.7.5.1.9
TEST/TASK REQUIRED: AP20 Grading curve to be submitted to Engineer for approval.
INSPECTION BY: UCCL Haigh Workman
TASK TIMING OR TASK FREQUENCY : Prior to using bedding material on site. PE bedding, pipe surround and haunching shall be AP20 in accordance with AS/NZS 2566.
ACCEPTANCE CRITERIA: Bedding grading curve accepted by Engineer.
UCCL: S
Client: A
COMMENTS:
Material Properties (Subbase - AP65)
SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
TEST/TASK REQUIRED: Subbase material meets FNDC Engineering Standards
INSPECTION BY: UCCL Haigh Workman
TASK TIMING OR TASK FREQUENCY : Prior to using subbase material on site.
ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
UCCL: S
Client: A
COMMENTS:
Material Properties (Basecourse - AP40)
SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
TEST/TASK REQUIRED: Bascourse material meets FNDC Engineering Standards
INSPECTION BY: UCCL Haigh Workman
TASK TIMING OR TASK FREQUENCY : Prior to using basecourse material on site.
ACCEPTANCE CRITERIA: Basecourse material test certificates accepted by Engineer.
UCCL: S
Client: A
COMMENTS:
Pipe and Rubber Rings
SPECIFICATION REFERENCE: Wastewater Specification B.7.8.3
TEST/TASK REQUIRED: Visual inspection
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : Visual inspection prior to use (clean and free from defects).
ACCEPTANCE CRITERIA: Photographs.
UCCL: W
Client: W
COMMENTS:
Pipeline Installation (PVC)
SPECIFICATION REFERENCE: Wastewater Specification B.7.8 and B.7.9 FNDC Engineering Standards Sheet 31
TEST/TASK REQUIRED: Visual inspection Pipeline installed to correct alignment, grade and level
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : On completion of installation of each length of pipe, prior to backfilling. Throughout installation of pipeline. Horizontal alignment +100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe.
ACCEPTANCE CRITERIA: As-built drawings. Photographs.
UCCL: P
Client: W
COMMENTS:
Stainless Steel Pipe Bridge
SPECIFICATION REFERENCE: Wastewater Specification 'Package 3 - Bisset - Pipe Bridges Specification
TEST/TASK REQUIRED: Visual inspection Pipe installed as per specification to correct alignment, grade and level
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : On completion of installation of each pipe bridge. Horizontal alignment + 100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe.
ACCEPTANCE CRITERIA: As-built drawings. Photographs.
UCCL: P
Client: W
COMMENTS:
Manhole Installation and Backfill
SPECIFICATION REFERENCE: Wastewater specification B.7.9
TEST/TASK REQUIRED: Visual inspection. Manhole checks including position, haunching, steps and sealed joints.
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : On completion of manhole installation.
ACCEPTANCE CRITERIA: Falls through manholes are to be within +5mm of design levels. Maximum deviation from vertical (manholes/chambers) shall be 10mm per metre.
UCCL: P
Client: W
COMMENTS:
Pipe Bedding
SPECIFICATION REFERENCE: Wastewater Specification B.3.4.1 FNDC Engineering Standards Sheet 31
TEST/TASK REQUIRED: Visual inspection. Compaction test on top of bedding.
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : Bedding installed as per specifications.
ACCEPTANCE CRITERIA: Photographs. Compaction test results.
UCCL: P
Client: W
COMMENTS:
Pipe Backfill (Outside of Carriageway)
SPECIFICATION REFERENCE: Wastewater Specification B.3.6.3 FNDC Engineering Standards Sheet 31
TEST/TASK REQUIRED: Visual inspection. Compaction test on top of GAP65.
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : On completion of GAP65 layer. On completion of ordinary backfill.
ACCEPTANCE CRITERIA: Photographs. Compaction test results.
UCCL: P
Client: W
COMMENTS:
Subbase
SPECIFICATION REFERENCE: Wastewater Specification B.3.6 and B.3.7 FNDC Engineering Standards 3.3.3.3 and Sheet 31
TEST/TASK REQUIRED: Visual inspection NDM testing
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : NDM testing on completion of subbase layer, prior to installing basecourse. Backfill and compaction completed as per specifications.
ACCEPTANCE CRITERIA: Compaction records. Photographs.
UCCL: P
Client: W
COMMENTS:
Basecourse
SPECIFICATION REFERENCE: Wastewater Specification B.3.6.2 FNDC Engineering Standards 3.3.3.4 and Sheet 31
TEST/TASK REQUIRED: Visual inspection NDM testing
INSPECTION BY: UCCL Haigh Workman
TASK TIMING OR TASK FREQUENCY : NDM testing on completion of basecourse layer, prior to sealing. Basecourse installed as per FNDC Engineering Standards, and NZTA B/02.
ACCEPTANCE CRITERIA: Compaction records. Photographs.
UCCL: H
Client: H
COMMENTS:
Detection Tape
SPECIFICATION REFERENCE: Wastewater Specification B.7.5.1.6 FNDC Engineering Standards 5.3.3.1.2
TEST/TASK REQUIRED: Visual inspection
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : "Sewerage" detection tape laid directly above all wastewater pipelines.
ACCEPTANCE CRITERIA: Photographs.
UCCL: P
Client: W
COMMENTS:
Pipeline Testing
SPECIFICATION REFERENCE: Wastewater Specification B.7.9.1
TEST/TASK REQUIRED: Air test
INSPECTION BY: UCCL Haigh Workman
TASK TIMING OR TASK FREQUENCY : Each section of pipeline is to be tested by 'Air Test', including Lunden junctions.
ACCEPTANCE CRITERIA: Drop in pressure shall not exceed 25mm over a period of 5 minutes.
UCCL: H
Client: H
COMMENTS:
Manhole Testing
SPECIFICATION REFERENCE: Wastewater Specification B.7.9.1
TEST/TASK REQUIRED: Visual inspection. Water test.
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : Visual inspection of each manhole prior to backfilling. Water test after backfill.
ACCEPTANCE CRITERIA: Drop in level shall not exceed 5mm in 10 minutes.
UCCL: H
Client: H
COMMENTS:
Wastewater House Connections
SPECIFICATION REFERENCE: Wastewater Specification B.7.8.10
TEST/TASK REQUIRED: Visual inspection. Survey.
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : On completion of each connection.
ACCEPTANCE CRITERIA: Photographs. As-built drawings.
UCCL: P
Client: W
COMMENTS:
Reinstate Driveways
SPECIFICATION REFERENCE: Wastewater Specification B.3.8.5
TEST/TASK REQUIRED: Visual inspection
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation. Driveways reinstated in the same material and to the same standard as existing prior to works.
ACCEPTANCE CRITERIA: Photographs.
UCCL: P
Client: W
COMMENTS:
Reinstate Footpaths
SPECIFICATION REFERENCE: Wastewater Specification B.3.8.5
TEST/TASK REQUIRED: Visual inspection
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation. Footpaths reinstated in the same material and dimensions as existing footpath, and constructed to FNDC Standards.
ACCEPTANCE CRITERIA: Photographs.
UCCL: P
Client: W
COMMENTS:
Reinstate Kerb and Channel
SPECIFICATION REFERENCE: Wastewater Specification B.8.5
TEST/TASK REQUIRED: Visual inspection
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : Kerb and channel profiles match existing. Concrete has minimum 28-day strength of 25MPa.
ACCEPTANCE CRITERIA: Photographs.
UCCL: P
Client: W
COMMENTS:
Concrete Pour
SPECIFICATION REFERENCE: Wastewater Specification B.4.4.2
TEST/TASK REQUIRED: Prepour inspection
INSPECTION BY: UCCL Haigh Workman
TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete.
ACCEPTANCE CRITERIA: Pre-pour inspection checklist. Photographs.
UCCL: P
Client: W
COMMENTS:
Asphaltic Concrete Layer (DG10)
SPECIFICATION REFERENCE: NZTA M10 Specification
TEST/TASK REQUIRED: As per NZTA M10 Specification
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : On completion of the pavement surface.
ACCEPTANCE CRITERIA: Test results submitted to Engineer. Photographs.
UCCL: P
Client: W
COMMENTS:
As-Built Drawings
SPECIFICATION REFERENCE: Wastewater Specification B.2.18.1
TEST/TASK REQUIRED: As-built records and coordinate data
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion. Final as-builts issued prior to Final Completion.
ACCEPTANCE CRITERIA: As-builts submitted to the Engineer for approval.
UCCL: S
Client: A
COMMENTS:
CCTV
SPECIFICATION REFERENCE: Wastewater Specification B.2.18.2
TEST/TASK REQUIRED: CCTV video survey to the National Standards
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : On completion of the installation of each pipeline with backfill to the top of the pipe.
ACCEPTANCE CRITERIA: CCTV results submitted to Engineer for approval.
UCCL: S
Client: A
COMMENTS:
RAMM Information
SPECIFICATION REFERENCE: Wastewater Specifcation B.2.18.3
TEST/TASK REQUIRED: RAMM information
INSPECTION BY: UCCL
TASK TIMING OR TASK FREQUENCY : RAMM information submitted to the Engineer on completion of works.
ACCEPTANCE CRITERIA: RAMM information submitted to the Engineer.
UCCL: S
Client: A
COMMENTS: