## Master List Templates
Id | Type | Name | Values | Prompting Name
98f3e20c-7459-44a1-acf3-d606bbabcc8c | checklist | Add Heyday On-site Penetration Register |  | Heyday On-site Penetration Register
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
59c53197-7f17-4c08-bf34-cbdecd6a2185 | checkpoint-no-value | Fire Stopping System No.
672e6ca0-d27f-5ade-be47-cadc764e3fd6 | dropdown | Select System No. | FAS190329 - Conduits within concrete,27912900 - Conduit through FRL
e82129a9-505d-4e71-b755-ee0177a1c10c | checkpoint-no-value | Penetration Type
cc41d543-a0b2-5338-bccb-350edabe3c42 | dropdown | Select Type | Floor,Wall,Ceiling
131473b5-4685-4902-9704-23cc5b0c0dad | checkpoint-no-value | Location
faf0f92a-b611-5142-9cc5-1997de933838 | textbox | Location:
0c4e0a22-6611-460c-a28a-e063b47bc23b | checkpoint-no-value | FRL
ff51926a-ed3a-538f-be24-62136736cc0a | dropdown | Select FRL | ~ / 120 / 120
9f625aa4-64a1-4726-aa04-9e338bb01d63 | checkpoint-no-value | Service Description
964bec46-4098-5d46-8d97-65a3ffddbac9 | dropdown | Select Description | Conduits within concrete,Concrete through FR compartment
3ce1e2b8-4527-4c0f-8dfd-51303366e887 | checkpoint | Photo of Fire Sealing & Label
fdca44a3-a610-4a4a-a0ea-7da07a734c72 | checklist | Communications - Cabinet |  | Cabinet
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a6b5c039-9104-4d59-ab1d-6bfb5762edd5 | checkpoint | Confirm rack has been earthed
83c98af0-89bb-42b3-871e-fe93cc9cd729 | checkpoint | Confirm cabinet has seismic fixings and bayed together.
0a237f42-78de-4a32-b6a8-8d1d0024fc3d | checkpoint | Confirm cable management installed
c1084f6e-3980-4a5c-8269-2e82fcc13c33 | checkpoint | Confirm cabinet has asset managed label on front and rear
cc59b323-0b74-425c-8606-50e8f1820b7c | checkpoint | Confirm Cabinet is correct orientation
7ea45823-f0f0-4797-a3d6-e4ef97ffaa13 | checkpoint | Confirm PDU-A and PDU-B are on correct side and plugged into correct power supply
2ff22c34-eb26-4df6-afa8-2ad76c2cc4a7 | signoff | Checked By (Heyday/MDE):
b1832b7a-a98e-4f92-936f-06626789fef8 | checklist | Communications - Copper |  | Copper
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
76c3fe8f-3ddc-4a5e-a05c-ba977ab9a969 | checkpoint | Cabling is not susceptible to mechanical damage.
e18f9918-2b47-40e2-91f9-5482c3f7b9ec | checkpoint | Cable is dressed on the cable pathways with velcro.
eee317b7-8f5b-4eb2-883e-61d2e1a00f59 | checkpoint | Apply a plastic wrap printed label to each end of the cable.
2f3a1f84-388b-47df-90de-dde96ff660f7 | checkpoint | Cable is terminated into a faceplate or surface mount block.
78caadc4-7dd4-4b82-a55a-b5670488ad92 | checkpoint | Cable is terminated into the correct patch panel reflected in the communication cabinet elevations.
fe7c9542-22b6-49bb-8910-c5e9721757f7 | checkpoint | The patch panel, faceplate/surface mount block are labelled correctly with a traffolyte.
dfbecaf3-200a-4be9-8412-b04a17a436d1 | signoff | Checked By (Heyday/MDE):
d80c0715-f329-4661-9a44-68e4b5a51855 | checklist | Communications - Fibre |  | Fibre
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
e2737053-d94a-48c5-b40d-ea6cb9f0e5d8 | checkpoint | Cabling is not susceptible to mechanical damage.
c283b042-76d5-463a-8cca-eae28e34775a | checkpoint | Cable is dressed on the cable pathways with velcro.
0f151bed-084f-43d3-bbb6-d3158693983c | checkpoint | Apply a plastic traffolyte label to each end of the cable.
434d0ada-b213-43de-a343-48e2bdb3bafb | checkpoint | Fibre optic reticulates into cabinet correctly and is terminated into fobot.
361e5676-c9be-450d-b966-9efe3d620a60 | checkpoint | Fobots is labelled correctly with traffolyte.
716f9a14-a9e5-4c50-ad9f-89cc55535c35 | signoff | Checked By (Heyday/MDE):
6074ec10-56f3-4474-abae-aef805bb6293 | checklist | ITP |  | ITP
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
652e967d-7a17-434c-bf03-94f23854ac39 | checkpoint | Please attach copy of ITP
df71fccc-889f-4250-bc86-4df129d6a8ae | checklist | LOT BREAK UP |  | LOT BREAK UP
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
dcdf5328-e886-4cde-95f0-59dde8dc5444 | checkpoint | Attached Mark up of Lot Breakup
0768c84e-b3bd-4c6a-aa09-13255ac65d50 | checklist | Quality - Busduct |  | Quality - Busduct
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
b5e3fe26-c783-40f9-bcd4-eaf2b88586e1 | checkpoint | Receipt of busduct/ busway & take off box's delivery to site
a3ff3953-176a-4f1f-aa7e-1986d652eda6 | checkpoint | Set out - Ensure correct size, type and spare capacity
d6a046bc-7068-4c9b-9b6c-f8328e22b064 | checkpoint | Accessories to be factory made items
65db417e-1f27-4f5e-819c-78b92e4a29e3 | checkpoint | Hangers installed as per the drawings
299dea92-5f16-4433-a952-cfa942e266da | checkpoint | IR Test of Busduct - Separate - Test Result Above 1M Ω
8454a122-48a5-4d58-aebe-c3d8bdefcfe4 | checkpoint | Busduct Piece are installed safely
c87d056a-92e3-4209-8b5a-28c6bf6d1ea5 | checkpoint | Busduct Torqued to 95Nm
29e3b00e-cad7-45d1-917f-5c5cf497b715 | checkpoint | IR Test of Busduct - Joined - Test Result Above 1M Ω
ac33c530-7829-4181-9de4-04f2f3f3f53c | checkpoint | Photos attached of installed piece
1d378708-99dd-41cd-983b-c8c2d8a87dfb | checklist | Quality - Cable tray/Ladder |  | Quality - Cable tray/Ladder
a1a33c20-dbe1-4801-9203-04858f5d91c5 | section | Quality - Cable tray/Ladder
f7304667-4e24-48f5-86d3-64ffdb1e21d2 | checkpoint | Receipt of Cable Tray delivery to site & storage
2bd9f9cf-263c-476d-95d4-0a08b088bef3 | checkpoint | Set out to be confirmed with latest AFC Drawings
e64772dd-b6dd-4bf5-8a12-dc36b7263180 | checkpoint | Accessories to be factory made items
fc0f799c-8b1b-4379-bc47-2f292f97907c | checkpoint | Correct Levelling & Alignment
b080b835-d7b7-432f-a0c0-8ab4fe9b2f95 | checkpoint | correct bracket and safe fixing
4a33f2d3-208c-4b01-be48-6274464e9497 | checkpoint | Correct Bends used (Cable Ladder)
3928498c-2649-4de9-8894-ce6451f89040 | checkpoint | Cable Tray Checked For Sharp Edges
818b9572-aaf8-4143-80ad-91e2dbb47f32 | checkpoint | Containment Earthing - As Per the Standards
ec96a558-76fa-48dd-91b2-bf90d58d063c | signoff | Signoff Required from Heyday & Head Contractor
2d94ecbf-4577-48d4-8ae1-f2e0f5ca54ef | checkpoint | Photos attached.
f5d4527b-a4f5-4f85-a73d-8bb4269b0fe5 | checklist | Quality - Distribution boards |  | Quality - Distribution boards
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d6119b14-f47e-46ad-9c3d-1dfc2d7431d3 | checkpoint | Receipt of switchboard delivery to site
bce8f233-f43b-4bb6-a305-e9445debc197 | checkpoint | set out to be confirmed with latest Switchboards Shop drawings
3fed3a41-f5ad-4054-adc2-0c781a13ca4d | checkpoint | Correct alignment to set out drawings
d3ccabc7-63ba-425b-ba90-8961928abe68 | signoff | Signoff Required from Heyday & Head Contractor
0b755a50-7baf-4f0c-8830-94a475ae7592 | checkpoint | Correct bracket and safe fixing
aa1624e4-fda7-4b38-9962-42d72de05b34 | checkpoint | Photos of boards attached
942ddc73-90e7-4113-b188-d0d2bd40f2b6 | checklist | Quality - Earthing & Lightning protection |  | Quality - Earthing & Lightning protection
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1479e842-cca4-487c-ab4e-fbc4bbd640de | checkpoint | Receipt of Cable & test point delivery to site
39de632f-40ed-467a-b184-4cb1d361cc72 | checkpoint | Correct cable size and Cable type installed per the shop drawing
949d0a9c-6e76-4913-a8b1-243717cdd555 | checkpoint | Installed and Terminated to final locations
6d5b64a1-3d75-444a-b7b6-bd7a5fc618ad | signoff | Signoff Required from Heyday & Head Contractor
232b8310-ad90-42ac-8360-ffb23fe6a001 | checkpoint | Photos of test piont and bonds attached
649a71d7-064d-465e-ba05-320512b949a3 | checklist | Quality - Electrical Equipment/Accessory Installation |  | Quality - Electrical Equipment/Accessory Installation
d18315df-1b72-43cc-9143-5c9bc3430f85 | section | Quality - Electrical Equipment/Accessory Installation
585c5f70-3264-4601-aca9-9f6dc7a514ed | checkpoint | Installed Correct Type/Colour of Equipment or Accessory
cac01609-7c33-4cab-af93-fbd489f9fe06 | checkpoint | Installed to the correct location as per drawings
912552dd-470f-4970-90de-7ef32e3bc3fa | checkpoint | Installed with correct fixings and made safe
3c9b09ea-59d1-4090-b937-0a7ad38b7c63 | checkpoint | Installed to the correct Circuit & DB Destination
47fca860-7d93-449d-8125-dc0d57e93b9d | checkpoint | Installed correct labelling
03dffa92-dc6d-46f4-a357-8a4226f1f897 | checkpoint | Final Check and No Damage to item
8cad35c9-294a-40ec-9219-3986eeb6d95b | signoff | Signoff Required from Heyday
befeb558-5dff-408c-be76-d2ce72f1844a | checklist | Quality - In Ground conduit install - HV ONLY |  | Quality - In Ground conduit install.
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
73a71ac9-bed4-4633-9d29-21efd7bbd825 | checkpoint | Receipt of conduit delivery to site & storage. (ITP Reference Item 1)
2622f687-370d-4ad8-902e-5f73f0b589b6 | checkpoint | Set out. (ITP Reference Item 2)
6259a244-bbfe-42b5-b5fd-9ed8c0ad949c | checkpoint | Excavation - Correct trenching alignment & depth. (ITP Reference Item 3)
90fc07f1-12f8-4be1-896f-b45f3eac4701 | signoff | Signoff Required from Heyday & Head Contractor
dd02b98f-0593-48ef-95db-8b6cc4b7ab98 | checkpoint | Conduit Installation. (ITP Reference Item 4)
c0e3dd45-3837-42c7-bee2-80fed1e7f336 | checkpoint | Spacer Frame Installation. (ITP Reference Item 5)
5761ad7f-9073-4e10-8201-47d52ca32c93 | checkpoint | Change of direction/bend Installation, correct bending radius used as per drawing. (ITP Reference Item 6)
d08685d6-ed34-483b-89b9-269076cad5c8 | checkpoint | Bellmouths installed within Insitu Pits. (ITP Reference Item 7)
b3c19a1d-81eb-4263-999c-3a3a7b5c1c09 | checkpoint | Glue Conduits together. (ITP Reference Item 8)
67b70002-92b4-4565-bbe6-d9c23f5fe188 | checkpoint | TSB Installation around & above conduits. (ITP Reference Item 9)
367f0d61-a448-4b6f-9362-f1c6a51d7b09 | signoff | Signoff Required from Heyday & Head Contractor
5aba8eea-2b46-4f4a-96b5-2272371c28af | checkpoint | 150mm cover of backfill above TSB. (ITP Reference Item 10)
cd6b3534-56e2-435e-b73b-aa9fcc6bee01 | checkpoint | Warning tape installation above 150mm cover. (ITP Reference Item 11)
f70d4a64-90e6-489b-9c09-8c9e5f9b1ce5 | checkpoint | Back fill & compact. (ITP Reference Item 12)
8162eec1-3d56-4a82-bde2-8d1f7d768500 | checkpoint | Rope & pathway test. (ITP Reference Item 13)
54eb1e84-db3e-4c93-95e4-fbc4fb10d586 | checkpoint | Sealing of conduits. (ITP Reference Item 14) HOLD POINT
53bfa6af-a21d-4791-91fd-86ad581731fa | signoff | Signoff Required from Heyday & Head Contractor
acb2f3e9-3777-4399-b35b-cd82a51e0bc9 | checklist | Quality - Inground LV & Communication Conduits |  | Quality - Inground LV & Communication Conduits
2d67222e-9ff4-42d5-833e-1ade2b24784b | section | Quality - Inground LV & Communication Conduits
9b2fffc9-270e-40a7-8705-dc47b2e2fc93 | checkpoint | Receipt of conduit delivery to site & storage. (ITP Reference Item 1)
70b2b64d-0827-4bee-80ee-6c7a6b30714b | checkpoint | Set out. (ITP Reference Item 2)
0a679e76-8055-432b-9110-4815fb67c9bc | checkpoint | Excavation - Correct trenching alignment & depth. (ITP Reference Item 3) HOLD POINT
59074d54-8fd4-43b0-a5b8-4cdfea916d9c | signoff | Signoff Required from Heyday & Head Contractor
357831f8-c75f-46be-9596-87d215933f06 | checkpoint | Conduit Installation. (ITP Reference Item 4)
9e6699ed-e0b0-4dd0-b3a0-700451229f5f | checkpoint | Spacer Frame Installation if required. (ITP Reference Item 5)
a87979ac-06d4-4e99-82f7-e6aaefb00a8f | checkpoint | Change of direction/bend Installation, correct bending radius used as per drawing. (ITP Reference Item 6)
333936bd-24ef-4be2-9e99-69381801f33f | checkpoint | Glue Conduits together. (ITP Reference Item 7)
6987a898-3ce5-4f8a-a5de-6ab949600aeb | checkpoint | 300mm cover of backfill above conduits. (ITP Reference Item 9)
8f0fea9b-58bd-4345-9e8a-4aa51bceb2c8 | checkpoint | Warning tape installation above 300mm cover. (ITP Reference Item 10)
dec68183-4c9b-4ee1-9342-effcea72e79a | checkpoint | Back fill & compact. (ITP Reference Item 11)
96c28ed0-6797-4ae4-b00d-b769a9c6d3bb | signoff | Signoff Required from Heyday & Head Contractor
3d9dc89b-30c6-419b-a47d-9320633a0ebf | checkpoint | Record photo evidence. (ITP Reference Item 14)
6ef4f278-b682-4732-b309-dda39a361785 | checklist | Quality - Light & Power Circuit Rough-In |  | Quality - Light & Power Circuit Rough-In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
01f55dbc-9321-42c9-8588-c4faba57d6e3 | checkpoint | Receipt of cable delivery to site & storage. (ITP Reference Item 1)
3779156b-7aa8-4293-98fc-e9c4a61a862d | checkpoint | Correct size & cable type. (ITP Reference Item 2) HOLD POINT
02fd3b3d-fed5-4ef9-a1eb-73eddf8ff184 | checkpoint | Installed to correct cable routing arrangements & circuit number. (ITP Reference Item 3)
3ce64644-d2fd-44a9-acc1-15989cddc134 | checkpoint | Installed to final location. (ITP Reference Item 4)
1db46d67-0d00-48c0-bd70-c109140314f1 | checkpoint | Photo evidence captured of cable installation. (ITP Reference Item 5)
da9add73-c80d-4e8d-a6a0-086057f02b00 | signoff | Signoff Required from Heyday & Head Contractor
cd19afae-43c1-494e-97bd-9a30d61e02a9 | checklist | Quality - Light Fitting Installation |  | Quality - Light Fitting Installation
fad17488-ad94-4b71-80cd-90db66bcd739 | section | Quality - Light Fitting Installation
89ecbeb9-1176-423a-a888-6e80c6c51b71 | checkpoint | Installed to the correct location as per drawings
0168e49d-c352-4cae-8363-eed09392b39c | checkpoint | Installed correct size and light fitting type
c53357d7-708d-4ff4-8f0b-7f960ca71412 | checkpoint | Correct Operation
04d30ae1-e08f-42ea-8806-db9349c16e3d | checkpoint | Installed to the correct Circuit & DB Destination
5b70a775-2872-4c45-919a-788a71d64678 | checkpoint | Correct labelling of light fitting (if required)
eb0747c8-65ab-474a-930b-ad1bca04f6de | signoff | Signoff Required from Heyday
443eca7d-a2e8-4c87-9677-f00b0242b663 | checklist | Quality - Light Pole Installation |  | Quality - Light Pole Installation
b332fb7b-427d-414c-b5cb-8e86f4847882 | section | Details
ab2d546b-f890-4fc1-81ae-7bc52acf70ba | checkpoint | Receipt of Pole Lights to site & storage. (ITP Reference Item 1)
1f8e819f-a4c7-406e-825d-37a9e6f5c53a | checkpoint | Select correct Pole Light Type for location. (ITP Reference Item 2) HOLD POINT
d7ce0c2f-d79b-4f14-817d-8498cb0cc100 | checkpoint | Install to the location as per Heyday IFC Drawings (ITP Reference Item 3)
0e2a6517-9ab1-4b35-85b0-3ce2f0bd3a56 | checkpoint | Connection to footing and levelling (ITP Reference Item 4)
2370bfe8-a969-4806-8e87-158d373a1720 | checkpoint | Base Plate Grouting (ITP Reference Item 5)
767d3422-cd9a-4ace-abe0-d8e0cf04d7e7 | checkpoint | Termination of Light Pole (ITP Reference Item 6)
e3fca214-7759-443c-952c-8c2daf00b1b9 | checkpoint | Photo evidence captured of Light Pole Installation. (ITP Reference Item 7)
eb807203-b6aa-40ce-bc9c-3a9203c55658 | signoff | Signoff Required from Heyday & Head Contractor
bc06466f-09e0-4844-adac-aec4b5269f76 | checklist | Quality - LV and Communication - Pit and Pipe Inspection |  | LV and Communication - Pit and Pipe Inspection
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8014076b-6fd0-4f39-92bc-06436c30abbd | checkpoint | Cover Slab and correct Pit installed per shop drawing.
7f8c709e-47a2-46a9-97f3-9530310e73c8 | checkpoint | Pit Lid installed to correct FSL
7392339a-0e99-4210-9eee-1c4acde014c7 | checkpoint | Conduits from pit out have been mandueled using correct size.
2762682b-f76d-4347-b346-e128b9f353ef | checkpoint | Ropes installed in conduits
4a19f46c-9fca-48f7-87c8-9ef56fa500f7 | signoff | Signoff Required from Heyday
e9793bd1-f449-4e14-bf49-ad1a79f8ff50 | checkpoint | Photo of pits installed.
ba235e82-281b-4be6-86a7-99b15884cf5b | checklist | Quality - Main Switchboard Install |  | Quality - Main Switchboard Install
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
4e2cdcce-3851-423a-a541-3b034abfec6f | checkpoint | Receipt of switchboard delivery to site
af37baef-ea2c-4d09-9044-e0784b0f5248 | checkpoint | set out to be confirmed with latest Switchboards Shop drawings
716a9f94-20d4-4671-948f-dc7edc48366e | checkpoint | Correct alignment to set out drawings
b2e7b34e-3d88-4de2-b56b-a13cac0dbf56 | signoff | Signoff Required from Heyday & Head Contractor
4592a97d-1ffe-468f-9314-db6d31bb43bc | checkpoint | Correct bracket and safe fixing
e1732cfa-bc3c-438f-99ff-b6c05049e4c7 | checkpoint | Photos of boards attached
86aa87a6-b5d4-4b51-9765-f9fe0fc446b6 | checklist | Quality - Pole Light Footings Installation ITC |  | Pole Light Footings Installation ITC
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
93472ed9-c576-4bed-b079-e12233246175 | checkpoint | Receipt of foundation cages delivery to site & storage. (ITP Reference Item 1)
791b4fb7-fecc-41d7-ba76-cc69cb27162e | checkpoint | Set out (Correct pier locations as per approved shop drawings). (ITP Reference Item 2)
19e95f7b-a15c-46ca-a66e-1812cf73670b | checkpoint | Correct trenching alignment & depth with excavator and auger. (ITP Reference Item 3)
22f2ae71-60be-47d2-a9f0-112b19deee8c | checkpoint | Install cage and rag bolts to correct finish level. (ITP Reference Item 4)
13281cde-694f-4b1e-9787-09b3d6d65227 | checkpoint | Install conduits and formatube. (ITP Reference Item 5)
23fa6f29-6099-4518-9c9d-54ac3c86a3d9 | signoff | HOLD POINT inspection prior to concrete
cd81f109-9a77-4b22-a318-90a67a3acbd7 | checkpoint | Concrete installation with tremie pipe. (ITP Reference Item 6)
17ea0ec2-33b1-4fee-be15-8539fba8033e | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 7)
1d223f93-c353-40b4-95bf-e85ae1de063a | signoff | Signoff Required from Heyday & Head Contractor
f008c625-0eb2-41be-bb21-70905f27afe1 | checklist | Quality - Pole Light Pier Installation ITC |  | Quality - Pole Light Pier Installation ITC
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
150bb9b1-6ff3-4517-a999-29c791e0df61 | checkpoint | Receipt of foundation cages delivery to site & storage. (ITP Reference Item 1)
40a15249-fc25-438a-a714-c3ec4f9948c6 | checkpoint | Set out (Correct pier locations as per approved shop drawings). (ITP Reference Item 2)
70c1d0ea-0b23-418f-af30-df6a3e39d09c | checkpoint | Correct trenching alignment & depth with excavator and auger. (ITP Reference Item 3)
a554b496-d39e-49df-ada2-7b544e3a5299 | checkpoint | Install cage and rag bolts to correct finish level. (ITP Reference Item 4)
df47fdc0-37ca-4661-9466-466795668e86 | checkpoint | Install conduits and formatube. (ITP Reference Item 5)
adbead86-a352-4716-ae61-5a3fcb4bca6c | signoff | HOLD POINT inspection prior to concrete
eef05d75-6bdd-4963-a418-fea84d40db8f | checkpoint | Concrete installation with tremie pipe. (ITP Reference Item 6)
ecb7f41c-9222-488e-a9dc-2ae0d04db3fa | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 7)
755b64e9-dc2a-4a45-92c7-18cf070d7538 | signoff | Signoff Required from Heyday & Head Contractor
74ef4895-c901-4195-b1e6-568fa108d3a6 | checklist | Quality - Pole Light Pier Installation ITP |  | Quality - Pole Light Pier Installation ITP
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d141cdf8-2c92-468d-981a-8d40874001e6 | checkpoint | Approved IFC Drawings
6d19f8f7-788c-5e0d-bc33-76dd10f80676 | note | Review drawings and revision status with Heyday drawing register, ensuring to only work to AFC drawings, and approved documents:
6537a2f2-5fc0-5d31-ad24-477d3b5fdbe7 | note | WSA50-MPX-02702-EL-DRG-000321[05]
50142c21-8e58-54b0-a011-450d0a00704e | note | WSA50-MPX-02702-EL-DRG-000324[01]
5ede2959-a4a4-5661-90b8-2e133bcd7ac8 | note | WSA50-MPX-02702-EL-DRG-000304[03]
1b604985-bcd6-5249-b8dc-453724b876b5 | note | WSA50-MPX-02702-ST-DRG-001202[04]
b906b77c-0024-4d28-b9bf-a934707889b0 | checkpoint | Material
4d042522-c3ed-59c0-98b3-e389f0bc615a | note | Only use material approved by Head Contractor through the required sample process listed on Heyday samples register as approved:
9dcf734f-1498-43bc-b595-e006ecacecff | checkpoint | Receipt of foundation cages delivery to site& storage.
e5fb6037-18c8-5625-b350-5b308891b02a | note | Review all delivered against approved product submission and confirm conformance. Components parts list, as stated on the purchase order/invoice, to be validated against received items
42000244-686e-4421-a8cb-59ed88c7b67a | checkpoint | Set out (Correct location set out as per approved shop drawings) .
641e1bda-b6cf-535c-a749-bdfc8f2a4302 | note | Set out to be confirmed with latest AFC drawings. WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
3ce17901-8e6a-45aa-9285-07af72c9dff6 | checkpoint | Correct trenching alignment & depth with Excavator and Auger. If rock is struck, geotech will be required to confirm socket depth
f446e29a-1c71-5f6e-b685-f90d8b55d83d | note | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
c8b8768d-7078-4443-93fd-a29b58825976 | checkpoint | Install cage and Ragbolts to correct finish level.
42cae0c5-c6c2-59c4-b958-c38b9208aedf | note | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
39ce1519-db25-4e34-adba-82c81eb82cb3 | checkpoint | Install conduits & Formatube.
9432e873-9bf2-5eee-998a-29466ac400f9 | note | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
03299ee3-8868-4dd6-97a4-ed326639b3b9 | checkpoint | Concrete installation using Tremie Pipe
0f27ed9f-3b54-5939-ac39-1a396cf37601 | note | WSA50-MPX-02702-EL-DRG-000321[05] WSA50-MPX-02702-EL-DRG-000324[01]
aff63e29-d37a-430a-b815-0b2ac0cb1d1c | checkpoint | Photo evidence captured for asset install
5f6419e0-e42e-5b67-978e-8347f3b8d982 | note | Photo evidence to be captured, stored and provided for formal submission where applicable/outlined within ITP
2401931c-f442-410d-a3b9-fdbcc09f344c | checkpoint | Completion of installation
bc61b16b-a422-592b-a8e3-872930dbfdba | note | Heyday supervisor to ensure that all work has been completed to relevant standards & approved drawings
1ffd0d95-180e-4ef8-8820-4b993ed022ab | checkpoint | Photo Evidence
44f4be71-9bd2-5438-9773-100944729e64 | note | Heyday supervisor to capture & submit photo evidence as part of completed works specified within ITC
d3dd1b34-8145-42d8-945f-de334445dffa | checkpoint | As-built survey & report
e1c38bfd-eb43-5e6e-a058-5a000c373a09 | note | Heyday supervisor to submit As-built drawings as part of completed works
c39d730b-b3ac-4805-bcfa-347c07a5600f | signoff | Signoff Required from Heyday & Head Contractor
2a7a5575-2a12-47c2-a292-10a24024510d | checklist | Quality - Power and Lighting Subcircuits |  | Quality - Power and Lighting Subcircuits
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
70aa64d9-0d08-47a5-8647-185834a86644 | checkpoint | Receipt of cable containment delivery to site & storage. (ITP Reference Item 1)
84059ae9-7244-4dd8-9a39-ebc63fff828d | checkpoint | Correct size & cable type. (ITP Reference Item 2)
4a470d59-f780-42db-bffe-6da8cc16b798 | signoff | Signoff Required from Heyday & Head Contractor
db00ad9e-a369-4a3c-bd2f-9ccd89e5e646 | checkpoint | Installed to correct cable routing arrangements & circuit number. (ITP Reference Item 3)
4219368a-1076-4619-8929-abca8707cfec | checkpoint | Installed to final location. (ITP Reference Item 4)
20a0c556-952f-4aa0-bd5d-f94f701bcb09 | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 5)
1edfb0b5-9856-4905-aedf-671e3f5cee52 | signoff | Signoff Required from Heyday & Head Contractor
14710401-9c29-4f39-b42b-46d1e98b2241 | checklist | Quality - Precast Pit Install |  | Quality - Precast Pit Install
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
086a6b84-79c1-498b-8fd5-7a0d0772c2d7 | checkpoint | Receipt of Precast pit delivery to site & storage
b14f26fa-c956-42c1-b0eb-9aff33b5c57e | checkpoint | Pit is built to approved shop drawings (photos attached)
130f2cdf-1e80-4855-95c0-2cd47b51596c | checkpoint | correct trenching and alignment & depth
9aded11b-2e7c-4a43-8a19-631766a35474 | checkpoint | installed to correct finish level
c15d1211-1381-4840-9688-999120feaeba | checkpoint | correct back fill installed around pit
81f8fe16-d331-4056-87d5-6661de7afbed | signoff | Signoff Required from Heyday & Head Contractor
cb7ac338-822e-4947-bc3d-0bac0e0bc5a9 | checkpoint | Install correct pit lid
8de1c1e5-d080-4a8f-9755-8cb1dff3eead | checkpoint | Photo of pit installed attached.
f8f7170d-7d95-45ff-a33e-8660a43544f1 | checklist | Testing & Commissioning - HV/LV Transformers |  | HV/LV Transformers
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
0969b89b-13b4-4408-9f80-44764c16f940 | checkpoint | Schneider Electric Transformer QA/QC Test Report – Installation Configuration Page 3.
71e45806-0bf8-420a-9058-dc8022588864 | checkpoint | Schneider Electric Transformer QA/QC Test Report – Pre-Testing inspection Page 4.
3db19474-7cc3-4bc9-96d7-b8a25713e7af | checkpoint | Schneider Electric Transformer QA/QC Test Report – Transformer Test - Page 4:
f8c6c0e2-0485-509a-931b-46c872a5edc9 | note | Continuity test on HV and LV Windings
3faf0bd7-0a5a-5492-be65-9c05fe1f5766 | note | ○ Insulation Resistance Test LV Winding to Earth
a9a2e7ec-06f4-5b0c-89c3-d73ab8bec5d5 | note | ○ Winding Resistance
d5f48f7a-6630-5728-8eb8-e0783cbc2636 | note | ○ Winding Ration verification (taps: +2.5%, +1.25%, 0, -1.25%, -2.5% )
07063b97-3ec1-52e0-b91d-4ecb899353d4 | note | ○ Vector Groups
b63500bd-c421-55e0-9a61-593f3e871930 | note | ○ Check bushings
bb642782-7878-5cb6-a87d-4afc54389d15 | note | ○ Control cubicle visual inspection
8d2f3627-9622-502b-9733-5ad37a7f6000 | note | ○ Control Cabling within the control cubicle visual inspection and connection verification against approved schematics
c61de0f1-9a75-591c-8fd3-a5716389ee98 | note | ○ Confirm opening of LV door operates “normally open contact when doors are closed”
5c13a156-5bca-4154-a40f-5738c1d988f4 | signoff | Checked By (Heyday):
ff0e237c-dd3c-4bd6-9493-b3cb341861c7 | checklist | Testing & Commissioning - Load Bank |  | Load Bank
536dda0e-5101-4baf-9bdf-b0735aff5fb9 | section | WSA20-MPX-04000-EL-ITC-31143000 - Component Tests (Pre-commissioning)
7bdbd1de-9025-4189-85e4-2fcb1213e2e6 | checkpoint | Sephco Commissioning Checklist
f3d07a75-f318-4c18-bc0e-9b2acceba9c5 | signoff | Checked By (Heyday):
62d202b1-8c66-4e1e-8901-ccb27238b552 | checklist | Testing & Commissioning - PFC |  | PFC
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1944b174-f008-4363-8bdf-1c008fa2b047 | checkpoint | WSA20-MPX-04000-EL-ITC-31102000 - Construction Tests (Pre-energisation)
f68e9d2d-b76e-4654-afa5-0ea82486de02 | checkpoint | WSA20-MPX-04000-EL-ITC-31073000 - Component Test (Energised)
9b9b1768-ae07-4672-ae74-d1727c05c53a | checkpoint | CT Ratio Verification (V,A,kVA) L1/L2/L3 - Component Test (Energised)
c057c646-daba-4f37-a524-666f830967de | checkpoint | Power Factor Correction Controller Configuration as per manufacturers recommendations - Component Test (Energised)
7b4885d9-2b6b-4d72-93c7-cb464dd5b560 | signoff | Checked By (Heyday):
55687e49-7ac5-41c7-95bb-08c0e7c58654 | checklist | Testing & Commissioning - PMCS |  | PMCS
6d39116f-93ac-4c31-b733-b41891044e4a | section | WSA20-MPX-04000-EL-ITC-31183000 - Component Tests (Pre-commissioning)
0f3e7711-e0b9-4442-9cde-9544fac38446 | checkpoint | Schneider Point to Point Validation ITP - RIOM
363f12e9-42ca-4ebd-9f72-465cb421c246 | checkpoint | Schneider Point to Point Validation ITP - PAC
909ed226-bacd-4172-948f-6bb3a9774ffe | checkpoint | Schneider Point to Point Validation ITP - EPS
4170b671-0120-496a-950c-fc6c643c72a1 | checkpoint | Schneider Point to Point Validation ITP - PFC
4bce19cd-c9e5-44b5-8633-e57edd635592 | checkpoint | Schneider Point to Point Validation ITP - UPS
512c4451-1ea2-4d4c-92e5-aa9bedb5a86f | checkpoint | Schneider Point to Point Validation ITP - EV
fb8cc9f5-9762-4676-8db2-7fb9a4072ff9 | checkpoint | Schneider Point to Point Validation ITP - IEM
fef1adbb-cd17-4792-83f6-ddad180e93d7 | checkpoint | Schneider Point to Point Validation ITP - eGSE
e0760722-56ae-4c39-9758-f4ad831a7800 | checkpoint | Schneider Point to Point Validation ITP - GEN
0d4a2136-bbf3-4120-9af8-aa4ee417b934 | checkpoint | Schneider Point to Point Validation ITP - LCS
f2e4baf3-db16-42c1-856b-c5d1ea2af0dc | checkpoint | Schneider Point to Point Validation ITP - EML
32ac393c-b449-49c8-8c01-4537449c011d | checkpoint | Schneider Point to Point Validation ITP - PV
2aaa59e8-f9a9-40e8-95e6-eb37298f6b25 | signoff | Checked By (Heyday):
ff22da6d-3cf0-4ac7-84a6-1401d58129f9 | section | WSA20-MPX-04000-EL-ITC-31184000 - System Acceptance Tests (Commissioning)
42e63be9-0b4d-45fa-a96c-67f05aaa6664 | checkpoint | Schneider WSA LV PMCS Cx ITP - RIOM
b1cacbf7-ed0f-4b96-9a82-abceea0421a7 | checkpoint | Schneider WSA LV PMCS Cx ITP - PAC
8c03faf9-2e4c-4ef7-9741-bad9b0bbc42d | checkpoint | Schneider WSA LV PMCS Cx ITP - EPS
d1aca762-82b0-4fa7-9cd5-d65258b3be37 | checkpoint | Schneider WSA LV PMCS Cx ITP - PFC
d5f5901f-5e6f-4899-b397-55aa27f163eb | checkpoint | Schneider WSA LV PMCS Cx ITP - UPS
c0daf05b-b0eb-4b4e-8f71-b97e9dc4a6e4 | checkpoint | Schneider WSA LV PMCS Cx ITP - EV
8ace8b4e-3b9a-43be-9525-4151be7b76cc | checkpoint | Schneider WSA LV PMCS Cx ITP - IEM
559e5a9a-153d-4f70-9936-accb5ef23056 | checkpoint | Schneider WSA LV PMCS Cx ITP - eGSE
e76c6a77-eb82-4ce1-b0ab-43b760b35fd1 | checkpoint | Schneider WSA LV PMCS Cx ITP - GEN
d50a52b4-a611-4608-996c-f6ed4059e72b | checkpoint | Schneider WSA LV PMCS Cx ITP - LCS
04659ead-350e-4522-adac-90c797c5c308 | checkpoint | Schneider WSA LV PMCS Cx ITP - EML
f983179a-9ad1-4eb9-a581-a3b64af3d443 | checkpoint | Schneider WSA LV PMCS Cx ITP - PV
5575884b-b5f1-4f3a-bcf7-d8139b45eee7 | signoff | Checked By (Heyday):
54731133-f18a-4d97-95e6-64aee3d66a70 | checklist | Testing & Commissioning - PMCS - (Energised) |  | PMCS - Energised
b70035bd-c922-47e0-9f91-0f5759ee6df6 | section | WSA20-MPX-04000-EL-ITC-31184000 - System Acceptance Tests
7ccf45df-e107-415e-9a6d-9245237e61b7 | checkpoint | Schneider WSA LV PMCS Cx ITP - RIOM
35fe0e6a-d70a-45f6-b5a0-9076eb4e528f | checkpoint | Schneider WSA LV PMCS Cx ITP - PAC
e0f9faba-82f3-4bde-aeea-b94722c0dd90 | checkpoint | Schneider WSA LV PMCS Cx ITP - EPS
b4961f39-3aa9-4694-9dc6-de81d5c81979 | checkpoint | Schneider WSA LV PMCS Cx ITP - PFC
86227350-4ca3-4fa3-b4b7-31f467675a19 | checkpoint | Schneider WSA LV PMCS Cx ITP - UPS
afe2194c-92fd-4db9-b886-e7adbef9c63c | checkpoint | Schneider WSA LV PMCS Cx ITP - EV
aa8f5b05-c914-45f0-85ac-f98ad2a0887a | checkpoint | Schneider WSA LV PMCS Cx ITP - IEM
8ad6dd46-99e8-4ea3-86e9-acb9990841c3 | checkpoint | Schneider WSA LV PMCS Cx ITP - eGSE
d330c9ca-c23a-4890-8100-15367f9d3983 | checkpoint | Schneider WSA LV PMCS Cx ITP - GEN
e8108dda-ac8d-427e-ac1a-b770391d63df | checkpoint | Schneider WSA LV PMCS Cx ITP - LCS
68acecc8-1749-4a90-a9db-d88123034461 | checkpoint | Schneider WSA LV PMCS Cx ITP - EML
13681449-c97e-47ca-83d4-503418a2b151 | checkpoint | Schneider WSA LV PMCS Cx ITP - PV
eba7d451-5aae-4829-a17e-b3335210cf9c | signoff | Checked By (Heyday):
6c383b39-f825-4304-9fd9-14040470c7da | checklist | Testing & Commissioning - PMCS - (Pre-Energisation) |  | PMCS - (Pre-Energisation)
80cb1efa-9413-4588-bbd4-416d894354f7 | section | WSA20-MPX-04000-EL-ITC-31183000 - Component Tests
0bc2971f-c935-4b69-be54-5aed9a755752 | checkpoint | Schneider Point to Point Validation ITP - RIOM
64746830-809f-4404-a799-04603a3e90e9 | checkpoint | Schneider Point to Point Validation ITP - PAC
3711391c-514f-4938-9967-a2538ffa1220 | checkpoint | Schneider Point to Point Validation ITP - EPS
007fcd38-df52-4f21-b06c-149e50cb0e72 | checkpoint | Schneider Point to Point Validation ITP - PFC
f61dbfe3-d3f0-4a24-bfd3-13f971c6385d | checkpoint | Schneider Point to Point Validation ITP - UPS
8a8b9076-eb21-4099-9cc0-ec74a028bc5f | checkpoint | Schneider Point to Point Validation ITP - EV
ca18920f-89c7-4222-8b3a-f7735b3a43bf | checkpoint | Schneider Point to Point Validation ITP - IEM
691ce5d3-7b5e-40f8-9a3e-b54ef81e8ac9 | checkpoint | Schneider Point to Point Validation ITP - eGSE
f03a126f-5637-4d04-af33-7b8030637f22 | checkpoint | Schneider Point to Point Validation ITP - GEN
aad1bf93-4560-481f-9bb8-940ce1c9a995 | checkpoint | Schneider Point to Point Validation ITP - LCS
75178553-dde5-47ef-9dbb-d4d130d134b8 | checkpoint | Schneider Point to Point Validation ITP - EML
c0da70a4-fe4c-4380-a6f9-7184ad3bf353 | checkpoint | Schneider Point to Point Validation ITP - PV
ac3afc66-f236-4331-9cfd-25ccb6c4835a | signoff | Checked By (Heyday):
eb8a49ae-7f4d-4e38-9f02-6cdfbf19ebe8 | checklist | Testing & Commissioning - Solar Photovoltaic System (Energised) |  | Solar Photovoltaic System (Energised)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
c81c44e5-267c-40b2-a310-23bc182cb8ef | checkpoint | SCS Commissioning Checklist Section 5 (System Measurements – AC Measurements)
a426b55b-f3e5-4f30-8dd8-13ee8bc08ab1 | signoff | Checked By (Heyday):
2e96ad2c-caef-477a-9068-962baf335263 | checklist | Testing & Commissioning - Solar Photovoltaic System (Pre-energisation) |  | Solar Photovoltaic System (Pre-energisation)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a03a5368-d0b8-481b-9289-debec47e63ce | checkpoint | SCS Commissioning Checklist Section 5 (System Measurements – Inverter)

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
1ce789a3-13b9-4e73-acab-6b052952a25d | checklist | Quality Mains and Sub Mains |  | Quality Mains and Sub Mains
56941fac-2db1-48ab-b940-3632c17ac0fb | section | Details
481c366a-fe5f-4bf9-b08e-3fe618e39573 | checkpoint | Receipt of cable containment delivery to site & storage. (ITP Reference Item 1)
c1f2e221-dde5-4dad-9b44-c6afb6999b40 | checkpoint | Cable storage & handling. (ITP Reference Item 2)
a952b6d5-c1b0-4efa-bc98-18fecdf45664 | checkpoint | Correct cable size & type. (ITP Reference Item 3)
2e077f6e-060a-4e49-a276-969004145f0b | signoff | Signoff Required from Heyday & Head Contractor
dd8f2a5e-5bac-4622-9945-985f7020ddc9 | checkpoint | Cable pulling tension to not exceed manufacturer's recommendations. (ITP Reference Item 4)
7199c90a-99f7-4c2e-ad30-b8eb856528f1 | checkpoint | Cable lubrication if required. (ITP Reference Item 5)
cc57e662-d195-4557-b8fc-88991a964bdd | checkpoint | Installed to latest drawings – schematics/single line diagram & cable containment drawings. (ITP Reference Item 6)
3700b49e-c745-4dde-9bf2-634c32593cff | checkpoint | Correct cable tag installed. (ITP Reference Item 7)
89bedb52-fb10-432d-9c5e-92594ea32e40 | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 8)
2007734c-08ee-4ea7-bd50-d84c77daae1f | signoff | Signoff Required from Heyday & Head Contractor
579e8254-1416-4373-9714-a80bae9b9be3 | checklist | Substation Earthing Inspection |  | Substation Earthing Inspection
62a898b2-f6e0-4591-bc14-0522ba8a9ad1 | section | Details:
cc096a5a-a547-4918-8c51-0dae4ac1849d | checkpoint | Visual Inspection of Pit
2ccf85d8-44ed-5696-a9fe-27b45edd008a | note | Photo Required of Pit
cfa7a13d-7bee-4cbd-b8da-81dedcf3f58d | checkpoint | Earth Resistance from Pit Earth Rod to Earth Bar
67446d85-d979-5751-a367-9cbdd434a363 | note | Earth Resistance to be <0.5Ω
7d3aed57-4013-5bac-931e-5a7f90003aa0 | note | Photo of Multimeter with results from Earth Rod to Earth Bar
6a32d84d-266b-4ff3-9e8f-293b4d104a9f | signoff | Checked By (Heyday):
00395d15-c232-400e-b298-cd573f6a4609 | checklist | Testing & Commissioning - UPS (Energised) |  | UPS (Energised)
f3e1cbad-b2ae-4e94-b407-8a4890326fde | section | Details
fdfaaa2d-ff73-42fa-a03d-542a79ed959a | checkpoint | Commissioning & Installation / Start-up Report - Unit pre start-up check – Page 7
e799e765-75f6-4b34-9a13-8ca4acee5b53 | checkpoint | Commissioning & Installation / Start-up Report - Unit Functional Check – Page 7
0a01ea4f-cb67-4be8-b374-02ed1def6419 | checkpoint | Commissioning & Installation / Start-up Report - Unit Final Inspection – Page 8
c3e2d737-0933-409b-b83f-2feb4a6641a9 | checklist | Testing & Commissioning - UPS (Pre-Energistation) |  | UPS (Pre-Energistation)
0e4869ae-5b31-45c1-82bf-e47ce2268876 | section | Details
9fce7efb-00fa-4dbe-8da7-cb82428781d1 | checkpoint | Commissioning & Installation / Start-up Report - System Room Check – Page 6
76622146-1a89-4937-b3b6-b3b6251e014f | checkpoint | Commissioning & Installation / Start-up Report - System Check – Page 6.
bd834737-5db3-404b-9559-9369c015de72 | checklist | Testing & Commissioning - UPS (System Commissioning) |  | UPS (System Commissioning)
5b7606ba-d5ae-41fc-8376-13c2d4483875 | section | Details
57bc2b37-cbf2-41b6-be97-f08b875fd4cc | checkpoint | UPS – Functional Performance Test Report
66cfeccd-867d-5d84-b88f-b0e6be08bdd0 | note | The following tests are conducted (see Schneider Electric - Site Acceptance test protocol for results and trends):
248e2182-3c88-548a-9d16-83cbfe1cffe2 | note | ○ Load Transfer test
3165be1c-67e3-513d-ba2d-739729acf2db | note | ○ Inverter to bypass transition on NO LOAD
ba06c38d-84b0-57ab-bb2f-af01b1a45b9e | note | ○ Inverter to bypass transition on FULL LOAD
4ad73757-b2d1-5e11-93d0-de966663e293 | note | ○ Load step test (0%-50%-0%)
6abf185b-84cd-59af-a6a5-7d2db2ef381f | note | ○ Load step test (25%-75%-25%)
af8c85e8-d471-58c9-95fd-2b7d7aa46aa1 | note | ○ Load step test (50%-100%-50%)
8b7ebabc-e30a-5299-a59e-03185a8dd2c9 | note | ○ Load step test (75%-100%-75%)
1869e058-9c4b-5cda-9106-e67d703976e6 | note | ○ Load step test (0%-100%-0%)
cc904bb5-37bd-559e-8661-48790dccc0b4 | note | ○ THDi and THDv measurements (0%, 25%, 50%,75%, 100%)
10f48170-9c16-5cb5-b41d-534c75ee3fd1 | note | ○ Expected Results: Total Harmonic Distortion (THD) is to be under 5%
36eb3717-5cff-57d2-b2b6-e013a4b9f1ac | note | ○ UPS efficiency calculation (Unity PF@0%, 25%, 50%, 75%, 100%)
a6c23fcf-6893-5fce-a12b-7cb207ee50e1 | note | ○ UPS battery discharge test (15min EOL)
293955cf-2d1d-4d00-b4c9-a555503de06c | signoff | Checked By (Heyday):