## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - RMU BUILDING SLAB | itp
section | Preconstruction
checkpoint-no-status | Location
textbox | Location of Foundation Construction
checkpoint | Design Drawings
label | Issued for Construction Drawings available
holdpoint | United Civil Hold Point
checkpoint | Survey & Setout
label | Visual Inspection of RMU Location setout
label | Benchmark established as a dataum for levels
label | Alignment with approved drawings and site plan
holdpoint | United Civil Hold Point
checkpoint | Calibration of Plant
label | All testing and measuring equipment calibration certificates valid
checkpoint | Site Clearing
label | Visual inspection of cleared area
label | Free from vegetation, debris, and obstructions
section | Material Procurement
checkpoint | Review of Concrete, and Reinforcement steel
label | Compliance with IFC Drawings, Specifications and Standards
label | All reinforcing bars shall be deformed grade 300 to AS/NZS 4671
label | All concrete construction shall be in accordance with NZS3109
label | Geogrid and Bidim to minimum Class B
label | Concrete strength shall be a minimum of 25MPa
label | Delivery Dockets supplied for each delivery/Pour
label | Material test certificates supplied for reinforcing steel
holdpoint | United Civil & CHINT Hold Point
section | Construction - Slab Foundation
checkpoint | Excavation to Subgrade
label | Relevant Specification: IFC Drawings
label | Test Method: Visual inspection and photos
label | Timing/Frequency: Visual Inspection of the foundation
label | Acceptance Criteria:
label | ○ No organic or unsuitable material is present
label | ○ Foundation is at the correct level
checkpoint | Foundation Subbase Construction
label | Relevant Specification: IFC Drawings
label | Test Method:
label | ○ Photos and dimensional check that the construction and RL's comply with the IFC Drawings
label | ○ Minimum of 200mm of compacted Gap40 over Geogrid and Bidim
label | ○ Test the foundation layers strength with a Clegg Hammer
label | Timing/Frequency: 4x sets of Clegg Hammer tests and measurements to determine the compaction of foundation layers
label | Acceptance Criteria:
label | ○ Visual Inspection and photos of compacted aggregate and tests
label | ○ Thickness of Gap40 shall be 200mm over bidim and geogrid as directed
label | ○ Clegg hammer tests shall meet a minimum CIV of 24 on the 4th blow for each test
holdpoint | United Civil & CHINT Hold Point
section | Construction - Concrete
checkpoint | Prepour Inspection - FORMWORK & REINFORCING INSTALLATION
label | Relevant Specification: IFC Drawings
label | ○ Steel Reinforcing shall comply with NZS3109
label | ○ Concrete formwork construction shall comply with NZS3104 & 3109
label | Test Method: Visual and dimensional check that the construction and minimum cover required complies with the IFC Drawings & Specifications and Standards
label | Timing/Frequency: Prior to pouring
label | Acceptance Criteria:
label | ○ Formwork shall be free of warps, bends or kinks, and the tolerances of the top surface of the form shall ensure compliance with the finished floor tolerances of +/- 10mm
label | ○ Reinforcing materials - hooks, bends, bars and surface condition of reinforcement, spacing and fixing, splices, cover and placing tolerances shall comply with NZS3109 unless modified in the IFC drawings
label | ○ Prepour Inspection completed and filled in
holdpoint | United Civil & CHINT Hold Point
checkpoint | Prepour Inspection - EMBEDMENTS
label | Relevant Specification: IFC Drawings
label | Test Method: Visual inspection, photos and dimensional check that any embedments comply with the IFC Drawings
label | Timing/Frequency: When installed and prior to pouring
label | Acceptance Criteria:
label | ○ Embeded items are installed to meet expected outcomes against the IFC drawings
label | ○ Noted in the Prepour Inspection ITC
holdpoint | United Civil Hold Point
checkpoint | Concrete Mixing
label | Relevant Specification: IFC Drawings NZS3104
label | Timing/Frequency: Prior to and for each pour
label | Acceptance Criteria:
label | ○ Concrete baching plant is certified to batch concrete under NZS3104
label | ○ Concrete strength to be 25MPa
label | ○ Concrete mix delivery dockets
checkpoint | Concrete Placement
label | Test Method: Visual Inspection during pouring
label | Timing/Frequency: During each pour
label | Acceptance Criteria: Proper compaction of poured concrete, no segregatation or honey combing
checkpoint | Slump & Strength Testing
label | Relevant Specification: Tests taken in accordance with NZS3112.2
label | Test Method:
label | ○ Slump Testing
label | ○ Cylinder compression testing
label | Timing/Frequency:
label | ○ Slump Tests are prior to pouring
label | ○ Compression testing shall be at 7, 14 & 28 days post pouring
label | Acceptance Criteria:
label | ○ Slump shall be 100 & Compression testing shall be a minimum of 25MPa at 28 days post pouring
label | ○ Test report/dockets shall be supplied
section | Post Construction
checkpoint | Curing & Surface Finish
label | Relevant Specification: IFC Drawings NZS3104 & NZS3109
label | Test Method:
label | ○ Visual Inspection of curing concrete
label | ○ Curing concrete shall remain damp during the curing period
label | Timing/Frequency:
label | ○ Slump Tests are prior to pouring
label | ○ Compression testing shall be a set of 3 cylinders taken from freshly batched concrete and tested in accordance with NZS3112
label | Acceptance Criteria:
label | ○ Slump shall be 100 & Compression testing shall be a minimum of 25MPa at 28 days post pouring
label | ○ Test report/dockets shall be supplied
checkpoint | Surface Finish
label | Test Method: Visual Inspection of surface for cracks, voids, and finish quality
label | Acceptance Criteria: No visible defects or honeycombing for each foundation post striking of formwork
section | Post Construction and Handover
checkpoint | Final Walkthrough & Inspection
label | Comprehensive inspection of all elements relating to the concrete foundations
label | Compliance with IFC drawings and specifications
label | Verify concrete foundations meet design and functional requirements from the IFC drawings to what was constructed
label | Concrete Foundations ready for subsequent construction activities
holdpoint | United Civil & CHINT Hold Point
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Punch List
label | Development of Punchlist with Client and Contractor Representative
label | Punch List closed out in a timely mannor
checkpoint | Documentation
label | On completion of the concrete foundations:
label | ○ Submission of all test results, ITC's and any as-built drawings
label | ○ Complete and approved by client
holdpoint | United Civil Hold Point