## Resources
Type | Id | Name | Values | Prompting Name | Postfix | Resource Id
checklist |  | INF-HSEQ CC0398-ITP-034 Carbon Steel Installation Rev C | itp | INF-HSEQ CC0398-ITP-034 Carbon Steel Installation Rev C |  | 0946edd3-a462-4b17-a35e-b93e00dd186c
section |  | 1.0 Pre-start activities
checkpoint |  | 1.1 - Set out
note | 414ca677-dc92-58d0-8b6d-25074380cd86 | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
note | 1e2ef3ea-f6a8-531f-b12f-58efd3c434d5 | ○ IFC and latest available revision used?
button | 5f14acec-88b0-5d7a-ad1a-cd44288832a7 | Acceptance | Yes,No,N/A
note | 16ecb757-55b7-5e4f-a7dc-a2b6601206bd | Key - H
note | 5c47a2ea-5776-50ca-ac36-feb0fab7248e | MDR/VIVA - W
checkpoint |  | 1.2 - IFC Submission & Approval
note | 3b4e695d-bb66-5bc4-9c4f-76b2e9aceb2a | Ref docs - Isometric Drawings
note | d92a8349-488c-5728-a859-737604a1a4bd | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
button | 47b3f934-2fce-589c-a321-1bd30d422a24 | Acceptance | Yes,No,N/A
note | 2d5f3756-105e-5cc6-a04d-65955528ff38 | Key - H
note | 37b36da5-8481-59c5-bcd0-ced661fbc836 | MDR/VIVA - H
note | 06278bb9-6755-540b-a1cd-69e8a02e8eab | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 1df0313b-8e97-5cda-aa7d-dd753dc8e818 | Isometric Drawings
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 1.3 - Permits
note | 7936c0ad-2d5c-509e-ba01-2f8f0ca221d2 | Ref docs - Symal Safety Procedure
note | 0dc3dc10-f277-5090-82d8-5505316dc9ad | Acceptance criteria - Have the below permits been created.
note | f17ee10d-469f-528c-8b0a-15959d768ee2 | – GPP
note | 593b9fae-8bea-5c7c-b0e5-5f56e84bc4b7 | – Working at Heights
note | 43cd8f0f-575b-5ebc-b046-523b9c3dfb9a | – Hot Works
note | 5265ebf6-c143-568d-b0e4-b653298bc4e8 | – Confined Space
button | 009b61af-dfa8-58cf-aee9-907ff4511d55 | Acceptance | Yes,No,N/A
note | 0ddd6ddd-71df-5c93-b3e4-fb161cf4163c | Key - H
note | 42cdd9ef-16af-59a2-91c3-58162cfa4145 | MDR/VIVA - W
checkpoint |  | 1.4 - Determine Lot Size
note | 8d580e88-f213-5a83-9c25-e878b3a3ecdb | Acceptance criteria - What is the lot size?
button | b2635b00-fa87-5f32-b51b-0955337b3c43 | Acceptance | Yes,No,N/A
note | b114c22d-ce82-5cc6-8c35-fcd9bbaacc23 | Key - S
note | b20974c2-4c8e-57c4-acb7-7093e920e3b0 | MDR/VIVA - W
checkpoint |  | 1.5 - Free Issue Materials
note | 61365588-4fa3-55c3-83ff-7be96fdd6040 | Acceptance criteria - Have the free issue materials been accepted and checklist completed?
note | 84370636-cfd5-577b-8b68-2c04928fde6f | ○ Have the materials and tag numbers/heat numbers been verified?
button | cebcc50b-7962-586f-8613-bafd7c2ae07e | Acceptance | Yes,No,N/A
note | 6dea74d1-3f74-5db2-99d8-d8069da0923e | Key - W
note | 15f73246-c7a6-5ae1-ab4d-69c0090a7078 | MDR/VIVA - W
note | d2349358-c3a2-586f-b996-984c3129b247 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 4ad592f7-af52-5f72-86a6-2a814d860d57 | Material Inspection Checklist
checkpoint |  | 1.6 - Pre-Qualifications
note | e4a2eb2e-3ee1-531e-98de-f92479ec8754 | Ref docs - Welder Qualifications and tickets. This ITP.
note | dfa5cf95-b0cc-5e8a-bcba-c2c4c8f19697 | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
note | 9cea0a23-05d6-5f97-bb4f-d953ffa09553 | ○ Has the training records for the STOPAQ applicators been provided?
button | 4418465e-9792-5c41-884c-fcc6d513c7a4 | Acceptance | Yes,No,N/A
note | 94b70614-6f97-5ca0-bc2c-966afde6bb09 | Key - H
note | 3fe58905-8b27-504d-977d-245c3706cca7 | MDR/VIVA - H
note | c276e91a-a0d0-5db8-b60e-612fd5967851 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 86328624-91f6-57d5-9ade-754e4f779150 | Welding Qualificaitons
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 1.7 - Bedding and Backfill Materials Approval
note | cbdfb958-dd63-5bbb-ad42-623add996c2c | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8
note | 4a72b740-9a92-5eaa-9dea-d2c053027ea2 | Acceptance criteria - Has bedding and backfill materials been approved for use?
button | 82c0636c-a445-510c-a12f-23eac6f67703 | Acceptance | Yes,No,N/A
note | 685c1b5a-9669-5c09-bde3-0f59201453f1 | Key - H
note | f17c64bd-c35b-5e18-b6ab-35d44e4e6e52 | MDR/VIVA - H
note | 9340c59b-7e72-55c4-934f-7d3d5d760d61 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | d028a8f1-0e4d-55a6-a54f-8539f1ad3340 | Material Approval
signoff |  | AUTHORITY HOLDPOINT
section |  | 2.0 Excavation and bedding
checkpoint |  | 2.1 - Service Location
note | 73088be7-9e4b-5d8d-913c-f005b2e8a72c | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
note | da79b004-3b69-5776-a9ba-11a315cf8003 | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
button | 415f0258-e2f7-57e4-b5fc-39de63ca7d79 | Acceptance | Yes,No,N/A
note | d11e7058-eae5-50fe-90a9-32bb9ab1be6b | Key - H
note | 793ef610-f807-5502-a51d-2d542ac76380 | MDR/VIVA - S
checkpoint |  | 2.2 - Excavation
note | 1b93e24e-9721-58a1-b702-d3a3b96281b6 | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.12
note | c6402caf-0bd5-580e-ad19-2f02aacfee4f | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth of 100mm.
note | 989b3354-6823-598a-bd87-4d6002810f6f | ○ Minimum trench width as per manufacture specifications pg. 17 is 1.25 x OD + 300mm.
note | 119ea929-0e68-5f4d-b474-dd2fd9ce3214 | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
button | 2ab8db07-350c-5dff-8497-7f0c1be497fb | Acceptance | Yes,No,N/A
note | 6a1413ac-6120-5100-8550-832c95614525 | Key - W
note | d4c4b22a-b179-5068-9d11-8f60d9251fd2 | MDR/VIVA - S
checkpoint |  | 2.3 - Bedding material
note | ed1636d4-42e0-588b-9b25-cd915270aaa9 | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8
note | 853a0b42-6f02-5aac-8fb1-5439b7eeb979 | Acceptance criteria - Has the bedding material been installed as per the manufacturer’s specification?
note | dc7d98e8-fd2b-5483-a1c5-bfd0792cf623 | ○ Conforms IFC drawing (if applicable)? Bedding depth minimum 100mm Overlay depth minimum 300mm.
button | 840003cc-e635-5701-a143-c835b3aac9f2 | Acceptance | Yes,No,N/A
note | ebcb7ddc-4804-5539-b326-c53253a4bba5 | Key - S
note | d56cc03a-9fe4-5729-9ce1-aac9f390b806 | MDR/VIVA - S
note | 3545a6a2-2a82-5543-b705-d67b4c14d4c6 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 40a493fd-fc73-56ff-b76a-11c82c4aca50 | Delivery Dockets
section |  | 3.0 Fabrication
checkpoint |  | 3.1 - Welding
note | c294a51d-6f54-5130-90f6-eb670c14e7e4 | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL, 235929-RE-ENG-INT-0003-WIITP – P11U, 235929-RE-ENG-INT-0003-WIITP – P11P RE-ENG-INT- 0072-PR
note | 465ee7ce-78b9-5f9b-a628-3ba97cc5a5aa | Acceptance criteria - Have the lengths been welded as per the manufacturers spec and welding duration?
button | 809ff6b1-6d07-56ad-b118-fd4277e06e74 | Acceptance | Yes,No,N/A
note | 3fbd0f91-d6ce-5bb4-98fe-7e484c7bf8e7 | Key - H
note | dab1c000-e60f-5d7d-8e8c-c8dbab41a417 | MDR/VIVA - W
note | c2164181-e3e5-5cf8-bf5a-043ea46d69f0 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | ec7e59e8-fd34-5653-88cf-ec8e46ce3bd9 | Carbon Steel Subcontractors ITP
tickbox | cfaeccec-037c-5a5a-ac7a-ecbd12b7947e | Welding Log
checkpoint |  | 3.2 - Non-Destructive Testing
note | 486a2b0c-a70a-5d36-bb12-7e04d0c41229 | Ref docs - 235929-RE-ENG-INT-0003-WI, 235929-RE-ENG-INT-0003-WIITP – P11U, 235929-RE-ENG-INT-0003-WIITP – P11P
note | a7a61130-a36d-576a-8592-aa416af83f9d | Acceptance criteria - Have the welds been tested as per the ITP’s referenced in the isometric drawings?
button | b443529e-8a04-58bb-b5a5-d1f82d910efa | Acceptance | Yes,No,N/A
note | 1120661a-67c7-54c2-b686-9022051c9962 | Key - H
note | ff5dff05-a015-5c5d-a941-629f4aece781 | MDR/VIVA - W
note | 7d3ff64f-f547-59cc-a508-2fcc22ba5410 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | e545d2cf-966b-5866-a54d-54122c96ea11 | Carbon Steel Subcontractors ITP
checkpoint |  | 3.3 - Coating and wrapping
note | 8bf95acc-370c-5182-864a-b7c36a80070d | Ref docs - 235929-RE-ENG-INT-0003-WI, 235929-RE-ENG-INT-0003-WIITP – P11U, 235929-RE- ENG-INT-0003-WITP – P11P, Isometric Drawings, RE-ENG-INT-0045-PR
note | 82ba2df6-08c4-5cca-b807-35c31573ac31 | Acceptance criteria - Has the application procedure been provided to MDR and approved?
note | b92bc546-f68e-511c-9f11-77f51a78aca1 | ○ Have the welds been wrapped as per the drawings and specification?
button | e08cbf14-f7b7-5978-9ac7-2e0598e6fdb2 | Acceptance | Yes,No,N/A
note | cddb41ac-92a2-57fa-a381-c5ac971b34c7 | Key - H
note | 4bfcee3d-db0b-5ca0-b7a3-b7f5a751462b | MDR/VIVA - W
note | 27da277a-a01f-5702-aad1-b809ff1e741a | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | d34aa907-7af7-536a-802d-404894677a4a | Carbon Steel Subcontractors ITP
section |  | 4.0 Laying
checkpoint |  | 4.1 - Lifting into trench
note | 3020b60f-2a20-52ee-8482-ba2733929e5f | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.2.1 Item 12.2.7
note | 0ebca3e8-b4e0-5995-a6dc-b31d69c47550 | Acceptance criteria - Before lowering in, caps shall be placed on open ends, flanges, etc., which shall remain in place until piping connection can be made. Particular attention shall be given to the need to protect pipes from damage due to loads from heavy plant, has this been completed?
note | 6107e8d1-45af-579a-98d2-b28b7b303cdb | ○ Have pipes been laid to true line and level?
button | cc886c0c-d974-50a1-88f1-4a4bbbc407ca | Acceptance | Yes,No,N/A
note | 2e9f9d7e-1632-5758-96ac-4976acbb047d | Key - H
note | 48bee62c-eb6b-56d7-a4ba-a3141c69c12a | MDR/VIVA - S
checkpoint |  | 4.2 - Haunching
note | 853ff899-9390-5b9c-9d97-19b9c9c8f666 | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL
note | 5bb92813-67f3-56b6-b3a8-bf427cb12253 | Acceptance criteria - Has the backfill material been haunched appropriately around the pipe?
button | 96cf41b5-b226-5b5c-b787-6ed21b678413 | Acceptance | Yes,No,N/A
note | 7b8372d3-6171-5afb-8ba0-0da9215f819e | Key - W
note | 0d6435e9-4738-5e3a-96b6-c2cf33abce91 | MDR/VIVA - S
checkpoint |  | 4.3 - Pressure Testing
note | 715e27fa-ff5a-5bd5-a1f3-4f5de9d2724b | Ref docs - 235929-000-CV-SP-00006 Section 13.4
note | d4829924-eecb-546f-8b28-2e9f3be92144 | Acceptance criteria - Is Air Testing or Hydrostating testing being completed?
tickbox | f0575c3c-2da0-5ade-a2dd-94b4afce478a | Air Testing
tickbox | af80b008-f334-552a-84bf-6ca854c2deee | Hydrostatic Testing
textbox | 5dc71d95-776c-5c33-9c70-f9e119557e77 | What is the test pressure?
note | 1dc7d2d9-f2e3-5445-831e-cf9e26916495 | ○ Has Testing been conducted to all joints and inspected to confirm no leaks?
button | 27fa593f-fe4d-5e25-87c1-edc660c550a2 | Acceptance | Yes,No,N/A
note | bff961a8-4f9e-5f1f-88f6-592b49071a48 | Key - H
note | be926e3f-3800-5ce5-b1d6-70e95496f49c | MDR/VIVA - W
note | 71d2ce08-9026-5fc9-8332-3765b7ba9488 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | ed5904ef-587c-5458-b14f-cb7361161eae | Testing checklist
checkpoint |  | 4.4 - Backfill Materials
note | be659b9e-7c0b-5f8f-a4f7-4c7627e2bd79 | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL
note | 0959da6b-0395-57e0-9d97-777ab07a1d6a | Acceptance criteria - Has Sand Back fill been placed to 300mm above Pipe?
note | ccd55caf-a398-5f89-8484-eba78cac6eac | ○ No compaction equipment to be used until 300mm above pipe.
note | ff5fcc12-b943-551e-8573-9939e1da334c | ○ Has select backfill been placed in layers not exceeding 150mm loose thickness?
note | 66b5b3ce-ca1d-5e48-9c8b-2d8b27123528 | ○ No compaction equipment has been used between 0-300mm above top of pipe, light compaction equipment has only been used from 300-600mm. above pipe.
button | ffb66a1f-570b-5f80-9c7e-751caf0c1935 | Acceptance | Yes,No,N/A
note | 83a8d920-af65-5333-b1d8-ac5849cef5c6 | Key - W
note | 22c456ff-938b-5283-b10d-c6a1817a0241 | MDR/VIVA - S
checkpoint |  | 4.5 - Backfill and Compaction
note | 5d1da675-3610-5f40-beb3-a1261a4d17c4 | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL
note | 57f84272-9aa3-550e-ae51-c48a1ee51404 | Acceptance criteria - Sand Fill - not less than 90% of maximum density or 70% of relative density, except that under paved areas the entire depth shall be compacted in 150mm layers to not less than 95% of maximum density or 80% relative density.
note | e59a1a36-5d06-55cc-a2c6-d42811dc859e | ○ Select Fill - Backfill under pavements shall be compacted to a dry density ratio of no less than 98% modified comp active effort.
note | 480854a0-65cb-54b9-83b0-a0cb506e7a48 | ○ Backfill to be in 250mm compacted layers.
note | a260f2aa-49ca-5118-9188-ed734407a01b | ○ Testing Frequency: Minimum 2 field density tests for each 185 m2 of each compacted fill layer, but no less than 3 tests for total area
note | e16bd1ac-11ae-54ea-aae9-1673a5f8507c | ○ Has compaction testing been completed as per the project specifications?
button | 96fa03c8-7a24-5525-b8e3-f1056e5019d0 | Acceptance | Yes,No,N/A
note | 46c8f2e3-495d-55b1-8237-e875090a51ff | Key - W
note | 94d0a05e-08e8-5d4c-95fe-f5c5408a3bb1 | MDR/VIVA - S
note | 224a8dba-bfd7-5f6b-9f42-48191f4b6cb2 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 4f4a6cd8-092f-521a-94f8-fdd7b33f3688 | Compaction Testing Results
section |  | 5.0 Testing and Conformance Check
checkpoint |  | 5.1 - Test Pack
note | e2a98f6d-59dd-5c22-9dd3-182a57980a79 | Acceptance criteria - Has a test pack been provided?
note | f1d9cf5e-27ac-5e86-a5fa-5bbe7744895b | ○ Test pack to include.
note | f7a2af4e-4e44-580d-a964-41ec8b9161c1 | – Test Procedure
note | 3afb6982-b28d-5c79-a7ce-2291127b05dd | – Test Map
note | f5aa3906-c8b4-5f00-afa5-4e2d551fd044 | – Equipment Calibration
note | ce701d07-e07f-57c3-9507-940b90a5e4e1 | – Equipment Details
note | e2f5bb24-9a06-5725-925a-f4ea5a191725 | – Exclusion zones if require
note | 423d8eec-6474-5252-9305-149d9f2bd3f2 | ○ Provision of testing log template
button | bc28ded6-eca5-59f7-bd74-6a9e752dda06 | Acceptance | Yes,No,N/A
note | cca49944-4970-53c1-9353-c2ea58f6df5a | Key - H
note | f9841f43-4346-5704-bc67-ef173fd1f9f9 | MDR/VIVA - H
note | ab617d9b-2f39-5d7a-82fa-bc63bf3036cb | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 914d8a34-6b14-5776-a3c3-1f4c4153b5e5 | Testing Log
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 5.2 - Survey
note | 2a5fb68a-c9ae-5c0a-9219-14d3c39ba437 | Acceptance criteria - Tolerances in alignments shall be limited to +/- 25 mm vertically or horizontally, unless otherwise specified on engineering drawing, has this been completed?
button | fa08bc86-b55e-52ed-9d4d-63b6278d14d2 | Acceptance | Yes,No,N/A
note | 2b143989-0709-5519-9296-7f7c8c55bc99 | Key - W
note | 67902516-9bdf-585f-9805-553d9100a5bd | MDR/VIVA - W
note | 5d8b0057-907f-516c-aeeb-62d02d72637a | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 35a0e63e-6b0d-5b7b-aa6b-ddbb1eedf264 | Survey as-built
checkpoint |  | 5.3 - Quality Submission
note | 2a979cfd-fae0-582e-9348-94db278ed327 | Acceptance criteria - Have all QA documents in-line with the specification been provided to MDR for review?
button | 6ad83100-20ef-5234-9588-0073c634af13 | Acceptance | Yes,No,N/A
note | 78b53b3d-e239-5cde-9ae9-ecd3ed391ca9 | Key - H
note | e4d21162-3d8d-505d-9c3e-1471fcc8a926 | MDR/VIVA - H
signoff |  | AUTHORITY HOLDPOINT
checklist |  | INF-HSEQ CC0398-ITP-035 Concrete Pile Cropping Rev A | itp | INF-HSEQ CC0398-ITP-035 Concrete Pile Cropping Rev A |  | 4c4a6751-f535-4b4a-a697-a5d955c6f6ee
section |  | 1.0 Preliminaries
checkpoint |  | 1.1 - Starter Bars
note | 8ae24b3d-abce-5ec3-a865-da3d22f551ae | Acceptance criteria - Are starter bars (if exposed) in suitable condition:
note | 26aae61d-2e11-5bc2-8468-d6ce6b5c6b60 | – Straight
note | 012b3866-40be-52a2-8ae8-c5bba30a2dfa | – Free from excessive rust
note | da809df4-11ed-55ca-9580-ad82b8752848 | – Correct height projections
button | f747c67d-98e0-5e95-b947-4f033c769e31 | Acceptance | Yes,No,N/A
note | b648de6a-d547-58ea-aa33-9dc2bb839aab | Frequency - Once per Pile
note | 8bf1e468-0fd0-5880-873b-68e44c04f331 | Key - S
section |  | 2.0 Pile Cropping
checkpoint |  | 2.1 - Set out
note | 547f3e8a-9c95-53c6-9279-ec3ac70702f9 | Ref docs - DWG No. GRN-92002-030002 – 10
note | 7a97ffcd-c497-5834-ab89-9a8989418304 | Acceptance criteria - Pile cut off has been marked by survey
button | 16891ff0-f0d8-5aca-a0b4-ea99bd4bdea6 | Acceptance | Yes,No,N/A
note | 32415fad-52df-55de-9551-5d7437b240d9 | Frequency - Once per pile
note | ea87b81d-777d-5230-beec-105541b3cec9 | Key - W
checkpoint |  | 2.2 - Pre-Cutting (if required)
note | e49d1463-e486-50ab-9dcd-8ba4792b90cb | Acceptance criteria - Has the pile been pre-cut along survey marked level i.e. ring cut method
button | 87296c93-4e49-505e-837e-62f45d55a68a | Acceptance | Yes,No,N/A
note | 6f185c69-5e93-501e-b2a8-f79cc06c5f79 | Frequency - Once per pile
note | 00abd880-eecb-5802-9f7e-6875a3e1f36f | Key - S
checkpoint |  | 2.3 - Irregular Concrete
note | 764a1a55-27f2-5386-9703-ac4da874dcc8 | Acceptance criteria - Large uneven/jagged concrete sections to be removed to create flat concrete cut off level
note | d90861ba-1252-5b52-98d7-e507ecc8f546 | Frequency - Once per pile
note | 10c8b0f0-c2ca-5cac-8a90-7fb2aad3a8dc | Key - S
section |  | 3.0 Conformance check
checkpoint |  | 3.1 - Tolerance
note | a730d33a-9f35-5641-bde1-b78330e193fa | Ref docs - DWG No. GRN-92002-030002 – 10, As per civil (235929) drawings
note | a4970c45-9438-592d-b7aa-d90ca2f68587 | Acceptance criteria - Survey to check actual pile cut off level is within +-+-25mm of cut off level.
button | e469f67c-a8e9-53ff-bcad-9e7658341987 | Acceptance | Yes,No,N/A
note | 1beded09-da3b-5934-9a83-5b8f9e0da0e0 | Frequency - Once per pile
note | 94c247b9-392e-570c-b7ca-c0cb7b147bc4 | Key - S
checkpoint |  | 3.2 - As Builts
note | 8fe34c38-2987-583d-9455-7320780f7cba | Acceptance criteria - Survey to pick up cut off levels for as-builts
button | 69d2f9bd-cbaa-5645-9baa-4cfcb2c102f5 | Acceptance | Yes,No,N/A
note | b57b76f9-0680-5eb7-94a2-6e5c4eb6ff82 | Frequency - Once per pile
note | eb59b1ea-608a-5ad2-ac26-b338b34c4cd4 | Key - S
checklist |  | [Rename] Document Upload Checklist |  | [Rename] Document Upload Checklist |  | 76c6cdce-e3d9-41a3-8540-d3cda204792b
checkpoint |  | Document Uploaded Below
checklist |  | INF-HSEQ CC0398-ITP-037 Earthing Installation Rev C | itp | INF-HSEQ CC0398-ITP-037 Earthing Installation Rev C |  | 7a0a6c07-608b-4b35-a60a-50d0dad50f36
section |  | 1.0 Pre-start activities
checkpoint |  | 1.1 - Set out
note | 8cee6730-a2af-57b1-9b57-a7060567d2b3 | Ref docs - Composite Drawings
note | f9db8eba-ea63-5a3b-b231-a62e4b8425d3 | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
note | 9cd90a20-55f5-5ed1-8e51-afbaaaabb4ef | ○ IFC and latest available revision used?
button | 38bfef6c-4477-56ff-b7bf-2e48acf3c825 | Acceptance | Yes,No,N/A
note | ccab05ea-96f2-5d9b-8845-685986d487cf | Key - H
note | 4736233e-544c-5c6d-9c9f-7c43296ff3e4 | VIVA - W
checkpoint |  | 1.2 - IFC Submission & Approval
note | 48ae4f29-13bc-5989-b102-f90696dad5c3 | Ref docs - Composite Drawings
note | 096dd421-f790-5fdd-b740-14fabb48a408 | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
button | 730ae177-d0a9-5ecc-8931-d7ed6e7a5bbd | Acceptance | Yes,No,N/A
note | 425d137c-e481-54b7-baac-c7f140c87657 | Key - H
note | 4520f176-6193-5385-af2c-2ea0c5485497 | VIVA - H
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 1.3 - Permits
note | 8643866f-3b27-5c58-abcb-607e9424f0ce | Ref docs - Symal Safety Procedure
note | cc5f3ad8-fd9e-59de-a80c-50fbf3185263 | Acceptance criteria - Have the below permits been created.
note | 62f01cff-b9fb-5db5-a10a-704c3b1a713c | – GPP
note | cfa9dec5-9be5-5741-8033-b68e5534d884 | – Working at Heights
note | 0be84294-74d3-5805-afad-4ba0450238f1 | – Hot Works
note | a1987483-24bf-55a4-8842-87af73d1479b | – Confined Space
button | ea83f727-45e6-5108-8083-72e0ec6ad20d | Acceptance | Yes,No,N/A
note | defa0d4d-5c33-58d2-9e91-f8ef1fed82fd | Key - H
note | 4043a63c-c6bc-5d89-b965-68229e6ffbb0 | VIVA - W
checkpoint |  | 1.4 - Determine Lot Size
note | 278c45ec-97a7-58c9-ac20-fd4bfa25fb30 | Acceptance criteria - What is the lot size?
button | eef4a63b-c72e-5ac2-a0b9-e21eb7301941 | Acceptance | Yes,No,N/A
note | 77204dd3-a107-585b-a5e4-284846c25127 | Key - S
note | 9f59d620-efb9-5df2-a905-30e42032d1bf | VIVA - W
checkpoint |  | 1.5 - Materials
note | 126b8a65-2968-50cf-8671-35425da66613 | Acceptance criteria - Have the provided materials been accepted, and checklist completed?
note | 11f792d8-9c8e-54ba-a08a-b1d0846c9ca3 | ○ Have the materials and tag numbers/heat numbers been verified?
button | 80741666-14ab-577f-967f-a2eb3ddb637c | Acceptance | Yes,No,N/A
note | ee94d348-599c-5e06-9e57-3a2b4f92428f | Key - W
note | 01ff3918-4f7c-59a6-8323-5dd349a05a49 | VIVA - W
note | 5d4ad777-f65b-52a4-abe0-ccda3623b65b | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | b3168178-9984-5c7f-89b6-0e87e2c916cc | Material Inspection Checklist
checkpoint |  | 1.6 - Electrical and Earthing Pre- Qualification
note | 4b91c8eb-c2ee-5a09-9668-41699dcfd468 | Ref docs - Welder Qualifications and tickets. This ITP.
note | a412595e-b980-5377-a87a-dd96c803b364 | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
button | c8e50075-a9a8-5b90-b3b8-b9435ffbfd2e | Acceptance | Yes,No,N/A
note | 4b7f81a9-4fea-5c02-a633-aed49cca798f | Key - H
note | fd60531e-9225-54c2-a328-1eb0c9676d5d | VIVA - H
note | 549b317b-2bfb-5e43-84be-89e06899345c | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | d759a7aa-28f7-5428-8682-3bff9b89a98f | Calibration Certificates
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 1.7 - Bedding and Backfill Materials Approval
note | 436174e2-eaea-5ba2-85c5-ccc504afad72 | Acceptance criteria - Has bedding and backfill materials been approved for use?
button | 05f36b85-69b2-57a6-ab82-85178e69e938 | Acceptance | Yes,No,N/A
note | 20b32423-f7a9-56c5-9906-1e4c08531f2b | Key - H
note | 6094a024-b76e-5a0f-b0cc-54ecf6e84fa9 | VIVA - H
note | 50e886ac-692b-5d7d-b1b0-677900b02e8a | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 0be29c63-0b82-5db8-a99b-ca4f7ec8709d | Material Approval
signoff |  | AUTHORITY HOLDPOINT
section |  | 2.0 Excavation and Bedding
checkpoint |  | 2.1 - Service Location
note | a6a4cd41-ff67-5b2d-814d-812a925ed46e | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
note | b72222ef-31fd-5235-84d2-e67c3bf48616 | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
button | 6660690b-af66-5259-bc7d-dfd50158f4a9 | Acceptance | Yes,No,N/A
note | aa9b01ea-8147-58f4-ac16-a6c9b3a7641c | Key - H
note | 1f4566f1-36c9-54ad-b24b-7e1d1a0b6e43 | VIVA - S
checkpoint |  | 2.2 - Excavation
note | 3fd93b6e-8747-57f5-8edd-a0c324789b22 | Ref docs - 235929-000-CV-SP-00002 EARTHWORKS
note | 495bbc0b-ed7d-5190-9ee0-ff5060f3ec4d | Acceptance criteria - Trench depth into buried ground 500mm width to provide sufficient width for earthing to reach design depth.
note | c3773a7f-7038-5d6c-88bd-6b5425a681ca | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
button | 1e5db9d1-aa8c-5dfa-b5a7-928cc4db3959 | Acceptance | Yes,No,N/A
note | ebb7ae07-bfcb-5a95-ad3f-8ca8b259c18b | Key - W
note | 5b793bf8-7b11-50f8-a3e8-59c629a88987 | VIVA - S
section |  | 3.0 Laying/Welding/Handover
checkpoint |  | 3.1 - Earthing Installation
note | 1d2b95cb-4390-5980-a304-8d45ab7fc01e | Ref docs - Viva Energy Earth Grid Connection Checklist (001) - ITP
note | 01dbcbc2-d472-5e1d-b3da-665f236bebcd | Acceptance criteria - Have works been undertaken as per the subcontractor’s checklist?
button | 368df9fc-11ad-5460-a7ff-8c4dea9f8e7f | Acceptance | Yes,No,N/A
note | 40ad3313-e035-5d46-8810-0c94ba2f6d40 | Key - H
note | ff7894d3-826d-5955-b2a8-e830f08ddb67 | VIVA - W
checkpoint |  | 3.2 - VIVA electrical inspection
note | 7772b47b-699a-5e49-9c0f-1e6a2f22c281 | Ref docs - New Item
note | 9c0cbd6e-4d47-5f69-9cc5-eebcca38149b | Acceptance criteria - Has the electrical inspector from VIVA been notified to attend the project site and review the installed earthing?
button | 243f7759-ac4f-5381-8a93-e2e425613cde | Acceptance | Yes,No,N/A
note | f6416a4c-6330-5a24-bc9f-cc9c58ae11ea | Key - H
note | 48e1ff56-6e99-54ab-bcce-f995099c8b6c | VIVA - W
checkpoint |  | 3.3 - Earthing Network
note | 78c81d56-ab20-58d5-a501-0d549b383be5 | Ref docs - 239529-CO-FM-00003 – Electrical Earthing by Area
tickbox | ad308061-8072-553d-9f1a-2e4df92be13e | Has earth Grid installed at correct depth of cover?
tickbox | bc035c23-b5ea-5126-8dc3-8d814b3d8986 | Have earth rods/connections/ferrules are of the correct type, length and material and located as per the approved drawing?
tickbox | b48f7b01-e8e3-5422-940b-f97933c91c99 | Has the cleanness and secureness of all earth rods/connections/ferrules been checked?
tickbox | cd286451-cd68-551a-bfbb-41f0f673a3e0 | Are all identification labels being correctly fixed and visible?
tickbox | d3698155-4d3b-52ad-84c4-90f3e70062b1 | Are all cable clamps are secured correctly, coated with anti-corrosive coating?
tickbox | da88522c-746b-5a9c-b980-3711e14ba93c | Are all cables of the correct size and type?
tickbox | c2cae75b-1bd2-53fd-986f-299cae0622f6 | Are all exothermic welds being acceptable?
tickbox | db16fb47-13c9-568b-9903-e8f5cfaa24f0 | Has the individual earth path / bar resistance been recorded?
tickbox | 92f8d563-eca5-5549-a8ea-c703fbd1d8b6 | Has the overall grid earth path resistance been recorded?
tickbox | 1a2439eb-5827-5814-a495-76eb37f3937f | Has the anti-corrosion material been applied?
tickbox | d84bfc1b-9f3d-5ca7-b0d3-b10d5d051ccb | Have 3.0m tails been extended as per the project requirements
button | 45692619-9886-52c5-b1ab-642068c4038e | Acceptance | Yes,No,N/A
note | fb08ad92-3d23-5bbf-bcc0-b28d71599733 | Key - W
note | fe854fa9-3616-501a-94c4-1ab64d7ded74 | VIVA - H
note | 95791d8c-9a9b-528a-8132-601b24dca2f0 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 57a38e06-0052-5c5d-93f7-d4e0674b48af | Earth Grid Connection Checklist (Rev 1)
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 3.4 - Electrical Earthing by Area
note | 1afbdddf-69a1-5ff5-bd83-4f0c4fc5ec31 | Ref docs - 235929-CO-FC-000034 – Electrical Earthing by Area VIVA Energy Earth Grid Connection Checklist
note | bedd8cc5-af96-5a02-a58b-c925bdcff87a | Acceptance criteria - Has the equipment earthing in area earthed via earth bosses or studs been installed as approved installation drawings and specification?
note | b3efdd5a-2565-53a4-a62a-34234df11773 | ○ Have all earth bosses and studs been tightly fitted with shake proof washers and coated with project specified protection?
note | 94d60ad9-2d51-5ca9-b0d2-df77460c8f8e | ○ Are all earthing conductors correct type and size not less than minimum size specified in approved installation drawings?
note | 3e51b72b-91c3-5b1f-8bfc-4ac80cbdd0a2 | ○ Are all earthing conductors properly installed and protected?
note | 4721d462-f575-586c-a40a-81f4005d7805 | ○ Has earth resistivity testing been completed?
note | 0b67eee8-5928-5471-8bce-81c1e5bf14ac | Structure Steelwork Earthing:
note | 4c4fddbf-f9c3-538d-b358-f5b44c870dc0 | ○ Has all structural steelwork that is bolted and provided with equipment earth bonding connected to the main earthing system where required?
note | e5d3d158-7ced-5ff4-b948-ba58a504e195 | ○ Have all earth Bosses/Earth Points been cleared paint /rust free prior to connection?
button | 13daae97-2f9a-5bd7-959e-cb70d2d46cb9 | Acceptance | Yes,No,N/A
note | 4c1cd6fd-f03c-5c6e-bdff-4b1252ea620f | Key - H
note | 4114626f-72ed-5db8-a2ae-2bd2c71359a2 | VIVA - H
note | 6d8e831b-e53d-5591-bdc5-aac6c6022df4 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Testing Checklist
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 3.5 - Backfill
note | 487668b8-16b3-53a4-b9c3-e6f22fedf167 | Ref docs - 235929-000-CV-SP-00002 EARTHWORKS
note | 659566b9-c039-53ff-8ca4-79f1d32bae6b | Acceptance criteria - Has backfill been completed to provide a compact and even surface?
note | cc414001-3505-511d-8ccd-d4c416442e68 | ○ Has testing been completed prior to backfill?
note | cbe10000-05db-58cc-9b3b-a9ba19a2449d | ○ Has all third party inspections been completed prior to backfilling?
button | 8c897e66-c8d4-5f84-a29a-b14e1d31057f | Acceptance | Yes,No,N/A
note | 4018d55e-932d-5c31-959d-29376e550a55 | Key - S
note | 6a3762fa-2805-55d6-8410-6501bea5ce81 | VIVA - W
checkpoint |  | 3.6 - Clean-up of site
note | 243c4a29-69e7-54f9-a307-2031f2764eb7 | Ref docs - 235929-000-CV-SP-00002 EARTHWORKS
note | f3956859-b308-5440-8888-6834a83739b3 | Acceptance criteria - Have the areas affected by the works been restored to a condition similar to that which existed prior to the commencement of the work?
button | 26725281-f51d-5428-afb0-927acb7d577f | Acceptance | Yes,No,N/A
note | 554f47ba-8a5d-5aea-9752-d8eb324484ce | Key - S
note | 7493cd86-c956-5d86-82b8-c74b01dfde1d | VIVA - S
checkpoint |  | 3.7 - Identification and recording
note | 90af6f27-0d17-5a94-8097-9ccfb60500af | Acceptance criteria - Have the actual installed location and depth of the earthing, and location of pits, been accurately recorded on an as built?
button | 6d3a8327-ee7d-548d-86b3-db7ecfdc9ae9 | Acceptance | Yes,No,N/A
note | d2d51ca3-206d-5f51-8100-a5c9f88815b4 | Key - H
note | dd4e0b01-2fc7-5f87-ac04-1713251b13b0 | VIVA - H
note | 5e90900a-3596-508c-a3f2-92f1d97fac5a | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 798d6317-ef59-5dda-8c92-976b88b7370c | As built
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 3.8 - Work is complete and complies with design plans / drawings / specs
note | ec21e9b3-5d1d-5848-99ed-4e9c836516c6 | Acceptance criteria - Redline mark-ups As-Built Survey: Earthing to conform to the required depths and locations.
button | 90ad3371-c0ee-5df7-b6a8-ed80c752254a | Acceptance | Yes,No,N/A
note | 22dda464-5331-511e-914a-0cc0527fe875 | Key - H
note | 65c49590-c187-5ea8-a1c3-a7d44798e24c | VIVA - H
note | 8df9d0d1-bfbc-5ae1-a3b2-e35ad5bf1bd5 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 73f1bef4-f865-5873-b180-46a67b44ace4 | As built
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 3.9 - Certificate of electrical safety
note | 14d30253-0ebb-534e-b20c-a681e54211b7 | Acceptance criteria - Electrician to supply Certificate of electrical safety for earthing installation
button | 0ef0eb60-e21e-521b-8016-faa0c1457ce4 | Acceptance | Yes,No,N/A
note | effdc95a-54bd-551b-9b74-5e57b43b9bc0 | Key - H
note | 658d1851-ee8f-574b-89c7-38ff328fdef5 | VIVA - H
note | 98e74aa0-7bdd-5f80-8c89-9baeec6f09ea | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Certificate of electrical safety
signoff |  | AUTHORITY HOLDPOINT
checklist |  | INF-HSEQ CC0398-ITP-032 GRE Installation Rev 1 | itp | INF-HSEQ CC0398-ITP-032 GRE Installation Rev 1 |  | 89d4c807-6fd7-47cb-ab95-9fa653e64bf6
section |  | 1.0 Preliminaries
checkpoint |  | 1.1 - Set out
note | 30713abf-c728-50b9-be2b-6ed4b4a9e9d2 | Ref docs - Drawings
note | 786e257b-6d88-5f96-94c1-2ea430fa376d | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
button | 3b23c7b9-71f8-5b57-a725-40fe12f52f8c | Acceptance | Yes,No,N/A
note | 4cf31203-4eee-51d6-9509-a70825913db4 | Key - H
note | e413c664-690d-5106-b782-861b88454577 | MDR/VIVA - W
note | 65d4218c-b18d-5ae5-8445-1dcdeeee490d | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
textbox | e2899be5-b8d7-58b5-84bf-564a010beee8 | Drawing No.
textbox | b405ebfc-9fbe-5046-b9cd-df742066b028 | Rev
checkpoint |  | 1.2 - IFC Submission & Approval
note | f96de24c-a172-59b5-81b7-e8d30660ffd6 | Ref docs - Drawings
note | 1993cee6-53af-5cdf-914a-2a07012ec46d | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
button | 00df8c37-fe2a-5b97-bbf3-5323ec4dcbbf | Acceptance | Yes,No,N/A
note | 588c79be-bedf-5ff9-a61a-09045614bcfe | Key - W
note | 239d854c-89d2-57f5-b7e9-6b1b122f3c5f | MDR/VIVA - W
checkpoint |  | 1.3 - GRE pipe confirmation
note | ba7e2e4d-dbad-5f0e-92b7-ea558b642845 | Ref docs - Drawings, QF-108-01 Material Receipt Initial Inspection
note | 936cd6f9-24e6-5ed5-aca3-7df2086375d0 | Acceptance criteria - Has the correct class & type of GRE pipe been supplied and free of defects?
note | b52e2cad-3baf-5e11-93f5-bf50dfda8077 | ○ Verification of material tag (heat) number
button | 54e1cb37-b599-5877-ac4e-d086997d692a | Acceptance | Yes,No,N/A
note | de104475-90b8-5af3-8ec7-309b331a5bfa | Key - H
note | eb5c0fc7-f264-5168-824f-f7e78a91288a | MDR/VIVA - W
note | fe2dca5e-38b0-54a9-a1c8-c7323eda5c20 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 97378374-0cce-5b5b-ae85-b1843024c635 | Material Inspection Checklist
checkpoint |  | 1.4 - Permits
note | facfa38f-1cd7-58f0-a248-1fb4e787f1d0 | Ref docs - Symal Safety Procedure
note | 25f4168a-d062-5e3b-aa57-b46b9db0948e | Acceptance criteria - Have the below permits been created as required.
note | e80a82e8-381a-531d-bcea-0134343b8a00 | – GPP
note | e47e8d71-7556-5d5f-8ed5-4e7b509a2c12 | – Working at Heights
note | b664ff73-05f5-51df-99d4-216f445adade | – Hot Works
note | cee09680-e01f-552a-aa6d-7b3e898cab09 | – Confined Space
button | 15b6ba1d-3c9e-5ded-8ab0-30aa5438e010 | Acceptance | Yes,No,N/A
note | f8c19699-76b6-5e43-a329-cab66101b23e | Key - H
note | 0ef20b02-7e86-5f25-9348-87e9cc93d093 | MDR/VIVA - W
checkpoint |  | 1.5 - Determine Lot Size
note | e21f428f-a0bc-5753-8bb3-35c1d7d4868f | Acceptance criteria - What is the lot size?
button | 2663c145-56ab-5646-b24c-8286a8e0e071 | Acceptance | Yes,No,N/A
note | 19d3046e-c7cb-57bb-bb39-8b3e3fc79912 | Key - S
note | be91c779-2273-528c-8cab-08fae293e146 | MDR/VIVA - W
note | 48a2fae0-d4d3-52d5-91d3-e3757a3f64f7 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 0e5fb777-fbc3-5563-9810-4fdb69d32e65 | Lot Map
checkpoint |  | 1.6 - Joint Pre-Qualifications
note | 1da3b421-5826-5393-84df-468965e8b937 | Ref docs - Qualified technician qualifications and this ITP
note | b89d1b2b-6593-5bf4-b701-1e0fa94ca9e1 | Acceptance criteria - Technician qualifications submitted to client for approval
note | 6c601e05-23e8-57e0-9dbd-3f2e7ca6d618 | ○ Welding Qualifications Equipment Calibrations
button | 0320eb26-4f89-5952-9e5a-12a6042e28ec | Acceptance | Yes,No,N/A
note | 06ae4ce3-f304-53b7-92f6-27013394d5c9 | Key - H
note | f23d664f-473f-5e88-887c-df62ed7d6583 | MDR/VIVA - H
note | 693d66bf-e7ff-5a87-acd9-365576b0e6bf | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 733e509e-ab28-5d1a-8831-c6361343a3b3 | Certifications provided to client
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 1.7 - Material Approval
note | 4f5ffb21-a37b-5c66-987d-32a2250ad910 | Acceptance criteria -
note | 7979c967-4c4d-5c97-8fc2-40445dcac3e5 | Have all materials been approved for use
textbox | 684403d9-1876-58f4-af5a-3db3e7715e9d | Bedding/Haunching Material
textbox | 5b25a19d-79c4-5f1a-a4cf-f6ae4256c98a | Backfill Material
note | ecff2fb0-fee7-5349-92fe-09c4c47939e5 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
textbox | 30197b59-df69-54e2-beb4-cc07e29b22c1 | Material Approval Reference
section |  | 2.0 Excavation and Bedding
checkpoint |  | 2.1 - Service Locating
note | cf29ad10-f86e-50dc-9540-73ee4d504b63 | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
note | 9cdd3930-cd3c-5455-a906-8d4d841d96f9 | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
button | 44c97db5-6c6d-55a7-b059-b5b01305bef3 | Acceptance | Yes,No,N/A
note | 74b04a3e-3017-5527-a473-10ae7f2b9fa6 | Key - H
note | 32df1a5b-1a2a-5b6c-a049-a9911ebd6328 | MDR/VIVA - S
checkpoint |  | 2.2 - Excavation
note | 16fbca72-4794-519e-a9fa-4e1de14d41bb | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALLSect ion 12.1.12
note | 62155c81-3b03-5392-b137-1d0fd014cd4d | ○ SUN_ENG_P RO_015 Bondstrand Piping UG Installation Procedure Section 3
note | bb9363e7-048f-5d7f-9c6a-127e57cd2445 | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth.
note | a53247f9-7304-595a-8b9c-353ff3bfc137 | ○ Width of excavation to be 1.25 * OD + 300mm
textbox | a82df1b2-f768-53a0-a213-1f4d37bb5124 | Pipe Diameter
note | 5fa84543-4642-5d7d-bb14-07e154d9c9df | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
note | 92fc4509-5166-59ea-96b5-f0bbd04d6c99 | ○ Trenches to be benched and battered as required (if trench >1m deep). Benches/batters to be 1:1. No material/plant to be placed within zone of influence.
button | de1d88cb-9936-5a9a-a462-b08004b2418a | Acceptance | Yes,No,N/A
note | ca7decc9-bd3d-5b95-875b-90d1d27d6afc | Key - W
note | c277ddbc-ba32-52ba-9e7c-e0bab806a685 | MDR/VIVA - W
checkpoint |  | 2.3 - Bedding
note | 54faa16d-8371-5b8b-bec7-391dde68b4e2 | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8.
note | f386c04f-2692-5e15-b5d1-61a2ab2612c2 | ○ 239529- MG1668- 15740-0400- SD-000010- NOV Bondstrand pipe installation guide - GRE
note | be5c67d8-a9c2-5bf9-a44c-859551ed1361 | ○ SUN_ENG_P RO_015 Bondstrand Piping UG Installation Procedure Section 3
note | 307f42ad-853d-598d-b7ce-168ed0d96f2c | Acceptance criteria - 150mm Bedding to be placed & compacted at the base of the trench.
button | a6732c34-6ebb-5d32-8ae0-4b8821ec0739 | Acceptance | Yes,No,N/A
note | c9d859d5-68ae-5fc6-9df0-e89bfe051a13 | Key - S
note | 5428a919-e1c4-57f0-9e89-a65ea123f96a | MDR/VIVA - S
note | a6dd7323-79be-573b-af5a-b1975bfa15b0 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 0b8e0979-7ff9-5f98-9748-6f5c29201350 | Delivery docket
section |  | 3.0 Bonding & Laying
checkpoint |  | 3.1 - Above ground fabrication
note | ac128511-4058-54f3-abc5-477770663af0 | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
note | 24c01a29-bf81-5ec9-a0c0-e9381b39454f | Acceptance criteria - Has works been conducted as per Sunrise ITP SUN_23_003?
button | e1039a33-f996-56f4-9ac0-6c7ef7b6b1bc | Acceptance | Yes,No,N/A
note | 7c318ffc-084a-5803-97d2-23e993a23be9 | Key - W
note | ad16aebf-dfd2-560a-9ad7-19d2b80f5f7f | MDR/VIVA - S
note | 149682e8-cca6-5aff-8df3-e93af23b1f9c | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | ce8994a6-7625-5ba1-ade7-29640d9d99f7 | QF-068-18 – GRE Bonding Joint Record
checkpoint |  | 3.2 - Lifting into trench
note | 8e861b5d-2860-52e7-8cf5-69cf6dbd59c6 | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.2.1 Item 12.2.7
note | 7c1c5b9d-26fe-5349-8623-42f0eb01bdce | Acceptance criteria - Before lowering in, caps shall be placed on open ends, flanges, etc., which shall remain in place until piping connection can be made. Particular attention shall be given to the need to protect pipes from damage due to loads from heavy plant, has this been completed?
note | 0ae23950-b10e-5318-afc9-b6c1442dd3a4 | ○ Have pipes been laid to true line and level?
note | c65b0773-d204-5979-80bb-ff6a3629d952 | ○ Has MDR been notified before the laying of pipework?
button | 86849bfc-cf35-5ada-b8b9-2f6ac00abff1 | Acceptance | Yes,No,N/A
note | 61838248-ac87-5356-a463-5bfd1bfff234 | Key - W
note | d94489fc-0488-594b-8b37-2bcb1844d20c | MDR/VIVA - S
checkpoint |  | 3.3 - In ground fabrication
note | dd92a3d5-6faf-55a8-88ab-3d2e1b31ef42 | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
note | 72f09452-57bf-51ff-960b-702c99a35d79 | Acceptance criteria - Has works been conducted as per Sunrise ITP SUN_23_003?
button | 741c6690-04de-5cc0-83bc-66718277384d | Acceptance | Yes,No,N/A
note | debd8762-a75c-54cb-8faa-652eba5c170e | Key - W
note | 2afe1bed-fd29-5200-9503-285e0c55a3c5 | MDR/VIVA - S
note | 9b72c91b-ca8e-5082-bb73-53d305b34568 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | f0f767ce-8ab1-5fcc-8ac6-8ce53bd3aaa0 | QF-068-18 – GRE Bonding Joint Record
checkpoint |  | 3.4 - Haunching
note | 0b2e9937-b249-51fa-8f22-89fcf2e2d0be | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
note | 57ddd853-6e4a-58ce-b5bb-6c5d199d68b6 | Acceptance criteria - Has the pipe been haunched?
note | 0fb8dd1a-6b10-5d5b-9199-ff5784090173 | ○ Have voids been removed from haunching material?
button | ae52b1d8-8849-5f4d-bac9-d89e53d43c2a | Acceptance | Yes,No,N/A
note | 7f6caa72-8b13-5cf2-ae14-d7b7e35fec87 | Key - W
note | d2485979-e57a-59e8-bbc2-455441c4159a | MDR/VIVA - S
checkpoint |  | 3.5 - Survey Pickup
note | 8f6a8730-4ed1-5d87-9e55-365b105e9f06 | Acceptance criteria - Has the pipe been picked up by the surveyor? Tolerances in alignments shall be limited to +/- 25 mm vertically or horizontally, unless otherwise specified on engineering drawing, has this been completed?
button | 89542738-7ef5-526f-8dab-702b999f512b | Acceptance | Yes,No,N/A
note | d8c1fafc-8cc4-5772-87f5-147a8d20f6a3 | Key - H
note | 5bc1259f-2ac4-5069-9458-305c5e040340 | MDR/VIVA - S
note | 2be8cae6-4c17-5bfd-88f3-4504bac1dc0f | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 9060a391-0bcb-5407-b7d7-e5964bc20d1b | Survey as-built report
section |  | 4.0 Testing and Conformance Check
checkpoint |  | 4.1 - Test Pack
note | 02a3257c-afbb-5eef-8166-5ca6f887ca65 | Ref docs - SUN_ENG_P RO_010 R0 GRE Hydrotesting procedure
note | bc78c93e-6e45-57fc-9b6e-c941fadc02d4 | Acceptance criteria - Has the test pack been reviewed and accepted prior to Hydrostatic Testing?
note | d828e2cb-e953-54ab-9fab-95395747e17f | Test Pack to include:
note | 77abd582-cab0-5f60-b942-9da198e90dea | – Pipe Runs/Location of testing
note | 09dbcddd-e90b-5e47-9782-1eab54dcf140 | – Materials initial inspection
note | 52d47666-02c6-5293-9aef-fd5a0c513019 | – Joint Inspections
note | 66a26b63-0d3e-5c48-94d4-93cc42915f80 | – GRE Bonding Joint Record Form
note | fa1782ea-204f-5d5e-b4b4-93018f62be9f | – Flange Record Sheet
button | 9b008a47-6087-5db9-84bb-2b399b318c99 | Acceptance | Yes,No,N/A
note | 594d641b-f31f-53d2-9650-4887a27fdc83 | Key - H
note | 72732447-ad9c-5613-9abc-7a3344f4ea3f | MDR/VIVA - H
note | fe18d6be-516e-55cd-8164-bbfd7b7fb75d | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 71a52ff0-e8af-5f42-b8a2-e22fbdf19b9d | Test Pack
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 4.2 - Hydrostatic Testing
note | 377786da-0344-56ed-ae85-34d86deb3eff | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 13.2
note | 3f8e3e78-d038-5d16-8891-a41a6d3be94d | ○ SUN_ENG_P RO_010 R0 GRE Hydrotesting procedure
note | 175a3580-8587-54d9-b551-621f8f9fac8c | Acceptance criteria - Has the pipework been tested as per the manufacturer’s specification for the required duration?
note | ad4363f6-0a97-58ab-8bb3-b84209370b72 | Integrity Test
note | 4d8896da-f11c-5d62-b634-f9b2deb7288a | ○ 2-hour test –1.5 x design pressure for 2 hour hold (Refer to Hold Point in Subcontactor ITP below). Visual Inspection required of joints upon completion.
note | 6572c86f-e9b9-542a-992e-5072b69ab849 | Leak Test
note | f860c02e-2245-53ce-bb0f-17bd2c97f9f6 | ○ 1.1x design pressure.
tickbox | 189b96c2-4484-5e24-a500-0822a6c0c2a6 | 2-hour test – Visual Inspection required of joints upon completion to verify no leaks.
note | 99b677ce-3a69-5618-9cb3-8d950b6accad | ○ Has the pipework passed the testing requirements with no leaks?
note | 3c19647f-14c1-54e8-8424-e903ef5c1f99 | ○ If no, proceed to item 4.2.
button | e2e2f63b-f74b-5a15-9eee-308e9e06edd7 | Acceptance | Yes,No,N/A
note | 6f821ff9-9060-5765-ab6f-560a9fba9052 | Key - H
note | 6e86834a-8065-5c43-a7d6-05be3b28e5df | MDR/VIVA - H
note | 316e3ad5-587e-59f0-ab2e-d6e82b29dad5 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | b9d2fc37-606a-5c5b-905a-abc5b048c9b7 | QF-129-01 – Hydrostatic Test Log Sheet
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 4.3 - Repair
note | 76ebf9bc-9f0c-5353-97b6-81e62e150b3d | Ref docs - SUN_ENG_P RO_012 Re-condition of Adhesive Bonding Socket - Joint repair
note | 4982ab20-9b71-511e-9fcf-8bfa8f129a95 | Acceptance criteria - Has the leak been identified?
note | ddb97047-c6f4-5989-b4e6-6d4ad2e63cf4 | ○ Has the leak been repaired as per the manufacturer’s specification/approved methodology?
note | ab4bcf9b-2a34-5864-9dda-0b49b0a58063 | ○ Has the pipework passed subsequent testing requirements?
button | bc56fd7c-f5fc-5a1c-a2ad-8f6169dc4193 | Acceptance | Yes,No,N/A
note | 47ba2257-e7b2-55d3-9318-726f18079f40 | Key - H
note | a4976d72-cb61-5eb1-bda6-83420e623f3b | MDR/VIVA - H
signoff |  | AUTHORITY HOLDPOINT
section |  | 5.0 Backfill
checkpoint |  | 5.1 - Sand Backfill
note | c73ab87a-ddf7-53c1-9bcd-9b7a6328c7f7 | Ref docs - 239529-MG1668-15740-0400-SD-000010-NOV Bondstrand pipe installation guide - GRE
note | 37bd37a6-3cca-5f49-9e40-8152b6cd09fb | Acceptance criteria - Has Sand Back fill been placed to 300mm above Pipe?
note | 52c71583-3096-5df8-968a-cd4929f34c93 | ○ No compaction equipment to be used until 300mm above pipe.
button | cf90d740-9af1-5b79-8f95-37f85efb4662 | Acceptance | Yes,No,N/A
note | 73ab7897-12ca-5d7a-9e13-1e3cc0df075e | Key - S
note | 4a6cc8a8-0e9a-5bad-92e6-94065a7f614e | MDR/VIVA - S
checkpoint |  | 5.2 - Select Fill Backfill
note | e91066dc-0e6c-5b32-8276-c12854580abc | Ref docs - 239529- MG1668-15740-0400-SD-000010-NOV Bondstrand pipe installation guide - GRE
note | 5a994ac1-8485-565a-af1e-6dee59842d6e | ○ 235929-000- CV-SP- 00002 – Earthworks
note | 425834b3-f996-5194-b8ff-7a9e2c56ffbe | Acceptance criteria - Has select backfill been placed in layers not exceeding 150mm loose thickness?
note | 1206039d-ad40-50fe-82eb-dacb2d265088 | ○ No compaction equipment has been used between 0-300mm above top of pipe, light compaction equipment has only been used from 300-600mm above pipe.
button | 8cf2ea21-09f4-5b4d-888e-b8681c961a36 | Acceptance | Yes,No,N/A
checkpoint |  | 5.3 - Compaction Testing
note | b8c3c111-55dd-5f8b-b0bf-9c40019ff2c1 | Ref docs - 235929-000- CV-SP- 00002 – Specification for Earthworks
note | cce24e23-ed0f-543e-8737-69745b54ced2 | Acceptance criteria - Sand Fill - not less than 90% of maximum density or 70% of relative density, except that under paved areas the entire depth shall be compacted in 150mm layers to not less than 95% of maximum density or 80% relative density
note | f05cbe95-f09e-501a-9b58-cab4516c9116 | ○ Select Fill - Backfill under pavements shall be compacted to a dry density ratio of no less than 98% modified comp active effort.
note | 979d99c5-d0c6-57df-9e61-69b0d4ceaa25 | ○ Testing Frequency: Minimum 2 field density tests for each 185 m2 of each compacted fill layer, but no less than 3 tests for total area
button | 2d893ed4-9f1a-558e-b36c-d9c3abd5c61b | Acceptance | Yes,No,N/A
note | a9038a37-5466-5ad8-9d01-42daedc1b920 | Key - W
note | 97e07f3c-cad4-5768-a95a-4170bd1b5a21 | MDR/VIVA - S
note | 6b97d6dd-7c8d-503d-85a4-ede8245822e7 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | e623dfe5-be91-5fff-ab70-3b9655ae2815 | Geotechnical Test Report
section |  | 5.0 Documentation Submission
checkpoint |  | 5.1 - Subcontractor ITP
note | 4fbaa0db-e332-57d3-b0f9-d61e4069d772 | Acceptance criteria - Has the subcontractor ITP been signed off and accepted by relevant parties?
button | f2826119-88c4-5752-87e8-e9589ef4dcac | Acceptance | Yes,No,N/A
note | 4a5daf6f-e66f-596a-866d-7e3d078b8bd0 | Key - W
note | 23ffdd2c-1a5c-500c-9d7e-bb535b963b4e | MDR/VIVA - W
note | 0e078a37-2b29-5edb-bc64-6eec0d5b6636 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 5f7bb4d0-975c-5f3b-b789-fe4f6a6012fe | ITP_SUN_23_ 003
checklist |  | INF-HSEQ CC0398-ITP-033 HDPE Installation Rev C | itp | INF-HSEQ CC0398-ITP-033 HDPE Installation Rev C |  | 8b6fa8ca-e145-4ec9-bf05-10b77b725a76
section |  | 1.0 Preliminaries
checkpoint |  | 1.1 - Set out
note | a6292148-9ef9-576b-876a-6a3228c3a892 | Ref docs - Isometric Drawings
note | 30d49bf9-bf87-555a-9142-cfb638dd1a3d | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
note | 777af535-d73e-522d-bad5-d1342c920d44 | ○ IFC and latest available revision used?
button | baaa4dce-60f0-5bda-bb77-1d18b5fbbbcb | Acceptance | Yes,No,N/A
note | 69525a4b-a83f-5dba-96ec-4dd2ce98e8d5 | Key - H
note | 75fc77d5-10df-514f-9046-8ff43be314e6 | MDR/VIVA - W
checkpoint |  | 1.2 - IFC Submission & Approval
note | dec92c87-4a17-5301-85e3-96ad48b33c3a | Ref docs - Isometric Drawings
note | aa5aff82-7327-5e54-b1ee-405d91f53eb3 | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
button | 5ea8d45b-c757-5bcd-867e-9e31a28d2dfc | Acceptance | Yes,No,N/A
note | 10aa048a-4a2b-5e36-8120-c71c41325150 | Key - H
note | 8b1beac1-ee1f-50da-b3a5-c32620ad7149 | MDR/VIVA - H
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 1.3 - Permits
note | 75044550-e011-5827-934e-1047e5295b04 | Ref docs - Symal Safety Procedure
note | 2f53dfb8-b636-5870-a70c-ddaa2e203e1f | Acceptance criteria - Have the below permits been created.
note | ee7b79b7-a422-58c3-ae16-3b4825f0da40 | – GPP
note | cbd7de83-1cfa-588c-925b-50faef882311 | – Working at Heights
note | c565a92e-678e-50c4-9a80-77ba93f14ced | – Hot Works
note | 37da19c8-f2c7-5560-8e2e-85056d504ae6 | – Confined Space
button | 2e83ef1d-c52e-57ac-9753-61d3bb87797d | Acceptance | Yes,No,N/A
note | 998714d0-37b6-5647-9e40-20ece287f20f | Key - H
note | c72ad560-228d-5162-974b-ed1b850f30c6 | MDR/VIVA - W
checkpoint |  | 1.4 - Determine Lot Size
note | 95bc59c1-84dc-5ac5-b099-f966678d4f4b | Acceptance criteria - What is the lot size?
button | ca144e43-02b3-51ff-b28a-0a6b2f95dd4a | Acceptance | Yes,No,N/A
note | fb350a70-f360-5d3c-b8b8-9679832e847c | Key - S
note | 8ffc48aa-2647-5c8b-ad40-bd4bfd8d7523 | MDR/VIVA - W
checkpoint |  | 1.5 - Free Issue Materials
note | 8cb1dd15-6c3a-538d-afa5-365a76ed69ec | Acceptance criteria - Have the free issue materials been accepted and checklist completed?
note | c317e274-bbb9-577f-86dc-67da2bc6e603 | ○ Have the materials and tag numbers/heat numbers been verified?
button | f9c138c1-88ab-50f2-a936-d57f53842991 | Acceptance | Yes,No,N/A
note | 093b0a88-d19a-59b6-adf4-5bf09988dfce | Key - W
note | 9bb19453-1ccf-564b-94f3-4cf0fc2c8209 | MDR/VIVA - W
note | 67fcb396-d200-5540-ac10-f27f98454743 | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
tickbox | 8ad617d5-1986-5509-84f0-9f17579cffd3 | Material Inspection Checklist
checkpoint |  | 1.6 - Welding Pre-Qualification
note | 2bf4c607-8896-58fd-acaa-5801629b057c | Ref docs - Welder Qualifications and tickets. This ITP.
note | 5fea360f-1e5a-5a47-ac70-0b5be4cc8390 | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
button | ac4d6a55-642e-53ff-82bf-cb39707a4b99 | Acceptance | Yes,No,N/A
note | 747ef420-5030-5a42-bd0e-516be4110254 | Key - H
note | 17c5f370-36aa-56b8-99ea-d2c2feb6836c | MDR/VIVA - H
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 1.7 - Bedding and Backfill Materials Approval
note | c0a6fb32-ddb1-5920-a2b1-f3516f94df7b | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8
note | 4809543e-a02c-554b-89b6-6acf92f3d9d2 | Acceptance criteria - Has bedding and backfill materials been approved for use?
button | 84aa6386-810f-5d2d-9bb1-87e4326e754d | Acceptance | Yes,No,N/A
note | 08f5bcb6-89d6-59ce-b4c7-8a1a27b30d97 | Key - H
note | 2fbac27b-b6a9-5d80-adcf-37f5b7c5bcc9 | MDR/VIVA - H
signoff |  | AUTHORITY HOLDPOINT
section |  | 2.0 Excavation and bedding
checkpoint |  | 2.1 - Service Location
note | 5dd1271f-23b8-57bf-b446-9814b79b0d35 | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
note | d6f50350-0a38-56fa-8ba9-2f88f5bc559a | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
button | 50020be2-4d60-5d34-af90-12534be4650a | Acceptance | Yes,No,N/A
note | 06e33099-3b99-5515-b2ff-33bc3bde8db8 | Key - H
note | 8b080e68-d17c-585e-b428-a14b0b5581ba | MDR/VIVA - S
checkpoint |  | 2.2 - Excavation
note | 801990cc-3d8f-59f9-b825-f3869fc6a830 | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.12
note | f09d4ed9-97f1-5213-8001-c610012d5571 | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth of 100mm.
note | 80567725-2c70-564e-aa8b-74b8e8aeff10 | ○ Minimum trench width as per manufacture specifications pg. 17 is 1.25 x OD + 300mm.
note | 2027e1e2-2bd3-50c6-a6ba-07fc74ba4ef1 | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
button | febf78d5-0a75-5b94-9d54-5db964304530 | Acceptance | Yes,No,N/A
note | d972d095-782b-5e8d-98c3-b8c23a12ae2a | Key - W
note | 67b8223a-7f02-56a3-8264-df70c1327889 | MDR/VIVA - S
checkpoint |  | 2.3 - Bedding material
note | b7189e56-3b2b-5ee4-b19b-14767440222f | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8
note | 095e3a5d-62ff-5ad4-90b6-0e52cf25ea14 | Acceptance criteria - Has the bedding material been installed as per the manufacturer’s specification?
note | d80a253f-5c86-56bd-8687-46da61181271 | ○ Conforms IFC drawing (if applicable)? Bedding depth minimum 100mm Overlay depth minimum 300mm.
button | 8119dad3-bb9b-5890-bb41-bc909f1a03f4 | Acceptance | Yes,No,N/A
note | 11eaa216-7440-5906-83fe-91890f345c6e | Key - S
note | c3d230db-b83b-51d3-84bf-0d5de65b2fef | MDR/VIVA - S
note | 353e2ab0-a278-5b21-8afb-d3ccabcea2b4 | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
tickbox | 97102a25-7ae9-5a93-867e-2d4d0b33cfd0 | Delivery Dockets
section |  | 3.0 Welding, Laying & Backfill
checkpoint |  | 3.1 - Above ground fabrication
note | 13e70ec3-9f05-5cde-8787-47f36f06e782 | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL, PIPA- POP014- Assessment- of- Polyethylene- Welds-Issue- 1.1 ISO-21307 PWS-WP-01 Butt Fusion Procedure
note | 044f2efa-8f96-553e-9ae2-b8a6e36e076f | Acceptance criteria - Have the lengths been welded as per the manufacturers spec and welding duration?
note | 792d69d2-a93a-5a76-9305-88d79ed00a0c | ○ Has the welding procedure in the reference documents been adhered to?
button | f1c179ac-91ca-5acf-951d-01e92be43848 | Acceptance | Yes,No,N/A
note | 8e2ac93d-dc16-5e31-a1e9-d8fd817a46cc | Key - W
note | 507a1234-5cb6-5d1a-8d8d-f5949b4e5bef | MDR/VIVA - S
note | 36a93b90-1638-597b-86c6-d05d48b7ac6a | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
tickbox | 5ad5572a-0763-54d9-a4ab-27d014293ad5 | Welding Checklist
checkpoint |  | 3.2 - Lifting into trench
note | 927b8a00-fbf3-5eaf-8885-bb34f958d942 | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.2.1 Item 12.2.7
note | a3d8b46d-b20b-5512-bdc8-f12156f44842 | Acceptance criteria - Before lowering in, caps shall be placed on open ends, flanges, etc., which shall remain in place until piping connection can be made. Particular attention shall be given to the need to protect pipes from damage due to loads from heavy plant, has this been completed?
note | 1accccc6-7ea0-50fb-b458-153b63e6841d | ○ Have pipes been laid to true line and level?
note | 904741bc-6a1b-5318-af63-3f471fa507d1 | ○ Has MDR been notified before the laying of pipework?
button | d62cec42-0de8-580f-8d6e-50d469b4018a | Acceptance | Yes,No,N/A
note | 7cbbe5ca-33e6-5f19-9957-212222bd1bfe | Key - W
note | 1126f779-e6bb-5990-b1bd-d8f7684f6c79 | MDR/VIVA - S
note | c12b6519-cf09-56eb-b367-95b785ecbf11 | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
tickbox | 3f7fe797-bc43-5e76-81a0-e7ca1039ce51 | Survey compliance report
checkpoint |  | 3.3 - In ground fabrication
note | 591ddb6f-e93f-54de-9eb3-179ff7d1a52a | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL, PIPA- POP014- Assessment- of- Polyethylene-Welds-Issue- 1.1 ISO-21307
note | 5f0e4d86-1969-5f27-b671-9a7f2192165e | Acceptance criteria - Are the EF couplings if required sitting outside of the ground of the trench as to ensure that water can’t enter the coupling?
note | 961276a7-50dd-5f15-a812-dc9bfae1be38 | ○ Have the welds been welded for the appropriate amount time?
button | aec4b034-ff4d-5531-b124-4d9ae48281d8 | Acceptance | Yes,No,N/A
note | 4917ec55-1396-50d4-b79b-c308a73ae303 | Key - W
note | acf00bce-1e19-5184-8822-0554dcfeb02f | MDR/VIVA - S
note | 865341f0-4693-5d82-99c3-504049e0f458 | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
tickbox | dffaebd4-3d7e-5581-9774-0ad92cc3322a | Welding Checklist
checkpoint |  | 3.4 - Haunching
note | 3ddf224c-a27c-5800-87ea-107b764ab78f | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
note | 1796658e-948c-5f28-ae59-df5a5cab6238 | Acceptance criteria - Has the backfill material shall be approved soil without large stones, organic matter or substances which may cause damage to the piping?
button | e72688b0-3e7e-56d7-9d8f-160c3606b1b0 | Acceptance | Yes,No,N/A
note | 28735f09-b4b7-5cef-afbe-615496c8ff64 | Key - W
note | e6087daf-51f2-55b6-9831-1d9f03c015f9 | MDR/VIVA - S
checkpoint |  | 3.5 - Back fill
note | 1ea0ec76-0e8f-5779-a9a2-a9e0af7424d8 | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
note | 7003f0aa-cc27-5e8d-ae29-195677c96071 | Acceptance criteria - Has Sand Back fill been placed to 300mm above Pipe?
note | 6337ae5d-cea5-55fb-9853-88883afdcbdc | ○ No compaction equipment to be used until 300mm above pipe.
note | 24fce5f4-70c5-5b13-9fc6-35346599ae9e | ○ Has select backfill been placed in layers not exceeding 150mm loose thickness?
note | 624262a4-c8ca-518b-aff9-32bdd7f9493b | ○ No compaction equipment has been used between 0-300mm above top of pipe, light compaction equipment has only been used from 300-600mm. above pipe.
note | 6a27772f-bfdd-55fe-a79c-e24ba8224043 | ○ Note: Backfill around joints/welds can not commence until testing has been completed.
button | f50ffb4f-d297-55bb-9c9a-9a35d82bdea7 | Acceptance | Yes,No,N/A
note | cfe7c527-e468-553a-a1ed-7cf28ad659f2 | Key - W
note | 93fa47ff-08a9-5940-a3d3-1c3853e81de4 | MDR/VIVA - S
checkpoint |  | 3.6 - Compaction
note | 4b82d837-137c-5c1b-8ea3-f83f1e287d12 | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
note | 01d655e2-7d8e-5d74-af47-858ce5275e08 | Acceptance criteria - Sand Fill - not less than 90% of maximum density or 70% of relative density, except that under paved areas the entire depth shall be compacted in 150mm layers to not less than 95% of maximum density or 80% relative density.
note | 1ca12511-58cc-521d-ae03-fb70045a30d3 | ○ Select Fill - Backfill under pavements shall be compacted to a dry density ratio of no less than 98% modified comp active effort.
note | 8e8b0f3f-eb4c-5053-8da5-079bb7499378 | ○ Backfill to be in 250mm compacted layers.
note | 7d7135b6-8e3b-5d78-9b8e-44820056eb82 | ○ Testing Frequency: Minimum 2 field density tests for each 185 m2 of each compacted fill layer, but no less than 3 tests for total area
note | 469f0599-3475-5556-adcc-0d41e3ac84ec | ○ Has compaction testing been completed as per the project specifications?
button | 8b69cb19-e15c-583b-8722-4517438d0306 | Acceptance | Yes,No,N/A
note | 33039fd4-02dd-55c0-84d1-ea9e3da26f3e | Key - W
note | 2c3a4d13-0a05-5970-957e-f8008aa9535f | MDR/VIVA - S
section |  | 4.0 Testing and Conformance Check
checkpoint |  | 4.1 - Test Pack
note | 30824e05-debf-5e60-938c-814660902142 | Acceptance criteria - Has a test pack been provided prior to testing? Test pack to include.
note | 62d6e9c7-7edd-5e39-91d1-fc5adfaf7bbd | – Test Procedure
note | 51ff042f-0a29-516b-bcf6-a1bea87e067b | – Test Map
note | e16b36d9-23da-57f4-b0ff-0d4f1b56fdfb | – Equipment Calibration
note | 6effca6d-f44b-5dbe-9d15-f98a2b356981 | – Equipment Details
note | dbf4d63d-2f04-535b-a028-9bc3d3cfcb1d | – Exclusion zones if require
note | 9bc90446-ae4b-5fb9-beee-22a23970a7e4 | – Provision of testing log template
button | 6d862293-e7f6-5770-a4d7-0069725300db | Acceptance | Yes,No,N/A
note | 89b277c1-8107-565a-ba0b-69e78baaf697 | Key - H
note | d17ac13b-2345-53a7-a6c1-d2f221e03e52 | MDR/VIVA - H
note | d15978e7-8139-5df6-b186-a2bac1948c7a | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
tickbox | d383484b-be8b-5400-92e7-03dd49eebfbe | Testing Log
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 4.2 - Hydrostatic Testing
note | 44710851-cffb-5d14-b9b0-9f29ef3f9e3e | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 13.2
note | a0485ed1-30e6-5734-a709-df1f41ee1dec | Acceptance criteria - Is the line a Pressurised Line? If yes refer to the below.
note | cd84b084-1c51-53dc-a0bc-234165d27e48 | ○ Testing Equipment is calibrated within 12 months from a NATA certified laboratory.
note | c13307b6-59ef-53cf-a12f-1fe3d3302085 | ○ Has the pipework been tested at 30 bar for 2 hours specification for the required duration?
button | cddb09b1-3ca7-5c99-9025-8292c5b3b681 | Acceptance | Yes,No,N/A
note | dee9065c-451b-5918-b7e7-d0792a06db39 | Key - H
note | d835d3d0-1167-557e-a89a-e92057801461 | MDR/VIVA - H
note | 2cec035e-ae1d-53a1-9fdc-f8b46d6c7947 | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
tickbox | 3882ad51-6729-5921-8f45-c9c2c398b6cd | Testing Log
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 4.3 - Leak Testing or Air Testing
note | 4d4ac72e-dda0-5242-b72a-66a2238ec2d2 | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 13.3
note | c5387118-571d-5b2d-a99d-0fc7c603d618 | Acceptance criteria - Is the line an atmospheric line?
note | ca083e23-c85d-5562-9304-d449080f6ab5 | ○ Atmospheric lines to be “full of liquid” tested shall be filled with water for at least 24 hours before visible inspection of the complete test system by the inspection team, water level in the test system shall be checked and marked at the start of the test and rechecked after twenty-four (24) hours during visible inspection of the system.
note | 9720ce4f-c3d2-50a7-9155-574a990d5c9a | ○ Concrete Sumps or other material that will absorb water shall remain full of water for minimum 24 hours prior to test running.
note | 8a741547-20b9-5e48-b7ea-be6cb58c834c | ○ Note: Losses from seepage / absorption may not be higher than 0.5 l/m2 of wet surface during the first 6 hours.
button | a0d3eeb5-9464-5c4a-81ce-d4e148a8a63b | Acceptance | Yes,No,N/A
note | 5a65c9ee-2f8d-5b51-837f-828fca8a9b5c | Key - H
note | dbb88179-0c43-5119-81e0-77392dc1454c | MDR/VIVA - H
note | 6071cc12-29eb-5d08-bd83-2fae1dcead4c | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
tickbox | 0c34a150-6216-5fc9-ac47-a2eeb5f80264 | Testing Log
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 4.4 - Survey
note | e8246ccc-f6f9-580e-b9f1-83dfbe7d7a96 | Acceptance criteria - Tolerances in alignments shall be limited to +/- 25 mm vertically or horizontally, unless otherwise specified on engineering drawing, has this been completed?
note | c10007d5-d281-5d23-82a4-f7d2ef418539 | ○ As-built Drawings
button | 13ad40cf-4054-5ba2-b867-0b78ff1c4537 | Acceptance | Yes,No,N/A
note | 128a51a3-a63d-5f41-84f6-a12fff51e13d | Key - W
note | 12730de3-ec15-50db-84cc-7a9ea9a6e5d2 | MDR/VIVA - W
note | 335ce6f0-7253-5aa0-a55c-88937ee10211 | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) - As-built Survey
checklist |  | INF-HSEQ CC0398-ITP-014 Electrical Conduit Installation Rev 1 | itp | INF-HSEQ CC0398-ITP-014 Electrical Conduit Installation Rev 1 |  | aab78521-e30f-49c2-a8de-8871263e6974
section |  | 1.0 Pre-start activities
checkpoint |  | 1.1 - Set out
note | 1103763d-3203-5b23-8d01-7ffd83b0a3bf | Ref docs - Composite Drawings
note | baea0935-acee-50fa-991a-e11a977b35f9 | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
note | 6087ad65-65cc-5e9e-8e86-2eaead5e0733 | ○ IFC and latest available revision used?
button | bbd68c2b-9710-5c52-8ce0-cb0c63029af3 | Frequency | Yes,No,N/A
note | ddbaf7dd-4446-55b8-869b-1831c4fc0d8a | Key - H
note | 576eb695-05f7-5ed1-a4df-dc13949ef257 | MDR/VIVA - W
checkpoint |  | 1.2 - IFC Submission & Approval
note | d4692abf-369a-5619-8e85-3be78cb86c88 | Ref docs - Composite Drawings
note | b5eb0725-54e5-505d-83fd-72367add37c2 | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
button | 8d2f11fe-99b3-557b-83b3-69b4294b5844 | Frequency | Yes,No,N/A
note | d1dae0c1-7ece-5256-96ec-a1a0d04d8609 | Key - H
note | 65f3cb6c-dd47-5ac2-9460-887af1cdce4c | MDR/VIVA - H
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 1.3 - Permits
note | ad696d41-c65c-5ce8-8ece-f4f5be10c6c1 | Ref docs - Symal Safety Procedure
note | eea60ce2-aa64-57ba-a299-fffbfdc8497a | Acceptance criteria - Have the below permits been created.
note | a3f79c57-07ad-54a6-b9bd-4d465fe8d825 | – GPP
note | 8cf2c107-28df-57e9-8cc7-865548497cdf | – Working at Heights
note | ef2e6c7b-74ad-542f-bba0-b1fd577953ce | – Hot Works
note | d7d058b1-616e-5e83-ae75-b0c075cd0a50 | – Confined Space
button | 14a317f5-b194-566b-8893-48b60747d7b5 | Frequency | Yes,No,N/A
note | 1922f7ae-3740-560b-88ee-1cf481d53473 | Key - H
note | 90e0dc93-a46f-5faf-8324-1f8747af9aeb | MDR/VIVA - W
checkpoint |  | 1.4 - Determine Lot Size
note | fb6a004b-76cd-55f5-a879-3c19728e41db | Acceptance criteria - Has the lot size been determined?
button | 9cac09c7-ed59-5cc6-948c-035ae399718d | Frequency | Yes,No,N/A
note | a9f11d2c-2831-5478-aa3b-835284bab343 | Key - S
note | 9bfe7bc8-c769-52b1-b350-4d0682d6a73d | MDR/VIVA - W
note | 4433b698-0407-56e0-94a9-553a24170e4a | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | c879e416-8961-5fb7-81f3-3086b15aa863 | LOT map
checkpoint |  | 1.5 - Delivered materials
note | faf54236-bf17-5c9c-a510-0925830b1a92 | Acceptance criteria - Has a material inspection checklist been completed?
note | 0da7ccb4-206d-537d-af25-0c2b7a3e269b | ○ Have the materials and tag numbers/heat numbers been verified?
button | e62be9ca-0b60-5cd5-8f05-735f6416edc3 | Frequency | Yes,No,N/A
note | e6edf1da-c880-5e3b-b553-67678fc0d9ad | Key - W
note | 34cdbfd2-d246-5709-82a5-1fb8e99f76f0 | MDR/VIVA - W
note | 90041ad3-1bf4-575e-adc4-350ceee5d705 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | b6f14163-44a5-5040-8abf-f57cf1fb6c9e | Material Inspection Checklist
checkpoint |  | 1.6 - Electrical and Earthing Pre- Qualification
note | 4e44ed13-1d43-5efb-8001-db91cda60ad3 | Ref docs - 235929- MG1668-CV- 003-SUBC-000181
note | 7767152d-32f3-5dc5-8011-8c292c318565 | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
button | c291cbd7-5b65-5765-97b5-9b611aae21b8 | Frequency | Yes,No,N/A
note | 04e35efb-135b-5b11-9ed5-eec76864af9d | Key - H
note | 3fc5f82f-71b3-530c-8a7b-62d7d692cb74 | MDR/VIVA - H
note | 138ad1c9-5dd5-52c5-951a-f81dc3e74ac9 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 79f0886f-656c-58c5-abc5-0666f09fa285 | Welding Qualifications
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 1.7 - Backfill Materials Approval
note | ed8555be-45a3-50a2-b0c0-0755765d3883 | Ref docs - 235929- MG1668-CV-
note | de896422-a54d-5dca-8546-0c6b65bdc8f4 | Acceptance criteria - Has bedding and backfill materials been approved for use?
button | fa2501cb-52ba-5577-b3b4-d486a91c9ecc | Frequency | Yes,No,N/A
note | 96e32297-2c94-5e65-88e4-f23054fee8d9 | Key - H
note | c9c517ec-e7e8-562a-881b-df30cae436df | MDR/VIVA - H
note | 45b31951-de66-5cef-b62e-21fc18f50108 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
textbox | 8a3fae06-4d66-5e3f-81de-6659c5faba2f | Approval number:
signoff |  | AUTHORITY HOLDPOINT
section |  | 2.0 Excavation and Placement
checkpoint |  | 2.1 - Service Location
note | f5dd4e52-7676-56dc-b9ff-06870f1c849e | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
note | 40263034-5fbd-5409-8659-6cf0454dc093 | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
button | d1e4ac7a-2717-54ee-90b6-8b38d4e68d1c | Frequency | Yes,No,N/A
note | 7111c7ff-dd0e-5948-a47e-fdd5346a030e | Key - H
note | 6dfab305-5162-50c9-80a8-2e614eaa0b0e | MDR/VIVA - S
checkpoint |  | 2.2 - Excavation
note | 31705c26-3c76-51d4-8a98-bc5f6aa51a63 | Ref docs - 235929-000- CV-SP- 00006 UG PIPE FAB and INSTALL Section 12.1.12
note | 438574e2-88a0-5442-bae3-c2c2577c2701 | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth of 100mm.
note | 5144d833-8b0d-5231-8261-1992d3ad92d9 | ○ Trench width to provide 50mm from edge of trench to conduit walls at minimum.
note | cae4db40-c0c5-5a73-ad3e-2ce422ebd58f | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
button | 0328c583-c28c-5b0f-ad1c-be938bf463ff | Frequency | Yes,No,N/A
note | 399e6f67-d97a-59ce-9df0-58f24d8d6d3f | Key - W
note | 9e6e5f6b-d082-5be5-9657-a4887e84a36d | MDR/VIVA - S
checkpoint |  | 2.3 - Conduit materials and size
note | 8d0c329f-feb7-574e-b1e4-5b628989250b | Ref docs - 235929- MG1668-CV-003-SUBC-000112 (Shop Drawings)
note | 4ae8a4a8-1792-5daf-8a31-08dc850e991c | ○ 235929-MG1668-CV-003-SUBC-000009 (UG Services AMS)
note | 37dd0192-aac6-5ab7-9eb2-ed23bee3fcd9 | ○ 235929-154-CV-08-92002-080001 (Rev1) & 080002 (Rev1) & 080005 (Rev2)
note | cfce4612-afba-5425-bc55-a962e200c674 | Acceptance criteria - Are the HDPE conduits approved for use?
note | c34bc2d7-1e1c-5007-bcf4-7111c1c4ccb3 | ○ Have the conduits been installed using approved couplers?
note | 4bf91e3d-d1a9-588a-bf38-201b2edac232 | ○ Has the installation of the couplers been reviewed by the client?
note | 48eacfb7-7956-5465-a20e-0f077b222dcd | ○ Has the bend radii been checked and adheres to the drawing?
button | d24125a3-2ed0-5837-9e7a-fbaf9eb2a87e | Frequency | Yes,No,N/A
note | d9452e8c-4d05-5488-9cdb-9ed8278023a7 | Key - W
note | 4db4758f-38b4-53f0-8d38-f3e9de71b780 | MDR/VIVA - H
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 2.4 - Conduit placement
note | 8516ec96-4321-5c27-ace6-7fbae8b2707d | Ref docs - 235929-154- CV-08- 92002-080001 (Rev1) & 080002 (Rev1) & 080005 (Rev2)
note | 6bd7b8f1-c44e-5c55-bf0d-ce090a0cb0c1 | Acceptance criteria - Have the Conduits have been placed as per drawings and specifications and inspected by a VIVA representative?
button | e9a6b259-ee54-5deb-a49b-b6993bfc6230 | Frequency | Yes,No,N/A
note | 93518f9a-1822-509b-a093-1c08852405aa | Key - H
note | ea77579a-f49b-543e-8272-8b0806f7dd5f | MDR/VIVA - H
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 2.5 - Backfill placement & Marker Tape & Rope
note | 147710ae-de45-5278-9b99-f058fcb01461 | Ref docs - 235929-000- CV-SP- 00002
note | 1a98b052-1c04-5779-acce-5710fb75c752 | Acceptance criteria -
button | 7fd662e6-da04-5ecd-8a78-35c76b49dbff | ○ Have all trenching works been recorded for as- built and digital data prior to backfilling? | Yes,No
button | bb11efe4-a379-57c2-9aea-54121f10378d | ○ Has bedding material/sand been placed for the full width of the trench over the conduits for a minimum cover depth of 200mm? | Yes,No
button | 83b09002-499e-575a-ba91-125d4c312726 | ○ Has marker tape been placed in-line and above the conduits on the surface of the sand layer? | Yes,No
button | 218a9bea-0d4c-537b-a384-d855b5e2c270 | ○ Has draw rope been installed through the conduit? | Yes,No
button | 5de0e56c-9cff-5303-a686-f5668c8ade0f | Frequency | Yes,No,N/A
note | 1f396bba-c341-536e-9c87-706ef810b30d | Key - W
note | a823cb7f-dcff-52f1-b558-66bf3cdf8538 | MDR/VIVA - R
note | b0d39732-d08d-57e4-8444-293ec10fffe1 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 0b91bb22-a9d0-59c3-b72d-6fdfbe4945ad | Photos
section |  | 3.0 Finishing
checkpoint |  | 3.1 - Clean-up of site
button | 6b81d36d-7ca2-5aa7-8f93-cfd3c837ff8a | Acceptance criteria - Have the areas affected by the works been restored to a condition similar to that which existed prior to the commencement of the work? | Yes,No
button | 319ebba0-564c-5502-a165-36e704ddb325 | Frequency | Yes,No,N/A
note | a3f7764f-b495-5837-86ba-119170beadd4 | Key - S
note | 5a6f278d-58a9-56cc-a207-402d379dc048 | MDR/VIVA - S
checkpoint |  | 3.2 - Identification and recording
button | 40871e02-7778-53f0-9565-4394a5f03baa | Acceptance criteria - Have the actual installed location and depth of the conduits, and location of pits, been accurately recorded on an as-built? | Yes,No
button | 9d421667-cb2b-55a4-939c-c5680e40e6dc | Frequency | Yes,No,N/A
note | 64b4cdf9-2523-56ae-b7c1-6facff86b4ac | Key - S
note | 62827790-ca8e-5df4-bfb9-24dfbc6eebad | MDR/VIVA - H
note | 9edaa3ec-4e81-5b63-b7f7-65ed012d4147 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | b791b950-b7df-52a5-982f-40f99a23a200 | As-built
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 3.3 - Work is complete and complies with design plans / drawings / specs
note | 4eb51d99-1e06-56ca-8683-abc147039ea0 | Acceptance criteria - Redline mark-ups As-Built Survey: Conduits to conform to the required depths and locations.
button | 6755acf2-cc83-5b9e-a4ea-ac001f1e36bc | Frequency | Yes,No,N/A
note | 6d1dfd6a-aac6-53a8-92cd-36344bce3c0a | Key - H
note | 7627c440-a603-5aa6-9eb6-1b2fc6950050 | MDR/VIVA - H
note | 6f58148e-825f-5a9e-a43d-38c6f0c855ef | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 89694bb5-8187-5a6e-9ba9-48e6e223b743 | As-built
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 3.4 - Certificate of electrical safety
note | b5568540-b843-5dff-9b6c-f1e3a6a038a3 | Acceptance criteria - Electrician to supply Certificate of electrical safety for conduit installation witnessed
button | 5f0a1fa8-5df5-54e6-b0ec-6e6992f5c869 | Frequency | Yes,No,N/A
note | 1073ef31-6b00-52e2-bbce-da3f4f345cb1 | Key - H
note | e72071bb-5764-581a-ba0f-08ed92ae0a45 | MDR/VIVA - H
note | 8d53235f-f828-5720-95c0-856d20016331 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Certificate of electrical safety
signoff |  | AUTHORITY HOLDPOINT
checklist |  | INF-HSEQ CC0398-ITP-003 Base Pavement Construction Rev B | itp | INF-HSEQ CC0398-ITP-003 Base Pavement Construction Rev B |  | c2d50d7f-6b8c-4b90-9a2a-f936795b5260
section |  | 1.0 Preliminaries
checkpoint |  | 1.1 - Determine lot size
note | 6501d8b1-cb43-5bdf-9dd5-67d2dba00fa2 | Ref docs - 235929-000-CV-SP-002
note | 8f839c3d-0f6f-57fd-ba40-2524e8f064c0 | Acceptance criteria - What is the lot size?
textbox | 5b2bd2ef-3e75-540d-8649-4edd104a0c67 | Acceptance |  |  | m2
note | cca7cbfa-c2a2-5d83-aafb-5efa18c67deb | Maximum lot size = 4000m2
note | 54c4c5c8-e11c-59fa-87eb-3fd3e9d0f909 | Key - S
note | 43d09c37-555c-5265-aaf5-711e3df335c7 | VIVA - S
note | 26acb492-9acd-5d06-9f7a-caaa1143b6cb | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 5f18f051-a676-5e3f-ba60-44534e570e48 | Lot Mark-Up
checkpoint |  | 1.2 - Survey set-out
note | e8633a6d-758b-59ef-888f-cfbd143e64c6 | Ref docs - IFC Drawings
note | 8aa7e653-16c3-56d5-a513-2a0363d44dbf | Acceptance criteria - Is the work area clearly pegged out for line and level?
button | 0cf98971-5246-5cfd-bb65-0aeee80bd42a | Acceptance | Yes,No,N/A
note | f05c6e9a-36fd-54f4-9394-97ae24b54482 | Key - W
note | 80487666-1cd6-59d5-9be7-ddf3c4831cbf | VIVA - S
checkpoint |  | 1.3 - Material classification and source
note | c8bdf585-db77-5229-bb64-061071d89421 | Ref docs - 235929-000-CV-SP-002
note | e7cdf885-173b-58de-9df0-d8f3b7831e41 | Acceptance criteria - Has the nominated materials been approved for use on the project?
button | de56d295-db70-5412-bccf-81f55a7a0d9e | Acceptance | Yes,No,N/A
note | 09c71a68-3758-568f-9a6d-6c9c77bb59ac | Key - H
note | da0fb1c6-15c0-5f0d-b6cd-10bfcd11bd24 | VIVA - H
note | 50b1f835-aba7-5703-b6c1-ad3b1bee2549 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 0b95c8ae-2a21-58f2-83fd-e8a8b36dcac9 | iDocs Approval Document
textbox | a0b6986c-2be2-535f-9125-dee4d5976015 | iDocs Number
signoff |  | AUTHORITY HOLDPOINT
section |  | 2.0 Conformance of previous layer
checkpoint |  | 2.1 - Conformance of previous layer
note | 81e0e4e3-8ddc-5612-87a0-8bea0288a50d | Acceptance criteria - Has the previous layer passed acceptance criteria?
button | b612900e-50a7-53c2-9c3e-25418ac21c1e | Acceptance | Yes,No,N/A
note | 20018853-84de-5729-a379-0079ffd0af5d | Key - H
note | 7189376a-d627-5626-ac23-398505e4b612 | VIVA - H
note | 69de0e78-36f8-56fa-8320-0efe083ebfcc | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 1dfb806b-055f-532e-a775-2f5f663def65 | ITP Number
signoff |  | AUTHORITY HOLDPOINT
checkpoint-no-value |  | Type of Pavement:
note | 92c74975-23d8-5dba-ac9b-cfbc0807f4fd | ○ For Crushed Rock Placement Below Concrete Pavement Refer to Section 3.0
note | bb8147f6-6b95-58d6-9639-45561ac2fbe2 | ○ For Crushed Rock Placement for Gravel Pavement Refer to Section 4.0
note | 6f7016fe-c9ef-5f8e-96f6-14ac56a767c4 | ○ If multiple pavement types exist please complete as applicable
note | fa1f7190-e811-5ac9-aa81-8394c776142d | ○ Please strikeout not applicable sections
section |  | 3.0 Crushed Rock Placement Below Concrete Paving
checkpoint |  | 3.1 - Placement
note | 01389caa-4b1a-5fa6-bc77-a97e7bfdaf7c | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | eedb55a1-590d-5c8e-bd12-a9b3399987a2 | Acceptance criteria - Has Class 2 Crushed Rock been placed to be a minimum of 250mm Thick as per IFC Drawings?
note | 49a7d8d8-0a74-59b1-a156-b8b99f0eca12 | ○ Crushed Rock Layers must not exceed 250mm thick lifts if additional Crushed Rock is required.
button | aa11b76c-a823-5d46-b72f-3ab49ffe384d | Acceptance | Yes,No,N/A
note | 13d22732-d375-567f-ae22-91ec50f1151b | Key - S
note | d33cfb8c-8769-50e6-b2c3-6b5e9d1a63ec | VIVA - S
checkpoint |  | 3.2 - Moisture
note | 35ca5b69-0a83-52dd-90db-9a5dd46b3dcf | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | d36c6c8c-68d5-5902-a3df-69c08681e1ac | Acceptance criteria - Has the material maintained at optimum moisture content (>85%), with additional water being added if required during compaction?
button | 56384fb5-6c00-5e73-9829-9bc53e2d806e | Acceptance | Yes,No,N/A
note | d9a60ee9-b6a9-5faf-94b2-132f3ffa344e | Key - S
note | dfbb937b-ae3c-5a8e-b34e-c057068ebd28 | VIVA - S
checkpoint |  | 3.3 - Compaction
note | 6f254900-fcbe-5d4b-8fd3-ef732cce8350 | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | b13d3546-2115-5f3d-a10f-5ad32e2d15eb | Acceptance criteria - Compaction Testing is to be completed at 3 tests per lot to the below requirements:
note | 9e51b6f7-df24-5291-853d-8e637d5708dd | ○ 98% MDD
note | 777dfafa-dd95-5ab7-84cf-43a2ea10dcb4 | ○ +-3% of Modified Moisture Content
note | d4759b59-4e66-559e-8bf6-e84562d8c480 | – If testing of the first 3 consecutive lots have achieved the above requirements testing is to be reduced to testing per 2 lots until such time that a lot fails to meet the specified requirements.
button | fc38b74e-a939-5072-bb4d-f2930e7803e7 | Acceptance | Yes,No,N/A
note | 3caeb15a-4034-5a12-9768-059f494dea8f | Key - H
note | cc0b4ae2-f2cb-50c8-9a1f-3885365cab1b | VIVA - S
note | 15b9e5e0-0d48-574a-8e61-7d86ed4b494d | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | ced06147-f3a9-5f5e-8a88-a800e350c339 | Compaction test reports
checkpoint |  | 3.5 - Test rolling
note | 8417ed8f-2d33-52ef-a780-bd97adf43f18 | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | a8f60c05-766d-5571-addc-cbcb1fc24664 | Acceptance criteria - Does the layer withstand test rolling without visible deformation?
textbox | e3bad8fa-53d1-560a-af29-9e43dcc80a08 | List attendees:
button | 96a4c8b6-a202-5e3e-a455-8cf8a1489620 | Acceptance | Yes,No,N/A
note | 9121f4ae-077d-5192-9de9-8264c6fc4043 | If ‘no’ please see below
note | 60e4dcc6-7e37-5a9a-8641-39b5671cd033 | If ‘yes’ please proceed
note | dd985b01-e537-5220-bc7c-0a7c3b8bebe5 | Key - H
note | f612c7e6-fcca-5810-a8f0-6ec9ace8f618 | VIVA - W
note | 3d64c171-4402-579f-80a6-972f4c57472a | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 823e135f-1efe-55b0-add1-ccb87dbe91b1 | Proof Roll Sheet
checkpoint |  | 3.6 - Identification of soft wet or unstable material
note | 97ec0340-9dee-5e5e-b847-719c46b8fabb | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | bb6b736c-dcf1-52ac-8f40-6f3784b729f9 | Acceptance criteria - What quantity of soft, wet or unstable material is present?
button | 9d156093-5a40-585f-813e-1c1b080e35b6 | Acceptance | Yes,No,N/A
textbox | e576fcb6-bb54-5c0f-8724-31107bfd1a20
note | 4cde47f5-e32c-561b-b519-d786462843ab | Key - H
note | 711c6f8c-97d8-5f7f-aed0-21b69f7e8ea8 | VIVA - W
checkpoint |  | 3.7 - Treatment of unsuitable material
note | 7cee4b29-d1cb-58e1-8c35-56348ddcbb6c | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | 99bdd0a0-8ccf-522e-94f1-0e32eeec3810 | Acceptance criteria - Has the nominated soft/wet spot been rectified by a remove and replace method?
button | 64a62daa-c37e-54dd-b280-2dd59e017376 | Acceptance | Yes,No,N/A
note | 45041a27-b536-5253-abd1-fa5e6a8ccc1e | Key - H
note | ac86a90b-0949-513b-8285-c65a5a3f4e25 | VIVA - W
checkpoint |  | 3.8 - Placement of Polythene Membrane
note | d828a38b-e40c-5ade-94aa-c9a127b199e4 | Ref docs - IFC Drawings
note | c5623489-4e10-5d5e-abbc-4fd16d806e60 | Acceptance criteria - Has the Polythene Membrane been installed above the completed Crushed Rock layer?
button | cf22dba4-bc72-5cf7-b78c-84e43e394556 | Acceptance | Yes,No,N/A
note | 7ba0d442-51ce-5efd-8ef4-30b7ca7ed19d | Key - S
note | e4125fc3-a679-5ef3-aa19-0754b7f8a6c9 | VIVA - S
section |  | 4.0 Crushed Rock Paving
checkpoint |  | 4.1 - Placement of Geogrid
note | 0dfc6fcf-b3d8-54cb-be50-3a61746a69f7 | Ref docs - IFC Drawings
note | 6f887263-f3e7-51de-b4bc-4c53f829ef5d | Acceptance criteria - Has Geogrid been installed where non-paved areas have been excavated?
button | 6add77c9-adf0-5e59-8097-b90ed6bf983e | Acceptance | Yes,No,N/A
note | e9c174ad-573b-5fa3-84ff-93dea5f41103 | Key - W
note | b1571a35-8fd3-55ca-8946-26ccf49e833f | VIVA - S
note | 0de21b6f-e82a-575c-aefb-940a38bbfcfa | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | f3ff3c71-43a1-54e0-8bdb-05d75404f2e3 | Material Approval
checkpoint |  | 4.2 - Placement of Crushed Rock
note | a903b078-bc18-51df-b13c-98e9eaabc123 | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | d72fa877-9882-5c97-bf6e-e26e10174d14 | Acceptance criteria - Has 20mm Class 3 Crushed Rock been placed to be 400mm thick?
note | 853dda95-b172-5def-a1dc-8a3763e8c205 | ○ Crushed Rock Layers must not exceed 250mm thick
button | 5a401019-1e96-5ec9-af57-9ee3a4591000 | Acceptance | Yes,No,N/A
note | cd392d81-4008-5da9-9916-cc3bdabb4f79 | Key - S
note | fa358042-4cbf-5c10-91c1-e7292a11b583 | VIVA - S
checkpoint |  | 4.3 - Moisture
note | 2331b14f-f1d0-57ed-870e-6dbaa9f9ee1a | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | 43495157-14fb-57dd-940e-3c1945e4c980 | Acceptance criteria - Has the material maintained at optimum moisture content (>85%), with additional water being added if required during compaction?
button | 6ec08d96-7bff-5e62-9518-0224f15059c6 | Acceptance | Yes,No,N/A
note | 6c99e8bd-c06d-578b-be29-711ddc8e0327 | Key - S
note | 156e0296-e4be-5c66-b962-6dbc51d53533 | VIVA - S
checkpoint |  | 4.4 - Compaction
note | 429d6bce-33c6-59a5-8d64-2ad478c6f108 | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | d3209243-9c30-5573-a1c7-30fafcce5b85 | Acceptance criteria - Compaction Testing is to be completed at 3 tests per lot to the below requirements:
note | 89d3e070-4413-528d-a4ab-06f872de98b9 | ○ 100% Standard Compaction
note | 7d6e1f91-a934-5645-955d-5a669e035a9e | ○ +-3% of Modified Moisture Content
note | cae85642-5db5-5937-8890-cff42144a5c2 | If testing of the first 3 consecutive lots have achieved the above requirements testing is to be reduced to testing per 2 lots until such time that a lot fails to meet the specified requirements.
button | 077a6c37-c1ca-518a-a2fe-3f5d83345928 | Acceptance | Yes,No,N/A
note | bbc07bbe-5011-5668-b581-002833c721dc | Key - H
note | 5e43bae2-a18c-5b73-802c-99b64fe06a10 | VIVA - S
note | 31de37d4-20c8-5b82-ac43-255a2389f771 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 2ab9353d-83ac-5c89-8b8b-fff09aebef9c | Compaction test reports
checkpoint |  | 4.5 - Test rolling
note | 97553362-56f8-5ff2-96e9-adceb75265b9 | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | e2b50d78-d3a3-5c10-8da2-5bbaef359853 | Acceptance criteria - Does the layer withstand test rolling without visible deformation?
textbox | 73e1ee2b-08c7-59b8-8150-983da127d3d2 | List attendees:
button | 9ed16321-b204-5483-84c0-64512d1e5bb4 | Acceptance | Yes,No,N/A
note | d94bbfa0-63bf-5cb6-84b5-b96884759f4e | If ‘no’ please see below
note | 99f6596e-bfaa-57ed-976b-bf8607a2d7da | If ‘yes’ please proceed
note | b404bfbf-5950-599a-85c1-593556c3903a | Key - H
note | 92ec5bda-49ea-54a3-997a-d6a6a08fec5c | VIVA - W
note | b44fcef6-f2ee-5175-8a9e-11575b2a3639 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 88894f45-536d-5d61-9345-5e915faf41f9 | Proof Roll Sheet
checkpoint |  | 4.6 - Identification of soft wet or unstable material
note | d9af96d1-8e5a-5322-b353-453a3f02f9b6 | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | 49f6f314-8b5e-5f7f-a09d-2ea51e17b811 | Acceptance criteria - What quantity of soft, wet or unstable material is present?
textbox | 57d94117-c5d9-5bab-9a31-aedeb125c5ff | Acceptance |  |  | m2
note | 2dc07789-628d-5968-8330-be11e9005f8e | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 14f24b55-a5a3-5dec-bcae-aeeaa06a36b3 | Photos
checkpoint |  | 4.7 - Treatment of unsuitable material
note | 7e103013-e4ba-5867-b406-eb6bdcf54080 | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | 8b850234-8a5d-5309-94cb-d3464137601c | Acceptance criteria - Has the nominated soft/wet spot been rectified by a remove and replace method?
button | cd5e9e8a-b263-5276-817a-74fadbaa2bd3 | Acceptance | Yes,No,N/A
note | e0c726a2-a991-5162-a318-691e492d7a7e | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | e99da963-0e22-5ffe-b518-56c61c6bc0b1 | Proof Roll Sheet
section |  | 5.0 Conformance check
checkpoint |  | 5.1 - Pavement finish
note | e3602dc3-74e4-5984-a2d1-dc831e4cf811 | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | 5ae04c9c-9fe2-5dab-9a1f-ccbd33dd9cbf | Acceptance criteria - Has the crushed rock layer been finished to a smooth and uniform surface?
button | cc0f4e16-2509-583f-9afe-298f60b0c4e7 | Acceptance | Yes,No,N/A
note | 2717a8ab-24fb-5764-8c65-53db17151273 | Key - W
checkpoint |  | 5.2 - Surface level of pavement courses
note | 053d23a8-26a5-5bff-87cd-6177a5936e8f | Ref docs - IFC Drawings 235929-000-CV-SP-002
note | 52c172d6-67d7-5bb0-95e7-f4602e1d0206 | Acceptance criteria - Has the prepared layer been surveyed in accordance with and verifying specified requirements?
note | b56f3ef5-c7f8-51f5-8117-6ae41b140ee4 | ○ Tolerance: +-15mm
button | fbe17cc5-0a4e-58f6-8614-779e62dcaadb | Acceptance | Yes,No,N/A
note | 6ecc219a-e6f4-5a30-bc48-062c3d1071c0 | Key - H
note | 563af117-9dcf-54aa-b1e7-1c84bd60befc | VIVA - H
note | 26c1a71c-e3c7-54f6-8619-3035514505c5 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 8128f3ee-2a3d-56f1-9e6a-fb0a34a30417 | As built reports
signoff |  | AUTHORITY HOLDPOINT
checklist |  | INF-HSEQ CC0398-ITP-002 Bulk Earthworks REV D | itp | INF-HSEQ CC0398-ITP-002 Bulk Earthworks REV D |  | c49b5c58-0a77-4f97-93e4-48886035b4bf
section |  | 1.0 Preliminaries
checkpoint |  | 1.1 - Determine lot size
note | 17c2ed7f-6649-5816-b0d9-c9f08c804f2d | Acceptance criteria - What is the lot size?
textbox | 939eeafe-eea4-5169-8369-1b238759f0fb | Acceptance |  |  | m2
note | d7856abb-22da-55e1-ac94-131e27f59581 | Key - S
note | 3f5c9f41-ba36-59f3-aa3e-d7d953263178 | MDR/VIVA Key - S
checkpoint |  | 1.2 - Survey set-out
note | 95c23751-464a-5c23-8c42-6c4475203c53 | Ref docs - 235929 IFC Drawings
note | a003dc98-8074-5f09-bf30-347080541f43 | Acceptance criteria - Has the work area been set out for line and level?
button | 414fc0b9-d0aa-503a-8b72-1acc0142d5e7 | Acceptance | Yes,No,N/A
note | 244e5a50-04fe-53a3-996b-948074e374a1 | Key - S
note | 87ade986-a2da-519e-a4d5-964d14d3564b | MDR/VIVA Key - S
note | 93a9bdc1-186a-52b6-a29c-66d2021e49f0 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
textbox | 5feb5bf7-0aac-5792-a0c4-02653b7d41cf | IFC drawing number:
textbox | 9f62bc1b-b9a8-564c-a937-859df44285e6 | Rev:
checkpoint |  | 1.3 - Excavation material classification
note | a386b8ef-731d-5cf5-85fd-d2db39fe7f49 | Ref docs - 235929-000- CV-SP-00002
note | 475ed1a0-a607-5f85-825b-1cafb9b13c08 | Acceptance criteria - Has the material being excavated been inspected with category agreed upon by Superintendent and/or Superintendents Environmental Representative?
note | 39dfcc38-a132-502d-b61c-e070d7fa269c | Tick category below:
tickbox | 16d27692-38e0-575c-8923-9bee94e3c519 | Common Fill (CF1)
tickbox | c9acafa7-2d96-5355-b866-959295f39c36 | Sand Fill (S1)
tickbox | dc14a3b9-f0b4-5abf-89ce-46bb6222f428 | Structural Fill (SF1)
tickbox | 48594622-3c27-5471-b593-1cc677bff502 | Topsoil (TS1)
tickbox | fdd39b43-d498-582a-af44-4616da946bd2 | Reuse of Site Won material
tickbox | c00254ca-c049-53a1-a7b8-1884a2c653d2 | Rock
tickbox | a54318c8-52cd-539d-88c0-f050911d3d4f | Contaminated Material
button | 1183bc04-d025-5e22-9ecb-27f15ba52dff | Acceptance | Yes,No,N/A
note | d2efc44e-4948-521c-a787-b6633d9f67ce | Key - H
note | 7b586300-13bb-5686-abd2-dfda87b38f31 | MDR/VIVA Key - W
checkpoint |  | 1.4 - Material Submission / Approval
note | a0176bd7-d038-5164-97ec-68460346314a | Ref docs - 235929-000- CV-SP-00002 Sec 11.1 Aggregate report
note | 881c9d6c-e129-5c59-9257-eb9855179d9b | Acceptance criteria - Has any imported material (to be used as permanent fill) been approved by MDR for usage on site.
button | 5d547fea-255f-56da-91aa-79525e69c8df | Acceptance | Yes,No,N/A
note | 3be45e37-2c04-58b9-a4c2-d8753b2f82f5 | Key - H
note | 0ab96b98-a950-5ce1-be24-24bc7efc1d34 | MDR/VIVA Key - H
note | 4f0825b1-5d2f-581d-b3fe-bebcc0e8520c | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 42e5086d-e728-57fb-b1df-376f7a475cd9 | Material mix design
signoff |  | AUTHORITY HOLDPOINT
section |  | 2.0 Bulk earthworks – cut
checkpoint |  | 2.1 - Subgrade preparation
note | 079f5e68-cd67-56df-b0cd-3c707fbe5dc2 | Acceptance criteria - Has the area been excavated to top of earthworks layer.
note | 7d15c849-32c2-5dd2-8314-4b8a1a458e35 | ○ Note: Existing surface material is approximately 200-300mm of crushed rock.
note | ded8d32c-22b4-56d2-978e-5e1449224d11 | ○ Is the surface evenly graded and free-draining.
button | 443106d1-8ecc-5b77-8c79-0478f9a1e8f8 | Acceptance | Yes,No,N/A
note | a53716f1-44f3-559b-9222-3b3f49b71e3e | Key - S
note | 543f0d46-93a3-5fb4-8c5b-c7498753c251 | MDR/VIVA Key - S
checkpoint |  | 2.2 - Material Export / Stockpiling
note | 743366f3-681d-5363-9d44-c0b79f0b780e | Ref docs - SMP 20359156-211-R-Rev
note | e8031a82-714d-5411-b201-9f3e72df01b8 | Acceptance criteria - Adherence to Soil Management Plan.
button | e142d24b-eeab-5ed9-9a2e-7c11f2d83c71 | Acceptance | Yes,No,N/A
note | b4742af9-5605-57e9-bd5d-53ecc9238a6b | Key - S
note | 2e09c9db-4dc1-5810-8cda-c8b97f430d49 | MDR/VIVA Key - S
section |  | 3.0 Bulk earthworks - fill
checkpoint |  | 3.1 - Preparation of surface
note | 247b5235-85c8-5547-b733-127f326c7585 | Acceptance criteria - Has surface been cleared of all loose material visible on surface.
button | 94210f34-239e-5a10-859b-1ba3ee25fd17 | Acceptance | Yes,No,N/A
note | 6d2f2968-c8a7-58ae-b197-1ea0492a2235 | Key - S
note | 5986627b-044d-5721-98fc-f156ab469f1f | MDR/VIVA Key - S
checkpoint |  | 3.2 - Compaction Trial for Blended Material
note | 600de072-e43d-5d8a-8b29-310d6c0f9dd1 | Ref docs - 235929-PE- WI-000009 - Backfill Specification
note | 6ef316aa-259f-5d74-990d-2ad22aa91172 | Acceptance criteria -
button | 3265b67a-9766-5a39-8ece-21c60a190621 | ○ Is the material to be used for backfill blended material. | Yes,No,N/A
note | 00f6c107-39d5-5e67-9602-24b0ca652853 | If No, go to item 3.3.
button | 87ff2c05-68f2-5396-a1f1-7eb495a3802a | ○ Has the compaction trial been undertaken? | Yes,No,N/A
button | 356fb490-cdc6-5a1b-b546-9af580793365 | ○ Did the compaction trial achieve the appropriate design backfill requirements of 70kPa? | Yes,No,N/A
button | 3339ed77-d485-5166-a70b-2d70228c0523 | ○ Does MDR approve usage of site blended material for backfill purposes? | Yes,No,N/A
button | 8f4995db-6b67-5ad9-b136-cd0a4dbb8d5c | Acceptance | Yes,No,N/A
note | 7e239d07-0614-5b34-b811-48925eaf4a53 | Key - H
note | e5fd72dd-8075-5ba8-a67a-0ecc5afc56e7 | MDR/VIVA Key - W
note | 5dfb2fbb-bad2-58e2-a061-7784fedb11df | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
textbox | a51ec0d1-a2fb-5fd1-b764-ceb991274e3f | MDR approval:
textbox | 0b7b470a-f52a-5f02-b88c-e9edcad8ceaa | (correspondence reference number)
checkpoint |  | 3.3 - Fill Placement
note | 119184bd-f636-5039-a4bc-8c3367637c5b | Ref docs - 235929-000-CV-SP-00002 Sec 12.2, 235929 IFC Drawings
note | 8fe5cde6-7b3f-5a72-8946-3885580a2681 | Acceptance criteria - Has fill been placed in maximum 200mm compacted layer thickness?
button | e434c6a8-d8c4-59f1-8425-5c6dcfa01fdd | Acceptance | Yes,No,N/A
note | e1ba56e0-6c97-5bc7-8eb9-5cfd038ffa44 | Key - W
note | 319a9a92-6fef-5c4c-a011-4dad984f2936 | MDR/VIVA Key - W
note | 8238465d-3205-5dbd-8a22-5814f173459c | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
checkpoint |  | 3.4 - Moisture
note | bdf9774c-c3d0-504f-841f-a11c1fdddcfe | Acceptance criteria - Has the material maintained at +/- 3% modified moisture content, with additional water being added if required during compaction?
button | 0f4d56a2-bda2-532b-9091-eafaab18f2b2 | Acceptance | Yes,No,N/A
note | bb7fa767-0045-5e73-a054-4da887129cfa | Key - S
note | 34a0df43-7447-5733-ad0b-0dd2d99083ce | MDR/VIVA Key - W
note | 28c50542-a9e3-515e-9348-931f076e399c | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | fd4397c8-78db-561f-9d22-ae417982ce64 | Test reports
checkpoint |  | 3.5 - Compaction
note | 8dd9625d-58f3-5dee-9a01-ee1f6a3e57f4 | Ref docs - 235929-000- CV-SP-00002 Sec 13 & Sec 14.2
note | 2c1c660f-8f9f-5b23-be56-388e897a363d | Acceptance criteria - Has the layer been adequately compacted achieving a mean value of minimum 98% MDD?
note | 1992ca89-242d-5eb6-84a4-40644a7ed472 | ○ Density test to be completed on first backfill to verify procedure. Procedure assumed to be equal henceforth (Inspector may request additional test upon insufficient density or compaction).
note | 53ea1341-e06d-547d-9811-a95dfe9944cd | Acceptance -
tickbox | 546263c4-daee-50e1-b864-598846089603 | Small Foundations
note | d51e168c-162f-5adf-bf72-52fdea3e663f | (1 test per foundation)
tickbox | 23220f2a-3f3c-57c2-b1d0-57f60b977850 | Large Foundation
note | 01aa0de9-31c1-5d45-aeb4-b608cb4902ed | (larger than 10m2) minimum 3 tests per lift
tickbox | 6436025b-dd51-55ff-9291-3dc905aa5e84 | Fill Areas minimum 2 tests per 185m2 but not less than 3 tests per area
note | 2ab8f6fe-1eb4-561d-84f5-4aa65506abc0 | Key - H
note | 52be4b23-9644-5961-8d24-4cc6ca25475a | MDR/VIVA Key - W
note | acbbca5f-8ef6-587f-bf83-cd62e724f47a | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | a7f397a5-8ecc-560c-856b-3123b1ee5078 | Test reports
checkpoint |  | 3.6 - Fill layer – test rolling
note | fa9b9cb2-6e5c-5ab7-ae3e-35fcfc6dd76f | Ref docs - 235929-000- CV-SP-00002 Sec 12
note | c71e2bf6-058c-503c-b18a-b7a318ffa9a9 | Acceptance criteria - Does the layer withstand test rolling without visible deformation or springing?
textbox | a9285242-a497-526b-8026-b59279a7e060 | List Attendees:
button | e091273a-d4b8-5080-bf13-985e291dfac3 | Acceptance | Yes,No,N/A
note | 8cbc68c6-937d-52ba-99a4-36cb9d70a2f9 | If 'no' please see below If 'yes' please proceed to Conformance Check
note | 39c24a2e-6181-598d-89b5-7e85ebabfe9c | Key - H
note | 441e742f-19dc-5f26-b13b-bb0253a4db09 | MDR/VIVA Key - W
note | c9e4d077-121e-5383-b93c-65cd02b4cb90 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 74ba581f-2fc9-5ce5-b627-f90f5236bd6e | Proof roll checklist [235929-MG1668-CV- 003-SUBC-000053]
checkpoint |  | 3.7 - Identification of soft wet or unstable material
note | 95e5b108-fac5-5515-b8c0-cc9048cdb6c9 | Acceptance criteria - Has any soft or wet unsuitable material been found?
button | e010e420-4c20-55bc-98eb-15eb30ae9f9c | Acceptance | Yes,No,N/A
note | febfea7e-0b56-5b46-8dc1-237eac1d2d42 | Key - W
note | 80d09676-4e64-50f1-87bf-572b396ef562 | MDR/VIVA Key - S
checkpoint |  | 3.8 - Treatment of unsuitable material
note | 7623fbb6-0b92-5c0e-acd8-4fa1c88f85a5 | Ref docs - 235929-000- CV-SP-00002 Sec 12.1, Symal Proof Roll Procedure Doc
note | 0526dd2b-c120-5c17-857b-56d93c49baa5 | Acceptance criteria - Have any issues been determined?
textbox | 44dcaf17-29d8-5dcb-b903-396ebbd75e82 | (length) |  |  | m
textbox | f2c2b076-ad13-5148-9185-a729d9f65fd5 | (width) |  |  | m
button | 498a0a65-ffd3-5383-9400-4d9a02b89f6f | Acceptance | Yes,No,N/A
note | 6a2b81fc-9995-5f0f-bde7-357d0f7e278d | Key - W
note | 8ce4edd9-e6a3-5cf4-bac8-f7eb4d94ab9b | MDR/VIVA Key - W
note | c1711777-6c0f-538d-94d4-5734d8e221ef | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Proof Roll Checklist, Dockets / Photos
section |  | 4.0 Conformance check
checkpoint |  | 4.1 - Subgrade level and shape
note | 4a32164d-617a-5d45-b7d9-c8c2d2c62728 | Ref docs - 235929 IFC Drawings
note | 1ec92379-64a0-51e5-8d42-44d7d51ad26b | Acceptance criteria - Has the prepared subgrade been surveyed in accordance with and verifying specified requirements?
note | 9d26e3ab-8309-5a70-8eae-6226750a50af | ○ Final grade +- 60mm
button | 57c34ad4-27ed-57c5-9994-5f4ed7d17c25 | Acceptance | Yes,No,N/A
note | 78001b3d-1342-56e5-a5f7-0ddd17672814 | Key - H
note | 19578b77-12aa-50e7-a3a6-6215b317b037 | MDR/VIVA Key - W
note | 60c3c6fe-2e3a-588b-9791-af591495ee2e | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
tickbox | 86e2d997-539e-568a-a7d5-4b04bc121298 | As built report
textbox | 5f382c3b-f132-5b5c-875d-59a7be186117 | IFC drawing number:
textbox | ad5daabb-5230-587b-bce5-a329176f6c59 | Rev:
checklist |  | INF-HSEQ CC0398-ITP-031 Blinding, Pile Caps and Slab Footings Rev 3 | itp | INF-HSEQ CC0398-ITP-031 Blinding, Pile Caps and Slab Footings Rev 3 |  | fb9861af-a689-4541-93a0-241e1cc8be4a
section |  | 1.0 General
checkpoint |  | 1.1 - Material Submission / Approval
note | 38dc39c1-97aa-5987-bc61-8cc1a17d59b7 | Ref docs - AS 3600 235929-000- CV-SP-00007
note | 66bc53e2-f270-563e-a4b5-d9d15ed3de85 | Acceptance criteria - Has the mix design to be approved prior to placement. Material properties meet project specification, AS 3600, AS 1379?
note | 2051261c-d26c-51f1-a53b-15cc5181a8cd | ○ Do Structural Elements meet: Minimum Concrete strength 40 MPa or as specified in Drawings?
note | 5f725601-87d4-5f25-98f8-ff0c4a102d4e | ○ Do Non-Structural Elements meet: Minimum Concrete strength 15 MPa or as specified in Drawings?
note | 0b478f3b-221b-593b-bd2a-27904927049d | ○ Has Steel Reinforcement schedule provided to MDR for review and approved?
note | fd49ac14-fc4c-577d-b810-d73735edd6c8 | ○ Do admixtures shall conform with AS 1478.1 and are permitted if used in accordance with manufacturers instructions?
note | bfd4a202-eac0-583a-8d60-53ff6f4a61f1 | ○ Mixtures containing calcium chloride shall not be used.
button | 1e83a2a2-1a47-58b0-9171-77d1d5b38a78 | Acceptance | Yes,No,N/A
note | de1c3c54-5e6f-59fd-9d9f-cc7d4a4f11f6 | Key - H
note | dc65c313-7a5a-5d5d-a677-e787b15d0c60 | MDR/VIVA Key - H
note | 556114eb-a1b4-5385-b989-cb03ac46bf52 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Mix Design Number, Bar Bending Schedules, Material compliance certificates
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 1.2 - Determine lot size
note | 5ae5a78b-cf2a-597c-bce9-680c9cdad51c | Acceptance criteria -
textbox | 9cc93c84-89f3-523e-af5a-3b1a4e2623ca | Lot Size = Each pour section per day (location or m2) or each structural (Pilecap)
note | dfe7de41-a4ef-5ac9-b818-c1a6c13751da | Key - S
note | c76448c8-724e-5395-b5f5-34fc6089ff77 | MDR/VIVA Key - S
checkpoint |  | 1.3 - Permits
note | 9bff6d0e-771e-52a8-946a-8d127d399758 | Acceptance criteria - The following are relevant, in place and signed onto:
note | 5af0f85a-9817-5358-b330-02e31e30ebc7 | – Penetration permit
note | da668d64-52b7-55d5-b6ed-31b53edc1a2d | – Hot works permit
note | f304070e-4b95-5b82-a3d3-695a812a5b09 | – Temporary work permit
note | 79378160-af0d-5fa8-97d6-79591e53e5bc | – Working at heights permit
button | 1b6ccd4a-1282-5b7c-b04d-9e07d17fb828 | Acceptance | Yes,No,N/A
note | 138c99c4-157f-5bbc-9974-29302a05cf6b | Key - H
note | 51da0678-2edf-5890-9cd5-b33a628dca49 | MDR/VIVA Key - S
section |  | 2.0 Blinding/Lean Concrete
checkpoint |  | 2.1 - Set out
note | 86fe4bc4-62ff-5c40-9bb9-3a7cd82075f1 | Ref docs - IFC drawings
note | 089626ac-9bbd-548e-bd18-dacf51ff92f9 | Acceptance criteria - Extents, grades and levels correct to relevant drawings. All services have been marked out.
button | 33a08e2f-ba2f-5484-a2b9-57125200af6a | Acceptance | Yes,No,N/A
note | f591230a-d954-5fcf-a8ca-acc37573e700 | Key - W
note | a4ef8778-38d4-53a9-b6bb-1d5f4a174358 | MDR/VIVA Key - W
checkpoint |  | 2.2 - Pre-Pour Inspection
note | ec7ee693-13c8-5626-ab42-5d7cca6da121 | Ref docs - Bulk Earthworks ITP 02
textbox | d6ed777d-3d29-5f36-8e20-774571a70ff7 | Underlying lot number: ---------------------------
note | 508b44c2-a4d5-5b6a-8064-f431605ab32e | Acceptance criteria - Has a pre-pour inspection been completed with the client, and they have verified in writing that the pour is able to commence?
note | 01eabe0a-10f8-5400-9041-d074788419d5 | ○ The foundation base excavation shall be tested, surface compacted and approved prior to placement of the blinding.
note | ae86cf42-f983-5714-ab6c-42571514a449 | ○ The foundation location, depth and dimensions shall also be checked and confirmed prior. to placing the blinding.
note | 4de94789-0a5f-514d-b31d-d228bee0d2aa | ○ Approval shall be provided, in writing, by McDermott to the foundation. subcontractor before commencing with concrete placement.
note | 766f8803-c430-5e51-9098-f4c55463bf94 | ○ Has this been completed?
button | be854e56-748b-562b-b097-10edb85de43e | Acceptance | Yes,No,N/A
note | 85c6c7fb-2f8a-53f4-b9f3-8d5eac4d1f55 | Key - H
note | e6e9c8c3-c1d8-54f1-88e0-e11486688fa5 | MDR/VIVA Key - H
note | ca558a49-2270-58c0-a08d-98204cced2cc | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Pre-Pour Checklist, 235929-000-CV-SP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 2.3 - Lean Mix Concrete
note | c0181690-db59-5f12-936c-d0cb9382f4ec | Ref docs - Section 5.1.2 of document 235929-000- CV-SP-00007
note | b999404c-0268-5609-b37f-fe95f278faf5 | Acceptance criteria - Approved Concrete Mix Design.
button | d4c31910-d804-590a-8b32-76c475a8e69a | Acceptance | Yes,No,N/A
note | 6983f950-b771-5c06-850e-ab5b59e303b2 | Key - W
note | 0c5e9dcb-64e5-5698-8cf9-c92c8380d069 | MDR/VIVA Key - W
note | 15a44087-ddb2-5c30-a1fc-a12f8ba0a5ef | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Dockets
checkpoint |  | 2.4 - Placement of Lean Mix
note | 49209e33-c527-599b-bd12-ae606910c89e | Ref docs - 235929-000-CV-SP-00007
note | a84414c6-b35c-56cf-b14c-8fc6cd13cf02 | Acceptance criteria - Has the blinding been poured to the correct level? The following are acceptable:
note | 5a62b3de-cf3f-5125-bd5e-4329bb47d03b | – Minimum Thickness = 50mm
button | 6e9a8561-a3de-5bbf-a3cd-386009a4c82c | Acceptance | Yes,No,N/A
note | 0a030111-d672-5aef-a44c-b2489fda43a8 | Key - W
note | 7387a6ed-a301-5b0b-b17e-e8e79b0d6977 | MDR/VIVA Key - W
note | d5da4906-4e10-5691-b7c4-785fe3ed91e4 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - As-built Survey
section |  | 3.0 Formwork
checkpoint |  | 3.1 - Temporary works requirements
note | c7819eff-ac8d-5ff9-b597-0f2b6f3a4a78 | Ref docs - SYM-INF-Temporary Work Procedure IFU 05122
note | fb975dca-1c9e-50e7-9e2d-f87b208c3eeb | Acceptance criteria - Formwork above 1.0m to be designed by temporary works engineer.
note | 2ab242e7-9df3-5ef7-8398-aa12988d9771 | ○ Has design to be undertaken by external consultant complying with AS1170 and AS3610 plus any project specification requirements?
button | 4478758b-9afd-5146-93d3-af9f63a08daf | Acceptance | Yes,No,N/A
note | f8449bb5-6135-5252-a322-90a42793f594 | Key - H
note | 1f9c2ac4-53bd-5031-986d-94e9fcfd3364 | MDR/VIVA Key - S
checkpoint |  | 3.2 - Pile Penetration
note | ca94c097-afa7-5f79-a50e-916650438797 | Ref docs - Civil Drawings IFC
note | 20309ffe-f6ee-590f-9186-18ba5bd6f161 | Acceptance criteria - Pile C.O.L to penetrate 50mm above blinding of pile cap (+/- 25mm).
note | 7b063ac0-ac9b-5948-9e3a-1146ce759369 | ○ Has the pile been determined to be free of cracking and concrete damage following cropping?
button | 9f1bb396-e983-53ed-ba99-e6d9d34cd1a8 | Acceptance | Yes,No,N/A
note | 344e6758-6c88-5409-8f2f-0a58e050cf22 | Key - H
note | 9de46810-e107-5e8a-96c8-6c10f3f048d1 | MDR/VIVA Key - H
note | 854479c7-f6e2-581e-8033-e770c58f9fef | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Report
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 3.3 - Formwork Setout and positioning correct
note | 5535dc21-45a0-5166-aeaa-70a54f48f3ca | Ref docs - Civil drawings 235929-000- CV-SP-00008; Section 6
note | e7480757-5b6f-5994-b7b2-b90610675b29 | Acceptance criteria - Is formwork checked for potential loose sections, ensuring no movement upon placement of concrete?
note | 5b47baf0-737f-596f-9bbf-ebb400095fe0 | ○ Is formwork in line with survey markings?
note | 7f7dd498-3c4f-5eff-9bc5-ce271fcbfc67 | ○ Have chamfers (if required) been attached to formwork in level manner?
button | 7d1dcfdb-096d-5461-ab3a-78ebee5e310f | Acceptance | Yes,No,N/A
note | 7ad068b9-91fc-590d-b608-0150ab8ff736 | Key - W
note | 1b82924b-a9bb-5542-aacf-0703c64a07b0 | MDR/VIVA Key - W
checkpoint |  | 3.4 - Concrete jointing
note | 4f59ced6-d6b0-5831-837d-bf1581fcd594 | Ref docs - Civil drawings
note | 91eede06-c374-5b5f-92ff-d89a7db6e3f2 | Acceptance criteria - Have construction joints to be installed as detailed on Drawings and notes using correct materials?
button | 5721c9c0-a3fc-546a-97d9-092302ebc07b | Acceptance | Yes,No,N/A
note | 0228c326-27c4-510e-b07a-cb7faf01793e | Key - W
note | 4c1d22f1-532a-514d-9c9b-f26cbffbb870 | MDR/VIVA Key - S
section |  | 4.0 Reinforcement
checkpoint |  | 4.1 - Steel reinforcement supply
note | f42931b2-66a1-51f1-be50-2c7e599cc49e | Acceptance criteria - Have steel tags checked against supply schedule prior to installation?
note | 61b24da6-4ac4-5952-8d6b-4337b1843aec | ○ Does the manufacturer hold a valid ACRS certificate?
note | fd813473-0387-5126-a63b-b569baf3b18c | ○ Is reinforcement is free from rust and other contaminates that may affect bonding?
button | e59386e9-e209-5aaa-82f8-cdd0697773db | Acceptance | Yes,No,N/A
note | 890a24d8-f366-56c7-b083-3bffc08bdef2 | Key - S
note | 8221f792-3caa-5c2e-ba97-26cff7f5ab2f | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Delivery Dockets / certificates / product tags, Incoming material checklist Photo’s
checkpoint |  | 4.2 - Steel reinforcement installation
note | d22409ec-ccf9-5370-b6eb-4dbbf8715b67 | Ref docs - 235929-000- CV-SP-00009, AS3600 17.5.3, 235929-000- CV-01-92002- 010002
note | 6810c17f-d835-59a0-ac94-7a3df2f24a31 | Acceptance criteria - Is steel installed as per the latest IFC drawings?
note | 70f1ae2d-0b63-5ef3-8fa0-1d2c9a22913e | ○ Does steel reinforcement conform with Steel Reinforcement Specification?
note | 866f16bd-0658-51b0-95d6-2bc197050c44 | – – – – – – – – – – – – – –
note | 4fdf6b1d-4ff2-5ef9-9362-2baa7e9ab501 | 17.5.3 Tolerance on position of reinforcement and tendons
note | 216d941c-878a-5ede-ab23-3d86b51297ec | The deviation from the specified position of reinforcement and tendons shall not exceed the following:
note | bf01ae81-1011-5a6a-81c4-8f7e5eb74919 | (a) For positions controlled by cover –
note | e7b5e44b-7575-5e12-a0c2-ecaff87cd733 | (i) in beams, slabs, columns and walls: -5, +10 mm;
note | f8f39c39-2cfc-51fd-ba00-ce6cfa6e2b3f | (ii) in slabs-on-ground: -10, +20 mm; and
note | ea7f388f-2b47-5ff4-8246-2e841888ff04 | (iii) in footings cast in the ground: -10, +40 mm,
note | a4f8bc42-4867-53e0-b2a1-65ce6b07823a | where a positive value indicates the amount the cover increases and a negative value indicates the amount the cover decreases.
note | 823636fa-9bb5-59e4-b47f-57b5832f0b1c | (b) For positions not controlled by cover, namely –
note | b9133cb8-cb80-5600-aaaf-d6ee1eb8d8d1 | (i) the location of tendons on a profile: 5 mm;
note | 99065f29-b07c-594f-841c-6df3a506c4d7 | (ii) the position of the ends of reinforcement: 50 mm; and
note | af268ade-110f-5716-a4cf-67cdaebfb06a | (iii) the spacing of bars in walls and slabs and of fitments in beams and columns: 10% of the specified spacing or 15 mm, whichever is greater.
note | ee259f74-8863-5c36-899c-9be71202c541 | – – – – – – – – – – – – – –
note | 16a1861c-5b6b-5fc6-846f-36200d7dcc3b | ○ Has minimum cover to inside face of wall must be maintained? All reinforcement shall be in accordance with AS 3600 & Civil drawings.
note | d2fe726d-b515-5987-9f1d-bbd12508d9b8 | – – – – – – – – – – – – – –
note | d63c2bfc-fe63-5578-a6d5-82ffca82744a | 8.1 CONCRETE COVER SHALL BE IN ACCORDANCE WITH AUSTRALIAN STANDARD AS 3600 OR THE VALUES STATED BELOW, WHICHEVER IS GREATER.
note | 0f40a8cf-669f-53ed-9c92-6f5ebb5f02ac | ○ PAVING (TOP) = 30 mm
note | 6d8f4b08-39eb-5b25-8d96-a62bdab591f1 | ○ PAVING (BOTTOM - AGAINST GROUND) = 50 mm
note | 16e94149-4024-5b9f-9d6f-42ae460a5559 | ○ FOUNDATIONS CAST AGAINST FORMWORK (INCL. EXPOSED WEATHER FACE) = 45 mm
note | 021a922d-e5d0-513f-890d-c06debe22372 | ○ FOUNDATIONS CAST AGAINST GROUND = 65 mm
note | 0973c0aa-da2f-5900-88f6-b3260841c5fc | ○ EXPOSED TO WASH DOWN WATER AND/OR PROCESS SPILLAGE = 50 mm
note | 81964aa0-8a8f-543e-8519-793fafead59f | ○ CAST ON LEAN CONCRETE = 45 mm
note | c7557033-23b8-54df-98eb-9909d90dc9ca | ○ CFA PILES = 70 mm
note | 9926baa2-c277-5d16-8aa2-294dd6120c87 | – – – – – – – – – – – – – –
button | 7e9e464f-63c6-50ef-a40b-8ee9989570f8 | Acceptance | Yes,No,N/A
note | 9f00da5c-02b5-57c6-9ee4-45d014933309 | Key - H
note | 5d6b38f5-845a-5e80-993e-560195f284be | MDR/VIVA Key - S
note | 05102a51-0c35-550a-ad38-1a1984d66084 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - IFC Drawing Number and Revision
section |  | 5.0 Structural Concrete Pour
checkpoint |  | 5.1 - Pre-pour Inspection
note | 239ffe9e-5ec3-5fd1-b0c4-f20c7e67ae4b | Ref docs - 235929-000-CV-SP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
note | 4db2740b-4bb6-5ccc-b27e-5b092ab54960 | Acceptance criteria - Has a pre-pour inspection checklist completed prior to placement?
button | 0b4afb99-2b27-5759-b940-2528358e76b5 | Acceptance | Yes,No,N/A
note | 9236e013-4ce8-5ec0-bf67-f3a5d594cb12 | Key - H
note | b137a84d-23cd-5150-ada7-fac772779c01 | MDR/VIVA Key - H
note | 52f81244-cb49-539d-80e2-05c4178e5004 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 5.2 - Placement
note | cf45ad69-6304-520e-ac92-0418c788afea | Ref docs - 235929-000- CV-SP-00007 Appendix 7.3 Concrete Truck Record
note | b20d327c-4997-5b05-b905-9173ff44a912 | Acceptance criteria - Concrete shall not be placed when temperature is less the 5°C or greater than 36°C. Between 32°C and 36°C admixtures and placing requirements must be met.
note | 3b518dbe-f4ef-51f9-a0de-f4b0f17e3944 | ○ Concrete shall be transported, handled and placed to prevent segregation, loss or leakage of materials.
note | 90b508b7-9702-5ee3-921a-475378d98e79 | ○ Concrete shall not be dropped from a height greater than 2m.
note | 5f46a6c2-e296-59d7-83f1-6aece02703d6 | ○ Concrete shall be discharge within 90 minutes of dispatch from plant.
note | 2deae49a-8fe0-535d-9ff4-94c49e292fcc | ○ For continuous pours, the maximum time lag between truck loads shall not exceed 25 minutes.
note | a8eeefbb-ca7c-5b1d-9a41-e4a56283a0b2 | ○ Concrete shall be thoroughly vibrated to ensure no honey combing, voids or surface defects occurs and compaction is achieve throughout structure.
note | 77a59b85-24df-5680-8886-66f8739d49d4 | ○ Water shall not be added to achieve slump greater than that specified. Slump test to be completed after water is added.
button | 895d47a5-a1aa-549c-a38c-11b1e0dd2ae1 | Acceptance | Yes,No,N/A
note | 2f23a380-2723-599a-8be2-b9d622724aab | Key - H
note | 74c06dfc-9064-5b62-9ade-07340b55e3cf | MDR/VIVA Key - W
note | 0d5bea98-5a15-51b4-a762-f1c9019ae34c | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.3 Concrete Truck Pour Record/Dockets
checkpoint |  | 5.3 - Slump Test
note | df23455f-3b5a-5d55-8fac-fa1d22e46fe8 | Ref docs - Section 5.1.1 235929-000- CV-SP-00007
note | 32e1fcef-a061-5f7c-ba59-e3482e2575f3 | Acceptance criteria - Slump must be within tolerance of designed slump.
note | c2171f33-7ce8-5763-adaf-bb6787dbadbf | ○ Testing shall be +- 15% of stated.
note | 86df0126-48a2-5e18-bd77-5ff70ac53d96 | ○ Approved mix design slump
button | d1ef89bb-380e-5796-91f7-2829c0908bde | Acceptance | Yes,No,N/A
note | ecd5aa8f-f4ed-54d6-a786-af29109ff584 | Key - S
note | 16baa9ec-1bc4-597c-b27e-8406c7aa512f | MDR/VIVA Key - S
note | f6a24409-a0b3-536c-afca-48d362553b0f | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test docket
checkpoint |  | 5.4 - Strength Testing
note | 6a712eec-24b0-515d-b216-0914620452ee | Ref docs - 235929-000- CV-SP-00007 Section 6.8
note | 436c519e-acfa-54a4-9e8c-583a2586890a | Acceptance criteria - Samples to be taken from chute. 5 cylinders collected per sample – 1x 7day, 3x 28day, 1x reserve.
note | 36fa5d97-aa53-5a90-b994-98f5f4f0ebc9 | ○ 1 test for the first 20m3
note | 5d6827c1-535d-50ae-b753-418f1a284471 | ○ 1 test per 40n3 thereafter
note | 35fcfc0c-c309-5d8d-9de0-4c58c778f5bf | ○ Frequency reduce to 1 test per 80m3 for pours over 400m3
note | 322fdf96-ea09-5a44-ad31-dbc9ae3f6d98 | Acceptance
note | a0426478-4d97-538c-b10c-52d69069e918 | – – – – – – – – – – – – – –
note | 1d705805-ea00-5501-94af-40d2904998cb | No. of samples ¦¦ Volume of concrete (m3)
note | eeedf888-d6b9-54ea-a141-1f1d40027f74 | – – – – – – – – – – – – – –
note | bbc71923-925e-575e-98d7-466e7be68a57 | 1 ¦¦ <20
note | 5a9c0c7a-b950-5538-a8d8-739efd701cfe | 2 ¦¦ 20-60
note | e971d102-313c-5225-a980-fd95f29b565d | 3 ¦¦ 60-100
note | 80c633b5-0611-5e1b-861a-88805ff61a31 | 4 ¦¦ 100-140
note | e2ab1c0c-441c-5b5d-9c66-11b4d40eb400 | – – – – – – – – – – – – – –
note | 9983feff-0c46-5f99-948b-86aed595806f | Key - H
note | 45500009-804d-54b6-8fed-29d19bac0829 | MDR/VIVA Key - S
note | 180eefb4-5dcc-5324-a1ed-2aaee9d8ddcc | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test report
checkpoint |  | 5.6 - Curing of Concrete
note | f7c0712b-8955-55e8-ab27-f69d4626a3a7 | Ref docs - 235929-000-CV-SP-00007 Section 6.5
note | c1edee11-ee08-5473-b83b-4a2a6ed25110 | Acceptance criteria - As per the approved Curing Methodology.
note | adf2a0c3-8e3f-5603-81f6-b2380f89ae5a | – Applied once bleed water has gone
note | 65f5950e-d5e8-54bd-8253-75674123c1e6 | – Continuous uniform film achieved
note | cb076cc0-2c21-551d-bb2e-620e61c15228 | – Rate of 5m2/L
note | b5547988-aa51-55c8-a251-12d415d7da7d | ○ Has curing been conducted as per approved curing methodology?
button | 817fae1c-00a7-52d5-a06c-fbc361bf5901 | Acceptance | Yes,No,N/A
note | 17874744-6164-5a97-933e-416f164d96fc | Key - H
note | 1e74c937-5f23-5ec4-bba8-f6195146f428 | MDR/VIVA Key - W
note | 92fa07e0-a3fe-5057-a34f-dd18e3de53c6 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Approved Curing Technical Data Sheet
checkpoint |  | 5.7 - Concrete Finishing
note | ca172474-abe9-5707-9354-92222823cb7e | Ref docs - 235929-000-CV-SP-00007 Section 6.4
note | 0e6e3ad2-49b5-5869-92fb-3e51d525d504 | Acceptance criteria - Finish concrete per schedule below:
note | a0814925-0f71-561b-b587-d7a05fccbb1e | ○ Interior walls or columns exposed: smooth form/rubbed finish.
note | c5f50b3a-6d8c-5caf-9989-bb2fea7549bf | ○ Exterior walls or columns exposed: smooth form/rubbed finish.
note | 5ecdd4ef-02b2-56c3-bb96-20a75b791a03 | ○ Walls below grade: rough form finish.
note | d6ea72f1-fd74-5653-ad3c-401c3053c4f9 | ○ Exterior slabs for spill containment: float finish.
note | a6b1b127-b96e-5e22-9317-4a01d53b7d2c | ○ Other exterior slabs (i.e. foot traffic): broom finish.
note | bc06f7d0-e86b-5d4f-a708-03e036c88fd7 | ○ Interior slabs: steel trowel.
note | a11f21c5-2d68-555f-8348-706701894c3a | ○ Interior slabs to accept additional finish: steel trowel.
note | 9dea0913-2eda-5e7d-b7bc-d4c125d26d0b | ○ Surfaces to be grouted: rough [6 mm amplitude] but even finish with laitance removed to provide good bond between grout and concrete.
button | a30e398c-0496-5a92-b198-9caff7926968 | Acceptance | Yes,No,N/A
note | 860f64e1-1579-5c3c-ad59-70ce5fcc6bdd | Key - S
note | 1c75f4e8-aabf-5861-9841-72c7b9f3affc | MDR/VIVA Key - S
note | 315fb1fd-846f-5914-a953-3709828694a0 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.3 Concrete Truck Pour
checkpoint |  | 5.8 - Formwork Stripping
note | fa3a5756-6946-57eb-acac-9d5d87d55622 | Ref docs - 235929-000-CV-SP-00007, AS1510, AS1509, Section 6.6 of 235929-000-CV SP-00008 CONC FORMWORK
note | 8b21296e-c06f-5993-954b-ae76c7df9417 | Acceptance criteria - Has Remove formwork progressively so no unbalanced loads are applied to the structure, or concrete is damaged?
note | 0c2c6fda-7612-55fb-aefd-5e0c545ef761 | ○ Has the formwork been removed in the same sequence as concrete placement to achieve similar concrete surface coloration?
note | 50ba77fb-2509-5919-89c0-9c478a004902 | ○ In accordance with AS3600 Table 4.4 and Section 17.1.5, removal of forms before 7 days would require a curing membrane conforming to AS3799 to be applied immediately or any other approved acceptable method of water retention in the concrete.
note | 621e2dc8-4940-5541-bdf8-c42a4b914fca | ○ Has this been completed?
button | 501e0beb-5a27-5550-b675-c737dea147cd | Acceptance | Yes,No,N/A
note | 396cd9db-d4ed-5070-8c8c-3651e219380c | Key - S
note | a95a6b67-8daf-5635-8665-fea3aa2b89dd | MDR/VIVA Key - S
checkpoint |  | 5.9 - Post Pour inspection
note | 83b22758-b60c-5795-93f8-c10d1940174c | Acceptance criteria - All abovementioned works have been completed in-line with the drawings and specification and backfilling around structure can be completed (if applicable)
button | 481205fd-06dc-5e83-86f2-969975dc853b | Acceptance | Yes,No,N/A
note | 1700a992-191f-5f1d-82cb-31f02e3c63b6 | Key - H
note | ec247bc9-a2be-5b86-9e16-1a94cc9299f9 | MDR/VIVA Key - H
signoff |  | AUTHORITY HOLDPOINT
section |  | 6.0 Completion
checkpoint |  | 6.1 - As Built
note | a4a248be-348c-596f-bb94-db2e17b0b3ee | Acceptance criteria - As built to be submitted after pour, showing set out, RLs, grades, extents, bolts, grout tubes, starter bars, etc.
button | dd426662-ba58-5d08-a428-ffd5f9a65067 | Acceptance | Yes,No,N/A
note | 31c043f2-f95a-5193-af01-8d294bcbac7a | Key - S
note | 2eae9447-6a3d-5a16-9da6-e962fa10673d | MDR/VIVA Key - H
note | f461e7b7-35df-5ee5-b3f2-3cd1c91fea8e | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Conformance report
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 6.2 - Concrete Test Results
note | b0567501-b655-5047-805f-92a97030f726 | Ref docs - 235929-000-CV-SP-00007 AS3600, AS1379, AS3610 IFC drawings
note | 4c830c25-5a30-5cde-8b1c-c4ad69c131fd | Acceptance criteria - Submission of 28 days results. Results meet requirements of 40MPa.
button | 882fd5d6-c066-5d45-ac9e-f6265108dcbe | Acceptance | Yes,No,N/A
note | 9378086f-efbb-56df-a8d4-c7f36335e80d | Key - H
note | 62736c2b-c383-51eb-814a-f744b74d40ff | MDR/VIVA Key - S
note | da0c4da8-e8c2-5f85-8aaa-0ab3912af901 | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - NATA endorsed test report
checkpoint |  | 6.3 - Concrete cracking approval
note | ee34ac15-e616-59bb-8540-c270d0479483 | Acceptance criteria - Contractor is to submit a concrete crack repair methodology to MDR prior to commencing any crack repair. Has this been approved?
note | ef164b3f-5bce-5145-a896-fd14f3aa7aa9 | – – – – – – – – – – – – – –
note | c19c26dc-0b16-532a-bdcc-050cae2b75d3 | Maximum Allowable Crack Widths in New Concrete
note | 843c554a-8132-52c5-9c68-020dd3a3602f | – – – – – – – – – – – – – –
note | 34360a93-ec16-558c-8d16-8eaae13492ef | Service Exposure Condition ¦¦ Crack Width, μm
note | a11b7ea0-7c7b-5a1f-afef-85f410f63e8c | – – – – – – – – – – – – – –
note | 7c9647fa-d9e2-5392-b4b3-156699739c90 | Interior ¦¦ 300
note | 3105f302-a6da-57b6-aee1-73160c8d4993 | Exterior air (or soil) ¦¦ 200
note | 320853ad-9ad1-5686-87f5-fd0b0b860ad3 | Water-retaining structures ¦¦ 100
note | f5b4a7d2-f20c-59ea-b522-91085f645b10 | – – – – – – – – – – – – – –
button | 75e83a5f-9507-5d54-aefc-f438730e4bd0 | Acceptance | Yes,No,N/A
note | 318f2ad8-d665-5344-8acb-3bf3225ac2b9 | Key - H
note | b16419de-1901-5fd9-bfea-cc56b3ed6245 | MDR/VIVA Key - H
note | 6d3a76c9-6037-5d0a-be16-9752f81fb2ae | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Concrete Repair Method Document Approval
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 6.4 - Concrete cracking repair
note | 4690863e-91d7-573c-928b-0dc622373387 | Acceptance criteria - Has concrete crack repair been undertaken as per the approved method?
button | d5217aab-b234-5307-ba82-f79ac01566e9 | Acceptance | Yes,No,N/A
note | 0a981ae8-f477-5408-a8fb-c610b4e47dfc | Key - H
note | b6f635be-858e-52e8-b614-4c5c61f0214a | MDR/VIVA Key - H
note | cb75cf7c-87e6-551c-a1d3-29fc188af5aa | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photo’s
signoff |  | AUTHORITY HOLDPOINT
checkpoint |  | 6.5 - Leak Testing
note | f0bc5ff6-a703-5ea3-94ad-c84071958231 | Ref docs - 235929-DM-AT-000002
note | ad1590fb-52e5-5324-9352-8b43e5d1fbb2 | Acceptance criteria - Has the nominated structure had leak testing completed and passed as per the approved testing procedure.
button | bc84f206-8228-5747-819f-45f42a58d86f | Acceptance | Yes,No,N/A
note | 235c43bb-6a7e-51e4-bd2a-d180ad9dea00 | Key - H
note | e4da6402-2ff7-5c05-9008-d7774e20e814 | MDR/VIVA Key - H
note | a9b4c81b-fe00-5038-b395-33a02fd6f0bc | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Water Test Check-list
signoff |  | AUTHORITY HOLDPOINT