## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ CC0398-ITP-021 Concrete Pavement Constructions Rev 0 | itp |  |  |  |  | INF-HSEQ CC0398-ITP-021 Concrete Pavement Constructions Rev 0
section | 1.0 Preliminaries
checkpoint | 1.1 - Determine Lot Size
label | Ref docs - IFC DRAWINGS
label | Acceptance criteria - Lot size Lot Size = Each pour section per day (location or m2)
label | Acceptance - Marked Plan
label | Key - S
label | MDR/VIVA - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Lot Map
checkpoint | 1.2 - Survey set-out
label | Ref docs - IFC DRAWINGS
label | Acceptance criteria - Has the work area been set out for line and level?
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - As Per IFC Drawings
checkpoint | 1.3 - Material Submission / Approval
label | Ref docs - AS 3600 235929-000-CV-SP-00007
label | Acceptance criteria - Has the mix design to be approved prior to placement. Material properties meet project specification, AS 3600, AS 1379?
label | – Minimum Concrete strength 25MPa or as specified in Drawings?
label | – Steel Reinforcement certificates of conformance provided?
label | – Do admixtures shall conform with AS 1478.1 and are permitted if used in accordance with manufacturer’s instructions?
label | – Are all admixtures free of calcium chloride?
label | – Has jointing materials & Sealants been approved?
label | – Has vapour barrier material been approved
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
textbox | Mix Design Number
bool | Material Compliance Certificates
textbox | Idocs Approval Reference
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 Form Work
checkpoint | 2.1 - Vapour Barrier Installed
label | Ref docs - 235929-000-CV-SP-00007 Section 6.2
label | Acceptance criteria - Approved vapour barrier installed on surface of crushed rock base?
label | ○ Are all lap joints minimum 300 mm and sealed with duct tape?
label | ○ Are major punctures in the vapour barrier patched of taped?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - W
checkpoint | 2.2 - Formwork Setout and positioning correct
label | Ref docs - IFC DRAWINGS 235929-000-CV-SP 00008
label | Acceptance criteria - Is formwork checked for potential loose sections, ensuring no movement upon placement of concrete?
label | ○ Is formwork in line with survey markings?
label | ○ Have chamfers (if required) been attached to formwork in level manner?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - W
checkpoint | 2.3 - Concrete jointing
label | Ref docs - IFC DRAWINGS
label | Acceptance criteria - Have construction joints to be installed as detailed and in locations nominated on IFC Drawings and notes using approved materials?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Delivery Dockets
section | 3.0 Reinforcement
checkpoint | 3.1 - Steel reinforcement Supply
label | Ref docs - IFC DRAWINGS
label | Acceptance criteria - Has correct reinforcement been delivered?
label | ○ Is reinforcement free from rust and other contaminates that may affect bonding?
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Incoming material checklist
bool | Delivery Dockets
checkpoint | 3.2 - Steel reinforcement installation
label | Ref docs - AS3600 17.5.3 235929-000-CV-SP-00009, IFC Drawing 235929-000-CV-01-92002- 010002
label | Acceptance criteria - Is steel installed as per the latest IFC drawings?
label | ○ Does steel reinforcement conform with AS 3600:17.5.3?
label | ○ Does cover to unformed surfaces comply with IFC drawings?
label | – – – – – – – – – – – – – –
label | 17.5.3 Tolerance on position of reinforcement and tendons
label | – – – – – – – – – – – – – –
label | The deviation from the specified position of reinforcement and tendons shall not exceed the following:
label | (a) For positions controlled by cover –
label | (i) in beams, slabs columns and walls… -5, +10 mm;
label | (ii) in slabs-on-ground… -10, +20 mm; and
label | (iii) in footings cast in the ground… -10, +40 mm,
label | where a positive value indicates the amount the cover increases and negative value indicates the amount the cover decreases.
label | (b) For positions not controlled by cover, namely –
label | (i) the location of tendons on a profile… 5 mm;
label | (ii) the position of the ends of reinforcement… 50 mm; and
label | (iii) the spacing of bars in walls and slabs and of fitments in beams and columns… 10% of the specified spacing or 15 mm, whichever is greater.
label | – – – – – – – – – – – – – –
label | 8.0 CONCRETE COVER
label | – – – – – – – – – – – – – –
label | 8.1 CONCRETE COVER SHALL BE IN ACCORDANCE WITH AUSTRALIAN STANDARD AS 3600 OR THE VALUES STATED BELOW, WHICH EVER IS GREATER.
label | ○ PAVING (TOP) = 30mm
label | ○ PAVING (BOTTOM - AGAINST GROUND) = 50mm
label | ○ FOUNDATIONS CAST AGAINST FORMWORK (INCL. EXPOSED WEATHER FACE) = 45mm
label | ○ FOUNDATIONS CAST AGAINST GROUND = 65mm
label | ○ EXPOSED TO WASH DOWN WATER AND/OR PROCESS SPILLAGE = 50mm
label | ○ CAST ON LEAN ON CONCRETE = 45mm
label | ○ CFA PILES = 70mm
label | – – – – – – – – – – – – – –
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - S
section | 4.0 Concrete Pavement Placement
checkpoint | 4.1 - Pre-pour Inspection
label | Ref docs - 235929-000-CV-SP-00007, Appendix 7.1 Pre-Concrete Placement Checklist
label | Acceptance criteria - Has a pre-pour inspection checklist completed prior to placement?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
button | Pre-Pour Checklist Attached? | Yes,No,N/A
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Placement
label | Ref docs - 235929-000-CV-SP-00007, Appendix 7.3 Concrete Truck Record
label | Acceptance criteria - Concrete shall not be placed when temperature is less the 5°C or greater than 36°C. Between 32°C and 36°C admixtures and placing requirements must be met.
label | ○ Concrete shall be transported, handled and placed to prevent segregation, loss or leakage of materials.
label | ○ Concrete shall not be dropped from a height greater than 2m.
label | ○ Concrete shall be discharge within 90 minutes of dispatch from plant.
label | ○ For continuous pours, the maximum time lag between truck loads shall not exceed 25 minutes.
label | ○ Concrete shall be thoroughly vibrated to ensure no honey combing, voids or surface defects occurs and compaction is achieve throughout structure.
label | ○ Water shall not be added to achieve slump greater than specified. If additional water is added, slump test to be performed after water is added.
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Concrete Truck Pour Record
bool | Concrete Delivery Dockets
checkpoint | 4.3 - Slump Test
label | Ref docs - Section 5.1.1 235929-000-CV-SP-00007
label | Acceptance criteria - Slump must be within tolerance of designed slump. Testing shall be +- 15% of stated approved mix design slump.
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Concrete Test Report
checkpoint | 4.4 - Strength Testing
label | Ref docs - 235929-000-CV-SP-00007 Section 6.8
label | Acceptance criteria - Samples to be taken from chute. 5 cylinders collected per sample – 1x 7day, 3x 28day, 1x reserve.
label | ○ 1 test for the first 20m3
label | ○ 1 test per 40n3 thereafter
label | ○ Frequency reduce to 1 test per 80m3 for pours over 400m3
label | Acceptance
label | – – – – – – – – – – – – – –
label | No. of Samples ¦¦ Vol. of Pour (m^3)
label | – – – – – – – – – – – – – –
label | 1 ¦¦ <20
label | 2 ¦¦ 20-60
label | 3 ¦¦ 60-100
label | 4 ¦¦ 100-140
label | 5 ¦¦ 140-180
label | 6 ¦¦ 180-220
label | 7 ¦¦ 220-260
label | 8 ¦¦ 260-300
label | 9 ¦¦ 300-340
label | 10 ¦¦ 340-380
label | – – – – – – – – – – – – – –
label | Key - H
label | MDR/VIVA - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Concrete Test Report
checkpoint | 4.5 - Curing of Concrete
label | Ref docs - 235929-000-CV-SP-00007 Section 6.5
label | Acceptance criteria - As per the approved Curing Methodology.
label | – Applied once bleed water has gone
label | – Continuous uniform film achieved
label | – Rate of 5m 2/L
label | ○ Has curing been conducted as per approved curing methodology?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Approved Curing Technical Data Sheet
checkpoint | 4.6 - Colouring of Concrete
label | Ref docs - 235929-000-CV-01-92002-010015 Note 9
label | Acceptance criteria - Concrete paving above conduit, shall be pigmented:
label | – Red for electrical;
label | – Green for instrumentation.
label | ○ The method to be used is the dry shake, with oxide minerals after bleeding.
label | ○ Pigments shall be used in accordance with the material manufacturer's specifications
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material Approval
bool | Delivery Dockets
checkpoint | 4.7 - Concrete Finishing
label | Ref docs - 235929-000-CV-SP-00007 Section 6.4
label | Acceptance criteria - Finish concrete per schedule below:
label | – Exterior slabs (i.e. foot traffic): broom finish.
label | – Other approved non slip finish (i.e. stipple finish)
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material Approval
bool | Delivery Dockets
checkpoint | 4.8 - Formwork Stripping
label | Ref docs - AS 3600 Table 4.4
label | Acceptance criteria - Minimum Initial curing requirement for 25MPa concrete:
label | ○ Cure continuously for at least 3 days or minimum average compressive strength of 15MPa
label | ○ Has the formwork been removed in the same sequence as concrete placement to achieve similar concrete surface coloration?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
checkpoint | 4.9 - Saw Cutting of contraction joints
label | Ref docs - IFC Drawings 235929-000-CV-SP-00007 6.4.4
label | Acceptance criteria - Should the joint detail differ from design this shall be changed only with written approval by the Client.
label | ○ Saw cut joints shown on the Construction Drawings within 12 hours after placement.
label | ○ The cut depth shall be 25% of the slab thickness.
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - RFI (if applicable)
checkpoint | 4.10 - Post Pour inspection
label | Ref docs - 235929-000- CV-SP-00007
label | Acceptance criteria - All abovementioned works have been completed in-line with the drawings and specification and backfilling around structure can be completed (if applicable)
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Post-pour Checklist
holdpoint | AUTHORITY HOLDPOINT
section | 5.0 Completion
checkpoint | 5.1 - As Built
label | Ref docs - YJRP-SPE- CC-M-0001
label | Acceptance criteria - As built to be submitted after pour, showing set out, RLs, grades and any cast-in elements
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Survey Conformance report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Concrete Test Results
label | Ref docs - 235929-000-CV-SP-00007, AS3600, AS1379, AS3610
label | Acceptance criteria - Submission of 28 days results. Results meet requirements of 25MPa.
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | NATA endorsed test report
section | 6.0 Crack Repairs (if applicable)
checkpoint | 6.1 - Cracking repair methodology approval
label | Acceptance criteria - Contractor to submit a concrete crack repair methodology to MDR prior to commencing any crack repair.
label | ○ Has this been approved?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Concrete Repair Method Document
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.2 - Crack Repair
label | Acceptance criteria - Has concrete crack repair been undertaken as per the approved method?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
holdpoint | AUTHORITY HOLDPOINT