## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | *Standard ITP - Aus Standards - Wet Area Waterproofing |  | *Standard ITP - Aus Standards - Wet Area Waterproofing
9e5178fe-275d-4f66-a1d8-c2dfb2595b6e | section | 2 - Construction Inspections
| checkpoint | Inspection Details
| textbox | Level:
| textbox | Zone:
2fcdccd6-ea1b-4aed-8a70-0e17ed1f631d | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
96201ade-dcca-5b3d-a6c5-a3ae93feee85 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
99c3f8df-eff4-5c8d-b2f4-6f1d29088d76 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter [Vulkem 350R/951NF datasheet]
| textbox | Test/ Inspection - Measurement
f86ac474-28c1-5697-be6a-e58d9bc3daf5 | note | Test/Inspection Frequency - Each wet area, every 20m2
6cf3e71d-c2ee-5a5c-ba3b-674348252abf | note | Inspection: Subcontractor - WS (I)
4565c4c6-4d2d-5474-95ab-41343318208a | note | Inspection: John Holland - PE (S)
90e49087-aac7-40a7-9806-ef8e4a339d89 | checkpoint | 2.2 - Drainage installation - puddle flange installation
2f3646ab-f896-5188-8e2d-b9987d4aec3f | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
cc328293-f678-536a-a587-7d253099f364 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
bae9c3b4-910f-5f63-ab36-ad95261ee082 | note | Test/ Inspection - Installation and Inspection
fd6c5132-e6cc-555a-914b-f6b58b43ecaa | note | Test/Inspection Frequency - Each wet area
674d7feb-eba4-5a6d-b15f-ee634970b934 | note | Inspection: Subcontractor - HS (I)
b23f7f36-3ad2-559f-908a-4d2593e464cf | note | Inspection: John Holland - PE (S)
0ffe2ed6-0447-46cf-afed-d36722c5e0ad | checkpoint | 2.3 - Substrate condition Inspection
5d6d53e5-3aa6-551c-bf8f-18cdce1ad464 | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
afe4b9f4-3b64-5a38-830b-95b79c4d457a | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
a82dd030-d95a-5c07-b8db-bfc492829914 | note | Test/ Inspection - Inspection
ac9e23b1-27d4-5e1c-ad64-e3d2eca86ca5 | note | Test/Inspection Frequency - Each wet area
ee4390cb-133c-5109-9c57-606c7eefbaee | note | Inspection: Subcontractor - WS (I)
f35105ec-12af-5c69-be4b-b4cadbd65ca1 | note | Inspection: John Holland - PE (S)
1f992917-9d30-4dfa-a190-aeab456f663c | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
92c8c68d-6b09-5dab-a8fd-05b6d5d32c88 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
da5a0942-7821-5f26-95fa-208ff67a190b | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
98fefd0d-925e-5bac-bf98-551f884c2609 | note | Test/ Inspection - Measurement
faeff10b-75b3-56af-b2d7-c899a11a825a | note | Test/Inspection Frequency - Each wet area
6f9a24e5-1fdf-589a-a5e3-636478bf997b | note | Inspection: Subcontractor - WS (I)
2b56515e-cb5f-50af-9e8a-0cb87667a866 | note | Inspection: John Holland - PE (S)
b93e8744-eb60-43cc-b6f4-0ced895eba20 | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
9ff264ad-7b1a-5588-8be7-20ea17178676 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
6e64d360-6c59-544c-a28c-b65ff527bff4 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
27a16273-0284-5da2-824e-9d581be54185 | note | Test/ Inspection - Installation and Inspection
77554298-3ff6-5ad6-bb6a-e873adddcdec | note | Test/Inspection Frequency - Each wet area
e0d31f59-aadd-56f9-909f-ce37e131c572 | note | Inspection: Subcontractor - WS (I)
90b6b4f7-00c0-580c-ac34-731f05263758 | note | Inspection: John Holland - PE (S)
757c4c65-646f-502d-a7de-8f021f3fc7b2 | textbox | Records & Comments - Measured fall:
| signoff | AUTHORITY HOLDPOINT
2666ef5e-cf95-460c-ac99-83ddac1acbb4 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
79bfe317-3b2f-546e-bc6b-f5dc7d568ad1 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
f12bc53a-6929-5f5d-84e0-5bab2f48354c | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
8e5b2e9b-f4b9-5abc-87e7-9d5e03dd8622 | note | Test/ Inspection - Measurement
f89588fc-de39-52e8-8a18-7360cded0ffd | note | Test/Inspection Frequency - Each wet area
c1eba538-3d18-5187-8321-0533f090efeb | note | Inspection: Subcontractor - WS (I)
5a9359f3-994b-5135-9d9e-797967732386 | note | Inspection: John Holland - PE (S)
2be213cf-2d02-4723-97b8-f1fc23d44fa6 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
f751970f-6540-57ba-b412-8d2b32672122 | note | Specification Reference - GBA-SPE-AR-AS-0001
ebb244f2-ead3-5244-a116-dc3ad39ceefc | note | Acceptance Criteria - Everything ready to install
7cb8199d-10a8-51f6-b690-5ef87bf733fc | note | Test/ Inspection - Review & Verify
6a20f454-0874-5024-9c2f-57d9a3f1245a | note | Test/Inspection Frequency - Each wet area
4e31e055-551a-58f9-bd57-e136d261e47a | note | Inspection: Subcontractor - WS (I)
14cd3ca7-96e7-5161-a412-6f72a6f22d46 | note | Inspection: John Holland - PE (S)
d85e862b-a381-5224-b140-93cbe102eb65 | textbox | Records & Comments - Temperature Reading:
87bd8b50-8a98-481b-b23c-4939fce47521 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
512f2459-4989-57fd-ad57-d2f7979cf269 | note | Specification Reference - GBA-SPE-AR-AS-0001
ea74eded-b5d6-567b-b59e-7c1908389fc6 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
8bd7ebce-35d3-52b4-ad24-7b42f2548933 | note | Test/ Inspection - Visual Inspection
774528bc-26dc-50f5-afdf-946a3f6af122 | note | Test/Inspection Frequency - Each wet area
8eea14f0-25c6-56af-bfcc-4fb7ee102f22 | note | Inspection: Subcontractor - WS (W)
740e9fd0-54a5-5b05-8024-575c846eb791 | note | Inspection: John Holland - PE (I)
| note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
c33abc46-1121-5322-ab2c-9c844f12f708 | textbox | Applicator Names:
90be6c50-2004-5485-a669-bb1c01f39847 | textbox | Temperature at placement:
867b5da5-6264-4fe9-9a76-772e0570c9b9 | signoff | AUTHORITY HOLDPOINT
35aecec2-4bb0-4d64-abc9-b30cc23777fe | checkpoint | 2.9 - Apply Vulkem 171 Primer in line with MAMS - take photograph of primer container with technical details and photo/video of application
5813fcff-c3fa-515d-8c3b-a671b0b2aaba | note | Specification Reference - GBA-SPE-AR-AS-0001
da34dfa3-7cf3-5726-b03e-3539abb3b1f4 | note | Acceptance Criteria - Vulkem 171 Primer applied
91fb654c-3331-5b92-bc67-2e75291e064b | note | Test/ Inspection - Installation and Inspection
ffbdfd99-9cb3-562b-9786-45557b0c82e4 | note | Test/Inspection Frequency - Each wet area
4d1763be-d098-52a7-b459-7feefd43f296 | note | Inspection: Subcontractor - WS (I)
d8f55d01-8993-5e8c-b7d1-c95c9dced01e | note | Inspection: John Holland - PE (W)
a97bf58e-a112-485f-bc71-1e7dcfd70208 | checkpoint | 2.10 - Apply membrane layers in line with data sheet and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
4727dca9-1b29-5144-9636-2e05a8c1bd9c | note | Specification Reference - GBA-SPE-AR-AS-0001
584bbd90-8cec-55f2-baa5-0778ecd41975 | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
d8f86bb1-b253-56bd-be67-05449cda4fab | note | Test/ Inspection - Installation and Inspection
d4a7e3d7-5260-5106-88e0-52374e408355 | note | Test/Inspection Frequency - Each wet area
39a1f77a-484d-532f-a8e1-420f334a61fa | note | Inspection: Subcontractor - WS (I)
3242926e-197d-572c-8ac5-c34263573b39 | note | Inspection: John Holland - PE (W)
5c3bce6d-2258-4ac0-bf9e-b2c25e9a7551 | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
409eb6fc-ba24-5b12-aef8-22282f640cae | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
6ba4f540-26b5-5a8b-b95e-7444a69dbafe | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
| note | 350R/951NF layer minimum curing/drying times:
| note | 5C - 12C ¦¦ 24 - 72 Hours
| note | 12C - 18C ¦¦ 6 - 24 Hours
| note | 18C - 29C ¦¦ 4 - 6 Hours
| note | 29C ¦¦ 4 Hours
a3662691-c8f7-5906-9555-6e1be417e81a | note | Test/ Inspection - Installation and Inspection
42aebd7c-83be-5abf-8099-f271c2603b2e | note | Test/Inspection Frequency - Each wet area
bbc0a9e4-d3fb-5ad2-b79f-060bef2cb33d | note | Inspection: Subcontractor - WS (H)
40bfb9b5-2cfd-5fef-b5ae-5065c62bcca2 | note | Inspection: John Holland - PE (H)
| note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
3d6cbf6a-eea2-5f3a-8aff-b4874d9ef498 | textbox | Layer 1 time:
191d1bff-9ee8-5aec-bb86-59fe48e5125a | textbox | Layer 2 time:
736b99ac-2a26-42c6-b1bd-b4b70d698769 | signoff | AUTHORITY HOLDPOINT
92a7c8f9-fb03-42a7-9c0a-bf78b6ade0eb | checkpoint | 2.12 - Membrane test - Flood / Electronic Leak Detection / Seam Probe test the area in line with the AMS instruction
a70f3f04-456a-5d95-b94f-733e238a407a | note | Specification Reference - AS3740 cl 4.5.4 / GBA-SPE-AR-AS-0001
8d065204-2c24-5ff0-a5b0-c1deb9514b2f | note | Acceptance Criteria - Flood test - no leakage observed / measured over 24 hours Electronic Leak Detection Test - no points of electrical conduction identified Seam probe test - no seam failures reported
a7ecd370-c4dd-5b17-a9e8-59d1f0816617 | note | Test/ Inspection - Test
17de7e5c-8d1b-5ff3-8bde-ce9ee18d2101 | note | Test/Inspection Frequency - Each wet area
e6b70776-4c08-5d3d-9f41-60edfa017c71 | note | Inspection: Subcontractor - WS (I)
a1f6dff6-3a6d-56fc-a144-a92cea55a68a | note | Inspection: John Holland - PE (W)
48cece36-a294-5706-8e11-9458e20903a6 | note | Inspection: Site Manager - DC (W)
| note | Records & Comments - Pass or Fail
71bc046e-5fa3-509c-9709-59b0f5a5b4c0 | textbox | Observed setting time:
a1fd0bd2-4591-40f4-9b62-d65fc189ca73 | checkpoint | 2.13 - 100% Witness Point: Supervise the follow-on Subcontractor(s) to ensure protection has been applied to membrane.
3b37c4b4-0303-5490-aca7-bfcf22a8b8f0 | note | Specification Reference - GBA-SPE-AR-AS-0001
be089706-55a9-535f-8844-99be51d8eec5 | note | Acceptance Criteria - Each layer applied in line with MAMS requirements - dressed into puddle flange
a9451b4f-d873-5258-a2b7-f767db6fd270 | note | Test/ Inspection - Installation and Inspection
666c3517-b86b-5788-94e5-13539fda90ec | note | Test/Inspection Frequency - Each wet area
8719a4bb-f238-5b31-8e97-b63ac11a8c55 | note | Inspection: Subcontractor - WS (W)
58b90d3b-ce92-5e50-9cfa-a40bd51e9268 | note | Inspection: John Holland - PE (I)
f0f3f7eb-1b9e-408f-8d21-07a6ae596c4e | section | 3 - Close-Out
3f7be114-21b5-4663-9804-7e96ec136e3c | checkpoint | 3.1 - ITP close-out.
39405c20-c8e1-5db9-9c97-9ec5a991f525 | note | Specification Reference - GBA-SPE-AR-AS-0001
64f109d6-c70d-5778-9e73-aa6ea73d3448 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
9cacd09a-dd10-533f-90e3-5d449a776bef | note | Test/Inspection Frequency - Each Lot
f8275ed9-c757-5104-866f-cbf5da065dd1 | note | Inspection: John Holland - QR (R)
| note | Records & Comments - Check all measurements are recorded and photos attached.
6dd754f2-e1cb-5317-932b-29ae8b5f331d | note | All records loaded into the Work Lot System and Verified.