## QA Folder Structure
QA Folder Structure
Allfire Site QA
| Basement 5 |  |  |  | Fire Systems ITP - Basements
| Basement 4 |  |  |  | Fire Systems ITP - Basements
| Basement 3 |  |  |  | Fire Systems ITP - Basements
| Basement 2 |  |  |  | Fire Systems ITP - Basements
| Basement 1 |  |  |  | Fire Systems ITP - Basements
| Ground |  |  |  | Fire Systems ITP - Ground
| Level 1 |  |  |  | Fire Systems ITP - Levels
| Level 2 |  |  |  | Fire Systems ITP - Levels
| Level 3 |  |  |  | Fire Systems ITP - Levels
| Level 4 |  |  |  | Fire Systems ITP - Levels
| Level 5 |  |  |  | Fire Systems ITP - Levels
| Level 6 |  |  |  | Fire Systems ITP - Levels
| Level 7 |  |  |  | Fire Systems ITP - Levels
| Level 8 |  |  |  | Fire Systems ITP - Levels
| Level 9 |  |  |  | Fire Systems ITP - Levels
| Level 10 |  |  |  | Fire Systems ITP - Levels
| Level 11 |  |  |  | Fire Systems ITP - Levels
| Level 12 |  |  |  | Fire Systems ITP - Levels
| Level 13 |  |  |  | Fire Systems ITP - Levels
| Level 14 |  |  |  | Fire Systems ITP - Levels
| Level 15 |  |  |  | Fire Systems ITP - Levels
| Level 16 |  |  |  | Fire Systems ITP - Levels
| Level 17 |  |  |  | Fire Systems ITP - Levels
| Level 18 |  |  |  | Fire Systems ITP - Levels
| Level 19 |  |  |  | Fire Systems ITP - Levels
| Level 20 |  |  |  | Fire Systems ITP - Levels
Safeguard Site QA
Rough In
|  | Basement 5 |  |  | Fire Electrical Rough In
|  | Basement 4 |  |  | Fire Electrical Rough In
|  | Basement 3 |  |  | Fire Electrical Rough In
|  | Basement 2 |  |  | Fire Electrical Rough In
|  | Basement 1 |  |  | Fire Electrical Rough In
|  | Ground |  |  | Fire Electrical Rough In
|  | Level 1 |  |  | Fire Electrical Rough In
|  | Level 2 |  |  | Fire Electrical Rough In
|  | Level 3 |  |  | Fire Electrical Rough In
|  | Level 4 |  |  | Fire Electrical Rough In
|  | Level 5 |  |  | Fire Electrical Rough In
|  | Level 6 |  |  | Fire Electrical Rough In
|  | Level 7 |  |  | Fire Electrical Rough In
|  | Level 8 |  |  | Fire Electrical Rough In
|  | Level 9 |  |  | Fire Electrical Rough In
|  | Level 10 |  |  | Fire Electrical Rough In
|  | Level 11 |  |  | Fire Electrical Rough In
|  | Level 12 |  |  | Fire Electrical Rough In
|  | Level 13 |  |  | Fire Electrical Rough In
|  | Level 14 |  |  | Fire Electrical Rough In
|  | Level 15 |  |  | Fire Electrical Rough In
|  | Level 16 |  |  | Fire Electrical Rough In
|  | Level 17 |  |  | Fire Electrical Rough In
|  | Level 18 |  |  | Fire Electrical Rough In
|  | Level 19 |  |  | Fire Electrical Rough In
|  | Level 20 |  |  | Fire Electrical Rough In
Fit Off
|  | Basement 5 |  |  | Fire Electrical Fit Off
|  | Basement 4 |  |  | Fire Electrical Fit Off
|  | Basement 3 |  |  | Fire Electrical Fit Off
|  | Basement 2 |  |  | Fire Electrical Fit Off
|  | Basement 1 |  |  | Fire Electrical Fit Off
|  | Ground |  |  | Fire Electrical Fit Off
|  | Level 1 |  |  | Fire Electrical Fit Off
|  | Level 2 |  |  | Fire Electrical Fit Off
|  | Level 3 |  |  | Fire Electrical Fit Off
|  | Level 4 |  |  | Fire Electrical Fit Off
|  | Level 5 |  |  | Fire Electrical Fit Off
|  | Level 6 |  |  | Fire Electrical Fit Off
|  | Level 7 |  |  | Fire Electrical Fit Off
|  | Level 8 |  |  | Fire Electrical Fit Off
|  | Level 9 |  |  | Fire Electrical Fit Off
|  | Level 10 |  |  | Fire Electrical Fit Off
|  | Level 11 |  |  | Fire Electrical Fit Off
|  | Level 12 |  |  | Fire Electrical Fit Off
|  | Level 13 |  |  | Fire Electrical Fit Off
|  | Level 14 |  |  | Fire Electrical Fit Off
|  | Level 15 |  |  | Fire Electrical Fit Off
|  | Level 16 |  |  | Fire Electrical Fit Off
|  | Level 17 |  |  | Fire Electrical Fit Off
|  | Level 18 |  |  | Fire Electrical Fit Off
|  | Level 19 |  |  | Fire Electrical Fit Off
|  | Level 20 |  |  | Fire Electrical Fit Off
Pre-Commissioning / Commissioning
Ewis
Basement 5
|  |  |  | Pre-Commissioning | EWIS - Pre-Commissioning
|  |  |  | Commissioning | EWIS - Commissioning
|  |  | Basement 4 |  | AS above
|  |  | Basement 3 |  | AS above
|  |  | Basement 2 |  | AS above
|  |  | Basement 1 |  | AS above
|  |  | Ground |  | AS above
|  |  | Level 1 |  | AS above
|  |  | Level 2 |  | AS above
|  |  | Level 3 |  | AS above
|  |  | Level 4 |  | AS above
|  |  | Level 5 |  | AS above
|  |  | Level 6 |  | AS above
|  |  | Level 7 |  | AS above
|  |  | Level 8 |  | AS above
|  |  | Level 9 |  | AS above
|  |  | Level 10 |  | AS above
|  |  | Level 11 |  | AS above
|  |  | Level 12 |  | AS above
|  |  | Level 13 |  | AS above
|  |  | Level 14 |  | AS above
|  |  | Level 15 |  | AS above
|  |  | Level 16 |  | AS above
|  |  | Level 17 |  | AS above
|  |  | Level 18 |  | AS above
|  |  | Level 19 |  | AS above
|  |  | Level 20 |  | AS above
Fire Detection
Basement 5
|  |  |  | Pre-Commissioning | Fire Detection - Pre-Commissioning
|  |  |  | Commissioning | Fire Detection - Commissioning
|  |  | Basement 4 |  | AS above
|  |  | Basement 3 |  | AS above
|  |  | Basement 2 |  | AS above
|  |  | Basement 1 |  | AS above
|  |  | Ground |  | AS above
|  |  | Level 1 |  | AS above
|  |  | Level 2 |  | AS above
|  |  | Level 3 |  | AS above
|  |  | Level 4 |  | AS above
|  |  | Level 5 |  | AS above
|  |  | Level 6 |  | AS above
|  |  | Level 7 |  | AS above
|  |  | Level 8 |  | AS above
|  |  | Level 9 |  | AS above
|  |  | Level 10 |  | AS above
|  |  | Level 11 |  | AS above
|  |  | Level 12 |  | AS above
|  |  | Level 13 |  | AS above
|  |  | Level 14 |  | AS above
|  |  | Level 15 |  | AS above
|  |  | Level 16 |  | AS above
|  |  | Level 17 |  | AS above
|  |  | Level 18 |  | AS above
|  |  | Level 19 |  | AS above
|  |  | Level 20 |  | AS above
Final Commissioning

## Checklists
type | name | values | prefix | postfix | usage count | user addable
checklist-flat | Fire Systems ITP - Basements
checkpoint | 25% - Exposed Ranges With Sprinklers Installed
checkpoint | 50% - Exposed Ranges With Sprinklers Installed
checkpoint | 75% - Exposed Ranges With Sprinklers Installed
checkpoint | 100% - Exposed Ranges With Sprinklers Installed
checkpoint | Other % (entered below) - Exposed Ranges With Sprinklers Installed - do not pass until 100%
textbox | % Exposed Ranges With Sprinklers Installed |  |  | %
checkpoint | Fire Hose Reels Installed
checkpoint | Rough In Ranges Lift Lobby Ceilings
checkpoint | Fit-off semi-recessed Sprinklers to Ceiling Grid (Lobby)
checkpoint | Fit-off Escutcheon Plates to Ceiling Grid (Lobby)
checkpoint | Sprinkler Control Valves Installed
checkpoint | Hydrostatic Pressure Test 1400KPA (All tests verified by Supervisor/Manager)
checkpoint | North - Combined Hydrant Main Located in Fire Stairs (Temporary Hydrant)
checkpoint | South - Combined Hydrant Main Located in Fire Stairs (Temporary Hydrant)
checkpoint | North - Hydrant & Sprinkler Test Drains Located in Fire Stairs
checkpoint | South - Hydrant & Sprinkler Test Drains Located in Fire Stairs
checkpoint | Passive Fire Completion % entered below - do not pass until 100%
textbox | Passive Fire Completion % |  |  | %
checkpoint | Total Floor Completion % entered below - do not pass until 100%
textbox | Floor Completion % |  |  | %
checkpoint | Floor Completed Sign Off
holdpoint | Sign Off
checklist-flat | Fire Systems ITP - Ground
checkpoint | 25% - Exposed Ranges With Sprinklers Installed
checkpoint | 50% - Exposed Ranges With Sprinklers Installed
checkpoint | 75% - Exposed Ranges With Sprinklers Installed
checkpoint | 100% - Exposed Ranges With Sprinklers Installed
checkpoint | Other % (entered below) - Exposed Ranges With Sprinklers Installed - do not pass until 100%
textbox | % Exposed Ranges With Sprinklers Installed |  |  | %
checkpoint | Fire Hose Reels Installed
checkpoint | Rough In Ranges Lift Lobby Ceilings
checkpoint | Fit-off semi-recessed Sprinklers to Ceiling Grid (Lobby)
checkpoint | Fit-off Escutcheon Plates to Ceiling Grid (Lobby)
checkpoint | Fit-off semi-recessed Sprinklers to Ceiling Grid (Amenities & Other Areas)
checkpoint | Fit-off Escutcheon Plates to Ceiling Grid (Amenities & Other Areas)
checkpoint | Sprinkler Control Valves Installed
checkpoint | Pumps & Tanks installed
checkpoint | Hydrostatic Pressure Test 1400KPA (All tests verified by Supervisor/Manager)
checkpoint | North - Combined Hydrant Main Located in Fire Stairs (Temporary Hydrant)
checkpoint | South - Combined Hydrant Main Located in Fire Stairs (Temporary Hydrant)
checkpoint | North - Hydrant & Sprinkler Test Drains Located in Fire Stairs
checkpoint | South - Hydrant & Sprinkler Test Drains Located in Fire Stairs
checkpoint | Passive Fire Completion % entered below - do not pass until 100%
textbox | Passive Fire Completion % |  |  | %
checkpoint | Total Floor Completion % entered below - do not pass until 100%
textbox | Floor Completion % |  |  | %
checkpoint | Floor Completed Sign Off
holdpoint | Sign Off
checklist-flat | Fire Systems ITP - Levels
checkpoint | 25% - Exposed Ranges With Sprinklers Installed
checkpoint | 50% - Exposed Ranges With Sprinklers Installed
checkpoint | 75% - Exposed Ranges With Sprinklers Installed
checkpoint | 100% - Exposed Ranges With Sprinklers Installed
checkpoint | Other % (entered below) - Exposed Ranges With Sprinklers Installed - do not pass until 100%
textbox | % Exposed Ranges With Sprinklers Installed |  |  | %
checkpoint | Rough In Ranges Lift Lobby Ceilings
checkpoint | Fit-off semi-recessed Sprinklers to Ceiling Grid (Lobby)
checkpoint | Fit-off Escutcheon Plates to Ceiling Grid (Lobby)
checkpoint | Fit-off semi-recessed Sprinklers to Ceiling Grid (Amenities & Other Areas)
checkpoint | Fit-off Escutcheon Plates to Ceiling Grid (Amenities & Other Areas)
checkpoint | Sprinkler Control Valves Installed
checkpoint | Hydrostatic Pressure Test 1400KPA (All tests verified by Supervisor/Manager)
checkpoint | North - Combined Hydrant Main Located in Fire Stairs (Temporary Hydrant)
checkpoint | South - Combined Hydrant Main Located in Fire Stairs (Temporary Hydrant)
checkpoint | North - Hydrant & Sprinkler Test Drains Located in Fire Stairs
checkpoint | South - Hydrant & Sprinkler Test Drains Located in Fire Stairs
checkpoint | Passive Fire Completion % entered below - do not pass until 100%
textbox | Passive Fire Completion % |  |  | %
checkpoint | Total Floor Completion % entered below - do not pass until 100%
textbox | Floor Completion % |  |  | %
checkpoint | Floor Completed Sign Off
holdpoint | Sign Off
checklist-flat | Fire Electrical Rough In
checkpoint | Correct cable used (eg Fire rated as required)
checkpoint | Cable Support
checkpoint | Segregation from other electrical services
checkpoint | Type of cable fixing & spacing
checkpoint | No cable joins between equipment
checkpoint | Conduit type
checkpoint | Conduit fixings
checklist-flat | Fire Electrical Fit Off
checkpoint | Sensor locations as shown on drawings
checkpoint | Warden intercom phone locations
checkpoint | Break glass alarm located as drawings
checkpoint | Hold open devices located as drawings
checkpoint | Interface with Mechanical services
checkpoint | Interface with DDC
checkpoint | Sensors fixed correctly
checkpoint | FIP installed & connected
checkpoint | Connection of system to Tyco for Monitoring
checkpoint | MASDS Panel Fit Off
checkpoint | Strobes
checkpoint | Commissioning completed - includes checking cause & effect
checkpoint | Inspection of system by an independent certifier
checklist-flat | EWIS - Pre-Commissioning
checkpoint | Power Supply
label | Check that power supply is installed as per AS3000
label | Check that permanent power supply is provided and available
checkpoint | Secondary Power Supply
label | Check that batteries are correct for use – size and type
label | Check that connections are correct and terminal connections tight
checkpoint | Speaker wiring
label | Speaker wiring is complete
label | EOL Device for each circuit seen
checkpoint | Installation
label | All cabling complete
label | Speaker install complete
label | Strobe install complete
label | Warden Intercom Point install complete
checkpoint | Documentation
label | Inspection & Test Document complete
checklist-flat | EWIS - Commissioning
checkpoint | Installation
label | Pre Commission Checklist complete
checkpoint | Speaker / Strobe circuits
label | All speaker circuits powered and normal
label | Strobe circuits powered and normal
checkpoint | Sound Levels Recorded
label | Ambient sound levels recorded
label | Alert / Evac sound levels recorded
checkpoint | Operation Testing
label | Check each zone operates off associated detection zone
label | Check cascade sequence
label | Check operation of Warden Intercom Points
checkpoint | Documentation
label | Sound system test recorded
label | Commissioning Documents completed
checklist-flat | Fire Detection - Pre-Commissioning
checkpoint | Power Supply
label | Check that power supply is installed as per AS3000
label | Check that permanent power supply is provided and available
checkpoint | Secondary Power Supply
label | Check that batteries are correct for use – size and type
label | Check that connections are correct and terminal connections tight
checkpoint | Detector and module wiring
label | Alarm wiring is complete
label | Loop wiring is continuous
checkpoint | Installation
label | All cabling complete
label | Detection install complete, spacing correct and type suitable for environment
label | Front entry strobe complete
label | Interface modules installed
checkpoint | Documentation
label | Inspection & Test Document complete
label | Fire Mode Matrix completed
checklist-flat | Fire Detection - Commissioning
checkpoint | Installation
label | Pre-Commission Checklist Complete
checkpoint | Programming of FDCIE
label | All detectors programmed correctly and fault free
label | All Input/Output devices programmed correctly and fault free
label | All modules programmed and functions written as per Fire Matrix
checkpoint | Detector Test
label | All detector dust covers installed
label | All detectors tested and alarm operating correctly
label | All sounders operate with associated smoke detector and reset when smoke clears
label | All signals to FDCIE registered (Interface with Security & BMS Checked)
label | Perform Full Function Fire Test 3.6 Correct signal to MFB initiated
checkpoint | Documentation
label | Detector test results recorded
label | Commissioning Documents completed

## Fire Systems Installation Matri
Fire Systems Installation Progress Matrix
|  | 25% - Exposed Ranges With Sprinklers Installed | 50% - Exposed Ranges With Sprinklers Installed | 75% - Exposed Ranges With Sprinklers Installed | 100% - Exposed Ranges With Sprinklers Installed | Other % (entered below) - Exposed Ranges With Sprinklers Installed - do not pass until 100% | % Exposed Ranges With Sprinklers Installed | Fire Hose Reels Installed | Rough In Ranges Lift Lobby Ceilings | Fit-off semi-recessed Sprinklers to Ceiling Grid (Lobby) | Fit-off Escutcheon Plates to Ceiling Grid (Lobby) | Fit-off semi-recessed Sprinklers to Ceiling Grid (Amenities & Other Areas) | Fit-off Escutcheon Plates to Ceiling Grid (Amenities & Other Areas) | Sprinkler Control Valves Installed | Pumps & Tanks installed | Hydrostatic Pressure Test 1400KPA (All tests verified by Supervisor/Manager) | North - Combined Hydrant Main Located in Fire Stairs (Temporary Hydrant) | South - Combined Hydrant Main Located in Fire Stairs (Temporary Hydrant) | North - Hydrant & Sprinkler Test Drains Located in Fire Stairs | South - Hydrant & Sprinkler Test Drains Located in Fire Stairs | Passive Fire Completion % entered below - do not pass until 100% | Passive Fire Completion % | Total Floor Completion % entered below - do not pass until 100% | Floor Completion % | Floor Completed Sign Off | Sign Off
| Basement 5 | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Text Value | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Text Value | Pass / Fail / N/A | Text Value | Pass / Fail / N/A | Holdpoint
Basement 4
Basement 3
Basement 2
Basement 1
Ground
Level 1
Level 2
Level 3
Level 4
Level 5
Level 6
Level 7
Level 8
Level 9
Level 10
Level 11
Level 12
Level 13
Level 14
Level 15
Level 16
Level 17
Level 18
Level 19
Level 20
25% - Exposed Ranges With Sprinklers Installed
50% - Exposed Ranges With Sprinklers Installed
75% - Exposed Ranges With Sprinklers Installed
100% - Exposed Ranges With Sprinklers Installed
Other % (entered below) - Exposed Ranges With Sprinklers Installed - do not pass until 100%
% Exposed Ranges With Sprinklers Installed
Fire Hose Reels Installed
Rough In Ranges Lift Lobby Ceilings
Fit-off semi-recessed Sprinklers to Ceiling Grid (Lobby)
Fit-off Escutcheon Plates to Ceiling Grid (Lobby)
Fit-off semi-recessed Sprinklers to Ceiling Grid (Amenities & Other Areas)
Fit-off Escutcheon Plates to Ceiling Grid (Amenities & Other Areas)
Sprinkler Control Valves Installed
Pumps & Tanks installed
Hydrostatic Pressure Test 1400KPA (All tests verified by Supervisor/Manager)
North - Combined Hydrant Main Located in Fire Stairs (Temporary Hydrant)
South - Combined Hydrant Main Located in Fire Stairs (Temporary Hydrant)
North - Hydrant & Sprinkler Test Drains Located in Fire Stairs
South - Hydrant & Sprinkler Test Drains Located in Fire Stairs
Total Floor Completion % entered below - do not pass until 100%
Floor Completion %
Floor Completed Sign Off
Sign Off

## Fire Electrical Rough In Progre
Fire Electrical Rough In Progress Matrix
Fire Electrical Rough In
Use this checklist ^^^
|  | Correct cable used (eg Fire rated as required) | Cable Support | Segregation from other electrical services | Type of cable fixing & spacing | No cable joins between equipment | Conduit type | Conduit fixings
| Basement 5 | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A
Basement 4
Basement 3
Basement 2
Basement 1
Ground
Level 1
Level 2
Level 3
Level 4
Level 5
Level 6
Level 7
Level 8
Level 9
Level 10
Level 11
Level 12
Level 13
Level 14
Level 15
Level 16
Level 17
Level 18
Level 19
Level 20

## Fire Electrical Fit Off Progres
Fire Electrical Fit Off Progress Matrix
Fire Electrical Fit Off
Use this checklist ^^^
|  | Sensor locations as shown on drawings | Warden intercom phone locations | Break glass alarm located as drawings | Hold open devices located as drawings | Interface with Mechanical services | Interface with DDC | Sensors fixed correctly | FIP installed & connected | Connection of system to Tyco for Monitoring | MASDS Panel Fit Off | Strobes | Commissioning completed - includes checking cause & effect | Inspection of system by an independent certifier
| Basement 5 | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A | Pass / Fail / N/A
Basement 4
Basement 3
Basement 2
Basement 1
Ground
Level 1
Level 2
Level 3
Level 4
Level 5
Level 6
Level 7
Level 8
Level 9
Level 10
Level 11
Level 12
Level 13
Level 14
Level 15
Level 16
Level 17
Level 18
Level 19
Level 20

## Overall Progress Matrix
Overall Progress Matrix
|  | Fire Systems Installation | Fire Electrical Rough In | Fire Electrical Fit Off
| Basement 5 | Fire Systems ITP - Basements | Fire Electrical Rough In | Fire Electrical Fit Off
| Basement 4 | Fire Systems ITP - Ground | Use this one ^ | Use this one ^
| Basement 3 | Fire Systems ITP - Levels
| Basement 2 | Can we use whichever of these applies? ^^
Basement 1
Ground
Level 1
Level 2
Level 3
Level 4
Level 5
Level 6
Level 7
Level 8
Level 9
Level 10
Level 11
Level 12
Level 13
Level 14
Level 15
Level 16
Level 17
Level 18
Level 19
Level 20