## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | Ceiling | [5 empty] | Ceiling ITP
section | Set out
checkpoint | Reflected ceiling plans current revisions checked and ceiling set out completed as per the current plans
holdpoint | HOLD POINT
section | Construction Generally
checkpoint | Install & fix to prevent looseness or rattling of ceiling components
checkpoint | Install the ceiling to allow for differential movement at abutting surfaces
section | Suspension system
checkpoint | Provide suspension system and workmanship as per supplier installation guides.
checkpoint | Provide additional back support or suspension members to prevent distortion, overloading or excessive vertical deflection.
checkpoint | Ensure that the failure of any one suspension point does not cause a progressive failure of the ceiling.
checkpoint | Where applicable, provide height adjustment with a length adjustment device at each suspension point.
checkpoint | Services: Do not fix to the installed services. Where services obstruct the ceiling supports, provide bridging and suspension on each side of the services.
checkpoint | Uplift: Suspension system and framing to resist uplift.
checkpoint | Tolerances: Flatness, twist, winding and bow: 1.5mm deviation from a 1.5m straightedge places in any position
section | Hold Point
checkpoint | Suspension system completed – Ready for installation of ceiling tiles, lining and panels.
checkpoint | Confirm all service trades are complete & ready for closing in of ceilings.
section | Ceiling Lining
checkpoint | Provide board lining to a finish and workmanship as per supplier installation guides.
checkpoint | Fit accurately and neatly, without distortion and free from air leakage and staining.
checkpoint | Set out patterned or heavily textured materials with a consistent direction of pattern or texture.
checkpoint | Cut ceiling unit edges: conceal, or finish to match prefinished edges.
checkpoint | Multiple sheet layers to fire rated and acoustic rated elements: Fill & flush up all joints on each layer and caulk up perimeters and penetrations before commencing succeeding layers. Stagger all sheet joints by minimum 200mm.
checkpoint | Board joints support: Provide framing parallel to the joint on each side. Do not fix the lining to abutting building surfaces
checkpoint | Flush joints: Provide recessed edge sheets and finish flush using perforated paper reinforcing tape. Locate & position joints to intersect light fixtures, vents or air diffusers.
checkpoint | Tolerances: Suspension system bearing surface for flush lined ceiling to AS/NZS 2589
checkpoint | Levelness: Max tolerance of ±5mm relative to the documented height datum for the ceiling in each room or space.
checkpoint | Trims & accessories: Provide trims at junctions with other building elements and surfaces, including walls, beams and penetrations.
section | Control joints
checkpoint | Align ceiling control joints with the structural control joints. Do not bridge structural control joints.
checkpoint | Provide purpose made PVC control joint beads where documented.
label | Provide framing parallel to the joint on each side.
label | Plasterboard lining: 12m centres
label | Fibre cement lining: 7.2m centres
section | Bulkheads
checkpoint | Integrate bulkheads with the ceiling structure and brace to prevent lateral movement. Where ceiling is terminated at the bulkhead, provide for seismic requirements
section | Acoustic installation
checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge
section | Tolerances
checkpoint | Where documented, place acoustic batts on top of ceilings system and butt to each other and to partitions.
checkpoint | Tightly butt and trim neatly around services items and other items.
section | Smoke baffles and acoustic baffles
checkpoint | Provide approved smoke and acoustic baffles where required
section | Additional checks for fire-protective board lining
checkpoint | Check the fire resistance levels on RCP
checkpoint | Fixings: Direct to concrete elements and to purpose made steel framing
checkpoint | Penetrations: Seal penetrations in the board lining to maintain the integrity of the required fire resistance level including suspended ceiling hangers and suspension systems for services.
checkpoint | Board perimeter: Provide fire sealant and trims at junctions with other building elements and surfaces, including walls, beams and penetrations to maintain the required fire resistance levels.
section | Access panels
checkpoint | Match the access panels to the ceiling in appearance and performance
checkpoint | Provide access panels supported and anchored to permit ready removal and refixing
checkpoint | Provide fire rated and acoustic rated panels where documented or where required to maintain the designated rating of the ceiling element
checklist | Door Frames | [5 empty] | Doors & Frames ITP
section | Take delivery
checkpoint | Frames as per design documents
section | Setout
checkpoint | Ensure Frames are set out as per Setout Plans.
checkpoint | Set out is to be read in conjunction with Door Schedule.
holdpoint | HOLD POINT
section | Execution
checkpoint | Frames are filled in accordance with acoustic or fire requirements where applicable
checkpoint | Frames are plumbed, levelled, straight and within acceptable tolerances
checkpoint | Frames are adequately fixed or anchored to the building structure.
checkpoint | Frames are installed so that they do not carry any building loads
checkpoint | Fire door frame note: Fixings to substrate to be in accordance with manufacturers instructions
checklist | Partitions | [5 empty] | Partitions ITP
section | Set out
checkpoint | Partitions set out plans current revisions checked and wall set out completed as per the current plans
checkpoint | Minimum/critical dimensions (face to face) on drawings checked
holdpoint | HOLD POINT
section | Stud Framing
checkpoint | Base & Head tracks fixed in accordance with steel stud partition design. Typically ≤600mm centres and 100mm from ends
checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 50mm
checkpoint | Stud spacings correct as per steel stud partition design. Noting max 450 centres for wet area sheeting.
checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 50mm
checkpoint | Door frame openings as per Rondo design
checkpoint | Full height partitions: Fix deflection head tracks to the floor slab soffit to allow a minimum deflection capacity of 20mm.
checkpoint | Rotate intermediate studs into tracks for friction fixing
checkpoint | Structural floor control joints: Disconnect partitions over joints with detached double studs and ensure bottom tracks, bracing and top tracks are not fastened across joints
checkpoint | 35 x 35 steel angle installed at internal corners of showers
checkpoint | Stud service holes: Splice additional stiffening to studs if site cut service holes exceed 1/3 the width of the member
checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details
checkpoint | Noggings: Fix noggings as per steel stud design.
checkpoint | Door frames: Installed
section | Bulk Insulation
checkpoint | Install acoustic and thermal insulation.
section | Hold Point
checkpoint | Framing system completed – Ready for installation of sheets.
section | Board Lining
checkpoint | Stagger end joints in a brick pattern and locate them on framing members away from the corners of large openings
checkpoint | Multiple sheet layers: Fill & flush up all joints and fixings in each layer and caulk up perimeters and penetrations before commencing succeeding layers.
checkpoint | Butt joints staggered on adjoining sheets and opposite sides of wall.
checkpoint | Fire rated recess joints staggered on opposite sides of the wall, or backed by steel nogging
checkpoint | Tape & Bead all joints and corners as required
checkpoint | Provide sealants at junctions between partition systems and with other building elements
checkpoint | Provide trim such as beads, moulding and stops to make neat junctions between lining components, finishes and adjacent surfaces
section | Control Joints
checkpoint | Control joints to coincide with structural control joints
checkpoint | Provide control joints as follows:
checkpoint | Plasterboard lined partitions: 12m centres
checkpoint | Fibre-cement board lined partitions: 7.2m centres
checkpoint | Board lined partitions in wet areas: To suit joints required in tiling and at max 4.2m centres
section | Tolerances
checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge
section | Additional checks for Fire Walls
checkpoint | Installed as per board suppliers design & install specification
checkpoint | Correct FRL achieved
checkpoint | Perimeter fire rated sealant completed.
checkpoint | All penetrations through fire walls below and above ceiling protected/sealed – Service penetrations sealing by others
checkpoint | Fire door frames installed
section | Additional Checks for Smoke Walls
checkpoint | Deflection heads and all joints sealed, taped and set (Sealant is approved prior)
checkpoint | All penetrations through smoke walls below and above ceiling protected/sealed
section | Additional Checks for Acoustic Walls
checkpoint | Deflection heads and all joints sealed, taped and set (Sealant is approved prior)
checkpoint | All penetrations through acoustic walls below and above ceiling protected/sealed
section | Access panels
checkpoint | Installed with consideration for required acoustic, smoke & fire rating.
checklist | Speedpanel | [5 empty] | Speedpanel ITP
section | Prior to Commencement – The following documentation are completed and approved
checkpoint | Samples and prototypes submitted and approved (Fire sealants approved)
section | Set out
checkpoint | Speedpanel walls set out plans current revisions checked and wall set out completed as per the current plans
holdpoint | HOLD POINT
section | Framing & Speed Panel
checkpoint | Powder coated speedpanel used where required
checkpoint | Fix tracks to floor & soffit per manual
checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details.
checkpoint | Ensure that the configuration is as per the Speedpanel site specific detailing.
checkpoint | Ensure that all caulking is as per the Speedpanel site specific detail.
checkpoint | Ensure openings are as per the specified jamb & door sizing.
checkpoint | Door frames: Installed
section | Tolerances
checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge.
section | Penetrations/Access panels
checkpoint | Installed as per Speedpanel design & install specification.
checkpoint | Correct FRL achieved.
checklist | Soffit Insulation | [5 empty] | Underslab Insulation ITP
section | SWMS
checkpoint | Swms are Approved Prior to Commencement
holdpoint | HOLD POINT
section | Sample Approval
checkpoint | Sample Submission approved via Aconex
holdpoint | HOLD POINT
section | Take delivery
checkpoint | Insulation panels arrive as per Design Documents and defect free.
section | Setout
checkpoint | Ensure most up to date drawings are being utilised
section | Execution
checkpoint | Mechanically fix panels to Manufacturers Specifications
checkpoint | Tape all joints and exposed edges with a minimum of 75mm wide silver tape
section | Completion
checkpoint | Lend Lease to Sign off on completed area