## Project Structure
Folder Structure |  |  |  |  | Checklists
Cleanaway - Rooty Hill
ITP Setout
SITE QA
| Fans / CU | Smoke Spill Fans | SEF - 1 | Roof Mounted Smoke Spill Fan ITP
|  |  | SEF - 2 | Roof Mounted Smoke Spill Fan ITP
|  |  | SEF - 3 | Roof Mounted Smoke Spill Fan ITP
|  |  | SEF - 4 | Roof Mounted Smoke Spill Fan ITP
|  |  | SEF - 5 | Roof Mounted Smoke Spill Fan ITP
|  |  | SEF - 6 | Roof Mounted Smoke Spill Fan ITP
|  |  | SEF - 7 | Roof Mounted Smoke Spill Fan ITP
|  |  | SEF - 8 | Roof Mounted Smoke Spill Fan ITP
|  |  | SEF - 9 | Roof Mounted Smoke Spill Fan ITP
|  | Outside Air Fans | OAF - 1 | Roof Mounted Fan ITP
|  |  | OAF - 2 | Inline Mixed Flow Fan ITP
|  | Toilet Exhaust Fans | TEF - 1 | Roof Mounted Fan ITP
|  |  | TEF - 2 | Inline Mixed Flow Fan ITP
|  | VRF Condensing Units | CU - 1 | Roof Platform Mounted CU - ITP
|  |  | CU - 2 | Roof Platform Mounted CU - ITP
| Air Conditioning Units | Wall Mounted Split System | ACU - 3 | AC Split System ITP
|  |  | ACU - 4 | AC Split System ITP
|  |  | ACU - 5 | AC Split System ITP
|  |  | ACU - 6 | AC Cassette System ITP
| VRF Branch Unit | Ceiling Mounted VRF Branch Units | BSU-1.1 | VRF Branch Unit ITP
|  |  | BSU-2.1 | VRF Branch Unit ITP
|  |  | BSU-2.2 | VRF Branch Unit ITP
| VRF Fan Coil Units | Ceiling Mounted Ducted Fan Coil | FCU-1.1 | Ducted Fan Coil Unit ITP
|  |  | FCU-1.2 | Ducted Fan Coil Unit ITP
|  |  | FCU-1.3 | Ducted Fan Coil Unit ITP
|  |  | FCU-1.4 | Ducted Fan Coil Unit ITP
|  |  | FCU-1.5 | Ducted Fan Coil Unit ITP
|  |  | FCU-1.6 | Ducted Fan Coil Unit ITP
|  |  | FCU-2.1 | Ducted Fan Coil Unit ITP
|  |  | FCU-2.2 | Ducted Fan Coil Unit ITP
|  |  | FCU-2.3 | Ducted Fan Coil Unit ITP
|  |  | FCU-2.4 | Ducted Fan Coil Unit ITP
|  |  | FCU-2.5 | Ducted Fan Coil Unit ITP
Fire Stopping |  |  |  | Ability to Add
Site Diary |  |  |  | Ability to Add

## Checklists
type | name | values
checklist | Roof Mounted Smoke Spill Fan ITP
section | General
checkpoint | Location Mark out Complete
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
checkpoint | Roof Penetration and Under flashing provided by others - Is correct and usable
checkpoint | Roof under mesh cut out and duct sleeve installed - sheet metal cover installed
checkpoint | Roof is cleared of all debris prior to Helicopter lift (by others)
checkpoint | Correct Fan Installed
checkpoint | Fan installed for correct direction of Air Flow
section | Sealing to roof penetration
checkpoint | Dropper Installed with mesh
checkpoint | Over flashing Installed
checkpoint | All flashing is sealed to stop water leaks
checkpoint | Electrical penetration is sealed
checkpoint | Maglocks in place
checkpoint | Provision for Access
section | Electrical
checkpoint | Electrical terminations - all terminations complete
checkpoint | Equipment Isolator - installed and correctly labelled
checkpoint | Lock Fitted to Isolator
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Roof Mounted O/A Fan
section | General
checkpoint | Location Mark out Complete
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
checkpoint | Roof under mesh cut out and duct sleeve installed - sheet metal cover installed
checkpoint | Roof is cleared of all debris prior to Helicopter lift (by others)
checkpoint | Correct Fan Installed
checkpoint | Fan installed for correct direction of Air Flow
section | Sealing to roof penetration
checkpoint | Over flashing Installed
checkpoint | All flashing is sealed to stop water leaks
checkpoint | Electrical penetration is sealed
checkpoint | Provision for Access
section | Ductwork
checkpoint | Flex connection to duct work
checkpoint | Duct work installed with clearance from other services
checkpoint | Duct work adequately supported
checkpoint | Duct work sealed through walls
checkpoint | Flex installed and adequately supported (Gutter Guard)
checkpoint | Provision for Access
checkpoint | Grills installed
section | Electrical
checkpoint | Electrical terminations - all terminations complete
checkpoint | Equipment Isolator - installed and correctly labelled
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Inline O/A Fan
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
checkpoint | Correct Fan Installed
checkpoint | Fan installed for correct direction of Air Flow
section | Sealing to penetration
checkpoint | Penetration Ready for Plenum Box and Louvre fit off
checkpoint | All flashing is sealed to stop water leaks
checkpoint | Provision for Access
section | Ductwork
checkpoint | Flex connection to duct work
checkpoint | Duct work installed with clearance from other services
checkpoint | Fan installed with anti-vibration mounts.
checkpoint | Duct work adequately supported
checkpoint | Duct work sealed through walls
checkpoint | Flex installed and adequately supported (Gutter Guard)
checkpoint | Provision for Access
checkpoint | Grills installed
section | Electrical
checkpoint | Electrical terminations - all terminations complete
checkpoint | Equipment Isolator - installed and correctly labelled
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Roof Mounted TEF
section | General
checkpoint | Location Mark out Complete
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
checkpoint | Roof under mesh cut out and duct sleeve installed - sheet metal cover installed
checkpoint | Roof is cleared of all debris prior to Helicopter lift (by others)
checkpoint | Correct Fan Installed
checkpoint | Fan installed for correct direction of Air Flow
checkpoint | Anti Vibration Mounts Installed
checkpoint | Access Panel Marked Out
section | Sealing to roof penetration
checkpoint | Over flashing Installed
checkpoint | All flashing is sealed to stop water leaks
checkpoint | Electrical penetration is sealed
checkpoint | Provision for Access
section | Ductwork
checkpoint | Flex Duct installed with clearance from other services
checkpoint | Flex duct adequately supported (Gutter Guard)
checkpoint | Plenum Box sealed to wall
checkpoint | Grille installed
checkpoint | Louvre installed
checkpoint | Access Panel installed (by others)
section | Electrical
checkpoint | Electrical terminations - all terminations complete
checkpoint | Equipment Isolator - installed and correctly labelled
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Inline Mounted TEF
General
checkpoint | Location Mark out Complete - Roof Penetration
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
checkpoint | Correct Fan Installed
checkpoint | Fan installed for correct direction of Air Flow
checkpoint | Anti Vibration Mounts Installed
checkpoint | Access Panel Marked Out
section | Sealing to roof penetration
checkpoint | All metal duct supported vertical and horizontal
checkpoint | Over flashing Installed
checkpoint | All flashing is sealed to stop water leaks
checkpoint | Electrical penetration is sealed
checkpoint | Provision for Access
section | Ductwork
checkpoint | Flex Duct installed with clearance from other services
checkpoint | Flex duct adequately supported (Gutter Guard)
checkpoint | Plenum Box sealed to wall
checkpoint | Grills installed
checkpoint | Louvre installed
checkpoint | Access Panel installed (by others)
section | Electrical
checkpoint | Electrical terminations - all terminations complete
checkpoint | Equipment Isolator - installed and correctly labelled
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Roof Platform Mounted CU
section | General
Checkpoint | Roof Platform Installed (by others)
checkpoint | Roof Platform properly secured to roof sheeting (by others)
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
section | Pipework
checkpoint | Pipework Penetrations Ready
checkpoint | All pipework insulated (glued joints)
checkpoint | All pipework supported on platform
checkpoint | Pipework Covers in place
Checkpoint | Penetration is sealed to prevent water ingress to roof
section | Condenser Unit Placement
checkpoint | Correct Condenser installed
checkpoint | Condenser mounts/anti vibration mounts installed
section | Electrical
checkpoint | Electrical power supply by others
checkpoint | Isolator installed adjacent to condenser by others
checkpoint | Power Available
section | Commissioning
Checkpoint | Pipe lengths confirmed by WAA representative
checkpoint | System pressure tested for 48 hours - 3500 KPA
checkpoint | System evacuated
checkpoint | Additional refrigerant charge
checkpoint | System test run on Cooling cycle and Heating cycle (minimum 2 hours each)
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | VRF Branch Units
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
section | Pipework
checkpoint | All pipework insulated (glued joints)
checkpoint | All pipework Supported and Correct (each port to correct VRF Fan Coil)
section | Drain to Tundish
checkpoint | All horizontal drain runs insulated
checkpoint | Tundish available
checkpoint | Drain terminated to tundish
checkpoint | Drain tested to tundish - min 5l
section | Electrical
checkpoint | Electrical power supply
checkpoint | Each Fan Coil wired to VRF Branch Unit
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Ducted AC System ITP
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
section | Pipework
checkpoint | Pipework rough in complete (FCU to VRF Branch Unit)
checkpoint | All refrigeration pipework insulated
checkpoint | All refrigeration pipework lengths confirmed by WAA representative
section | Fan Coil Unit
checkpoint | Correct Fan Coil Installed
checkpoint | R/A Plenum with filters installed
checkpoint | Anti Vibration mounts fitted to FCU and R/A plenum
checkpoint | Supply Air plenum installed with flex connection
checkpoint | R/A and S/A connections lagged
checkpoint | Drain rough in from FCU to tundish point - horizontal runs insulated
text | Number of filters
section | Duct Work
checkpoint | Duct work installed with clearance from other services
checkpoint | Duct work adequately supported
checkpoint | Duct work sealed through walls
checkpoint | Dampers 100% open
checkpoint | Flex installed and adequately supported (with Gutter guard)
checkpoint | Ready for ceiling sheeting
checkpoint | Access panel installed (by others)
checkpoint | Grilles installed
section | Electrical
checkpoint | Electrical interconnect and Outside Air Fan roughed in
checkpoint | Wall Controller roughed in
checkpoint | Fan coil and condenser terminations complete
checkpoint | Wall controller installed
checkpoint | Electrical supply roughed in by others
checkpoint | Isolator installed adjacent to condenser by others
checkpoint | Power available
section | Commissioning
checkpoint | Drain terminated to tundish
checkpoint | Units correctly addressed
checkpoint | Air Balance Completed
checkpoint | System test run on Cooling cycle and Heating cycle (minimum 4 hours each)
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | AC Split System ITP
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
section | Pipework
checkpoint | Pipework rough in complete
checkpoint | Drain rough in - Pressure Pipe - Green Glue
checkpoint | Drain Test - min 1L
section | Fan Coil Unit
checkpoint | Correct Fan Coil Installed
checkpoint | Drain terminated to tundish
section | Electrical
checkpoint | Electrical interconnect roughed in
checkpoint | Fan coil and condenser terminations complete
checkpoint | Wall controller roughed in.
checkpoint | Wall controller/remote installed.
checkpoint | Electrical supply roughed in by others
checkpoint | Isolator installed adjacent to condenser by others
checkpoint | Power available
section | Condenser
checkpoint | Floor and Wall finishes complete. Tundish complete
checkpoint | Plinth or Platform complete (by Others)
checkpoint | Correct Condenser installed
checkpoint | Condenser mounts installed
checkpoint | Drain terminated to tundish
checkpoint | System pressure tested for 24 hours - 3500 KPA
checkpoint | System evacuated
checkpoint | System test run on Cooling cycle and Heating cycle (minimum 2 hours each)
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | AC Cassette System ITP
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
section | Pipework
checkpoint | Pipework rough in complete
checkpoint | Drain rough in - Pressure Pipe - Green Glue
checkpoint | Drain Test - min 1L
section | Fan Coil Unit
checkpoint | Correct Fan Coil Installed
checkpoint | Cassette system has adequate support
checkpoint | Drain terminated to tundish
checkpoint | Unit fascia installed.
section | Electrical
checkpoint | Electrical interconnect roughed in
checkpoint | Fan coil and condenser terminations complete
checkpoint | Wall controller roughed in
checkpoint | Wall controller installed.
checkpoint | Electrical supply roughed in by others
checkpoint | Power available
section | Condenser
checkpoint | Floor and Wall finishes complete. Tundish complete
checkpoint | Plinth or Platform complete (by Others)
checkpoint | Correct Condenser installed
checkpoint | Condenser mounts installed
checkpoint | Drain terminated to tundish
checkpoint | Isolator installed adjacent to condenser by others
checkpoint | System pressure tested for 24 hours - 3500 KPA
checkpoint | System evacuated
checkpoint | System test run on Cooling cycle and Heating cycle (minimum 2 hours each)
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Fire Penetration
checkpoint | Fire Penetration labelled & caulked in accordance with AS 4072.1 Drawing Reference No AO101
checklist | Site Diary
checkpoint | Areas of work accessible for the day
text | Number of workers on site
text | HSR on site today enter name
text | First Aider on site today enter name
text | Injury on site today enter name
checkpoint | Work area - Take a photo & add a comment