## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | SF15-ITPCL-Sprinkler Installation-DAFP-04 | itp |  |  |  |  | SF15-ITPCL-Sprinkler Installation-DAFP-04
section | 1. ROUGH IN
checkpoint | Pipework installed as per approved workshop drawing
checkpoint | Correct pipe sizes as per drawing
checkpoint | Correct type, temperature sprinklers installed
checkpoint | Pipework supports to AS 2118.9
checkpoint | Sleeves and fire stop material to penetrations (where specified)
checkpoint | Ok to proceed with blockwork and stud framing
date | Date:
textbox | DA Initials:
checkpoint-no-status | Hydrostatic Pressure Test:
textbox | Start Pressure: |  |  | kPa
textbox | Time:
textbox | Client Initials:
textbox | DA Initials:
label
textbox | Finish Pressure: |  |  | kPa
textbox | Time:
textbox | Client Initials:
textbox | DA Initials:
section | 2. FIT-OFF
checkpoint | Sprinkler location to approved workshop drawing
checkpoint | Sprinkler spacing to AS2118
checkpoint | Correct type, temperature sprinklers installed
checkpoint | Ok to proceed with sheeting ceilings
checkpoint-no-status | Hydrostatic Pressure Test:
textbox | Start Pressure: |  |  | kPa
textbox | Time:
textbox | Client Initials:
textbox | DA Initials:
label
textbox | Finish Pressure: |  |  | kPa
textbox | Time:
textbox | Client Initials:
textbox | DA Initials:
section | NATURE OF INSPECTION
checkpoint | Escutcheon plates installed and flush
checkpoint | Shields/guards below 2100 provided (where specified)
checkpoint | Exposed pipework painted (where specified)
checkpoint | Distance below slab to AS2118.1
checkpoint | Deep fat fryer(s) and associated duct protected to AS2118.1
checkpoint | Concealed space protection to AS2118.1
checkpoint | Sprinkler under ducts/obstructions to AS2118.1
checkpoint | Sprinkler inside A/C units to AS2118.1
holdpoint | Signed:
checklist | SF16-ITPCL-Sprinkler & Hydrant Commissioning-08 | itp |  |  |  |  | SF16-ITPCL-Sprinkler & Hydrant Commissioning-08
section | 1. TOWNS MAIN WATER SUPPLY
checkpoint | Street stop valve visible and in order
checkpoint | Fire Brigade Suction Booster complies to AS2419.1
checkpoint | If mains type booster, associated stop valve are monitored, chained & padlocked
checkpoint | Backflow preventor padlocked open
checkpoint | Block Plan and Pressure Limitations notice installed
checkpoint | Emergency instructions specific to job installed
section | 2. WATER STORAGE TANK
checkpoint | Tank construction & installation satisfactory
checkpoint | Water supply to tank chained and padlocked
checkpoint | Freeboard & overflow provisions satisfactory
checkpoint | Ball/Float inlet valve set correctly for correct free board
checkpoint | High/low level alarms tested and working
checkpoint | Tank full and indication working
checkpoint | Tank overflow provisions satisfactory
checkpoint | Access ladders satisfactory
section | 3. ELECTRIC PUMP SET (AS2941)
checkpoint | Pump frame bolted to plinth
checkpoint | Pipe supported satisfactory
checkpoint | Controller to AS 2941 & sufficient door clearance
checkpoint | Liquid filled pressure gauges 2500 kPa at each discharge
checkpoint | Suction gauge -100/1600 kPa from TM and/or -100 to 250 kPa compound gauge from tank installed
checkpoint | PRV connected to open drain or re-circulation valve installed
checkpoint | Complying pressure switch arrangement with by-pass
checkpoint | Pressure switch wired correctly for drop in pressure
checkpoint | Pump start setting labelled on pressure switch
checkpoint | Gland drain installed to floor drain or pit or mechanical seal
section | 4. DIESEL POWERED PUMP SET (AS2941)
checkpoint | Pump frame bolted to plinth
checkpoint | Gland drain installed to floor drain or pit or mechanical seal
checkpoint | Pipe supported satisfactory
checkpoint | Pump start setting labelled on pressure switch
checkpoint | Controller to AS 2941
checkpoint | Liquid filled Pressure Gauges 2500 kPa with sufficient door clearance at each pump discharge
checkpoint | Suction gauge -100/1600 kPa from TM and/or -100 to 250 kPa compound gauge from tank
checkpoint | Suction and delivery vibrations bellows (if required by client) or engine on rubber mounts
checkpoint | Starter panel clear of all alarm faults
checkpoint | Exhaust pipe lagged up to 2Metres
checkpoint | Condensate drains installed on exhaust
checkpoint | Suction and delivery isolating valves monitored
checkpoint | Water-cooled with closed primary loop to open drain
label | Note: Air or radiator cooled not acceptable unless room ventilation engineered
checkpoint | Engine Stop mechanism satisfactory
checkpoint | Diesel fuel tank full
checkpoint | Complying pressure switch arrangement with bypass
checkpoint | Pressure switches wired correctly
checkpoint | PRV installed & connected to drain satisfactory (unless overspeed controller installed)
checkpoint | Modulating relief valve installed
section | 5. JACKING PUMP
checkpoint | Pump automatic start/stop operational
checkpoint | Pump sufficiently sized to provide suitable margins between jacking pump, electric pump, and diesel pump cut-in pressures
checkpoint | Pump power supply independent of main fire pumps
checkpoint | Pump check valve upstream of on/off pressure switch (automatic)
checkpoint | Manual override (inching button) provided
section | 6. INSTALLATION RISERS
checkpoint | Sprinkler / Floor Isolating Valves monitored and accessible
checkpoint | Flow switches accessible and not installed under pipe
checkpoint | Flow switch drains and solenoid valves installed correctly
checkpoint | Ring Main Isolating Valves installed accessible and monitored
checkpoint | Carpark, ground, and podium floor Hose Reels on metered domestic supply
checkpoint | Fire rating of penetrations satisfactory and complete
section | 7. VALVE ROOM
checkpoint | SSVI plate installed
checkpoint | Room Clean and free of debris
checkpoint | Sprinkler system pressure tested
checkpoint | DN15 test valve and DN 50 min. waste valve installed? (Note: Annubar test valve may double as waste valve if suitably located and labelled
checkpoint | Alarm Gong tested
checkpoint | Alarm line orifice drain installed
checkpoint | Isolating valve locked in correct position ie. Alarm gong, pressure switch
checkpoint | Pipework painted (red for pressurised, black for drain)
checkpoint | Check valve installed above alarm gong isolating valve (if no orifice drain)
checkpoint | Lock, straps, signage & labels
checkpoint | Block plan installed
checkpoint | Spare box installed and filled
checkpoint | D A Fire Service stickers fitted on FIPs, alarm valves, pump starters & spare box
checkpoint | Anubar installed correctly (9 diameters before, 3 after)
checkpoint | Anubar flow test complete
checkpoint | Anubar pipe opening fitted centrally above open drain hole
section | 8. GENERAL
checkpoint | Test ASE and get certificate of completion from Romteck (or similar)
checkpoint | O & M manual submitted
checkpoint | ‘As built’ drawings submitted
checkpoint | operation of ALL flow switches received on fire indicator panel
checkpoint | Sprinkler installation ITP complete (SF15)
checkpoint | Fire alarm interfacing ITP complete (SF17)
checkpoint | Hose Reel and Hydrant installation ITPCL complete (SF38)
holdpoint | Signed:
checklist | SF17-ITPLC-Fire Alarm-06 | itp |  |  |  |  | SF17-ITPLC-Fire Alarm-06
section | 1. Rough In
checkpoint | Approved workshop drawings
checkpoint | Wirings suitably fixed
checkpoint | Correct type of wiring installed
checkpoint | Correct type of wiring fixing installed
checkpoint | Fire stop material to penetrations (where specified)
checkpoint | In slab conduits inspected and acceptable before pour
checkpoint | Ok to proceed with sheeting ceilings
section | 2. Fit-off
checkpoint | Locations to approved workshop drawing
checkpoint | Approved type of detector installed
checkpoint | Detectors suitably fixed
checkpoint | Addressable detectors numbered
section | 3. Panels
checkpoint | FIP in correct location
checkpoint | Labelling complete.
checkpoint | Battery type and capacity correct
checkpoint | ASE monitoring equipment installed and connected
checkpoint | FIP manual inside FIP
checkpoint | Repeater mimic panel installed
checkpoint | Alarm bell installed and working
section | 4. Commissioning
checkpoint | ITP checklist fire alarm installation complete
checkpoint | ITP checklist for commission of fire alarm interfacing complete
checkpoint | Block plan installed
checkpoint | As built drawings supplied
checkpoint | O & M manual supplied
holdpoint | Signed:
checklist | SF39-ITPCL-EWIS-OWS-03 | itp |  |  |  |  | SF39-ITPCL-EWIS-OWS-03
section | 1. Rough In
checkpoint | Approved workshop drawings
checkpoint | Wirings suitably fixed
checkpoint | Correct type of wiring installed
checkpoint | Correct type of wiring fixing installed
checkpoint | Fire stop material to penetrations (where specified)
checkpoint | In slab conduits inspected and acceptable before pour
checkpoint | Ok to proceed with sheeting ceilings
section | 2. Fit-off
checkpoint | Locations to approved workshop drawing
checkpoint | Approved type of speaker installed
checkpoint | Speakers suitably fixed
section | 3. Panels
checkpoint | EWIS/OWS in correct location
checkpoint | Labelling complete.
checkpoint | Battery type and capacity correct
checkpoint | EWIS/OWS manual inside EWIS/OWS panel
section | 4. Accessories
checkpoint | WIP location and labelling
checkpoint | BGA location and correct type
checkpoint | Strobe lights and sounders working (where specified)
section | 5. Commissioning
checkpoint | Operation of EWIS/OWS from FIP
checkpoint | ITP for fire alarm interfacing complete
holdpoint | Signed: