## Table 1
Inspection and Test Plan
Contract:
Customer: | [5 empty] | Neoen / Tesla
ITP Title: | [5 empty] | Pavement Base Layer
ITP Number: | [5 empty] | 3200-0706-ITP-CE-003
Current Revision: | [5 empty] | A
Current Revision Date: | [5 empty] | 2024-12-11
Status: | [5 empty] | Draft
Lot Number / Area
Lot Description
ITP Approval
Workflow |  |  | Name | [6 empty] | Title / Position | [9 empty] | Signature |  |  |  | Date
Prepared by: |  |  | Edwin Mendoza | [6 empty] | Senior Civil Project Engineer | [13 empty] | 2024-01-10
Reviewed by: |  |  | Edwin Mendoza | [6 empty] | Senior Civil Project Engineer | [13 empty] | 2024-01-10
Reviewed by: |  |  | Mehdi Farahmand | [6 empty] | QA/QS Lead | [13 empty] | 2024-01-10
Approved by: |  |  | Matthew Sultana | [6 empty] | Site / Construction / Project Manager | [13 empty] | 2024-07-11
Revision History
Date |  |  |  |  | Revision Number | [5 empty] | Revision Details
2024-12-11 |  |  |  |  | A | [5 empty] | First draft issued for review / comment
Title: Inspection and Test Plan- Pavement Base Layer ID: UGLMS-4-987 Version: 8.0 Date Published: 13/06/2024 UGL Governance System - Uncontrolled Document when Printed
ITP Number: |  |  |  | 3200-0706-ITP-CE-003 | [17 empty] | ITP Title: |  |  |  | Pavement Base Layer
Contact Details | [8 empty] | Summary of Requirements | [12 empty] | Principal Codes / Standards | [5 empty] | Records
Customer: |  |  |  | Neoen/ Tesla |  |  |  |  | Process Qualifications: Installation of pavement base layer i.e., spreading, compaction and testing. | [12 empty] |  AS1289 - Methods of testing soils for engineering purposes  AS3798 - Guidelines on earthworks for commercial and residential developments  MRTS04 General Earthworks  MRTS05 Unbound Pavements | [5 empty] | (MDR Insert as marked )
Operations Mgr: |  |  |  | Mark Groth | [23 empty] | Inspect Release Cert
Project Engineer: |  |  |  | Edwin Mendoza | [23 empty] | Deviations/Concessions
Quality Rep: |  |  |  | Mehdi Farahmand | [23 empty] | Material Certificates
Subcontractors | [8 empty] | Traceability: | [18 empty] | Conformance Certificate
Design: |  |  |  | UGL Engineering |  |  |  |  | Material | [5 empty] | Alloy Verification: | [12 empty] | Welding Records
Drafting: |  |  |  | UGL Engineering |  |  |  |  | Heat Treatment | [5 empty] | Pressure Testing: | [12 empty] | Welder Qual. Register
Subcontractor: |  |  |  | Western Down Civil |  |  |  |  | Consumable: | [5 empty] | NDT | [12 empty] | NDT Reports
[9 empty] | Welder ID: | [5 empty] | WPS | [6 empty] | Client Specifications | [5 empty] | Report on Repairs
[9 empty] | Electrical: | [5 empty] | Instrumentation | [6 empty] | N/A | [5 empty] | Heat Treatment Records
Dimensional Records
Surveillance / Inspection Key | [8 empty] | Heat Treatment: | [12 empty] | UGL Procedures/ WI’s | [5 empty] | Non-Conformance Rpts
HOLD POINT (H): Nominated point beyond which work shall not proceed without verified acceptance by nominee | [21 empty] |  3200-0706-PLN-001- QMP  3200-0706-PLN-004 -ERP  3200-0706-PLN-005- CEMP  0706-C-DRG-0001 Cover Sheet and Drawing List  0706-C-DRG-0002 General Notes  0706-C-DRG-0003 General Arrangement and Set Out Plan  0706-C-DRG-0004 Bulk Earthworks Plan  0706-C-DRG-0006 Earthworks Sections Sheet 1 of 2  0706-C-DRG-0007 Earthworks Sections Sheet 2 of 2  0706-C-DRG-0008 Finished Grading Sheet 1 and 2  0706-C-DRG-0009 Pavement Plan  0706-C-DRG-0011 Earthworks Sections and Details  0706-C-DRG-0012 Erosion and Sedimentation Control Plan Construction Stage  0706-C-DRG-0013 Erosion and Sedimentation Control Plan Completion  0706-C-DRG-0014 Erosion and Sediment Control Details  0706-C-DRG-0015 Drainage Details Sheet 1 and Sheet  3200-0706-ITC-CE-002 Pavement Subbase Layer | [5 empty] | Pressure Test Records
[9 empty] | Dimensional Control: | [18 empty] | Drawing & Data Sheets
Misc Verification Records
WITNESS POINT (W): Points at which the nominee shall be notified and invited to witness an activity but further work may proceed without the presence of the nominee. | [8 empty] | Testing (NDT): | [18 empty] | Electrical Test Sheets
Position
[9 empty] | Acceptance Specification: | [18 empty] | Operations Manager |  |  | OM
REVIEW (R): Verify by examination of documentary evidence that inspection / tests have been satisfactorily conducted. | [27 empty] | Project Engineer |  |  | PE
[9 empty] | Pressure Testing: | [18 empty] | Quality Representative |  |  | QR
[28 empty] | Pre-Processing |  |  | PP
SURVEILLANCE (S): Continuing evaluation of the status of methods, analysis of records and monitoring of activities on a random basis to ensure quality of requirements will be met. | [8 empty] | Elect. / Instrumentation: | [18 empty] | Technician |  |  | T
[28 empty] | Welding Supervisor |  |  | WS
[9 empty] | Notes: All sampling and testing for earthworks, pavement and concrete shall be taken by a NATA accredited laboratory. | [18 empty] | Workshop Foreman |  |  | WF
VISUAL (V): 100% Visual inspection of work / item to ensure compliance with code / spec | [27 empty] | Document Controller |  |  | DC
[28 empty] | Store Person |  |  | SP
DIMENSIONAL (D): Measurement of critical dimensions to ensure work/item is within tolerance | [27 empty] | Subcontractor |  |  | SC
[28 empty] | Elect. / Instrumentation |  |  | E/I
ITP Number: |  |  |  | 3200-0706-ITP-CE-003 | [18 empty] | ITP Title: |  |  |  | Pavement Base Layer
ITEM NO.: | PROCESS ACTIVITY |  |  |  | PROCEDURE / INSTRUCTION | [6 empty] | ACCEPTANCE CRITERIA | [5 empty] | RELEVANT SECTION |  |  |  |  | VERIFYING DOCUMENT |  |  | VERIFICATION (SIGN & DATE) |  |  |  | REMARKS
[26 empty] | S/C | UGL |  | Client
STAGE 1: PREPARATION WORKS
1.1 | Permits and Approvals |  |  |  | Ensure Permits are in place including, but not limited to:  Excavation Permits | [6 empty] | NA | [5 empty] | NA |  |  |  |  | NA
1.2 | CEMP and Emergency Response Plans |  |  |  | Controls established within CEMP and ERP shall be adhered to throughout works. | [6 empty] | 3200-0706-PLN-005 – CEMP 3200-0706-PLN-010 - ERP | [5 empty] | 0706-C-DRG-0012 0706-C-DRG-0013 Erosion and Sedimentation Control Plan |  |  |  |  | Site Audits as works progress. |  |  | R | R |  | S
1.3 | Identification of underground services |  |  |  | Use of DBYD and pothole to positively identify underground services. Use progress As-Constructed drawings for installed buried cables | [6 empty] | NA | [5 empty] | UGL Safety Critical Risk Control – Excavation and Trenching |  |  |  |  | DBYD / Excavation Permit Survey (if required). |  |  | H | H |  | S
1.4 | Approval of Subcontractor SWMS |  |  |  | Submission, review, and approval of all subcontractor SWMS for the works | [6 empty] | SWMS Approved | [5 empty] | UGL-Contractor HSEQ Requirements |  |  |  |  | UGL SWMS Review Forms and approved SWMS. |  |  | H | H |  | S
1.5 | Conformance of Materials |  |  |  | All delivered materials and procured items conform to project specification and AFC drawings. | [6 empty] | As per Drawings and Specifications | [5 empty] |  MRTS05 Type 2.1 |  |  |  |  |  Material Certificate  Test Reports complying to Type 2.1 material by NATA accredited laboratory. |  |  | R | R |  | S
1.6 | Inspection Measuring and Test Equipment (IMTE) Registers |  |  |  | Supply of all calibration certificates to the Engineer including but not limited to: Survey equipment | [6 empty] | Visual | [5 empty] | UGL 3200-0706-PLN- 001 QMP Section 9.8 |  |  |  |  | Calibration Certificates. |  |  | R | R |  | S
STAGE 2: CONSTRUCTION WORKS
2.1 | Setout of pad |  |  |  |  Registered Surveyor to set out pad with pegs and markers.  Check surveyor marks against known structures, such as boundaries, fences | [6 empty] | Drawing provided showing marked out areas and exclusion zones. | [5 empty] |  Drawing Number: 0706-C-DRG-0003  Drawing Number: 0706-C-DRG-0002 General Notes G8. |  |  |  |  | Survey complies with checks and contract drawings. |  |  | H | H |  | S
2.2 | Underlying ITP/ITC closed and signed off. |  |  |  |  Verify ITC if closed and signed off. | [6 empty] |  Signed off ITC document 3200- 0706-ITC-CE-002 Pavement Subbase Layer | [5 empty] | NA |  |  |  |  |  Survey Conformance Report for finish surface uniformity  3200-0706-ITC-CE-002 Pavement Subbase Layer |  |  | H | H |  | S
2.3 | Base Layer (Class 2.1) |  |  |  |  Spread material and compact to maximum: - 150mm Typical Battery Storage Platform - 150mm Typical Sealed Road Pavement - 150mm Typical Substation Platform  Compact material to 100% SMDD.  Minimum CBR 80%.  Trim final surface level for uniformity within tolerance. | [6 empty] |  Material compacted to 100% at specified maximum thickness layer.  CBR 80%  Tolerances ±5mm  Maximum ±5mm in 3m straight edge at any direction.  Minimum 4 test per lot | [5 empty] |  Drawing Number: 0706-C-DRG-0011  MRTS05 Type 2.1 (Class 2.1) |  |  |  |  |  Survey Conformance Report for finish surface uniformity  SMDD material test report  3200-0706-ITC-CE-003 Pavement Base Layer |  |  | H | H |  | S
2.4 | Proof Rolling |  |  |  |  Proof roll using either 7,000 litre single rear axle or 10,000 litre tandem near axle water tanker | [6 empty] |  No perceptible surface deformation | [5 empty] |  MRTS05 Cl 9.4.7  Testing Method Q723 |  |  |  |  |  Visual |  |  | H | H |  | S
2.5 | Finish Platform -Single size dressing layer |  |  |  |  Spread single gravel dressing layer minimum 100mm thick.  Single size clean gravel and free of unwanted materials | [6 empty] |  Final surface free of loose material and properly clean.  Visual and spread evenly. | [5 empty] |  Drawing Number: 0706-C-DRG-0011 under Typical substation platform detail with gravel layer. |  |  |  |  |  Visual and at random checking. |  |  | R | R |  | S
STAGE 3: ITP CLOSE-OUT
3.1 | Compilation of survey records |  |  |  | Sub-contractor to provide survey records to Engineer for review and acceptance. Deviations or changes to AFC Design shall be highlighted to Engineer. | [6 empty] | Provision of CAD file of Works. | [5 empty] | UGL 3200-0706-PLN- 001 QMP Section 11.1.1 |  |  |  |  | As-Constructed drawing |  |  | R | R |  | S
3.2 | Develop Punchlist |  |  |  | Walkdown and inspection of works and development of punch list with Engineer and or Supervisor. | [6 empty] | Punchlist closed in a timely manner. | [5 empty] | UGL 3200-0706-PLN- 001 QMP Section 9.7 |  |  |  |  | Master Punchlist Register |  |  | R | R |  | S
3.3 | Closeout of NCRs |  |  |  | Any NCRs that have been raised during the progress of the works have been formally closed out and lessons have been captured. Refer to UGL Quality Management Plan. | [6 empty] | NCRs close out in a timely manner. | [5 empty] | UGL 3200-0706-PLN- 001 QMP Section 9.5 |  |  |  |  | NCR Closed, signed off. |  |  | R | R |  | S
3.4 | Changes captured and agreed within RFIs |  |  |  | Any deviations to AFC Design or Contract Specifications are to be captured, recorded, and agreed via the Formal RFI process. | [6 empty] | All RFI’s to be agreed or accepted in a timely manner. | [5 empty] | UGL 3200-0706-PLN- 001 QMP Section 11.1.1 |  |  |  |  | RFI Register |  |  | R | R |  | S
3.5 | As Constructed records – Red Line Mark-Up (RLMU) Drawings. |  |  |  | Sub-contractor to compile and record changes on AFC Drawings, to be issued to UGL Engineering via Teambinder. | [6 empty] | NA | [5 empty] | UGL 3200-0706-PLN- 001 QMP Section 11.1.1 |  |  |  |  | As-Constructed Drawing / RLMU drawing |  |  | R | R |  | S
COMMENTS AND NOTES
ITP COMPLETION AND SIGN-OFF
S/C Representative | [11 empty] | UGL Representative | [12 empty] | Client Representative
Name: | [11 empty] | Name: | [12 empty] | Name:
Signature: | [11 empty] | Signature: | [12 empty] | Signature:
Date: | [11 empty] | Date: | [12 empty] | Date:
ITP Number: |  |  | 3200-0706-ITP-CE-003 | [10 empty] | ITP Title: |  |  |  | Pavement Base Layer
Attachment A - Inspection and Test Plan Notes
Document Rev | [6 empty] | Activity Ref | [5 empty] | Change | [7 empty] | Reason for Change
Pavement – Base Layer INSPECTION & TEST CHECKLIST (ITC) Checklist No: 3200-0706-ITC-CE-003
Project No: |  |  | 3200-0706 | [5 empty] | Title: |  |  | Pavement Base Layer |  |  |  | Client: |  |  | NEOEN TESLA
Description: |  |  | CE – Pavement – Base Layer
Lot No: | [8 empty] | Drawing / Area Ref:
Work Pack No: |  |  | 3200-0706-WP-002: General Civil Works | [5 empty] | ITP Ref: | [6 empty] | 3200-0706 -ITP-CE-003
NOTE: Strike through sections that are not applicable.
Item |  | Description | [16 empty] | Yes |  |  | No | N/A
1 |  | Prior Works
1.1 |  | Materials are compliant to design
1.2 |  | Surveyor pad layout/ pavement layout
1.3 |  | Installation of Erosion and Sediment Controls installed
2 |  | Pavement – Base Layer
2.1 |  | Typical Battery Storage Platform
2.1.1 |  | Tie-in new material on existing by cutting the seal with road saw straight and a vertical face.
2.1.2 |  | Base Layer: Crushed Rock (Class 2.1) with minimum CBR 80%
2.1.3 |  | 150mm thick per layer compacted to 100% SMDD Actual SMDD value: Test Report number:
2.1.4 |  | Finish base surface level Survey pick-up (As-Constructed) Tolerances: ± 5mm V/H
2.2 |  | Substation Platform
2.2.1 |  | Tie-in new material on existing by cutting the seal with road saw straight and a vertical face.
2.2.2 |  | Base Layer: Crushed Rock (Class 2.1) with minimum CBR 80%
2.2.3 |  | 150mm thick per layer compacted to 100% SMDD Actual SMDD value: Test Report number:
2.2.4 |  | Finish base surface level Survey pick-up (As-Constructed) Tolerances: ± 5mm V/ H
2.2.5 |  | 100mm single size gravel dressing layer
2.3 |  | Typical Sealed Road
2.3.1 |  | Tie-in new material on existing by cutting the seal with road saw straight and a vertical face.
2.3.2 |  | Subbase Layer: Crushed Rock (Class 2.1) with minimum CBR 80%
2.3.3 |  | 150mm thick per layer compacted to 100% SMDD Actual SMDD value: Test Report number:
2.3.4 |  | Finish base surface level Survey pick-up (As-Constructed) Tolerances: ± 5mm V/ H
2.4 |  | O&M Platform
2.4.1 |  | Tie-in new material on existing by cutting the seal with road saw straight and a vertical face.
2.4.2 |  | Base Layer: Crushed Rock (Class 2.1) with minimum CBR 80%
2.4.3 |  | 150mm thick compacted to 100% SMDD Actual SMDD value: Test Report number:
2.4.4 |  | Finish base surface level Survey pick-up (As-Constructed) Tolerances: ± 5mm V/H
3 |  | Proof Roll
3.1 |  | Conduct proof roll using either 7,000 litres with rear single axle or 10,000 litres double rear axle water truck. No perceptible movement on the finish surface.
4 |  | Post Works
4.1 |  | Final sweep to remove loose and unwanted materials prior to bitumen
4.2 |  | Clean-up of Site
Comments
Checked – Subcontractor
Name: | [7 empty] | Signed: | [8 empty] | Date:
Verified – UGL Project Engineer
Name: | [7 empty] | Signed: | [8 empty] | Date: