## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Curtain Wall Per Zone Checks |  |  |  |  | Yes | Curtain Wall Per Zone Checks | 37e9de45-9ea3-4e6f-9490-47d64c20696d
checkpoint-status |  |  | checkpoint | 1. Bracket correctly installed and torqued, drift screw installed, confirm no changes were made to brackets during panel installation. Torque requirement for the T-bolt HBC-C 60 N*m, HBC-C-N 185 N*m confirmed as correct
checkpoint-status |  |  | checkpoint | 2. GRC in good condition, no cracks, damage or other defect. Repairable damage to be repaired after agreeing an appropriate on-site remediation approach. GRC has been installed to curtain wall panel as per design
checkpoint-status |  |  | checkpoint | 3. Fins are correctly installed to panel in correct position, including the correct fixings are used. (M5*10 SS316 socket head machine screw for vertical fins, M8*25 SS316 socket head machine screw for horizontal fins)
checkpoint-status |  |  | checkpoint | 4. Gutter plate and sleeve is installed in correct position and is sealed.
checkpoint-status |  |  | checkpoint | 5. Panel installed in correct position and height, with all required accessories rubber seals are installed.
checkpoint-status |  |  | checkpoint | 6. Expansion gap between panels is consistent.
checkpoint-status |  |  | checkpoint | 7. Slab edge insulation (Thermal insulation: Chaoming 100mm Insulation rock wool / Fire rated insulation: ABM Fire-rated rock wool,) is installed as per manufacturer's requirements. No visible gaps and compacted in accordance with manufacturers requirements
checkpoint-status |  |  | checkpoint | 8. Smoke Seals correctly installed and sealed using Sikasil-WS-305 S Fixing type to subhead: 4.2*13 SS316 pan head screw; Fixing type to concrete: Hilti X-P 20 G3 MX concrete nail, spacing 300mm.
checkpoint-status |  |  | checkpoint | 9. Pelmet and skirting installed in position, with pelmet flush with bottom of transom.
checkpoint-status |  |  | checkpoint | 11. Four way stack joint was sealed at sill profile.
checkpoint-status |  |  | checkpoint | 12. Sliding and swing door open and close in good condition & have the correct/approved hardware. / jockey sash
checkpoint-status |  |  | checkpoint | 13. Jockey sash opens to specified width and operates as specified
checklist-flat |  |  | checklist | Curtain Wall Per Panel Checks |  |  |  |  | Yes | Curtain Wall Per Panel Checks | 47457432-cbd4-4029-93af-7ba37fbd5463
checkpoint-status |  |  | checkpoint | 10. Glass is in good condition (attach photos).
checkpoint-status |  |  | checkpoint | 14. No defects/scratch/dents/distortion/crack (attach photos).
checklist-flat |  |  | checklist | Window Wall - Per Panel Checks |  |  |  |  | Yes | Window Wall - Per Panel Checks | 4db88c64-6086-433b-86b1-41d7a41526e3
checkpoint-status |  |  | checkpoint | 10. Glass is in good condition (attach photos).
checkpoint-status |  |  | checkpoint | 13. No defects/scratch/dents/distortion/crack (attach photos).
checklist-flat |  |  | checklist | Window Wall - Per Zone Checks |  |  |  |  | Yes | Window Wall - Per Zone Checks | 58ccb155-23fc-4b11-8467-f6ad27db3631
checkpoint-status |  |  | checkpoint | 1. Sub-sill, subhead and supporting structure (if required) in position with sub-sill flashing installed. Check expansion bolts are used and nuts are tightened (45N*m for M10 bolts, 60N*m for M12 bolts). Confirm correct torque and no changes were made to sub-frame during panel installation.
checkpoint-status |  |  | checkpoint | 2. Gaps between concrete and sub-sill and sub-head are fully sealed & foam installed for wind.
checkpoint-status |  |  | checkpoint | 3. Fins are correctly installed including capping piece and mechanically fixed to panel in correct position, including the correct fixings are used. Fixing type and sizes confirmed correct (M6*20 SS316 socket head machine screw for fins, 4.2*13 SS316 countersunk screw for caps)
checkpoint-status |  |  | checkpoint | 4. Gutter plate and sleeve is installed in correct position and is sealed.
checkpoint-status |  |  | checkpoint | 5. Panel installed in correct position and height with all required accessories, rubber seals are installed
checkpoint-status |  |  | checkpoint | 6. Expansion gap between panels is consistent.
checkpoint-status |  |  | checkpoint | 7. Insulation in between supporting steel structure (Thermal insulation: Chaoming 100mm Insulation rock wool / Fire rated insulation: ABM Fire-rated rock wool, is filled as per manufacturer's requirements. No visible gaps and compacted in accordance with manufacturers requirements
checkpoint-status |  |  | checkpoint | 8. Flashing installed in correct positions (internal & external as per design) and sealed.
checkpoint-status |  |  | checkpoint | 9. Pelmet and skirting installed in position, with pelmet flush with bottom of transom.
checkpoint-status |  |  | checkpoint | 11. Sliding and swing door open and close in good condition & have the correct/approved hardware / jockey sash
checkpoint-status |  |  | checkpoint | 12. Jockey sash opens to specified width and operates as specified
checklist-flat |  |  | checklist | Pre-installation |  |  |  |  | Yes | Pre-installation | 65e35ba2-30f1-47e0-954b-842676eeba77
checkpoint-status |  |  | checkpoint | IFC drawings received and current revision approved - photo of title block with revision
checkpoint-status |  |  | checkpoint | All hobs have membrane and no physical damage evident
checkpoint-status |  |  | checkpoint | Floor survey completed and levels within acceptable tolerance
checkpoint-status |  |  | checkpoint | Grid lines established and identified