## Table 1
Inspection and Test Plan Reviewed and Approved by Customer | Project Structure Specification C07 Rev. 01 IFC structure OWG | Inspection and Test plan shall be submitted to the Engineer for review and approval before fabrication is commenced. | IFC DWGs | PM/PE
Shop Drawing approval | Project Structure Specification C07 Rev. 01 IFC structure OWG | Shop Drawing st1all be submitted to Engineer for review along with Shop Drawing Check form | ShopDrawing Check form | PM/PE
Welding Procedures - Structural | AS/NZS 1554.1:2014 Category SP | Details of the welding procedures to be used including details of the equipment and consumables before any welding is carried out. No welder shall carry out work for which he is not certified. | Welding Procedures HERA/CSWIP Stamp | PM/PE
Welder Qualifications - Structural | ASINZS 1554.1:2014, ISO 9606-1:2017 | A list of proposed welders and their welding certificatesto be provided prior to any welding being carried out. No welder shall carry out work for which he is not certified. | WOT by Authorised Person (Welding Supervisor) | PM/PE
Procurement of materials in line with JFC drawings and Technical Specification | Project Slruclure Specification C07 Rev. 01 IFC structure OWG | Materials match that specified in Project IFC drawings and Technical Specification. Structural steel Material shall be sourced from suppliers certified by ACRS Material test certificates shall report all element required by AS/NZS relevant standard, plus total boron content (Manufacturer certificates shall from ILAC MRA laboratories) | Supplier Material Certificate | PM/PE
Procurement of Welding consumable to match Weld procedure and parent materials. | ASINZS 1554.1 | Welding consumables and gas match what is specified on the appropriate welding procedures. | Supplier Material Certificate PFS Welding Procedures | PM/PE
Material inspection upon receiving | Project Structure Specification C07 Rev. 01 IFC structure DWG | All material st1all be inspected against IFC drawing to make sure material grades, type, thickness, size are in compliance with IFC DWGs. | IFC DWGs | Team Leader
Manufacturing Work Pack Issued to Production Manager | Project Structure Specification C07 Rev. 01 IFC structure OWG | Job barcodes, Inspection & Test Plan's, IFC Fabrication Drawings, Reference Drawings/Info, Welding Procedures, weld map, welding log info. traceability sheet |  | Production Manager
Identification and traceability for main items | Project Structure Specification C07 Rev. 01 IFC structure OWG ASINZS 5131 | Lot traceability shall be provided for main structural members. connections between main structural members and major plate components. Tracibility as per AS/NZS 5131:Amd 1:2020 5.2.3 (ii) for minor components including cleats, connecting brackets and !he like. | IFC DWGs | PM/PE
Manufacture of steel structure Tack welded only | IFC OWGs | Manufacture completed as per IFC Fabrication drawings. All tack welding shall be pertormed in accordance with PFS weld procedure. Welding consumables. process & any applicable pre/post heat requirements shall comply with approved welding procedure's. | IFC DWGs | Team Leader
Pre Weld Dimensional Check (Tack Check) | IFC Drawings | Dimensional survey of fabncaled items against IFC drawings. Measured dimensions shall be within stated tolerances unless noted otherwise. Project specification clause C0702.1.3 Functional Tolerances shall be class 2 as per AS/NZS 5131 Table F2.1 to F2.10 Inspections recorded in line will1 SHEQ-01-02-0035 Product lnspection Procedure | IFC DWGs | Team Leader
Welding | ASINZS 1554.1 ASINZS 9606.1 | All welding shall be pertorrned in accordance with PFS weld procedures Welding consumables, process & any applicable pre/post heat requirements shall comply with approved welding procedure's. Welder ID. weld date & consumable batch are recorded on traceability register. | Welding Procedure and Welder Qualification | Team Leader
Post Weld Dimensional Check | IFC DWGs | uImensIonaI survey o aonca1ec1 nems agaIns1 Ir-L. drawings. Measured dimensions shall be within stated tolerances unless noted otherwise. Project specification clause C0702.1.3 Functional Tolerances shall be class 2 as per AS/NZS 5131 Table F2.1 to F2.10 Inspections recorded in line with SHE0-01-02-0035 Product lnsnection Procedure | IFC OWGs & Workshop Pack. | Team Leader
Weld Visual Scanning (PFS Internal Check) | IFC Drawing | 100% of all welds shall be subject to visual scanning | PFS NOT Register | Team Leader
NOT inspection | Project Structure Specification CO? Rev. 01 | NOE shall include as a minimum: 100% Visual Scanning, 100% Visual examination The Welding Compliance Inspector shall complete all inspections including any additional inspection, tests and reports necessary due to any welding or welding related workmanship defects. | Stamped NOT report | PM/PE
Prolective Coatings Preparation | Project Structure Specification C07 Rev. 01 | Removal of all weld spatter and dressing of any weld to removed sharp edges / spatter. All st1arp edges are ground to a smooth 2 mrn radius. | NIA | Team Leader
Fabrication NCR (if any) | Project Structure Specification C07 Rev. 01 | All Non-conformities reported in PFS NCR system during manufacturing of steel structure need to be submitted to Client for approval | - | PM/PE
Lighting and conduit bracket- assembly | Project Structure Specification C07 Rev. 01 IFC structure OWG | After coating, the bracketes to be assembled on GRP material | IFC DWGs | Team Leader
Holing | Project Structure Specification C07 Rev. 01 IFC structure DWG SHEQ-01-02-0040 | Manual holing shall be pertormed on GRP material. | IFCDWGs | Team Leader
Dimension ct1eck | IFCDWG | Compliance with IFC DWGs |  | Team Leader
Visual inspection of Fasteners | lFC Drawing | AU fasteners (bolts, nuts, washers) are to be in complied with the Project requirement (Grade, Size and Length) | IFC Drawing | Team Leader
Snug tightening of fastener to fasten the brackets to the GRP material | Standard operation procedure for steel structure boll lightening SHE0-01-02-0038 | 100% of fixings securing brackets to be inspected for snug light condition and marked with coloured paint pen to confirm fixing condtion has been checked and verified. |  | Team Leader
Assembly of the angles between brackets | Project Structure Specification C07 Rev. 01 IFC structure DWG | The angles to be assembled between bracket with fasteners | IFC OWGs | Team Leader
Snug tightening of fastener to fasten angles to the brackets | Project Structure Specification C07 Rev. 01 IFC structure DWG | The angles to be assembled between bracket with fasteners |  | Team Leader
Final Inspection | IFC Drawings, AS/NZS 1554.1:2014 Category SP | Visual and Dimensional inspections completed by PFS Project Manager to confirm manufactured items have been manufactured to acceptable standard & tolerance and approved to progress to proleclive coatings. >Confirmation that dimensional inspections have been completed in line wi!h SHEQ-01-02-0035 Product Inspection Procedure >Confirmation that required quantity and type's of NOE has been completed and any identified defects have been remediated. | IFC DWGs | PM/PE
Compile, review and submit documentation | Project Structure Specification C07 Rev. 01 IFC structureDWG | Documentation, Certificates and reports to support manufacture of steel structure and subcontracted items compiled in!o PFS Manufactures Oala Report | PFS Manufactures Data Report | PM/PE