## Table 1
NDT inspection | Project Structure Specification CO? Rev. 01 | NOE shall include as a minimum: 100% Visual Scanning, 100% Visual examination, 100% UT examination of all butt weld, 10% MT examination for fillet weld The Welding Compliance Inspector shall complete all inspections including any additional inspection, tests and reports necessary due to any welding or welding related workmanship defects. | Stamped NOT report | PM/PE
Protective Coatings Preparation | Project Structure Specification CO? Rev. 01 | Removal of all weld spatter and dressing of any weld to removed sharp edges/ spatter. All qharp edges are ground to a smooth 2 mm radius. | N/A | Team Leader
Fabrication NCR (if any) | Project Structure Specification CO? Rev. 01 | All Non-conformities reported in PFS NCR system during manufacturing of steel structure need to be submitted to Client for approval | - | PM/PE
Inspection the free issue pannel uppon receipt at PFS work shop | Pannel DWGs | Check pannel to make sure the quantity and/or dimension are based on approved DWGs. | Pannel DWGs | Team Leader
Panels Pre-assembly | Project Structure Specification CO? Rev. 01 IFC structure DWG | After painting, Client supplied pannels for decking and balastrades to be assembled. Handrails need to be assembled in the shop | IFC DWGs | Team Leader
Dimension check | IFC DWG | Compliance with IFC DWGs |  | Team Leader
Visual inspection of Fasteners (Free issue I | IFC Drawing | All fasten rs (bolts, nuts, washers) are to be in complied with the Porject requirement (Grade, Size and Length) | IFC Drawing | Team Leader
Snug lightening of conposite component fixings | Standard operation procedure for steel structure bolt tightening SHEQ-01-02-0038 | 100% of fixings securing composite material to structure are to be inspected for snug tight condition and marked with coloured paint pen to confirm fixing condtion has been checked and verified. |  | Team Leader
Final Inspection | IFC Drawings, AS/NZS 1554.1:2014 Category SP | Visual and Dimensional inspections completed by PFS Project Manager to confirm manufactured items have been manufactured to acceptable standard & tolerance and approved to progress to protective coatings. >Confirmation that dimensional inspections have been completed in line with SHEQ-01-02-0035 Product Inspection Procedure >Confirmation that required quantity and type's of NOE has been completed and any identified defects have been remediated. | IFC DWGs | PM/PE
Compile, review and submit documentation | Project Structure Specification CO? Rev.01 IFC structure DWG | Documentation, Certificates and reports to support manufacture of steel structure and subcontracted items compiled into PFS Manufactures Data Report | PF'S Manufactures Data Report | PM/PE