## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
80dfb780-035d-5666-9f26-1e3fd33cf5fd | checklist | DN1210-0003 - Stormwater Drainage Line Record | itp | DN1210-0003 - Stormwater Drainage Line Record
d1c4b54a-b4c4-539e-9691-c0d96368dc14 | section | SET OUT
c5d6f50a-ccb6-53db-bb19-e28206919615 | checkpoint | 1 - Confirm Stormwater alignment is as per latest Drawing revision and does not clash with other Services.
a4065fb7-47d2-51b3-8490-491671bfbe94 | note | Comments: Design Engineer to approve if the location needs to be moved.
27872ba7-cfde-54f2-b0b3-7b5d9f6503cf | textbox | NCR/OFI/RFI No:
274a37be-f134-5256-8964-164983e5d09a | checkpoint | 2 - Check Survey Set out and mark out completed.
3125fab0-e6d9-5e66-8bdd-a0deb9806432 | note | Comments: Max. 10m interval
8ac7e125-0b01-530b-adbc-7c83d866cc8e | checkpoint | 3 - Confirm correct location of Manholes or Chambers, Catchpits.
d08aedaa-d3c4-534b-93e0-a8b3f97ae182 | textbox | Comments: Refer to Dwg:
250e19d1-e2cb-5fbb-b958-1502f46075be | section | TRENCH EXCAVATION
a97a1b49-0483-5c2a-aeff-5b999d064122 | checkpoint | 4 - Ensure permits are in place.
c4f9efec-88e3-5916-8886-90616352200c | checkpoint | 5 - Pothole existing services data in place.
a88916c6-f006-5573-8093-21c6e2687901 | checkpoint | 6 - Confined Space Permit required?
1ce99c41-985e-5ed5-8590-6256ee7c23d6 | note | Comments: Trench depth > 1.5m must be shored or battered.
d0547d1e-a8b7-5c80-b83d-cd2c32bdda0c | checkpoint | 7 - Foundation test conducted.
452644e1-e467-5193-9154-2a774c1233b8 | note | Granular Material: Scala 3 blows/100mm 5% CBR
1e418d7c-dc6c-5e26-aa25-6358e957c892 | note | Cohesive Material: Shear Vane Strength 70kPa
fe505ecd-66c2-5d92-97f3-03de78b849b1 | checkpoint | 8 - Undercut required?
82e249bc-038f-574c-b7df-489b09b5f54a | note | Comments:
e957ffca-6498-5936-9eff-b596c5779659 | textbox | Undercut depth:
a3e6936b-8b42-55e4-b322-93da889abab3 | textbox | Metal:
366236e9-d9d4-5404-9128-b2d28615f3e4 | section | STORMWATER PIPE INSTALLATION, BACKFILL AND TESTING
31d5f8ad-f5a7-5de8-b074-5818082d2a1f | checkpoint | 9 - Check actual horizontal and vertical alignment achieved
8c616601-5035-5ce0-9364-a7b6cf83728a | checkpoint | 10 - Ensure pipe is checked & cleaned before being laid into the trench.
7337a6cc-1af5-5a5f-9107-c0f023787fdb | note | Comments: No vandalism, surface damage or deterioration. No install if found defective.
856ead07-9789-5994-9bcc-73fdb1d2732b | checkpoint | 11 - Line, level, and grade conformance checked
e84812bd-8c2d-5281-a984-59b5181bd154 | checkpoint | 12 - Ensure Bedding, surround & backfill materials are well-compacted and tested.
e9f4ee5a-ea12-5e98-b07b-d0f785a5d524 | note | GAP20 - NDM- minimum 95%
d2d34806-3576-5342-8847-b6be96f78380 | note | LRAP65 - NDM- minimum 95%
0d1bfd0d-b01a-562d-a2dc-f55be211f7e4 | note | Comments: At every 200mm compacted lift
e75614fe-2c0c-5b12-9fa9-4b0f2b88bdab | checkpoint | 13 - Ensure installed pipeline has CCTV completed
2601f2b1-185c-5ffa-824a-9f0fefb7305d | note | Comments: No internal surface cracks. Clean from debris and contaminants.
3df15f87-6988-5d80-a0b5-df40e70b3938 | section | ACCEPTANCE
955faf87-29fa-529e-a42f-37e0ac363031 | checkpoint | Inspection By: Downer
9cfcbcb4-0357-5e51-b5a4-fb2be1210189 | textbox | Name:
8663f0dc-3ff4-54d0-8b86-4ffda6e49df8 | date | Date:
32b75610-717e-5075-a935-2468bbb9ba63 | signoff | Signature
26510945-d224-4c04-b6b5-0fbecfb28301 | checklist | DN1210-003 ITP Earthworks - Berm Backfill Rev 0 | itp | DN1210-003 ITP Earthworks - Berm Backfill
b567e37b-305b-4691-ab94-997e3525e2b6 | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS (MATERIAL TESTING & APPROVALS)
ae751a62-077f-4903-8007-09eabdd22652 | checkpoint | 1.1.1 - Weathering Resistance
170d24d6-9aaa-5a61-9714-6d3639b3fdd5 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
512865cd-9a30-59f2-b1c6-17dece2c767f | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
219a3981-3a3a-55bd-b780-74ab0986caad | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
f25d1e77-f126-5a80-af63-e918627bf828 | note | Verifying Document - IANZ Accredited Report
89c43b3a-8d27-5262-bbd0-f584e6beedda | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
d97eb3b9-672a-56bc-91c9-d66ab3b0160f | note | ○ Results to Engineer 2 wks before importing
f9597cbb-85fd-510f-852b-7a2ac6faf220 | note | Verification Activity: Activity - HP
e423c072-3524-5539-a79c-65fe85db3243 | note | Verification Activity: By - ENG
3a53d180-37da-4794-96f1-2c57191058d6 | signoff | AUTHORITY HOLDPOINT
4621ae14-9d3f-4092-8bdc-fb91a7d23106 | checkpoint | 1.1.2 - Los Angeles Abrasion Test
5459d323-a895-5181-8dd2-a5a78f7b1dd2 | note | Detail - NZS4407:2015, Test 3.12 - The Abrasion Resistance of Aggregate by use of the Los Angeles Machine
3b7a0f7d-79e4-5b1b-b7a0-c3f124c211a0 | note | Acceptance / Conformance Criteria - 0.5
0ddf40e4-ab58-5b23-a819-0d492f361e48 | note | Standard / Specification - PS 16.5.5, Appendix V
a56fe015-436d-58c3-860d-c80232f81fa9 | note | Verifying Document - IANZ Accredited Report
d72445bf-ad35-5f36-9523-021cf4c08d4c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Required
ed4b7968-8888-5eb7-a02e-c08d10663fc9 | note | ○ Results to Engineer 2 wks before importing
f33b5661-1301-54dd-a6b5-01710a39df56 | note | Verification Activity: Activity - HP
62db03b1-767b-510f-84b1-dcffa41b7b55 | note | Verification Activity: By - ENG
0b6b78a6-31f1-4901-9607-f42fa97fa179 | signoff | AUTHORITY HOLDPOINT
ec0f526f-6a69-4bcc-bc78-077bd42de97e | checkpoint | 1.1.3 - Particle Size Distribution
834aff6f-f08b-579a-8bd1-cede2f04c2fd | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
8c0bf74e-0e20-5cca-bfb9-7db89783479f | note | Acceptance / Conformance Criteria - No Particles >200mm
cbbeee61-7095-5cc1-ac91-aeb41afe45d7 | note | ○ Maximum fines 10% passing 75micron sieve
55eddd53-3f67-5c5b-bbf1-1ca4d0ca3dff | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
ce403317-715f-5224-a0eb-2a4e21a9d974 | note | Verifying Document - IANZ Accredited Report
8ac422ba-606e-582a-a37b-de668b26fd02 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
c4575f95-29c0-5072-aa90-cf28a1dc5343 | note | ○ 0-400 - 2 tests
1faf988a-add7-5d72-a88b-3c1f71e64b60 | note | ○ 400-1,500 - 3 tests
866b8657-e118-5221-a273-57d7cb135a58 | note | ○ 1,500-4,000 - 4 tests
dfcaf6e4-305a-5955-9cca-45aec79ac805 | note | ○ >4,000 - 1 test for each additional 1,000m3
748b1587-859b-52de-912f-d63aff835bfa | note | – Results to Engineer 2 wks before importing
26711431-b97d-512d-bca6-bc51a82062e4 | note | Verification Activity: Activity - HP
8a1e80a2-5e9e-50d7-96bd-ebea22ee0c6e | note | Verification Activity: By - ENG
1f9e51cb-ecfe-4e36-a665-8117c203dfcb | signoff | AUTHORITY HOLDPOINT
b9c36af9-cacf-4685-9849-b5b3cce9a8fe | checkpoint | 1.1.4 - Maximum Dry Density and Optimum Water Content
77dc297a-b0d2-5fec-ab26-f7a374aaa011 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
774c6f36-018c-5319-a837-7596092ad73a | note | Acceptance / Conformance Criteria - Report Value Only
7aa77f23-5fa0-50c9-bed5-72b1b05dc4bc | note | Standard / Specification - Appendix XVIII, Appendix V
964cd6ca-b827-5bc5-9873-14f2591f0801 | note | Verifying Document - IANZ Accredited Report
14813e4f-e19a-51ed-b6ef-ccd0a296613d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
eb869f09-6a1c-5cab-be26-45194aa2b622 | note | ○ Results to Engineer 2 wks before importing
bab267a8-a813-5045-b8a9-37f18d17a4d1 | note | Verification Activity: Activity - HP
9c1d7416-706e-57f1-b3a7-033045f150eb | note | Verification Activity: By - ENG
87730b18-0c88-4532-968b-4c16a64cbb39 | signoff | AUTHORITY HOLDPOINT
313869ad-e4d9-4ce7-a906-54a77553c69d | checkpoint | 1.1.5 - Soaked CBR
b87e76ea-1e79-59ed-88a6-d487054ed8a2 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
66c07f5e-e6c7-5738-8837-53615c535a16 | note | Acceptance / Conformance Criteria - >25%
852d6290-9082-5256-a910-8fde398d9e5c | note | Standard / Specification - PS 16.5.5, Appendix V
46b18c6f-cbdf-5b99-9606-1a5bfcb50b5d | note | Verifying Document - IANZ Accredited Report
96aa03dd-6d33-517b-be25-b9c32644e019 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
1758c525-e975-592e-a7b3-914b9f092788 | note | ○ Results to Engineer 2 wks before importing
dd1adc3b-47ae-576f-a191-48fb85156421 | note | Verification Activity: Activity - HP
6ed9aa3a-b493-5ffc-9e0c-e3b96b7ad94e | note | Verification Activity: By - ENG
2baa5519-d187-4e8d-aef1-96d204ab3928 | signoff | AUTHORITY HOLDPOINT
0cce9f39-1fe9-4cb7-84a0-1347889a24bf | checkpoint | 1.1.6 - Solid Density
9c9be7ce-a4ed-5593-bddc-204edaac5bd9 | note | Detail - NZS4407:2015, Test 3.7.1 - The Solid Density of Aggregate Particles
0e1d6109-85c8-5dbb-adae-26b462d0f52b | note | Acceptance / Conformance Criteria - Report Value Only
4e3a1109-c507-5ac6-b181-a34c1204ee91 | note | Standard / Specification - Appendix XVIII, Appendix V
7c46fb2d-3b2e-5a72-adf2-52668ed6141e | note | Verifying Document - IANZ Accredited Report
f7705853-d6d8-55ce-9e48-1503adda94bc | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
ccc3ce36-6a79-59c8-9659-716ac1366231 | note | ○ Results to Engineer 2 wks before importing
1a1872d4-ffab-5795-9840-d6f6ac460aff | note | Verification Activity: Activity - HP
f1351d8f-4411-5f37-ac20-8ba4d499f16e | note | Verification Activity: By - ENG
9c032d01-4a60-4715-9580-0367e8722237 | signoff | AUTHORITY HOLDPOINT
9785d001-7bf6-4b2d-8e8f-ddc9322fc6d5 | checkpoint | 1.1.7 - Crushing Resistance
f8da953e-df9e-587f-8c0d-c8921c062455 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
7d890827-de77-5e6f-9f0a-68dde121faa4 | note | Acceptance / Conformance Criteria - >100KN
629ba928-8e42-5014-9037-51e19f1f69b8 | note | Standard / Specification - Appendix XVIII, Appendix V
b07c9dee-9e38-562e-8a2b-bd18421d659a | note | Verifying Document - IANZ Accredited Report
41987e16-5327-5b19-a5e1-9b9f516a2c90 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
54286504-b1e6-503b-aaa4-a4069e1d5d47 | note | ○ Results to Engineer 2 wks before importing
24adba30-fbd5-5c97-bdfb-bc6005ea0014 | note | Verification Activity: Activity - HP
c4e32125-e677-5994-8b23-b1b70a0a1052 | note | Verification Activity: By - ENG
4b425774-86b8-497d-b2d2-6bcd40a72d7e | signoff | AUTHORITY HOLDPOINT
8a26f54e-e6b9-4e37-a364-c24ae4b7703a | checkpoint | 1.1.8 - Geotextile -Only Under Strutual Fill
ed34fa9d-ea58-5764-903a-61aea8490f01 | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation.
55b7212b-8605-5a6e-b6d3-08fea246cf6d | note | Acceptance / Conformance Criteria - Engineers Approval
db20c58a-3d32-5945-b9e3-c61e2a5bce5d | note | Standard / Specification - PS 16.5.7, Appendix V
addf8051-6cfe-509a-ad18-2cfe2f82a5b4 | note | Verifying Document - Data Sheets
0c8190f7-6f91-5a96-b755-7ed564e383b8 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
282ccef2-904b-5a19-9c7b-1a56bec90019 | note | Verification Activity: Activity - HP
99d9d6ae-1258-5499-b7e4-12efc9088624 | note | Verification Activity: By - ENG
0b07cb24-1dc5-4366-b336-4241081bba50 | signoff | AUTHORITY HOLDPOINT
8c64aa70-7d69-4b88-acb1-7b54840e23dd | checkpoint | 1.1.9 - Laboratory Testing for Soil Suitability
58c2b8c9-9287-5d7d-956f-47a3bb0c0f85 | note | Detail - Soil Test Results from Hill Laboratories to confirm that topsoil suitable to for reuse
33f06718-b1ec-510b-b56e-8d831f07f1e4 | note | ○ Soil Reaction
664bbeb1-140e-578c-99a5-1a6d7ee79c93 | note | ○ Electrical Conductivity
4c0cb2b2-93b2-5cc4-83c7-ef4d0c7002bf | note | ○ Mechanical Analysis (texture)
a2f2662e-0706-569e-9c2c-a9a07881a482 | note | ○ Stone Content
550829dc-1225-5a80-afbe-cb7579a4da3d | note | ○ Nutrient Levels of nitrogen, available phosphorus, available potassium and available magnesium
9e615e84-63e4-5625-a015-f388525c6f7f | note | ○ Organic Matter Content
41b89eca-e1aa-5caa-bbfa-6dd1fd937e4b | note | ○ Check for Toxic or Hazardous substances
61950528-1621-5792-aa14-d12e960b70e4 | note | Acceptance / Conformance Criteria - Engineers Approval
bd4a2f79-8e39-50c2-af05-49b16ab1f38e | note | Standard / Specification - NZTA P39:2013 3.1
34ef85cc-c7d0-5565-b46d-0978a305be5d | note | Verifying Document - Hill Laboratories Test Report
7aef608a-586d-5f47-bb9c-1e8f0274bf2e | note | Testing Quantity Required (based from schedule qtys) - 10 equal samples taken from site, mixed together, then 1kg of soil sealed into a plastic bag and sent to lab for sampling
92fc6694-157e-5d62-a1d2-aa3d69efdfb0 | note | Verification Activity: Activity - I
b0f4265a-f627-5607-aee6-728315986084 | note | Verification Activity: By - SE
b3289ac5-b9ad-4084-89c1-bf5603717c12 | section | SECTION 2 – CONSTRUCTION - STRUCTURAL FILL ON BERM AREA
37ad755a-9095-4037-927e-b926371a854d | checkpoint | 2.1.1 - Compaction -Clegg Hammer
5e328567-d191-5a23-af52-78be541c04f9 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
9267bc8b-fd00-561d-9c4b-2b4ebb08037c | note | Acceptance / Conformance Criteria - Structural Fill
9667dfdc-9e21-5142-acf4-6ea9e9c7d7d2 | note | – Min CIV 18
62d08faa-61b8-5d38-8113-bba54b286091 | note | – Ave CIV 20
0a56712a-c6ef-5ac8-83f0-3993dbc1f117 | note | ○ Non-Structural Fill
8777bf59-fd9a-5878-a9f8-2d34a7457fa2 | note | – Min CIV 10
3b623987-3d65-5ea5-8698-bbb7c7eb3160 | note | – Max CIV 12
8e426650-b5de-5e57-92dc-bbc832eebad6 | note | Standard / Specification - Appendix XVIII
0958c8ec-0a9f-5776-8e3e-d2aaa916bb3c | note | Verifying Document - Clegg Hammer Report
b42fa6b7-12bb-583d-bc64-0fbcb27ac8ac | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
fafe8632-2fa0-541c-9c89-3bb6091719f8 | note | Verification Activity: Activity - I
e1ae69a9-943c-53f2-9871-82e4cb23c00d | note | Verification Activity: By - SE
7626dd1d-1b0a-4c69-a009-ddab4adbff12 | checkpoint | 2.1.2 - Compaction-NDM
7beb85a9-ef6f-594b-a5ab-766a5d338a51 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
c7a7531e-ae45-5c65-b65e-8f122e02ad18 | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
a8c61459-cda2-560f-a158-796bc659e919 | note | ○ Non Granular Material
729ac588-2525-5c18-8492-6353269039f4 | note | –Max Air Voids 8%
9b197cf0-ee03-5ba3-ae3f-cbdbcf9f50da | note | Standard / Specification - Appendix XVIII
b47c213a-3c33-59f1-bfa5-12cd7415225f | note | Verifying Document - IANZ Accredited Report
1be65343-0039-5e4a-a4cb-12ef661bc825 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
4122a55a-5c4b-5ebf-be12-e9de4f20070e | note | Verification Activity: Activity - I
d1847105-e1b8-5285-8dcd-a4b816c5e6fb | note | Verification Activity: By - SE
62151bee-e9c8-486a-bb5e-a3721c9fb835 | section | SECTION 3 – CONSTRUCTION - SITE WON LANDSCAPING FILL
aa275cff-9a3a-4d4f-8dc2-5b79d62faac4 | checkpoint | 3.1.1 - On Site track-able Testing
31a18122-4dc9-5abc-9e77-81cac707f0ee | note | Detail - Fine grained Type A3 site won materials may be considered suitable for use as landscape fill providing that it is ‘track-able’ by the contractor’s plant.
682f3a6b-0a2d-54b4-a9ae-9c6ac148180e | note | Acceptance / Conformance Criteria - Trackable by Contractors Plant
cfe28071-1c42-5a3f-926c-af452fbb9fbd | note | Standard / Specification - PS 16.5.5
0ca63b01-d21a-5e89-829c-61846109642a | note | Verifying Document - Site Engineer Site Record
e95b9f7e-556d-5897-960e-6706ae58ee9b | note | Testing Quantity Required (based from schedule qtys) - Before placing any fill each day for each area worked.
932d499e-2f5f-5de7-8c85-69926bd2baf0 | note | Verification Activity: Activity - R
86614c1b-a96c-5e77-8218-5ef3f1dcead4 | note | Verification Activity: By - SE
d3ff9700-c046-4bb0-aa1a-206c1c9ff540 | checkpoint | 3.1.2 - Shear Vane
eb8d7a86-c7c4-5c00-b8cd-9ce7a00c7549 | note | Detail - NZ Geotechnical Society 2001 - Guideline for Hand Held Shear Vane Test. Fine grained Type A3 site won materials may be considered suitable for use as landscape fill providing that it meets minimum shear vane strength of 30kPa.
fc47615d-3eae-5151-98ac-c4413e5e2e1e | note | Acceptance / Conformance Criteria - Min >30KPA
109ce713-b887-5fbd-a09e-c86b3bc46615 | note | Standard / Specification - PS16.5.5
42995995-62cb-5aab-8e2c-346ef7311632 | note | Verifying Document - Shear Vane Report
c8d3e686-b50a-52ef-8222-1b1c5136ea56 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed fill per 200mm vertical ‘lift’.
4788c8aa-2f17-5a86-adc9-40a109b291cb | note | Verification Activity: Activity - R
36b9c113-480a-5762-9067-9ae6a4f8a5a6 | note | Verification Activity: By - SE
04aeec45-6acf-40d4-ac1a-aef0adc7f266 | checkpoint | 3.1.3 - Proof Roll
ef2b91af-b75f-58bf-8260-dbcae5988862 | note | Detail - Visual Inspection of Proof Roll
615dd5d6-e020-52d5-a08d-8f4c3aa8802e | note | Acceptance / Conformance Criteria - Visual Inspection
1a0d17ac-c730-5b7c-990e-e8303c69b509 | note | Standard / Specification - Appendix XVIII
d4bdaf0a-2e0e-5d01-b23f-51c8ecf9f748 | note | Verifying Document - Visual Site Record
a08850e6-08de-5ce9-bd9f-df22f4c4e6b4 | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
bdd7aa09-9e72-5ae6-95f8-fcf28af7531e | note | Verification Activity: Activity - I
e9b5e678-7b74-58a8-8f2c-121046110d49 | note | Verification Activity: By - ENG
e71c0795-e8c0-4e24-bcfe-9363c22f4806 | section | SECTION 4 – CONSTRUCTION - TOPSOIL PLACEMENT
a92b39d0-e9d3-459e-a1af-8deba1750c1a | checkpoint | 4.1.1 - Topsoil Placement on cut and fill embankments
176d7427-5e00-5955-9be9-644f2f5fd3ef | note | Detail - Confirmation of thickness and material suitability
985e9bda-f7f6-519d-b619-b4219c0d352e | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
39d89a24-94a3-5e2b-a857-b2c69092f1b2 | note | Standard / Specification - PS 16.6.3 b)
208a124b-128b-5678-8332-a67b9850d5c5 | note | Verifying Document - Visual Observation
d7bdad61-f850-5ee5-b3ca-4c01dec9c18f | note | Testing Quantity Required (based from schedule qtys) - Once per lot after topsoil re-spread
9dec7009-fe0c-5007-9cd3-1a27aa0f23d6 | note | Verification Activity: Activity - I
9f1d53be-bd27-519a-90a3-80b8c922e570 | note | Verification Activity: By - SE
b8532d23-cfbe-4812-bac6-5c6e480ab014 | section | SECTION 5 – AS-BUILTS
27cb25e4-9be1-4694-9bc8-14ea687588df | checkpoint | 5.1.1 - As-Builts
ec1b2587-20e7-5fa4-ac50-5ac630699408 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
bfe00ec1-02dc-5b18-8b0c-543ee3bdf9f9 | note | Acceptance / Conformance Criteria -
818401b3-0d18-596c-b13e-a634beb2ff38 | note | Standard / Specification - PS 16.7.6
30cb67ff-b755-5db4-a87c-fe94c02d411d | note | Verifying Document - Survey Records / Redpen markups
4f67fd81-d5a4-563d-a650-6775c82d0045 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
bcedf0cd-96f7-5ff1-be78-c407b1d3e10d | note | Verification Activity: Activity - D
43ced653-744f-5b41-885d-4346e13e247f | note | Verification Activity: By - SE
67764006-38ab-4e1b-b2e3-b5efe59f2171 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
43f340f1-c8c5-5d92-a5c2-30d25ce9a4f8 | textbox | Contractor's Rep Name:
020fe78c-de8f-5639-9a0d-ea64537ae1e4 | textbox | Engineer's Rep. Name:
7ce4bd3b-9108-54da-af53-1d5e16435c90 | date | Date:
6c3b4162-ec2b-42ac-ade4-b412cfd97dbb | signoff | Add Signature
e065a17d-81db-479d-9e6e-0454bfdc957d | checklist | DN1210-003 ITP Earthworks - Settlement Installation & Monitoring Rev 0 | itp | DN1210-003 ITP Earthworks - Settlement Installation & Monitoring
fad5ec38-f156-4a66-99cc-56afb17012c6 | section | SECTION 3 – SETTLEMENT INSTALLATION & MONITORING
4325c26c-80c8-4d4a-832b-19115f29d959 | checkpoint | 3.1.1 - Instrument Reading Notice
8c88e885-d079-56fe-8534-8a197fff1990 | note | Detail - The Contractor shall inform the Engineer two days in advance of planned instrument readings so that the Engineer may observe the work.
d03406c5-31b3-5060-a4de-f36c65dd0891 | note | Acceptance / Conformance Criteria - 2 days notice to Eng
6eca6dbd-c82d-506c-a616-43e4ceaae748 | note | Standard / Specification - PS 16.8.2
96909bf5-d670-5530-bbb4-44779f893f48 | note | Verifying Document - Site Records
0c734e60-b3ae-51b7-a0ce-fa13c209ace2 | note | Testing Quantity Required (based from schedule qtys) - Every Time
1422055b-e2a6-5068-aa83-584675f6dceb | note | Verification Activity: Activity - I
18803931-4b9b-5ee6-b7ac-0f4e0519f3f3 | note | Verification Activity: By - SE
25d05582-2766-4d3e-84ec-87f6666206ae | checkpoint | 3.1.2 - Results Submitted to Engineer
7280cb77-04ca-5925-9e1c-e9741b07226e | note | Detail - Results will be submitted to the Engineer within 1 day of reading the instruments
eaadb0e3-faac-523b-ae07-890586c144bd | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
c787a454-90af-5e3d-a494-dbc37b1988b3 | note | Standard / Specification - PS 16.8.2
32c71a89-a793-544b-8620-dfa7ed5da42c | note | Verifying Document - Site Records
833777af-a12c-5bee-8cdd-c4e02232faf0 | note | Testing Quantity Required (based from schedule qtys) - Every Time
409be5f9-136e-5d7b-ad34-f8b707ba7519 | note | Verification Activity: Activity - I
6b005556-5efc-5051-8ccd-07eb8e524412 | note | Verification Activity: By - SE
1a6ddd3e-e5cc-463a-b5e9-7c789fff5870 | checkpoint | 3.1.3 - Baseline Readings
074ea846-917a-5878-ae6c-eed5465be46b | note | Detail - The Contractor shall take 3 sets of baselines readings from all instruments at 2 day intervals
5a878dcc-b07d-5544-b00f-dc2f844aa9a2 | note | Acceptance / Conformance Criteria - Engineers Approval
9353c49e-7db4-54d3-be36-edd712367d81 | note | Standard / Specification - PS 16.8.2
a7d940fe-8995-5783-9807-25f56c50ac3b | note | Verifying Document - Site Records
ac333fb5-690f-532f-8c25-8ec5d4640e5f | note | Testing Quantity Required (based from schedule qtys) - Every 2 days
9201b6dc-5587-52c6-b250-cf10c6597944 | note | Verification Activity: Activity - I
1d3e0eb3-7487-59a2-ad53-ac06ed6bdddb | note | Verification Activity: By - SE
3575e7a3-cc2a-4906-abbb-37cea3216b7d | checkpoint | 3.1.4 - Readings During Active Fill Placement
f68e66f8-595e-592d-a748-66e2b3fc5857 | note | Detail - During active fill placement, the Contractor shall read all monitoring plates twice a week or every 1 metre of fill whichever is more frequent
755f509b-f243-52af-b5d3-b26b5b3d1be7 | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
d8f008dd-2abc-5463-a613-733698ac9367 | note | Standard / Specification - PS 16.8.2
af758653-9fbe-5a8b-b619-91b17587cfeb | note | Verifying Document - Site Records
63b514b7-7068-518e-ad80-b71c06ab6942 | note | Testing Quantity Required (based from schedule qtys) - Twice a week
915bda8a-a9a1-52e5-904f-d5f1bc444a2e | note | Verification Activity: Activity - R
6ee5c505-f87d-50a6-b696-75d7a6057951 | note | Verification Activity: By - SV
6f3e8292-276a-446a-98d4-cb5f12bdb82e | checkpoint | 3.1.5 - Readings During No Active Earthworks in Area
e6f30a42-f97d-55dd-ba7c-5322e9304237 | note | Detail - The Contractor shall read all monitoring plates weekly if there is no active earthworks taking place in the area
4ebce20d-e3a7-572d-b471-30cf96c1997d | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
3a092fb8-12ee-576d-9a78-b4ceec795cb1 | note | Standard / Specification - PS 16.8.2
f8f744d1-f6e0-5586-ae62-10fb092fc1eb | note | Verifying Document - Site Records
82f9294f-5e97-5c0d-96bd-239e7b17e694 | note | Testing Quantity Required (based from schedule qtys) - Weekly
5ab80245-646f-5cc7-b8fe-d704899e4ac0 | note | Verification Activity: Activity - R
151c5a7a-84b7-5896-99fc-740a168a8dfd | note | Verification Activity: By - SV
9b389a66-c0c8-4bde-a9f7-cb310ff7518e | checkpoint | 3.1.6 - Settlement Monitoring Termination
706d668d-86ae-5758-b976-96a0cbef5541 | note | Detail - The criteria for terminating the embankment preload are either: Three consecutive measurements indicating the t90 settlement value has been achieved, A rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed. The settlement readings shall be evaluated by the Engineer to assess the need to extend the monitoring.
af7aca07-bd9c-5b63-a39d-7957b503fe19 | note | Acceptance / Conformance Criteria - Either:
b7fe0a61-4234-55c0-8c64-21b8cb2ceef8 | note | ○ 3 Consecutive Measurements showing T90 settlement value achieved
8dc8a5fd-0159-54e1-b52d-8be00ca27ca0 | note | Or
bf452f69-8553-57d7-af73-abe62f7be910 | note | ○ Rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed
8ff71d6e-9a66-5535-85a0-314783171c9d | note | Standard / Specification - PS 16.8.5
31757f56-c6df-572d-8f76-286259498fe5 | note | Verifying Document - Site Records
2ec99de1-edcf-5b23-85ca-39924bbd94ad | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
e28f3159-1acd-5c68-893a-a5ccaebb44dd | note | Verification Activity: Activity - HP
c8ddf84e-12ee-564a-b836-66dc6a8fb2b1 | note | Verification Activity: By - ENG
186a46a9-fa61-4352-8124-f491956fa16e | signoff | AUTHORITY HOLDPOINT
3e91e37f-7a0a-42bb-ad9c-ad4818fee5cf | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
1bbbd3ff-7896-52fc-86dd-2fad382450ec | textbox | Contractor's Rep Name:
8b9685d4-de7a-5c77-b2aa-3a27feadb32f | textbox | Engineer's Rep. Name:
34c68be1-431d-52a5-a76e-90328604858e | date | Date:
1ea57cc6-cfbf-44c0-ade0-502a5af4b2f8 | signoff | Add Signature
5c175e72-73d4-4b90-8947-518f9d50e046 | checklist | DN1210-003 ITP Earthworks Rev 7 | itp | DN1210-003 ITP Earthworks
303056fd-4628-4f15-b71f-dd6773c8f7b7 | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS (MATERIAL TESTING & APPROVALS)
d2b3bff5-f06b-4fce-9f05-326e50333af4 | checkpoint | 1.1.1 - Earthworks Methodology
b54321a1-ba3d-5299-8b17-46f3fe2de711 | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points for review and approval prior to works.
3ecb78fa-ecee-50b4-b42d-8c0ee2e0bec1 | note | Acceptance / Conformance Criteria - Engineers Approval
36085e54-fa35-5052-8a25-39e2fa5faed4 | note | Standard / Specification - Appendix V
23de603c-c47a-520f-af72-8353684128b4 | note | Verifying Document - Approved Methodology
58b41e61-fda2-533c-9756-71ea7c47ec24 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
54f222d8-f404-5d04-ab3a-d711a768afa7 | note | Verification Activity: Activity - HP
71a56ecc-e5a9-5010-b833-3327f3fa0022 | note | Verification Activity: By - ENG
fac27750-aac3-4c8f-900e-4499eece46bf | signoff | AUTHORITY HOLDPOINT
fdca8724-5a24-4428-966a-2048ffaa3bee | checkpoint | 1.1.2 - Ecology Sign Off
de7cc084-8a7e-5062-8885-4beac2238b18 | note | Detail - Confirmation from Ecology that earthworks can proceed
ac74a2e1-ad78-5e1d-935f-c8b0da4460c1 | note | Acceptance / Conformance Criteria - Email
6d10bfbc-9fd6-5742-9840-91d9dfddf372 | note | Standard / Specification - Internal Hold Point
b597ccc1-b99e-5f2e-8b9c-75ff3d9cbe8d | note | Verifying Document - Email from Ecology NZ
5406859a-4cd0-501c-b631-9480c9166f4a | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
baf4db9f-241d-5d1b-ad87-0bea2c6070d0 | note | Verification Activity: Activity - H
bbe336d6-2093-5ee2-bf3d-57793b7f8984 | note | Verification Activity: By - QM
08284768-1309-487e-add9-77155722f850 | checkpoint | 1.1.3 - Erosion & Sedimentation Controls
6318f672-1100-520b-9d61-e99c9e9e2fef | note | Detail - Confirm that Erosion and Sedimentation Controls are in place prior to earthworks proceeding
9968e49b-02f7-570a-9914-a285687c8160 | note | Acceptance / Conformance Criteria - As-built Completed
4699fa64-737e-5131-a123-68bdaf5da5a8 | note | Standard / Specification - Internal Hold Point
c9a32c2a-7fd5-5fa7-85fa-660037f379b2 | note | Verifying Document - ESC As-built
a0f0541e-f9c0-53a3-90e7-f436f0b036da | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
908cb5d9-ffb9-56ca-8a17-aa18d67ead87 | note | Verification Activity: Activity - H
f1a90b54-11ef-58ca-8bbe-5ff33f2a0201 | note | Verification Activity: By - QM
731f64c5-3239-4097-b5bb-6c62a50b6ea7 | checkpoint | 1.2.1 - Weathering Resistance
9323e9fa-411b-564a-ba98-cf2381f32b2c | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
64660634-199a-5b28-81a6-c33c118708cc | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
7beeb14e-b964-5787-8301-ec00078a6856 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
78f3a799-d019-5a08-94b7-32e24708ea98 | note | Verifying Document - IANZ Accredited Report
2d49902e-aaac-51a7-8ef1-c414d16ac8d3 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
b5d9229e-0c48-5719-a2d5-406a900a5ded | note | ○ Results to Engineer 2 wks before importing
343eb87f-30de-5e46-9864-09aef9015747 | note | Verification Activity: Activity - HP
f5c08cb6-1492-5264-8582-51ed7f060d25 | note | Verification Activity: By - ENG
4586777f-85ff-4c10-b96b-316acb2c3025 | signoff | AUTHORITY HOLDPOINT
3447d2a8-001a-4182-bd12-c7ac443e36b7 | checkpoint | 1.2.2 - Los Angeles Abrasion Test
4a29c643-08f3-5082-9622-692d26bee30e | note | Detail - NZS4407:2015, Test 3.12 - The Abrasion Resistance of Aggregate by use of the Los Angeles Machine
138d02b4-aa1e-55d5-b234-5b3834189d19 | note | Acceptance / Conformance Criteria - 0.5
b55ed5f7-9d7a-5e31-b58f-1a290f3d401e | note | Standard / Specification - PS 16.5.5, Appendix V
f065e9b9-4e2c-53a6-9e3f-f78ad23a631d | note | Verifying Document - IANZ Accredited Report
5804356a-2dda-5e0d-b0b1-12580016799a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Required
426ab0eb-7d43-5b24-8b31-ac4ffa1e6d3a | note | ○ Results to Engineer 2 wks before importing
2da53da6-474c-524e-9bc2-4a5cd43bb1f0 | note | Verification Activity: Activity - HP
faaa5c90-c6c6-5a9e-b5e8-943b87c8cfa6 | note | Verification Activity: By - ENG
850433b6-6282-4cb6-b5ef-63f3203853c0 | signoff | AUTHORITY HOLDPOINT
efda3374-67ed-4c3d-aab6-287f314217f4 | checkpoint | 1.2.3 - Particle Size Distribution
e5a4aaf0-cd15-5c0c-8907-01833dff0445 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
05474fc5-9854-5a7d-87b9-ec4c102492bc | note | Acceptance / Conformance Criteria - No Particles >200mm
783a80bd-3e6e-5fb5-b9a8-13fc553256a4 | note | ○ Maximum fines 10% passing 75micron sieve
3d384da6-c6b1-5fb5-bd30-9c9863950995 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
01f7afe2-fb81-52e0-ab83-b6352c6237e6 | note | Verifying Document - IANZ Accredited Report
62945f89-c600-5943-8e2d-6ac9e8f794d3 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
bc699431-960f-5400-a10a-f9792dc7848b | note | ○ 0-400 - 2 tests
54af8373-d8d8-508c-85b1-b596bbc4ad2b | note | ○ 400-1,500 - 3 tests
97bc0605-d4e5-5786-aa60-90eeb080079a | note | ○ 1,500-4,000 - 4 tests
be292f7e-3d13-5482-92d1-7ea77e965b46 | note | ○ >4,000 - 1 test for each additional 1,000m3
76edf664-22fe-5829-babf-0b0fa99faea3 | note | – Results to Engineer 2 wks before importing
94a4d334-1a17-52cf-8802-0eaad037977f | note | Verification Activity: Activity - HP
7c1439fc-45f6-5868-99e8-c9e27a8e53c1 | note | Verification Activity: By - ENG
f8037966-ccc5-4ebd-946f-55a33132a8b4 | signoff | AUTHORITY HOLDPOINT
ffdf51e2-099b-4bc3-8aa9-8eb24dc5a439 | checkpoint | 1.2.4 - Maximum Dry Density and Optimum Water Content
6a80a402-fed1-5ab4-8735-891b9b3f259a | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
3c82990a-2966-527b-a0c8-e215b8da8432 | note | Acceptance / Conformance Criteria - Report Value Only
39b6effd-914b-514b-90b9-9b378772267c | note | Standard / Specification - Appendix XVIII, Appendix V
fd9c603e-27e1-5be0-907a-846ff1715f29 | note | Verifying Document - IANZ Accredited Report
b945f03a-5a13-5655-9cc4-da40dc8b5601 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
63627248-d4a1-5770-b0d3-9292755c2945 | note | ○ Results to Engineer 2 wks before importing
e3210932-db56-5d6e-b884-b313c9a8ebc6 | note | Verification Activity: Activity - HP
6fa0668e-5f19-518e-8084-f050c0f1c71f | note | Verification Activity: By - ENG
bb65aacd-3b82-4a3e-be21-88c061eb3bba | signoff | AUTHORITY HOLDPOINT
24f31b94-c55b-4494-babc-ce41090c9bc5 | checkpoint | 1.2.5 - Soaked CBR
b0cf16ce-74ed-59f7-9550-397fcf350dfe | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
e47d4ff4-32b9-5826-8626-c7d6fe067700 | note | Acceptance / Conformance Criteria - >25%
15007102-f284-54c6-a07c-f6eeabe117a6 | note | Standard / Specification - PS 16.5.5, Appendix V
3d2d6dc5-3ea6-56be-904b-2cb62c33028e | note | Verifying Document - IANZ Accredited Report
b9e8388c-1782-56db-b8c4-4033476f45ab | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
1e27e463-22e1-5ca8-853f-0a717139d760 | note | ○ Results to Engineer 2 wks before importing
ea9cb904-fdb1-5764-84ca-226a10a2ec8d | note | Verification Activity: Activity - HP
87f00616-eed4-5200-97d1-43595bb3534d | note | Verification Activity: By - ENG
f4470fd9-abc1-446f-ad3e-fef78f8f8536 | signoff | AUTHORITY HOLDPOINT
c2d6c7c2-5225-4612-8dff-382c60b87aef | checkpoint | 1.2.6 - Solid Density
a211f159-81a4-5f16-9749-05dae1a64c2f | note | Detail - NZS4407:2015, Test 3.7.1 - The Solid Density of Aggregate Particles
c2c62408-4f26-54f7-9a9b-bfbccf0b12b1 | note | Acceptance / Conformance Criteria - Report Value Only
c7d59b1a-ee60-5807-a359-9a0417c7577d | note | Standard / Specification - Appendix XVIII, Appendix V
f984006f-54f7-5f9b-931a-bcab79f5f55c | note | Verifying Document - IANZ Accredited Report
bdb7c925-c24d-59a9-86bc-486b31c5450e | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
b76cf549-485d-531d-b3ea-293cb8c1a658 | note | ○ Results to Engineer 2 wks before importing
b05ce438-0af2-59f8-b3b9-759f7160b5ef | note | Verification Activity: Activity - HP
ad494320-e326-5fba-a3ac-cb5c0cf72424 | note | Verification Activity: By - ENG
c3fe690d-7235-47be-a001-99480fca0400 | signoff | AUTHORITY HOLDPOINT
55f6818e-9cb2-4849-9221-98695d647053 | checkpoint | 1.2.7 - Crushing Resistance
69631f1d-b15a-5123-83ef-54f9862b5520 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
f2e11580-7622-54b4-9ac8-783a08101e34 | note | Acceptance / Conformance Criteria - >100KN
90175253-7b17-5bc5-b131-5c4e93693a03 | note | Standard / Specification - Appendix XVIII, Appendix V
b674f20b-6e99-5271-a41c-09d102fd25c7 | note | Verifying Document - IANZ Accredited Report
8b64aba2-e772-546c-b5c9-cb013e73430d | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
4bd9d97e-c29b-5aa2-965b-6eb6435f984f | note | ○ Results to Engineer 2 wks before importing
4348b55b-233c-50ed-ac7e-e7f45f3d4a65 | note | Verification Activity: Activity - HP
6793ecce-2d95-52e7-b71f-365337eb94e1 | note | Verification Activity: By - ENG
8ec5394a-aad2-4dfc-8b36-587c27d32e20 | signoff | AUTHORITY HOLDPOINT
e0ff3f8b-86e6-4a82-890e-a55973b66460 | checkpoint | 1.3.1 - Geotextile
499eb3e7-03e0-5062-b030-62be8dd116da | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation.
28458302-2a22-5df8-a90f-7b56779e6e47 | note | Acceptance / Conformance Criteria - Engineers Approval
7d0ae580-4982-5307-b233-3b00ca03d6b5 | note | Standard / Specification - PS 16.5.7, Appendix V
8fcb4c15-fc6c-5141-ab20-333712a65209 | note | Verifying Document - Data Sheets
37989989-ddbf-5768-a256-7701d8dd15c6 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
b2191c4b-7492-5113-b5d3-d6f5fd86b975 | note | Verification Activity: Activity - HP
3c8026be-9dd4-5b81-a99f-4d1f23e68c42 | note | Verification Activity: By - ENG
8f593ffe-d9da-4344-ba7e-b837cefbdeda | signoff | AUTHORITY HOLDPOINT
8479a4bd-6711-484a-b09d-c6642e6fc75b | checkpoint | 1.4.1 - Compaction - Clegg Hammer
ba185bfe-34d6-5e79-b291-84a70f101ff8 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
7d5caeb2-41dd-507c-a6a0-d68c133c07f0 | note | Acceptance / Conformance Criteria - 9 CIV
e70e7165-c595-5fda-940a-885b0634107e | note | Standard / Specification - Appendix XVIII
38dd833a-4402-535c-aff8-e7586a73f87c | note | Verifying Document - Clegg Hammer Report
35d1dedb-960b-5cde-8bf0-621462a992dd | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
6e67567b-12c7-5b09-8a45-79f9c52e1d22 | note | Verification Activity: Activity - I
b0456465-c2ed-51f7-aad0-78a59606d908 | note | Verification Activity: By - SE
b0fe2bc5-d461-454d-aab8-1ad0e2365f5f | section | SECTION 2 – CONSTRUCTION - CUT SUBGRADE TESTING
b25aad17-9f95-41bf-886b-f1c0da0f6856 | checkpoint | 2.1.1 - Proof Roll
7c44a610-aac9-546d-ad1c-92b090bfb06c | note | Detail - Visual Inspection of Proof Roll
14edfdfc-b43b-58ac-b98b-4a0dbefc535a | note | Acceptance / Conformance Criteria - Displacement <15mm
7d22d071-4a56-597d-9e7a-73d23c4d9f1f | note | Standard / Specification - Appendix XVIII
c809b721-04d8-5c18-8779-eae27b69c8c6 | note | Verifying Document - Visual Observation
4d52eab4-57ac-5952-af21-2c737a39a7c0 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
3542baac-de0f-5880-a6bc-6c9cd50d10ab | note | Verification Activity: Activity - V
b86e7420-ad3a-5f1f-91b0-491a22f9d83c | note | Verification Activity: By - SE
e548dcc7-8a77-4900-a139-c6b40bfe6799 | checkpoint | 2.1.2 - Cut Subgrade Inspection
802a779b-af0d-54a2-84c7-df8db746028c | note | Detail - Engineer to inspect all foundation surface inspections
59bc9c3e-c476-574b-a13d-fb02db0b9022 | note | Acceptance / Conformance Criteria - Engineers Approval
50105bc2-5dfe-5ddb-bab9-57eb53375e71 | note | Standard / Specification - Appendix V
09824e2e-bbe9-588d-adb9-9a78fbcc493b | note | Verifying Document - Visual Observation
1beb47c1-9206-50bb-bc42-30cb96dd8ebb | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
0a1ba364-f39a-5993-ba89-ceaefb54e321 | note | Verification Activity: Activity - HP
a67e8c7b-d622-567a-aab3-465ab576124b | note | Verification Activity: By - ENG
5d70dadb-e012-4470-98dc-e990aca6af52 | signoff | AUTHORITY HOLDPOINT
16fbda90-0633-4e65-8c39-d95196b98b3c | checkpoint | 2.2.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
b6d525d4-48c5-56c2-8b06-d1cfc55e8539 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
80053b84-2254-5a40-b848-fb77ea349b2f | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
54e9ea4c-42aa-56c7-8228-1adc3dbd732d | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
26af992f-0610-50a0-a1ff-8ba57e20ac3b | note | ○ Single Test Min SU: >50kPa
cb98c106-fb9b-52a2-bf12-ada31844efee | note | Standard / Specification - Appendix XVIII
4f61b6a4-0af1-5c10-b6a5-efe4e3223dda | note | Verifying Document - Shear Vane Report
7c8085b3-7634-5963-8c16-494660f3d2fa | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
58c9409b-a1cd-5e42-bd91-d3e150c74afb | note | Verification Activity: Activity - I
89272bcf-2ca0-512d-bf75-8d0d8c1b6aaf | note | Verification Activity: By - SE
6910f6a0-c2dd-4113-a6c4-e95816430985 | checkpoint | 2.2.2 - Cut Subgrade Testing - Cohesive Soil Scala Penetrometer
e3ef30b6-a7de-5b34-a02d-a60a9963f587 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
74681f98-af2f-595d-a145-d13ce4419e4e | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
129ddc91-515f-5059-b0cd-a2d429f67152 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
68437886-55c8-57c2-97a0-d3952a4dacf6 | note | Standard / Specification - Appendix XVIII
f2fca783-effc-562c-aff3-defa848c9c84 | note | Verifying Document - Scala Report
58f2c4ad-f5b7-57c0-aab0-990fa4c8d4e2 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
810a7b4d-1286-55a7-9455-de997a57a99d | note | Verification Activity: Activity - I
87578ed1-1259-5fdc-b531-946549b10ce6 | note | Verification Activity: By - SE
98a2275d-c6d3-4203-8622-932b785521e4 | checkpoint | 2.3.1 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
c57673b3-36aa-5aaa-a4f5-96145f5f0cb3 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
bf00692b-91c0-5550-bd48-6050455e9fdd | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
4e96809e-9c8c-5432-914e-57919538b785 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
c277027a-5318-5fa7-a324-144c992734f0 | note | Standard / Specification - Appendix XVIII
a08fb907-2794-51f2-8887-7591d38635a0 | note | Verifying Document - Scala Report
eccddbc4-f52c-51c6-ade8-0833303a51b6 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
56de6bfc-dbf2-588e-8b96-ca27b62ae385 | note | Verification Activity: Activity - I
9ff0ec38-0d65-5b1a-a3ce-9fb6739d584b | note | Verification Activity: By - SE
bb46cd09-db95-453e-933f-b090c7275d3d | checkpoint | 2.4.1 - Release of Hold Point
e2c35c78-2572-5521-9864-319a0fa57169 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade complies with the requirements of the project specification - PS 16.6
57256ee3-f62e-5996-861e-07a80056b2a1 | note | Acceptance / Conformance Criteria - Engineers Approval
de5a3679-a3e1-5f0b-a46f-3ae6793bec5b | note | Standard / Specification - PS 16.9.3
33f62c93-07fa-5df1-b596-b57b15d65057 | note | Verifying Document - Hold point released
2471ecb1-5291-569e-aa26-45e0a1a80c0c | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
ad7d1533-d40c-5d0e-99ce-647fae8cf9db | note | Verification Activity: Activity - HP
5401b672-9f9f-55fd-95af-2c6cedeaab0e | note | Verification Activity: By - ENG
f90214b3-18db-4a00-a736-e1a8bb82993a | signoff | AUTHORITY HOLDPOINT
90e576d8-cc5c-4fd7-92e3-2960aa6506bb | checkpoint | 2.5.1 - Subgrade Level Confirmation
31751713-e6ca-5720-b0d4-8f516b9f7b38 | note | Detail - Confirm subgrade is 735mm from finished height
dd204690-627f-5eb2-86f9-782fe2d570fc | note | Acceptance / Conformance Criteria - String lines - or equivalent are 735mm +0mm/-30mm
09351d8e-7d11-5e71-98c5-9513c4c6528c | note | Standard / Specification - PS 20.14.5
cb0c4664-0fd2-582b-9fac-1095cc5641c2 | note | Verifying Document - String Sheet
5e3b7a11-2f6c-5b0e-adfe-302686547bce | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage
5bcc0761-2a2d-5bdc-afa4-a45f5f706abd | note | Verification Activity: Activity - I
07544134-ee67-5742-aa15-ecff47c57209 | note | Verification Activity: By - SE
bd03d26c-f49b-42a6-b5df-049394ab4049 | checkpoint | 2.5.2 - Subgrade CBR Testing
eb2abe03-3b62-59ce-b773-f65d8d0cb364 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
18345c87-655b-591c-96fd-55b5f89d9f8d | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
233be916-a020-580e-bdef-15039726e1b5 | note | Acceptance / Conformance Criteria - Pavement Type 1
cf7071d8-6519-5dd4-9ab2-f17eadeb4f09 | note | – CBR >6
4ee83d8e-5f05-557c-bd90-73bfd7018c27 | note | – Min 3 blows / 100mm
97c0d418-8b27-5c24-97c2-d6aa124028c2 | note | ○ Pavement Type 2, 6, 7
2a30d082-745e-5208-815b-aad55a904971 | note | – CBR >2.5
fc6a4d4d-fab9-5c41-b97b-f65484234045 | note | – Min 2 blows / 100mm
70b4c641-9cd1-5976-b2bd-66a824d21548 | note | ○ Pavement Type 3, 4, 5, 8
04cd5ab5-a2c7-5aed-b5d7-c07a6e2498ca | note | – CBR >3
1af515a7-e2df-524a-be8a-321faa83c230 | note | – Min 2 blows / 100mm
df511d36-8c75-53da-851a-f6a25cd35646 | note | Standard / Specification - PS 20.4.1
035298bf-e34f-5501-a5cb-961fc581cfda | note | Verifying Document - Scala Report
890bc04d-8045-5eda-abc6-f47351870744 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100M2
f2616a21-4e62-55ec-92ce-1fb6748ffe13 | note | Verification Activity: Activity - I
6cad3431-aecb-5574-81f3-c268475e72d7 | note | Verification Activity: By - SE
69b4c20b-b692-414f-9292-fd600c88bad6 | checkpoint | 2.5.3 - Release of Hold Point
8ddd67c6-ace5-5871-affc-505da18d001c | note | Detail - To release the subgrade hold point and be able to start placing pavement layers, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
2634c5bc-2fa9-50cc-a0c1-24a7412ebbb0 | note | Acceptance / Conformance Criteria - Engineers Approval
57f5350b-d90a-5c16-b167-e0b82030a2c4 | note | Standard / Specification - PS 16.9.3
e3489ad1-dc7a-5654-924b-1520fabca738 | note | Verifying Document - Hold point released
41b6c4a2-875e-5fe5-93ec-34e4fd28b080 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
03743c6b-1193-50e0-b283-c10b6f9c0f12 | note | Verification Activity: Activity - HP
ab30ef15-d65e-5e96-833e-816d96620267 | note | Verification Activity: By - ENG
4b3a292c-5e2c-4592-bf22-ecf0a17bc575 | signoff | AUTHORITY HOLDPOINT
e3838121-13aa-456e-ab15-cb42ae242859 | checkpoint | 2.6.1 - Release of Hold Point
a9272ade-1f15-5893-8405-61ba1b7e1507 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
170c4c56-6bfd-5526-8829-62c778c5919c | note | Acceptance / Conformance Criteria - Engineers Approval
25b59fca-5824-55ea-8831-7c8883b27644 | note | Standard / Specification - PS 16.9.3
6e5e0851-dc28-5001-8b66-def9acb6068b | note | Verifying Document - Hold point released
d17ce4fd-6858-586d-a868-2c409a653898 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
3321fb00-22af-52ab-ae26-64f76d924342 | note | Verification Activity: Activity - HP
96126ca6-f571-5b96-a0c8-f00856c79af2 | note | Verification Activity: By - ENG
d6d021b3-b559-489b-b10d-9dc88d525c9d | signoff | AUTHORITY HOLDPOINT
b85c944c-29db-45cf-98aa-18d7c5d46f27 | section | SECTION 3 – CONSTRUCTION - UNDERCUT TO WASTE & BACKFILL
d85b9ad6-dbe5-42ce-bfea-135c90bc50c1 | checkpoint | 3.1.1 - Undercut Surface Inspection
cd33c94b-cfcc-5375-ac11-a5424f1b1d06 | note | Detail - Engineer to inspect undercut surface
55db45b7-85f1-5ffb-94b2-ba0f73ea8c2d | note | Acceptance / Conformance Criteria - Engineers Approval
b77a59b3-041a-5b1f-a967-68165ce41cbe | note | Standard / Specification - Appendix V
d743ad26-3a6d-533c-86e2-8878d5b16570 | note | Verifying Document - Engineers Approval
1a9fa6f3-91c6-55dc-88d9-419eb2abd59f | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
d8f9c1f1-b971-54d4-b0eb-6cf46bef6595 | note | Verification Activity: Activity - WP
492085f2-dba0-5904-9245-a9f1260ad2c8 | note | Verification Activity: By - ENG
dd4d6de1-af98-486e-8ccc-9e9d980df449 | checkpoint | 3.1.2 - Placement of Geotextile on Undercut
401d021e-fc97-512f-af2f-085193ffc4f1 | note | Detail - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
c0ed44c6-777d-56ae-a8f8-f5558d16a49f | note | Acceptance / Conformance Criteria - Engineers Approval
72ae6244-2dd7-5c94-80f2-2d25a8ec3ba0 | note | Standard / Specification - PS 16.6.4, TNZ F/7: 2003 8.3
d37b9680-c0ba-530c-9c7e-8e36543956a2 | note | Verifying Document - Photos
3c5918f8-cf4a-52de-9a2c-442afda763d4 | note | Testing Quantity Required (based from schedule qtys) -
85fc08b7-6e40-5d73-b346-26f5a64b5f32 | note | Verification Activity: Activity - WP
ac469fa2-0bcf-5ab9-873e-3eb4dc5de405 | note | Verification Activity: By - ENG
72f8681a-a3da-440c-bae2-b07d39be9e4d | checkpoint | 3.1.3 - Subsoil Drain inspection
4413dc54-09ed-58bb-9b6d-af26a609b767 | note | Detail - Subsoils to be placed at base of cuts where directed by the Engineer
d8767c0f-6b70-5a97-93a5-105495d9cc72 | note | Acceptance / Conformance Criteria - Engineers Approval
9ba6c479-87af-5157-a341-ac8fcf3015be | note | Standard / Specification - PS 16.6.4
4eaa83af-1112-5e89-ab2d-8ac1c45c7769 | note | Verifying Document - Photos
39ffe601-51f0-5b23-a77d-044b3d051ecf | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
27c5b002-4dd5-57a5-a14f-7d5f6c496170 | note | Verification Activity: Activity - WP
91741e7b-81eb-572f-a343-e872ff509c2b | note | Verification Activity: By - ENG
501ba117-3dad-478f-84d0-648246f93493 | checkpoint | 3.2.1 - Release of Hold Point
bfa29bb4-58da-5d2c-a3f7-295303333eba | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
e2720518-6484-5917-add2-4c765cc25618 | note | Acceptance / Conformance Criteria - Engineers Approval
344b9972-a7de-537c-b292-2dae112896d9 | note | Standard / Specification - PS 16.9.3
4049e86b-b61c-597d-8d5d-ed21edbffb5f | note | Verifying Document - Hold point released
c105c5cc-629a-5f68-838e-af983d196363 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
d3e715cc-f759-523e-a3e1-b788374aa11b | note | Verification Activity: Activity - HP
026a6091-33bc-543d-8d0c-07d2d35af0a6 | note | Verification Activity: By - ENG
25543144-e012-4919-8f7a-ddc6e33036e9 | signoff | AUTHORITY HOLDPOINT
05f763ae-27dd-4b10-92b7-f2447437a290 | section | SECTION 4 – CONSTRUCTION - COMPACTION OF IMPORTED FILL
1a477d7f-bb1b-46a9-b7a1-860a2a9e22dc | checkpoint | 4.1.1 - Placement of Geotextile
509b6537-0099-555a-b2da-737ff8bc4097 | note | Detail - A layer of Class B Geotextile Fabric to be placed between cut surface and imported A1 Structural Fill with 500mm overlaps
6acd658d-028c-5fbb-97d0-ba3aea8a65d7 | note | Acceptance / Conformance Criteria - Visual Inspection
a05a9376-7bfe-525d-bb25-382152137661 | note | Standard / Specification - NTC084
de7feb83-e69e-5a24-8362-626ee0358e04 | note | Verifying Document - Visual Observation
6ec7b33b-2a07-518f-b44f-b8b30ae86dbe | note | Testing Quantity Required (based from schedule qtys) - As Required
1badb84d-979c-55cb-aa73-2f640f763d31 | note | Verification Activity: Activity - I
5a96edd8-3047-5ac3-a92f-bc23c02f8424 | note | Verification Activity: By - SE
6c38888a-71d0-481f-ac4c-cb0ab1a3ab2b | checkpoint | 4.2.1 - Compaction - Clegg Hammer
738f7f59-087d-50ef-ab2f-8a547c87943f | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
dd0978f6-bcac-5122-aaf9-4e487b4d4339 | note | Acceptance / Conformance Criteria - Structural Fill
052f008a-2922-5eec-ba5f-a788adc8d4ff | note | – Min CIV 18
1138f60e-6b87-5eb1-9b09-feb617c07f4e | note | – Ave CIV 20
7b793600-6db1-59f5-ba6b-a7902e72004c | note | ○ Non-Structural Fill
dab79e9a-7aa5-5591-b2e9-7e763b03e92d | note | – Min CIV 10
c33b7681-e3fe-5df9-8674-70e1b61ad771 | note | – Max CIV 12
bd04d59a-d4a4-566c-b7f1-755d8b16d681 | note | Standard / Specification - Appendix XVIII
e0c01415-20a1-5157-b360-321a750c66c8 | note | Verifying Document - Clegg Hammer Report
298cc7ca-0e6d-5bc8-b3f0-20a801d63ce4 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
6ec4df28-6db8-546b-8ae9-dfb41a4249c0 | note | Verification Activity: Activity - I
f3ae9792-731d-5782-ab5e-1a15e4ddeb81 | note | Verification Activity: By - SE
3fe4601e-c0aa-4383-8ce6-88d90bb98957 | checkpoint | 4.2.2 - Compaction - NDM
4ebf5a77-d909-5f7f-b8eb-e001765a459d | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
2bf190d6-4993-5e6b-8dfe-733c53f1bd0d | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
31c663b8-86b3-5063-9ce4-500a0924bc82 | note | ○ Non Granular Material
a01b40fe-d860-5f8d-879c-bcb2c60788bd | note | – Max Air Voids 8%
863d9c7f-cdf4-51cb-a834-cd27b3b4326a | note | Standard / Specification - Appendix XVIII
4a1c1302-07b3-53dc-8495-b9e09b23448e | note | Verifying Document - IANZ Accredited Report
2cd10ec3-273e-5366-b5cd-6f326eaf7c43 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
4903f512-9540-5764-adbf-0535c70de76e | note | Verification Activity: Activity - I
20faa1bf-d90f-5f5f-90ca-e59b02087600 | note | Verification Activity: By - SE
41b823e2-1640-43b3-a1a9-ac174fbb8289 | checkpoint | 4.2.3 - Compaction Trials
436f8cf1-ffff-5577-8c1b-1b119bff09ee | note | Detail - The Contractor shall carry out compaction trials of the various soil types and combinations on site, and any imported fill materials, using different layer thicknesses, types of rollers and conditioning plant (ie construction discs and scarifiers). The trials shall be conducted over the duration of the earthworks operation with the objective of determining the most suitable and efficient techniques to meet the compaction requirements. The trial details, test data and conclusions shall be reported and copied to the Engineer within five days of completion of each trial.
05a703ae-00d4-502d-9bdb-9801d8149c75 | note | Acceptance / Conformance Criteria - Engineers Approval
a2cb9619-9ca3-5760-91e7-d42e0a5b898c | note | Standard / Specification - PS 16.6.5
8b2f1700-277a-5199-9e39-bd99117960cc | note | Verifying Document - Trial Results
707538c8-e68a-514a-a62d-63af7aee88f3 | note | Testing Quantity Required (based from schedule qtys) -
63b41250-9606-5605-b4f9-56ef41123643 | note | Verification Activity: Activity - R
3815bfc3-a198-5f87-8c8a-7e95d182f36c | note | Verification Activity: By - ENG
64908577-c580-4600-9123-29a2f7c55f35 | checkpoint | 4.3.1 - Compaction - Structural Fill Scala Penetrometer
5dfac380-27a7-54ed-b302-72cfc94b7580 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
eb02f41c-b099-587b-b555-dacced7fec8c | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
2b803d1b-466f-5b9c-98e1-49925e2df4a8 | note | Acceptance / Conformance Criteria - Minimum 5 blows per 100mm penetration
c93696e8-ffb0-51ab-93d3-013cba0b4a4e | note | Standard / Specification - PS 16.5.12
7662651f-bf37-56cc-b262-47d16110be7a | note | Verifying Document - Scala Report
16225484-c0d2-521a-9d47-c4da947e66f8 | note | Testing Quantity Required (based from schedule qtys) - Minimum 1 test per 500m3 of filling evenly distributed over the extent and depth of the filling. A minimum of 1 test per 500mm lift or part thereof to be completed through the full lift thickness.
c5e187bb-4939-5046-b8a3-de1db913c0c4 | note | Verification Activity: Activity - I
941a690d-888c-5135-b282-7f40fc897295 | note | Verification Activity: By - SE
16da8ce6-3eb3-4aa2-9c0f-cb5326e9ccb1 | checkpoint | 4.3.2 - Compaction - Structural Fill NDM
1ea87b41-922e-51f7-bbac-f5ac49ba7823 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
726ca3dd-365c-5aab-b1ed-f9d261e569f7 | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
d8cd8c27-2381-539a-a3aa-8c7b795c7a2b | note | Standard / Specification - PS 16.5.12
3b0d2f79-2139-5eb2-bd30-a1c43ce71b18 | note | Verifying Document - IANZ Accredited Report
f244003d-f71c-5484-badf-ae6e7db3eb92 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
f00e77b8-6f2b-5583-bc9a-d678ccbee5cb | note | Verification Activity: Activity - I
d24709ba-b704-57e7-90a2-470f066486ad | note | Verification Activity: By - SE
8a61aab7-dfc3-44ca-a986-6dcb1bad7ec4 | checkpoint | 4.3.3 - Pumice Sand Fill
a860a83b-830f-5cb4-920e-424879252086 | note | Detail - Pumice Sand Material shall be contained with an outer layer of fill with a minimum thickness of 600mm. Must be Hardfill and/or imported Type A1 material and/or Type A2 material and/or Type A3 material
818594b2-876e-5de4-9378-cb53c10acb54 | note | Acceptance / Conformance Criteria -
f433b870-5d84-5f10-834a-6cf43350b69c | note | Standard / Specification - PS 16.5.12
4c164150-3d89-5b28-b719-3f3727bfa48b | note | Verifying Document - Site Records
f0074700-70d9-548e-af59-3a8651186146 | note | Testing Quantity Required (based from schedule qtys) -
cb959169-fbdf-51ac-b2b6-a7a29ee4b133 | note | Verification Activity: Activity - E
d8b0615b-e718-5a4d-a4c1-d25cd6f35b6d | note | Verification Activity: By - SE
de6ca4ae-557b-4d21-a6bf-aff6d3c9aada | section | SECTION 5 – AS-BUILTS
82f88d2c-afa4-4b25-a0cb-97c4f1ceed3d | checkpoint | 5.1.1 - As-Builts
e953a216-b3c8-56bb-a727-4feee46a2dd0 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
f0cfb15a-dfdf-5596-a741-16283765dcb6 | note | Acceptance / Conformance Criteria -
907821e5-8148-5e0a-9a11-3d58d3ba82f5 | note | Standard / Specification - PS 16.7.6
54bf521d-ef3a-57c9-b5f2-bb3a645e8d34 | note | Verifying Document - Survey Records / Redpen markups
d7286cc2-32ae-5d9f-8935-f2877bb578f6 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
6ecb3006-2660-5a36-a033-a58c1ad4de38 | note | Verification Activity: Activity - D
80702710-d31b-5c91-9d3c-e823087a4ab7 | note | Verification Activity: By - SV
bb3b2017-5215-4a2d-af74-4df7b9be66d1 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
1476d4ad-8734-592d-a70a-9630d7e1cf97 | textbox | Contractor's Rep Name:
ccdcf735-5e01-571e-af47-f4a0514e45c8 | textbox | Engineer's Rep. Name:
45799344-c8bb-5d8c-a127-4eeca12894d5 | date | Date:
77d64376-76f5-4734-b1b4-312475957ff7 | signoff | Add Signature
e8a51180-e519-5178-a260-808bdd591ab6 | checklist | DN1210-003 ITP Earthworks Rev IFC5 | itp | EAR-DN1210-003-LOT-001-Zone 1 North-A
8508ff53-5f3a-5f4c-8d26-a8afd00d3eae | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS
fa40f6b3-5282-5e90-aaa6-c7c2328827d1 | checkpoint | 1.1.1 - Earthworks Methodology
0d104855-89f4-593a-85bd-a50e0fe9215f | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points for review and approval prior to works.
25a842ae-f368-56bf-896b-35fc18939be2 | note | Acceptance / Conformance Criteria - Engineers Approval
bcf47cec-4f3a-530c-9d04-d1129bd3fe6a | note | Standard / Specification - Appendix V
37a6a238-f616-5b99-a3c7-9f3188b36a68 | note | Verifying Document - Approved Methodology
39b5f231-e8ac-5ae7-ae5b-1d3a6d1a3e2c | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
7fc060d6-a7d5-5929-b685-00c4c82f5444 | note | Verification Activity: Activity - HP
de17480b-9985-509f-b3bc-3d9282f4410e | note | Verification Activity: By - ENG
0810d078-72c3-5cc9-b875-7cd778a6935d | signoff | AUTHORITY HOLDPOINT
f4cd2823-6ed1-52de-8392-a796d0472357 | checkpoint | 1.1.2 - Ecology Sign Off
cab789a8-b93b-5ae2-8087-75845ee54abf | note | Detail - Confirmation from Ecology that earthworks can proceed
56e8fc5e-abb4-53f4-95cd-424f70f8dea3 | note | Acceptance / Conformance Criteria - Email
54b8b3a8-a4b8-5826-84b2-0394718c82c0 | note | Standard / Specification - Internal Hold Point
5b86395a-bf45-5246-af35-80455d218425 | note | Verifying Document - Email from Ecology NZ
c89c534e-0044-576a-bc67-1065b357bdfd | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
2ea624cd-7e2b-5a5c-8310-b435b1f9d82d | note | Verification Activity: Activity - H
4714b52a-304b-57fd-a3c9-afe336ad757b | note | Verification Activity: By - QM
efd14769-e8c6-51fc-8d27-f504bf699318 | checkpoint | 1.1.3 - Erosion & Sedimentation Controls
90189df5-862e-578d-ac66-0cec0908d406 | note | Detail - Confirm that Erosion and Sedimentation Controls are in place prior to earthworks proceeding
60bf084c-2ef1-5d5d-bb11-3730f8061b1c | note | Acceptance / Conformance Criteria - As-built Completed
e50e3322-03bc-5b50-a82f-b1b5726dfa72 | note | Standard / Specification - Internal Hold Point
a6624630-2f33-5e2f-9195-8980356dc0db | note | Verifying Document - ESC As-built
eccc1421-408d-5927-9abf-dafa4be2987d | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
98deee31-b439-56dd-bbc4-ce083ff8680d | note | Verification Activity: Activity - H
54de11cd-f76c-5415-91b9-aecf8d005251 | note | Verification Activity: By - QM
0d87e467-4cb2-552a-ac73-f66d3a3d9150 | checkpoint | 1.2.1 - Weathering Resistance
455b43de-ffc1-5af2-a1de-cf40fa18ea41 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
f8552aff-4b9f-5d2c-a904-d6da94d55840 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
303ebd44-48a4-571f-842c-465066d59d51 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
f35bdac5-7335-562e-a47e-19736f7337b6 | note | Verifying Document - IANZ Accredited Report
f5d5ff0f-2b7c-5113-b628-c021affab5ff | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
8fe01f64-c7b3-59ce-8bdb-e04d432f27e1 | note | Verification Activity: Activity - HP
27b4c96d-f6f1-577e-832e-aca2fad4548c | note | Verification Activity: By - ENG
b743bb5e-1c16-53b6-b8bc-16628422b606 | signoff | AUTHORITY HOLDPOINT
084e82bd-1f23-51d2-8dc8-d681090cbe21 | checkpoint | 1.2.2 - Los Angeles Abrasion Test
6d44388d-ed58-540b-ba94-b9114a6f53d0 | note | Detail - NZS4407:2015, Test 3.12 - The Abrasion Resistance of Aggregate by use of the Los Angeles Machine
6af9c5f7-9082-58c6-a445-b02aea78da9a | note | Acceptance / Conformance Criteria - 0.5
81f1e4c6-0496-593b-aaf7-2460f9b0bc05 | note | Standard / Specification - PS 16.5.5, Appendix V
83bdb4ff-97b9-5efb-bb6b-0afeb201ad98 | note | Verifying Document - IANZ Accredited Report
2233790e-3df5-58d8-950c-3a824e566622 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Required, Results to Engineer 2 wks before importing
4e604921-3ac9-5f94-aa82-22b57f94de55 | note | Verification Activity: Activity - HP
147b59c3-fe37-534c-9bbb-5d24fd9d31a4 | note | Verification Activity: By - ENG
8bc26f80-2039-56bd-bb37-e46ffc1c9fe7 | signoff | AUTHORITY HOLDPOINT
d93131df-e262-5431-b317-9d9d9006e3ee | checkpoint | 1.2.3 - Particle Size Distribution
a247f6ea-c2f1-5c89-a542-e6c3b691162b | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
a5ae7ee5-97af-5ab1-a4a9-f34f0615fc4a | note | Acceptance / Conformance Criteria - No Particles >200mm, Maximum fines 10% passing 75micron sieve
30c42a9c-5468-5ddc-8294-ee4b44b237fe | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
af373d42-19f1-5ebe-9a47-dee81487a830 | note | Verifying Document - IANZ Accredited Report
1107cdc3-faec-5731-a82c-a43b17dd3fb0 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
a1e0c85f-e622-50ce-9b8b-a2a1ff24b887 | note | ○ 0-400 - 2 tests
77c7929e-be41-5f74-9c23-69d4baa66048 | note | ○ 400-1,500 - 3 tests
81c9e55d-68ec-593b-955c-8cfe75a66d11 | note | ○ 1,500-4,000 - 4 tests
c8a6f68a-17d0-57ec-873e-fdf59f3bd15f | note | ○ >4,000 - 1 test for each additional 1,000m3
e8a86c27-404e-5dcf-ad75-7093fad8fc25 | note | – Results to Engineer 2 wks before importing
cea069ba-656a-5d8b-a896-3a16bc7a2650 | note | Verification Activity: Activity - HP
7fddd767-f5a6-5c7c-b124-9737d1789702 | note | Verification Activity: By - ENG
cfc336bd-ca9a-5b9e-abd3-a9fa9f2c427e | signoff | AUTHORITY HOLDPOINT
2291f8cc-7920-56fb-b158-84bfdf300c25 | checkpoint | 1.2.4 - Maximum Dry Density and Optimum Water Content
e3bb3786-dfb5-5944-80d0-3bca0eae2690 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
c9c03eee-c3c6-5b8f-bf85-9c8cc2963a5a | note | Acceptance / Conformance Criteria - Report Value Only
735a4b90-cf66-5701-b2ec-83c51d897255 | note | Standard / Specification - Appendix XVIII, Appendix V
b6933e85-9e77-5e0d-ac53-02b2bb6ed28a | note | Verifying Document - IANZ Accredited Report
c90cab11-e5f8-5e38-af10-b817d24bac03 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
e92c2404-f896-5eb7-96ad-0389257f7de1 | note | Verification Activity: Activity - HP
ddbd66dd-516f-5c64-9c78-5a56b46248bd | note | Verification Activity: By - ENG
575e78dd-342d-5a92-8d82-7739e63face1 | signoff | AUTHORITY HOLDPOINT
f1395031-71d6-5468-bf80-c760a6ab6370 | checkpoint | 1.2.5 - Soaked CBR
405d3666-c324-5372-8944-f29095b45593 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
8b3db5d7-2af7-5ece-82a4-c56b78a1e74d | note | Acceptance / Conformance Criteria - >25%
b9dea11c-5f41-58bc-ac45-51cb9785a966 | note | Standard / Specification - PS 16.5.5, Appendix V
a0188409-65e1-5017-ae63-28794e961176 | note | Verifying Document - IANZ Accredited Report
5d8ecde9-fa21-58ca-b177-86a352aeb58b | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
4568dd7f-8d2f-5e6f-b936-479b8a1f7dee | note | Verification Activity: Activity - HP
a85d81f3-c063-51ca-8606-a7cf85fcdc13 | note | Verification Activity: By - ENG
931a1aa8-1380-5a21-bb4d-7282459c2c4a | signoff | AUTHORITY HOLDPOINT
51757bfb-8689-56b5-85cc-9ee5c479f783 | checkpoint | 1.2.6 - Solid Density
86feadec-2cf4-54f2-92ca-451a5718cf11 | note | Detail - NZS4407:2015, Test 3.7.1 - The Solid Density of Aggregate Particles
c0c95f97-4b89-571b-9b8a-3eb659c2137c | note | Acceptance / Conformance Criteria - Report Value Only
4b795ca1-e4f8-5e95-b7aa-b41b5ce72d32 | note | Standard / Specification - Appendix XVIII, Appendix V
6af41c27-9d65-5220-96d6-422dfba7bede | note | Verifying Document - IANZ Accredited Report
0e33c057-1ab0-59b0-aa65-0d9e4596204e | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
e70b4675-8a59-557b-bc32-7e541f2bcb2c | note | Verification Activity: Activity - HP
4c5917fd-dd41-5f03-8fb8-0d49e52f5baf | note | Verification Activity: By - ENG
4ff72493-ec09-5550-980d-b8ce9f81958c | signoff | AUTHORITY HOLDPOINT
f3c7ffc2-519c-5933-8152-8d50f951f298 | checkpoint | 1.2.7 - Crushing Resistance
e3895585-b89f-5ff3-a848-8bd602992717 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
7c707ea0-5bf2-515e-851d-5a872650e550 | note | Acceptance / Conformance Criteria - >100KN
a86e42bb-c961-58ca-8d7d-2f2810d541fe | note | Standard / Specification - Appendix XVIII, Appendix V
789dae34-e3d8-59c1-baea-43317b01c78d | note | Verifying Document - IANZ Accredited Report
9a719381-f8b5-5c9c-a7d3-f70743da7f1d | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
c8ea3b12-2b63-57ab-8fb2-bdc4261830b1 | note | Verification Activity: Activity - HP
37d17fc2-2563-5cf7-885a-aaded160a990 | note | Verification Activity: By - ENG
18198a09-45c8-58df-b28e-13ce7c3dc8f8 | signoff | AUTHORITY HOLDPOINT
d14ec928-f5ca-5c95-8a07-42e01557e8ce | checkpoint | 1.3.1 - Particle Size Distribution
5500a823-de90-5fae-b654-46fac739d405 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
fb118fa7-7067-5703-a701-3521776172af | note | Acceptance / Conformance Criteria - Report Value Only
c0c1507c-ef34-5ff8-b5f2-2d67df5faa81 | note | Standard / Specification - PS 16.5.12
f629e6c6-6c58-5b68-b3c7-f663ac7e7ecd | note | Verifying Document - IANZ Accredited Report
3f63d8cf-77d4-5e1f-898e-de00f21d5404 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required?
e989a096-c208-544e-b3d3-79a5413d7251 | note | Stockpile size:
b2fc4c02-b88c-5191-860a-8fd102257e24 | note | ○ 0 to 400m3 – 2 tests
b9c060e1-3635-5a39-abe6-32c06bcaaf86 | note | ○ 400 to 1500m3 – 3 tests
2bf659e3-f2c6-5582-9b7a-6b45dc6096c5 | note | ○ 1500 to 4000m3 – 4 tests
77c86e10-7365-56fd-b6e4-4d3cd7293646 | note | ○ >4000m3 – 1 test for each additional 1,000m3
2e4a7d5c-6504-5210-b630-49aee01502f6 | note | – Results to Engineer 2wks before importing
98a632fe-7838-5415-83bf-bcdbcd57418d | note | Verification Activity: Activity - HP
40ab8af6-15c9-56b6-9825-58a59e44fc21 | note | Verification Activity: By - ENG
3e090f90-6d14-5042-ae03-d0f85981b5d0 | signoff | AUTHORITY HOLDPOINT
33862698-337a-599f-92ba-d701669d85d9 | checkpoint | 1.3.2 - Maximum Dry Density and Optimum Water Content
56d35ba2-765a-58eb-847e-ecb2a74da5e3 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
ac589409-3515-5145-898d-cce30efe5571 | note | Acceptance / Conformance Criteria - Report Value Only
e434a1b1-a134-552e-87c8-633a2375f5fc | note | Standard / Specification - PS 16.5.12
c30be714-03f2-52c1-b30d-506b1280e513 | note | Verifying Document - IANZ Accredited Report
9d9e5a1f-8a0b-550a-b5eb-12e72cf9c410 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
05cd823d-e183-52a6-9e4f-fe4022db5aaa | note | Verification Activity: Activity - HP
1136acd7-a8da-533f-8fdf-30e0d8cd75b9 | note | Verification Activity: By - ENG
a211f4ec-e2a7-5d58-86a4-27239dd6b739 | signoff | AUTHORITY HOLDPOINT
b6a22ad6-5fc9-58a1-a864-f178b18a9095 | checkpoint | 1.4.1 - Crushing Resistance
16c2530f-9a49-54de-8328-b7d6d3aa0ffd | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
aa510cf1-5dec-5617-8513-48cf38aa40c0 | note | Acceptance / Conformance Criteria - >100KN
b3e554f2-3531-538b-be07-66f41752baf6 | note | Standard / Specification - Appendix XVIII
e05b8394-37d9-5b43-970a-2b3f5a2d638c | note | Verifying Document - IANZ Accredited Report
8830ac9f-4dbe-5315-ad7f-39f34c3d3407 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
9dfbdb6f-bc40-5bdf-ad5b-3ccf30f3ffee | note | Verification Activity: Activity - HP
d65ba4d4-1351-57c0-ade1-641d6be463ea | note | Verification Activity: By - ENG
a398b73d-efa3-5256-ae85-9411c1e2ca37 | signoff | AUTHORITY HOLDPOINT
3f788f51-4f7d-5c69-b850-f5390fcb2c2e | checkpoint | 1.4.2 - Particle Size Distribution
7c63cec1-d77f-571c-82f5-f04a3fe85bd3 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
e257efc7-a9b0-583a-927c-7cc989ea73ff | note | Acceptance / Conformance Criteria - Max Particle Size 53mm, Max 10% passing 13.2mm sieve
080b8c60-2510-5f1d-a9bc-62fd78e805d6 | note | Standard / Specification - Appendix XVIII
20af941c-9c90-5052-83f2-a997a07fd26a | note | Verifying Document - IANZ Accredited Report
3d076029-5037-5ffe-b7b7-a4d803a2cbd1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3, Results to Engineer 2wks before importing
f3cc4b76-e86e-5cd5-b78b-2cb413dedc6e | note | Verification Activity: Activity - HP
aa4e1f07-9947-5ccc-9368-37ecdbc742e1 | note | Verification Activity: By - ENG
ad8b4c0a-d700-5a74-8728-bbff13e996d3 | signoff | AUTHORITY HOLDPOINT
3356783d-4613-55b3-837d-756350b0e3a3 | checkpoint | 1.4.3 - Weathering Resistance
ea32fa72-b426-5fce-8499-e60b73cb0cc0 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
d53186d9-99b3-50e1-ad38-3116af32fdb1 | note | Acceptance / Conformance Criteria - CA or better
43cc3027-84d8-5f0a-968c-6a110e28fc24 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
56a7ef2d-1538-5382-ab04-2a5d78ce4f43 | note | Verifying Document - IANZ Accredited Report
45a931e4-c16b-5b2d-a219-99b82043c1a7 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
4f11e08b-a428-5496-9f61-7f9fefa86fee | note | Verification Activity: Activity - HP
8cd1c7e3-2ff9-5744-aeff-4108c6661726 | note | Verification Activity: By - ENG
ead9a554-7f33-5535-8618-d239ca258e84 | signoff | AUTHORITY HOLDPOINT
cfa973b9-821b-5366-9e96-aef5debe1f37 | checkpoint | 1.5.1 - Geotextile
3a88df61-3f1a-550c-94d9-b7af2c87bf57 | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation.
f32ac2fc-585f-5298-ad31-f1bf364ebe5f | note | Acceptance / Conformance Criteria - Engineers Approval
e40b5f84-336c-54fd-acce-915b13a43f8b | note | Standard / Specification - PS 16.5.7, Appendix V
a7859f63-d29a-5e59-b2c7-0459b955ea14 | note | Verifying Document - Data Sheets
43e247ac-a68e-5bc6-8e38-943217724484 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
981ea3d0-0edc-552d-b40f-7a710ccf5c87 | note | Verification Activity: Activity - HP
5ecb55bf-6dd3-5a7e-8b3a-5a025ad69587 | note | Verification Activity: By - ENG
c9f84dd4-62d1-5a68-a153-52aa059ba6e2 | signoff | AUTHORITY HOLDPOINT
a870b3cc-abd4-5d52-8269-fe725225c68d | checkpoint | 1.6.1 - Laboratory Testing for Soil Suitability
010d3206-ba9e-55a2-96ba-898263e8f9ac | note | Detail - Soil Test Results from Hill Laboratories to confirm that topsoil suitable to for reuse
a40d8b74-816d-5384-858a-37018196f028 | note | ○ Soil Reaction
8a17c5bb-8886-5ba2-b97f-dd797a8bf017 | note | ○ Electrical Conductivity
ac7eb074-bf3e-5c77-b56d-1d9e06434a0d | note | ○ Mechanical Analysis (texture)
501fa943-68c2-57b5-8881-80661b33f270 | note | ○ Stone Content
cdd2f9e9-e38f-57da-a77b-76810a24894c | note | ○ Nutrient Levels of nitrogen, available phosphorus, available potassium and available magnesium
228916c7-3c91-52ec-9095-02bc4182f6ff | note | ○ Organic Matter Content
d3ae7535-eeb1-5748-8d1f-40ad3e815a0f | note | ○ Check for Toxic or Hazardous substances
599b7b46-d953-52ac-9a14-61415586f08d | note | Acceptance / Conformance Criteria - Engineers Approval
580f54ed-bd7f-5fa6-9e96-4f1eee364204 | note | Standard / Specification - NZTA P39:2013 3.1
e58a48e4-074e-5419-b8f4-c5115d268738 | note | Verifying Document - Hill Laboratories Test Report
bca7e7ce-8f0c-5c46-bbe7-9c9b00e3649c | note | Testing Quantity Required (based from schedule qtys) - 10 equal samples taken from site, mixed together, then 1kg of soil sealed into a plastic bag and sent to lab for sampling
4caf85c5-b3d1-51f2-ae8a-4eacde45cd51 | note | Verification Activity: Activity - I
5fdd1e21-9457-50e5-a7b9-3ccd39339507 | note | Verification Activity: By - SE
4df8d327-6e97-5620-a77a-66465636c9d2 | checkpoint | 1.7.1 - Crushing Resistance
bb0e2a6c-a45b-5db4-b8d7-08d582b8ac57 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
ba712546-75dd-559d-b99e-74a050d1816a | note | Acceptance / Conformance Criteria - >100KN
52bea34c-e074-5e00-a0c4-110c2fd14b0a | note | Standard / Specification - PS 16.5.15
e0276c72-f5d1-5a5a-b2ed-30cec3d27c7c | note | Verifying Document - IANZ Accredited Report
a1e15caf-d908-521b-b7e3-116ea85c296e | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
648a71f2-1a92-5393-9276-44c978ca5c2c | note | Verification Activity: Activity - HP
c2f15038-3c58-5879-a074-69089a4d70a3 | note | Verification Activity: By - ENG
0d7c8bd5-7fac-5d51-bc8b-91194e4b4abb | signoff | AUTHORITY HOLDPOINT
621ec4b2-6500-5108-af41-38730533fa09 | checkpoint | 1.7.2 - Particle Size Distribution
e3453d2b-0f0e-5943-9abe-cc046e755504 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
85fce51a-65df-581a-babc-225b335772c3 | note | Acceptance / Conformance Criteria - Max Particle Size 130mm, Max 5% passing 19mm sieve
c257f09e-5315-521b-8cbc-041c26fb48b6 | note | Grading:
c099953a-e37d-57fe-96b4-3f59410c70f3 | note | Sieve Size ¦¦ % Passing
09d74a72-95fc-5e21-a00d-26ffd88a0617 | note | 130mm ¦¦ 100
04df46af-e4ee-52c2-9dc5-7b4002ab8a19 | note | 100mm ¦¦ 70-80
a94322fc-9d15-5144-aae2-4c3bf59e08c8 | note | 63mm ¦¦ 0-50
28b131f0-aff3-59c9-97b0-28e2661b5215 | note | 37.5mm ¦¦ 20-25
11068d5c-8ed9-587c-a6bf-1502dffde10a | note | 19mm ¦¦ 0-5
e5788552-54a4-52b4-8b57-1b0349f98c2e | note | Standard / Specification - PS16.5.15
bc4a4fda-5277-5c68-b952-c532c651c723 | note | Verifying Document - IANZ Accredited Report
1d53f9e0-ed2b-5d55-9549-abab5654a418 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
223c2905-6dda-55e8-9d4d-7f716e02477f | note | Verification Activity: Activity - HP
a825d26f-eab0-5dfe-b8bc-f8375b209886 | note | Verification Activity: By - ENG
2c0f8c29-ad41-5a2a-b635-0a0aff717668 | signoff | AUTHORITY HOLDPOINT
37e76f2f-26c4-42ce-82a2-cdc5007ac58c | checkpoint | 1.8.1 - Maximum Dry Density and Optimum Water Content
07a0a6d7-28b0-54cf-9b02-7634c86a9eb7 | note | Detail - NZS4402:1986, Test 4.1.2 - Standard Compaction Test
c7cb3026-3ee0-5aa2-b0b5-c7273980332b | note | Acceptance / Conformance Criteria - Results to Engineer for Approval
da7f72a5-80f7-5f05-a89a-81afc4889f96 | note | Standard / Specification - Appendix XVIII
18a30af1-bd29-5090-a98e-5ddbdd85539e | note | Verifying Document - IANZ Accredited Report
787ba455-3085-5b0e-bb72-b2200a32b9e1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per source
20002216-97bc-56ef-928b-63449f19a710 | note | Verification Activity: Activity - HP
2d762234-fa6d-506e-8739-259f54918c65 | note | Verification Activity: By - ENG
c4476e83-179a-4066-b48b-38c709c473a6 | signoff | AUTHORITY HOLDPOINT
28a9939c-3398-5e1c-b9f3-fc35b3f555e1 | section | SECTION 2 – SITE WON LANDSCAPING FILL
01aef69a-6763-59ca-9c8d-736ee53b831a | checkpoint | 2.1.1 - On Site track-able Testing
3f42d642-f175-542b-82b1-b5985457f28f | note | Detail - Fine grained Type A3 site won materials may be considered suitable for use as landscape fill providing that it is ‘track-able’ by the contractor’s plant.
7fff358b-d85f-5211-aeca-a69e18d3e5bb | note | Acceptance / Conformance Criteria - Trackable by Contractors Plant
a197c149-fbfd-5ba1-8b7f-8b20882dc8c2 | note | Standard / Specification - PS 16.5.5
4f8645a9-3bfc-5a34-b967-f66786a89908 | note | Verifying Document - Site Engineer, Site Record
75d1d38d-26b7-5102-b1ff-f76a43a42a76 | note | Testing Quantity Required (based from schedule qtys) - Before placing any fill each day for each area worked.
74103d69-a1be-5ff9-86a8-29373f64ed06 | note | Verification Activity: Activity - R
93001987-c82a-50b0-a687-c7bf697943d7 | note | Verification Activity: By - SE
cea9f37d-9fcc-59d5-a86b-752d34abb6de | checkpoint | 2.1.2 - Shear Vane
e26b7ef8-d97c-53fd-98d6-bd056ebb8715 | note | Detail - NZ Geotechnical Society 2001 - Guideline for Hand Held Shear Vane Test. Fine grained Type A3 site won materials may be considered suitable for use as landscape fill providing that it meets minimum shear vane strength of 30kPa.
dd7408db-f9e9-5c49-a395-0b757e41b7eb | note | Acceptance / Conformance Criteria - Min >30KPA
8967e5c2-9ac2-5a5e-a527-f835a8f34437 | note | Standard / Specification - PS 16.5.5
82c157b0-e50a-5f86-a528-dfb1cca45419 | note | Verifying Document - Shear Vane Report
226b4377-b9bc-53ee-90bf-2d4a82840a3b | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed fill per 200mm vertical ‘lift’.
580e74ff-fe93-5045-83c9-aa7c7882396a | note | Verification Activity: Activity - R
9776a4e5-9649-571d-a52c-cfd171f98003 | note | Verification Activity: By - SE
6d1d7126-1928-59ff-a877-462c509c0a9e | checkpoint | 2.1.3 - Proof Roll
bd66fb71-ae1b-5640-b1f8-904acfcf4caf | note | Detail - Proof Roll
3a58ea8b-4e5e-56ec-a645-4316abdd9086 | note | Acceptance / Conformance Criteria - Visual Inspection
beb4eb0e-ca18-56a8-8abb-ef2a25f558ab | note | Standard / Specification - Appendix XVIII
f8e8deaf-c24b-52ec-bbc5-dd57761b1134 | note | Verifying Document - Visual Site Record
d7d3c93d-c661-51d9-96fa-2886ab91ae83 | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
4800964a-2e44-58dd-8ae5-6cfefab59414 | note | Verification Activity: Activity - I
95fe8f2d-d11b-5ad8-9773-a44dc77da221 | note | Verification Activity: By - ENG
39d605b8-01ec-570b-b293-b6919dc2d8c2 | section | SECTION 3 – CUT SUBGRADE TESTING
0fcfb85c-2785-506a-902a-ef8862f376ed | checkpoint | 3.1.1 - Proof Roll
9b8ee6b6-c1d8-5143-a084-b27a5d279ae0 | note | Detail - Visual Inspection of Proof Roll
6f3952ff-2a7a-5418-ab3f-a84b218867af | note | Acceptance / Conformance Criteria - Displacement <15mm
b2a0f6ea-38ff-504e-8302-4c02f4902b36 | note | Standard / Specification - Appendix XVIII
0cfbc095-713f-50b2-b962-1709167fda88 | note | Verifying Document - Visual Observation
6de84e34-6b3b-5965-ad4a-b91f06ab0ce5 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
12589d38-c993-5bb1-81fa-7b4ba2669742 | note | Verification Activity: Activity - V
fe3486b0-6cc4-5d9b-a6e9-154171770e1c | note | Verification Activity: By - SE
93b11d4a-04e4-5cfd-8dab-0a37521cebb5 | checkpoint | 3.1.2 - Cut Subgrade Inspection
1ad4f939-cb75-5ff9-9543-62cea2bb10fb | note | Detail - Engineer to inspect all foundation surface inspections
7e8b5e53-75e3-5e68-998b-905d79354b01 | note | Acceptance / Conformance Criteria - Engineers Approval
70e6c899-f866-57d8-8fdb-aac02ae513c1 | note | Standard / Specification - Appendix V
3397ab39-8b75-56fd-be39-bd2c305125cb | note | Verifying Document - Visual Observation
f9f254a0-753e-5be3-9750-266085fb3728 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
e9f36af9-e15c-5a9e-af0f-738b50136eb1 | note | Verification Activity: Activity - HP
dc69b9db-23b1-5a06-8db4-abefd628ef4e | note | Verification Activity: By - ENG
963aa0be-3122-5fa7-9edb-c9242f2cacf8 | signoff | AUTHORITY HOLDPOINT
1c232ad4-ca6f-5352-879b-6dc0de1ab807 | checkpoint | 3.2.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
e7163e68-b0e3-5f2f-96a5-ce33320c1c53 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
45014ec0-1f8c-5270-b530-7f36a1ee06ac | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
58bfd0b1-7958-5993-a896-e3e22028cf3c | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
ffe515da-ee85-5ede-9fbf-b3c85024cae4 | note | ○ Single Test Min SU: >50kPa
af1d3197-a6e5-5b8f-8b21-ad8da62ca655 | note | Standard / Specification - Appendix XVIII
d8f50f3c-cc10-5a51-a094-69f7d2654f34 | note | Verifying Document - Shear Vane Report
15f00dfd-9baa-5595-b893-bc90b866bd83 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
739cd2cf-8354-588f-910e-bdad0829c121 | note | Verification Activity: Activity - I
847bef16-6e0a-527a-8e2f-63bb3d5f7e61 | note | Verification Activity: By - SE
90e0aec2-fe18-571c-ab93-111c98467327 | checkpoint | 3.2.2 - Cut Subgrade Testing - Cohesive Soil Scala Penetrometer
b5d7ad09-54d7-5e1f-b147-e713fc784924 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
7e769fe4-3a85-5663-8597-cce49df0563e | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
c701c9ae-eb66-55ac-a955-752cb3f99dc5 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
1cfb59e9-e301-58d7-b234-ec9b84187ba8 | note | Standard / Specification - Appendix XVIII
dc550f5d-09c6-57fa-a9de-3afe17fe3ff6 | note | Verifying Document - Scala Report
d87efcc5-a697-588f-b1e9-d5a654ad196d | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
ff7ce86c-a7b2-50c1-9745-dd2b9d4105fb | note | Verification Activity: Activity - I
4a5b9405-45dc-5570-976c-7e17d705d1db | note | Verification Activity: By - SE
b5bc1a9e-ce3c-5ab7-9191-e1d4655e8d28 | checkpoint | 3.3.1 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
099ba27f-0aa3-5787-b331-288eca947e13 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
37b6532e-c53c-5014-8b83-16a87e3980b3 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
4842107b-db4e-51fc-be72-d50f5651a07d | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
a851bc90-faa8-5ded-a6b2-6d85e2e71932 | note | Standard / Specification - Appendix XVIII
df52a6eb-a78c-5b0b-8224-d27e7dfe1e35 | note | Verifying Document - Scala Report
d99347d2-cfb0-5075-b6f9-15124550728f | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
c7722149-203e-5f1e-9298-257ba8192655 | note | Verification Activity: Activity - I
243c1c30-7a47-5092-a5e5-8ca7fc0e922d | note | Verification Activity: By - SE
e30f05d0-ec2c-5e4b-a54a-d592b64bb134 | checkpoint | 3.4.1 - Release of Hold Point
9c8ca8ca-c3ff-5943-95c9-08571de46e16 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
b47056ce-32ca-584b-b801-937b80fcb179 | note | Acceptance / Conformance Criteria - Engineers Approval
190bbdb6-7726-574c-b85d-8f227be9e743 | note | Standard / Specification - PS 16.9.3
af2bc54a-add3-5907-9179-35f1b262589c | note | Verifying Document - Written Certification
6cc1ee2b-ab37-5006-80a2-362747077ea2 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
3ae6586d-f990-52a3-aea5-9767d20674ab | note | Verification Activity: Activity - HP
0480d17f-a566-54d9-836c-af9c3b82637b | note | Verification Activity: By - ENG
b785ceee-e615-5a5f-b0ef-f5834a2e49e4 | signoff | AUTHORITY HOLDPOINT
839606ac-0bf2-5c84-9972-67e9133f6bc2 | checkpoint | 3.5.1 - Subgrade Level Confirmation
5b1ee707-e641-5e41-9f82-01c7339af913 | note | Detail - Confirm subgrade is 735mm from finished height
f8acf895-08fb-5d6a-9df3-ae46998181f2 | note | Acceptance / Conformance Criteria - String lines - or equivalent are 735mm +0mm/-30mm
5a940419-9a05-569d-877c-84fd3a38bdaa | note | Standard / Specification - PS 20.14.5
14a675cd-e791-50fa-8907-42ad9b0d9518 | note | Verifying Document - String Sheet
dec9c9a2-e516-5c97-896f-06ea24f80b97 | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage
df5c4d78-8ba2-528d-8713-a359de273af9 | note | Verification Activity: Activity - I
473ff51d-3dff-59b1-8fea-b9093f074bc8 | note | Verification Activity: By - SE
4c2880cb-6b19-5352-afc6-0af4ec16bf79 | checkpoint | 3.5.2 - Subgrade CBR Testing
9ca2adba-5d8d-5dc1-b774-1c01f427537d | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
ef3e9759-440a-5d30-accb-f608039c6584 | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
413c7606-9deb-5791-8045-219bf3b5639b | note | Acceptance / Conformance Criteria - Pavement Type 1: CBR >6, Min 3 blows / 100mm
fcc1c763-3684-5936-bb03-cc49bb839751 | note | ○ Pavement Type 2, 6, 7: CBR >2.5, Min 2 blows / 100mm
4dd10b43-71a1-5056-b0ec-c9395db70abf | note | ○ Pavement Type 3, 4, 5, 8: CBR >3, Min 2 blows / 100mm
03481636-9962-5510-bc10-bc410b962eb6 | note | Standard / Specification - PS 20.4.1
1eaac8e5-1e60-55ee-bf47-075dcfa3326c | note | Verifying Document - Scala Report
cd9bc73e-313f-5da3-8b2c-60d448857ce2 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100M2
9eede4ac-42fd-59bf-a294-befab2d2c9f3 | note | Verification Activity: Activity - I
a4c82a62-8b1c-55b1-b1ce-fa9fec3223ed | note | Verification Activity: By - SE
efd6bce0-9436-5a8a-8e4d-3b3dfcc3122c | checkpoint | 3.5.3 - Release of Hold Point
e475e1c5-a240-5723-908b-52369cf8c165 | note | Detail - To release the subgrade hold point and be able to start placing pavement layers, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
0bcc3327-3c68-5d53-a953-398933445973 | note | Acceptance / Conformance Criteria - Engineers Approval
e0a1bb27-639e-577b-b592-4ad81e2f14da | note | Standard / Specification - PS 16.9.3
50a81bc8-d86a-5883-afc1-bc0c5af0b02c | note | Verifying Document - Written Certification
717f4e33-a87d-5781-9f0d-32815dc7150a | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
441f4220-c389-573b-9551-3c1e828d4aa5 | note | Verification Activity: Activity - HP
0c0f8dcc-cd0d-5220-9466-b3c8d4d984a6 | note | Verification Activity: By - ENG
fa6a9276-7859-5e26-9e07-5da5d76a8c15 | signoff | AUTHORITY HOLDPOINT
fcd783e9-5837-58e1-a505-866715da12e7 | section | SECTION 4 – CUT SLOPE INSPECTIONS
65f19254-c0e0-5cee-bd75-e32db1abf131 | checkpoint | 4.1.1 - Cut Side Slope Inspection
eafb8a5a-c8d7-568a-a4da-a4044af9fde7 | note | Detail - Inspection records to include photographs, logged soils (to NZ Geotechnical Guidelines) and shear vane testing
59b61895-d03a-524f-9906-0bab0c512fae | note | Acceptance / Conformance Criteria - Engineers Approval
332d06ad-16bf-5aca-b370-c5a9bc5b2ce6 | note | Standard / Specification - PS 16.6.4
02068a19-61ba-5c61-9eea-0ab28547c7d8 | note | Verifying Document - Site Records
3bd18812-56b9-5747-a8f3-19c7b1be802a | note | Testing Quantity Required (based from schedule qtys) - As per Engineer
8d9f33b2-ec66-5b3c-a304-18eefd5ee936 | note | Verification Activity: Activity - WP
1d2eba01-d547-5a5c-92e1-b224ce415b25 | note | Verification Activity: By - ENG
778e9838-7b8c-5e69-b413-633633b57f38 | checkpoint | 4.1.2 - Cut Slope - Soil Log
c04a919e-c3f7-5310-82a5-6b0fab022ab9 | note | Detail - Soils to be logged to NZ Geotechnical Guidelines
98ac6f09-aeb2-5fba-ac8a-b5a07c7cf703 | note | Standard / Specification - PS 16.6.4
17949f10-fbe3-5c39-a253-67d116933f92 | note | Verifying Document - Soil Log
c4091482-ed12-5378-86ad-800c128c3b79 | note | Verification Activity: Activity - I
b49bef8e-cbd1-5bb3-a6b0-dd65950a5a8f | note | Verification Activity: By - SE
a9f13abe-59e6-5a91-872b-201daf1550be | checkpoint | 4.1.3 - Cut Slope - Shear Vane Test
f8f335cf-3f36-5edf-a43b-76b204e464f3 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
ebca4ad6-34af-5360-96a7-2623ea7582fe | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
fccd3323-eab8-5990-8196-1a8cab2d2b22 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
bf61c6d8-7def-56c8-aadf-0dc8ba0f3866 | note | ○ Single Test Min SU: >50kPa
f0b03302-2718-5660-9e96-a23051f8f0a7 | note | Standard / Specification - PS 16.6.4
161edf4e-7dec-5d2d-81b1-e869e63b344b | note | Verifying Document - Shear Vane Report
e4a94a26-48e1-5152-97d6-7945234ff646 | note | Verification Activity: Activity - I
6abadc46-ca3d-5b6d-bf59-eef1c4f35e1f | note | Verification Activity: By - SE
eb0520ee-76a0-5f5b-8ab0-028f5cd672d6 | checkpoint | 4.1.4 - Drainage Measures if Seepage Encountered
df6a0f47-131d-5150-b664-3e2398ea95bd | note | Detail - Borehole Drains or ballasting may be required, to be directed by Engineer
19ac0b9a-87bd-5144-b9fb-134e403d3d9a | note | Acceptance / Conformance Criteria - Engineers Approval
e59e8ee8-111e-53aa-9e73-d14afd7e90cd | note | Standard / Specification - PS 16.6.4
5e2d2b7f-51c3-57b0-ab11-e99bf1b733c6 | note | Verifying Document - Engineer approval
1233e552-20a2-5624-a4b6-4473dd62d5e0 | note | Testing Quantity Required (based from schedule qtys) - As per Engineer
78e176d2-830b-592f-815a-f533b10fd2ce | note | Verification Activity: Activity - I
b12fbd0d-43d9-5b7c-85cf-2c14f962f961 | note | Verification Activity: By - ENG
b76f45ae-9c1b-51f2-b20c-9ff3446f93b4 | checkpoint | 4.1.5 - Design and Grade Check
d719a61e-92cb-5e04-a1be-67e6cc3b5d2c | note | Detail - Confirm cut slopes have been correctly excavated to design and grade
7ee5a497-9330-50c0-addb-17edd94fe61d | note | Standard / Specification - PS 16.7.1
a08bc602-6e70-59ce-aa28-f1a0ccacb0c3 | note | Verifying Document - Survey Records
66361d3e-45e1-580e-a089-e35463605c13 | note | Verification Activity: Activity - D
0b86cd24-d47e-536d-989e-374847218eaa | note | Verification Activity: By - SV
e04bc573-50a3-54df-8ec4-f2c2fee33603 | checkpoint | 4.1.6 - Stabilisation of Cut Slope Surface
93e98976-6385-56c4-b2d9-349860fcabb3 | note | Detail - Cut slope surfaces to be topsoiled and grass seeded or planted as soon as possible
c916b7dd-a5b1-5dff-90e8-7a56abd81c49 | note | Standard / Specification - PS 16.6.4
5ee42616-31e2-5674-8247-0e6757e2ec47 | note | Verifying Document - Site Records
10ef3a43-e9c7-5964-9a27-cd58df1bd030 | note | Verification Activity: Activity - C
8d4b2d50-9b81-5dd1-9d74-3e40d5f922ed | note | Verification Activity: By - SE
d332b165-be98-57b1-ae8f-c8df339988ac | checkpoint | 4.2.1 - Release of Hold Point
975dc4ff-47f3-5f6e-a731-5b7c043b0a8f | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
85c880c7-d82d-59e8-bf83-e56b043e6a6c | note | Acceptance / Conformance Criteria - Engineers Approval
52598269-cb1d-5ef3-82c7-10df60d04119 | note | Standard / Specification - PS 16.9.3
8c918a19-dd3b-5fa3-b3ac-92294c75f309 | note | Verifying Document - Written Certification
16e9480e-295f-5c45-b8b2-2a9314f1aa63 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
a9f9dc2b-f96f-5aff-83b8-5a9bd212cbb1 | note | Verification Activity: Activity - HP
88c6a9e1-47af-540e-806c-68cde2824c9c | note | Verification Activity: By - ENG
8ab96904-8ef4-591a-ae23-4d319981dd1d | signoff | AUTHORITY HOLDPOINT
d8949eb3-2a58-53de-a569-51450984c878 | section | SECTION 5 – UNDERCUT TO WASTE & BACKFILL
03329000-37e3-5dad-9c5f-fc644c03e0c8 | checkpoint | 5.1.1 - Undercut Surface Inspection
256db5c3-1fdd-5a71-85eb-078779522eb6 | note | Detail - Engineer to inspect undercut surface
4f0a304a-13ed-5f07-8d40-20244ff6ff4d | note | Acceptance / Conformance Criteria - Engineers Approval
c73ff527-8e22-5569-a18b-7840e24e53d8 | note | Standard / Specification - Appendix V
1c058744-4d82-5867-bfc0-c5300dc33d61 | note | Verifying Document - Engineers Approval
339e749c-f490-539c-8c6a-74df1480e8d2 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
84cdccf5-8b1d-5cf9-b7b9-0481b6737256 | note | Verification Activity: Activity - WP
4729c983-c925-5f73-b89a-6b1c52193b49 | note | Verification Activity: By - ENG
4063604d-63cd-5791-a2a5-9f4966e1ea3a | checkpoint | 5.1.2 - Placement of Geotextile on Undercut
5b33c92d-043e-5403-808c-d48497af90f3 | note | Detail - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
e54f28cb-9f6e-5015-90c6-d723332121e1 | note | Acceptance / Conformance Criteria - Engineers Approval
bda4a583-1021-5daf-8d37-7911b23579fb | note | Standard / Specification - PS 16.6.4, TNZ F/7: 2003 8.3
d649f041-1fdd-5aca-b4f7-2ff276e9ac5c | note | Verification Activity: Activity - WP
dd3c4e48-bee9-51f9-8e85-4f2dc9eac914 | note | Verification Activity: By - ENG
0baec06e-bca7-5764-b694-c995a1192578 | checkpoint | 5.1.3 - Subsoil Drain inspection
2d0fd9b7-688e-5f3d-82b3-d58e0a3ef953 | note | Detail - Subsoils to be placed at base of cuts where directed by the Engineer
982df744-6067-5c7e-98fd-3961f3c508e0 | note | Acceptance / Conformance Criteria - Engineers Approval
6da8b5af-6c4d-5267-8841-accb283d54c9 | note | Standard / Specification - PS 16.6.4
5afd4a8d-a2ca-5131-9bd7-f5e260b93cb1 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
38840069-bfa3-5364-bbc0-2bd7c1144c91 | note | Verification Activity: Activity - WP
3ab6db38-4e76-5e78-8fdd-3e93a3812b55 | note | Verification Activity: By - ENG
2b5c3c35-e44a-5fba-9f5b-5f34c6490527 | checkpoint | 5.2.1 - Release of Hold Point
edd45759-2e74-5acd-b50e-431368d9a029 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
45a44b68-29f9-503a-a771-b808ad16301d | note | Acceptance / Conformance Criteria - Engineers Approval
1fa0514e-4bcf-5990-906f-c570a3ce781b | note | Standard / Specification - PS 16.9.3
207fa720-d016-5723-914d-bf51f2305824 | note | Verifying Document - Written Certification
86d88f28-47d0-5253-b632-5fe62c626db2 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
17df2965-bb15-5c5f-8049-a05afca06b8c | note | Verification Activity: Activity - HP
9fd18c9d-d502-54fe-a461-d72145cac5f0 | note | Verification Activity: By - ENG
9b33e9a0-b387-5cd5-a9ff-916d70c37976 | signoff | AUTHORITY HOLDPOINT
48724bee-4e03-5805-b57e-bbb948c422e4 | section | SECTION 6 – COMPACTION OF IMPORTED FILL
d03f7fd2-b98b-5017-b443-b66ce56e2a47 | checkpoint | 6.1.1 - Placement of Geotextile
c57c4551-aaa4-5098-9046-dc7d23f1ca0e | note | Detail - A layer of Class B Geotextile Fabric to be placed between cut surface and imported A1 Structural Fill with 500mm overlaps
37271b8a-817a-51c3-bbb2-d5d76e057393 | note | Acceptance / Conformance Criteria - Visual Inspection
4fb6212e-baa8-5eff-a2d5-03c6d4e2558d | note | Standard / Specification - NTC084
2e01a5a2-2afe-5bc3-8a9f-4e1a52fe8fb9 | note | Verifying Document - Visual Observation
ca6b7040-f14a-5848-86e7-4d95f44a0433 | note | Testing Quantity Required (based from schedule qtys) - As Required
e746025b-3f23-52a5-be29-352a14f73322 | note | Verification Activity: Activity - I
4e1b258e-ef24-5986-8e5b-6ba6f754acd1 | note | Verification Activity: By - SE
36a35987-56f2-51a2-91ba-2c48bca739e3 | checkpoint | 6.2.1 - Compaction - Clegg Hammer
0f2983b7-0568-5f98-bf54-760e89e688dc | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
8b60bda0-eda7-5390-9c06-55463cbb2483 | note | Acceptance / Conformance Criteria - Structural Fill: Min CIV 18, Ave CIV 20
a63a7a49-961d-5112-8522-5443d908eb4c | note | ○ Non-Structural Fill: Min CIV 10, Max CIV 12
e0d6243e-271d-51bf-9c25-8ebf8af78bd9 | note | Standard / Specification - Appendix XVIII
9efe89ee-da3f-5938-a7ae-ec3d36454d92 | note | Verifying Document - Clegg Hammer Report
63b9977d-c247-56d7-9957-540db297f44b | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
da53d111-535f-5332-9db3-53fa60557f5d | note | Verification Activity: Activity - I
c2e31214-2a6b-5bef-a595-9e52c9d2c119 | note | Verification Activity: By - SE
cdac7ed8-dfb2-526c-8f48-c0fe5bf13a94 | checkpoint | 6.2.2 - Compaction - NDM
2c4ccefe-38da-5fc2-8bb2-c6945688099c | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
3724cddd-6f8d-5ace-809e-68271568c1c6 | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
a19928ce-c7ec-5942-8017-5d3627ba5b15 | note | ○ Non Granular Material: Max Air Voids 8%
d47982e4-4647-5723-bfdc-11c2198d30db | note | Standard / Specification - Appendix XVIII
791913a0-97cd-5b7a-8f96-9a0d77c59f7b | note | Verifying Document - IANZ Accredited Report
e0a1361f-ecca-52ad-a951-76b7a3156784 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
2d1f61eb-9a2f-5829-aab5-26186d7d5c05 | note | Verification Activity: Activity - I
a70f7328-fca2-57e8-9a83-3f7f38cce54c | note | Verification Activity: By - SE
8c46c409-8ae9-5510-81ae-2409a0dcb7a5 | checkpoint | 6.2.3 - Compaction Trials
9fb0a691-7ac5-5dca-8c58-d0e9c3d76f5b | note | Detail - The Contractor shall carry out compaction trials of the various soil types and combinations on site, and any imported fill materials, using different layer thicknesses, types of rollers and conditioning plant (ie construction discs and scarifiers). The trials shall be conducted over the duration of the earthworks operation with the objective of determining the most suitable and efficient techniques to meet the compaction requirements. The trial details, test data and conclusions shall be reported and copied to the Engineer within five days of completion of each trial.
3715385f-a561-5dd7-b387-5c2817e306af | note | Acceptance / Conformance Criteria - Engineers Approval
28fa0445-6822-5c24-8724-bf30bf57c3be | note | Standard / Specification - PS 16.6.5
02e21e85-d46b-5b2f-92ae-37890408c2b8 | note | Verifying Document - Trial Results
d8d8c67a-d433-5868-9b91-98d9f5538656 | note | Verification Activity: Activity - R
34f9dfbc-e9c4-5c59-bf71-dfaac063b803 | note | Verification Activity: By - ENG
fbe3407d-cb28-52a0-a9de-c1bce268da67 | checkpoint | 6.3.1 - Compaction - Structural Fill Scala Penetrometer
7a8230f3-b188-52e8-aa73-d5f2d0b3e33a | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
34d9409d-c083-52a0-9e7b-f7e27ac8f8af | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
54a7f7f0-b056-540b-a7af-b20795be7efd | note | Acceptance / Conformance Criteria - Minimum 5 blows per 100mm penetration
832e7712-9da7-5535-a5e3-0eb2027e1332 | note | Standard / Specification - PS 16.5.12
832ab02a-47ae-5c44-977b-7199f6f02552 | note | Verifying Document - Scala Report
9ecc2a3e-80a0-5277-afdc-ef68ad121dd1 | note | Testing Quantity Required (based from schedule qtys) - Minimum 1 test per 500m3 of filling evenly distributed over the extent and depth of the filling. A minimum of 1 test per 500mm lift or part thereof to be completed through the full lift thickness.
5d3a0d63-003c-558d-bc43-947c1fd61c82 | note | Verification Activity: Activity - I
85cb4824-3b4e-509d-8ee7-77ff323494df | note | Verification Activity: By - SE
6241f96b-6fc2-50ef-b732-f04924079f36 | checkpoint | 6.3.2 - Compaction - Structural Fill NDM
457c1a4a-0d41-588f-8702-c1c4a51c4d9c | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
c05456f7-d00a-50d5-803f-ea928a114d3e | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
287a7df2-dd75-5da1-bcec-82fbdd445e4b | note | Standard / Specification - PS 16.5.12
907be105-d2bc-5ef8-9187-cbfb4713d2ea | note | Verifying Document - IANZ Accredited Report
6e64e8f1-6ee5-5b54-992c-73f9536ae0db | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
74fd0876-618e-5c8c-8f44-246e7956aa20 | note | Verification Activity: Activity - I
5bf1ae9e-7c5d-57ec-bc85-47db527cb0d1 | note | Verification Activity: By - SE
662ad010-253b-5a12-a529-7441614b3b64 | checkpoint | 6.3.3 - Pumice Sand Fill
daf880a4-f3be-5c2b-a7ea-53ce71075fac | note | Detail - Pumice Sand Material shall be contained with an outer layer of fill with a minimum thickness of 600mm. Must be Hardfill and/or imported Type A1 material and/or Type A2 material and/or Type A3 material
40545462-e55a-5c89-9da8-15ad69319790 | note | Standard / Specification - PS 16.5.12
3c76e7cd-c115-50e1-9d7c-a1a308ba9d33 | note | Verifying Document - Site Records
cc9db91d-3c94-5e65-9d7d-6b02cada1074 | note | Verification Activity: Activity - E
6c9f6c43-0716-55c1-a18c-b2d004bb9431 | note | Verification Activity: By - SE
6a73a8a8-7989-5156-8499-c39920491575 | section | SECTION 7 – TOPSOIL PLACEMENT
01cae0f9-1947-5325-aa64-e60f3c87d461 | checkpoint | 7.1.2 - Topsoil Placement on cut and fill embankments
2474dbde-e949-5825-9b4b-c6df21ad6318 | note | Detail - Confirmation of thickness and material suitability
efdd939b-0b67-51ff-9c20-e9a31679142d | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
9f0d6b38-9cb1-5f20-8d1b-46eeacaa7afe | note | Standard / Specification - PS 16.6.3 b)
ff47695f-9562-5a11-8a20-fb3b61c78347 | note | Verifying Document - Visual Observation
b85c747e-a11d-51f6-86b7-3c2b2be7644a | note | Testing Quantity Required (based from schedule qtys) - Once per lot after topsoil re-spread
496ce2b8-6b30-5794-949b-4a9acf650e0c | note | Verification Activity: Activity - I
3843524f-0169-5361-a158-82aaeea0e21b | note | Verification Activity: By - SE
a3330d98-78c7-560f-9006-8e2f8e055412 | section | SECTION 8 – SETTLEMENT INSTALLATION & MONITORING
bc29cfd2-ded1-5198-97c7-6d976446c060 | checkpoint | 8.1.1 - Instrument Reading Notice
9138d2a5-833b-5d74-bc27-4fb87fa471e1 | note | Detail - The Contractor shall inform the Engineer two days in advance of planned instrument readings so that the Engineer may observe the work.
1e74c7bd-cbb9-57f6-a3fc-41e86ab88902 | note | Acceptance / Conformance Criteria - 2 days notice to Eng
32e603b1-d51a-555a-9b5b-3ae1fba7f11a | note | Standard / Specification - PS 16.8.2
81db03e5-3ca8-5ed3-8ded-74b94252a0e8 | note | Verifying Document - Site Records
59a2d2b4-d219-5b31-8aca-a96c70384634 | note | Testing Quantity Required (based from schedule qtys) - Every Time
66cda388-c788-521b-9da5-06a0dac81c62 | note | Verification Activity: Activity - I
bf5d7d6e-ff88-5976-aefe-afe83d1a306c | note | Verification Activity: By - SE
1ebb286f-cdd7-51fb-9b19-9386a0211bf8 | checkpoint | 8.1.2 - Results Submitted to Engineer
c14766cc-5b05-5e9e-8968-a8f891dde82a | note | Detail - Results will be submitted to the Engineer within 1 day of reading the instruments
5335b5b4-a095-50ff-8d86-02475f1c74f7 | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
d77f647a-7ef6-5995-9898-0abf6db1436d | note | Standard / Specification - PS 16.8.2
cd195672-6e20-5687-8a8a-5486969f3faa | note | Verifying Document - Site Records
8f444ee1-3401-5e8c-92a1-9e2b05cb1bdd | note | Testing Quantity Required (based from schedule qtys) - Every Time
aa36d35b-ea46-5784-89b2-b02175228e69 | note | Verification Activity: Activity - I
22e987e2-931a-5270-9981-b956d623df17 | note | Verification Activity: By - SE
3d3ae3dd-ace9-5090-92fc-553517c39048 | checkpoint | 8.1.3 - Baseline Readings
dfca4c58-fdd4-5702-9323-368c136a86a0 | note | Detail - The Contractor shall take 3 sets of baselines readings from all instruments at 2 day intervals
7d7dde4a-8e18-5e2b-bc02-3f856da9833e | note | Acceptance / Conformance Criteria - Engineers Approval
6c77cae2-2305-5f56-ad2f-78a74f336c0d | note | Standard / Specification - PS 16.8.2
6d9a1bd9-92a3-5ef2-ae83-bff9e90cd391 | note | Verifying Document - Site Records
e256acef-02eb-5bb1-8dc4-855e82f54d50 | note | Testing Quantity Required (based from schedule qtys) - Every 2 days
bc0afed1-86b2-57d1-b82d-6e51bbf0cdcd | note | Verification Activity: Activity - I
c6189f79-8669-53bd-8a75-f954d309a934 | note | Verification Activity: By - SE
e7a7f3e9-840e-5da4-93a5-63a071074afc | checkpoint | 8.1.4 - Readings During Active Fill Placement
e44330d5-ed03-599e-a3a7-d98a1d807dc1 | note | Detail - During active fill placement, the Contractor shall read all monitoring plates twice a week or every 1 metre of fill whichever is more frequent
29ad938d-fe00-5843-81d2-04a1d04c717b | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
78a29925-300c-55bf-a802-7c47ead2c5b9 | note | Standard / Specification - PS 16.8.2
4f00d42e-75e9-53dc-81f5-3b0677f631a3 | note | Verifying Document - Site Records
92842721-614a-5dde-8394-5f4167684317 | note | Testing Quantity Required (based from schedule qtys) - Twice a week
c217781a-8dad-5447-9963-264f19054387 | note | Verification Activity: Activity - R
1add7908-816a-5f48-8d57-c988710064bc | note | Verification Activity: By - SV
292e3aee-3636-5d32-b777-37a5679b000d | checkpoint | 8.1.5 - Readings During No Active Earthworks in Area
4f95a597-dd8a-5d92-b90f-6e4fd48f41f0 | note | Detail - The Contractor shall read all monitoring plates weekly if there is no active earthworks taking place in the area
c50dcb36-a678-56c8-a2f3-e136fd02c974 | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
c0d929ff-b2b6-51f3-bd86-fe245d3f7164 | note | Standard / Specification - PS 16.8.2
0a3146b3-4fd6-5afc-acd1-d62a2c160f7d | note | Verifying Document - Site Records
c24b8e98-91db-5bac-a829-810e5b768020 | note | Testing Quantity Required (based from schedule qtys) - Weekly
56cd2f44-d76d-5f0b-858b-9d87e4a66efa | note | Verification Activity: Activity - R
4ccef1a1-0513-534b-a6da-01e3f8933e81 | note | Verification Activity: By - SV
3200ddaa-39d0-5fe0-9db2-2ecb08f5e205 | checkpoint | 8.1.6 - Settlement Monitoring Termination
41909bd1-c111-50ef-9ea0-d20a274f7c8c | note | Detail - The criteria for terminating the embankment preload are either: Three consecutive measurements indicating the t90 settlement value has been achieved, A rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed. The settlement readings shall be evaluated by the Engineer to assess the need to extend the monitoring.
04d71d13-3552-5c80-8c41-dd528492d383 | note | Acceptance / Conformance Criteria - Either:
893459fb-3c53-5781-9524-5c7b643d954f | note | ○ 3 Consecutive Measurements showing T90 settlement value achieved
35e75f1b-655f-58d6-bcc9-4333b68485d0 | note | Or
70dd8156-ed59-54c2-a968-6d6090f5d9bb | note | ○ Rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed
53bf25f9-7e2b-5d23-8304-d9057582f22b | note | Standard / Specification - PS 16.8.5
29d23c9c-69f8-5d17-a7ca-1cefeb89b766 | note | Verifying Document - Site Records
2c1e3aca-5656-59a9-9771-9c4c0025318e | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
235ec686-c02a-504b-8871-5000f1a4acc7 | note | Verification Activity: Activity - HP
68bc82d5-caeb-5c67-a0e7-45bb554ab3b1 | note | Verification Activity: By - ENG
3b7e976e-ce37-508c-81a6-0d741734da4e | signoff | AUTHORITY HOLDPOINT
c2ecee3d-6862-5c26-a56d-8a8fd80e012c | section | SECTION 9 – AS-BUILTS
87d570ee-8f54-5bac-a996-aebcb3a25e28 | checkpoint | 9.1.1 - As-Builts
9c194c9a-20c1-554d-aed9-1682811ad650 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
8fdc0114-4e8f-5d6c-b3bb-e38f552a7dcf | note | Standard / Specification - PS 16.7.6
40b6e49a-8eed-58df-9985-66114f70dcaa | note | Verifying Document - Survey Records
50dce19e-a7e6-5fe2-94f5-ec7a3d724fb3 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
8f937779-f78c-5919-b1d6-1d1713891f4d | note | Verification Activity: Activity - D
cadde33f-dce0-57f2-9ff3-6800d7cf10a0 | note | Verification Activity: By - SV
bc936585-a3d5-4d37-b676-71b44bc44bca | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
65e3e954-9a74-59b4-b341-57e0db4a8462 | textbox | Contractor's Rep Name:
ce03386e-128f-52f4-b6e5-b8924a9da172 | textbox | Engineer's Rep. Name:
959ed28e-b26b-57af-b422-57dec9d22799 | date | Date:
5c21dece-c4c2-4e20-a595-9ebaca22ba99 | signoff | Add Signature
79b9d58a-1aa2-5eea-bfd9-318b1d6e9f9b | checklist | DN1210-0004 - Manhole and Catchpit Record | itp | DN1210-0004 - Manhole and Catchpit Record
d1c4b54a-b4c4-539e-9691-c0d96368dc14 | section | SET OUT
c5d6f50a-ccb6-53db-bb19-e28206919615 | checkpoint | 1 - Confirm Stormwater alignment is as per latest Drawing revision and does not clash with other Services.
71262383-01c1-5613-ad46-bff2bab3c896 | note | Comments: Design Engineer to approve if the location needs to be moved.
d2def37c-d86f-54ce-b45c-d3024d8835bd | textbox | NCR/OFI/RFI No:
274a37be-f134-5256-8964-164983e5d09a | checkpoint | 2 - Check Survey Set out and mark out completed.
0b503a68-1b97-50a8-a97a-bc702fb52c75 | note | Comments: Centre point of MH
8ac7e125-0b01-530b-adbc-7c83d866cc8e | checkpoint | 3 - Confirm correct location of Manholes or Chambers, Catchpits.
0a2a6f02-603b-5660-abe7-d20ea331dbbd | textbox | Comments: Refer to Dwg:
250e19d1-e2cb-5fbb-b958-1502f46075be | section | TRENCH EXCAVATION
a97a1b49-0483-5c2a-aeff-5b999d064122 | checkpoint | 4 - Ensure permits are in place.
c4f9efec-88e3-5916-8886-90616352200c | checkpoint | 5 - Pothole existing services data in place.
a88916c6-f006-5573-8093-21c6e2687901 | checkpoint | 6 - Confined Space Permit required?
3de7c1f9-e10b-55e6-b358-b4b95cf017e8 | note | Comments: Trench depth > 1.5m must be shored or battered.
d0547d1e-a8b7-5c80-b83d-cd2c32bdda0c | checkpoint | 7 - Foundation test conducted.
204ee721-a86e-5bfc-920e-789193837958 | note | Granular Material: Scala 3 blows/100mm 5% CBR
f1e92492-cd35-5b56-bdb7-58b5e99c2ec3 | note | Cohesive Material: Shear Vane Strength 70kPa
fe505ecd-66c2-5d92-97f3-03de78b849b1 | checkpoint | 8 - Undercut required?
3cf705f8-3b73-57a8-9c73-5c846dd6bcff | note | Comments:
2667e1cc-5437-510d-ab2f-3ea8cca1a95f | textbox | Undercut depth:
0b44c423-6b70-5fd1-90d1-a764b513787b | textbox | Metal:
4d6c7d1f-d51c-5cd4-97ac-d770a5fad3c1 | section | STRUCTURE INSTALLATION, BACKFILL AND TESTING
23cbe7bd-59d2-5b80-bafa-bf0b49b2cd60 | checkpoint | 9 - Installation of Precast Base Unit on Bedding
d3ffa4bb-d69e-5c00-a5a7-31c0e2fe014a | checkpoint | 10 - Installation of Precast Risers to Lid Level
a515fd04-1c2d-594f-a1de-9a6f419cb951 | checkpoint | 11 - Installation of Manhole/Catchpit Furniture, Steps / clamps
461dbaa5-adaa-5114-960c-83cc8ba2cd05 | textbox | Comments: If N/A- why?
b2499e8b-1ba2-5efb-9386-1005dc876b0d | checkpoint | 12 - Haunching around pipe connection and benching of MH base.
4490b37f-ad0b-5071-a217-8ed8cd47f48e | checkpoint | 13 - Installation of Precast Lid
f6ab9e4b-bec3-5876-b593-f4bc2ae87edb | note | Comments: 300mm above pipe or per IFC drawing
56f4f4ca-29f8-5b3b-b138-ce05266a7562 | checkpoint | 14 - Epoxy- Joints exterior and Interior.
bfdcd0db-a8da-56fd-8b05-8096da758035 | checkpoint | 15 - Backfill around Manhole/Catchpit – testing as per below:
88145006-0079-5875-ac9d-20b186233e9f | note | GAP20 - NDM – minimum - 95%
399e53a4-5218-52f1-a739-9526c860fc0d | note | LRAP65 - NDM – minimum - 95%
8bf87f7c-5a78-5031-8553-dc01677f3080 | checkpoint | 16 - Installation of Cast Iron Frame A Cover Lid Level – set with contour
3df15f87-6988-5d80-a0b5-df40e70b3938 | section | ACCEPTANCE
1f07076b-0076-5f85-b701-97b80c9dd552 | checkpoint | Inspection By: Downer Engineer
3ed9f10d-d7e5-5cab-b036-1ba6c52c1d81 | textbox | Name:
52d07045-b101-5db4-a0c7-f5df59879a7c | date | Date:
a877c709-a54c-5683-8723-668e3595d3f3 | signoff | Signature
284281b0-d493-5cc0-97d7-48c49655d6b7 | checklist | DN1210-006 ITP Pavement - Type 2 - Rev 2 | itp | DN1210-006 ITP Pavements Rev 2
8508ff53-5f3a-5f4c-8d26-a8afd00d3eae | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS
93f30d2d-3e56-50c9-9bd3-5beffe13a132 | checkpoint | 1.1.1 - Geogrid
6ac3edcd-a18c-5733-aec7-06c3a3fd497e | note | Detail - The Contractor shall submit the full details of the geogrid they propose to use to the Engineer for approval prior to installation.
e1465fc9-f1aa-5057-ac0f-5003b12d12a6 | note | Acceptance / Conformance Criteria - Engineers Approval
b46f5045-f195-581a-88d6-16abb80390ea | note | Standard / Specification - PS 20.5.2, PS 16.5.13
79e82902-7c33-5eb1-9ef3-9aca4eee9adb | note | Verifying Document - Data Sheets
ed7871b9-575b-5299-8436-447deb7c2e11 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
cee074c5-40f1-5c02-85d7-a78442c3c9f1 | note | Verification Activity: Activity - HP
77f0f7ed-2077-59b8-b7db-4980558ee76e | note | Verification Activity: By - ENG
84031b1b-c029-5fd2-a7d7-e24c84fe30af | signoff | AUTHORITY HOLDPOINT
3a027d9d-66e5-5b0f-9721-a8c1d3b87fcc | checkpoint | 1.1.2 - Geotextile Fabric
c532d749-a5ef-5c38-ab1d-3d265b7611ce | note | Detail - The Contractor shall submit the full details of the geotextile fabric they propose to use to the Engineer for approval prior to installation.
be535660-8d85-5846-8d57-50f0172cbb73 | note | Acceptance / Conformance Criteria - Engineers Approval
1cd09b83-7c92-5c4e-b0d8-903380c2613f | note | Standard / Specification - PS 20.5.2, PS 16.5.14
587c2b92-cba0-559e-ad03-6314fbef71ed | note | Verifying Document - Data Sheets
c2321eef-3e3a-5095-b50e-a234b11e1833 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
1d3e9db8-a5ea-532c-9e77-817b2d9b4dea | note | Verification Activity: Activity - HP
b6a9b042-e1f5-58a4-8008-fd4adde3cc3e | note | Verification Activity: By - ENG
26b7265b-d3f4-5735-83f1-9fe60d84cd62 | signoff | AUTHORITY HOLDPOINT
ed84c0c4-748e-5387-895f-ad74a2ec012c | checkpoint | 1.2.1 - Crushing Resistance
1517bcfb-bb12-5e2b-92f1-b96e227a2eda | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
7dad6ced-f56d-5b2e-87ab-f65bfcb0c7bc | note | Acceptance / Conformance Criteria - >100KN
a2c2031e-09d3-5e0f-af13-e520f20baa0c | note | Standard / Specification - Appendix XVIII
bb174a8d-7ed9-5040-8249-b66aee897132 | note | Verifying Document - IANZ Accredited Report
66c5c54b-1076-53cc-892c-16fd040dfda3 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
54bb250d-1164-5d06-b952-caa8a16e2924 | note | ○ Results to Engineer 2 wks before importing
f4715e37-7564-538a-b6bc-487264603d64 | note | Verification Activity: Activity - HP
87ba601d-f22f-517e-b051-e6aa3e1317a4 | note | Verification Activity: By - ENG
adcc761f-5e53-5005-86f3-480d4f123fd3 | signoff | AUTHORITY HOLDPOINT
4c2e10ea-a175-5501-8be0-7d21ee763da0 | checkpoint | 1.2.2 - Particle Size Distribution
3f78be19-5dc0-5a94-856e-16319da0c146 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
55384137-ebc9-5d31-b8cf-193274234304 | note | Acceptance / Conformance Criteria - Max Particle Size 53mm
bd879df8-6647-535b-92d3-71c355e11970 | note | ○ Max 10% passing 13.2mm sieve
33befdab-e8cc-53bd-86f4-3e1fe7a022b3 | note | Standard / Specification - Appendix XVIII
48a6b8c6-5784-56f1-bf51-9720e4dbafac | note | Verifying Document - IANZ Accredited Report
e173c21b-cf0c-563c-a3ae-8fa2d28dbbb3 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3
943b5235-da03-5c2b-a373-33983d6f6a4c | note | ○ Results to Engineer 2wks before importing
4bb95a93-2be2-53d3-93ec-fd0353562eef | note | Verification Activity: Activity - HP
e68bc3d5-f9c9-5a6b-bb96-686566b9fec6 | note | Verification Activity: By - ENG
cee16103-a60f-5369-a9e2-e6254b70928e | signoff | AUTHORITY HOLDPOINT
0db13832-0d7b-5811-9f2b-9036b5e2af35 | checkpoint | 1.2.3 - Weathering Resistance
948550e4-3ec5-595c-a387-9ae2f109058f | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
be81eb03-fb6e-5c51-8c0c-eba179bd0121 | note | Acceptance / Conformance Criteria - CA or better
4a67f625-1073-5180-8062-f598d42bbec9 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
b5f62c44-a545-5811-a235-f0150daced0b | note | Verifying Document - IANZ Accredited Report
cd72ab1b-0e87-57ca-8fdb-e7767554a5ef | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
06b19ba1-6f34-5a8a-943e-e9bf4068b8e7 | note | ○ Results to Engineer 2 wks before importing
134fffe0-bb95-5474-acff-4a0b80d25681 | note | Verification Activity: Activity - HP
3580e4fd-7fea-50c9-b73b-1d753f2ebcb4 | note | Verification Activity: By - ENG
f8ad0c43-4aea-5958-8a75-98ef19bda0d6 | signoff | AUTHORITY HOLDPOINT
5f985f9c-dd22-577d-8c94-898c7067297e | checkpoint | 1.3.1 - Crushing Resistance
7d88ae8f-aacb-5ba1-a9dd-37055c7c23bd | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
3a031fb5-ace4-54b7-b252-460cb31ce1b6 | note | Acceptance / Conformance Criteria - >100KN
f13071fb-691a-5c0c-bca7-10798e7568d5 | note | Standard / Specification - NZS4407:2015 Test 3.10
42024e8d-9dd2-5725-9f08-4ca5ee761e3d | note | Verifying Document - IANZ Accredited Report
675f19af-3f03-5ad3-9a88-86c2a2a6163b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
1ea7cb42-aff4-527d-8938-d60909eed40e | note | ○ Results to Engineer 2 wks before importing
98ebac46-eddd-5a3f-9636-73e72d829ab2 | note | Verification Activity: Activity - HP
9024e84e-5bb7-5456-943b-72dfc7f76479 | note | Verification Activity: By - ENG
e1cc8513-47de-563e-b2e1-210990b82f31 | signoff | AUTHORITY HOLDPOINT
679d1cf7-1c37-591d-ade8-40e0077a84fa | checkpoint | 1.3.2 - Soaked CBR
b17195be-2350-537e-a4f1-c686c9597816 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
41a6630f-929c-5520-af0d-c4d419268605 | note | Acceptance / Conformance Criteria - >25%
e7eee3f0-beb3-5fb6-87d0-fe4ea1a7ae74 | note | Standard / Specification - NZS4407:2015 Test 3.15
63e32444-6124-5d0b-9b01-2bf96924ad2b | note | Verifying Document - IANZ Accredited Report
b8a06ec3-447a-5a39-9abc-a7b864014a51 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e76faaf1-fe0c-5c37-9516-d8a9bac6924a | note | ○ Results to Engineer 2 wks before importing
e63c1d29-1a59-5bc0-8852-a4b89c27d701 | note | Verification Activity: Activity - HP
0bf3c9eb-ca20-524c-995e-6d89f61b796c | note | Verification Activity: By - ENG
22329d2a-5eb0-5d2f-a227-929669dd0fd5 | signoff | AUTHORITY HOLDPOINT
4ed8e59c-467c-5ed9-acf7-1b572e5a503d | checkpoint | 1.3.3 - Weathering Resistance
34bc591f-30c4-5f4b-b481-f749d39a491b | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
072767ee-0561-5a26-9ef8-64c69049d9ee | note | Acceptance / Conformance Criteria - CA or better
feedd065-2f88-54e7-8635-ebe561ed2ee7 | note | Standard / Specification - NZS4407:2015 Test 3.11
6d135723-edf7-55e4-b16d-59a27ac38342 | note | Verifying Document - IANZ Accredited Report
4a18710c-fdb7-545d-bf88-8d83d6544412 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
01c71aa5-4e8f-5d97-bef0-809cf3781743 | note | ○ Results to Engineer 2 wks before importing
475aa73a-9a71-5372-b0cc-560306eadffc | note | Verification Activity: Activity - HP
0ced78a5-267e-5b1b-834c-4e17421f1aa5 | note | Verification Activity: By - ENG
258e872d-a211-5144-a411-e1eacd40a379 | signoff | AUTHORITY HOLDPOINT
8cf048f8-1300-5e8e-a662-95d0f261ac5f | checkpoint | 1.4.1 - Particle Size Distribution
e5fa3848-73e3-523d-9284-2545c0d5fd87 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
44fcb242-d1f3-5d8f-92dc-8b0f10b6cff7 | note | Acceptance / Conformance Criteria - Fitting within standard AP65 grading curve
a3c7aaf0-6404-5902-867a-804015eb596c | note | Standard / Specification - NZS4407:2015 Test 3.8.1
4bc54ea8-a896-5fd2-b6ff-f9015d32b433 | note | Verifying Document - IANZ Accredited Report
f4909142-1a5c-58b7-8333-7b8b6d085886 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
ac296b3c-0da4-551c-8922-98e75b0094c8 | note | ○ 0-400 - 2 tests
b58ff792-a573-5c7f-a938-085f3316b50d | note | ○ 400-1,500 - 3 tests
4746ccc3-3f06-534b-b2eb-db8a12c27607 | note | ○ 1,500-4,000 - 4 tests
c66bc070-6799-5bb2-8636-cb3fb4b6edc1 | note | ○ >4,000 - 1 test for each additional 1,000m3
93883602-1fbc-55f4-896c-67067d7eb706 | note | – Results to Engineer 2 wks before importing
f0e7814c-c9ee-5263-add3-e23f07a7b09c | note | Verification Activity: Activity - HP
90d665bf-f40a-59a0-af98-b2880beaf127 | note | Verification Activity: By - ENG
f922a06d-cac3-5c61-8fcc-c4925e79effc | signoff | AUTHORITY HOLDPOINT
47abf264-56bd-59c4-a276-c61dae763677 | checkpoint | 1.4.2 - Maximum Dry Density and Optimum Water Content
4499f4ad-f72c-5f73-8230-68caed1cb4cb | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
e3759e13-1749-5c96-a2f4-94d15751df05 | note | Acceptance / Conformance Criteria - Report Value Only
85f030b9-0f34-564e-8ed6-4fac153ef291 | note | Standard / Specification - NZS4402:1986 Test 4.1.2
f2510355-2e29-54de-a9cb-66e844e25e36 | note | Verifying Document - IANZ Accredited Report
83646c8e-f4b7-595c-ab2b-76e89287b8c8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e666ed9c-a803-5724-97e9-8f6209591bdb | note | ○ Results to Engineer 2 wks before importing
e44d8f7e-e7e6-5752-9d97-68d459847a91 | note | Verification Activity: Activity - HP
11bc04c8-46da-5fcf-80ca-298bc5c2c362 | note | Verification Activity: By - ENG
1221a0cb-dfc4-5d49-965e-bb9d0085ffae | signoff | AUTHORITY HOLDPOINT
b2938728-cc53-58e7-9f1b-0baf459daaae | checkpoint | 1.4.3 - Plasticity Index
67fc375f-8de5-539d-ba76-5a0a1638c85c | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
782e2c95-0e1a-5478-ab4a-58b458395351 | note | ○ NZS4407:2015, Test 3.3 Plastic Limit
70e469cb-9e03-5e51-b3ee-b68ba0cf856e | note | ○ NZS4407:2015, Test 3.4 Plasticity Index
2e4c8fcb-5bb6-5dd1-b454-ebbad6d874a0 | note | Acceptance / Conformance Criteria - NP
8c944f3e-aac8-50aa-9931-e15ed0170446 | note | Standard / Specification - NZS4407:2015 Test 3.2 NZS4407:2015 Test 3.3 NZS4407:2015 Test 3.4
b207f059-6a83-5f03-b3bf-fb16a437186d | note | Verifying Document - IANZ Accredited Report
0c1b8321-ed56-565b-b159-9894c9cec91b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
b0e0af85-d46a-5e28-b08c-502a847308bb | note | ○ Results to Engineer 2 wks before importing
737b6779-90a8-5acb-92f8-a5def5c3d85b | note | Verification Activity: Activity - HP
f0f15341-5f32-5df7-9b82-bf2fbdbab5b1 | note | Verification Activity: By - ENG
2130d6d8-a12e-56f9-b162-c0c07b0bb707 | signoff | AUTHORITY HOLDPOINT
eda8ae89-4166-5dcf-b5c1-0555f7e90d29 | checkpoint | 1.4.4 - Sand Equivalent
48443824-0139-55f2-a533-12054bc550a0 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
9297c6c1-a4fb-5783-8180-20eb7a73824b | note | Acceptance / Conformance Criteria - >25
8c1daf38-8a05-5acd-8b8d-8694a9a9ea77 | note | Standard / Specification - NZS4407:2015 Test 3.6
78bd499e-8a65-5b60-a872-7542e50ee79f | note | Verifying Document - IANZ Accredited Report
f5f856c0-165b-59b9-bcc8-0878e288a7c9 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
0ef4d92e-8673-5ef5-81d5-091f65cad3cc | note | ○ Results to Engineer 2 wks before importing
dbd73ed9-3c6b-58be-946b-193f01e5e124 | note | Verification Activity: Activity - HP
c5314346-dcd4-59a4-99a2-2f788de14d47 | note | Verification Activity: By - ENG
a4e028df-2c24-5c0b-b955-97ddb96388d8 | signoff | AUTHORITY HOLDPOINT
f674adf9-4247-5a76-b2e9-b3657e6ced65 | checkpoint | 1.4.5 - Clay Index
20acd18c-e04f-5a9e-9f71-2413af2e804e | note | Detail - NZS4407:2015, Test 3.5 - Clay Index Test Report
148661c4-7060-5082-bcb3-b2aba5208283 | note | Acceptance / Conformance Criteria - Report Value Only
2e708397-9b23-5d86-9c08-5436428c26a5 | note | Standard / Specification - NZS4407:2015 Test 3.5
cbf291b1-265c-5231-816c-3a4f1f08f704 | note | Verifying Document - IANZ Accredited Report
98d4c346-268c-50f2-8b33-f7ff9d44415d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
c06c540c-002a-5391-9285-c47efeec67dc | note | ○ Results to Engineer 2 wks before importing
e0134cbd-67f2-56b2-8b90-c8e4563c387e | note | Verification Activity: Activity - HP
383f7aee-61b1-5a1d-9fa0-e70f63b07ba9 | note | Verification Activity: By - ENG
85b694a7-1d1f-5216-b70c-8ab4eadd76df | signoff | AUTHORITY HOLDPOINT
c8b1d175-5f5d-5f00-9439-4d640014e228 | checkpoint | 1.5.1 - Crushing Resistance
01438abd-a7b8-5b30-9852-092688c76841 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
94841520-5752-56e5-8276-7094df24d800 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
33acede1-53b8-5ed6-a06e-54de2b7c5e7c | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
258f09ab-3e03-5e2c-9436-42b64a80f462 | note | Verifying Document - IANZ Accredited Report
75a2b696-b288-5e67-88f9-0f237b2f0d83 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
72a5b06b-398b-5018-9f6f-9c08f64cf1c1 | note | ○ Results to Engineer 2 wks before importing
98ba8984-a319-519d-9ef3-2058ca901299 | note | Verification Activity: Activity - HP
5eb4a7f6-748a-59c6-bbdc-937afdd0a7c6 | note | Verification Activity: By - ENG
c7885017-b248-587f-9d80-5265c567d250 | signoff | AUTHORITY HOLDPOINT
34e08bfa-b1e5-5a8e-952f-d8363084b498 | checkpoint | 1.5.2 - Soaked CBR
c7e2f01d-42bb-5bdd-9fd5-714022f95480 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
83e3a001-3d3d-514f-9f34-63fb738bdf55 | note | Acceptance / Conformance Criteria - ≥ 60%
0d29adce-b152-50e7-afdb-641350392408 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
75d4f7d2-5801-55c4-a473-5dabe0060293 | note | Verifying Document - IANZ Accredited Report
aec3f8ae-fb87-5c72-9cbe-5c0c82a2e235 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
6adbab04-e7e7-5f17-a334-1196189ed69d | note | ○ Results to Engineer 2 wks before importing
bdbc63d9-44ea-5d56-be39-fe3a88959820 | note | Verification Activity: Activity - HP
7e4dcc56-d732-517d-b124-a4e54fe92bd9 | note | Verification Activity: By - ENG
21362b24-5eae-5d82-bf51-7063bc20fcbc | signoff | AUTHORITY HOLDPOINT
e0ee8b37-5207-5a67-9235-4db5443a5a46 | checkpoint | 1.5.3 - Weathering Resistance
8c02c934-636c-57e8-bbb6-973ec9d7a377 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
c2e973a7-3bda-5f85-9d60-f9e95b1e7862 | note | Acceptance / Conformance Criteria - CA or better
0c4b66d6-35d4-5795-91e6-6045f195c57b | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
4eb7d36d-4d27-5c49-b85d-7d7a0fbd6e39 | note | Verifying Document - IANZ Accredited Report
30d2ea4c-645d-5804-b20b-1172403f2745 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
8555ae75-b9f5-593d-a1fc-651952af38f7 | note | ○ Results to Engineer 2 wks before importing
df1ece9c-2429-5b93-a84b-46e922d930b1 | note | Verification Activity: Activity - HP
13d242ef-1556-579d-bf11-fc690a5246e4 | note | Verification Activity: By - ENG
307eadad-dc3e-520c-bd11-926abfbdf1a6 | signoff | AUTHORITY HOLDPOINT
be766fdf-de48-5496-8902-95cb926372dc | checkpoint | 1.6.1 - Particle Size Distribution
afc63c1d-7a5e-5ade-ba57-33e6f233757c | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
42ec3bcf-c697-5020-ac2e-a6e2f46aca61 | note | Acceptance / Conformance Criteria -
11b3b027-6462-50c9-b4bc-268e3b733f9f | note | – – – – – – – – – – – – –
7d6b9c5c-35af-5282-bcb5-5a886ceca8b3 | note | Sieve Size ¦¦ % Passing
5629087b-b521-5fe2-97de-1268342789e0 | note | – – – – – – – – – – – – –
0395ea83-31db-5cd5-b2be-921663413061 | note | 63.0mm ¦¦ 100% passing
76a59ec4-eb15-5ff1-8dcc-0e78f1a210a9 | note | 37.5mm ¦¦ 55-85% passing
f068d9c3-e2f5-56f1-9cbb-7a6a378942d4 | note | 19.0mm ¦¦ 33-65% passing
21b236f8-30b0-5a42-aab5-eb103f884a91 | note | 9.5mm ¦¦ 20-50% passing
4b451d00-ac48-5830-a03a-96b1c05b7e64 | note | 4.75mm ¦¦ 10-36% passing
cca22675-3c65-5263-8404-5c3a9a51fbe9 | note | 2.36mm ¦¦ 5-27% passing
cddbeb4e-e884-5418-99ad-4f7cc0735485 | note | 1.18mm ¦¦ 2-20% passing
ef14642a-0be7-5e00-8bdb-7e9184cf4e8b | note | 0.425mm ¦¦ 1-13% passing
3ce79264-d0da-5fbd-a58b-c3dfb85bbd4b | note | 0.075mm ¦¦ 6% max passing
7bc702a5-474f-50d0-9a8d-04d2394b435e | note | – – – – – – – – – – – – –
8a1b8243-d16a-5934-ae82-7d28f937e38b | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
52f228bf-99e0-5c09-b21a-92fbcff47a29 | note | Verifying Document - IANZ Accredited Report
f1a0c1a1-e058-5ca7-977d-12a089b95097 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
8c2053ec-407b-5cc0-be91-b580953454b5 | note | ○ 0-400 - 2 tests
5d3a0052-cd19-56e6-9e90-899c953ca979 | note | ○ 400-1,500 - 3 tests
89ccf57c-e416-5b9f-84ce-d03a610ed645 | note | ○ 1,500-4,000 - 4 tests
4520b710-b4af-58bf-85fa-e5a120cf40d8 | note | ○ >4,000 - 1 test for each additional 1,000m3
67f70142-0878-5eea-9773-0ad3252ac566 | note | – Results to Engineer 2 wks before importing
36f75e96-1cd3-59bd-9fd2-99902b66b7ff | note | Verification Activity: Activity - HP
f4223ca7-1e0f-5ec2-b1c3-92c4e2e7ad6a | note | Verification Activity: By - ENG
55f6b97f-a0ef-5509-80e3-4cbba5b25836 | signoff | AUTHORITY HOLDPOINT
caaf95fd-2094-5bb8-8bec-67f91091c1d0 | checkpoint | 1.6.2 - Shape Control
072ab6ce-8c41-5daf-9b44-a2849e82cab9 | note | Detail - Tolerance allowed from approved grading curve (%)
02c2a873-5fc0-52e6-8a33-5a71636c1f69 | note | Acceptance / Conformance Criteria -
e199ebe5-7b71-5340-9d2b-407cb752b83f | note | – – – – – – – – – – – – –
14b7eba2-f6d1-511b-9be1-b7ad57a65204 | note | Sieve Size ¦¦ % Tolerance
a567df51-0446-5eae-8c34-17d89de23ed3 | note | – – – – – – – – – – – – –
2b931a6a-cb2e-5ddb-91bf-cb0f28d711ca | note | 37.5 – 9.5 ¦¦ 34-50%
6c446530-aae5-55e0-9408-8e11ff380f14 | note | 19.0 – 4.75 ¦¦ 18-40%
acba0edb-138f-5a17-ae06-50e22b297ddb | note | 9.5 – 2.36 ¦¦ 12-32%
ad1be66f-7aa5-51c3-8883-709e1258b9d1 | note | 4.75 – 1.18 ¦¦ 6-24%
ccf8fba8-e634-5ecd-81e7-4692492db16d | note | 2.36 – 0.6 ¦¦ 2-20%
6bef8454-4bea-5d39-838e-3194471d9c2f | note | 1.18 – 0.3 ¦¦ 0-15%
325124ed-f1ad-517a-a700-b18c2fe668e0 | note | 0.6 – 0.15 ¦¦ 0-12%
445280ea-7c7f-58d9-b79e-4dca086b82d5 | note | – – – – – – – – – – – – –
db26026a-1ed0-5962-8361-f5fb81cb6f01 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
1b8891b2-02bd-51d5-9d9f-16b878dc04da | note | Verifying Document - IANZ Accredited Report
69ed027e-c706-52b8-8cbd-6bb85407f7af | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
bb7398d3-0519-5ce1-a518-e93d6c143e28 | note | ○ 0-400 - 2 tests
b04b3f09-aea4-5295-9de1-c6f61b5f1524 | note | ○ 400-1,500 - 3 tests
42df31e6-a33b-5d1b-bc93-ea1ad69c7a1b | note | ○ 1,500-4,000 - 4 tests
da97a941-481e-5c38-81cb-3ba029faee0c | note | ○ >4,000 - 1 test for each additional 1,000m3
73468e33-5ed7-5e18-9492-707620ceaf89 | note | – Results to Engineer 2 wks before importing
e3f51ade-c2d4-5df5-aebd-167686e14dc6 | note | Verification Activity: Activity - HP
32d325e7-eef4-525f-ad8f-93f91502c71e | note | Verification Activity: By - ENG
6cff9c4a-facf-5300-bd4c-e1b20fd4bb30 | signoff | AUTHORITY HOLDPOINT
ed826021-51b3-5439-99ac-54c432e8af8f | checkpoint | 1.6.3 - Sand Equivalent
6b935366-f67e-515c-a5a3-716ca8a2ba3d | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
deb6986c-5b5f-5124-bbb1-c590aaaf4db0 | note | Acceptance / Conformance Criteria - ≥ 30
a8116b3b-0ed0-5bca-bc26-db27989c6294 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
180bbf1d-5f37-51f2-bfe9-32f9a8a9bf5b | note | Verifying Document - IANZ Accredited Report
6100e88f-e8fb-5f8d-a878-efffecbb87a1 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
1e24a64e-af4c-5175-b765-7311dcda9797 | note | ○ 0-400 - 2 tests
e8034803-9506-5300-baf0-3fb3b6cae353 | note | ○ 400-1,500 - 3 tests
9364c3fc-4d3f-533b-897e-91387d3ae7fa | note | ○ 1,500-4,000 - 4 tests
591d2da9-ec93-5fbf-8ae9-d8e6d078e4f1 | note | ○ >4,000 - 1 test for each additional 1,000m3
dff31db3-f635-5ad0-9a10-ea9664b04659 | note | – Results to Engineer 2 wks before importing
f8fc7d49-adf6-503c-a908-353080911e3f | note | Verification Activity: Activity - HP
182aaa08-edb4-5bd7-bf24-7e7928e9e1a2 | note | Verification Activity: By - ENG
6901966c-9669-50d5-b04b-3eb27016ca86 | signoff | AUTHORITY HOLDPOINT
c2630989-ebd4-59ac-9b00-da45e0ca90d7 | checkpoint | 1.6.4 - Cone Penetrometer Limit
45854cf4-a7cc-56b7-a35f-9e9a94dd9b18 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
b09f0cfc-7499-5964-be03-ac394212238c | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 25
fb978d9a-b5e5-5c3d-bbe1-d440726ecbdc | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
af048f81-5ab3-5d05-ba01-5669402fbf9c | note | Verifying Document - IANZ Accredited Report
84fe6473-678c-561e-a314-ebdd83e258d1 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
9c31e1a6-cc6b-54df-b083-469171a060d0 | note | ○ 0-400 - 2 tests
63f1651a-c0c7-59c9-bd3b-dbc8a6aeb6e9 | note | ○ 400-1,500 - 3 tests
f0d6d72d-f7b5-5cd5-9481-13f81b304b9d | note | ○ 1,500-4,000 - 4 tests
fe810a58-c474-5d4b-b602-1a1b5d80e188 | note | ○ >4,000 - 1 test for each additional 1,000m3
41bca39c-b3e3-5d2f-b5ef-91b4516adbd7 | note | – Results to Engineer 2 wks before importing
57c52052-205f-585d-b1bc-eb46f324eab5 | note | Verification Activity: Activity - HP
5f81fcd4-b178-55fa-9921-428e903821e0 | note | Verification Activity: By - ENG
4a85db6d-5756-5b33-847b-4c92a593ed52 | signoff | AUTHORITY HOLDPOINT
9b54ee39-e5f8-5b11-928b-a66ec127db33 | checkpoint | 1.6.5 - Plasticity Index
fb9a449a-1a4a-5df9-8249-26cf2be37b68 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
2752871c-0019-5173-95cb-65d927587771 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
5f027b7c-31bc-59b1-8231-3121eed86ae2 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
0c92e546-076c-527b-b38d-91e0f561202e | note | Verifying Document - IANZ Accredited Report
60e59c0a-05af-52af-915a-d6bed6ce69c0 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
ccb3c2b5-dfec-5d53-a744-f7a852c817dd | note | ○ 0-400 - 2 tests
ba507eb1-e82a-56fc-b70d-d11675ad30dd | note | ○ 400-1,500 - 3 tests
186dfb54-3c65-5a2e-bab5-eb9e89f59b18 | note | ○ 1,500-4,000 - 4 tests
1cc39e36-02ed-5c01-a2e8-be413be2b95d | note | ○ >4,000 - 1 test for each additional 1,000m3
438ac739-c2c2-502c-9d36-6550e6a92373 | note | – Results to Engineer 2 wks before importing
979107d4-e7f1-5aa8-bf6e-6f5dafcfa936 | note | Verification Activity: Activity - HP
a285c70f-0706-5fc5-a637-b7813541b9ac | note | Verification Activity: By - ENG
cbc9d276-320b-5638-9c2a-31281d96a6ba | signoff | AUTHORITY HOLDPOINT
dcab115c-9154-5fdd-a72f-f20bf343f4a3 | checkpoint | 1.6.6 - Accelerated Weathering
7b7bf50b-d26b-50d3-b58f-0ca514fe90bf | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
f6195fa8-f77d-5cbb-b6d7-2b3b297f9dc9 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
7b7add49-4589-5d15-a11f-f4479718ddc5 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
2a485930-59a1-56a1-a0ef-d611fe9974a5 | note | Verifying Document - IANZ Accredited Report
b4cbc3ca-8881-58a2-a256-622071605df2 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
cc32e1b4-bc25-547d-9357-875b53db9eff | note | ○ 0-400 - 2 tests
294d0c37-3745-5cc5-968d-e3d9f00aac15 | note | ○ 400-1,500 - 3 tests
21b5e54a-2d44-557c-b87b-f430fb85ddfa | note | ○ 1,500-4,000 - 4 tests
db1245eb-fd85-550f-87fe-483b9a7e5126 | note | ○ >4,000 - 1 test for each additional 1,000m3
184a9b66-ce16-5803-b3b9-1397eee2e571 | note | – Results to Engineer 2 wks before importing
0624afcd-70e1-5e22-bb1e-c140fd945959 | note | Verification Activity: Activity - HP
6535c7e0-2aa6-59aa-b040-02bc1c99aa03 | note | Verification Activity: By - ENG
6b9745a5-966c-5488-8ec3-e653d9f85eb5 | signoff | AUTHORITY HOLDPOINT
7a800fc0-1e63-543d-b3eb-9b78df73e3a7 | checkpoint | 1.6.7 - Maximum Dry Density and Optimum Water Content
8b8af90a-b043-580a-9706-0b0284cda8b5 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
90d0e7a4-33af-58b2-96ed-fb60c6c8bae3 | note | Acceptance / Conformance Criteria - Report Value Only
8f561e22-a37b-5b89-a9a4-8e52019697b5 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
243dcd90-b765-58c3-857c-3b75b4f3f35a | note | Verifying Document - IANZ Accredited Report
88569e98-785a-51b8-a81d-01ed2a58e76a | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
f263d608-a142-56ee-ada0-08b28834f794 | note | ○ Results to Engineer 2 wks before importing
424c78fd-7b32-5a9d-8c9c-3835c046f282 | note | Verification Activity: Activity - HP
fb972efb-64a1-5490-bb19-07834a778a5f | note | Verification Activity: By - ENG
be7f0025-4d03-5d0c-8da9-84b785a21758 | signoff | AUTHORITY HOLDPOINT
d7a6912e-9edc-5761-b53b-87858c42b973 | checkpoint | 1.7.1 - Cement Modified Maximum Dry Density and Optimum Water Content
ed4cf536-0221-54d7-81dc-d614b8827d21 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test using 5% cement
e292a394-6f92-545f-948f-132aaa47e5e3 | note | Acceptance / Conformance Criteria - Report Value Only
60a25b7d-173b-5776-b692-f77154f3e7e4 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
4c289582-16b7-524d-b1ba-367d474ba083 | note | Verifying Document - IANZ Accredited Report
41e753e2-5147-581b-a0b3-bc3a6ad2f01a | note | Testing Quantity Required (based from schedule qtys) - 1 Test at 5%
4e2c09ca-d123-561d-8649-5e53557c2147 | note | ○ Results to Engineer 2 wks before importing
525d7eb6-996d-5130-b208-8a8fc6a87dd0 | note | Verification Activity: Activity - HP
9bb77728-008c-5b3c-9889-d0b72a9e7364 | note | Verification Activity: By - ENG
27e8ec3c-36e4-540a-92b6-c2263eb72b72 | signoff | AUTHORITY HOLDPOINT
4c1005da-b170-5f17-acaf-a0b8efdfc978 | section | SECTION 2 – SUBSOIL DRAINS
3a9aa7b7-54e5-5092-9ef8-3e33a828f3f5 | checkpoint | 2.1.1 - Subsoil Drain inspection
7868e328-4d23-5691-8770-cae5b4d4f551 | note | Detail - Subsoils to be placed below kerb lines and inspected by Engineer
3bcb6d41-bae3-5deb-9491-2c7d228b1520 | note | Acceptance / Conformance Criteria - Engineers Approval
d57e16ed-6919-52c1-95f7-70fd58165787 | note | Standard / Specification - PS 17.6.3
c577da4a-72fa-5c18-b4c8-55b22115f979 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
93e1a397-b736-5c9a-8ebf-dc57911d4862 | note | Verification Activity: Activity - I
41dd316c-c3e0-5062-be0c-067fe9eea269 | note | Verification Activity: By - ENG
e56ae963-bc62-520f-b544-a42dcdae9917 | checkpoint | 2.1.1 - Excavation
cdb3458c-7630-5e66-b6cb-ca25937d57ce | note | Detail - Excavtion of Trench should be within tolerances.
40d99778-f0aa-5e21-a611-7908c054c452 | note | Acceptance / Conformance Criteria - 335mm deep x 300mm wide
5ab95e11-ee18-5b52-9137-a2541cb12f0f | note | Standard / Specification - Drawings
d6faa342-f2ae-5806-b119-ca7da8667f84 | note | Verifying Document - Checksheet
6d182f0b-404e-52bc-a7e2-244b7b2bd3a5 | note | Testing Quantity Required (based from schedule qtys) - While Construction
3a47aaea-d771-5ddf-8085-2e93554bcfd9 | note | Verification Activity: Activity - M
79b0301d-dd74-539a-a7c8-7e937d007611 | note | Verification Activity: By - SE
082565ed-d47c-553b-9b97-ad38d4e14da1 | checkpoint | 2.1.2 - Placement of Bidim
344b9e30-8f40-58cf-b76d-c1ca2bf7adf5 | note | Detail - A29 Bidim to be placed andd wrapped around Trench.
631b007d-bd15-5f77-a730-97ae04418b88 | note | Acceptance / Conformance Criteria - Minimum Width 300mm.
6beb958f-f379-5d02-a555-4ecda4642f8c | note | Standard / Specification - Drawings
4ef1ca6a-6fb4-55b4-bda0-c4a927c86648 | note | Verifying Document - Checksheet
803bc173-e3bc-52d1-9793-cdbc1bb2a959 | note | Testing Quantity Required (based from schedule qtys) - While Construction
0988b146-098d-536f-bc8e-a9fbca975f8a | note | Verification Activity: Activity - M
514da5a4-b747-5c78-afdc-210572ab4f06 | note | Verification Activity: By - SE
dde19193-4b1f-5c77-8127-b5518f3fbd5d | checkpoint | 2.1.3 - Cushion (Bedding)
b4cfd0b2-3b4c-58c8-90e2-e551dfb4f122 | note | Detail - Pipe must have 75mm of Cushion. Drainage 60:40 Material to be used.
c294d646-8459-5aea-8bc2-487924083423 | note | Acceptance / Conformance Criteria - Minimum 75mm
0744bd33-a98a-57f8-b154-902dc44dc06e | note | Standard / Specification - Drawings
64d5b4c2-6fed-5710-9436-b106a1b24db6 | note | Verifying Document - Checksheet
407e2e0f-286a-5aea-bb87-a68dd38c0d09 | note | Testing Quantity Required (based from schedule qtys) - While Construction
c14d4c54-57ad-5972-b6f5-2785b804d38d | note | Verification Activity: Activity - M
582f1401-3333-5ddf-a464-d26d70abc96f | note | Verification Activity: By - SE
70e501d2-021b-5208-8c4a-a75a34ef2fb5 | checkpoint | 2.1.4 - Placement of Pipe
a9ebf62b-949f-5767-9ece-c494ff7acb15 | note | Detail - 110mm Perforated Pipe to be laid Down
122428a3-f35c-5817-b700-62e537a55f99 | note | Acceptance / Conformance Criteria - As Per Drawings
5238ffd0-8d3c-5491-be3c-84e34eb7008f | note | Standard / Specification - Drawings
37de8b47-21c0-5782-962c-3a8134f02583 | note | Verifying Document - Checksheet
41d449b3-e63c-548e-94b9-a01f7c8176c2 | note | Testing Quantity Required (based from schedule qtys) - While Construction
b89b98b6-fe33-5794-9a08-989a50473c2e | note | Verification Activity: Activity - M
5a1b0ef7-6f45-5fa4-990e-0655251c80b6 | note | Verification Activity: By - SE
f1f568b8-4530-5632-a55b-175f9a06927b | checkpoint | 2.1.5 - Backfill
0acee75e-890f-5323-b025-f28d84e82fcc | note | Detail - Pipe Must have a 150mm cover from Bottom of Pavement. Drainage 60:40 Material to be used.
81530b6c-07f7-553f-9624-771066d2518b | note | Acceptance / Conformance Criteria - >150mm Cover
a443c08d-9a74-5bfb-ae0c-f94d513f8a21 | note | Standard / Specification - Drawings
a9674791-131e-5bba-a956-b2008e9bd8db | note | Verifying Document - Checksheet
28c038e7-6229-5510-a7ab-b847ddc50ff1 | note | Testing Quantity Required (based from schedule qtys) - While Construction
30b7238b-eb99-5a30-9d5b-fb624982f99f | note | Verification Activity: Activity - M
f74c140a-a34a-5cd9-8623-8632d710cae4 | note | Verification Activity: By - SE
8a9f9b68-09a7-55c6-8987-51db7b75daad | section | SECTION 3 – PLACEMENT OF GEOGRID AND GEOTEXTILE FABRIC
ccf9594e-d49f-5329-bf83-626fe37fa59f | checkpoint | 3.1.1 - Placement of Geotextile Fabric
415e5660-d373-530b-919a-5202818ba849 | note | Detail - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
2024858b-c0eb-5e8c-bd06-e789df837600 | note | Acceptance / Conformance Criteria - Visual inspection
cde3dff5-c040-532f-9565-be662c449405 | note | Standard / Specification - NTC0097
adb1d676-72e5-5de3-aec7-cdb1a68471f5 | note | Verification Activity: Activity - WP
e6b6b0a9-36bd-53f2-a597-d57f65f8d644 | note | Verification Activity: By - ENG
ac5f9cb4-cd40-5b3c-8bd5-624f64275a3b | checkpoint | 3.1.2 - Onsite Check by Engineer on Geogrid
4f5ebb76-0931-5c69-b304-957ecbe93037 | note | Detail - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
4b2f85c5-b2a2-59e0-8675-d17f58111be6 | note | Acceptance / Conformance Criteria - Visual inspection
c6fa8314-912c-547f-8d10-b9a954bdbdc6 | note | Standard / Specification - NTC0100
15e337d8-0423-5638-a916-94c470827d39 | note | Verification Activity: Activity - HP
93d51212-68bb-5070-9c33-12d1a099ac41 | note | Verification Activity: By - ENG
eb08b0ac-65e3-542c-979a-67945f78695a | signoff | AUTHORITY HOLDPOINT
030f9409-3014-523d-91b6-81f9b1a23f7e | checkpoint | 3.1.3 - Placement of Geogrid
166e9956-1924-5458-85f2-6719bbe4e5ce | note | Detail - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
f9c619ac-cb30-5417-9146-6cc67c38db53 | note | Acceptance / Conformance Criteria - Visual inspection
6ec490da-5f83-5d26-b01f-48becd32dace | note | Standard / Specification - NTC0100
77e52eaf-1927-5f7d-9ed9-501a797ccaa0 | note | Verification Activity: Activity - WP
e5830aea-f1d0-5c3a-9135-dbedab1df752 | note | Verification Activity: By - ENG
c85b9499-6bb3-50cc-bff6-dda40dbcab08 | section | SECTION 4 – SUBGRADE IMPROVEMENT LAYER TESTING (UNBOUND AP65)
fbb83861-2f3e-5f9e-b7aa-a3a6f3dddc54 | checkpoint | 4.1.1 - Plateau Density Test
c48daefa-a277-52ee-bba6-769b0ab0db6f | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
b5b4de30-5108-5a03-81cc-35530b3904fe | note | Acceptance / Conformance Criteria - Plateau Density Report
941c8fff-c4a4-534a-9b0a-7128f4cffd9a | note | Standard / Specification - NZTA B/02 7.5
deb94de3-9a57-5ffd-be75-78a102cf2c96 | note | Verifying Document - IANZ Accredited Report
e0fe0d02-b179-5f2e-8524-ac2e5806a203 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
fc9bf276-24bb-5b36-8897-c8e8a807af69 | note | Verification Activity: Activity - I
20c27d30-bfe4-5aa7-b9d7-f43375c665e3 | note | Verification Activity: By - SE
8978f6d9-9591-5dfb-be5a-ffb27e512bcf | checkpoint | 4.2.1 - 3m Straight Edge
088ac201-f650-57b1-b6bc-f73ae733637f | note | Detail - Formation check to ensure surface is smooth
4b2ae4f8-e2fd-55bb-8d15-850187cae87e | note | Acceptance / Conformance Criteria - +/- 10mm
7a7eb108-7af9-5f00-81d5-45280caae87f | note | Standard / Specification - TNZ B/2 7.7
d4bbf039-0622-5518-8cea-7e16a0b6460b | note | Verifying Document - Check Sheet
b748789f-5e3f-58ef-8c72-932d96d35498 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
9acae8a8-22e8-5d47-b432-47bb2acf0616 | note | Verification Activity: Activity - I
d0644fb8-e0ce-550d-a37c-ba0441023c2f | note | Verification Activity: By - SE
706bd440-6a52-559d-9175-cad4665e6d2c | checkpoint | 4.3.1 - Stringlines or equivalent
29d7b230-00ec-5e79-bbae-95ef785924e0 | note | Detail - Stringlines or equivalent to check finished height of surface
5d47af75-e454-5d22-be07-1bfa69a2c953 | note | Acceptance / Conformance Criteria - -25mm + 5mm
660b65e9-ac2b-510f-994a-42e76760fe5e | note | Standard / Specification - NZTA B/02 5.1
9021868d-dc91-5f0c-80ec-c887b901b5f0 | note | Verifying Document - Check Sheet
9eb68c1d-38bc-5318-8d7c-767cb0c507cf | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres, 1 set = 5 tests
5de7bb6e-ac69-54a3-a800-361f0cc08207 | note | Verification Activity: Activity - I
bb65ba39-4fad-5d33-acc7-ba525da961e9 | note | Verification Activity: By - SE
5fa3f95a-3bc5-594a-9cd0-86a23e986f7a | checkpoint | 4.4.1 - Compaction - NDM
b3e0a7c7-932d-5cdf-976c-9887a8a4b92a | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
51c3766d-56c5-5c8e-a7db-7eec9003e34a | note | Acceptance / Conformance Criteria - Ave >95% of MDD
6815098c-c50c-59ae-b4a3-91930674c259 | note | ○ Min >92% of MDD
2a847921-bc4c-55ee-ba71-f9fe7cfbd5aa | note | Standard / Specification - NZTA B/02 7.6
82fcedde-721f-53bb-b393-a4703ea904a2 | note | Verifying Document - IANZ Accredited Report
098882bb-07d1-5c67-9f2a-6f34c3e36ea5 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
1dec6fc1-0382-5cbe-8b6f-a1cc7e3fdb1d | note | Verification Activity: Activity - I
1e3dea94-7f3d-5b12-b985-918274ad160c | note | Verification Activity: By - SE
11f5f52e-5681-4508-8566-1ff68828d2c1 | checkpoint | 4.4.2 - Benkelmen Beam
25cd01df-96b7-5a7d-bd58-daf5a95e75db | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane. Unbound layer.
6554958c-26b0-5c81-91a6-31b28f5488a0 | note | Acceptance / Conformance Criteria - 90th Percetile: 2.43mm
d6be88d7-21e4-56d1-bd8b-2151dfae5e48 | note | ○ Maximum: 2.9mm
d493d0bc-b68e-580b-aa69-5c13f24e9c3d | note | Standard / Specification - PS 20.14.5, NTC0160
1871db32-e221-5f53-8c6c-755b8593c002 | note | Verifying Document - IANZ Accredited Report
3e912a8a-f7e5-5ebb-ae88-fabe6a67c1c5 | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
a857019d-9340-5c08-9daf-1792e70d307b | note | Verification Activity: Activity - HP
dbba3f50-f2fc-58e3-97e7-18e16a948bee | note | Verification Activity: By - ENG
b00d6f4a-d5b5-42ad-be81-c0f9188e3db7 | signoff | AUTHORITY HOLDPOINT
7f714426-2f7b-568b-bd6a-870227ac8b5a | section | SECTION 5 – CEMENT STABILISED SUBBASE LAYER CONSTRUCTION
f23d3bcf-da57-5faa-8a63-954c685b2a11 | checkpoint | 5.1.1 - Plateau Density Test
cc5f710f-c4ed-5c9b-a3be-990e22dfa28f | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
bf533fd2-ad71-5e44-9c36-a61901c633a6 | note | Acceptance / Conformance Criteria - Plateau Density Report
2fce7f8d-8a25-52b9-b95f-e0f6009718de | note | Standard / Specification - NZTA B/06 7.6
46f34ce2-7eab-5e4e-9b00-7899202a71eb | note | Verifying Document - IANZ Accredited Report
12413265-7538-57d2-9e63-9a00e79dce81 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
3af0906a-5adf-5b4d-a703-94ce4401a938 | note | Verification Activity: Activity - I
dd208442-5db2-5e6f-b924-5361162f923a | note | Verification Activity: By - SE
519755ef-020c-5639-a123-8278fec8211a | checkpoint | 5.2.1 - Mat Test
3af287c4-0c7b-586e-a188-04e717f43c63 | note | Detail - 1m2 Canvas - used to check the 24kg (as per Lab Report) of cement being used per m2
15827eea-b40a-53f9-8d61-1dc6fbcc0bf9 | note | Acceptance / Conformance Criteria - Visual inspection, check sheet
3b271596-991e-50f5-adac-4db47c83bc17 | note | Standard / Specification - NZTA B/06 7.3
021e202a-7448-56a9-832d-5154ae51f643 | note | Verifying Document - Stabilisation Check Sheet
1299122d-27ff-5fc0-9414-bd10351d8c12 | note | Testing Quantity Required (based from schedule qtys) - Every 400m2
1ae9d442-98d0-5a35-811f-6e73fd734ab1 | note | Verification Activity: Activity - I
66a8b26d-f02d-5534-82ae-2069436fc603 | note | Verification Activity: By - SE
216475f9-90fc-539b-a7f1-2cbd864aa2f9 | checkpoint | 5.3.1 - 3m Straight Edge
2799ccef-e235-5fef-acb3-02f0188c0289 | note | Detail - Formation check to ensure surface is smooth
e663fc4b-5283-54b5-baa3-8def825e970d | note | Acceptance / Conformance Criteria - +/- 10mm
4355a172-055c-56ae-b53a-eec1d136258b | note | Standard / Specification - TNZ B/2 7.7
5f278734-eb6f-5a9c-a5dd-7d6b03cdc8ea | note | Verifying Document - Check Sheet
a17d7473-6bc7-5453-b39d-c60b35032160 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
13a51fcf-8054-552f-bb6c-05308400b6b0 | note | Verification Activity: Activity - I
342a1c0a-fc4e-5caf-b169-bd55eb9de0b7 | note | Verification Activity: By - SE
bae58215-8e95-53f1-a9bb-6b791787c1cb | checkpoint | 5.4.1 - Stringlines or equivalent
44d49f23-c3f2-58b5-b0d0-821852551e99 | note | Detail - Stringlines or equivalent to check finished height of surface
ce5b35be-82e1-5799-8ac9-d045425e8399 | note | Acceptance / Conformance Criteria - -15mm + 0mm
e248cf33-c919-5c6b-9dc4-29eb13a53c94 | note | Standard / Specification - NZTA B/06 8.2.2
970703c8-ef3c-5d54-8639-053c64ddeb76 | note | Verifying Document - Check Sheet
082f348d-cbc0-55ae-949e-0258d86692e7 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres, 1 set = 5 tests
27f78099-aac1-563c-a55e-9e8172fdee3c | note | Verification Activity: Activity - I
1e03d02a-991e-549b-a9f7-8e740b9b36ee | note | Verification Activity: By - SE
f640c8ea-d18b-5d5e-b3e4-62ed7ea38a47 | checkpoint | 5.5.1 - Compaction - NDM
b5c1649b-be4b-5e88-9bd7-a9b789892514 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
35590d4f-df2c-5301-8a1c-333294b4fe3f | note | Acceptance / Conformance Criteria - Ave >95% of MDD
3be65a71-19ee-5288-aeb9-d3e145807af7 | note | ○ Min >92% of MDD
29e0cac3-6215-5876-9ee9-729d7a1541a9 | note | Standard / Specification - NZTA B/06 8.1
1b527a3e-999d-5791-bfeb-2d7d1ee56548 | note | Verifying Document - IANZ Accredited Report
15699b62-4a02-5811-a39c-2dba1a235dab | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
df5faff6-3ef6-5c5d-a445-64da9f246d62 | note | Verification Activity: Activity - I
c55b1a8c-9950-5b09-b5da-294eebac1360 | note | Verification Activity: By - SE
63167d57-bcbc-581f-8f9c-e3d4369162fb | checkpoint | 5.6.1 - Curing of Stabilised Surface
5fbe1084-a0c0-584a-b744-289e95a14bc0 | note | Detail - No traffic allowed on stabilised surface for 7 days unless approved by Engineer
4bb833fe-c737-50ea-aade-317352e5de71 | note | Acceptance / Conformance Criteria - Stabilisation Check Sheet
66749a5e-75d2-5be7-a277-4e7c57ed56a5 | note | Standard / Specification - NZTA B/06 7.8
5fb8d73b-2c34-5068-bc56-b9c2b4d6b5e2 | note | Verifying Document - Stabilisation Check Sheet
82c9d842-3f9f-524e-9214-e457c7b4eb2d | note | Testing Quantity Required (based from schedule qtys) - Upon Completion of 7 day period
fbdf4a58-a344-562c-9f10-5ed969d8bfd0 | note | Verification Activity: Activity - I
3c4a46cc-cdac-55f1-b0a5-994f7af0dfe3 | note | Verification Activity: By - SE
19525c46-c718-58f4-85f9-e34ae46fdf46 | checkpoint | 5.7.1 - Benkelmen Beam
98786ce2-9ffe-55bf-88e6-8d370dff77d5 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
948c2021-2367-5312-96ec-6df9102a7a29 | note | ○ Unbound layer.
95b04bd6-2c3a-5290-99c3-7ce0ca1fe8dd | note | ○ Cemeneted Layer.
17bf2a14-2bb1-59bd-a0f2-015eabcdfd64 | note | Acceptance / Conformance Criteria - 90th Percentile: 1.03mm
04e51b7d-2d03-52eb-b179-1ca4f280d344 | note | ○ Maximum: 1.19mm
f52601d8-0668-549f-a046-fce27556bf31 | note | Standard / Specification - PS 20.14.5, NTC0160
972b4f4e-816c-5b56-b816-0455d7fa1036 | note | Verifying Document - Test Report
c603ed99-a2cf-5b91-b478-1f9022478da4 | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
7e0782e8-31b9-5c50-94d1-65083b32ce10 | note | Verification Activity: Activity - HP
bba8f27a-aaf8-5ac6-954b-6be5ef86e47d | note | Verification Activity: By - ENG
975a7f97-1e87-4e17-84ed-4b306dfa317b | signoff | AUTHORITY HOLDPOINT
f9cf37be-9207-5ed8-87eb-d126d9905e66 | checkpoint | 5.8.1 - Unconfined Compressive Strength with 5% cement
2ca3865f-8469-5707-9ac3-df7f8170c999 | note | Detail - NZS4402:1986, Test 6.3.1 - Unconfined Compressive Strength
b584ecb8-11fc-5350-9880-582a1f815d27 | note | Acceptance / Conformance Criteria - >5mPa
1032ea49-9f3b-5d9d-8541-1590f0406afa | note | Standard / Specification - PS 20.14.5
c6dc379a-a6fc-53d4-a0e4-5c24e738d37a | note | Verifying Document - IANZ Accredited Report
618dfbf3-99cd-50cb-aaa4-6029b352452a | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval - no less than 5 working days prior to placement of cement bound material
03b03acf-437b-562c-b9d2-d6d14956b206 | note | Verification Activity: Activity - HP
27ac9251-a399-5b62-b34f-b404ad43b2be | note | Verification Activity: By - ENG
7d5b7306-3909-57dd-b7b6-4ed4e8a45f24 | signoff | AUTHORITY HOLDPOINT
9bb2814f-26a1-4222-a180-801ad64fc39f | checkpoint | 5.8.2 - Mixed material testing (ITS)
fad6d81c-060c-5ed7-bc95-c11f5bab3fe0 | note | Detail - During mixing, the contractor shall take a pair of representative samples behind the mixing plant per lot or at a minimum of 2 pairs of representative samples per day. These samples shall be placed in a sealed plastic bag and cured for 1 hour before compacting into a mould and testing the indirect tensile strength (ITS) of the mixed material according to NZTA T/19
a754223d-8a59-55a1-84a7-37539205418f | note | Acceptance / Conformance Criteria - Report Value Only
ca1b4ece-b51c-587c-9a86-b1930426b06e | note | Standard / Specification - TNZ B6 7.5
d6148c98-e436-5b68-94ba-486f4ad8be09 | note | Verifying Document - IANZ Report
27e9dba3-171e-5cb7-9b71-fff9415fd15e | note | Testing Quantity Required (based from schedule qtys) - While Construction
7a5b71f3-6362-557b-a320-a57ac9f29391 | note | Verification Activity: Activity - HP
f99f322d-bb1c-5ae3-9070-ecf56985cf31 | note | Verification Activity: By - ENG
e7ec50d1-43ff-4bee-8b3d-2ee1bb7076c8 | signoff | AUTHORITY HOLDPOINT
1086364d-de9f-4ac8-a4fc-f3741dd8925e | checkpoint | 5.8.3 - Pre-cracking
bd277821-4e60-534a-af56-4b6079e0afdc | note | Detail - Pre-cracking of the cement-bound sub-base layer, shall be done between 24 and 48 hours after stabilisation is completed.
1a7abf99-2426-57e0-942a-84537035eaa7 | note | Acceptance / Conformance Criteria - shall be done between 24 and 48 hours after stabilisation is completed.
1d91d225-6df6-5cfe-8092-e69de92fc94e | note | Standard / Specification - TNZ B6 - 7.7
d44b88ae-c9a9-516d-8857-cc5ee87d7bad | note | Verifying Document - Visual Inspection
6f825cef-a40d-54ae-9386-2b0099444af3 | note | Testing Quantity Required (based from schedule qtys) - Across Cemented Bound Area
9b573b27-11d6-5326-b057-797c6ad8c08b | note | Verification Activity: Activity - I
b185f731-2159-5a96-ab43-89585b076ff3 | note | Verification Activity: By - SE
4f8a2be1-d186-573d-bbb7-0edff722e943 | checkpoint | 5.9.1 - QA Submission
c7436c11-9247-58a0-bac8-909fc8ff6be8 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
c4d0bcd4-7fa6-574e-874f-1f829aa06ed3 | note | Acceptance / Conformance Criteria - Engineers Approval
f367719d-e9d2-5282-9348-90f09ad25558 | note | Standard / Specification - Appendix V
2985bb19-e111-50ef-a961-2171be9903d1 | note | Verifying Document - All test reports
94ac8523-73aa-5f65-9057-2ced3838246b | note | ○ Material Test Results
6d34ef49-8448-5167-8d0f-06abff7e5028 | note | ○ Laboratory MDD
6d4206ec-6b89-52f1-b760-425c0526f5ac | note | ○ NDM results
f70053d0-1d53-564f-a20d-c339b393d893 | note | ○ Proof Roll
f2b7406e-53c6-5be4-9d24-5b6dbdb8fba7 | note | Verification Activity: Activity - HP
149cacc9-267e-5394-844d-7935b6f0b5b9 | note | Verification Activity: By - ENG
ea68ee32-4883-5055-b88e-cf365d2c5f26 | signoff | AUTHORITY HOLDPOINT
40980c22-697d-5bb0-a7ce-88d236624533 | section | SECTION 6 – KERB & CHANNEL PREPARATION
971e81ae-83b7-5da5-9a8c-d1c45890d09c | checkpoint | 6.1.1 - Stringlines or equivalent
e434b038-c141-5b69-aebd-40202139aab9 | note | Detail - Stringlines or equivalent to check height of surface prep
22c94c73-b0a3-5538-aef5-c2fe4f083604 | note | Acceptance / Conformance Criteria - +/-5mm
146ad516-7797-53a1-800b-9347e3983730 | note | Standard / Specification - PS 21.7.6
a7a88b91-5951-56fe-950e-4a564ada05d3 | note | Verifying Document - Check Sheet
59d095d5-2a76-58e1-862f-b96dbc923f35 | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
e46f6082-5b25-5281-aa3c-4b7798fc5f3f | note | Verification Activity: Activity - I
c9cef1eb-dbb6-52c4-8bf7-10608beb25c4 | note | Verification Activity: By - SE
36a35987-56f2-51a2-91ba-2c48bca739e3 | checkpoint | 6.2.1 - Compaction - Clegg Hammer
2da0abb8-7532-5883-8118-c393b6210192 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
f9c39ecb-88f6-5212-80c8-d7e740978c92 | note | Acceptance / Conformance Criteria - Min 25 CIV
6a9ce316-74c2-53b2-8ab9-7f765fa20e5a | note | Verifying Document - Clegg Hammer Report
df84fd3c-b7b7-5cfa-8d83-2f99a08c0767 | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
e9f96654-48b4-5451-8db0-3f0bc5ed9838 | note | Verification Activity: Activity - I
d387a782-cdb6-5763-bcce-033e6da78dc6 | note | Verification Activity: By - SE
36d029d6-34c9-5e91-93ce-791ffd26d7f9 | section | SECTION 7 – AS-BUILTS / REDPEN MARKUPS
baf9c479-b65c-5f5e-8f66-06d9120fccaa | checkpoint | 7.1 - As-Builts/ Red pen markup
aa35aae9-176d-573f-b665-da8ffde9a384 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
5eebddc1-bf5c-5f87-86af-aef3f1c4277b | note | Standard / Specification - PS 16.7.6
2be5ae1b-3798-55e6-968d-a05a7b72df3c | note | Verifying Document - Red pen markups
9eb681da-1c5a-530c-9e7c-d2d2f2b0f1e4 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
4cde1caf-95ab-56e6-99dc-e56d010d1a4c | note | Verification Activity: Activity - D
c9f0b89c-0c96-5411-b2c7-e49674f8054a | note | Verification Activity: By - SV
48312c0b-12e8-475f-baaf-3e3a6966058e | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
de6a491f-cde9-5c0a-bbb5-ddc66b5c7d95 | textbox | Contractor's Rep Name:
3e19eb86-f2c5-5e8e-8950-02c84fbe801d | textbox | Engineer's Rep. Name:
4342eb16-d77a-5109-a6c5-cd6f688b255a | date | Date:
a78d5e74-8a28-4923-9a07-3a7b3e770186 | signoff | Add Signature
6243490f-d892-46aa-843b-26d9afc1ebd0 | checklist | DN1210-007 ITP Stormwater Rev 2 | itp | DN1210-007 ITP Stormwater
91860b7d-86d2-48ee-9c77-824ab1a122f1 | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
1f6c1f36-7222-440e-a6b4-7fc08f4b5cdc | checkpoint | 3.1.1 - Extent of Line Setout
b1a391bc-23f1-5b3e-8c1f-34f15a4a2391 | note | Detail - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Stormwater drawings.
bfcab93e-1083-553f-aa58-675da1c66e73 | note | ○ Identify any clashes before construction.
c14f79d6-153d-52c4-a524-1618ebdc3e9f | note | Acceptance / Conformance Criteria - Engineers Approval
5107d41a-677c-5c57-b7f9-0ec34ee92b9a | note | Standard / Specification - Design Drawings
c531b7f7-dc3e-5eb4-a011-2c1afa646db8 | note | Verifying Document - ITP Sign Off
fb6c5809-d401-5ae3-8042-0d0bf01bad6c | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
e52f5cc9-5d66-5b1c-ac9c-aa86d5114640 | note | Verification Activity: Activity - M
8cbbdee6-b963-5eac-976d-9e9ff081082b | note | Verification Activity: By - PE
056ca988-be0f-4f41-8200-5825e3e71bef | checkpoint | 3.1.2 - Existing Stormwater system
7044ecbe-1906-5e3f-8390-362b9d746fe3 | note | Detail - Confirmation of existing stormwater network.
5ff3c6e4-99b0-5d1c-a005-cef1368cc99b | note | Acceptance / Conformance Criteria - Survey Informations
5bbea793-81da-5af6-a158-26540450df8a | note | Standard / Specification - Appendix V
2c25ee65-73ea-5ef0-96af-9eb559a5c903 | note | Verifying Document - Survey data
b6a3eda1-2dd2-5fc1-b8d7-6ce33c34645d | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction, Review existing service location drawing supplied by WSP.
2142e384-9baa-5d79-a83a-4b929ace6a12 | note | Verification Activity: Activity - HP
1c2c3361-4ad6-5490-97d6-d8f32d01eea4 | note | Verification Activity: By - ENG
697dc2d1-47ff-4803-b196-dd6b526c8e62 | signoff | AUTHORITY HOLDPOINT
e7371e0d-fec1-421c-81ac-578b9c466fbc | section | SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
e9284dd5-bba8-4c92-b08a-447286020382 | checkpoint | 4.1.1 - Material grading: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
e27b62e6-b471-502c-9e9a-4f48ae2cdf99 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
9f7bb193-9944-5884-bce0-0fda33845f0a | note | Acceptance / Conformance Criteria - Stockpile size 1500 to 4000m3.
ce3abfce-f80e-5d28-9b42-093ad8251f85 | note | ○ PS- Table 21.2 for GAP/AP20
b5361b24-9c14-5764-9de0-57900729d29f | note | ○ PS- Table 20.3 for Overlay and Embedment Zone Material
597d0917-6e63-5169-a97e-fca4cff24118 | note | ○ NZTA F/6 for Drainage Aggregate- Grading section 2.2
6a0b6b30-aaf4-5037-9ffb-6caeb087fa4b | note | Standard / Specification - PS-21.7.2
04a4297b-a890-5f20-93ab-4d62531a060a | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
093e689a-41fc-5da6-a254-8d4301d116a3 | note | Testing Quantity Required (based from schedule qtys) - 4 Test, 1 Test for each additional 1000m3
f71fd95f-6cdf-54c5-91ce-14e134ecf047 | note | Verification Activity: Activity - HP
8edebdb2-063b-583d-a1a5-38fb883dda86 | note | Verification Activity: By - ENG
280bd6c4-105b-4c65-9656-41490a58bebb | signoff | AUTHORITY HOLDPOINT
1b35046e-6844-43d1-81ae-4f8fd14a1e95 | checkpoint | 4.1.2 - Weathering index: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
9b275664-8a31-5408-b105-410be9151b14 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
89b77a7b-40e5-5786-ae3a-85b8c9b800b6 | note | Acceptance / Conformance Criteria - Engineers Approval AA to CA
2f7fb771-d701-5103-aa6d-467e1018d6f7 | note | Standard / Specification - PS-21.7.2
a0e0f6a4-37ac-51e4-81be-5f7130dcba60 | note | Verifying Document - Lab Test Report NZS 4407.3.11
f549971b-050b-5288-a261-5d22085353d9 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
73824006-a048-5b53-a964-c6ba88d6ab3a | note | Verification Activity: Activity - HP
9c1a39d6-fb89-5e53-a511-2e9c9a0e38e2 | note | Verification Activity: By - ENG
741786d6-1780-42a8-a7ef-e6436f9fb5cb | signoff | AUTHORITY HOLDPOINT
adb98c65-97d4-479f-9519-8aa63f9cc880 | checkpoint | 4.1.3 - Crushing Resistance: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
d671f15b-283e-544f-b42f-b5ed43b19a64 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
4c459540-042a-57df-90c4-08a92d5d9166 | note | Acceptance / Conformance Criteria - Engineers Approval >100kN
c150f69f-5ddf-5713-bbf2-fffa2a639d72 | note | Standard / Specification - PS-21.7.2
72f40ae5-5c5d-5a7e-a4a4-9447db4d1e82 | note | Verifying Document - Lab Test Report NZS 4407.3.10
c4e8a32f-471e-5c1e-88fd-ebb110bd1b80 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
2159791e-0e1b-5e69-bb02-22d334a71b02 | note | Verification Activity: Activity - HP
236bdb74-79df-5449-9644-d8ba588e9dda | note | Verification Activity: By - ENG
e54376e3-e08f-4aaa-8edd-9b95e90371d4 | signoff | AUTHORITY HOLDPOINT
80629f28-d759-470e-871d-9cea6c1c39b3 | checkpoint | 4.1.4 - Geotextile/Geogrid
bec0236a-ba31-5f7e-979e-ab2bbd86cf6f | note | Detail - Minimum Strength Class C & Filter Class 1 or TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
29df9062-f649-504a-9fb9-3ce97e6cee9d | note | Acceptance / Conformance Criteria - Engineers Site Representative to inspect trench.
54f560bf-c5e0-539d-8d43-198b63b6104e | note | Standard / Specification - PS-16.5.7
48659beb-2f80-569b-b1e6-6cf9c1ec67f8 | note | Verifying Document - Certification
f42d7a93-2f5d-54a8-aef5-a032ad5f8a76 | note | Testing Quantity Required (based from schedule qtys) - 1 time
268010f9-5d30-549c-9e0c-4775fe004646 | note | Verification Activity: Activity - HP
eeba243b-94bc-5b0f-a4df-824b7f8530b1 | note | Verification Activity: By - ENG
084d2d1f-df8d-4799-bb96-1d869c7aa312 | signoff | AUTHORITY HOLDPOINT
6270d6f9-1bc1-46d4-b9c6-67da0183ac82 | checkpoint | 4.2.1 - Riprap test Criteria
8ccf0812-6c3d-5340-b1ee-f9a35558a705 | note | Detail - Weathering Index of Coarse Aggregate.
f6337c0c-701d-5060-849f-9a9f84ade06a | note | Acceptance / Conformance Criteria - Engineers Approval AA to CA
3a402864-a740-5a78-a9a7-0818bdf11e82 | note | Standard / Specification - PS-21.7.4
c536e9cc-8fc1-51d0-b86b-ff762a485a89 | note | Verifying Document - Lab Test Report NZS4407.3.11
243b5a98-b129-51d1-98e9-6587f911fdf3 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
e73b0ddb-03d7-509b-bd4c-afdae136dd34 | note | Verification Activity: Activity - HP
a1ebfaf0-97ac-547b-bc08-e6e7138f5758 | note | Verification Activity: By - ENG
14bae06f-ee8e-4945-9366-4abca3f9e414 | signoff | AUTHORITY HOLDPOINT
345bfac6-93dd-4267-b149-49604dbf8a30 | checkpoint | 4.2.2 - Riprap test Criteria
040916f6-b308-5f1a-a4dc-59b5db1ef0a4 | note | Detail - Crushing Resistance of Course Aggregate.
16477e47-be25-5770-8ff1-1b5571ef9a7f | note | Acceptance / Conformance Criteria - Engineers Approval > 150kN
685517be-9ed1-5e15-9438-6469ca585344 | note | Standard / Specification - PS-21.7.4
4867b192-57f5-5062-a5aa-0681982cd686 | note | Verifying Document - Lab Test Report NZS4407.3.10
0b3d8f16-f6b5-55c1-aa57-739a11853713 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
c777e1d0-3092-53d3-b40b-12dabe8ddf14 | note | Verification Activity: Activity - HP
e0360f02-aab4-5e91-b1e5-00c8e24e73bd | note | Verification Activity: By - ENG
5de6aaa1-9287-4a7c-b04a-f6f88912f8e9 | signoff | AUTHORITY HOLDPOINT
8c547b6c-2905-4947-812b-1ff4752a0ceb | checkpoint | 4.2.3 - Riprap test Criteria
67c801b2-a55c-5466-8e05-8c37212bf528 | note | Detail - Solid Density of Aggregate.
475cf24b-acf1-51d0-8be6-3ff39ebbfbd0 | note | Acceptance / Conformance Criteria - Engineers Approval ≥ 2.65 tonnes per m3
080054e4-d137-5b71-b8e8-6efc764c95eb | note | Standard / Specification - PS-21.7.4
8e13dadd-c34b-5e63-9a0a-464e99ed3afd | note | Verifying Document - Lab Test Report NZS4407.3.7.1
ab97d2e1-e4de-5112-8810-c960169d2fca | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
34dd8818-bc35-5873-aa3f-b02d2ba18a13 | note | Verification Activity: Activity - HP
028ee2fa-0193-5a7a-8ea1-45e655708cf7 | note | Verification Activity: By - ENG
3e079b06-5bec-4229-954a-b6288ff8c4f5 | signoff | AUTHORITY HOLDPOINT
93c4e992-b6de-43f0-9af4-126fb357e6aa | checkpoint | 4.2.4 - Riprap test Criteria
c8837801-e9ee-52e1-ae82-5c20ffee56c6 | note | Detail - Grading of the material.
5d6c2815-58d7-519e-8526-22cb3a88be8e | note | Acceptance / Conformance Criteria - D=50 150mm Riprap Grading
038b4949-3785-5ff2-bb79-af257d2a8296 | note | ○ Aperture Size - 230mm
13cebb69-5df6-50c2-9b57-a3aaa3222aa3 | note | ○ Aperture Size - 150mm
9be29026-a58b-516a-9e75-cd4e6e2bb8d2 | note | ○ Aperture Size - 95mm
fe8d7e1b-1bf0-5280-b916-6fcf7fd138e7 | note | Standard / Specification - PS-21.7.4, PS-21.5.14 Table 21.3
bfc9fa3b-fea6-518f-9656-11d6549f8e83 | note | Verifying Document - Lab Test Report NZS4407.3.8.2
ae7f9e73-9b6e-5755-8a59-8dfa1b18773e | note | Testing Quantity Required (based from schedule qtys) - Percentage passing - 85
5646ac1f-19a1-57aa-bd2c-de21197ef3fc | note | ○ Percentage passing - 50
5c85a3c6-4a91-516a-b9ec-479e44eac365 | note | ○ Percentage passing - 15
ead4cbbc-3053-5f7c-900e-fa29c4e06610 | note | Verification Activity: Activity - HP
fc4517a8-82d9-53f4-87b4-7834671f16b0 | note | Verification Activity: By - ENG
a1053f26-396c-4326-8598-0eae4b677f62 | signoff | AUTHORITY HOLDPOINT
4a293944-6aef-44bf-a74a-2e876288433e | checkpoint | 4.2.5 - Riprap test Criteria
2776a8ea-c4b0-514f-aba4-aa53e5d94f4f | note | Detail - Point Load Strength.
0ac28da7-063c-5ea5-9281-29a75181e4f0 | note | Acceptance / Conformance Criteria - Engineers Approval >1.5 Mpa
6494bfd6-677e-5b72-9de1-487ca484c0a6 | note | Standard / Specification - PS-21.7.4
5ad4c8d6-bfd9-5a12-b11a-fd0a9449e66f | note | Verifying Document - Lab Test Report ASTM D5731
d14763bb-9aeb-553b-b760-3158566047be | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
d9507a31-aaa8-54d1-a1e3-5c5746c5c9cb | note | Verification Activity: Activity - HP
06f83fcb-a792-544a-993c-4a33302168aa | note | Verification Activity: By - ENG
e7737960-c305-4e2b-87e7-de374c9127da | signoff | AUTHORITY HOLDPOINT
38db9b72-6ac4-4983-b10a-b3c5ab6270dc | checkpoint | 4.2.6 - Riprap test Criteria
8d9c7a61-5627-554d-9998-635d06ff60d1 | note | Detail - UCS Rock
b2a84eb0-83ab-543e-b2ee-b71a8239db4a | note | Acceptance / Conformance Criteria - Engineers Approval >30 Mpa
ef1eb8c9-eb39-5e63-add9-d30a334524ea | note | Standard / Specification - PS-21.7.4
abb05262-acaa-5345-9d5b-09fccebd1f3a | note | Verifying Document - Lab Test Report AS4133.4.2.1
b8f7d3f4-7d8c-51c1-9d8f-8fac1014e8d6 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
b7ad2099-d8bd-56e2-9fe4-348207881f11 | note | Verification Activity: Activity - HP
b327aeac-3264-59d5-90a0-a4ee54e16e92 | note | Verification Activity: By - ENG
0c16189f-ba41-4cf9-a542-626404a028be | signoff | AUTHORITY HOLDPOINT
53c2e517-1c45-45a9-8328-a0c8790c514c | checkpoint | 4.3.1 - Pipe and fittings (uPVC SN16, PVC, PP, PE and Concrete pipe).
7c40070b-e16e-595c-8910-0077dc9e9b6e | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
5142f3e7-ef4e-561f-8020-2a1af27708f9 | note | Acceptance / Conformance Criteria - Site Engineer Approval
a221d819-f365-5d3c-ad03-d42ce482d2bc | note | Standard / Specification - PS- 21.5.1
08692960-22ea-55bb-a65b-7553066efe8b | note | ○ PS- 21.5.2
db33b970-59b3-55ef-8f1b-75f6e4be8b57 | note | ○ PS- 21.5.3
c9b904e5-89ed-546e-8bc1-c91c1f79e13f | note | Verifying Document - Delivery Dockets
aad5bf3f-2ce4-5609-af67-97511325dc48 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
6cd35658-cd9f-5af2-a390-015c65d0e8fb | note | Verification Activity: Activity - H
188e3d5f-f879-5599-b931-b9755cf99a45 | note | Verification Activity: By - SE
54cdc9d4-8de6-46ae-9ee2-203d80ec31e8 | checkpoint | 4.3.2 - Stormwater - Structure (SWMH, SDMH, GMH, CP, DCP, CPMH, MP, HW)
9becf11e-7fd8-541b-9179-56bc2b8cb781 | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the Structure are correct and in good condition.
ff5beef0-4865-5c1a-aa08-117091a06811 | note | Acceptance / Conformance Criteria - Site Engineer Approval
6ff91433-ce68-5d2a-a792-f0e57fabc02e | note | Standard / Specification - PS- 21.5.4, NZS 3109:1997
bcedf3cd-4427-5942-8084-06925a340df6 | note | Verifying Document - Delivery Dockets
5805cdc6-7e31-5966-bcdf-be4b7620b11a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
8b4eef2c-ca8b-587b-9753-ccd15e142d75 | note | Verification Activity: Activity - H
7010832a-d7b2-53b0-ad57-ef0c7ace03a7 | note | Verification Activity: By - SE
a4831a83-4278-4537-b516-6e5e4fad1517 | checkpoint | 4.3.3 - Granular Material (GAP20/AP20, GAP65/AP65/LRAP65/Riprap and Drainage aggregate)
6a4b6710-62ee-5367-9e38-ce9f313346a7 | note | Detail - Confirm Specification and material in good condition.
c523fa49-09ee-5b63-838f-b83e106524bd | note | Acceptance / Conformance Criteria - Site Engineer Approval
2bd3323b-a687-53d6-a07d-5fae8262fa23 | note | Standard / Specification - PS-21.7.2
29019a12-abac-5a5d-9cc4-3d9d1c6c37be | note | Verifying Document - Delivery Dockets
12d85ec9-87b8-527a-8951-3db01addef3b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
df1d08ed-1e50-5c31-b4ea-63f3614983d0 | note | Verification Activity: Activity - H
c04dad5e-1a2f-5aba-9141-7169dbbc768e | note | Verification Activity: By - SE
172c7da1-98ab-4481-beca-fe0644c30e72 | checkpoint | 4.3.4 - Geotextile/Geogrid
e7188d46-b163-58e5-a706-c086dd4b12d1 | note | Detail - Minimum Strength Class C, Filtration Class 1.
2feef71e-a1bd-516a-88c6-a85de0d7e3a2 | note | Acceptance / Conformance Criteria - Site Engineer Approval
63e9893d-e5f2-59be-9d12-2cfb7c0713be | note | Standard / Specification - PS-21.7.3
e4663b64-b657-5ee6-b775-06924df43c21 | note | Verifying Document - Delivery Dockets
debcb283-aa1c-56fa-8e2d-7a4c8f145be3 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d7fd3967-9b04-5a42-a224-7fe6e5fa6f6b | note | Verification Activity: Activity - H
bc1dcd2f-86d4-5fd1-b9fa-7473b56fe35e | note | Verification Activity: By - SE
421af29f-f053-4515-b5e2-7f390ce810d9 | section | SECTION 5 – CONSTRUCTION ACTIVITY
d541f2b5-b5a9-4fe2-88f3-1c8f7a51b068 | checkpoint | 5.1.1 - Foundation Compliance
f2d70fdd-79e5-5a85-bac6-ab438541621d | note | Detail - On Granular or Cohesive Material
9f50823c-e84c-5c28-8e0d-66e1fa1c86a4 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
cb01c880-d065-5e79-94a1-6c60063b859c | note | ○ Cohesive Material: Vane Shear Strength 70kPa
20ce7916-ef70-57c3-983b-6473c3a43e5d | note | Standard / Specification - PS- 21.7.2 Appendix V
22a42a2a-e8e6-5009-8575-15c392f726b6 | note | Verifying Document - Scala/Shear test result
7b284cdb-aea1-5346-9857-45fe6b2aab53 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
b8f2a61f-f206-54d0-9233-26d6b80ba7c5 | note | Verification Activity: Activity - W
eddc97d9-50fe-54af-aa5e-603fd83f5a74 | note | Verification Activity: By - SE
3ec4d9ce-53f0-425b-9686-577cb82b9668 | checkpoint | 5.1.2 - Undercut approval
74156dba-0cd8-5e12-adf7-5fcda94d2351 | note | Detail - On Subgrade
d4c0c93a-7f91-5aec-8616-03692169f63f | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
be44bf7b-8dc8-55bf-aeb0-bf413b9be237 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
7d52afc8-5fb0-506b-a353-d6456ffc1514 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
83856250-a797-532a-b997-cc3a681c2d5e | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11, AS/NZS 2566.2/2002
40f29e64-722e-5578-8dea-eefac7b839d5 | note | Verifying Document - Lab Test Report
700cd3d5-f704-5aa3-807a-24db0cfd3e38 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
08d19d19-9285-54c7-b141-ab7b28297f41 | note | Verification Activity: Activity - H
d609c58e-b521-54e5-8c35-4c9bc709b9e8 | note | Verification Activity: By - SE
c02e771d-a368-4980-8005-cefcfc249f39 | checkpoint | 5.1.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
6b0a53e6-2522-535d-806b-b5652c787508 | note | Detail - On Granular Material
18a480e9-b095-5918-9d71-b89ff455ea83 | note | Acceptance / Conformance Criteria - Clegg Reading >10 CIV for non-trafficable areas
0653a80b-7c43-5f4f-8ba4-73f24080d9f9 | note | ○ Clegg Reading >25 CIV for trafficable areas
ee3e13dd-0d07-5cae-9958-18cd93864821 | note | Standard / Specification - PS- 16.5.12 Table 21.12
f23fc7bc-306c-56b6-afd3-9267df87538e | note | Verifying Document - Lab Test Report
380e0df7-8c08-5065-afd7-861e8744c44a | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
07b4536a-1768-5700-a55b-cd887fe35bf0 | note | Verification Activity: Activity - H
e04ed112-5552-57b2-9049-410ead2d139b | note | Verification Activity: By - SE
ce414afa-6795-4ec0-af11-26b305604d08 | checkpoint | 5.1.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
c72b6448-4e65-5739-acc7-2905607baeab | note | Detail - On Granular Material
08333a38-4564-57d2-9ece-236b3449db08 | note | Acceptance / Conformance Criteria - Clegg Reading >10 CIV for non-trafficable areas
10d55a8f-ebcf-5b89-96b6-b58ee35bb7be | note | ○ Clegg Reading >25 CIV for trafficable areas
c6baf4d3-368b-5654-9bc5-0fe95c0a45e6 | note | Standard / Specification - PS- 16.5.12 Table 21.12
70f4e652-1187-52c9-abdf-108a1107478c | note | Verifying Document - Lab Test Report
fbf7a69f-29f6-5f15-b54d-60e8d7569542 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
dfccf01a-73c6-5afe-81e8-7b81d205dcb2 | note | Verification Activity: Activity - H
bd9c851b-0d36-5cbd-ba98-286b6c3eaceb | note | Verification Activity: By - SE
6fe324db-af45-4a87-be32-3b2fd47a3055 | checkpoint | 5.1.5 - Survey
cf61054e-359a-572c-aa44-f71f561ade1b | note | Detail - Inspection of Structure
8b6ebb1b-d6d5-5e61-a86e-a68e62cefc7b | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
5a0b442b-3ce5-58ed-9549-adfc2b018851 | note | Standard / Specification - PS- 21.7.6
50999c72-c9cd-5594-bf6b-34d8124d0385 | note | Verifying Document - Survey Data
900c5c5e-40bd-5e54-8fc0-532c389f6275 | note | Testing Quantity Required (based from schedule qtys) - Continous
61739254-0c1d-513a-8133-b9c4c2d59a72 | note | Verification Activity: Activity - H
841da375-4453-5d94-99a5-aa8d4e72f527 | note | Verification Activity: By - SV
cf31c96c-33fe-476e-a4eb-32e690a40fab | checkpoint | 5.1.6 - Backfill Compaction Testing
804c7f8a-e362-52a2-9a36-dcfb29598048 | note | Detail - On Granular or Cohesive Material
da67ee36-4dba-59a3-84fc-a15bac451e42 | note | Acceptance / Conformance Criteria - GAP20 Backfill Compacted in 200mm layers around pipe.
2b8a89c2-e03c-585a-832b-09016c400a1d | note | ○ Clegg - 12 CIV
ac105918-af32-5573-8bb6-29efadf7056c | note | ○ AP65 Backfill Compacted in 200mm layers.
b775e52c-ecf8-5067-a81a-94f8f4c1885c | note | ○ Testing to be completed on maximum 200mm lifts of backfill
c4841e26-b9fe-58aa-845d-e95872ffab01 | note | ○ Clegg - 28 CIV
24d384de-3d66-5e2a-803d-8d1e22ad78fa | note | (or)
b7f5d96f-0005-5b32-b2e5-2028a011348a | note | ○ Cohesive Material in 200mm layers.
13fb92fd-2bf0-5beb-b0e8-449ae0dcd3c0 | note | ○ Shear vane - 50Kpa
deb15747-c04a-5ca8-b9f2-14bf270680da | note | Standard / Specification - PS- 21.6.12 Appendix V
d2bb0ec4-5a08-50a4-933a-258857f93c3e | note | Verifying Document - Lab Test Report
935c61a3-c15e-5a4d-9505-712123e0132f | note | Testing Quantity Required (based from schedule qtys) - GAP20- 4 test per lift
f3aa5636-c7a2-52bb-b80d-38afa51e704b | note | ○ AP65 - 6 test per lift
3f24dd64-0ad5-5668-956b-3bf87477a56a | note | ○ Cohesive - 4 test per lift
29c61d84-33ab-5570-a631-a1aff7c32bd7 | note | Verification Activity: Activity - H
641f5d3c-86d2-5814-b064-30b2393d7ac5 | note | Verification Activity: By - SE
aef7fe80-c341-4eaf-9541-87e972190e3c | checkpoint | 5.1.7 - Pre-Backfill Inspection
615c6e57-e986-509d-9e7c-fb3ad154d1ce | note | Detail - Inspection of Structure
57d41f80-b2ef-553e-8ccc-f10ff686f059 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
e2b4f463-63a6-5183-9035-5ec0a9f6498f | note | Standard / Specification - PS- 21.6.11
5512018c-5b5f-5523-94d4-b95234143437 | note | Verifying Document - Manhole/Catchpit Record
357d37ae-0b63-5986-956f-6bb3f6c834c5 | note | Testing Quantity Required (based from schedule qtys) - Continous
986e212f-a771-5241-b6a3-1561b95d0b5d | note | Verification Activity: Activity - I
243f1ed2-9ff3-50df-b236-51a79275294c | note | Verification Activity: By - SE
bad54fe7-87c2-4a86-b60a-cf897cf4a155 | checkpoint | 6.2.1 - Foundation Compliance
4551bbd2-3797-56fd-8b11-e221d79fbacc | note | Detail - On Granular or Cohesive Material
94ec64d7-6585-5c71-9d76-4805a9a6604b | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
97a49ee6-d96d-588e-b581-f928a76abfd5 | note | ○ Cohesive Material: Vane Shear Strength 70kPa
5c58a11e-cfbc-51a3-b9d1-d4551b84bd57 | note | Standard / Specification - PS- 21.7.2 Appendix V
8cbee485-fddd-5a98-933a-018987e99d27 | note | Verifying Document - Scala/Shear test result
707472ed-5f24-54b1-99dc-ee6ad5d26112 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
706329ef-1b0a-5ee2-9b8f-dcee7c2a1d7d | note | Verification Activity: Activity - W
e8082687-5b31-5657-a7d2-8f6cfad41308 | note | Verification Activity: By - SE
e69e3069-b18e-4168-8a70-d969c90fbb00 | checkpoint | 6.2.2 - Undercut approval
3ff2d350-aeea-515a-88c9-46430a5914c4 | note | Detail - On Subgrade
9844a34c-509d-5baf-9a66-1ce340a20e83 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
7a9b53e3-b781-5ac7-b8b0-96f1e4063d81 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
d1729efe-8c6a-5468-b751-ddc7b0dd85b1 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
521be026-cc38-5724-bb6c-fcb18e338448 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11, AS/NZS 2566.2/2002
137d7323-5a6f-5f54-9cab-b7ebd6bcd62d | note | Verifying Document - Lab Test Report
6790be82-584f-5d44-8418-846e8e51d406 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
63a9af3d-a20f-5130-b37b-233b2190a506 | note | Verification Activity: Activity - H
5bae103f-9d02-52cb-8199-2121430c56e5 | note | Verification Activity: By - SE
0e5d623c-6721-49be-9b51-82750e7d1ffb | checkpoint | 6.2.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
1e06a325-afb4-5564-b229-35817cf1a955 | note | Detail - On Granular Material
c39b4638-46eb-5054-8a92-677669554f79 | note | Acceptance / Conformance Criteria - Clegg Reading >10 for non-trafficable areas
9c68ec11-af7d-53f2-90c4-b85370d8ed4c | note | ○ Clegg Reading >25 for trafficable areas
95d83a8e-c2c1-5c9c-aa42-376402f6f3b1 | note | Standard / Specification - PS- 16.5.12 Table 21.12
a12d0602-04cd-5fa5-bd07-33cd32edaaf8 | note | Verifying Document - Lab Test Report
c8845d01-70af-5bf8-9dd0-117339f1b1eb | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
e2af8eb8-a92b-5ab8-9ac6-85b642de6048 | note | Verification Activity: Activity - H
d1f7079c-d27f-5dc5-8f33-0227cd62ffef | note | Verification Activity: By - SE
1106d108-40f4-4efa-8fc0-ff41449ff9da | checkpoint | 6.2.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
b1a083e8-570f-58f7-a162-0e1330cdb2b3 | note | Detail - On Granular Material
585c15dc-84c0-5662-91c3-3879f6bba0fc | note | Acceptance / Conformance Criteria - Clegg Reading >10 for non-trafficable areas
1a0fda56-5554-5443-8754-4142230024cd | note | ○ Clegg Reading >25 for trafficable areas
0341b253-f019-5379-97d5-e3bed7e2ab2d | note | Standard / Specification - PS- 16.5.12 Table 21.12
0c21b711-e0b2-5984-9bd6-622eb2acaa7c | note | Verifying Document - Lab Test Report
9a3eb411-631d-5afb-a4c7-ab1a95071de0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
cc18570a-a35c-5f3c-8831-0c588add5855 | note | Verification Activity: Activity - H
adaed823-6d18-5a6c-b960-f29e0a215f33 | note | Verification Activity: By - SE
1ca65fc5-29a9-4b50-ad06-aac83ab4c41c | checkpoint | 6.2.5 - Survey
112a1439-3208-5d0a-959c-c4141dc8a33f | note | Detail - Inspection of Structure
7f1a7d48-fccc-5b41-8713-51426324a642 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
3df86829-a11e-5b46-801b-246927800b22 | note | Standard / Specification - PS- 21.7.6
6eeaca8c-b266-514e-a74a-5756b19aef69 | note | Verifying Document - Survey Data
5e6ae193-fa50-5b88-802d-6f019ef72eac | note | Testing Quantity Required (based from schedule qtys) - Continous
4a57cf69-dae5-5ae1-8fda-361b17488c5d | note | Verification Activity: Activity - H
3b75f9dc-64c5-52b3-aceb-bd74a961ed60 | note | Verification Activity: By - SV
e2889a69-f57b-4c7d-83ad-60afa79a7407 | checkpoint | 6.2.6 - Backfill Compaction Testing
06e05fee-b75a-56ce-9633-335f68b2fd49 | note | Detail - On Granular or Cohesive Material
7e6f8e80-4b74-53cb-9d46-dfb2b350a0e1 | note | Acceptance / Conformance Criteria - GAP20 Backfill Compacted in 200mm layers around pipe.
ef42c6b2-beab-59bc-8bed-22c24525943b | note | ○ Clegg - 12 CIV
5de568a5-e0ef-563e-b2c2-b2e4a3310a57 | note | ○ AP65 Backfill Compacted in 200mm layers.
fb8464be-2c66-54d3-bd0e-e11096cea91c | note | ○ Testing to be completed on maximum 200mm lifts of backfill
5866a065-0b63-5c60-9e3c-93a9e0fe7c93 | note | ○ Clegg - 28 CIV
ecfa5e95-694c-5844-91ba-892e86cd6abe | note | (or)
459a4b83-eb02-515b-89a2-7e780ca68e96 | note | ○ Cohesive Material in 200mm layers.
ce92555c-0b93-5e99-abf6-648f1ca23e26 | note | ○ Shear vane - 50Kpa
70d2ae16-bc9a-57fe-a62d-21b07b40c583 | note | Standard / Specification - PS- 21.6.12 Appendix V
da78984d-6744-5a23-a25b-eb6bbb714972 | note | Verifying Document - Lab Test Report
65d53e82-3468-5df9-91e1-e9ecc85ce7dd | note | Testing Quantity Required (based from schedule qtys) - GAP20- 4 test per lift
0edb9626-c610-55e8-a066-00d021c83b78 | note | ○ AP65 - 4 test per lift
7aefe565-c3a7-510e-b4e5-d545a17c3b2b | note | ○ Cohesive - 4 test per lift
6bbbedbc-9dbd-594f-8cee-1f07612e3967 | note | Verification Activity: Activity - H
574f84a7-5a37-52c0-9522-bd4f293ea1b2 | note | Verification Activity: By - SE
4d7f910d-48d7-4c09-a55c-271720dce85b | checkpoint | 6.2.7 - Pre-Backfill Inspection
8e4ebb37-a2f4-5b84-8c92-b4b13cb65529 | note | Detail - Inspection of Structure
ea13673e-41ae-508c-ab3b-57582e264f5e | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
65a9b65e-3906-516f-be4d-f5b542d45242 | note | Standard / Specification - PS- 21.6.11
eccfc0c4-7385-596b-8dbc-c2033f30600a | note | Verifying Document - Manhole/Catchpit Record
6d1a6cc5-bc52-57d3-b74e-5ed1eeb482cf | note | Testing Quantity Required (based from schedule qtys) - Continous
d655a83b-b5ca-5185-9ad0-2b73801f545e | note | Verification Activity: Activity - I
99f63f53-b368-5cce-bba4-0f9e1453c2ed | note | Verification Activity: By - SE
d1b0ec54-088b-49f5-8ec0-54fcc83c6c40 | checkpoint | 6.3.1 - Foundation Compliance
b51b89fb-b5e2-5fca-b3ff-4c6c3f152471 | note | Detail - On Granular or Cohesive Material
feb1fb45-e982-590d-807a-9d8ec477797b | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
24f397b6-aca8-599f-8765-6e7584ff5696 | note | ○ Cohesive Material: Vane Shear Strength 70kPa
95889af5-e892-5c5f-be57-c650d2b82ec5 | note | Standard / Specification - PS- 21.7.2 Appendix V
47816982-5fa9-5c9d-a3e7-137af18edfcf | note | Verifying Document - Scala/Shear test result
9d750e91-bc76-5579-a742-73154ab1c582 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
ae8251cc-0bef-5a8c-9dbf-84dcdfcc225a | note | Verification Activity: Activity - W
8611f10e-a9b1-53ed-ac86-cc2c07b401b6 | note | Verification Activity: By - SE
254960b5-f643-4c43-a385-90229fc9ce8e | checkpoint | 6.3.2 - Undercut approval
b895c055-7968-5221-9817-c02b63a57ac8 | note | Detail - On Subgrade
30ffb4de-fd77-5b26-8444-b466b1a29a99 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
a2a754ca-fbb8-5ee3-9600-006dc8b900e5 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
d30db96a-2856-5858-a6a8-e299947505cb | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
f38702a5-c43d-5532-9c6d-67e1b2a34be4 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11, AS/NZS 2566.2/2002
748e04cc-c906-5e0a-97d9-b1be1720d806 | note | Verifying Document - Lab Test Report
42096d81-117c-5c04-8da7-1f7c37903053 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
df171ac1-0e3c-5149-951d-00b03aacd600 | note | Verification Activity: Activity - H
ccd6eef5-b6e7-5558-b247-eef111c81c33 | note | Verification Activity: By - SE
6aff2683-32a7-4486-9682-280d4c248719 | checkpoint | 6.3.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
e9ef7608-f312-5b54-9d41-965160539fa1 | note | Detail - On Granular Material
4530c16a-5f4c-5041-a5e9-49c4e9960f84 | note | Acceptance / Conformance Criteria - Clegg Reading >10 CIV for non-trafficable areas
334fc72e-97ee-59e4-9dcc-7961e5b211de | note | ○ Clegg Reading >25 CIV for trafficable areas
b0849eb8-0834-532c-9cbc-caf94011b473 | note | Standard / Specification - PS- 16.5.12
59a0d915-c3af-5271-81da-278c0a2b1c11 | note | Verifying Document - Lab Test Report
640ee597-1eb4-5075-ae77-451b2e36b9bf | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
a9b3985f-c206-5497-8b69-0bdb70f57136 | note | Verification Activity: Activity - H
31670510-a9c1-58fc-99dc-30a3633d3fb0 | note | Verification Activity: By - SE
5336408a-ec33-499f-a076-f0b5e48bacd2 | checkpoint | 6.3.4 - Bedding and Embedment Zone Compaction Testing (Polypropylene(civil boss)/Polyethylene Pipe).
88782855-1ca3-5115-ac80-48ff035864e7 | note | Detail - On Granular Material
7ab8bc70-01a1-59a7-b29a-ea3dd0ee4beb | note | Acceptance / Conformance Criteria - Bedding Zone: 100mm(for DN300 & DN375) 150mm (for pipes greater than DN375)
f2bf8091-69a7-5abf-bd41-aafd0a5315aa | note | ○ Embedment Zone:
4c2a22d3-26e1-5bd3-ac99-dd9295e12502 | note | — Pipe Dia ≤450 - 150mm GAP20/AP20 - Overlay
1faa0b2e-32c8-5baf-8499-9647e8bbab19 | note | — Pipe Dia 450< D ≤900 - 150mm GAP20/AP20 - Overlay
21dc4e99-789c-53f2-8cad-891d7eac5b4b | note | — Pipe Dia 900< D ≤4000 - 150mm GAP20/AP20 - Overlay
2ea7d940-4a11-5bbd-b3b6-345d0abe06fd | note | ○ Minimum Compaction - Trafficable and Non-Trafficable Clegg Reading >12% CIV
8cc3fa7e-dee7-56ff-b558-b2b0296dd6cb | note | Standard / Specification - PS- Table 21.7, PS- Table 21.12, AS/NZS 2566.2/2002
baa913f2-44ca-5969-9d43-7d9a6746f0c9 | note | Verifying Document - Lab Test Report
bec25e13-b892-5bf9-9bd8-b1758d996fab | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipeline with aminimum of 1 test between each pit/manhole.
6b327059-76f2-5270-9989-01d15fe4e1ee | note | Verification Activity: Activity - H
f68583d7-e9fd-58c4-9683-026b24069559 | note | Verification Activity: By - SE
fecf1f8e-4dab-445a-89df-bb3ed6861e9e | checkpoint | 6.3.5 - Survey
0c925f89-4d67-5987-a04f-8b5a6a614208 | note | Detail - Surveyor to Setout
303c24df-1649-5dd5-bf94-874a8be03607 | note | Acceptance / Conformance Criteria - Vertical design Setout:
b21c4af4-f412-5274-bd5b-6909048e3795 | note | — Pipes ≤ 1% grade: +/- 10mm variance
a54a79a6-67bf-5f2e-ba79-3acef12dc7ad | note | — Pipes > 1% grade: +/- 20mm variance
5668ca63-b136-5cd5-8615-2236a841ac95 | note | ○ Horizontal design Setout: +/-30mm variance
67c5f321-93d3-5cf3-9e8a-bfcfb67a43e6 | note | Standard / Specification - PS- 21.7.6 Table 21.15
77f5caf1-f273-525b-b273-632e688b19a2 | note | Verifying Document - Survey Data
8350902f-9d0c-585c-b016-9e0c5e8700ea | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
328cc940-b9cf-59dc-8641-8c33bbf75dcf | note | Verification Activity: Activity - H
b1e56299-7df4-53d9-94ee-9795289123ab | note | Verification Activity: By - SV
8f218996-c9f0-431d-8e33-f2eab57943a1 | checkpoint | 6.3.6 - Backfill Compaction Testing
11d30ec6-8542-59fd-8535-ef704372fd76 | note | Detail - On Granular or Cohesive Material
b6daa787-db93-5bd9-9cc4-bd9846fd85fb | note | Acceptance / Conformance Criteria - AP65 Backfill Compacted in 200mm layers.
3e9c85d8-a393-51b5-9aca-82dc00e283cb | note | ○ Testing to be completed on maximum 200mm lifts of backfill
c7b22c59-2f35-5167-8f41-db897fbbdd12 | note | ○ Clegg- 28 CIV
aa75d23b-1f5e-5621-a84c-f5544729838d | note | (or)
dd94e88b-7f4a-5a01-b22c-df16c8c2e376 | note | ○ Cohesive Material in 200mm layers.
7b8ac4c5-c447-5f15-be3e-71748a7abbc7 | note | ○ Shear vane - 50Kpa
180ca9bb-d0c1-5ee6-b2df-e9119a7902e4 | note | Standard / Specification - PS- 21.6.12 Appendix V
218fde14-75c3-5ac1-a4b4-9b5cddc2e56f | note | Verifying Document - Lab Test Report
e20bc37c-f276-5e75-b97d-52775c0ab193 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipeline with aminimum of 1 test between each pit/manhole.
e3398b96-d7c0-58b0-95d8-4fbfab874eca | note | Verification Activity: Activity - H
a0c63a65-4cb8-56e7-9ef3-9bc1860077e4 | note | Verification Activity: By - SE
381a4179-be62-4fb9-ae2c-19462c4a2c78 | checkpoint | 6.3.7 - Pipe Inspection
f5ed69ee-10a2-5e2f-af51-504d6b472623 | note | Detail - Inspection of Drainage line
8a346fe5-c6ef-56de-9951-ff7a11a76b50 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
b843a1f5-497e-5250-86b3-faa95dff6fdf | note | Standard / Specification - PS- 21.7.6
79c7983e-9f5f-5f49-8e7f-5953794a8c73 | note | Verifying Document - Drainage line record
33a0dd05-6e45-58e2-8b64-4530925a6687 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
cfab3d52-c273-52e3-a628-b5db808bd838 | note | Verification Activity: Activity - I
22523c9c-d85b-51c2-903e-96b07c98914f | note | Verification Activity: By - SE
2127f704-9cc7-4042-a465-3b4f779d03b0 | checkpoint | 6.4.1 - Foundation Compliance
ead0f1e1-cfdb-58e1-b03c-969734c1a7c2 | note | Detail - On Granular or Cohesive Material
c292d81b-34f2-5296-8fc7-18fa2ec1864f | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
986a6cff-05d2-5520-8507-ad21a6fe1a06 | note | ○ Cohesive Material: Vane Shear Strength 70kPa
cd84e5d8-4d3a-58f6-92b8-d4eb27c0338f | note | Standard / Specification - PS- 21.7.2 Appendix V
3e93ab28-7f10-553f-943f-4d1f980c77d1 | note | Verifying Document - Scala/Shear test result
5369b206-f393-59da-a383-fa29502806ff | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
f780c438-25e1-5ad2-8dc3-4cd2de219835 | note | Verification Activity: Activity - W
21176950-6e9b-57a4-b660-074bdf2b3dcc | note | Verification Activity: By - SE
456142a1-b11b-46ef-8a86-458234301635 | checkpoint | 6.4.2 - Undercut approval
c067984c-b6a9-5133-bd3c-6c164f3dd92b | note | Detail - On Subgrade
6ab3d3a7-3972-5a9f-b311-9924cafd0f7f | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
60a869c2-f38f-52c0-abc9-07e59c3100bc | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
3014fa2d-7d7b-5bbc-a512-60d57545f3da | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
98a1c9e5-2edb-528d-9d4e-c8bb6a850136 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11, AS/NZS 2566.2/2002
4968ef5d-ab39-5443-ad83-2e0fd748dda6 | note | Verifying Document - Lab Test Report
80550213-acff-522c-8824-522c74d93c76 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
4157df82-4a77-5c23-8db2-97ee9c9f4d13 | note | Verification Activity: Activity - H
32937e32-fc4b-53f3-86dc-2c36cb64428b | note | Verification Activity: By - SE
d24ee8ce-60ca-43c1-ab11-72002ad993d9 | checkpoint | 6.4.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
9876112b-e61b-5aef-8a30-d92255571473 | note | Detail - On Granular Material
389c1f6d-8aab-515e-8b15-fa72297ff34c | note | Acceptance / Conformance Criteria - Clegg Reading >10 CIV for non-trafficable areas
9cd30ee0-dbe2-5df3-8f77-801d9be00db7 | note | ○ Clegg Reading >25 CIV for trafficable areas
09bfa8a9-623d-54cb-afcc-f572d491463a | note | Standard / Specification - PS- 16.5.12
2f495d6d-bc68-57c7-8622-001420b7984b | note | Verifying Document - Lab Test Report
c99d068e-98a6-5875-993f-9d9f056a4224 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
d6a5117b-2ffc-5265-ab14-7a8917638f3e | note | Verification Activity: Activity - H
b93d6097-0850-57e4-9837-319fd74b5919 | note | Verification Activity: By - SE
0d8d940c-81d1-48d8-ab78-c50a61ac892d | checkpoint | 6.4.4 - Bedding Compaction Testing
4ede6d63-0d60-5325-bb8e-d4dbc6cd4770 | note | Detail - On Granular Material
457159e3-9197-51fa-88a1-5e5e594755df | note | Acceptance / Conformance Criteria - Bedding Zone: 100mm(for DN300 & DN375) 150mm (for pipes greater than DN375)
ec9658e0-e16d-599d-b88d-7b30df160634 | note | ○ Minimum Compaction - Trafficable and Non-Trafficable Clegg Reading >12% CIV
73690262-3a82-5d36-afea-9249b59ca091 | note | Standard / Specification - PS- Table 21.6, PS- Table 21.12, AS/NZS 2566.2/2002
b19575c2-0ebb-5130-93f0-083a9b2d2fa4 | note | Verifying Document - Lab Test Report
8dffa7d1-9320-57be-89c7-a54cae4d44fb | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
250161ed-f7a9-53a4-8e08-fab5bf363101 | note | Verification Activity: Activity - H
e15a4e98-2f55-599a-b822-c3e86ab552cc | note | Verification Activity: By - SE
7d83346a-a7ca-4e52-b76e-23ff55475bb6 | checkpoint | 6.4.5 - Haunch Zone Compaction Testing
558deabf-6104-5e6a-8a76-6046cdd54bc2 | note | Detail - On Granular Material
8cf13473-0595-55ed-ae1b-1ee743d72e7c | note | Acceptance / Conformance Criteria - HS2- 100mm if D≤1500 (or) 150mm if D≥1500
534078a5-f108-548a-b24d-ea1665459048 | note | ○ Minimum Compaction - Trafficable and Non-Trafficable Clegg Reading >12% CIV
6ca7192a-c647-5c3a-acae-091c2bb02756 | note | Standard / Specification - PS- Table 21.6, PS- Table 21.12, AS/NZS 2566.2/2002
b074e194-6d9e-5faf-9bbd-6c14b46f2418 | note | Verifying Document - Lab Test Report
f36aec97-d7f3-5fb1-bf23-d7145a7a1c23 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
265d286f-a47f-54f5-a750-de4c93b4b3e9 | note | Verification Activity: Activity - H
7e9e4b40-7dcd-5504-b6d5-294cc1b90c1d | note | Verification Activity: By - SE
9aaefef9-af34-46e8-ab8c-90057306e3c8 | checkpoint | 6.4.6 - Side Zone Compaction Testing
17117f2e-1bfd-592e-8d93-8d1b83370771 | note | Detail - On Granular Material
5d5633bf-26f3-56d0-8bd5-42077b55f74c | note | Acceptance / Conformance Criteria - HS2- 100mm if D≤1500 (or) 150mm if D≥1500
33eb20b4-86e1-5fb8-b033-bdfec3967233 | note | ○ Minimum Compaction- Trafficable and Non-Trafficable Clegg Reading >12% CIV
f1d3ac80-d8b1-5752-b0e0-4e61631e2060 | note | Standard / Specification - PS- Table 21.6, PS- Table 21.12, AS/NZS 2566.2/2002
9d69d555-6f46-5848-b97f-0ac1436ef1ee | note | Verifying Document - Lab Test Report
8aed4311-83b4-5ec3-b8e6-63b47d3c8cbb | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
7d48524b-a1e3-57e3-beec-3920df29d3d4 | note | Verification Activity: Activity - H
b1e72550-3e83-5016-9725-48cc486aad53 | note | Verification Activity: By - SE
bb0da2f3-9e8a-42f8-88ed-181e1f579d51 | checkpoint | 6.4.7 - Survey
1f82a810-ce68-5b76-910c-da7d77937b43 | note | Detail - Surveyor to Setout
05112abc-c80c-5cc9-9f56-780b11fcbe2f | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
14b8322e-6bce-56dc-a8fe-c44cd97efcb4 | note | Standard / Specification - PS- 21.7.6 Table 21.15
42cae4a6-96c1-519e-a2dc-3e79b63392ef | note | Verifying Document - Survey Data
2e1a4cca-ede5-5d07-bd97-7edd1a2b84c2 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
f6162b45-0e23-55dc-b99e-85d558e60f3f | note | Verification Activity: Activity - H
a02efa10-38b1-5ad3-80be-abccf90e2100 | note | Verification Activity: By - SV
9abdc1fa-1765-465e-9f5a-bf2a8763b9ff | checkpoint | 6.4.8 - Overlay Zone Compaction Testing
8d6877dc-aa82-5ffe-8177-5c0f0ebf79e9 | note | Detail - On Granular Material
e399de89-5f85-5f78-af03-d0260d1e1e8a | note | Acceptance / Conformance Criteria - Minimum Compaction- Trafficable and Non-Trafficable Clegg Reading >12% CIV
19ebfa77-251e-51d1-805f-7b6be2c91e27 | note | Standard / Specification - PS- Table 21.6, PS- Table 21.12, AS/NZS 2566.2/2002
5c298d88-fc1a-5c77-9bd5-cdd9d6d379a9 | note | Verifying Document - Lab Test Report
2b4a9a87-cef2-57cb-984a-81c846cc1229 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipeline with aminimum of 1 test between each pit/manhole.
78f4289f-c40f-573f-aa8e-c607a0cec89e | note | Verification Activity: Activity - H
76212a60-7d62-5f72-abc3-afb87cfd451f | note | Verification Activity: By - SE
33c0ecf5-a051-4368-bcfd-391ddce613dc | checkpoint | 6.4.9 - Backfill Compaction Testing
eb761d91-5fc9-5048-a7b3-b4b8ec0559ab | note | Detail - On Granular or Cohesive Material
2adaf062-1093-545b-89bb-076c434dd9fc | note | Acceptance / Conformance Criteria - AP65 Backfill Compacted in 200mm layers.
fbf2cb49-fcdb-503f-a81a-061a8457ecf3 | note | ○ Testing to be completed on maximum 200mm lifts of backfill
83644f2c-00c5-5137-9990-fbad3ebfd6c3 | note | ○ Clegg - 28 CIV
198eab81-d1f9-546a-9bec-ecb365c8289b | note | (or)
ca05defb-e269-5c07-a1b2-b97b8a6cc365 | note | ○ Cohesive Material in 200mm layers.
739713b5-64c8-52e8-ade1-9ec47442caf8 | note | ○ Shear vane - 50Kpa
3e1ddc8d-90db-57c7-8996-5adbf62b9476 | note | Standard / Specification - PS- 21.6.12 Appendix V
8f5a994f-3bbf-5153-aa90-2231a6359fa1 | note | Verifying Document - Lab Test Report
7a5406a0-a886-513d-994e-d6e92c60001c | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipeline with aminimum of 1 test between each pit/manhole.
0129e4b5-0fda-5fce-990a-ae10722fbe09 | note | Verification Activity: Activity - H
e763d457-b390-5598-81a8-87233cee206a | note | Verification Activity: By - SE
b32c7f1e-944f-47b8-8328-9ff257e92175 | checkpoint | 6.4.10 - Pipe Inspection
964388d9-21ce-5f41-9816-0b455e39b7b5 | note | Detail - Inspection of Drainage line
4c1d338a-4994-55da-b14e-3816b6d2fd0e | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
b4ae75a9-083b-5735-bc48-699bb9445c1a | note | Standard / Specification - PS- 21.7.6
91da4862-ba58-523d-99e2-e16efe095a86 | note | Verifying Document - Drainage line record
fab1a1e9-ce12-5d8b-98f6-b026e5f9b59a | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
1833a117-db66-54e2-b153-ed34230e17a6 | note | Verification Activity: Activity - I
5f307944-e2c7-5bdc-a52a-22cd3074017c | note | Verification Activity: By - SE
cd05755b-6530-4d68-901b-b86b051f2845 | checkpoint | 6.5.1 - Headwall and Wingwall Foundation Compliance
185f2e52-321b-51c2-a6e6-7a861486047a | note | Detail - On Granular or Cohesive Material
77b9cc44-ace7-589f-9de6-2b1d303d8bdb | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
2041ecb8-9364-564c-ab9b-d00b48259b1b | note | ○ Cohesive Material: Vane Shear Strength 70kPa
3a2cf4bf-144e-5779-8417-91fda8e1b522 | note | Standard / Specification - PS- 21.7.2 Appendix V
5c8f3297-06a4-5d87-800d-5e375195d026 | note | Verifying Document - Scala/Shear test result
3e5ee455-acca-5a00-8a54-2d8c47c69730 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Structure
466ea7b1-d5a6-5574-b250-b5b64056261e | note | Verification Activity: Activity - HP
ed428e12-c64b-547e-a62b-f53c1b2bf758 | note | Verification Activity: By - ENG
98a88dc9-37c1-43ce-a597-80f47325c373 | signoff | AUTHORITY HOLDPOINT
88ca8e9f-4f67-4545-a15e-88a6810a899e | checkpoint | 6.5.2 - Undercut approval
fbdc269e-16f6-5a81-9799-6964e9e2c65f | note | Detail - On Subgrade
45d76a45-a37e-5408-a560-b2fbbb1efd3e | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
f3962eef-25d1-5f51-be4a-ace7f6293695 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
51828099-4761-5cd7-92ad-a2b27d95055f | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
01f97c97-eeb6-5097-ab31-e804e5040563 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11, AS/NZS 2566.2/2002
57933872-1a6a-5acb-912d-be2e54af1c1e | note | Verifying Document - Lab Test Report
a646b70c-27d0-553c-9662-472978e9f851 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
3c64d34a-9e27-58f8-b94b-4f7f5649b182 | note | Verification Activity: Activity - H
bf7b7f83-f624-50d4-ae8d-bfdbf70577bd | note | Verification Activity: By - SE
9fb39278-c14d-45d4-800d-874c46a64151 | checkpoint | 6.5.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
d3a3ce3e-9b26-5f78-88a5-f835d9114acd | note | Detail - On Granular Material
dd49e3e8-d46a-5954-82f3-c662e08fc6eb | note | Acceptance / Conformance Criteria - Clegg Reading >10 for non-trafficable areas
d88b3ec8-7dbc-54ee-8298-725034a975f8 | note | ○ Clegg Reading >25 for trafficable areas
3b857764-725c-5fe5-a397-9c77e2446bfe | note | Standard / Specification - PS- 16.5.12
f842f9fc-1e83-512d-a9c6-ee8cd7a3690b | note | Verifying Document - Lab Test Report
62ffbeb0-f851-5c49-b21d-10ca075e6ffc | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
e3ad1f74-85b4-57a3-a76f-d01e36a8686a | note | Verification Activity: Activity - H
0131611a-1bf0-5624-a443-60903c5b6a05 | note | Verification Activity: By - SE
18b5b9e0-aa19-4cbb-ad4f-a07006104a8d | checkpoint | 6.5.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
37eef4c8-97c4-5859-ac82-70e5d09b8ffd | note | Detail - On Granular Material
901f072e-a5a8-5dcb-917c-c74f68da5899 | note | Acceptance / Conformance Criteria - Clegg Reading >10 for non-trafficable areas
df7b9b1c-4165-5a8c-9ef0-b348480fcc15 | note | ○ Clegg Reading >25 for trafficable areas
f1918f33-cbd9-5046-8af9-c296e2313dea | note | Standard / Specification - PS- 16.5.12
f2d95ab2-2e1e-5e84-a369-a3ab2f9efe42 | note | Verifying Document - Lab Test Report
1edf19aa-4934-5c36-84f8-06c64f9a8e76 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Structure
61511731-ee49-5500-8210-87915447110a | note | Verification Activity: Activity - H
4d5a4491-b8a4-50ac-a4bb-46865323155d | note | Verification Activity: By - SE
d84f6891-ac4e-466c-afdf-803ecfc76911 | checkpoint | 6.5.5 - Survey
d44f4dd5-4c5d-5b4a-a34b-2708940fd966 | note | Detail - Inspection of Structure
579337a8-ca86-5ce9-bb1c-fd1a66d3d5e1 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
ba604925-4ee7-53c1-a7ae-0b271c39bc8c | note | Standard / Specification - PS- 21.7.6
3df2ae70-e12c-55bf-b641-b910735bbbb8 | note | Verifying Document - Survey Data
393b4662-7dcf-5679-853e-32fffcc59952 | note | Testing Quantity Required (based from schedule qtys) - Continous
a794916d-3aae-5514-a592-57f28421f63b | note | Verification Activity: Activity - H
16e3534c-f1e4-5f91-a997-f5b6138ab285 | note | Verification Activity: By - SV
446b9c76-4a1b-45dd-be3c-9a6b3ef21794 | checkpoint | 6.5.6 - Backfill Compaction Testing
93683a25-4100-5d37-9a1d-a1707a7e4b0b | note | Detail - On Granular or Cohesive Material
33b793a5-a45f-5d5c-a0b7-12c01c74d0be | note | Acceptance / Conformance Criteria - GAP20 Backfill Compacted in 200mm layers around pipe.
d2d20bbc-01ee-539e-baa0-1e0d932052ec | note | ○ Clegg - 12 CIV
f44559d3-0643-500f-95ac-0751cf8b4b65 | note | ○ AP65 Backfill Compacted in 200mm layers.
1a157aab-9e07-5dbe-8bc5-f060e0c2da50 | note | ○ Testing to be completed on maximum 200mm lifts of backfill
77bcd838-fb98-5709-9c80-ab96ab4948e3 | note | ○ Clegg - 28 CIV
78beccf7-386a-5c1b-b686-3980fe73ed99 | note | (or)
41b34cde-504d-59eb-96f3-9995c23af164 | note | ○ Cohesive Material in 200mm layers.
ff4aff06-c84a-599b-b030-67a1fa555094 | note | ○ Shear vane - 50Kpa
f634568e-1e23-582a-bed7-9177d339c7ea | note | Standard / Specification - PS- 21.6.12 Appendix V
7728a924-b7c2-5d1b-a4a2-7e5c6dce609a | note | Verifying Document - Lab Test Report
c8c5ee46-041b-5be8-b416-a1d47e989a30 | note | Testing Quantity Required (based from schedule qtys) - GAP20- 2 test per lift
e07cc1fe-f3b8-59b2-9a46-205a175057c0 | note | ○ AP65 - 2 test per lift
1efad246-225f-5f72-b906-4c5cccc9e573 | note | ○ Cohesive - 2 test per lift
287cbc88-bef6-5e8e-a1c1-ad8edb61ceaa | note | Verification Activity: Activity - H
b05ccaa4-4379-5c93-a732-3c9ffb2829ab | note | Verification Activity: By - SE
f8ceaa11-20db-4b79-992d-2ac54d61dfb2 | checkpoint | 6.5.7 - Pre-Backfill Inspection
bebd6af7-15df-560d-912e-e3b648d3f920 | note | Detail - Inspection of Structure
ccbf20e2-8598-5a9f-bee9-36f9408056bb | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
1645d5d5-49b5-5131-9f67-1d4c7fd65b98 | note | Standard / Specification - PS- 21.6.11
4f5527bf-7b56-5108-b22b-cdcbe7995ab3 | note | Verifying Document - Manhole/Catchpit Record
3d0db4b5-4e7f-5217-9bad-f9e981de43b1 | note | Testing Quantity Required (based from schedule qtys) - Continous
c1812839-345d-5ad8-b92d-ae8dc685cea0 | note | Verification Activity: Activity - I
fe951612-825c-58ae-947a-5e9acaf59b34 | note | Verification Activity: By - SE
fbf4a3da-0656-4e11-b481-5456fdddba77 | checkpoint | 6.6.1 - Riprap Foundation Compliance
d92dbb86-d051-5abb-8552-825dd0ffe7d2 | note | Detail - On Granular or Cohesive Material
736664ff-6ce6-5736-b28c-fe24e46c1aa5 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
74367d89-c893-5a23-ae85-d28be2d3e20c | note | ○ Cohesive Material: Vane Shear Strength 70kPa
f7061cc1-69f2-56a6-9bd8-ff35f1b09e10 | note | Standard / Specification - PS- 21.7.2 Appendix V
9b40a004-3026-55bb-b088-bac0ebb026fa | note | Verifying Document - Scala/Shear test result
7c0d78e5-bc03-54ca-b198-a42cf6063890 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
a414e1a8-dd15-5a4f-8776-45d816bab0cd | note | Verification Activity: Activity - W
9004ea67-e52d-5bbf-a35e-b8ccefa375b3 | note | Verification Activity: By - SE
8d07e9d1-37a4-45b4-abf6-36367f746c6d | checkpoint | 6.6.2 - Undercut approval
44a18c0c-401d-51c8-82a0-4b7855cdebfc | note | Detail - On Subgrade
58ffa302-8e86-5eb0-a6c4-d43f188b4e0b | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
b4f00509-cc32-526d-a358-327f1cd5c034 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
46d4c2bd-b7a5-53da-aae6-83e7244e24d5 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
6b46fd55-978b-5f98-a56e-eb0ae39ae638 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11, AS/NZS 2566.2/2002
f2c1bb1b-19ed-5509-88bc-fbe430b6c1f0 | note | Verifying Document - Lab Test Report
1f3d0c4c-3c57-559c-8cce-e1d9cd01d87e | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
4520938f-5169-5a61-a498-4c3c5c886b39 | note | Verification Activity: Activity - H
84b559ee-0aad-558b-86d8-b2cfaf7de091 | note | Verification Activity: By - SE
04cd3fd0-1085-4171-a695-07aeb0566cbf | checkpoint | 6.6.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
c93b14de-a304-52a6-94ef-5a40e26e7556 | note | Detail - On Granular Material
cca410c6-cf04-528c-b84a-cd3180cde606 | note | Acceptance / Conformance Criteria - Clegg Reading >10 CIV for non-trafficable areas
a998ad61-d5e4-508e-a919-ca52d1d2888d | note | ○ Clegg Reading >25 CIV for trafficable areas
56051342-abef-53d4-bb71-5d92b5a24f80 | note | Standard / Specification - PS- 16.5.12
da3b8e07-62af-556a-b4fb-31fad0bcad6d | note | Verifying Document - Lab Test Report
bb99e03e-af89-5346-8eb2-45d547a05a80 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
6d40c8cf-0dab-5f1a-8dd5-e17d3e520fb2 | note | Verification Activity: Activity - H
c3d76e25-7ffc-5378-bb22-d1846d76d78e | note | Verification Activity: By - SE
7e5a9037-0b49-4750-9896-997643b8eaf9 | checkpoint | 6.7.1 - CCTV Inspection
7d87e58b-f9c2-5be6-8e1f-8796c94817b5 | note | Detail - CCTV stormwater pipes at completion of trench backfill but prior to final surfacing (pavements, etc.)
adba4e97-14ac-5030-abba-148c8395bc66 | note | Acceptance / Conformance Criteria - Every stormwater pipeline 225mm diameter or greater.
73a183b1-f9b2-5689-86b2-8c24d124c848 | note | Standard / Specification - PS- 21.7.6, PS- 21.7.8
01e5b8be-bc23-5875-a4bf-3451dd48fede | note | Verifying Document - CCTV Report
51e3f350-597b-5f76-a4bb-af8135071178 | note | Testing Quantity Required (based from schedule qtys) - 1 per line
67366b2d-bd5d-5aa1-8f76-0bee6d475444 | note | Verification Activity: Activity - S
c560ea14-73c5-5c4c-b5e2-2e0a1f7d31d0 | note | Verification Activity: By - PE
fe721f6f-eb8d-4b5b-8793-967b04063899 | section | SECTION 7 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
9aaf90c1-bfdb-42a7-8e85-e9f704bae1ec | checkpoint | 7.1.1 - Survey As-Builts
06c25efe-9793-5ada-a470-d2d30367855b | note | Detail - Quality Check on New Works based on the tolerances in RITS
5a1b0eb5-28cd-5bc5-86f9-1652ce6bb4b9 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
20c135ab-e762-56d5-b72d-03cba7af8e63 | note | Standard / Specification - PS-21.7.7
688c2b64-5683-5e1f-b81d-fd1b5957c523 | note | Verifying Document - Red pen markup only
9688f967-9be7-5901-a66c-f306a848ce4f | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
5c34ddbb-ca1f-5912-a7c2-655ad81e840a | note | Verification Activity: Activity - H
ac3558cb-41c8-5ba0-bd59-7330086521ab | note | Verification Activity: By - SE
c144acbc-0b66-47c2-aad0-e84eb14de847 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
07d47999-6f63-5a87-83c3-8ffc9506aa43 | textbox | Contractor's Rep Name:
566aea65-3f94-5f26-91ca-64c334f4822a | textbox | Engineer's Rep. Name:
de933729-61d6-5b6a-ba88-755d9add38e8 | date | Date:
6219e91f-7869-4874-a28d-8207339dc7c8 | signoff | Add Signature
ff1dd30e-f24a-4b4b-9eac-bf686c0f70de | checklist | DN1210-008 ITP Noisewall 1 Rev 1 | itp | DN1210-008 ITP Noisewall 1 Rev 1
dc439d04-ad5e-5573-818f-c5c286b26df4 | section | SECTION 1 – PRE-CONSTRUCTION - MATERIAL, PERSONNEL & THIRD PARTY APPROVALS
5ba25caa-7a71-5139-8d6d-82357c289e49 | checkpoint | 1.1.1 - All metalwork to be approved by the engineer after fabrication
87bdd074-adec-58fd-a63c-e6d5e028f17e | note | Detail - Hot dip galvanised to standard hdg 900
98c69e01-29f3-53f2-8d6f-dd8f1cafe8dc | note | Acceptance / Conformance Criteria - Engineers Approval
b0b5c028-b263-5d86-8468-bed9858bf891 | note | Standard / Specification - PS 18.6.3
c6975e6d-cf42-58a9-96dc-90bbede7ad84 | note | Verifying Document - Visual inspection
071be570-ee9f-5a57-8e93-4b073c8c9c16 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
9bee1edf-40d8-5d3f-9a5d-4906f515415f | note | Verification Activity: Activity - HP
79f83faf-d5c7-5db3-9443-d9741f98c18e | note | Verification Activity: By - ENG
068dedb1-7fbd-5e00-a102-f41752de9010 | signoff | AUTHORITY HOLDPOINT
5b77c275-c7aa-5684-bd40-ba54d126d5bf | checkpoint | 1.1.2 - Hot rolled steel plates
2c47a6e9-a08e-5739-8f29-c7e8d3d02837 | note | Detail - All hot rolled steel sections shall be grade 300 complying with AS/NZS 3679: part 1
0dabdb54-74a7-54dd-ae40-de3ad20818e8 | note | Acceptance / Conformance Criteria - Grade 300 - AS/NZS 3679 Part 1
c76b6bca-e6f4-56fa-b7bb-d1453d9508b2 | note | Standard / Specification - PS 18.6.3
a46f0673-50f2-5848-9a66-351ee8402005 | note | Verifying Document - Supplier data sheet/ Mill certs
f71ae4d5-a759-5b64-b484-b80fad78b13a | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
80d4a903-5755-56af-b710-67b364d9d378 | note | Verification Activity: Activity - WP
b76c6864-d65d-5d6e-ba9b-54b00ad6a871 | note | Verification Activity: By - SE
993a2c97-80d3-5c56-8bb5-3a0cd3e51097 | checkpoint | 1.1.3 - Cold formed steel plates
d229f0f2-364a-5210-8086-72c1ce3bc2bc | note | Detail - All cold formed steel sections shall be grade 350lo complying with AS/NZS 1163
ba4d8304-9bcc-5de9-bb60-487d32752774 | note | Acceptance / Conformance Criteria - Grade 350 lo - AS/NZS 1163
c8b7045d-4e65-5004-b178-2faf397810e7 | note | Standard / Specification - PS 18.6.3
d30d11e5-c982-50e0-8b24-1c3de7152c7d | note | Verifying Document - Supplier data sheet / Mill certs
88a15989-7ae8-53ff-bf84-0175e84754d0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
7c299bb9-c2f8-54d8-a453-63e52980a80f | note | Verification Activity: Activity - WP
27df037d-7969-5882-879b-edce791de7c5 | note | Verification Activity: By - SE
db79d8f7-33e2-5c0e-862f-cefa1df6e8e5 | checkpoint | 1.1.4 - Mild Steel plates
a32c4834-9a78-539c-a5d5-7389c11d1b7d | note | Detail - All mild steel plate shall be hot rolled grade 350 complying with AS/NZS3678 (AS/NZS 3678-350)
7cd9c1c7-b21f-5d70-88cb-fbbfeaa4afd6 | note | Acceptance / Conformance Criteria - Grade 350 - AS/NZS 3678 (AS/NZS 3678-350)
d88a1b24-e1db-52f5-8aaa-7b85b0ae3e0f | note | Standard / Specification - PS 18.6.3
46e7120f-018f-5703-8219-bb5e63b2883d | note | Verifying Document - Supplier data sheet / Mill certs
a914bf70-1c36-5e5c-897c-04a8c79f8ab1 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
5f2399dc-817f-55ed-a292-855b1c106f85 | note | Verification Activity: Activity - WP
c77476e6-0463-533c-a9c8-eac096afef73 | note | Verification Activity: By - SE
4efd7e12-8765-507c-8da0-599a589078b5 | checkpoint | 1.1.5 - Round bar/rod
d5ef4756-3498-5ae0-9a8b-684db7d96f7f | note | Detail - To be grade 300 to AS/NZS 4671
fbc5f7fb-ae65-5167-953f-1701743687a8 | note | Acceptance / Conformance Criteria - Grade 300 - AS/NZS 4671
b4cd69d2-a6ba-5f3c-9b24-fa0050b144d7 | note | Standard / Specification - PS 18.6.3
c4b46c52-20a5-5af5-ac60-51251bebc3eb | note | Verifying Document - Supplier data sheet / Mill certs
e6e6c9c9-4a44-573d-9963-66dcef45d4e0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
4d58bc98-af07-5c06-b891-53233ccb29c2 | note | Verification Activity: Activity - WP
56ab8d87-e873-54cf-a6c1-e57300c7fd8d | note | Verification Activity: By - SE
1e999714-ded7-5714-ab23-b5f574a633d9 | checkpoint | 1.1.6 - Bolts and treaded rods
1e50e369-0191-5760-bd17-89eba5bce932 | note | Detail - All bolts and threaded rods shall be category 4.6/s to AS 1252
2d982ca6-dcd0-5c16-b12e-41a1e5c8cdf4 | note | Acceptance / Conformance Criteria - Category 4.6/s to AS 1252
844e284f-14e5-5b7f-be6d-cb835df0005b | note | Standard / Specification - PS 18.6.3
29b0a3f2-dd61-5e2b-97cc-688a22af3ac7 | note | Verifying Document - Supplier data sheet / Mill certs
791a825e-9754-565d-9548-7fc700f2c145 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
d3c70cf8-f765-5516-bc1b-8e0a2780853b | note | Verification Activity: Activity - WP
bfc76215-8b62-5cc8-8738-8c55a68ce26c | note | Verification Activity: By - SE
d47b70c7-d4f7-50b0-a088-bbd13a0577a5 | checkpoint | 1.1.7 - Rough or sharp edges
8239cc44-df77-5242-9d2a-53a51beb9e26 | note | Detail - All rough or sharp edges or protrusions to be buffed smooth
17f0a785-ff6a-5f0f-9d31-ed21bf94dabd | note | Acceptance / Conformance Criteria - All rough or sharp edges or protrusions to be buffed smooth
b5b71663-219b-5d9f-b957-16d39207e4cc | note | Standard / Specification - PS 18.6.3
cc58fa48-e238-53d1-85fc-bf562f0e3f01 | note | Verifying Document - Visual inspection
59159e4c-59a9-5256-99c1-d369a80f0b82 | note | Testing Quantity Required (based from schedule qtys) - During construction
14acb6ad-ba1b-5e05-8b3c-2c7e58085328 | note | Verification Activity: Activity - WP
730fa375-2c73-551a-be83-c3d2fc2ee5c9 | note | Verification Activity: By - SE
704a29d7-c4e9-5cfa-84e8-252fd7bf2eb1 | checkpoint | 1.1.8 - Epoxy Coating to the Steel column
da36ea66-3e4c-5373-8400-500b2eeccdc8 | note | Detail - High build epoxy paint all round the UC column concrete interface
4f50d82f-af3a-5dee-a5b8-897551e5b9f3 | note | Acceptance / Conformance Criteria - all columns must be coted with epoxy at steel and concrete interface
3831f71a-b15d-5fee-a9a9-57072adab45d | note | Standard / Specification - WSP-DR-STR-0306
3b331bb3-c95a-5cb7-93b2-40083c5e8e22 | note | Verifying Document - Visual inspection
c71ecc60-3158-574f-b678-6bc87e3f42be | note | Testing Quantity Required (based from schedule qtys) - During construction
e57e7e2d-40fe-5f23-b707-093f89a44736 | note | Verification Activity: Activity - WP
7b63766e-38d0-5caa-954f-4697e765b776 | note | Verification Activity: By - ENG
95a62a2d-dc41-5729-8c34-772c79c3554e | checkpoint | 1.1.9 - Butynol sheeting - membrane
5a887d98-a2d4-54ae-a390-0257dd636dcd | note | Detail - Butynol or any similar approved shall be used between timber and steel
2ca757a4-cbc8-566c-a551-e5db903dcfc1 | note | Acceptance / Conformance Criteria - Membrane seal
b6b16dcb-822a-55ae-88cc-938242b76771 | note | Standard / Specification - PS18.6.3
ef5fb293-1a54-57d4-96f0-4323475e14ee | note | Verifying Document - Supplier data sheet and Engineers approval
82673ede-b43f-50e3-bcde-fc08d9726de8 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
2a6cfa88-e388-5cd9-ac3a-21a9ef606b81 | note | Verification Activity: Activity - HP
345840de-24e7-571d-b77f-bf487038ee5b | note | Verification Activity: By - ENG
ba2ef6ed-92a6-53c7-bfe9-b134dba90eb7 | signoff | AUTHORITY HOLDPOINT
e6bb1c37-103d-54be-bbb4-bf36c50c5f77 | checkpoint | 1.2.1 - Timber
54251110-fb04-5634-804a-92c22b624288 | note | Detail - Timber shall be VS8 grade radiate pine complyng with NZS 3603 and graded to NZS 3631
fcd03198-8f9c-5850-84d0-b493cd0ba8d4 | note | Acceptance / Conformance Criteria - VS8 Grade radiate pine with a Timber strength - 11.7MPa
5e992fc1-b3d7-5182-9932-816b8f7679e4 | note | Standard / Specification - PS 18.6.3
c4f87a52-0519-5ae8-b336-5759aea2f92c | note | Verifying Document - Supplier data sheet
fa6a83af-5c9d-580d-a86b-e5a78110f7e3 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
a50d4d7b-7c36-5752-a447-950f2b4e1fb5 | note | Verification Activity: Activity - I
e1de97ba-ae1c-5ab1-918a-6404fe0c2bb2 | note | Verification Activity: By - SE
30369b36-252b-59e5-8453-1ef6cc725793 | checkpoint | 1.2.2 - Timber - in contact with the ground
5152ee6b-48c1-5452-b7f7-665c012b4671 | note | Detail - Round or rough sawn piles in contact with the ground to be H5
c3eeb317-ac30-5f95-9d7e-3101991d8efb | note | Acceptance / Conformance Criteria - H5
75f7dbe8-72b9-5f1a-b8f7-15826c932b2d | note | Standard / Specification - PS 18.6.3
bf956d8b-9861-5579-80f7-03b4bee0420a | note | Verifying Document - Supplier data sheet
23055f9c-ecab-5a59-a7fb-780233919e42 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6e964ee1-46bb-52ad-b717-a5218a6e0fdd | note | Verification Activity: Activity - I
f380da60-80b7-5056-9f3a-2277ffcf4687 | note | Verification Activity: By - SE
94a81899-257a-5ffe-8a11-73f210325de7 | checkpoint | 1.2.3 - Timber - not in contact wth the ground
43baedb1-f8dd-5799-ac13-68a41cd4a8ae | note | Detail - Rough sawn timber not in contact with the ground to be H3.2
cc284ec9-df83-5816-ad1e-e548ef3fd65a | note | Acceptance / Conformance Criteria - H3.2
8995acd9-333c-570a-aec6-e20765ea8fac | note | Standard / Specification - PS 18.6.3
7cc07edd-fd8c-54ae-9d41-96ce81f43ac9 | note | Verifying Document - Supplier data sheet
7544f38c-33b7-522c-846e-628837afbd0f | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
91921caa-8caf-5c2e-9d1c-53429a51783a | note | Verification Activity: Activity - I
51024bff-9929-505d-af6d-acbf42b96537 | note | Verification Activity: By - SE
ee29378b-32d7-5f42-aa47-1090de8ff24e | checkpoint | 1.2.4 - All timber components of noise wall
c2944171-e8da-5bd4-8444-bbb67bfefd09 | note | Detail - Timber treatment shall comply with requirements of the NZ Timber Preservation Council incorporating - MP 3640. All timber shall be branded to NZS3640:2003 and must be treated not less than 2 months prior to use.
6448cf6e-b977-5414-adad-2b8f783fe839 | note | Acceptance / Conformance Criteria - MP 3640 NZS3640:2003
00a5bf57-9093-5222-a8de-7d7dded3457f | note | Standard / Specification - PS 18.6.3
1e318461-45a4-58c1-8ed2-c2bcf92458f5 | note | Verifying Document - Supplier data sheet
8c1efafa-2b61-531e-8f1f-39397d4d62b1 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
a0d72391-9573-5058-a0eb-84b413e05e9b | note | Verification Activity: Activity - I
3f823901-11f9-5b7a-981a-3f0f4aac3691 | note | Verification Activity: By - SE
f9d62092-ddd4-595b-9974-ca2ed9af18d3 | checkpoint | 1.2.5 - All timber components of noise wall
0efa02f3-da79-5b77-bdd5-a4d5f22e1971 | note | Detail - Timber shall have a moisture content less than 18% at time of installation to avoid excessive shrinkage effects.
20c0394f-4abc-5d3b-8f4d-edef79533980 | note | Acceptance / Conformance Criteria - Timber shall have a moisture content less than 18% at time of installation to avoid excessive shrinkage effects.
2d87e160-dae4-5e64-b3a7-76c6a9977cb4 | note | Standard / Specification - PS 18.6.3
94f6326b-2489-5eb6-be61-4aa3bd13487b | note | Verifying Document - Supplier data sheet
307a1a62-bac2-522c-a99c-4cf8b742b1ba | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6a315b29-999f-5814-ba87-a57841b3c4c0 | note | Verification Activity: Activity - I
bc525129-b4b8-5d43-885b-04861ce2640c | note | Verification Activity: By - SE
3272a837-e1fc-58a0-bc7d-7379bc60c516 | checkpoint | 1.2.6 - All timber components of noise wall
544ad440-b824-5da8-aee9-8bd16b5721e5 | note | Detail - Treat all cut surfaces with clear zinc naphthenate preservative and in accordance with NZ 3602.
f76dc74f-24e1-549f-88e4-1abf6be9aa7f | note | Acceptance / Conformance Criteria - Treat all cut surfaces with clear zinc naphthenate preservative and in accordance with NZ 3602.
37588d10-c423-59ed-961c-c956f7444c29 | note | Standard / Specification - PS 18.6.3
64c3846b-da7a-5d28-afc5-0c21935d4daf | note | Verifying Document - Supplier data sheet
d518a1e3-9870-5cfd-a733-66bea55e6cfc | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
eaf54b00-742e-551f-b9ec-5f73e8687585 | note | Verification Activity: Activity - I
911327c4-79d1-5baa-bb99-d9fb85bf6469 | note | Verification Activity: By - SE
f9dfbf52-7921-564c-a925-33cba059da58 | checkpoint | 1.2.7 - Galvanised bolts
2440ec0a-26dc-5d22-924a-c6e698d6f007 | note | Detail - All galvanised bolts in contact with H5 treated timber shall be protected using CP grease in pre-greased holes
855e0003-4cf5-5e72-8e20-f8b1614cf3e2 | note | Acceptance / Conformance Criteria - All galvanised bolts in contact with H5 treated timber shall be protected using CP grease in pre-greased holes
42f7b2c3-d6c9-51a6-8261-8b52eb60acaa | note | Standard / Specification - PS 18.6.3
e0a8034f-f8a9-5a0b-b2ba-c642ba4a4544 | note | Verifying Document - Supplier data sheet
3c2a2849-e465-5a3c-9b68-b756239e59e9 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
f4e95223-4a6a-5b04-8f80-6bfc0009a868 | note | Verification Activity: Activity - I
d4334259-f555-5639-a09f-63f567035a45 | note | Verification Activity: By - SE
e1936029-7894-51a0-a7be-3a1a2e755a8a | checkpoint | 1.3.1 - FH Nails
28d68371-a3d5-511d-b574-81b8c7782309 | note | Detail - General structural use 75mm x 3.15mm FH nails . All nails shall be flat headed, unless otherwise shown, hot dip galvanised and fully driven
db628c59-bf96-53a3-807a-f39fd18dcc9b | note | Acceptance / Conformance Criteria - 75mm x 3.15mm FH Nails
4a24bfb7-c4b1-5ca4-98da-eb87499c26ca | note | Standard / Specification - PS 18.6.3
05837ee9-a67a-5272-9bcb-f7894e309c17 | note | Verifying Document - Delivery dockets and supplier data sheet
fa89e629-1bca-55aa-aec2-dbd87af7df2f | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
82240e18-b2c3-525e-a2bd-727bb0d0d38b | note | Verification Activity: Activity - I
d179c9ba-17a7-5947-bae0-079338a7cc4e | note | Verification Activity: By - SE
92dc6277-2665-5d70-9e48-177822abec7e | checkpoint | 1.3.2 - Bolts
6fd1fc27-2e0a-5602-b948-507ecdba4eab | note | Detail - Bolts shall be M12 hot dip galvanised engineers bolts fitted with 50x50x5 galvanised square washers both ends. Washers for coach screws shall be provided in accordance with NZS 3604
672ea647-fc9d-597d-a6f1-13f399bfe296 | note | Acceptance / Conformance Criteria - M12 hot dipped, 50x50x5 galvanised square washers
f0c14c3d-8f7f-5a83-bc6c-760c84878fa1 | note | Standard / Specification - PS 18.6.3
aa565e89-d839-522b-9d92-689160284664 | note | Verifying Document - Delivery dockets and supplier data sheet
9ecbbaa8-0958-51a5-9143-d165d1ec9f6c | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
42240d1d-3fb6-54ad-979c-dcceb7e9c33c | note | Verification Activity: Activity - I
d49b33e6-b909-5d28-a95a-0e9dd644da3e | note | Verification Activity: By - SE
f6166390-0424-550a-b578-335017e863af | checkpoint | 1.3.3 - Bolts within 100mm of ground
ef0a452e-c447-559d-b720-ec3894f29512 | note | Detail - Bolts within 100mm of ground to be stainless steel.
910e16b5-6385-5c14-b82a-1a3eddeba3a0 | note | Acceptance / Conformance Criteria - Stainless steel bolts
aad17169-f7e8-5347-b07f-98395edf6661 | note | Standard / Specification - PS 18.6.3
126723f5-ecf6-5a58-a83c-f5b39d7d2534 | note | Verifying Document - Delivery dockets and supplier data sheet
4c1ffdfc-2a94-538b-909e-c3a8044cabe0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
413b49f0-dcc7-5238-8eab-d5a8b84ec194 | note | Verification Activity: Activity - I
3581952e-8803-5645-a554-6a585406dae6 | note | Verification Activity: By - SE
52dad3df-5c5f-542a-9707-5e4361323e21 | checkpoint | 1.3.4 - Coach screws
057507f2-4ca3-53ed-b8f0-f91c2e0da906 | note | Detail - All screws shall be hot dip galvanised and screw fixings shall be pre-bored.
1172649a-ca70-5d69-8e0d-9831d8152c9f | note | Acceptance / Conformance Criteria - Hot dip galvanised
43aeca2a-3829-5bf7-9322-fe2d86805984 | note | Standard / Specification - PS 18.6.3
a00ac75c-241f-517d-b981-d91e3044bfad | note | Verifying Document - Delivery dockets and supplier data sheet
7d2e118d-6fb3-5f8f-a6c3-dfbb5789eab7 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
df201f03-523a-5c04-b873-1de4e77e82bc | note | Verification Activity: Activity - I
96482dff-afec-5c12-b89f-0f524336fc05 | note | Verification Activity: By - SE
868e15d2-a829-5664-9f4e-1c730798c2ea | section | SECTION 2 – CONSTRUCTION ACTIVITY
8abc6212-3111-540b-9738-78a20e86ed40 | checkpoint | 2.1.1 - Setting out of Noise wall 1 all Posts
db9796ec-3de3-5f3e-a2b1-b371b55d636e | note | Detail - Setting out to follow design coordinates and levels within tolerance as specified in PS 18.5.7 section (e).
53c8d121-406a-5754-9665-84e5ce60fddc | note | Acceptance / Conformance Criteria - Engineers Approval
1ac7c545-fb56-5f43-9e9d-71200baa4099 | note | Standard / Specification - PS 18.6.1
49eefdea-60f2-5a7e-9485-4e81f54dee3d | note | Verifying Document - Visual inspection
9b22254b-b8c5-5fe2-abd2-fa7d667abe0e | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
d1b4e7ef-1486-5850-8c93-780e3ff27f28 | note | Verification Activity: Activity - WP
d5b62a0e-ab48-51a2-a5ca-bac0bff62f81 | note | Verification Activity: By - ENG
ac86be99-18f9-57a8-bf7c-14f69d596955 | checkpoint | 2.1.2 - Geo Technical investigation on each post holes
45032e44-c37a-598f-82f4-efe6d77a54e1 | note | Detail - Holes are to be 400mm dia and 2.8m deep. Shear vane testing to be completed to a strength of 60kpa
89cde49d-cbed-5656-8b76-5995c7d79101 | note | Acceptance / Conformance Criteria - Shear vane strength of 60kpa
815a6b13-4eda-5a1c-a9bb-3617264cd253 | note | Standard / Specification - PS 18.6.2
754362a4-9655-5c9c-92cb-f40197172609 | note | Verifying Document - Shear vane test report/Visual inspection
f9620d0c-b2c0-56cb-bd18-a6a4a167c6e9 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
c233521d-d38f-54bc-a9e0-72be1d3f9899 | note | Verification Activity: Activity - HP
4209a781-2ab3-588f-8d78-e9fa3287449d | note | Verification Activity: By - ENG
9e47e5c7-cb75-541e-a14f-4afa4b5d7a68 | signoff | AUTHORITY HOLDPOINT
2cdf9c15-2c63-5aac-9f2e-a940d4990caf | checkpoint | 2.1.3 - Noise wall footing concrete
139e9071-f02a-51c5-872c-60346393be5c | note | Detail - 17.5 MPA Concrete
9a2ac467-7a99-507c-88f3-8c9200f75b7b | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 17.5MPA
01f3b2d3-71df-5c0e-a557-cebe048096f7 | note | Standard / Specification - PS 18.6.2
a31d14e4-0d82-51e2-8601-61322fbf976b | note | Verifying Document - Concrete Delivery Docket
324e5e6c-bff7-5126-a664-7c0f7209f2b4 | note | Testing Quantity Required (based from schedule qtys) - During Construction
3216a620-a366-5d1a-8ff3-dfedb315054d | note | Verification Activity: Activity - I
2d5f18ab-85ce-56a2-b39b-83bbed73787d | note | Verification Activity: By - SE
b0af36a8-2e1e-5d8c-8d3d-b3d850c71730 | checkpoint | 2.1.4 - Installing Wooden Railings
207f27c0-a0e6-587f-8899-c5cad0ebc6df | note | Detail - with sufficient embeddment of nails and connecting details as per drawings
b8c45349-31a7-5ed8-9b83-67be91a22764 | note | Acceptance / Conformance Criteria - Skew nails shall be installed as shown:
6543a4e4-ab92-5a54-b0b3-4b3930c38246 | note | Standard / Specification - PS 18.6.3
6487da79-9484-5263-a42b-99a80c9b5613 | note | Verifying Document - Noise wall Checksheet
5ef90dfc-9ed5-55fb-8406-0f069a808cc3 | note | Testing Quantity Required (based from schedule qtys) - During Construction
89875b75-8f03-53ee-8339-893c9791911f | note | Verification Activity: Activity - I
a98fea2e-6479-5811-8272-80c2c4a34be4 | note | Verification Activity: By - SE
47886ec3-63d6-5e34-814f-8a266d50043d | section | SECTION 3 – POST CONSTRUCTION (HANDOVER)
49e56452-d262-55bb-8e2e-45db3938f81d | checkpoint | 3.1 - As-builts
790edb2b-229c-5e7c-980d-fe019c0d306d | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
4915cc5a-a225-518b-a3da-ffe8886dca97 | note | Acceptance / Conformance Criteria - All changes to design need to be captured on the noise wall drawing set
71b63e81-f275-5591-812b-c0601b22bae6 | note | Standard / Specification -
f046623b-db5a-53f8-bd6b-d4e4b89d9e10 | note | Verifying Document - Redpen Markup
9cd59d86-5195-5dd3-a4f3-42f6def3fa28 | note | Testing Quantity Required (based from schedule qtys) - During construction and after finishing
ffc5e08f-200b-5cd0-ab09-336f592f225b | note | Verification Activity: Activity - WP
a1abcf24-c909-5eb5-a2d0-6730301d1972 | note | Verification Activity: By - SE
e5125254-ffa1-40a7-8898-657a0b543ade | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
5b316864-b58a-55a0-8416-0635f30f4dea | textbox | Contractor's Rep Name:
17ce483e-e328-5e7a-a60e-0fd11ed74c75 | textbox | Engineer's Rep. Name:
32adacd4-f54c-55af-8dc0-0fabac71ba31 | date | Date:
e325a840-3071-4552-9013-4b3bb5e9bd70 | signoff | Add Signature
8c66c8f7-6bc4-445f-9130-ad10c40b11b7 | checklist | DN1210-009 ITP Underpass Rev 0 | itp | DN1210-009 ITP Underpass Rev 0
9cbb510e-fd5d-4219-af3d-5f436531ae9e | section | SECTION 1 – EARTHWORKS SUBGRADE
4b8442c9-d337-4db5-bde4-ea2c0d5abaed | checkpoint | 1.1.1 - Cut Subgrade Inspection
a0cd40f0-6ab6-5c48-add2-ed14c5397384 | note | Detail - Engineer to inspect all foundation surface inspections
56d04848-e1a7-5446-98e4-0807d8202465 | note | Acceptance / Conformance Criteria - Engineers Approval
dcb61ee7-d946-5ae2-9ced-7f1232dee7c8 | note | Standard / Specification - Appendix V
f8ca2430-1672-59d8-ad0b-e1ef73b9dc37 | note | Verifying Document - Visual Observation
00b32753-c725-5f62-8254-8d76c67a0b4b | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
eb77ce94-f291-5f30-908c-de65ca7cafa3 | note | Verification Activity: Activity - HP
c68a4b1e-7c0e-5ccc-80b5-058d3f24f57a | note | Verification Activity: By - ENG
393a82f7-b3c7-4080-85fb-ffdc930f746a | signoff | AUTHORITY HOLDPOINT
fe906f2c-8564-45d4-b12a-24e38a51b667 | checkpoint | 1.2.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
be2404ff-fd22-511b-b3c0-b5d7a4fd1024 | note | Detail - This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
8d54c44f-b86c-5d57-a64b-bcbf5bf3abf4 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
fe06a3a4-0846-5222-a3a0-edd8a6fb88c0 | note | ○ Single Test Min SU: >50kPa
aa0752af-6a98-5d2a-ad94-e08764c7d8b7 | note | Standard / Specification - Appendix XVIII
10ae48b3-fc36-53eb-8b6c-a690e9910492 | note | Verifying Document - Shear Vane Report
693dc52b-b004-517b-9639-b6e5c7dec805 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
65e1976c-483d-5485-bccd-9162b55ed8ef | note | Verification Activity: Activity - I
debc24a2-16c1-5050-9e31-7890bf0629a9 | note | Verification Activity: By - SE
e52b86a5-b667-471a-b63f-e45d88af79e8 | checkpoint | 1.3.1 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
4869fba6-e378-5d3e-a433-53b2a5b7d6c4 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
bb41ccfb-e9d6-5e81-b6d3-d777072128ee | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
cb72e9a4-eb8f-5c81-bcb4-c753560d01e2 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
c6f25b73-2fc1-5a47-9227-1eb1b10e4308 | note | Standard / Specification - Appendix XVIII
f8e82909-0414-58c2-b20c-8ff47b597494 | note | Verifying Document - Scala Report
1c1239f6-e846-57a7-968c-ece61f59413e | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
ab485686-7a4d-500c-9b95-08e2b73ee3dc | note | Verification Activity: Activity - I
f1b63378-316d-526a-874b-6337508b9bb9 | note | Verification Activity: By - SE
34f35990-312e-4551-ac9c-b683685967e2 | checkpoint | 1.4.1 - Undercut Surface Inspection
3455ad10-4902-5b88-bbc5-24f8bcfd63d7 | note | Detail - Engineer to inspect undercut surface and determine undercut requirements.
0568c8dd-fb95-5072-a6f8-038c12c96935 | note | Acceptance / Conformance Criteria - Engineers Approval
f21f8e30-459a-569b-b9e2-d80120fecb88 | note | Standard / Specification - Appendix V
cf29355c-d20e-5bfc-af1b-667d39dadc50 | note | Verifying Document - Engineers Approval
2ffa16c2-ba28-5f7c-bde9-6cb10a3911bf | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
c404a650-32c9-5fbc-8d11-12557dd3053c | note | Verification Activity: Activity - WP
8f692dc3-bc9c-5729-a9b7-e88689700cc3 | note | Verification Activity: By - ENG
e13da792-0d1e-4e73-8b23-6fb9cdad2ed7 | checkpoint | 1.4.2 - Placement of Geotextile on Undercut
ff42db0e-2d67-5894-ae0f-fd07af6dbfb8 | note | Detail - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
e2ab5f07-bcc4-5382-9338-c1f66e789a76 | note | Acceptance / Conformance Criteria - Engineers Approval
038eb8a9-66e4-5a21-9b3f-c4e5745f4241 | note | Standard / Specification - PS 16.6.4, TNZ F/7: 2003 8.3
8eab2ff8-a0b1-5974-a0dc-7de5168d9650 | note | Verifying Document - Visual Inspection
8e0a2ffe-d77f-5819-9b4a-aaa3aa1cf5bf | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
5a73b327-2ec0-59db-9a95-33b1419c270c | note | Verification Activity: Activity - WP
d4defb56-fadd-595f-93a3-3aa564d245d7 | note | Verification Activity: By - ENG
05bf4ffa-fdd0-4c21-8138-feaf4e0eb7ef | checkpoint | 1.4.3 - Backfill undercut
095c2041-8e00-5ca2-8df7-954b56ff9d42 | note | Detail - Backfill undercut with AP100 and lightly compact.
d1e87609-4f3c-5327-8303-6e4099783099 | note | Acceptance / Conformance Criteria - Engineers Approval
c889b3ab-5893-5352-8ba6-81f5f065de84 | note | Standard / Specification - In Eight ref: DN1210-WSP-NTC-0207
fceb0599-f45e-5daf-b736-49b9537d253f | note | Verifying Document - Visual Inspection
46a0f26a-f8b7-5b57-9c99-a939af10d9aa | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
06095ac4-9afa-5ef1-8b34-b21ee75c6eac | note | Verification Activity: Activity - I
4739a17c-b638-576e-ad7a-4b102099a57f | note | Verification Activity: By - SE
9fbc893c-6858-4254-a22e-1619e2055582 | checkpoint | 1.5.1 - Foundation Compliance
af159101-811b-525d-b715-dfa8a00b310e | note | Detail - On Granular or Cohesive Material
f7d29786-abb3-581c-87fe-958e09b0baaa | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
3ae2950a-5c95-5c22-b09d-ea9c027c45a8 | note | ○ Cohesive Material: Shear vane Strength 70kPa
715bdcf2-fe84-554f-83d5-5e216502b802 | note | Standard / Specification - PS- 21.7.2, Appendix V
002f0a75-0eaf-5dfe-8d46-844fdd4ff0ba | note | Verifying Document - Scala test result or Shear vane result
15a94ab6-1330-5869-82a8-fa738139e2ba | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
ab67b06f-33ce-55aa-bc40-5d7922e22376 | note | ○ 0-5m: 1 Tests
6592e4e6-d65e-5971-b859-c7ed132017e1 | note | ○ 0m-10m: 1 Tests
06d0b956-7e20-5dda-8f11-462811cdcb4d | note | ○ 0m-20m: 2 Tests
8270c8c9-0c3b-5ef0-9622-52fe305a1634 | note | ○ 0m-50m: 4 Tests
ffef4716-d092-5218-963e-90386cab37df | note | ○ 0m-100m: 6 Test
65050099-fa93-5d77-9a83-42dfb50bdbb9 | note | Verification Activity: Activity - W
3ed704c2-162e-5324-9c7e-411d440f4555 | note | Verification Activity: By - SE
e1095b8c-8ca4-4b3a-91a6-279bb38a48e2 | checkpoint | 1.5.2 - Undercut approval
1e9b6bf3-a2ae-5c69-85a2-a0d2288a9661 | note | Detail - On Subgrade
b8a979cb-284c-53df-87cc-9682ee4fb002 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
7c9e669a-f46c-505f-8095-ed4d6ec3501a | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
ec1b08ad-fbac-502d-9619-727f500868c1 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
a2d365fc-f241-5c0a-85fb-f723f4e45c4d | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11, AS/NZS 2566.2/2002
a6a599cc-7453-5fce-b0e4-5f5f582b90d1 | note | Verifying Document - Lab Test Report
6f307141-ff67-5a1b-b326-3cfb57d12570 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
e2677a2d-b7c9-5070-a4bc-9498788edbb7 | note | Verification Activity: Activity - H
9fbbf2a3-f31e-533d-be3c-a88504ca5168 | note | Verification Activity: By - SE
d824467f-f395-4d60-bb18-39202da292cb | checkpoint | 1.5.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
456117ec-526a-5acb-9c04-04505c7ed8bf | note | Detail - On Granular Material
71cbaeb2-f85d-51f8-805e-ef348fcd5b56 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
f6bff517-46ea-5b0f-91bf-63dcebe58bb9 | note | Standard / Specification - PS- 16.5.12
d0fe12d2-e82b-5c89-b16e-49dfdb76b0cf | note | Verifying Document - Lab Test Report
9a11e13b-0711-5f63-8bc9-7885945b841c | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
c41ccd72-3ab2-5de7-901f-6c716816cd48 | note | ○ 0-5m: 1 Tests
a69a76a3-ce97-5598-a58e-4ba970efe853 | note | ○ 0m-10m: 1 Tests
247a0ed3-c3dc-535c-93f7-a4491d7ae496 | note | ○ 0m-20m: 2 Tests
bc6a4c42-e2c3-5bea-ac1a-29daa8f3d3c3 | note | ○ 0m-50m: 4 Tests
3ae612af-6f82-501c-9486-3e08129d6f21 | note | ○ 0m-100m: 6 Test
14acd621-7ff5-582f-8fa0-75a4abd4cdbb | note | Verification Activity: Activity - H
a65a9578-faf0-51a5-9896-623c654b80b0 | note | Verification Activity: By - SE
9718a80a-5001-4764-a31d-45120910a2a0 | checkpoint | 1.5.4 - Bedding and Embedment Zone Compaction Testing (Polypropylene(civil boss)/Polyethylene Pipe).
8e941255-4a30-5dd6-bfde-8a74e8033298 | note | Detail - On Granular Material
a543fc8d-e18d-5ccf-874d-ce86b7f22b36 | note | Acceptance / Conformance Criteria - Bedding Zone:
0e40f8ef-b50a-592b-a63c-81ce89f360ad | note | ○ 100mm(for DN300 & DN375)
ad0f9091-69ee-52dc-a18b-59c1444a560a | note | ○ 150mm (for pipes greater than DN375)
c7a91e8a-b12f-518b-a823-9d80b8c8e88f | note | Embedment Zone:
fb1dc8aa-33f9-5671-b8ba-ec5b2e18f640 | note | ○ Pipe Dia ≤450 - 150mm GAP20/AP20 - Overlay
5644ec67-4fab-5cf3-9422-5df2cad58949 | note | ○ Pipe Dia 450< D ≤900 - 150mm GAP20/AP20 - Overlay
e14f2639-7490-5c8b-90c4-5da88a772183 | note | ○ Pipe Dia 900< D ≤4000 - 150mm GAP20/AP20 - Overlay
8c4b3f37-a138-5cfc-b419-9fa0b898f6fd | note | Minimum Compaction - Trafficable and Non-Trafficable 95% MDD on metal.
7c645d58-3fbd-5a4d-848f-6173f65da55c | note | Standard / Specification - PS- Table 21.7. PS- Table 21.12, AS/NZS 2566.2/2002
1e0a314c-d559-5b45-be17-16935aacf9ec | note | Verifying Document - Lab Test Report
8318e27d-7abb-52f0-aa95-784b8c93cb57 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole.
42c0682b-f1de-51f2-96af-1e7f0d9f103c | note | ○ 0-5m: 1 Tests
cbad12a8-c336-56ca-8dba-a090b934cfad | note | ○ 0m-10m: 1 Tests
47648d79-369a-5ba8-be0b-49c4d485e448 | note | ○ 0m-20m: 2 Tests
9ead80b9-8aa5-5113-9974-900a39812bf5 | note | ○ 0m-50m: 4 Tests
a4761450-d00c-53ae-87f4-d836fb515cab | note | ○ 0m-100m: 6 Test
ae313561-afb6-5e12-8501-8433f6064499 | note | Verification Activity: Activity - H
0585439d-af8d-50e8-9e75-31cc6ceefe2e | note | Verification Activity: By - SE
6a6d5cce-9102-4e60-91b5-48841b4a7a69 | checkpoint | 1.5.5 - Survey
1cd870a1-06d7-51b9-8817-3e63f8e2feb3 | note | Detail - Surveyor to Setout
70eafa9f-a639-5bcc-b430-9d599c1f23c4 | note | Acceptance / Conformance Criteria - Vertical design Setout:
c578fbc5-444d-5e06-9039-12f38ebd486f | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
38804002-e67d-50a0-8737-96bf122f1c32 | note | ○ Pipes > 1% grade: +/- 20mm variance
bd1a64ba-8351-5616-945c-bc6e55542f00 | note | Horizontal design Setout:
0a052d36-449d-51b0-84a3-cc396a21d5c6 | note | ○ +/-30mm variance
d59e00d5-46bc-54ba-9a29-3c635ef741e3 | note | Standard / Specification - PS- 21.7.6, Table 21.15
62c334ce-67a3-5223-be11-181fb4168741 | note | Verifying Document - Survey Data
dec7f80b-48b9-54f0-9896-988efa80ed3d | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
f4c53f68-ef8a-5991-9a1f-16e5fa089977 | note | Verification Activity: Activity - H
499691a4-cf9a-5b6d-93fb-e9d5d8efb2cb | note | Verification Activity: By - SV
beda0927-ed15-49f2-aad4-5a49fce0cc44 | checkpoint | 1.5.6 - Backfill Compaction Testing
0ece060a-c6a6-550f-ae6f-b0ca429237bd | note | Detail - On Granular or Cohesive Material
2cf4dae0-67a3-5511-b1be-74811fd560c3 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65
de437d89-1753-535d-914f-03849b7e2a94 | note | ○ Backfill Compacted in 200mm layers.
4ad80bc2-d7a9-5242-a2cc-572db4ff3764 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
9a95282c-66cf-5ea2-9f74-fe077afdb482 | note | Standard / Specification - PS- 21.6.12, Appendix V
353489ea-d367-5283-a791-c8af10e28a8b | note | Verifying Document - Lab Test Report
0307a37c-ef56-53e6-bf8e-cca9a94c6eda | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole.
563d0b46-9651-55d1-abdb-50c20b52981a | note | ○ 0-5m: 1 Tests
76f0f0d6-5f0a-5d15-a1c4-cef9e9eaa12b | note | ○ 0m-10m: 1 Tests
fac98e3c-2d3f-5540-a0d9-c5ac68dbc872 | note | ○ 0m-20m: 2 Tests
009ae553-4784-513c-91d7-9c29c0aad035 | note | ○ 0m-50m: 4 Tests
2cea7500-b836-5cf6-bea0-df701b086a03 | note | ○ 0m-100m: 6 Test
7665f11e-0068-5e53-976a-60ac8f841a07 | note | Verification Activity: Activity - H
e4c705da-8fe0-5401-b7a2-395db72c9b30 | note | Verification Activity: By - SE
4a82f6f0-5fd6-41f7-ab5a-086e05d6066e | checkpoint | 1.5.7 - Pipe Inspection
adeefd12-12e8-5344-8556-02775b23de3d | note | Detail - Inspection of Drainage line
c4bdce43-e672-5aa7-b4e6-a2d0de74d584 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place.
a3ca49b5-61f6-55d6-9a65-9dfb76aad7c0 | note | ○ Check for gaps and/or defects and check pipe alignment for straightness
9870d81d-f277-5496-9f35-954c12d10209 | note | Standard / Specification - PS- 21.7.6
7de63379-c512-5bf2-81f5-e3c3c8d751f2 | note | Verifying Document - Drainage line record
60c2159e-17a8-5257-8af3-f28cd8717275 | note | Testing Quantity Required (based from schedule qtys) - Continuous, 1 per Line
215585ac-84e5-551f-8eec-d2bceadf1ea5 | note | Verification Activity: Activity - I
b6e5e62d-bf4b-5c54-9896-450424d69290 | note | Verification Activity: By - SE
5098333f-b1f2-4fb2-bdbd-bd6705741763 | checkpoint | 1.6.1 - Settlement Monitoring
9ab273f2-d0c2-5c59-860d-63096aa807fd | note | Detail - Settlement monitoring with installing the settlement plate at underpass foundation level and as described in PS 18.5.4 during the construction at various levels.
32c593fd-f4fd-5e6f-81cd-b31bc9b3df54 | note | Acceptance / Conformance Criteria - Settlement monitoring done regularly after completion of foundation, on completion of precast installation, on completion of cover fill, on completion of finish structure.
11147817-30a5-59fc-91a7-fef472bd7b5a | note | Standard / Specification - PS 18.5.4
83c0c449-1483-55a5-a279-c4236a036770 | note | Verifying Document - Installation of Settlement plates/Visual Inspection
05202b70-f054-52f5-9d36-293e902fd939 | note | Testing Quantity Required (based from schedule qtys) - as per construction sequence per PS 18.5.4
7554c2d7-e688-5be8-88e9-d7614ebfa08f | note | Verification Activity: Activity - I
52af0cfb-d5ad-5709-9658-e2ac78c8114f | note | Verification Activity: By - SE
7e7b0425-1cea-4d85-a51e-47aec741c801 | checkpoint | 1.6.2 - Placement of Geotextile
00e294f0-252b-5803-93cf-3ce1d395f81a | note | Detail - A layer of Class C Geotextile Fabric to be placed between cut surface and imported A1 Structural Fill with 500mm overlaps
6b4af9bc-7516-507d-9fb8-c7b0daa72025 | note | Acceptance / Conformance Criteria - Visual Inspection
297f8f30-128f-5fc3-8ee8-3d814f9f97ae | note | Standard / Specification - NTC084
708d07a7-f47b-54e2-a7c8-d95569d42957 | note | Verifying Document - Visual Observation
48a2b78c-544f-5da9-ab49-f5c001d04237 | note | Testing Quantity Required (based from schedule qtys) - As Required
0259cc79-c61e-5dc1-ac97-abe31230e87e | note | Verification Activity: Activity - I
6eb1bc75-4ca6-5812-9408-8f3ac7750361 | note | Verification Activity: By - SE
753bb261-4be3-45aa-ba40-5836cc15e71f | checkpoint | 1.6.3 - Compaction - Clegg Hammer for GAP65 & AP40
3407b06f-b7ec-5ce3-9ccb-91d68c726119 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
77f69b77-c171-54f6-ae71-1aef17c735bd | note | Acceptance / Conformance Criteria - Structural Fill
20fc8612-5f23-548a-88c5-c882ca737028 | note | ○ Min CIV 18
e2864c38-4608-5f29-aedc-9f2cc4ff0c87 | note | ○ Ave CIV 20
a6e77705-22a6-5bdf-bd5c-587b902deebf | note | Standard / Specification - Appendix XVIII
0f725119-6faf-54c5-8a94-d1ebc129d963 | note | Verifying Document - Clegg Hammer Report
6df0a4a4-1028-5927-9ff8-e58ecb7a594e | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
0675c4e1-b656-55b1-8444-235b03960aa4 | note | Verification Activity: Activity - I
7645cbe0-c842-5197-beb8-d6660992e759 | note | Verification Activity: By - SE
e88f547e-3776-4d3d-8204-cebbc1b5d70d | checkpoint | 1.6.4 - Placement of Geogrid
b2975911-af36-523e-a6a7-74596419e05d | note | Detail - The Durargid X 40/40 Geogrid shall be placed on top of the GAP65 layer and the first AP40 layer.
ed04be36-abf8-5259-9aec-3aa7bfef814d | note | Acceptance / Conformance Criteria - Visual inspection
be12496c-5d4d-53eb-921d-539f36ccfd78 | note | Standard / Specification - STR Drawings Sheet 203
2c563733-746e-567e-b267-921c59469b30 | note | Verifying Document - Visual Inspection
a7dfc397-9a7a-5291-a89d-b900c00cb754 | note | Testing Quantity Required (based from schedule qtys) - Across gravel raft
8bb6db61-b6a3-5e2e-909f-52f128bae1eb | note | Verification Activity: Activity - WP
5ba5a8c8-b230-5aa2-b560-7b00a3c0e34c | note | Verification Activity: By - ENG
09af1979-c0eb-4464-a1c5-d490d3ebf876 | checkpoint | 1.6.5 - Compaction - NDM on top AP40 layer
86eb0b4d-46c4-5cc0-a2dc-1761af70f049 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
4f119d60-fe61-5d87-94cd-8182a0e7a991 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
45701040-3a75-57e0-baf1-4a9542cbcee5 | note | ○ Min >92% of MDD
97a78d24-612c-5f07-bde2-59ab67752b28 | note | ○ Non Granular Material
08c34fad-8ea0-5087-88e2-ad9c21554a32 | note | ○ Max Air Voids 8%
7d3a2816-5482-52fd-9feb-c17a3a655e91 | note | Standard / Specification - Appendix XVIII
6a814472-c8cc-5cec-9b85-ef0d80e4b3c7 | note | Verifying Document - IANZ Accredited Report
06dd1acf-4757-5203-8cf6-0f3b5628701d | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) on last lift of AP40
4790c63b-148c-5515-8989-9053dcef6dff | note | Verification Activity: Activity - I
5be44172-93e4-502b-a97c-6a9ab138002d | note | Verification Activity: By - SE
d00539b7-a37e-4a54-86fc-99c174064fa8 | section | SECTION 2 – PRE-CONSTRUCTION - MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
98ac3291-8fcb-4b79-a303-a5f78034f153 | checkpoint | 2.1 - Reinforcing steel and Strands
6ee5e622-1e47-5aec-bfe1-908d6e21d166 | note | Detail - All Reinforcement bars and strands used in structural concrete to be approved by the engineer prior to construction.
8b079b6e-8507-579d-8bf2-a755f268ba16 | note | ○ Post tensioning strand to be high tension ASTM galvanized and complying with AS/NZ standard
2d69da43-7f09-5cb3-9809-1b421c23b305 | note | Acceptance / Conformance Criteria - Test certificates shall be obtained from the manufacturer for all strand, cable and bar to be used in the work and copies shall be forwarded to the Engineer at least one week before the programmed commencement of any work incorporating these materials. Test certificates shall be traceable to the batch of material supplied to the work.
8a2fd099-fe8f-53bf-b44a-d1695de6e219 | note | ○ High yield steel, Grade 500E, Seismic MA.
df4c4f93-d326-5469-8deb-23163b32cf3f | note | ○ Post tensioning strand to be high tension ASTM galvanized and complying with AS/NZ standard
b787fca1-167a-5db8-8f82-e7b44e5e96a7 | note | Standard / Specification - PS 18.3.3, 18.5.7 and 19.13.1
c1195fa5-e62a-53c1-b80b-cd2bb33668fc | note | Verifying Document - Supplier data sheet/ Mill certs
cad8bb9a-6298-5693-884b-728e8dab0575 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
7be52d19-6068-5b4e-a8d0-b5413a876870 | note | Verification Activity: Activity - HP
54577b7f-abee-52aa-adc7-6c4444ac6907 | note | Verification Activity: By - ENG
c930413a-f551-4011-841c-9e75a2884b0e | signoff | AUTHORITY HOLDPOINT
054664b9-4677-4549-87cc-8f7f88ea4038 | checkpoint | 2.2 - Concrete Spacer Blocks
40a291eb-2760-5b32-89f2-8f062ef5089f | note | Detail - Reinforcement cover spacer blocks shall be either made from concrete with a specified strength at least 10mPa stronger than the surrounding concrete; or Plastic spacer blocks.
7ae311f7-9c11-5f7a-aba3-46a0058cbd84 | note | Acceptance / Conformance Criteria - Concrete cover spacing blocks = at least 10mPa stronger than surrounding concrete.
f4292a3a-786b-5597-bfa3-539575c39e76 | note | Standard / Specification - PS 19.3.2
3d49c541-bff7-539f-9bcb-bbd73b622bde | note | Verifying Document - Supplier data sheet
f2270a73-7eed-5078-be2a-1d5d4ee78d91 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
0ead33a5-aae0-51f4-84b3-af4bf0dd8aab | note | Verification Activity: Activity - I
3a47b668-a67f-51d3-9820-75ea5b3f990c | note | Verification Activity: By - SE
6d19217b-ae81-4598-a21a-0d06112e60fd | checkpoint | 2.3 - Concrete mix design
2d9b1435-2e86-5496-8db4-81786a1c97ef | note | Detail - Approved mix design - Concrete shall be of the class as defined by NZS 3104 have a minimum 28 days compression strength as specified for various members: for underpass apron pour: 40mpa
c155e949-e408-5442-869a-fa6076b7a67d | note | Acceptance / Conformance Criteria - 28 Day concrete requirements: UNDERPASS APRON POUR: 40MPA
19e29b6d-60e4-55a5-93e7-93a0129dbd29 | note | Standard / Specification - PS 19.3.3
c3fd48a1-0ea1-59e2-bd1f-2c2b4b3a124f | note | Verifying Document - Approved Mix design
1776dea2-fe02-550f-b7af-acfebaec49f9 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
d4ecf044-8714-5243-a147-86e522207e77 | note | Verification Activity: Activity - HP
e6c009fc-538e-5bbd-8257-8dde660e675c | note | Verification Activity: By - ENG
af78300d-bc80-4bef-bd3c-eb3daf8d766a | signoff | AUTHORITY HOLDPOINT
112d5e6f-6a38-4b93-98c7-8fa5aa205502 | checkpoint | 2.4 - Shop Drawing Approval
28134cf2-3f94-5607-ae04-8972ca7e5f0a | note | Detail - Shop drawing review and approval from Engineer and Production QA Records to be submitted
5dd2acf6-c9fb-5aa6-adfb-3964a0af4d64 | note | Acceptance / Conformance Criteria - Send shop drawings to the Engineer for review, at least 14 days prior to manufacture. Any variations between the Drawings and shop drawings shall be clearly identified and brought to the attention of the Engineer.
52276d51-53b3-58c9-bff0-7c06447b4b0b | note | Standard / Specification - PS 19.12.6
c911f45f-e747-5235-ba32-499fc2340fe8 | note | Verifying Document - Shop Drawing Approval, QA records
ccacee30-b42f-59cf-bd71-a4b54e5ac82d | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
4c51dc64-cc6b-5e60-96a5-ff9166dfe6f3 | note | Verification Activity: Activity - HP
1e401908-a478-54cc-bf78-1437b6d84622 | note | Verification Activity: By - ENG
2f239c55-e127-40bb-983f-51ea9acb6428 | signoff | AUTHORITY HOLDPOINT
347fc3f6-5078-4d12-9b92-c160e23445f6 | checkpoint | 2.5 - Anti-graffiti products
c210295e-c36f-5044-a9a7-804652249d5c | note | Detail - Permanent (not sacrificial) anti-graffiti coatings shall be applied to the exposed faces of all concrete surfaces including wingwalls. The coatings shall have a design life of not less than 10 years. The Contractor shall submit the proposed extent of application for authorisation by the Engineer.
e8a85e98-fb32-5a55-8764-1bec862cb1be | note | Acceptance / Conformance Criteria - Permanent (not sacrificial) anti-graffiti coatings shall be applied to the exposed faces of all concrete surfaces including wingwalls. The coatings shall have a design life of not less than 10 years. The Contractor shall submit the proposed extent of application for authorisation by the Engineer.
65cbfd85-113d-5c05-a89e-696679902480 | note | Standard / Specification - PS 14.7.1
14a8414a-1f36-593f-95ca-4b2630562be2 | note | Verifying Document - Details of pre qualified product
9e4acfb1-9e70-5118-a277-4955791080a5 | note | Testing Quantity Required (based from schedule qtys) - Prior to Application - Engineers Approval
dee39587-1844-5b4d-b54b-e0ae387782ac | note | Verification Activity: Activity - HP
aa3b591e-5d75-5d97-be98-253a708bd6c2 | note | Verification Activity: By - ENG
eddb478f-fd43-45e0-bd2a-0ab7a4df6900 | signoff | AUTHORITY HOLDPOINT
de1219a8-7346-4686-86a3-93830b04b437 | checkpoint | 2.6 - Joint Sealing and Waterproofing Sealant
3b3406a4-fe7c-552b-a12b-0bb9029efe32 | note | Detail - Pre approved joint sealant meeting the specification requirements
babdf75a-97d4-50ad-b6c3-dc60194d4a02 | note | Acceptance / Conformance Criteria - Joints are to be sealed using a fuel resistant, multi-component polysulphide sealant designed for horizontal and vertical joints in concrete and is joint sealant pourable or gunning grade as appropriate.
5e7e3c69-0ce5-5fb4-8bdb-f976a5d88e98 | note | Standard / Specification - PS 19.12.6
da0d4644-d3e1-5f65-94aa-eef6020bd4b6 | note | Verifying Document - Delivery dockets and supplier data sheet
aaa11a3e-e381-5e2b-90d5-dd0215db4fca | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - Engineers approval
b3201498-86d2-5b0f-a925-af184133c362 | note | Verification Activity: Activity - HP
0efdf45a-058d-5193-bf43-506ab8082958 | note | Verification Activity: By - ENG
2dd7e97d-5551-4ebc-94a6-150f91f7c794 | signoff | AUTHORITY HOLDPOINT
3a6fea7d-6e89-4f82-90e7-5898dd0f59c8 | checkpoint | 2.7 - Compressible filler board
cd6241a8-a7bc-50db-82c4-8911efbd19ce | note | Detail - Compressible filler board specification to meet the project requirements.
93f534c0-5787-5cef-9c3c-9eb4e653eb26 | note | Acceptance / Conformance Criteria - Details of the compressible filler board proposed to be used as a construction joint shall meet specification requirements.
d55176a6-0b21-55b5-ba57-50ccce15cd7e | note | Standard / Specification - PS 19.12.6
0b18717e-65d9-5900-b9e2-2b03041de7e9 | note | Verifying Document - Delivery dockets and supplier data sheet
768a2b11-128d-5af9-babb-c4d2a1b63b76 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6550a22e-67ad-59b0-8d52-c00f68d041c1 | note | Verification Activity: Activity - I
7d266dc1-f48e-507e-905e-e70b4299ec11 | note | Verification Activity: By - SE
2697b654-750c-4ff8-aa49-4f6626ff73ba | checkpoint | 2.8 - Application of Non-Slip Coating - Sikafloor 91 or Sikafloor150
28b71e12-8a73-5ee8-81c0-43e983b63249 | note | Detail - Proposed product to be approved by Engineer
741009c7-be12-59a0-9e15-2d8fe1278e3f | note | Acceptance / Conformance Criteria - The top of the underpass floor slab and bottom chamfers will have Sikafloor 91 or Sikafloor 150 applied after the installation of the box culvert segments. The thickness of this is to be between 3 and 5mm. The application of the product must be done in accordance with the manufacturer’s specifications.
9adbff8c-ab5b-53b5-8ced-b217bc2e5317 | note | Standard / Specification - PS 19.2.4
a0406e4f-e678-5eb4-aba9-e485a35f3307 | note | Verifying Document - Product data sheet
ed52e13a-496a-573e-9c0b-0dd3604a6802 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
3f6448ae-b28a-5a5c-aa54-daf731b65f13 | note | Verification Activity: Activity - HP
8fa51e85-e480-5fd4-91a9-b0c57e94ba14 | note | Verification Activity: By - ENG
cb56397e-bbd9-4f9a-a88f-e2763b64fda0 | signoff | AUTHORITY HOLDPOINT
ef3bd09a-5ad5-491b-b32b-eafa8dea5b3f | section | SECTION 3 – CONSTRUCTION ACTIVITIES - BLINDING AND PRE-CAST POUR
743821ff-023a-4216-96c8-0465bcf4c605 | checkpoint | 3.1.1 - Setting out of Underpass Blinding level with 1% fall towards Northern end
da107dbd-ebc6-548e-bdce-ab234bbbba1c | note | Detail - Setting out boxing and complete site checks as concrete is poured to ensure flat surface for placing precast units
8991ec2a-175c-573b-9022-788568cb84ea | note | Acceptance / Conformance Criteria - Site supervisor verification
f4d5ef9a-b56c-59f3-b19d-8957e8abf1e4 | note | Standard / Specification - PS 18.5.3
601aab22-e044-5f64-967c-750de51dbfe0 | note | Verifying Document - Visual inspection
b3fdecdd-20fc-5492-a180-5accd09136c1 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
7a07d5f2-753f-524c-a259-c02af50dfdad | note | Verification Activity: Activity - I
972f6d69-24d8-507b-aa62-0a0486ab05cc | note | Verification Activity: By - ENG
bb27ef25-7e0a-4f33-aa0b-5b3fa71eb456 | checkpoint | 3.1.2 - Blinding Concrete
566e16dd-4b63-5501-9555-df90b7526c52 | note | Detail - Concrete Compressive Strength on 28 days to gain min of 10MPa
07aa5203-90f3-5bb0-a29a-eb347cc827ab | note | Acceptance / Conformance Criteria - Blinding concrete shall have a minimum 28 days compressive strength of 10 Mpa and comply with the requirements for prescribed mix concrete specified by NZS 3104
c1ff74e2-1afb-5816-8cc4-e001cd452b7e | note | Standard / Specification - PS 19.3.3
62fa7ccf-e9fd-5a0e-80be-9b8ad7c1cc74 | note | Verifying Document - Concrete Delivery Docket
31fda7e1-0ba5-5e3b-b01f-c93a69a86fac | note | Testing Quantity Required (based from schedule qtys) - During construction
4fbac7e9-eed8-5404-b5f8-fbe847e41803 | note | Verification Activity: Activity - I
f49fd7d8-a07a-572f-94db-1b2498e04b1d | note | Verification Activity: By - SE
c04c514d-9fb7-4444-aaa0-39ad4a3daad1 | checkpoint | 3.1.3 - Setting out of positions of the Underpass units
8b2bb112-121b-5c1a-aaed-64fe529a0e91 | note | Detail - Setting out to follow design coordinates and levels within tolerance as specified in PS 18.5.3 by approved licensed surveyor to certify the Set-Out positions.
aca4d159-3362-5644-a4bb-b21523482828 | note | Acceptance / Conformance Criteria - Engineers Approval
102cfe0d-fa65-5311-98b0-51bcdd33df81 | note | Standard / Specification - PS 18.5.3
ef75cc33-167a-5733-9f52-997c0a792375 | note | Verifying Document - Visual inspection
51bc48ac-bf65-5b39-a90f-a06b5e0b1603 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
6902b5a7-357a-5b04-88e4-540c8c52884b | note | Verification Activity: Activity - I
5fd546ca-d84b-572e-8d8f-e5b3aec6abba | note | Verification Activity: By - ENG
7d8cdb34-b9f8-4d3d-8620-0ff7caad10b2 | checkpoint | 3.2.1 - Forms and Moulds
11c8e98b-9a53-5ecf-aea6-9f7da49169ce | note | Detail - Tolerance on the placement of internal forms and moulds shall be +-5mm
33073ce1-2331-590f-be72-877f30a53e4e | note | Acceptance / Conformance Criteria - Moulds shall be rigid accurately formed and of sufficient strength and stiffness to prevent distortion under vibration.
0d4cebc9-9b7e-5516-b4d6-0064d688071d | note | Standard / Specification - PS 19.12.5
705f1538-5abe-52d9-9225-b9fe46afc3f3 | note | Verifying Document - Manufacturer QA records
e467ac5f-ffd3-56db-8620-e8243e0e7467 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
a71aed16-8a76-55c5-92f5-0079d755e766 | note | Verification Activity: Activity - I
e3b9a82d-6972-5407-b7c7-546b8661f899 | note | Verification Activity: By - SE
76d2c678-26cd-4103-95c6-7d5639b68f38 | checkpoint | 3.2.2 - Pre Pour Inspection
a4c4b271-3bd6-5fe1-86ac-129b80d950ce | note | Detail - Pre Pour inspection to check:
409e4cea-c55e-55e4-a987-ca3c28794195 | note | – Reinforcing
bbfe4b89-b369-5465-8852-89885a2c4ef9 | note | – Moulds
ec274a89-ad2d-5507-83ca-56a47c0b3562 | note | – Cover Spacer Blocks
16efd87b-5b2c-5d7e-97cf-89f1276abd2f | note | Acceptance / Conformance Criteria - The Engineer shall be informed 8 hours prior to the casting of any unit, to allow the Engineer to attend the pre-casting plant to inspect before and during production of the units.
46f51f83-86de-5e90-a2e4-8d2858148dfc | note | ○ Reinforcing shall be pre assembled wherever possible into rigid cages using a template or jig. Reinforcing shall be tied together with wire unless otherwise accepted by the Engineer
380ea89e-831d-52b9-a9a1-57563c7799c9 | note | ○ Confirm correct type and location of cover block is used.
8bae5121-0038-54a0-b70e-67dd06e95772 | note | Standard / Specification - PS 19.3.2, 19.4.3 & 19.12.3
51162623-9a26-5e86-bfe9-db9eba5940e3 | note | Verifying Document - Pre pour inspection checklist, Manufacturer QA records
d0417c94-c97b-50c6-a501-32e74feda823 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
4b1a5982-bc2f-5763-a1ed-32bf66e7c059 | note | Verification Activity: Activity - HP
e64ca039-8c89-50c9-886b-4d8a567911fe | note | Verification Activity: By - ENG
fb5b8559-ed9a-4c02-bfbd-b666f62c1ac9 | signoff | AUTHORITY HOLDPOINT
f542d24b-d3ea-4c94-b99a-05c42215516f | checkpoint | 3.2.3 - Concrete sampling and testing
36aaa947-c97c-593a-a4fc-2e27217c206a | note | Detail - Pre cast Methodology from Pre co to submit to Engineer and Compression Test Report
469273a4-dee2-5800-82ed-7314a28f71ec | note | Acceptance / Conformance Criteria - For pours under 150m³: three standard cylinders shall be made for each 50m³ of concrete placed, or part thereof, for testing of 28 days compressive strength in an approved laboratory.
091e3fab-a089-58f7-b22b-8d814723378f | note | ○ For repetitive precast underpass units with 6.42m3 each pours undertaken on a regular basis, three standard cylinders shall be made for each of the first five pours of any one type, and thereafter three standard cylinders shall be made for every fifth pour of that type for testing of 28 days compressive strength in an approved laboratory.
62f7f6c2-a59a-526c-b063-c6b862cb46e0 | note | Standard / Specification - PS 19.4.3
6f46bbda-91f6-5ef1-be30-0d715d7e3d07 | note | Verifying Document - Slump Test/ Compressive strength test Report at 28 days/Pre pour inspection checklist
89bc52a1-495e-5f19-a18f-93453754ecc9 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
9f958ada-543d-53f1-879f-98808994175d | note | Verification Activity: Activity - HP
657f490e-85d8-5b07-8eb6-f0557b0595aa | note | Verification Activity: By - ENG
c700d85c-6232-4e9b-8bc1-19ede21ec0c5 | signoff | AUTHORITY HOLDPOINT
b2aea290-4700-4434-9e95-80fba8abc8e9 | checkpoint | 3.2.4 - Surface Finish of pre cast concrete Units
8f8b150d-e826-5d52-a573-8f5ffccb08ee | note | Detail - Surface finish to comply the requirements for pre cast concrete units.
0cf1de62-1c3e-571f-b892-4879defbcdbc | note | Acceptance / Conformance Criteria - For all precast concrete units all surfaces except those against which concrete will be subsequently placed, shall have a concrete surface finish complying with the requirements of NZS 3114, F4 finish for formed surfaces and U3 finish for unformed surfaces.
8efac5ed-e8c8-5945-b78b-64ce498b476d | note | Standard / Specification - PS 19.7.1
02eccc6f-a59d-5c63-a6bc-90aee7aa8b43 | note | Verifying Document - Visual Inspection
51237cd1-2d26-532b-84d9-33326dae53b8 | note | Testing Quantity Required (based from schedule qtys) - Each Item
f028b363-a603-57c0-bdc8-d7c998cbc8e5 | note | Verification Activity: Activity - I
49da067e-58f9-541e-9684-761267356be6 | note | Verification Activity: By - SE
ef9a936b-49b4-4283-8526-0d5b481d9ee1 | checkpoint | 3.3.1 - Post Pour inspections
3af22d0c-fd8d-5794-b861-a20191bc0a06 | note | Detail - Post Pour inspection
80ee11aa-abbd-5a5c-9974-033520bc6bc8 | note | Acceptance / Conformance Criteria - Following the concrete pour and stripping out form works: the concrete shall be inspected for Size, Shape, Features, inserts, reliefs, and Finish against the drawings.
a55727af-a0f2-513f-954f-996dfb62bf79 | note | Standard / Specification - PS 19.3.1
205d056b-583b-591e-b215-6ed717f32959 | note | Verifying Document - Visual Inspection/Post pour checklist
6c865795-6974-52e0-a1e4-5e6859f79a4a | note | Testing Quantity Required (based from schedule qtys) - Each Pour
2ab43b02-f61b-5091-a8dc-c50b224e8a65 | note | Verification Activity: Activity - HP
8fadb844-0327-5704-919d-831f77c37a11 | note | Verification Activity: By - ENG
26a55d1e-79d5-4d2a-875c-f0aa45d141f1 | signoff | AUTHORITY HOLDPOINT
ab880dad-4e87-48d0-bb94-48b3dc48b874 | checkpoint | 3.3.2 - Defective Concrete Finishes
901f00d6-f99d-5fd4-a30f-278c0de647fd | note | Detail - Repair of defective concrete finish other than that due to minor porosity of the surface shall be carried out only when approved by the Engineer.
88d8dfd8-67b4-5d27-b087-5af5dd2280a9 | note | Acceptance / Conformance Criteria - Repair of defective concrete finish other than that due to minor porosity of the surface shall be carried out only when approved by the Engineer.
7d93d3eb-172e-52c5-ad9f-ac0d075a138c | note | Standard / Specification - PS 19.3.1
abe0ce5a-6fbb-5e6d-9fd0-7573c58cc427 | note | Verifying Document - Visual Inspection/ Post pour checklist
64938b64-e8a3-5194-a13a-5bd373df6903 | note | Testing Quantity Required (based from schedule qtys) - All Concrete Elements
a0f6c396-5a1d-5488-9f5b-ebd7f5ed45fe | note | Verification Activity: Activity - HP
f6ec05d6-5373-5bcc-9aff-16259a71f1ff | note | Verification Activity: By - ENG
a7f61ff1-9c2e-4b05-bede-ee9a714b2a42 | signoff | AUTHORITY HOLDPOINT
8c5eb30a-6314-46c5-9c85-1f6bfc4d2bed | checkpoint | 3.3.3 - Joint Sealing of Pre cast members
1aefbf62-b47a-50cc-b9f8-0edcfa1cbda8 | note | Detail - Joint sealing of pre cast members
76b3906f-be09-57bf-a11c-9d910a743cd5 | note | Acceptance / Conformance Criteria - Joints are to be sealed using a fuel resistant, multi-component polysulphide sealant designed for horizontal and vertical joints in concrete and is joint sealant pourable or gunning grade as appropriate.
bc6ad653-9b56-5a4f-a3f5-b8cdbb5a4c1e | note | Standard / Specification - PS 19.12.6
ec666cfd-8d31-545f-887d-32cd7d8fb27d | note | Verifying Document - Post installation inspection check list
57bec8fa-b74c-5853-a2db-1fa4e5f13504 | note | Testing Quantity Required (based from schedule qtys) - After placing pre-cast units
c92aa63b-aeec-5dd6-9861-b58db6f729a7 | note | Verification Activity: Activity - I
a5f3a0ed-35b7-55c9-8b40-17275e59ee88 | note | Verification Activity: By - SE
c547d492-7791-4678-b19a-9c2e897d1999 | section | SECTION 4– CONSTRUCTION ACTIVITY- POST TENSIONING OF UNDERPASS UNITS
4b3e96cc-b7cd-4059-b926-e9de5444999f | checkpoint | 4.1.1 - Detail methodology for Post Tensioning of Stage 1 of underpass units to develop and send to designer for approval
b6532d1f-31ac-5f80-8b27-5c02ec716b46 | note | Detail - Detail method of stressing
31c8e749-af8d-51b2-bd20-9ef4cbd19dd4 | note | Acceptance / Conformance Criteria - 1*15.2 Galvanized, greased and sheathed strand per corner (Ungrouted) to be inserted in each corner for stage 1, 16 units of underpass.
72be10b5-b9f6-58a9-9e25-d0968ba269f6 | note | ○ Both ends will have a 40mm rebate for grouting.
ff81736b-92f6-50f5-ab2f-77d338b7daa9 | note | ○ And those strands will be tensioned to meet the project specification.
3e3855a8-973f-58b4-9f9c-bf406378fd6a | note | Standard / Specification - PS 19.14.1
6120e120-c076-5557-8c98-263e865ec928 | note | Verifying Document - Method Statement
50856ec0-211d-56c9-beb7-ff56ab87eb75 | note | Testing Quantity Required (based from schedule qtys) - Before installing units
d1450bba-53c3-556a-9b73-a98abdbf4940 | note | Verification Activity: Activity - HP
340e5539-766a-5640-a815-200e433c4221 | note | Verification Activity: By - SE
99af2022-6107-4b9b-93e2-882ac41c9512 | signoff | AUTHORITY HOLDPOINT
91e514be-2f6d-40d1-8952-ad778e899a4a | checkpoint | 4.1.2 - Detensioning of stage1 underpass units for Stage 2 construction
27868745-3f1f-5854-b3cb-d77d03b4b1ef | note | Detail - Detail method of stressing
a75d5579-b6f2-55e8-8d0e-fdebfcd046a5 | note | Acceptance / Conformance Criteria - Detensioning will be done on one corner at a time, remove wedges via special pocket pull new strand and tension.
e11626ae-7955-55b5-9cc0-80430dc8bb71 | note | ○ This will ensure at least 3 corners remain under tension at any given time.
ddc48088-4995-5eb6-90ac-53f6d8f77fc5 | note | Standard / Specification - PS 19.14.1
85900feb-bcec-5a7d-a8de-495a8aa820e1 | note | Verifying Document - Method Statement
05db36fc-1143-5d4a-ba92-32eca6df128b | note | Testing Quantity Required (based from schedule qtys) - Before landing stage 2 units
953591ce-2dfb-598c-bfec-c1ec9c6569c6 | note | Verification Activity: Activity - HP
fef0c05c-f23a-545c-b2b5-23d090154eee | note | Verification Activity: By - SE
f071a83d-4bae-4420-99b8-adf4912bdf6c | signoff | AUTHORITY HOLDPOINT
c9acdfb6-da11-480c-9718-28d50b055f41 | checkpoint | 4.1.3 - Stressing Operation
bab6b2c6-7a6e-5b0b-97d2-a0d1519bc99e | note | Detail - Post tensioning of strand to be done not to exceed 80% of maximum ultimate breaking strength. Post tensioning strands to be stressed simultaneously or following the sequence of stressing as noted on shop drawings.
788e0d38-a00e-5b00-ae34-687325d9db78 | note | Acceptance / Conformance Criteria - Stressing forces shall be as per NZS 3101 section 19 for maximum permissible levels of force within a strand during and after stressing. In no case shall a strand be stressed to greater than 80% of its ultimate breaking strength.
9643bbce-20aa-5e48-9b31-343803549e3a | note | Standard / Specification - NZS3101 Section 19 PS 19.14.1
210d969f-8019-5d03-877e-d947873ca451 | note | Verifying Document - Method Statement
1fbfe15a-19d5-52d2-980e-a17d1bb48aaf | note | Testing Quantity Required (based from schedule qtys) - All units for tensioning
cf72f6d7-17ba-56fd-8f0d-6dbe62890225 | note | Verification Activity: Activity - HP
678bf252-cb56-5a1a-952a-81efd10ab685 | note | Verification Activity: By - SE
602d350f-6d14-4cfa-be7c-4f7a01a7fb0b | signoff | AUTHORITY HOLDPOINT
391cc4d0-27f2-4f28-80be-93b70840dea9 | checkpoint | 4.1.4 - Concrete Strength at time of stressing
49e1119f-0cb0-54f1-9ae5-457c104dd442 | note | Detail - Samples taken during construction of concrete member to be tested for compressive strength and the results shall be used to determine the acceptability of the structural member for stressing.
b6ce2c3a-a12d-56f0-8a6b-13eb92b1da43 | note | Acceptance / Conformance Criteria - The minimum compressive strength required before stressing shall be 30MPa unless noted otherwise on the drawings.
8400ef00-3c23-5fad-9eb0-e2a34536470f | note | Standard / Specification - PS 19.14.1
bba88764-998c-532e-a36a-84317772f629 | note | Verifying Document - Concrete Test Reports
dd934fd1-adcf-5c02-8401-5176969b7f8b | note | Testing Quantity Required (based from schedule qtys) - as per test report in section 2.2.2
159f1885-3efe-51bf-9277-de4b54028d92 | note | Verification Activity: Activity - HP
6a4331a0-8f57-5276-94f0-feb9bdc73488 | note | Verification Activity: By - SE
c4240516-9180-4a35-af5b-5548fb73fb21 | signoff | AUTHORITY HOLDPOINT
271c0361-0225-4204-9952-09fef53e8b3f | checkpoint | 4.1.5 - Stressing Calculations
ec01499d-cbd5-5a4e-97eb-f7783c83b0b4 | note | Detail - Calculation done will form the basis of comparison to the actual stressing results recorded as an indication that the appropriate levels of stressing are being achieved in each strand.
8af9c0ec-8220-5041-9ce7-c183c533ae8a | note | Acceptance / Conformance Criteria - Theoretical calculations for each strand size and profile to determine theoretical jacking forces and corresponding theoretical elongations.
9b9a6c76-d37c-5dbe-8bd4-05dbb108bd04 | note | ○ These calculations shall be based on the assumed property of strand and forwarded to the Engineer for review and approval at least 7 working days prior to the stressing operations commencing.
bbf19dbf-e342-5604-9cf9-49de8ce94589 | note | Standard / Specification - PS 19.14.1
03208da9-adc2-5af1-a505-80cc95d7a659 | note | Verifying Document - Calculation data sheet
29d15933-8fb1-51e6-92c3-28db7df794d1 | note | Testing Quantity Required (based from schedule qtys) - All units for tensioning
63883fdd-295b-598f-876d-427dc85f8fc7 | note | Verification Activity: Activity - HP
9712cb12-53a1-5803-8144-2966f82f403d | note | Verification Activity: By - SE
53e183f5-5ceb-486d-916f-dcbf44e8ca36 | signoff | AUTHORITY HOLDPOINT
e4504edc-9c9f-4828-9cd0-f0e3852bf700 | checkpoint | 4.1.6 - Protection of Strands
a08f0595-5198-5794-9aa4-1756acd2d54e | note | Detail - Post tensioning strands shall be cut flush with the end faces of the pre cast unit (including any recess) unless noted otherwise on the drawings. Gas cutting of Strand is not permitted.
6f5745eb-927a-5143-9467-fe01acb6c4bd | note | Acceptance / Conformance Criteria - Cut ends of the strand sealed and protected with minimum of 5mm of epoxy mortar or a coat of high build epoxy paint.
b3e238f2-1dd7-5583-9333-cf58fdc9837e | note | Standard / Specification - PS 19.14.1
51ae7e2b-59c8-5496-ab86-dc73312001a9 | note | Verifying Document - Visual Inspection
eeb1c7b1-4010-5db5-ae5d-d520150e3bbd | note | Testing Quantity Required (based from schedule qtys) - All units with Strands
08b3f00f-6069-5ad6-8465-0a95a619aff5 | note | Verification Activity: Activity - I
1127bf7c-48a2-5c53-9252-c469717f64f5 | note | Verification Activity: By - SE
05f94978-8045-42cc-8184-b35f662547dc | checkpoint | 4.1.7 - Stressing Records
46da9cc4-f658-5e81-b422-9cda4c00f056 | note | Detail - Record of stressing shall be taken and reported to designer.
b7f1efc3-22de-5a5b-90c8-5a333ce51ba9 | note | Acceptance / Conformance Criteria - Stressing record as per PS 19.14.1 section IV, subsection I
baa29a25-c972-531f-9951-dab01df2ced6 | note | Standard / Specification - PS 19.14.1
fae6a2f1-b6fe-5199-b072-886c99a8d8ce | note | Verifying Document - Stressing records
c92109ae-44cf-5377-a5d5-cb32e2f87e36 | note | Testing Quantity Required (based from schedule qtys) - All units with Strands
3391ef56-9f28-5847-a914-200fbc8a9495 | note | Verification Activity: Activity - I
6717b9df-aaf7-5864-8142-29783163d0db | note | Verification Activity: By - SE
0c20247a-43fe-4d64-b29d-159a375fb0f8 | section | SECTION 5 – CONSTRUCTION ACTIVITY- UNDERPASS WINGWALL, DUCTING AND BACKFILL
2d8dbf3a-79ed-472c-bc86-6e0bdea01edc | checkpoint | 5.1.1 - Position Monitoring
9d4d376f-5792-591e-b049-dd2fea75b27b | note | Detail - Surveying to be done on the primary structural elements as their construction is completed, location of base slab, strip footing, roof of slab, top of wing walls
850ce3ff-078b-5249-a668-450b4fbd0b60 | note | Acceptance / Conformance Criteria - Surveying done as per PS 18.5.4 on various stages of the construction of underpass. Position of underpass as built and recorded
56ad3c4f-d78d-51a9-b723-ebfdcff2f3e0 | note | Standard / Specification - PS 18.5.4
e2498386-238d-5033-998e-2c72b1e4d2de | note | Verifying Document - Survey recording of position to the required tolerances
83cbee7f-e309-5f3f-81b4-51162fda9eda | note | Testing Quantity Required (based from schedule qtys) - When each construction step finishes
5049c4c8-db9a-57ff-978f-bf4b5ad223da | note | Verification Activity: Activity - I
345e81f4-4809-5ec6-a67c-92d0b3d1ca4a | note | Verification Activity: By - SE
d117ffb8-9fe4-4428-8b13-db3b74ec10ec | checkpoint | 5.1.2 - Placement of Geotextile on Cut Surface
4f4e44ed-e792-593e-9326-d974ef4e3f00 | note | Detail - Geotextile to be placed up the sides of the cut surface, with joints overlapped by 500mm minimum
9ace3f27-f864-55c4-9bb9-5773e6220ec5 | note | Acceptance / Conformance Criteria - Engineers Approval
4c17289c-f0cb-5897-a32d-e8b4c3ab3e74 | note | Standard / Specification - PS 16.6.4, TNZ F/7: 2003 8.3
d4f496bb-12a3-5c84-8414-7375ca46fbb9 | note | Verifying Document - Visual Inspection
21346a48-1f98-5ae7-9583-2cdb6faea446 | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
428515bc-0aa7-50f3-807b-b2df2144e9ca | note | Verification Activity: Activity - WP
8c52ebfc-5481-5105-a10f-133ceb95be38 | note | Verification Activity: By - ENG
4720299d-b74f-4bb7-95b6-92251043ffcf | checkpoint | 5.2.1 - Trench Excavation
12c458e6-5f63-56ac-98bd-1ea4a381545e | note | Detail - To be excavated to within a tolerance.
d6b0c441-49d1-5e49-a668-1015283d1965 | note | ○ Not more than 100 metres of trench associated with each site shall remain open at one time.
48798956-ffbe-5d4d-aa81-9596837d4532 | note | Acceptance / Conformance Criteria - +/- 100 mm of the planned horizontal.
da97c883-6c14-5db0-8a47-d2b5436b9cdd | note | ○ The maximum deviation shall be 1 in 20 in both the horizontal and vertical planes.
46eba14b-2c80-5fa0-a95b-2d9ba3e13370 | note | ○ Less than 100m
2839ef16-3858-5a27-b09e-cab445652ccf | note | Standard / Specification - PS 25.13.2 (Ai)
144f0dd6-6007-5621-bf4c-120d7625af77 | note | Verifying Document - Survey
cec979cd-1ae7-5d59-8fc9-4695e685adf0 | note | Testing Quantity Required (based from schedule qtys) - Every time
5098021c-e984-5930-be44-86e807c87eaf | note | Verification Activity: Activity - M
dc15560d-331e-5ed7-8d8e-514c95d54a5f | note | Verification Activity: By - SE
e315953f-7b5d-4c1c-ab61-383fa6dbff35 | checkpoint | 5.2.2 - Unsuitable Materials
4f96230f-e13e-5d8f-b920-f9da3b18fa02 | note | Detail - All confirmed unsuitable material shall be excavated down to suitable materials.
05b52d11-98e8-52a4-a694-738665227dec | note | Acceptance / Conformance Criteria - Dig Down to Get Suitable Materials or get Engineers Approval.
91175973-14d5-579d-9d61-9e9ceaa8ce2f | note | Standard / Specification - PS 25.13.2 (Bii)
b6f70c2a-efd9-5860-8f00-1206353078f2 | note | Verifying Document - Visual
5564928f-982e-571a-9529-57a92c686cfc | note | Testing Quantity Required (based from schedule qtys) - Every time
8487ae28-63f0-5cf1-9879-edd30a057da3 | note | Verification Activity: Activity - M
cd25888b-2dc8-5171-be25-266080ac2099 | note | Verification Activity: By - SE
81842a5e-f487-4f07-ba95-6be359c05238 | checkpoint | 5.2.3 - Foundation Compliance
edda29b8-b2fc-57a6-8a85-bf43e36d6bdd | note | Detail - It shall be de-watered prior to installation of bedding material.
e9866990-8b9a-56d1-9080-b4230571bf71 | note | ○ If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
8a7d25f8-d8cf-5df3-a483-13a8400420fc | note | Acceptance / Conformance Criteria - Witness.
6bc9084e-9654-5865-bec9-c2ed77b57959 | note | ○ 50mm granular layer shall be laid and compacted before the bedding layer is laid.
95045a1e-ef57-5048-8910-689600548db5 | note | Standard / Specification - PS 25.13.2 (G)
6d9996d7-c96c-5252-a985-e280837b74b0 | note | Verifying Document - Visual Inspection
fc91a45d-7439-566b-abc8-b7cdbb339770 | note | Testing Quantity Required (based from schedule qtys) - Every time
366c7612-dbb3-55ac-b6fd-3b12bb9eff54 | note | Verification Activity: Activity - M
ab4d3980-6849-530e-9e98-9529ceed4b4a | note | Verification Activity: By - SE
953f1403-f2fd-4a09-973f-d623ad462f96 | checkpoint | 5.2.4 - Bedding
00c1cc82-a2bc-52e9-977a-59995f5aa69a | note | Detail - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
3939bf03-a99f-5063-aff7-28d7d4e872ae | note | Acceptance / Conformance Criteria - Mixed Dust to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
d3ef4cba-c403-56ee-b225-e728640456c9 | note | Standard / Specification - PS 25.13.2 (g) Modified by Engineer WSP
e2d5321b-3d6d-59b9-947e-e9f30be4599b | note | Verifying Document - Visual Inspection
47601345-8dfc-5f03-800e-570381e2cadd | note | Testing Quantity Required (based from schedule qtys) - Every time
7d9fd81b-a996-524d-93b7-ac725a72123d | note | Verification Activity: Activity - M
88ea430f-d416-510e-be3a-45bd0d7bb64d | note | Verification Activity: By - SE
19d03263-3bc6-45fa-9bea-c7009d7e74d6 | checkpoint | 5.2.5 - Bedding (Enchased in concrete)
0125ab28-16bb-566a-a07f-135b7caf881e | note | Detail - Concrete Bedding to be placed. Compressive strength of concrete used no less than 20MPa
f291dfaa-02fe-57d1-b9f3-90657629f6ed | note | Acceptance / Conformance Criteria - 50mm
9663a4f8-540c-5f8b-99bb-4ee1aacc7e65 | note | Standard / Specification - PS 25.13.7 c)
893a2c45-af46-5d29-9f9b-98ee86d2d055 | note | Verifying Document - Visual Inspection
af8fc72c-6d1b-5c7f-b8d3-f3e35bdd8cc7 | note | Testing Quantity Required (based from schedule qtys) - Every time
f0fbc2ab-acdd-51c4-b6b8-29a2adb85cb4 | note | Verification Activity: Activity - M
0071623d-f263-5101-a102-7ad9d8aa7532 | note | Verification Activity: By - SE
3510d5a0-994b-482a-b4c3-19150811d7a7 | checkpoint | 5.2.6 - Installation of Ducts
bdf1b4ec-5a9a-524f-aa87-7a101a7f9071 | note | Detail - If more than 2 ducts are being placed.
0252a6ca-25cf-5998-800c-4443e38d6b26 | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
9aaa6cf3-e61f-5847-bd32-afb89c900ee8 | note | Standard / Specification - PS 25.13.7 (B3)
c405d751-c1d6-5a5c-b6d8-85f14c167dcf | note | Verifying Document - Visual Inspection
913055fb-8e2e-5e4b-9ed7-1316c4bd589c | note | Testing Quantity Required (based from schedule qtys) - Every time
3ce5d948-1fae-5973-949a-5a71a7116ce9 | note | Verification Activity: Activity - M
8e3fa9e1-c440-5fca-ab81-50fd398d4638 | note | Verification Activity: By - SE
3ada663c-3179-4e56-bc4f-996a8d82e034 | checkpoint | 5.2.7 - Warning Tape
eed58be1-4b6a-535b-a9f2-32954920a2c3 | note | Detail - Warning tape to be placed above services.
a4c5f7ac-68e1-5cd9-bd7c-62bccc87981d | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the duct
e07291d4-b2f8-5f84-9da7-620a5a54ae39 | note | Standard / Specification - PS 25.13.7 b) iii & f)
23094f91-2eb3-51c8-93ee-c14e4f6cecb7 | note | Verifying Document - Visual Inspection
e1b8a1f0-a497-590d-9885-cecced8fe883 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
ff8defd8-884c-5ed2-8609-c48585e6c5bd | note | Verification Activity: Activity - M
12ceb7d7-2e54-5700-9c83-f07a69aef06c | note | Verification Activity: By - SE
f288613d-4b12-46cb-8a24-c1837ca78f76 | checkpoint | 5.2.8 - Overlay
1bedc859-16e1-5bd3-95ab-6cbe43269280 | note | Detail - Mixed Dust to be placed and compacted
79496bd8-0294-55ca-86b6-50dc7493355d | note | Acceptance / Conformance Criteria - 100mm thick mixed dust
29f9711e-18d1-5b57-b0e8-4a3f2cecc027 | note | Standard / Specification - PS 25.13.7 b) ii
9f798b8b-12a0-5124-a113-bed897b37ca4 | note | Verifying Document - Visual Inspection
8e79d3f1-4758-5c46-b187-250aeea61086 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
1ed5eca0-4f6f-5614-9aa2-153018048ec0 | note | Verification Activity: Activity - M
4ed9dd4e-0cf2-5019-9d79-9c6cdde58724 | note | Verification Activity: By - SE
b27003d0-9dfd-4db5-8003-7bc92329dd88 | checkpoint | 5.2.9 - Overlay (Concrete Enchased Ducts)
ad6d068f-e680-51db-9136-5865a855f484 | note | Detail - Overlay and surroundings to be placed with concrete.
45715326-d292-56ca-9b7d-f5246353e57c | note | Acceptance / Conformance Criteria - 100mm thick on top of Ducts
ec8c7066-a58c-5f84-aeec-b4b7145d3a51 | note | ○ 50mm thick side of the Ducts
2041a20c-b033-55f8-bf4b-d800ecfc3d96 | note | Standard / Specification - PS 25.13.7 c)
35c8b8c9-7b39-5a63-b066-ce65f93a83a2 | note | Verifying Document - Visual Inspection
68895aca-e2f0-51d7-a50a-4bf3e244f188 | note | Testing Quantity Required (based from schedule qtys) - Every time
ef1bbfdf-7471-5f3d-bfae-8007e793d205 | note | Verification Activity: Activity - M
2d4d9d29-e5d3-5e14-83bf-40cc7bf0cd2b | note | Verification Activity: By - SE
e624363c-a7f3-4200-a908-a5b14169eacd | checkpoint | 5.2.10 - Overlay Testing (Concrete Enchased)
8d88067b-4374-578d-8395-03ed663a20a6 | note | Detail - Placed Concrete needs to meet the strength Criteria
b927d677-4629-5641-8ca0-79e8c7c017c9 | note | Acceptance / Conformance Criteria - >20 MPA
6798d431-cd48-5667-80a3-b73f6bd42773 | note | Standard / Specification - PS 25.13.7 c)
1f17467d-a0da-5b95-af8b-8ad9bdb443ae | note | Verifying Document - Concrete Dockets
f1eb4010-1385-502a-bd4b-73969c04cee3 | note | Testing Quantity Required (based from schedule qtys) - Every time
55953956-15ee-5394-a217-22b1fe1e3848 | note | Verification Activity: Activity - H
2d660eb5-0e08-5e2c-a959-c7556381edf2 | note | Verification Activity: By - SE
64805427-a955-44ec-9a77-7a6dc956a887 | checkpoint | 5.2.11 - Backfill
35b4f383-981a-5baa-83f3-13b250ed4318 | note | Detail - GAP20 to be used if site material is not approved.
ea9adb7c-a127-5983-8734-0239bf2fab3c | note | ○ NDM Testing to be carried out.
55944cb5-0e24-593f-96c8-0365910ff710 | note | Acceptance / Conformance Criteria - 100 to 250mm thick compacted material.
9dc423a4-c2e2-5e81-8302-d6c9364543c7 | note | ○ Min 92% compaction and Average of 95%.
ea6fc683-4426-5153-b766-50899414f681 | note | Standard / Specification -
135e3174-5d3e-527b-abfd-e2ae985b4f6e | note | Verifying Document - Lab report.
05fc38b2-f8d2-5de5-b16f-4079127ae001 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
b860155e-326e-57e1-835a-b0107d384955 | note | Verification Activity: Activity - H
db5dc94a-43b2-5fc0-b7e6-254220f27db1 | note | Verification Activity: By - SE
6532af4f-afed-4f67-8d27-3de12a41f404 | checkpoint | 5.2.12 - After Completion of Ducts
8239b708-733b-51bc-aa24-9cd0cc89ed57 | note | Detail - The Contractor shall pull the pig through the ducts to ensure there are no blockages between access points and no foreign material remains in the duct.
1767dcc3-b3e9-5631-be44-fa112e2e6729 | note | Acceptance / Conformance Criteria - The diameter of the pig used for proving the duct or pipe shall be at least 90% of the actual internal diameter of the pipe or duct being proofed.
845d1ce5-7c97-5fc2-990c-6b3743696db8 | note | ○ No blockage inside the pipe
259f0715-9e54-5a8e-b0b4-4a8c3ec73616 | note | Standard / Specification - SP 25.13.7 E(1)
7c37438a-31e0-5688-8c6d-ceb6c3192878 | note | Verifying Document - Visual Inspection
dc8dc9c9-13e9-564e-a0dd-9c2adb9ad114 | note | Testing Quantity Required (based from schedule qtys) - Every time
84af8afa-fa91-5b24-b5df-30f46092f196 | note | Verification Activity: Activity - M
e913a630-16ea-5b53-bca3-ff110b3b2943 | note | Verification Activity: By - SE
0ab1d969-52e7-4609-8ba5-59874021d1d7 | checkpoint | 5.2.13 - Caps
a197ce51-f9fa-5bcb-a6f8-97892e79ddd7 | note | Detail - All duct ends shall be capped
e8277531-4066-5eb4-9142-c076f1b20a62 | note | Acceptance / Conformance Criteria - Capped ducts
fc0a637d-fa90-532d-85f0-99268ca4ab61 | note | Standard / Specification - PS 25.13.7 (EV)
63b634fc-8ce0-53c4-a992-5fef4566d9a9 | note | Verifying Document - Visual Inspection
f23c1148-dd8e-5a0c-9580-dbbdb7d02448 | note | Testing Quantity Required (based from schedule qtys) - Every time
40cb83ce-da21-5375-8812-0bcc2c84c620 | note | Verification Activity: Activity - M
a96d5487-5e3b-58d5-be11-d1f6da9ca088 | note | Verification Activity: By - SE
0ea2403f-f487-47a1-98ea-bd1d451f097f | checkpoint | 5.2.14 - Survey As Built
0f97076e-f9b9-5ee5-af67-4915753127d9 | note | Detail - As Built every ducts joint before backfill
7a18a043-5908-5c70-a8d2-1d166882148f | note | Acceptance / Conformance Criteria - Completed as per drawings
d3b8f093-79ef-5a2e-a626-66c0d31ef19f | note | Standard / Specification - Standard Practise
1e7b502a-3e65-5177-ac0c-ae473a925309 | note | Verifying Document - Survey
8eb9a18f-a4ab-5826-b695-f46b49b67cd3 | note | Testing Quantity Required (based from schedule qtys) - on going
f42a3d97-dbdd-5a0f-af35-38176c6ddf6b | note | Verification Activity: Activity - H
f2a8847e-fb7d-5c71-8636-56a4f1913943 | note | Verification Activity: By - PE
88fef857-c750-4c83-a42e-8117326904ec | checkpoint | 5.2.15 - Compaction - Clegg Hammer
7a0bbcce-3e13-502e-bd40-7ad881131259 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
610eeec0-e29b-56ac-9dcd-b8e0977cd69f | note | Acceptance / Conformance Criteria - Structural Fill
f3a115bc-08bd-51aa-bdd2-13ca761c3cac | note | – Min CIV 18
25b78a8c-387c-52b4-94a1-0a6c09fffe68 | note | – Ave CIV 20
ccaf93f5-693a-534f-a88d-9d87c2b2973f | note | ○ Non-Structural Fill
67292336-2707-5ca4-bcf6-ef183c9f4c88 | note | – Min CIV 10
b991e857-bca8-5e5e-ba50-672c207f6387 | note | – Max CIV 12
9e0d0391-ffcb-5c9a-8729-f3e6b6291828 | note | Standard / Specification - Appendix XVIII
f89bd28b-6969-5cbb-b7e9-1dd4d39a753b | note | Verifying Document - Clegg Hammer Report
8c526c58-5498-5708-a465-ebc0a6193112 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
cb1f0f94-3b42-5e49-82e7-d39b298f7b27 | note | Verification Activity: Activity - I
a5b69548-1b4b-535c-8021-712703182a68 | note | Verification Activity: By - SE
b62e7030-7e52-49f7-802b-cbc0d327f889 | checkpoint | 5.2.16 - Compaction - NDM
9b629f71-cead-58ba-a66a-fe19f088a88b | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
0f2df5b9-2703-5e36-814b-7b0c2d9401d4 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
eeaf73ce-25c8-56ef-9ee3-6b2a6480baa0 | note | ○ Min >92% of MDD
b1c2136a-ad22-505b-b360-8ae9aa54d2f6 | note | ○ Non Granular Material
357e89a6-ac37-50d6-8d9a-5733063903c6 | note | ○ Max Air Voids 8%
6c12459e-b0e7-5299-893c-e157fc1e4371 | note | Standard / Specification - Appendix XVIII
1fc5c8e4-504b-57b7-987f-7b61070a775d | note | Verifying Document - IANZ Accredited Report
8a930f07-36b4-5e34-bf77-71059fb8294b | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
978a88bc-73b1-53bb-ae92-752db5453d06 | note | Verification Activity: Activity - I
66cab62a-ec6b-5f99-988d-26aeea676605 | note | Verification Activity: By - SE
bd3ed90e-e6c3-499f-a3e7-0701800a596f | checkpoint | 5.3.1 - Subsoil Drain inspection
698c917c-c9f9-55b8-b7d9-02920c8761a5 | note | Detail - Subsoils to be placed adjacent to the underpass and inspected by Engineer
053828d7-155b-5199-8545-6e376e3fb2ee | note | Acceptance / Conformance Criteria - Engineers Approval
8bad0038-c7ac-5541-b53d-3f1ba532cab9 | note | Standard / Specification - PS 17.6.3
ee14da95-e29e-5632-bf79-81bd249a3b6c | note | Verifying Document - Visual Inspection
fb8186ab-bc8c-524e-95ca-409f71b03b1a | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
4ca194fc-5360-5a54-9477-9ef71171d09e | note | Verification Activity: Activity - I
120d1428-1bb4-5fe7-8985-01b8505b28d9 | note | Verification Activity: By - ENG
cddc7fe7-2b45-4a26-b614-75577cec6684 | checkpoint | 5.3.2 - Excavation
f48ffdd4-1097-5135-ac9d-36a5a775a974 | note | Detail - Excavation of Trench should be within tolerances.
1f15e36b-91ce-5a67-ade8-e4665fc6cf40 | note | Acceptance / Conformance Criteria - 335mm deep x 300mm wide
f18d3b34-7c13-519c-8ca1-372251fcf7c8 | note | Standard / Specification - Drawings
b6429cb3-bbf5-5ec4-9969-5fa745f2d824 | note | Verifying Document - Checksheet
23f0d1fd-38ef-5c51-801a-150a8b96d50d | note | Testing Quantity Required (based from schedule qtys) - During Construction
872f847b-8b6a-5a06-bd10-be6168908453 | note | Verification Activity: Activity - M
20ee4664-1e9f-5213-b8d0-a3e6836b992c | note | Verification Activity: By - SE
84b345e8-bc11-4931-94f8-b2b718b5d4e9 | checkpoint | 5.3.3 - Placement of Bidim
1b0bd37d-5e46-560b-b0a4-0fb6657694ae | note | Detail - A29 Bidim to be placed and wrapped around Trench.
7d8766ba-095a-5f94-9cc2-a17ca23d8b0c | note | Acceptance / Conformance Criteria - Minimum Width 300mm.
0445d078-84c9-572e-b83e-6c2d9913e148 | note | Standard / Specification - Drawings
6640dd3a-f7cb-59c4-841f-0837c303f463 | note | Verifying Document - Checksheet
8b8f6d93-79c4-5fae-8de3-cda69955dcc4 | note | Testing Quantity Required (based from schedule qtys) - During Construction
41b1306a-94bf-57be-9eb3-b97ee9fb52e5 | note | Verification Activity: Activity - M
8f53af20-66fd-558c-b15f-511b1dd42af1 | note | Verification Activity: By - SE
78c559b1-e0ee-4ab4-a5b5-cb63ec996f1a | checkpoint | 5.3.4 - Cushion (Bedding)
9d0f8e41-7690-551a-b37e-59bd50a2a506 | note | Detail - Pipe must have 75mm of Cushion. Drainage 60:40 Material to be used.
356da31f-468c-5b7c-8e73-bf548fb32ab9 | note | Acceptance / Conformance Criteria - Minimum 75mm
d0c8a570-c1cf-5636-a36e-dc2bf7ee2732 | note | Standard / Specification - Drawings
6cc9e6dc-6955-5905-978c-0cbd947e7fd4 | note | Verifying Document - Checksheet
2adb462e-b4dd-5c5c-8aa6-60aa96356953 | note | Testing Quantity Required (based from schedule qtys) - During Construction
32c0a2c2-1b9e-5628-90eb-c8aef0845edc | note | Verification Activity: Activity - M
dff824f7-a40d-5bd2-93c0-965af79b5272 | note | Verification Activity: By - SE
756440af-c1b3-49ad-8171-8f327a5f9483 | checkpoint | 5.3.5 - Placement of Pipe
291eb7fa-db53-51d8-be16-61855b343c27 | note | Detail - 110mm Perforated Pipe to be laid Down
b51c189f-970e-5e7d-9509-4f121d87a5da | note | Acceptance / Conformance Criteria - As Per Drawings
c2edbed1-3b8c-58f8-bed0-a436539e539f | note | Standard / Specification - Drawings
7ac00807-fd4c-5cdb-a222-0c9b543bf9c0 | note | Verifying Document - Checksheet
e1cbdfda-5425-5d62-8067-ea047dd95dd6 | note | Testing Quantity Required (based from schedule qtys) - During Construction
a244f73f-f9a5-5d1c-8ba0-713a885b9a65 | note | Verification Activity: Activity - M
4ecfc7d8-c3ed-508c-afe1-6cad3ae29e82 | note | Verification Activity: By - SE
e1c00396-cf67-4abd-add1-58e9014e29a6 | checkpoint | 5.3.6 - Backfill
0b95e677-217f-5dbf-a5d3-eb5fa570dd41 | note | Detail - Pipe Must have a 150mm cover from Bottom of Pavement.
2b59aedd-ac8f-5c66-9960-480e273dae21 | note | ○ Drainage 20:40 Material to be used.
18c57cc4-d906-5fa0-af9b-f996a2999e67 | note | Acceptance / Conformance Criteria - >150mm Cover
c13b938b-e6d5-56e0-af03-a9c5378d147a | note | Standard / Specification - Drawings
7a5dcb1e-26d1-5c80-9d2b-49ee2efb0a90 | note | Verifying Document - Checksheet
52b1f0af-3a5c-5cb1-9e37-6c8559d96573 | note | Testing Quantity Required (based from schedule qtys) - During Construction
025dd61a-b677-52b0-b981-90e0ded7096d | note | Verification Activity: Activity - M
58be6f5a-f280-507d-8b04-3de278a3dc5d | note | Verification Activity: By - SE
097a0d9d-145e-4f9a-9831-32ab2556840c | section | SECTION 6 - UNDERPASS GRATED TRENCH DRAIN
6b02624f-a62d-41ce-a371-baafc433125c | checkpoint | 6.1 - Installation of Channel Drain
fd3bcfde-68eb-50de-9757-abf188950a47 | note | Detail - 300mm wide grated trench drain with WAVE HEELSAFE grate to be located at end of underpass apron. Trench drain to connect to SWMH2.1.5 via dn150 pvc-u sn16 pipe. Grated trench drain to have min. loading class C.
4350ab82-c826-5d8f-b5ed-f5feaf2c456e | note | Acceptance / Conformance Criteria - Installed as per manufactures instructions
736f585b-cebf-536c-9341-c6e49dd10ebe | note | Standard / Specification - 21.5.8
60afc622-a7f9-54c6-9359-210f594a11bc | note | Verifying Document - Inspection and record
050ec89a-3938-517a-8508-b0ca2667366f | note | Testing Quantity Required (based from schedule qtys) - During Construction
ca284089-bb5d-565a-8825-9f21355766bd | note | Verification Activity: Activity - WP
f4886b0c-d361-5478-82da-d6d0f4743363 | note | Verification Activity: By - ENG
52fda9e0-b946-4406-a739-88a4a74e8e3a | section | SECTION 7 - AS-BUILTS/ REDPEN MARKUPS
ffcb0ed9-f730-461a-8a14-6d1552b2e891 | checkpoint | 7.1 - As-Builts/ Red pen markup
c32deded-47ce-574f-9586-a7c1a494984c | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
992cae27-87bb-559e-a203-0ec564f395cc | note | Acceptance / Conformance Criteria - As built drawing red pen markups
5344aad5-2565-5cde-893b-8a953d2fc3b0 | note | Standard / Specification - PS 16.7.6
9090d8ab-0867-5037-8956-891f95f06a0e | note | Verifying Document - Red pen markups
459397cb-9589-5e70-82f4-d45dd115ab97 | note | Testing Quantity Required (based from schedule qtys) - During construction
eb857af8-8fd8-5a85-befe-b287607784ff | note | Verification Activity: Activity - D
66f09670-03d3-5c08-913b-62664b64b9d6 | note | Verification Activity: By - SE
ea42ec14-fba5-4b05-a6ca-93a37285cf37 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
1e8467bf-0481-5a1f-a8e8-87c82681a6d7 | textbox | Contractor's Rep Name:
20cadb38-f718-5861-ba34-4ffd25245641 | textbox | Engineer's Rep. Name:
aa2a294b-6827-5870-8ffd-d1e2b17a7102 | date | Date:
721787b5-0541-414d-acab-197ff67345b7 | signoff | Add Signature
cb408ba4-bd34-41b8-8178-d2351e6b7080 | checklist | DN1210-010 ITP Landscaping & Urban design Rev 2 | itp | DN1210-010 ITP Landscaping & Urban design
eb8ec20c-86d0-4505-a33d-edfe56343c31 | section | SECTION 3 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
83e039f0-c7a4-4c12-98b6-cdabf3eff79f | checkpoint | 3.1.1 - Wetland & Landscaping Methodology
46028ae3-27f9-5d0e-8f5d-92c3c0cc5fa5 | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Wetland & Landscaping including, testing, inspection and hold points for review and approval prior to works.
8087fb4f-dbb8-53a9-8b93-35af4ab8aafe | note | Acceptance / Conformance Criteria - Engineers Approval
1523e86e-5880-5569-8eff-f912c427b091 | note | Standard / Specification - Appendix V
05a1f326-cc0a-5783-9e89-e4b53183ffc1 | note | Verifying Document - Approved Methodology
d1a51edb-5740-51ea-99e9-bbe383a4cf16 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
8167ca02-2dc8-5137-8da9-f000d227424e | note | Verification Activity: Activity - HP
3735f0e3-154b-5cfd-9f44-1521a18f5e23 | note | Verification Activity: By - ENG
54f41565-a55a-40b1-ba00-c28052dc776a | signoff | AUTHORITY HOLDPOINT
5d765fd7-33a5-4028-8073-6c641c53cb01 | checkpoint | 3.1.2 - Bentosure geosynthetic Clay liner
ab3d44e6-6f4a-5284-b675-cfcdc6af7034 | note | Detail - Permeability value of bentosure liner
4d9a69d8-4f3a-5105-849a-7b49e8c9ce61 | note | ○ Liner Approved for use
03d56080-2490-5a8a-833c-6e945728a984 | note | Acceptance / Conformance Criteria - permeability value of 1 × 10⁻⁹ m/s
f7d4611b-2263-584d-b9b4-7c4a3bace1c0 | note | Standard / Specification - Refer to installation guide
91b53aa4-ee2f-52be-8511-4a4dd103a1f0 | note | Verifying Document - Delivery dockets
3422f80d-b98a-57af-af6b-492fa9b1a008 | note | Testing Quantity Required (based from schedule qtys) - Once per source - prior to commencement of works
cf87400a-34c3-591d-a4fa-04ec1ded4980 | note | Verification Activity: Activity - HP
2c240095-7bd3-5f3b-b7e3-3ea76737e5d1 | note | Verification Activity: By - ENG
3cc800bd-8070-4457-9acd-6d5369fd055a | signoff | AUTHORITY HOLDPOINT
a5dae480-bfc2-4e38-8c60-157678fdd249 | checkpoint | 3.1.3 - Geotextile Fabric
e49f0622-ddc4-572c-bf92-db3d0ce4734f | note | Detail - Geotextile fabric approval
cdccde0e-61cb-59ff-8b77-db9ec505b644 | note | Acceptance / Conformance Criteria - Class D geotextile fabric
c5597fe4-ea70-55ae-83dc-196c50c5941d | note | Standard / Specification - PS 21.5.15
ec2959ab-f331-53cd-8976-f226a2b4b61b | note | Verifying Document - Engineers Approval
1880fbaa-eb9a-5d11-8107-6af3e5f67446 | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
da4e4a8c-20a1-5908-a5fe-f532815cfbfd | note | Verification Activity: Activity - HP
2ce2f90a-2229-517d-a2bc-c25815d85ff0 | note | Verification Activity: By - ENG
8c8cd1d6-e17e-411a-b7c4-26f4817378d4 | signoff | AUTHORITY HOLDPOINT
db85a55e-28e4-43c3-a8e5-31b2908d4654 | checkpoint | 3.1.4 - Topsoil Analysis
7714d797-7e35-51cf-bd89-10cd64fda571 | note | Detail - Testing of on-site and imported topsoil for quality.
d7c9fb2d-4bb7-5627-ad63-86bb3a1a5401 | note | Acceptance / Conformance Criteria - Topsoil must meet the criteria specified in the project standards.
344d0f6c-9ddc-55f2-b413-63212da2b98e | note | Standard / Specification - NZTA P39: 2013, Section F
a0570efd-1635-5ac0-a75a-5f5cc168d723 | note | Verifying Document - Soil Testing Report
d8d62011-e60d-5a21-b8a4-19251413300f | note | Testing Quantity Required (based from schedule qtys) - Once per source
728f317e-ad00-569d-bf09-e3661dc1da85 | note | Verification Activity: Activity - HP
e07adb2b-d38b-5d11-9b05-bd84d950beb8 | note | Verification Activity: By - SE
0cd4c5cf-b4b1-49f5-9dde-700d8d803a5c | signoff | AUTHORITY HOLDPOINT
08c663d7-9ae7-446a-a43c-a3f617b4e618 | checkpoint | 3.1.5 - Mulch Material Verification
b83f524f-cb2a-52f2-bb12-c69e7f465121 | note | Detail - Verify that the mulch used meets the specified criteria (e.g., pallet mulch, arborist mulch).
59e0ba58-ae36-56aa-a758-0d630b824cf9 | note | Acceptance / Conformance Criteria - Mulch material should be free of contaminants, sufficiently aged, and appropriate to site and slope conditions
0641a84b-5cd4-5a07-b630-43b287fd0ceb | note | Standard / Specification - NZTA P39: 2013 Section 3.9
ef74c60f-dcf9-5a3c-bbfa-cff24d575d5e | note | Verifying Document - Mulch Material Certification
f034961b-fbed-55f5-8369-3c496b37bd01 | note | Testing Quantity Required (based from schedule qtys) - 100% of mulch used
07197bc7-4e3c-5c21-ba19-649479ffb070 | note | Verification Activity: Activity - HP
79b15e5a-d44e-5f2a-91e5-e5e657d196e6 | note | Verification Activity: By - ENG
7672595f-8fd6-4a99-81d6-2dfd7cdc0cce | signoff | AUTHORITY HOLDPOINT
40e74ab6-89d3-41db-8bb6-860fd6989836 | checkpoint | 3.1.6 - Biodegradeable Weed Mat
bbbb50f1-f298-5f12-9236-11c0f76bdaac | note | Detail - Biodegradeable weed mat approval
b15d9fce-a571-5768-ad35-c0b90dc320d1 | note | Acceptance / Conformance Criteria - 450 GSM, 7mm thick, biodegradeable weed mat
c438c7d2-acec-52ec-afe7-df8651fd0b59 | note | Standard / Specification - PS 27.3.8
d7afa6d0-4821-5905-a934-a5127ef95019 | note | Verifying Document - Weed Mat Approval
bfa8de33-0a80-550e-a549-48b725953e5b | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
6cabe846-7fdf-5dec-b5e0-b66d36420263 | note | Verification Activity: Activity - HP
0e6d8aec-0776-5b64-83f4-299cddf50e77 | note | Verification Activity: By - ENG
333c02c7-27e5-4090-af33-418ea26ac357 | signoff | AUTHORITY HOLDPOINT
158ada92-6131-410c-8dcf-0cebe69e68e5 | checkpoint | 3.1.7 - Rock Rip Rap Approval - Grading
a4915688-3549-5e4e-918e-7da566a26034 | note | Detail - D50=150mm Grading Approval D50=250mm Grading Approval
8b2f4e7a-11c6-531e-8783-d67bacfb0668 | note | Acceptance / Conformance Criteria -
192f4ecc-2cc2-525d-b6f5-564e953d3b23 | note | — — — — — — —
9535e72a-e7e5-54a2-a4fc-9f1bf92f2763 | note | TABLE 21.3: D50 = 150mm Riprap Grading
c6244d5e-32ab-5aca-9eee-1930d8f7ed4f | note | Aperture Size (mm) ¦¦ Percentage Passing
9dc51a53-4105-588d-a63d-15d909b5a000 | note | — — — — — — —
3c5125f7-4e18-5e04-9ec7-0fe596602cec | note | 230 ¦¦ 85
6822eb02-4414-593a-b0a0-90d6dbc8050a | note | 150 ¦¦ 50
fef2211e-3458-5664-a6f2-c520dd2d9adf | note | 95 ¦¦ 15
e4e0de40-9b21-59b8-988d-795406076063 | note | — — — — — — —
18d89ed7-3a34-5722-b9fb-3c488ee7b0ba | note | TABLE 21.4: D50 = 250mm Riprap Grading
ec59b22b-e72c-531d-a2ae-f6e258752e67 | note | Aperture Size (mm) ¦¦ Percentage Passing
8e231631-cfbe-540c-bf83-30f305f0c9f8 | note | — — — — — — —
620b1d34-add5-535e-987d-b9d1ada6e373 | note | 380 ¦¦ 85
e21bf53e-2a0f-5d5a-bf1f-83bd1ce69a3f | note | 250 ¦¦ 50
682fca77-a4c5-581a-b72e-158e60c5a4b6 | note | 160 ¦¦ 15
e02ba952-7274-5ac5-8483-3d785b335055 | note | — — — — — — —
dbe15b61-93e3-57ce-bbe3-86ab45300e0f | note | Standard / Specification - PS 21.5.14
44e73bbe-d4b8-5ee0-9adc-431fe9310a06 | note | Verifying Document - Engineers Approval
a546f0ca-5b9f-5d22-8e52-997d8d0f2adf | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
f93c6755-f247-5ad7-a20f-2ca375eef0b3 | note | Verification Activity: Activity - HP
f0fc992a-2956-5eb3-903e-1848893326a9 | note | Verification Activity: By - ENG
f6c06556-f610-442d-9979-0bc4a2158ea4 | signoff | AUTHORITY HOLDPOINT
49299d54-ef61-4f8b-bb0e-c9bcda1093c7 | checkpoint | 3.1.8 - Rock Rip Rap Approval-Weathering
cd08cb19-7998-556a-93b6-8fabe7991551 | note | Detail - Weathering Index of Coarse Aggregate
67dfcea9-3d1c-513b-8a6b-a2926085ef73 | note | Acceptance / Conformance Criteria - AA to CA
654b7767-f765-5899-a928-feeca3ef46f5 | note | Standard / Specification - PS 21.7.4
e76c0585-ede9-5816-8db3-6e510da621f9 | note | Verifying Document - Engineers Approval
1a4500a0-3f9c-560d-9f19-c6eeea86b87d | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
a6b8b75c-b88e-5720-89d3-1fe073c814c7 | note | Verification Activity: Activity - HP
7b9673c5-5ec0-5c25-a76c-6f5d732696e8 | note | Verification Activity: By - ENG
757b4f5f-ee84-4ebb-8b3c-a76e88d0a08d | signoff | AUTHORITY HOLDPOINT
4325c820-bff4-4c6c-8ef1-6125f2c5675a | checkpoint | 3.1.9 - Rock Rip Rap Approval-Crushing resistance
0ca0606a-6e28-5c0e-99b0-ea486e311723 | note | Detail - Crushing Resistance of Course Aggregate
79b118ec-73b9-5479-ad39-ad3285c940f4 | note | Acceptance / Conformance Criteria - >150kN
8ee1ffb0-149e-50ff-a2b2-b6bd79c3be5c | note | Standard / Specification - PS 21.7.4
05202a6f-1dc2-5ed5-ac24-c04e5d3977bf | note | Verifying Document - Engineers Approval
326bb85d-3af2-5816-92e9-c9c2db8eed80 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
b69b1c6e-4a3c-584f-b381-864f259cee03 | note | Verification Activity: Activity - HP
4aa2baad-9978-57b3-a715-d090a98c63c1 | note | Verification Activity: By - ENG
dc6b2f0b-99b4-431e-8f94-a0f0779a0250 | signoff | AUTHORITY HOLDPOINT
ca05b24d-fca4-49ff-912a-bd618f6c78af | checkpoint | 3.1.10 - Rock Rip Rap Approval-Solid density
9f5958f6-5593-59f8-a6f1-9a96e9d3af11 | note | Detail - Solid Density of Aggregate
4ca77a39-d3bb-5290-b2d1-6305ba94fa13 | note | Acceptance / Conformance Criteria - >2.65 tonnes per m3
e51a5a8d-255b-553d-aca7-3bb70bf2c618 | note | Standard / Specification - PS 21.7.4
abc65d99-4fb7-5496-9b78-d13ab6bc2a0a | note | Verifying Document - Engineers Approval
4cdd034c-d8f1-56d8-ba72-50a92fd55f99 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
1cf71c8e-34eb-5ca4-ba7f-db29bce78428 | note | Verification Activity: Activity - HP
4da7c962-f122-5b2b-bbfc-9834cfcca522 | note | Verification Activity: By - ENG
cdd79dba-3610-4892-a4d1-7aabc933ff6a | signoff | AUTHORITY HOLDPOINT
e814e8ad-148d-463d-94f0-8ff3e85cd214 | checkpoint | 3.1.11 - Rock Rip Rap Approval - UCS
3ca13aa9-b07f-50a3-a505-60ac6a94c30d | note | Detail - 1 per 1000m3 AS4133.4.2.1 >30 MPa
90fe63c4-8572-5c87-ac96-539120375383 | note | Acceptance / Conformance Criteria - >30 MPa
dd2741f0-54e5-5c41-842b-51db4ea4a954 | note | Standard / Specification - PS 21.7.4
5bcc0cbf-9e20-5d06-bcb5-e003cf4dd298 | note | Verifying Document - Engineers Approval
c5416028-45ca-5cca-b2ed-388c8f60d0e0 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
fd9a22f2-5361-5903-9a7c-3451148afcc0 | note | Verification Activity: Activity - HP
b303198d-4ab1-53ae-a5d2-f27fc340358e | note | Verification Activity: By - ENG
6ac35604-bfaf-4eb0-a3b5-4a74663573e3 | signoff | AUTHORITY HOLDPOINT
eecf707c-d2db-4b89-b015-2129c926bf3e | checkpoint | 3.1.12 - Rock Rip Rap Approval-Point load
b1d9a8f0-b569-5ea2-a759-544c11c60cf9 | note | Detail - Point Load Strength
ee098f4a-639d-5fd0-bc2d-87118707e0ac | note | Acceptance / Conformance Criteria - > 1.5 Mpa
d3c031ce-4495-55e4-8bb5-22a7f5f0107c | note | Standard / Specification - PS 21.7.4
043974b1-4aec-5f14-9491-6ecbd2603d63 | note | Verifying Document - Engineers Approval
c75b5801-9b91-520c-ba2a-69620bbc5d68 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
b5b8c77e-05ee-5cc3-8465-23998c1f402e | note | Verification Activity: Activity - HP
0533d7d1-e035-539a-be7a-ff5761d5f8b5 | note | Verification Activity: By - ENG
636ece22-b3d4-4939-bb7e-4e76e2d9512f | signoff | AUTHORITY HOLDPOINT
679bbbfc-2ba2-42d7-98ea-2357284eb2c2 | checkpoint | 3.1.13 - Hydro-seeding
7e393238-a167-557e-9bdc-4e35025bba3a | note | Detail - Grass mix approved
d0824b45-bd4d-52f1-8c43-48ece2de0dd7 | note | Acceptance / Conformance Criteria - Send seed mix to engineer for approval
9fba1008-3fbb-5db1-8b2f-ac54c44c6c91 | note | Standard / Specification - NZTA P39: 2013, Section F
cbc29c9c-78c3-5f7c-a84e-7c686316530d | note | Verifying Document - Seed Mix
3ea244fc-e263-5aac-9831-49e28ebcda2f | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
fca7f248-9dba-5691-930b-b5df775d444c | note | Verification Activity: Activity - HP
c33fd9d6-b8f3-5010-9922-a686de70a1d6 | note | Verification Activity: By - ENG
022e3abc-f5cb-4b46-8fbc-4237d7eee0c8 | signoff | AUTHORITY HOLDPOINT
6f566e05-0788-4df0-a99b-a1b4d5277579 | section | SECTION 4 – CONSTRUCTION ACTIVITY
e3f4af80-fd5f-4e0e-bbf4-f1b9f3f826ef | checkpoint | 4.1.1 - Setting out Notice
f429e22f-5035-5ee0-b945-f60ee48c8d0e | note | Detail - Confirm that the site has been marked out according to the project plans and specifications before planting of trees begins.
2935eefa-9db2-5964-ab06-eca038dc0818 | note | Acceptance / Conformance Criteria - The Contractor shall provide written notice to the Engineer, at least two days prior to Setting out.
66787e5f-4f86-5392-a81f-50db1618f3a3 | note | Standard / Specification - PS 27.3.2
81ccde72-32eb-59c8-8b03-be4ab0b531e3 | note | Verifying Document - Setting Out Notice Report
3150ebbf-0833-50d4-80b1-ef613fe41bb2 | note | Testing Quantity Required (based from schedule qtys) - Before each stage
ae21bc22-f547-5ee0-8b03-2e63bdf97e38 | note | Verification Activity: Activity - HP
87a1c9f5-ca67-5052-9967-255d8ee6a942 | note | Verification Activity: By - ENG
46051f75-7552-4528-887b-b4755fef6b66 | signoff | AUTHORITY HOLDPOINT
a34e7708-1e55-43ea-b4d8-d15031a9b62d | checkpoint | 4.1.2 - Site Grading
da9bc0d8-c762-5333-b9b8-99760dc55dac | note | Detail - Grading for planting areas to ensure drainage.
b3613f26-8d29-5906-a868-d93bec3343c6 | note | Acceptance / Conformance Criteria - Smooth, flowing contours with proper drainage.
1ff5ef2a-f9f0-508f-ad65-d3278e52646d | note | Standard / Specification - NZTA P39: 2013, Section G, PS 16.6.3
cc9c0bda-29ae-5e63-b2ff-bb593aa48ccb | note | Verifying Document - Visual Inspection
0f14f72f-6edd-5ef9-8622-b0c1e25bc7b6 | note | Testing Quantity Required (based from schedule qtys) - 100% of areas
d41f5f47-4bab-5c60-b397-19fde91f36a4 | note | Verification Activity: Activity - I
16f8f3af-7b8f-52a6-9363-81ed3c46d292 | note | Verification Activity: By - SE
e2cd57ef-84b7-4307-ae8b-188ecf0ef239 | checkpoint | 4.2.1 - Pre Planting site walk over
2c32ed4a-57ac-5ede-a362-299fb4c1f936 | note | Detail - Confirm setout and ensure site is free from debris and is ready for Planting
df876be3-7497-5d93-8044-005e7606dcc2 | note | Acceptance / Conformance Criteria - 1. Confirm planting set out is acceptable as per design drawings
ba93325b-528a-5544-98d2-ff518e1a7d75 | note | 2. Confirm herbicide has been applied before planting
3adc072d-f11c-5d2a-ba78-c4b3b397d377 | note | 3. Confirm delivery of Plants and Trees is correct
5e00eb82-031d-5a30-9cbd-f79a11a8ef9f | note | 4. Site mostly clear from vegetation and debris or rubbish
4140d0a6-26ae-5739-bbba-95ca4caeaa9d | note | Standard / Specification - NZTA P39:2013 Section C and PS 27.3.2
1363457b-134f-5139-b9e7-7275743d5453 | note | Verifying Document - Visual Inspection
c4a70ac2-09e2-5d16-b737-c813859bbea2 | note | Testing Quantity Required (based from schedule qtys) - Once Per Establishment
36f99183-75df-5080-8c57-de915b4c3f34 | note | Verification Activity: Activity - HP
47bb9d19-283b-532b-92cc-ce0eed4d91bf | note | Verification Activity: By - ENG
ef10586f-9a0f-4f6e-b0c1-f4323d92e2bf | signoff | AUTHORITY HOLDPOINT
ad2f9048-f6da-471b-b6f8-1a88616bf30c | checkpoint | 4.2.2 - Confirm planting layout / pattern
1cded343-5367-5e2a-85fb-5e919d2ac481 | note | Detail - Layout a sample section of plants in the pattern and density as shown on the design as per WSP-DR-UDL set and confirm this is acceptable before planting.
9f564e3e-5372-5761-87e2-79dccc590860 | note | Acceptance / Conformance Criteria - For planting areas less than 2000m2: the sample area should a minimuim of 5% of entire area
0db31363-97c3-5b45-8c83-2bb4762b5313 | note | ○ For planting areas more than 2000m2: sample area should be a minimum of 2% of the entire area.
b2e7b647-2a85-55d0-9b51-3d32ddbf756e | note | Standard / Specification - PS 27.3.8 section b and NZTA P39:2013 Section B
da776a23-298a-52ed-b96f-513322689290 | note | Verifying Document - Visual Inspection
396b2d8a-58c1-550d-8efd-15daf7f79982 | note | Testing Quantity Required (based from schedule qtys) - Once per planting type mix
613a81c8-f1d9-5064-bf7f-e235797b1b3b | note | Verification Activity: Activity - HP
c0f458a1-a3bd-5152-9da7-c237ba7d5fd2 | note | Verification Activity: By - ENG
8deb1708-7c04-4598-b36f-6dc31ee65dd4 | signoff | AUTHORITY HOLDPOINT
40137973-1277-4157-9cb3-0647b1dd2232 | checkpoint | 4.2.3 - Planting Density
5efb079a-6ac7-5962-abbd-3213196bcb28 | note | Detail - Plants shall be spaces as specified in the drawings. Either 500mm c/c or 1000mm c/c.
6b94578f-4da6-50ec-a0ae-f1152ac47459 | note | Acceptance / Conformance Criteria - Plants designed to be 500mm c/c should be between 350mm-750mm apart.
185123ba-e03b-5f8a-bf22-9e6abcf65188 | note | ○ Plants designed to be 1000mm c/c should be between 750mm-1250mm apart.
d0a80a1f-2ad7-5959-93d2-231246afc169 | note | ○ This allows for a slightly varied pattern to look natural.
33c9c980-8fb0-54b0-8d21-dbc46f419e5a | note | ○ Avoid a grid pattern if possible.
9e01d911-73b0-5c5d-8449-9d26d08a4c6e | note | Standard / Specification - UDL 250 - UDL 253
38180871-5d47-5a9e-85f3-7e88c408aad0 | note | Verifying Document - Visual Inspection
9ad56f17-2633-5af5-a7e0-a1eb5da94402 | note | Testing Quantity Required (based from schedule qtys) - Once Per Establishment
16b1a02a-2a53-5c3e-bf6d-4612ffa9bfa0 | note | Verification Activity: Activity - M
507454c9-cb3e-5f33-a2bc-4113587436e5 | note | Verification Activity: By - SE
053cd186-2eb7-4a50-8a0a-7fc207244406 | checkpoint | 4.2.4 - Tree Pit Excavation
35d50633-5304-5633-a191-d7b09c478326 | note | Detail - Excavation of tree pits according to specified dimensions.
9657acce-18ce-567a-8b2f-8e75e1863e3e | note | Acceptance / Conformance Criteria -
a605f5c0-21ad-5d9d-929b-1a05b37b5406 | note | — — — — — — —
26087662-e4f7-5c90-ba1a-c3c9a385c25b | note | TABLE 1
1d2e35a0-734e-567e-8e9b-5e4f1face01b | note | PLANT SIZE (LITRE / PB) ¦¦ NO. OF STAKES ¦¦ TREE PIT SIZE
b748923b-aa77-53f7-96ba-09d6d0b06d36 | note | — — — — — — —
17664076-a209-5363-a007-497e0ca71dbe | note | LESS THAN 15LT / PB28 ¦¦ 1 ¦¦ 2X SIZE OF ROOT BALL
999a2bb3-e99a-50b0-94f8-60a5abbbfacb | note | 45LT / PB95 ¦¦ 3 ¦¦ 1000x1000x1000 mm
40e9a898-fc5d-56f7-a09e-7970cae8d35a | note | — — — — — — —
caf52696-f13a-5784-860e-8adce2463ecb | note | Standard / Specification - 2-32735.02-WSP-DR-UDL 0402 Rev 1
6edab29b-71cd-50c1-8823-0fc5bfddc07e | note | Verifying Document - Visual Inspection
3e141354-ee4d-5b26-8fca-853349d5c82b | note | Testing Quantity Required (based from schedule qtys) - Per tree pit
c7ae54ff-4900-5392-a30c-e78f57d65673 | note | Verification Activity: Activity - I
8d8d58fb-1038-5628-93a7-ffb2c514fe8f | note | Verification Activity: By - SE
241a32b6-adcc-41a7-bc48-ef92395964a7 | checkpoint | 4.2.5 - Timber Stakes
7395d724-e61d-5f57-8311-faab71e240f7 | note | Detail - Timber stakes used for landscaping must be of specified type, treated to prevent decay, and meet size and quality requirements.
03561456-d7f1-59ed-879f-63e8e3fdeca9 | note | ○ 50mmx50mmx1500mm H4 Treated Pine Stakes
72e102a0-061e-5f3d-b72a-8fbbde6c77e5 | note | Acceptance / Conformance Criteria -
bc7c1ba5-a1e8-5726-8e29-9b1d8237eef7 | note | — — — — — — —
d41301bb-4b49-58a4-9196-d2ac54391caa | note | TABLE 1
98de51d1-066e-5e91-817b-760618acd2f9 | note | PLANT SIZE (LITRE / PB) ¦¦ NO. OF STAKES ¦¦ TREE PIT SIZE
756d26e9-ebab-50cb-9b19-75394c5df0f8 | note | — — — — — — —
c217e824-69a8-5299-a6ea-a169208e8b6b | note | LESS THAN 15LT / PB28 ¦¦ 1 ¦¦ 2X SIZE OF ROOT BALL
4038e9a9-84bd-55fe-abfc-ded0bccd5663 | note | 45LT / PB95 ¦¦ 3 ¦¦ 1000x1000x1000 mm
f47dff36-7f39-56fc-ae0c-545708170efd | note | — — — — — — —
9a605133-0e08-5764-840c-8a5ade92270a | note | Standard / Specification - NZTA P39: 2013, Section I
8db64302-0bc3-5d8e-86a0-5d3142f30ed0 | note | Verifying Document - Material Dockets
3bd8726e-3da0-5741-b729-79683abee79b | note | Testing Quantity Required (based from schedule qtys) - Per order
b9727d07-6617-5fb0-8977-3df9cf02e815 | note | Verification Activity: Activity - I
1d9b3e37-f5df-5fd6-bc67-0e79dee0256d | note | Verification Activity: By - SE
530db255-64b6-4e02-abf0-1779a66c2e83 | checkpoint | 4.2.6 - Fertilising
770a1c03-e2fb-5106-b7f0-b6c40955ef96 | note | Detail - All plantings shall have two-year slow-release fertilizer tablets installed at the time of planting.
150e18e8-52fa-51a8-a346-635b97cba3f2 | note | Acceptance / Conformance Criteria - Fertiliser tablet placed in bottom of hole before planting. Fertiliser composition: 6:15:3 (N:P:K). Up to 14l is 1 tab, 45l is 4 tabs
3eb081a6-7ce6-50fc-a3e6-8312deaa0481 | note | Standard / Specification - NZTA P39: 2013, 3.13
810e051c-f161-5eb2-93e3-4a02e7ff2552 | note | Verifying Document - Site Records/photos
68964ab5-25f9-517c-8e12-244ac8627a96 | note | Testing Quantity Required (based from schedule qtys) - Each Area
54c9bbbf-12a6-5d6f-b92a-02012921270a | note | Verification Activity: Activity - I
91dea2d9-fd61-57af-afd6-6cc1b22b5875 | note | Verification Activity: By - SE
f0d92e33-db6a-46c2-b9cd-2fa02e92d5cb | checkpoint | 4.3.1 - Mulch Spreading
0c88a6a7-2ca2-5579-9430-d71e2214859a | note | Detail - Correct mulch application on flat sites
fd4cf15d-f644-5bee-bbb9-f1edacb89b23 | note | Acceptance / Conformance Criteria - On sites flatter than a 1:3 grade (1.0m high by 3.0m metres long), mulch shall be spread evenly to a depth of 80-100mm after settlement, over the planted area, creating an inverted cone hollow around each plant stem with a maximum 25mm depth around plant stems.
ca537df3-157a-5531-b9df-3af302be6bab | note | Standard / Specification - NZTA P39: 2013, Section G
4f2610d2-ee5f-5c2e-b1cd-4526e9789ba6 | note | Verifying Document - Site Records / As Built Survey
d3a4a0d6-6d4a-5c53-9f45-6cee6b7dbb05 | note | Testing Quantity Required (based from schedule qtys) - Each Area
a0fc951e-35eb-5de9-ab93-bb7e188e727d | note | Verification Activity: Activity - I
87b0c546-7e35-5494-bcb8-a2c6a7efc937 | note | Verification Activity: By - SE
79a20be1-5945-4e3a-90b5-3cecb1ba2336 | checkpoint | 4.4.1 - Pre Bentosure liner inspection
f0aa58a1-8002-5e3d-b696-5a382a998bd6 | note | Detail - inspect before installing bentosure liner
05bc3235-3b32-555e-8a65-3c0e6d9af4db | note | Acceptance / Conformance Criteria - Ensure subgrade is smooth, compacted, and free of sharp objects, debris. Confirm BentoSure rolls are delivered intact, labeled, and stored properly (off the ground, covered). Confirm panel layout plan and anchor trench dimensions are per specifications.
5060e12d-ffd0-5cb7-bc49-40b4b1e94a43 | note | Standard / Specification - Refer to installation guide
17962df2-f031-557c-9a2c-5752bad467e1 | note | Verifying Document - Visual Inspection/Check list
f1eb7081-02c6-5961-9846-5413f33e5a80 | note | Testing Quantity Required (based from schedule qtys) - For all liner areas
6a6e23de-e5f8-5434-98b8-96bd4f6c317d | note | Verification Activity: Activity - HP
e147826b-e0c1-5801-b71e-3f82ecd55cc3 | note | Verification Activity: By - SE
2a7242d3-e19a-4454-9d16-ed212599866a | signoff | AUTHORITY HOLDPOINT
c6da693c-a7d9-4775-9862-3a6144546bea | checkpoint | 4.4.2 - Bentosure Liner key Footing
d27cbef2-c906-558f-accd-b022f72d8b30 | note | Detail - Anchorage for Bentosure
af0b6f1f-ba4f-5c6b-96d3-6568d0696154 | note | Acceptance / Conformance Criteria - 600mm Deep/400mm wide Anchorage key in footing
3f7f0401-fd13-5c9d-9705-53212a66d8b4 | note | Standard / Specification - Refer to installation guide
8a3c7cbc-9a25-59d8-8893-59912dd5a055 | note | Verifying Document - Site Records/photos
4291b83d-117b-50f4-b733-b7f9fc7acaed | note | Testing Quantity Required (based from schedule qtys) - For all liner
f5d45931-bd7f-54db-b2e9-c23eff8d851e | note | Verification Activity: Activity - I
9ad8be5e-e975-583a-ad52-27c358061873 | note | Verification Activity: By - SE
ba5fd816-7480-4f0f-81d7-822d1882fc24 | checkpoint | 4.4.3 - Bentosure liner laps
b94b742d-0fce-5e94-a27e-da80787595de | note | Detail - longitude and latitude overlaps
b3ce3baf-1137-53a1-84aa-4c6401fb7ad6 | note | Acceptance / Conformance Criteria - Longitude 300mm/Latitude 500mm overlaps minimum
03b37cdf-c9f8-5fd8-8d2b-e54af851478c | note | Standard / Specification - Refer to installation guide
e0e73e9d-1fcc-51ce-8215-d0fd970ed713 | note | Verifying Document - Site Records/photos
2fac11c9-ad42-56a1-aff5-22a2055a7383 | note | Testing Quantity Required (based from schedule qtys) - Each Area
2840f7e3-93e0-5bbe-8eb6-dffc5eef95fe | note | Verification Activity: Activity - I
ac13117b-beda-5ea9-8155-f0c1e4f90470 | note | Verification Activity: By - SE
a6621a81-06bc-4953-b0f0-2c6d5a84b042 | checkpoint | 4.4.4 - Post Bentosure liner inspection
fb689b2d-304b-5317-b284-799570abf851 | note | Detail - Post inspection - after bentosure has been laid and before any topsoil is placed on top
fb9f2d92-5f0a-5eb5-a908-77ab565a676e | note | Acceptance / Conformance Criteria - Verify panels lie flat without wrinkles or folds.Check seam overlaps Inspect anchor trench dimensions and proper backfilling.Confirm cover soil is free of sharp objects and is at least 300mm thick.Inspect for tears, punctures, or wrinkles; repair as needed with 300mm overlap and bentonite application.
34526856-dd92-5e76-8468-ee1206a42f60 | note | Standard / Specification - Refer to installation guide
a490117d-a3dc-5e05-a783-e7fdced65100 | note | Verifying Document - Visual Inspection/Check list
c14640c4-eacb-5468-91f2-95b4c45cd2ba | note | Testing Quantity Required (based from schedule qtys) - For all liner areas
a58e0304-3481-5e79-9c0b-6cee6d6b6fd9 | note | Verification Activity: Activity - HP
d72002dd-8bff-5ed7-bfb7-d463052cb58f | note | Verification Activity: By - SE
90d25bbe-2056-4e8d-94c0-a0e4910c17e6 | signoff | AUTHORITY HOLDPOINT
295fdab5-6064-46ab-a01a-5516a4f965f2 | checkpoint | 4.4.5 - Bentosure Liner key Footing
af37d35e-64d2-5bfb-8db4-0b3eb3326a68 | note | Detail - Anchorage for Bentosure
2241ec6d-22d3-50fe-969a-c1bb239cb8b6 | note | Acceptance / Conformance Criteria - 600mm Deep/400mm wide Anchorage key in footing
91229bb1-9cfc-5933-8309-ac51583a0d59 | note | Standard / Specification - Refer to installation guide
c3aa3b52-a819-5b4a-9b16-d76ce3284c84 | note | Verifying Document - Site Records/photos
9c715b11-a12e-5d08-8d84-64415b96381e | note | Testing Quantity Required (based from schedule qtys) - For all liner
11ee6c53-3f83-580c-bc1f-9110550b0d85 | note | Verification Activity: Activity - I
bfe9269a-6aaa-537b-91e3-7aad69c5bdfa | note | Verification Activity: By - SE
d6be8597-7188-47fb-94ca-5c8efd40cdf8 | checkpoint | 4.5.1 - Weed mat laps
87d99fec-885c-58f7-b68d-9f7f6e8f4e04 | note | Detail - Lap joints
15e46d53-211d-56ca-a504-8d1504f6b7b8 | note | Acceptance / Conformance Criteria - On slopes steeper than 1:3 biodegradeable matting shall over lap 100mm between adjacent rolls and 500mm longitudinally
136a79a3-32c9-53b4-8291-800e5b843542 | note | Standard / Specification - NZTA P39: 2013, Section G
89f7fb94-b044-5bfd-b587-a25a10b709cf | note | Verifying Document - Site Records/photos
ba7ce572-01e6-5795-9132-98e4b581a9cb | note | Testing Quantity Required (based from schedule qtys) - Each Area
f81b5fbf-3156-5e52-a146-bcaa78354cbd | note | Verification Activity: Activity - I
2c6576af-a54a-54ce-b6fa-2956e1b2257d | note | Verification Activity: By - SE
8abaded4-123c-4f6a-ae0a-0b2bbd8da63b | checkpoint | 4.5.2 - Weed mat keys
fdb32903-ef11-5007-aca3-73c25a76783e | note | Detail - Key in edges
87676b80-1806-5b4c-9495-aae28d27e964 | note | Acceptance / Conformance Criteria - On slopes steeper than 1:3 edges shall be keyed in to topsoil 150mm x 150mm
625acfb5-3bef-5ced-bf31-3c16a2bc0cca | note | Standard / Specification - NZTA P39: 2013, Section G
79ce59a3-17af-537b-b90b-6ffb56c85213 | note | Verifying Document - Site Records/photos
d5471712-9b1f-5706-85fb-f2fd81ab2de1 | note | Testing Quantity Required (based from schedule qtys) - Each Area
c41f4312-f791-5312-b560-b3741fafdb4d | note | Verification Activity: Activity - I
90974446-aefc-5952-b1fa-a9f94faf87ec | note | Verification Activity: By - SE
695f53e0-e66c-4c9c-8129-897789de27ad | checkpoint | 4.5.3 - Weed mat pins
638515a0-7692-5ad7-bea4-4082c6bb564a | note | Detail - Freqency of pins
be83d1f6-730b-55db-a933-b8a140a8bc63 | note | Acceptance / Conformance Criteria - On slopes steeper than 1:3 biodegradeable matting shall be pinned with frequency of 2 per m2 min.
a2b64ce9-643e-54ef-80d4-451f28b95dd8 | note | Standard / Specification - NZTA P39: 2013, Section G
22d8979f-7ddf-5149-9395-f5deee442de2 | note | Verifying Document - Site Records/photos
634e8c10-3ecc-5a6e-86d6-e2d5f7e22da3 | note | Testing Quantity Required (based from schedule qtys) - Each Area
7e33322b-6a2b-5f8e-a5e9-df9e389505f6 | note | Verification Activity: Activity - I
ac483f94-c6dd-5f6a-a5c2-cc8f9b0d9071 | note | Verification Activity: By - SE
1bafbd6b-8b0a-4049-8395-862b8b2728ab | checkpoint | 4.6.1 - Establishment of sown areas
e7899eef-2fa1-5acf-bb0e-6fc9b9c523ef | note | Detail - Apply grass seed as soon as practical after area is prepped. Protect newly established grass areas.
c729c17a-f107-5fbd-82bf-ecccc57d28e3 | note | Acceptance / Conformance Criteria - Newly established grass shall be protected from damage by pedestrian and vehicular traffic until grass has reached a self-sustaining state. Newly grassed areas shall be maintained with regular mowing (90mm-30mm) ensuring that all clippings are removed from adjacent hard surfaces.
0add6dcd-f1b0-5952-95f2-bf1db61f774e | note | Standard / Specification - NZTA P39: 2013, Section G
afe6c79f-58af-55f1-be88-21b44fac348b | note | Verifying Document - Site Records/Photos
ea9c5038-ff43-53d1-9ceb-03b96087bf76 | note | Testing Quantity Required (based from schedule qtys) - Each Area
13a790c0-fc5a-5e3d-8db7-21fd9b70c556 | note | Verification Activity: Activity - I
46c96d9a-2ee1-5526-a01d-a255ad8088e5 | note | Verification Activity: By - SE
034beb8e-f93b-41b0-8ba4-23dfff2e9630 | section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
c2ed7d92-366d-42f0-bf02-173d7cb9bed7 | checkpoint | 5.1 - As-Builts/ Red pen markup
0f3d054a-6507-511d-8682-61e118e3728f | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work.
056ce52a-7789-5626-883a-68a7fb98a0c4 | note | Acceptance / Conformance Criteria - Record of work completed
7614e07a-81b1-5b92-b2b8-a692965f2a40 | note | Standard / Specification - PS 16.7.6
d92aef66-3273-5b88-add1-a3ef30e504a6 | note | Verifying Document - Red pen markups
cc19ae0d-30c3-5644-96e3-4bdc07e628cb | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
c0b6e686-4f17-57e2-ab5d-9b0e625652ee | note | Verification Activity: Activity - D
b5524563-2b39-5b38-ae8e-049650b3344f | note | Verification Activity: By - SV
55c27316-02b1-4b45-9c15-381307640434 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
363d02c5-c49c-5944-baa6-1343290259ec | textbox | Contractor's Rep Name:
009e9d3b-491f-53d2-b3ea-fd5fa539ea4c | textbox | Engineer's Rep. Name:
76ad72eb-8a43-56a4-9f1b-2009ee129834 | date | Date:
1f1d9a39-14b6-4be2-8d65-598b1ee9e5ef | signoff | Add Signature
c8d1e418-0de5-47c8-8d7a-6d870334a545 | checklist | DN1210-011 ITP Wastewater Open Cut Rev 0 | itp | DN1210-011 ITP Wastewater Open Cut
0f588adc-77f9-48e7-9aad-54c4b1da8537 | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
299075c4-5c9d-4274-973a-04447a19d1b8 | checkpoint | 1.1.1 - Pipe Laying
69307b7e-c0c1-532e-b07d-ba0b52a3d24b | note | Detail / Activity - Method statement
1c27c28d-8dd3-545f-87b0-10d8f63a1dda | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
09bd9dab-b8eb-5a15-8f9f-9bae701fd467 | note | Standard / Specification - PS- 22.3 Appendix V
a7f808e5-1c36-5f4f-b03c-4d8a45f3bb52 | note | Verifying Document - Wastewater Construction Work Pack - Open Cut Sign off
d7bf0fb2-e732-5759-960e-6467e9db3b44 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
aaed5e31-bb50-51db-8467-12838ffa24d7 | note | Verification Activity: Activity - HP
309c64ae-b0ae-5dd1-b980-56720c0b08a3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
27bcd6d2-5684-5c86-8637-274294e91b11 | note | Verification Activity: By - ENG
b9581f36-1f1b-4052-8a86-a417d7d54eff | signoff | AUTHORITY HOLDPOINT
a204e3aa-26b3-4be8-b9e5-4f604ebb02f9 | checkpoint | 1.1.2 - Butt-Fusion Welding
38d11196-8824-51c6-b260-1f028c74a6d1 | note | Detail / Activity - Method statement
d84e6b16-1a37-5441-95ab-af41a20d866e | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
a0ff76dd-5abc-5506-84b3-af4540100af6 | note | Standard / Specification - PS- 22.9.4
78ddb59f-3f95-5b8b-b4bb-fde293cf7279 | note | Verifying Document - Wastewater Butt-Fusion Welding Work Pack Sign off
788ae0c5-622a-5b17-9509-2e8ec3f716af | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
15d86717-51f6-59af-a3f0-6edd9326e50f | note | Verification Activity: Activity - HP
1706e69c-85a4-51bf-bdc4-03af7cea8fe0 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6f2f14af-92b2-5eab-8696-5671639fd783 | note | Verification Activity: By - ENG
6ffa504c-8ddb-43e1-8c30-c916a0ceab9b | signoff | AUTHORITY HOLDPOINT
3388db01-c23a-4674-ae24-d92ca51bf4e7 | checkpoint | 1.1.3 - Electrofusion (EF) Welding
1b3b6d42-9999-57f8-b7ec-0c6988804de1 | note | Detail / Activity - Method statement
b7ab8378-4ef3-584e-8114-dcfad7e36d01 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
e1dbcab1-f463-5905-a6e7-2948db64ff74 | note | Standard / Specification - PS- 22.9.5
2fcddb95-7437-53e4-8246-c5f350a9ed13 | note | Verifying Document - Wastewater Electrofusion (EF) Welding Work Pack Sign off
325cb855-dd93-5844-ad44-67fa255c45c8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
c0547089-3351-52f1-809c-d6f0b162bb65 | note | Verification Activity: Activity - HP
3710d36e-b605-5a3e-b8eb-af7e5ba043f3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a17f6ab0-aaea-511c-82b1-1c47ac6d477c | note | Verification Activity: By - ENG
adb5dd0f-a3c9-4723-80a0-44d248faa341 | signoff | AUTHORITY HOLDPOINT
0122b533-1e35-4e7c-9cb9-b0f2b272cafa | checkpoint | 1.1.4 - Pipeline Pressure Testing
426a1ab0-f2ff-5859-ab7f-a5370fd8fbe8 | note | Detail / Activity - Method statement
66c5521d-e8f1-5603-9cdc-f70eb7db7a92 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
3f5c0943-dddb-5597-bc56-21d3367636b2 | note | Standard / Specification - PS- 22.3 Appendix V
69e09f37-166f-51d6-a427-30b47b42e94e | note | Verifying Document - Wastewater Pipeline Pressure Testing Work Pack Sign off
a7d78aba-f5f6-5ea6-bd3c-286fff9a683c | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
9c68304e-bb32-52f4-ac97-d0e2a515e1e3 | note | Verification Activity: Activity - HP
01fd9b37-e70d-5373-955f-2f173071be6b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
36fa88a2-4cb1-53c5-ae12-af67abd81b5e | note | Verification Activity: By - ENG
5a233e3d-8bda-4ac7-b265-1412daf6457c | signoff | AUTHORITY HOLDPOINT
e69e77f6-387a-4b57-9631-ebba6768fc5d | checkpoint | 1.1.5 - Extent of Line Setout
0c00b8ef-6558-58b6-944c-d122bb37eb8c | note | Detail / Activity - Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings.
4a7f6042-a3d1-59d6-8c63-2800645d12fb | note | ○ Identify any clashes before construction.
4c7f3cb0-7025-5868-8044-909048992288 | note | ○ LOT - markup
6270c23e-106d-544a-97a5-df33f0725b6a | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
4daa92a8-8234-57be-b970-bd996363bee6 | note | Standard / Specification - Design Drawings
3cb386ef-f18c-5f7c-8579-75864761b59e | note | Verifying Document - ITP Sign Off / Mark-up
31ff7e7f-e83e-51e1-a283-27d1cef67edc | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
813a6e92-8aaf-5a00-99c7-57d7655dd186 | note | Verification Activity: Activity - HP
7b5b46f0-f72f-5c7f-9e79-cf709c01a3e3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
461ef13c-8efb-5564-ab87-86790b676801 | note | Verification Activity: By - ENG
abe7f8a1-8a1a-449a-83eb-70b5c4b1fc72 | signoff | AUTHORITY HOLDPOINT
047d7115-2e03-4997-b839-b2b091c2fb1f | checkpoint | 1.1.6 - Existing Wastewater system (If any)
e7900500-da4e-51f7-9a04-02ed56a13279 | note | Detail / Activity - Confirmation of existing Wastewater network.
328ec7f9-2c75-5301-a372-8b709db28c8f | note | Acceptance / Conformance Criteria - Survey Informations
30cb13f6-65d2-573d-93b3-443452b5b830 | note | Standard / Specification - Appendix V
1ef3df51-82a4-5912-9a9f-57f96b6b8241 | note | Verifying Document - Survey data
d8c04ed5-5bda-54e6-b83a-650b388522bd | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
f2c60e7d-6ef1-5983-a3a8-bebe9fa57c9d | note | Verification Activity: Activity - HP
86e9c52e-f167-5ca2-b750-66debd0f65e3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a1c70f5e-abc1-591b-8ed5-eb4c76056786 | note | Verification Activity: By - ENG
f09f7f93-7fb4-4eac-9c5a-886160cae258 | signoff | AUTHORITY HOLDPOINT
9362e772-38cd-4fcb-b8a4-25e0f0559541 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
6b8aecea-823b-404b-8911-253aa1e50b6c | checkpoint | 2.1.1 - Material grading: Materials (Imported sand and AP20) MDD
63d4c020-79c7-560c-b789-6d9a7d69490c | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone compliance.
36cc880a-e1aa-58b6-bad8-d307d941db01 | note | Acceptance / Conformance Criteria - Embedment Zone Material accordance with AS/NZS 2566.2
eb81b2d8-3cb6-5df1-8988-6892d510a53c | note | Standard / Specification - PS 22.13.1
0512002a-a118-5651-b204-bba9216a3c7c | note | Verifying Document - Lab Test Report, NZS 4407.3.8.1
e3b7513e-0a3f-5c87-8899-173fb36b6587 | note | Testing Quantity Required (based from schedule qtys) - 1 Test for each additional 1000m3
513142f5-d2f2-5cdf-a1ba-cd20c625d26a | note | Verification Activity: Activity - HP
03843f2a-1790-5568-af5a-0db07eb1f79a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b5ab0006-723d-565d-8022-272889787130 | note | Verification Activity: By - ENG
97779da6-9fce-442e-9e80-8116c3bb3a15 | signoff | AUTHORITY HOLDPOINT
b685762c-c35b-49a8-8cec-eb2498c8b94b | checkpoint | 2.1.2 - Material grading: Materials (Imported sand and AP20) PSD
15c81c65-b31f-5550-b001-d139322edadd | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone compliance.
a1e1037f-48cf-5297-9ae7-bc24869f4602 | note | Acceptance / Conformance Criteria - Embedment Zone Material accordance with AS/NZS 2566.2
f141b141-5b4c-5f71-9c73-663f10907516 | note | Standard / Specification - PS 22.13.1
d08756c2-edfb-58ed-baef-2c3b66787b33 | note | Verifying Document - Lab Test Report, NZS 4407.3.8.1
5c96fff6-e38e-5ba9-9a22-20e0f1f52f3e | note | Testing Quantity Required (based from schedule qtys) - 1 Test for each additional 1000m3
f80c6562-4556-557d-b558-f8b6549c44c2 | note | Verification Activity: Activity - HP
3df68d53-30d9-5639-8ae9-6f2b73e556c7 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
91f5846d-d38b-50f8-b37d-a5a16def689a | note | Verification Activity: By - ENG
8f5d7486-3a29-4f8c-a0dc-7ed9f990943d | signoff | AUTHORITY HOLDPOINT
f1faa230-8b06-4059-882e-bd84ebbbf52c | checkpoint | 2.2.1 - Material grading: Materials (Excavated Pumice GAP65/AP65) MDD
0e190bb8-14c4-5edd-9122-45c3e9e6fb8b | note | Detail / Activity - Trench Fill and undercut material compliance.
2d123c17-f0d4-59ef-b5b0-21aff1d6636b | note | Acceptance / Conformance Criteria - Trench fill - TNZ F1
6223bab8-f7b0-5547-a339-b5f7197dd0e3 | note | ○ IFC Drawing WST-0320
ca5d7a67-8001-54ed-b682-30ad53629c9c | note | ○ PS - Stormwater Specification
d9003dea-90c0-56fd-a99c-838a60064715 | note | Standard / Specification - PS 21.7.2
0b15375b-7038-5338-a5b9-26a72f72d751 | note | Verifying Document - Lab Test Report, NZS 4407.3.8.1
cbcedeec-0df5-5d3d-aa49-b3a152bf14d0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test for each additional 1000m3
7b1649bb-9a73-5df0-9e41-042f900b7086 | note | Verification Activity: Activity - HP
f39a9b25-8abb-5c15-9d13-a00dc9690a81 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
247f11f7-a363-5eab-b231-4a51c12309ca | note | Verification Activity: By - ENG
5113fb71-e3ae-4429-963e-7af11ccd5812 | signoff | AUTHORITY HOLDPOINT
6a97fe5f-e4b5-45e9-a021-d0e0f255be9c | checkpoint | 2.2.2 - Material grading: Materials (Excavated Pumice GAP65/AP65) PSD
01d79828-56bd-5f3d-9340-dbb50cbf4dae | note | Detail / Activity - Trench Fill and undercut material compliance.
2899101d-b38c-5aa5-9ea0-48f49cd5fc92 | note | Acceptance / Conformance Criteria - Trench fill - TNZ F1
db53130e-b7f7-592a-a190-f16a18f66915 | note | ○ IFC Drawing WST-0320
71aad77c-4990-55f5-bcac-659f1db527a8 | note | ○ PS - Stormwater Specification
965b0172-b85b-5eba-9037-05cce18670fa | note | Standard / Specification - PS 21.7.2
fcd82aff-11b7-5aa6-9c44-b2c57080303b | note | Verifying Document - Lab Test Report, NZS 4407.3.8.1
4c4072a1-86a3-5f79-ab1e-7c61837b1a20 | note | Testing Quantity Required (based from schedule qtys) - 1 Test for each additional 1000m3
f6a9eb63-b5ec-5768-8712-ad2d13d6ec1e | note | Verification Activity: Activity - HP
52bd6ddf-7f62-5a56-b0c4-32400cc78faa | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1a11dd84-38ca-5f47-97a5-332750f44593 | note | Verification Activity: By - ENG
9e7b18bc-8dcf-4a4f-a358-78e04953a19b | signoff | AUTHORITY HOLDPOINT
65e8758a-c5c9-4834-bf5e-9d488418cf02 | checkpoint | 2.2.3 - Weathering index: Materials (Excavated Pumice GAP65/AP65)
b36db8d6-98ee-5e98-a38b-189c444f5ce2 | note | Detail / Activity - Trench Fill and undercut material compliance.
b9a1a652-9d0a-557c-a003-49adbf5e4605 | note | Acceptance / Conformance Criteria - Trench fill - TNZ F1
72d796cd-d390-552b-848f-82d308b58548 | note | ○ IFC Drawing WST-0320
1a6351da-53ca-560a-a7e3-ee372b5f9e8a | note | ○ PS - Stormwater Specification
1c59e22e-c7bf-587e-98ff-f1eb866217f0 | note | Standard / Specification - PS 21.7.2
fa624fa9-1b4d-55b2-bcc6-eb8db18d3f3f | note | Verifying Document - Lab Test Report, NZS 4407.3.11
c24c3816-5e1d-54be-8138-c591dd38a5b4 | note | Testing Quantity Required (based from schedule qtys) - 1 test per source
f55be268-5e98-5898-b33d-8dc582090939 | note | Verification Activity: Activity - HP
261a3799-7012-54a2-9446-b2a01a63a65b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
122b264d-df0c-5fdf-ac0e-9f9ade9469ca | note | Verification Activity: By - ENG
564b4e3d-5d5f-4cf5-a357-55d6f16f706a | signoff | AUTHORITY HOLDPOINT
e2ab8314-be9d-4c97-a2e1-56cd93b83481 | checkpoint | 2.2.4 - Crushing Resistance: Materials (Excavated Pumice GAP65/AP65)
853bf6b1-8a33-5dc1-8a77-d840829fb027 | note | Detail / Activity - Trench Fill and undercut material compliance.
f0421502-cfc8-5633-b82b-d9d7bf31869e | note | Acceptance / Conformance Criteria - Trench fill - TNZ F1
c7020bc6-3654-5b5c-950d-34a1e692aa11 | note | ○ IFC Drawing WST-0320
c71d053a-28f0-511d-9767-de9773228300 | note | ○ PS - Stormwater Specification
b1a3a047-c1e0-5a63-a890-5d2f40f58ea3 | note | Standard / Specification - PS 21.7.2
478fccf4-1894-5a8d-b5c2-a666eaca3ec8 | note | Verifying Document - Lab Test Report, NZS 4407.3.10
375d8d45-e020-5db7-a3ad-b40dbfd48b8b | note | Testing Quantity Required (based from schedule qtys) - 1 test per source
7ee4ad42-aa73-51fb-9b6c-b8d78aae0f0b | note | Verification Activity: Activity - HP
a556b06d-e568-5e0f-8e7e-229e01cbcc9f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e0bbdf21-3ace-54f7-b38c-ba3395741ba5 | note | Verification Activity: By - ENG
d0dbf79d-af56-4147-a26d-3d8b43a8b9f9 | signoff | AUTHORITY HOLDPOINT
445cdfe8-afc3-4a64-88cc-3055af15d31b | checkpoint | 2.3.1 - Pipes (PE/ Sleeve)
cd6e0332-f215-5e0c-b2a8-0e226e9b33e9 | note | Detail / Activity - Manufacturer's record and location of extrusion plants.
dbe223f5-9518-59c8-a75b-cf1d7e16ed28 | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
674e8b82-da68-5a9a-8612-8f94c4c74d87 | note | ○ Full Traceability information and certification of analysis for the resin batch.
058d1801-6abc-5f4c-842c-27cad6fe7b96 | note | Acceptance / Conformance Criteria - Engineer approval
c8a7e04e-bd39-55e9-9bfc-76d0afe33f91 | note | Standard / Specification - PS-22.4.1 (d)
83f9ba81-b91d-5e17-8abb-8095755b5422 | note | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets.
eafcb51c-e3d4-511a-97be-64517a9dffa4 | note | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
f970312d-0329-5825-9b48-00423a7603d1 | note | Verification Activity: Activity - HP
217c5d85-a00d-53ed-b3ec-3fde857780a8 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a3932c0e-2e38-5095-b626-4244fc48308d | note | Verification Activity: By - ENG
cb03afa8-3358-4292-8019-c79b8a47ae84 | signoff | AUTHORITY HOLDPOINT
6119b3a3-89a6-403a-9807-a95bb1cb56e9 | checkpoint | 2.3.2 - Green Dome Odour Filter
efd93454-9472-5b63-bda2-d06770be5323 | note | Detail / Activity - A Green Dome Odour Filter (Model GDOF36) complete with DN150 ducting.
720abfc3-4f05-5fb1-ab92-c95e59d733d6 | note | Acceptance / Conformance Criteria - IFC Drawing 0323-1
ae57b777-ec38-532b-bc37-69c89d5734f8 | note | Standard / Specification - Model GDOF36
4bf0d5b9-1c37-5f29-9c7e-8eab9c86f2e4 | note | Verifying Document - Delivery Dockets
ed1b9603-b8dd-5e3c-93d2-05eafed2ab3c | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
b9fe6ff9-b83b-5780-b0cd-126bb4671201 | note | Verification Activity: Activity - H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b490a747-4277-5fe8-a975-89ea65b8fc0c | note | Verification Activity: By - SE
67466b53-61fd-429d-b080-0d2439709835 | checkpoint | 2.3.3 - Valves, Adaptors, Flanges and Fittings
a36e4d36-ebed-5524-915f-ac9a90406a88 | note | Detail / Activity - Have a pressure rating no less than the designed pressure.
044d2234-e989-5155-855e-f60ae4b45d8f | note | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
0d53f2ef-e118-5b2f-83f8-d1e499b0958f | note | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
9713a556-ba0d-50f9-a9a9-a901d927ff34 | note | Acceptance / Conformance Criteria - Engineer approval, AS/NZS 4129
d9325437-abae-5c0e-8c19-9bbe6b1cff05 | note | Standard / Specification - PS-22.4.2
64834250-5f3b-58cd-9eca-d8c7356ad9c4 | note | Verifying Document - Delivery Dockets
1623f670-4401-5d52-9e94-33509000b72f | note | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
17dc9f7a-a0fe-5b3b-a4d6-d5205f522821 | note | Verification Activity: Activity - HP
46795a2c-c679-5bdc-b4d0-c5c70664a67b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ca9c20d9-8d0f-5664-86d8-634cb0f9c595 | note | Verification Activity: By - ENG
18c104a6-8a20-4051-b425-828ef538ba69 | signoff | AUTHORITY HOLDPOINT
0b7ade51-07f2-4b67-9b00-ed63b60b05e8 | checkpoint | 2.4.1 - Pipe and fittings. (PE100- DN200 PN10, DN180 PN10, DN400 PN16, DN500 PN16).
db646308-549a-5feb-bc5f-705d0fee2823 | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
c43ff3b8-17a3-5b54-a02f-cff46382c972 | note | Acceptance / Conformance Criteria - As Per Drawings
34e3c333-4fe6-5449-810b-37a2cd07740f | note | Standard / Specification - Design Drawings
5cc7180c-91a5-580b-8563-fb9d4c03702a | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
4c8c600b-f2db-50cb-9c51-98b533b40049 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
e612cc4a-6169-5ad5-92fb-20a03451c1cb | note | Verification Activity: Activity - H
56d235bc-1c94-5e90-896d-1e0d3d7a696f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
07ce395b-016e-5ac9-82aa-ae0f846a9e34 | note | Verification Activity: By - SE
33d64e49-b6de-46a9-b5c5-184274781ff4 | checkpoint | 2.4.2 - Valves, Adaptors, Flanges and Fittings
2abae2e3-eb07-5552-8434-d882dd681a5c | note | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
abe61d51-99f0-53ee-a4d2-83a6969a0b7d | note | Acceptance / Conformance Criteria - As Per Drawings
f58d87d3-7844-5cb4-9854-64efb4d1ad88 | note | Standard / Specification - PS-22.4.2
5131af6d-79bb-56ab-bd3a-5a4ae3a07b6a | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
89bbb1a0-422a-5686-8b8f-d4252f26e0be | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
f8e0b079-2702-52da-99e9-a5b7b73be253 | note | Verification Activity: Activity - H
4607d824-47b9-5108-a578-e945d1f3da23 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
87b143cd-e0f6-5e7f-bcf4-cfbe9b0edc01 | note | Verification Activity: By - SE
369e361e-4918-4ef4-b481-3ee248ec9670 | checkpoint | 2.4.3 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
99f42f5c-420b-5ac4-85f8-b6807ab262f0 | note | Detail / Activity - Confirm Specification and material in good condition.
f8c61ea5-3563-5ec9-8d98-f942a265f3f2 | note | Acceptance / Conformance Criteria - Site Engineer Approval
45ab8368-5356-51bb-a6cf-a1d92ccfa025 | note | Standard / Specification - PS-22.4.1
19106153-823f-5506-9b49-f50829ba1867 | note | Verifying Document - Delivery Dockets
3add0376-a722-5a5f-9dcd-e9db946b7575 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
4deeac4a-32c1-517e-99ab-ced5f706ae72 | note | Verification Activity: Activity - H
9a507282-b7a5-5796-b8d9-4dc5c4da826b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8e0824c5-08c9-5ef3-b817-aac21582cffe | note | Verification Activity: By - SE
cac7fbdf-6df4-4818-8a59-3791c6ee356c | checkpoint | 2.4.4 - Bidim/Geogrid
fd836e45-9367-5541-be45-1aacf57f7aa6 | note | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
3ca5aaf9-f46d-53f6-b9d6-599aaa6ca5cc | note | Acceptance / Conformance Criteria - Site Engineer Approval
ed0095a2-f6a5-5690-8a61-44bb366498a6 | note | Standard / Specification - PS-22.4.1
2ee600c4-3cdc-5cf2-b147-ffdb5d2c60fe | note | Verifying Document - Delivery Dockets
efe23815-05bb-5216-9c66-2013a1fa8027 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
12a28ac8-39f2-5e24-b680-37311fc02b45 | note | Verification Activity: Activity - H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
27acb9bd-c281-5272-92a9-23f1701d9398 | note | Verification Activity: By - SE
10bd6aca-7fc3-4fb4-b0ec-872d5596ccf5 | section | SECTION 3 – CONSTRUCTION ACTIVITY
3642cfb5-a232-495f-a3e9-b353ac249617 | checkpoint | 3.1.1 - Foundation Compliance
5b9ecbc0-3a66-5230-9d9e-21ccbb2d8151 | note | Detail / Activity - On Granular or Cohesive Material
276c50a1-6b35-5d08-881e-e934c36a3228 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
291b0c66-d4d5-5354-a277-0570736cc2ae | note | (Or)
a0a0e25a-3c01-57eb-bd49-7e9cb43d7aae | note | ○ Cohesive Material: Vane Shear Strength 70kPa
12adaa71-3a1b-549f-80cc-137ee12cc373 | note | Standard / Specification - Appendix V
da7fe8d9-c4ff-548f-9914-df92ec53cc3d | note | Verifying Document - Scala/Shear test result
f6dff767-dcc5-5c8a-9a2f-f2fc04aa1b6c | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
f3df22b4-835d-5c25-ad86-fd08b76ee3a0 | note | Verification Activity: Activity - W
cc4b79a4-46b0-53fa-94a3-030a818a1313 | note | ○ Review of text reports/records or other evidence of compliance
8d631a94-a6a5-58a8-bee5-688cd4b4dd95 | note | Verification Activity: By - SE
0c78897e-586f-4338-affc-79675371ad5e | checkpoint | 3.1.2 - Undercut approval
8ee6f765-88ae-5687-ad7c-1a7f43d57b80 | note | Detail / Activity - Trench Foundation
96c69c00-ba57-5367-b2eb-f71768d425c0 | note | Acceptance / Conformance Criteria - 300mm Max cut
54da3093-3972-5338-8f7f-5dfa7dbde26f | note | ○ IFC Drawing Sheet 320
c1828a75-275b-54e3-b65d-790e80a4a147 | note | (Or)
8100c88b-bf9c-510e-bb66-169a27f8691a | note | ○ Engineers approval
a45504ce-a4bd-5b2c-ba00-94f36fbb4788 | note | Standard / Specification - IFC Drawing WST 0320. AS/NZS 2566.2/2002
1814587f-523b-578f-8940-d34f7c242338 | note | Verifying Document - Lab Test Report / Wastewater line record
158f7eef-4014-5ff5-93e9-a42f6d401a46 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
027078c9-fd13-5f44-9929-6ef3b0beeb11 | note | Verification Activity: Activity - H
c01f7e4d-f088-55f9-8065-9c44cf4209e3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0502a114-cb87-5a2f-9913-e346638f4256 | note | Verification Activity: By - SE
0270bad1-a6bb-4561-a980-0fb3c4bdb887 | checkpoint | 3.1.3 - Undercut Backfill Compliance (PAP5)
34ec93f5-a982-5d40-9c3f-96ff40f37ea2 | note | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
94c94f44-aba0-520e-bb38-43fccc076285 | note | Acceptance / Conformance Criteria - Visiual Inspection
cc8b006e-5deb-5ad3-91ad-a7f984e48993 | note | Standard / Specification - IFC Drawing WST 0320
6ccacff5-aa4b-5dc0-b147-b6a776045d90 | note | Verifying Document - Lab Test Report / Wastewater line record
9c9c62ff-ad3b-5f16-86e0-ec8f2429a074 | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
cfac9e27-1487-55da-a2ba-7ad80b76dd69 | note | Verification Activity: Activity - H
09f9fe2b-2c85-596b-af1e-53006f14b691 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c2fc6cdc-2e59-5624-b243-51a2500ee140 | note | Verification Activity: By - SE
125b5a66-97e2-4b8e-b83b-cd3d1b096ad2 | checkpoint | 3.1.4 - Bedding Zone Compaction Testing (PE Pipe)
c2b95ca8-0431-5095-bb35-88043de97b95 | note | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand or GAP20)
15fb79c9-7045-5196-b00f-76c8c962afe5 | note | Acceptance / Conformance Criteria - Bedding Zone:
510faa0f-1204-5d6d-ba1b-766e8698f5bb | note | ○ 100mm minimum thickness (compacted) over the bottom of the trench.
6ba336f5-9422-5575-b058-6a11ea12abc6 | note | ○ Minimum Compaction - Trafficable 95% MDD and Non-Trafficable 85% MDD
f201301c-2a6f-5666-ad05-49d2a7c3abfa | note | Standard / Specification - IFC Drawing 0320-1, AS/NZS 2566.2/2002
2ee42e88-f276-59f2-8e0f-553d41023b8a | note | Verifying Document - Lab Test Report
d9185c1d-b149-57ac-9752-c6d0034c8282 | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 20m evenly spaced intervals.
e98a47eb-c7af-5c75-8a5c-2540f09c454d | note | Verification Activity: Activity - H
3001de09-4099-565c-9688-542be5c5d059 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5e982e1d-78fc-5cfb-835b-3b020430ae68 | note | Verification Activity: By - SE
ead767a0-d2a0-4add-ab99-134e777d80bf | checkpoint | 3.1.5 - Laying of Pipes
78cee73a-55dd-5716-82d7-b14a1428add9 | note | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
f034a005-c4f0-5ea9-8286-f81f79eec0fd | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
568842f1-d6d3-561b-8f8b-d27e379105d0 | note | Acceptance / Conformance Criteria - As Per Drawings. Facing upwards.
73b71578-5c34-500b-ae1c-826c0eb0ebbc | note | Standard / Specification - PS22.7.1 C
4f8a32c0-6c1e-5d96-9506-b5656ccf6645 | note | Verifying Document - Visual Inspection / Wastewater line record
2dcb6974-87c4-5bb3-873a-ead9dafdfeb0 | note | Testing Quantity Required (based from schedule qtys) - Every Line
6e0609a0-ce1d-5c01-9d97-d3315f85f337 | note | Verification Activity: Activity - H
b3384957-e2af-5499-962e-f9175e266a6c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0ca41f10-ea1e-5310-b021-5e7d1be42c1b | note | Verification Activity: By - SE
2ad4f35d-a568-4ab4-be8f-9a72c06e9c65 | checkpoint | 3.1.6 - Pipe Installation on Curved Alignments
993176c7-1da7-506b-98fb-7fe03b8c77a4 | note | Detail / Activity - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
8a75ea21-ddab-5c9c-a13a-1efcd7106369 | note | Acceptance / Conformance Criteria - AS Per POP 202
bd6fbfd8-ef63-5e6a-bc8a-16fe25b3b378 | note | Standard / Specification - PS 22.7.1 D
71db1f3f-210e-591d-ab77-5297f18f115b | note | Verifying Document - Visual Inspection / Wastewater line record
5c5802d9-7d97-52a5-8680-f5dd16637424 | note | Testing Quantity Required (based from schedule qtys) - Every Line
a58d9027-ea8e-51c9-9970-5e07a8d9eda2 | note | Verification Activity: Activity - M
9ff1be09-61aa-50c3-84fa-ab31e3d9d1f4 | note | ○ Monitor on Random Basis
58e93ded-44de-5997-b523-edcadad09714 | note | Verification Activity: By - SE
87887334-82ca-4a3e-84ae-d36b69672b4d | checkpoint | 3.2.1 - Flanges
2058549d-f52c-5e6d-99c4-a049dc776a42 | note | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
d3a5169c-01ad-583d-822f-5dc5ab6c63d4 | note | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
b31d2664-7542-50d9-9a9b-e37c7978d99a | note | Standard / Specification - PS 22.7.5
51c24cc4-9674-570c-b24d-7d2fbb256649 | note | Verifying Document - Visual Inspection
4af85927-d398-52e0-9ee7-872007d7be67 | note | Testing Quantity Required (based from schedule qtys) - First flanged joint
daf7aa0b-928f-5196-947f-72cb32757c1e | note | Verification Activity: Activity - HP
362f27aa-d758-5e61-b6b9-d744255eb91a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3b6625d2-f611-559a-b309-a2409fd66d6c | note | Verification Activity: By - ENG
1a183f05-a77f-44ba-8daa-e94233dce801 | signoff | AUTHORITY HOLDPOINT
0ea35940-b246-41f1-a252-d517907e54b2 | checkpoint | 3.2.2 - Bends
c6fa6617-fc1a-5cbd-aad2-5536b4b9ff59 | note | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
5ac2732d-583f-54d6-b330-0de6d8bf7466 | note | ○ Fitting must meets the same PN rating as the adjacent PE 100.
bfbe51cd-36d2-5af6-9529-532b507fc68b | note | ○ Fittings must be suitable for producing the joints shown on the Drawings.
2ceabf2c-696e-5029-9dcb-a784314dc8c8 | note | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
b0bcdcef-f827-5282-ba0e-ac562c6ffbf8 | note | Standard / Specification - PS 22.4.2
3335dd70-9b76-5973-bfee-f94ca631a20e | note | Verifying Document - Visual Inspection
fa9d1ab7-b406-5646-b0cf-73d3d354d6e8 | note | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
86c8107d-0527-552a-8601-1b2468691344 | note | Verification Activity: Activity - H
96c01fdc-7f4b-55e1-9254-89455b34f9db | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8e18b3c5-5d5e-578f-89d1-925546834eba | note | Verification Activity: By - SE
c68fba1d-f1d3-4f3c-a4ba-02ac5f7726ce | checkpoint | 3.3.1 - Butt-Fusion pre construction weld test
4d51a74a-cabe-5053-affb-a7f2e1baa5cb | note | Detail / Activity - One weld on the most common size of pipes used for the project.
195b8545-0b54-57f6-9706-fbc548df36cb | note | ○ One weld on the thickest wall (highest PN) pipe
fed9789a-ff88-56ba-a967-20bd7ad6d505 | note | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode.
0288af2f-fdd2-5675-bb6e-ce4a89b23885 | note | ○ WMS Report.
2d5fc79c-fe0f-5054-bcac-ad55c3f7a31c | note | Standard / Specification - PS 22.9.6 (a)
c81c34bb-a2d2-5643-b91d-e03c1ac1018d | note | Verifying Document - Visual Inspection
1921a9e1-5c13-501e-ad8d-bdf74bad170a | note | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
a7877d4c-01f3-52ed-bd39-b29101c9e102 | note | Verification Activity: Activity - HP
f7f1558f-8ba6-5005-9fbe-15e4e0f89429 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3557f036-7e80-5f45-92f7-d07603b39fd2 | note | Verification Activity: By - ENG
c9d6f711-dacc-4e34-a676-d21f6f073cc9 | signoff | AUTHORITY HOLDPOINT
5264fb45-157a-49be-89eb-f5e9f6961051 | checkpoint | 3.3.2 - Butt-Fusion Welding
b7a659ab-9c7c-5bf9-8b0c-d918f3225a0d | note | Detail / Activity - Use only semi-automatic or automatic welding machines.
8cf98727-671d-508e-a8a3-73d7ae22aa15 | note | ○ Maintain a site record for all butt-fusion welds.
b74784b1-47fa-56a9-b1ae-d2a7f5e1ad15 | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
258dfff0-d8e4-5354-b2cc-eb3ba182a71f | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
f49d3776-049b-5142-831f-9e921b0d0ebf | note | ○ WMS Report
98256989-230f-5f33-8b17-eda107315d9a | note | Standard / Specification - Appendix 22. PS 22.9.4 C
537ab3b7-428c-5a49-b5d1-7a746e890d1b | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report.
f0fcebc1-c43e-531a-9d43-03e2284d7e32 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
cccf4169-14da-5e9d-a968-8e62a4a6a03f | note | Verification Activity: Activity - HP
415662c7-616c-558d-930d-d6e3497616ef | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4894d2f5-d762-5c62-9189-b93568a48916 | note | Verification Activity: By - ENG
ee57b4c6-3c6c-49ee-922f-a95fd370ec86 | signoff | AUTHORITY HOLDPOINT
fe66110d-ee83-49e2-be8e-bc4a6be64b37 | checkpoint | 3.3.3 - Butt-Fusion Construction weld test
541feffc-b020-5760-8b3a-468ab865051c | note | Detail / Activity - Test at least two welds from the first 50 welds.
76395f63-4315-5ff1-a4a5-d020abdaf477 | note | ○ One of the welds to be selected by the Engineer for satisfactory result.
2ca1a5bd-e4cd-5035-bc33-30ea41a3f3c4 | note | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
368f5aaf-3cd8-5dec-a7af-9cde2a5d025b | note | Standard / Specification - PS- 22.9.6 (a) (iv)
2276f622-9cea-5230-9b95-15d457aace41 | note | Verifying Document - Test report
aa63c14d-68a4-51d4-90c6-0a230b402348 | note | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
f556a726-7489-5205-b726-4798527dd2cb | note | Verification Activity: Activity - HP
1861fa86-ba8e-5eb4-b182-b85c8e45ab8c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4753d60f-37a3-5e1d-9d94-a84fb7c0afb9 | note | Verification Activity: By - ENG
7bee8cbf-f7b8-4886-a030-90b960565c26 | signoff | AUTHORITY HOLDPOINT
c4d8da74-1fc8-4702-8e71-1c53025c2c50 | checkpoint | 3.3.4 - Survey
cd3ba98d-4bfd-5ce1-aa76-36b925b77b74 | note | Detail / Activity - Inspection of Pipeline Inverts
f130e06c-a9eb-5a49-9402-083e24f7ba8e | note | Acceptance / Conformance Criteria - Vertical design Setout:
feb6d12c-8944-5af3-bc5f-1a19559cf856 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
6e76ab56-4d04-590e-862e-43fcfd83407c | note | ○ Pipes > 1% grade: +/- 20mm variance
54e7cbe3-ff52-51bf-be32-7420243ebb05 | note | ○ Horizontal design Setout: +/-30mm variance
4777a216-e684-5199-a46a-295d35b50e2d | note | Standard / Specification - PS- 21.7.6 Table 21.15
3afa0fc7-aca0-530e-ab82-a1886e0fefb5 | note | Verifying Document - Survey Data / As-built record
8269c385-f3cb-59aa-825f-45edceac9fb6 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
294697b7-8b99-5b11-8f36-8ff5bcf15c92 | note | Verification Activity: Activity - H
2dc1b142-adaf-5b18-9c8b-3483353c27a3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1b1e5c46-dfad-5063-ae1e-55f33e68aa23 | note | Verification Activity: By - SE
e4f764a9-ef79-42c3-a310-d80950739a4f | checkpoint | 3.4.1 - Electrofusion (EF) pre construction weld test
9e111d95-1649-5c7e-8e26-119f78624879 | note | Detail / Activity - Use the designated welding equipment and the approved WMS.
17f4a785-b02b-5180-8fd6-30aa690be4ff | note | ○ On the largest size of PE pipe used in this Contract
ccd41dbd-c0bd-5237-808d-a19fa57b57c4 | note | Acceptance / Conformance Criteria - ISO 21751 (strip-Bend test) or ISO 13954 (Peel-decohesion test)
2f5ea580-5481-5c20-9ebe-49dadd4c9c62 | note | ○ WMS Report
ba205a52-7296-545b-b1d6-0ba2499ab426 | note | Standard / Specification - PS 22.9.6 (b)
5da68782-101d-5d3e-8c57-3a734545f325 | note | Verifying Document - Visual Inspection
d2173e55-9ce8-5a76-bf79-34377bbd38c4 | note | Testing Quantity Required (based from schedule qtys) - One test welds per operative(Welder)
35ab3c8c-67ce-5050-af9c-d0074f19b334 | note | Verification Activity: Activity - HP
45d765c2-8ea4-59ed-bd01-8f0471ff3c2c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
087a71c7-0a48-502d-99c7-eaa8fdec5f1f | note | Verification Activity: By - ENG
78eeed18-5051-4d13-ada8-feac99f0fa07 | signoff | AUTHORITY HOLDPOINT
f2a7c31e-763f-4797-8b56-291c50f1b99f | checkpoint | 3.4.2 - Electrofusion (EF) Welding
7ef18837-afb1-5bb5-98ea-02e4b9258868 | note | Detail / Activity - Required if Butt fusion welding cannot be perform.
c575f147-8be5-51ac-991a-5fadd4d99ead | note | ○ EF Jointing in accordance with PIPA POP 001.
4d683b36-2d76-5b2c-acb7-7b9d224bfe22 | note | ○ The lead welder or welding supervisor must verify on the site record form.
25f2e7d4-f504-5d32-b6ad-7704fbdfef14 | note | Acceptance / Conformance Criteria - WMS Report
73312eec-00b0-53c5-a2a8-734a0fbdbc7d | note | ○ Checklist (refer to CWP).
fcf8ffbd-ed47-59ac-ba60-e9589fe67f68 | note | Standard / Specification - PS 22.9.5 Appendix 22
e9d55126-8211-56ec-8048-d9fb56e81ecf | note | Verifying Document - Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report.
c996f5a7-e604-56eb-a874-eb791236cc14 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
03c7f04f-3946-555f-9c4c-fef0d57eedd1 | note | Verification Activity: Activity - H
f4372999-1ddd-5540-b826-0360d5a2e769 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6066519b-4270-53b4-94c7-3971a249911d | note | Verification Activity: By - SE
b57e0824-0cb7-4236-b824-615ad984578d | checkpoint | 3.4.3 - Electrofusion (EF) construction weld test
ef201a59-5c53-5c12-b117-857ca02577f1 | note | Detail / Activity - EF weld quality to be maintained.
2a13bbb9-12ae-5d9d-9f96-2d9e8adc1b6a | note | Acceptance / Conformance Criteria - EF coupler and EF saddle testing
08b6bd64-0230-56be-9baf-00e2d4f6785d | note | Standard / Specification - PS- 22.9.6 (b) (iv)
49827065-f3ac-572b-85b9-1ec98aedbd37 | note | Verifying Document - Test report
4fa03908-433a-52d1-b293-e6b5570f2d57 | note | Testing Quantity Required (based from schedule qtys) - 1 in 10 test
31e9b334-5e58-5cea-9fa0-5abe14392368 | note | Verification Activity: Activity - HP
5f0520eb-10e7-5ee2-a79f-3d880df50c36 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5f00cf91-b246-568b-9c88-891b34220701 | note | Verification Activity: By - ENG
439d0609-9a8f-42c7-9e76-ef273d9cb957 | signoff | AUTHORITY HOLDPOINT
b5b8cbb8-fc94-4c45-a8fa-db26b5dd9e0e | checkpoint | 3.4.4 - Survey
add1188d-af85-5248-9ae1-b65b9110ec62 | note | Detail / Activity - Inspection of Pipeline Inverts
f996d8cb-d17a-5946-b4bb-add205bbeb4b | note | Acceptance / Conformance Criteria - Vertical design Setout:
0a6d7885-7c1d-5d17-93bc-7c3d117b1c77 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
321d1360-b495-56fa-89af-9b7cd62eec0e | note | ○ Pipes > 1% grade: +/- 20mm variance
7097dacd-57a5-5e80-8405-03ab7dbfb06a | note | ○ Horizontal design Setout: +/-30mm variance
87e48dc4-cc9e-52fa-878b-f1ba6df07379 | note | Standard / Specification - PS- 21.7.6 Table 21.15
72a2f83d-f131-5054-b0e3-36ba1a9bffe6 | note | Verifying Document - Survey Data / As-built record
9f479144-df2e-5447-95e8-a1ba2d069560 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
33a3e236-e43d-57d2-a151-578f980f3328 | note | Verification Activity: Activity - H
f0e56d6e-0a7f-5581-b72c-78e933f4817a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a9abaadc-ecc1-59ed-9b3a-c2d55c9ee9f0 | note | Verification Activity: By - SE
c87e0e3a-5762-4ece-925d-2f2117c3581b | checkpoint | 3.5.1 - Emebment Zone - (Side Haunch Overlay)
2198a488-6d6b-56c9-aee6-f8cd55e68d13 | note | Detail / Activity - Granular Sand backfill Compacted in 200mm Layers.
dee0f174-d44f-5a02-afe4-cd148ab9171a | note | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays.
e859cedf-169f-5d82-86e6-98a7a68d1332 | note | ○ NDM BS to be Carried Out
134871c5-ef49-5bf5-bec5-c47033534939 | note | Acceptance / Conformance Criteria - in 200mm layers.
1a7c4421-2104-56e8-b17c-9604815be328 | note | ○ More than 85% of MDD.
908f7557-81a9-5027-b12b-45666d4378f6 | note | Or
06feef18-6412-5370-81ce-fa9da06b5034 | note | ○ Minimum Compaction- Trafficable 95% MDD and Non-Trafficable 85% MDD
53c3c5b4-ef68-5fea-8fa7-5260daf95eae | note | Standard / Specification - IFC Drawing 0320-1
46a5759e-2443-5aa4-b637-5ccb11958401 | note | Verifying Document - Lab Report / Wastewater line record
fdc03492-962a-57c7-b62d-7b7487fb28a4 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals. 200mm lift.
f786b390-4ff6-5904-b23f-da6f7ab3f81e | note | Verification Activity: Activity - H
b6fdc62c-e07c-51f7-a33d-a2e9ac1ca401 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5548e626-85fb-5f04-90f7-f9906fc78461 | note | Verification Activity: By - SE
91f4d083-a60d-4c93-9311-e407d256dd95 | checkpoint | 3.5.2 - Pipe Markers
8521c1fb-9b3a-5f50-9dcd-63b2dadddbce | note | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
32e02472-0aa7-5212-8115-71faf3cedc24 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
192e7d1f-cb05-536a-acb8-a17f9ac927a7 | note | Acceptance / Conformance Criteria - AS Per Drawings.
f9adb7ac-16e7-54fd-ac8a-fe453a212b9a | note | Standard / Specification - PS 22.7.3 a
8b2c8f1c-0a31-582f-9873-5dfd09242372 | note | Verifying Document - Visual Inspection / Wastewater line record
bc8e769e-49d5-52fc-84f9-0f3278af8e56 | note | Testing Quantity Required (based from schedule qtys) - Every Line
2e026beb-e2bd-523b-a424-f240121cc1a5 | note | Verification Activity: Activity - H
0854144f-fa8b-5c83-bcf2-0fa684aea2b1 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f338c095-6574-552c-9152-d237f2e22187 | note | Verification Activity: By - SE
0e38e2f9-1a38-426b-8291-96534cf2c17d | checkpoint | 3.5.3 - Backfill Compaction Testing
dd68ea1f-e65f-5081-b95e-8256a1f9f71b | note | Detail / Activity - GAP65/AP65/LRAP65 Backfill Compacted in 200mm Layers.
602e875e-181d-51ea-9136-5d87a973f7fc | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
91f2e973-5b9d-5ed7-a9ef-c398add0a106 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers.
3a81fedf-b846-5b8d-9fee-ea6cf9f8d4b1 | note | ○ Testing to be completed on maximum 200mm lifts of backfill.
8fed19d1-ada4-5f12-aeb2-dec5771f3f5b | note | ○ LRAP65 - achive 90% NDM on Grassed Area and 95% NDM on Shared and Carriageway.
307b1a4e-3f0e-5087-8454-45f556580c1d | note | Standard / Specification - PS- 22.13.5 NDM Standard 25832, NZS 4402 Test 4.1.3
239303ba-114c-53c0-89f7-77a979a03d5b | note | Verifying Document - Lab Report / Wastewater line record
fa4a4a8b-e937-55e7-99f2-23b8abe02c5e | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 20m evenly spaced intervals..
d746177d-f176-545c-9064-521ba7f52021 | note | Verification Activity: Activity - H
faedee6d-52b1-5e9b-b838-6dc9e2c43389 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5f4258be-f723-5604-8840-e92913c39bf3 | note | Verification Activity: By - SE
0e459007-a1a8-428f-bfdb-73f074b5711d | checkpoint | 3.6.1 - Pipe Inspection
dfbee3a6-1a37-56ed-97e3-dbac83579952 | note | Detail / Activity - Inspection of Drainage line
f485c883-e273-5e6a-8277-1e19f3cbd222 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
fb4629ff-4e8f-5def-b2c5-8ecacef1f38a | note | Standard / Specification - Internal
d924abfb-6a1d-53f0-9d52-528e77c06fa5 | note | Verifying Document - Wastewater line record
09cef8a5-5d23-5a5d-a638-343e834ca6f4 | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
1f0c034a-4d52-516e-a951-b087af1ccfbd | note | Verification Activity: Activity - I
77635919-f6a5-5f3f-a3af-7f1136e67a19 | note | ○ Formal inspection activity to be undertaken and recorded.
55486e2f-2fb3-5faf-89e8-7b5bfe372762 | note | Verification Activity: By - SE
30d7eee6-33ae-48f8-b39c-438bc320d529 | checkpoint | 3.7.1 - Pressure Acceptance Testing
3b06cb80-94a1-5055-b67d-e0f897f48c7d | note | Detail / Activity - Backfill/cover with embedment before testing
591c2940-1220-5107-a948-25f9747265f4 | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
34e10bf0-4906-50a1-8c2c-6fe80250f0d8 | note | Acceptance / Conformance Criteria - Wastewater Rising Main Pipelines – 800kPa
c65f5295-0eb2-57c1-a3a1-9142a519a1c3 | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
7969fbf6-135c-5bef-8294-b5866b5463e1 | note | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
c2f42f87-2fe8-5610-a68c-bff41cb5752e | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
3175f7a9-619c-5df8-bead-79743478a0de | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
95276c5d-4fb7-5e79-95ed-a2eb7ec57f47 | note | Verification Activity: Activity - HP
575f9f87-1162-525c-a5b7-6555b7140a0b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a6117092-aade-5896-a2c7-94295a8d889d | note | Verification Activity: By - ENG
45e79789-15df-4382-b27e-07fd8b2df1bd | signoff | AUTHORITY HOLDPOINT
a69d486f-b42e-4d22-aaaf-49b6fa324777 | section | SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
20078e99-75b4-4ec6-88b6-27e902fe3139 | checkpoint | 4.1.1 - Survey As-Builts
ad780205-4068-5d54-9d65-482824118cf1 | note | Detail / Activity - Quality Check on Nee pipeline and structure based on the tolerances in RITS
4ff1db64-9b94-55b1-83fe-0a0e70545fc6 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
11bb7a13-6d62-597d-ae32-1f4b7b5b1f52 | note | Standard / Specification - Project Specifications
4bbb8d57-ab12-5ad5-8927-76c2da7568c9 | note | Verifying Document - Red pen markup only
8be1b147-8e24-5f65-bea2-ad83f2e64732 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
4f9cc613-942d-5804-ad3c-6082f9de8b62 | note | Verification Activity: Activity - H
ea2fae57-d1a3-55e9-a7e8-4eff479349af | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ff85eaf6-0b21-5580-b910-b7926f346902 | note | Verification Activity: By - SE
73f818c1-121d-439a-b7c9-d754294a6c57 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
321f5209-28e1-533c-8039-e64de6236244 | textbox | Contractor's Rep Name:
dae81756-a607-5b4c-a60c-4c1e72f2e99b | textbox | Engineer's Rep. Name:
c2520112-335c-50b4-96ed-303b8d315493 | date | Date:
92377e05-430d-46ee-be23-996d57fa68f6 | signoff | Add Signature
1c847ce8-773c-41a4-ade1-cbe98fb80e9c | checklist | DN1210-012 ITP DG7 Surfacing Rev 0 | itp | DN1210-012 ITP DG7 Surfacing
ad7f7449-42c7-4f24-96ed-e9edfed9db04 | section | 1.0. Pre-Commencement Activities
2b16dcf5-1814-4af5-9f64-ba8cf08eeae9 | checkpoint | 1.1 - Approved JMF for Asphalt Base or Wearing Course
8d3f94d8-9c7b-5e6b-a12a-16f069e5ac94 | note | Detail of Activity / Test - As Per DN1210-WSP-GCO-0160
ecebda1e-9513-5120-98ab-14eb21aa0096 | note | Action (Hold, Monitor, Witness) - H
283413a4-e590-50bc-a495-eb8af8c3f1bc | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
b0552fa9-7726-5174-936b-c04e1c009923 | note | Inspection / Test method - Confirm requirements are followed
18b96fe3-37b6-5756-ad01-38e6be401ef2 | note | Acceptance Criteria - JMF Validated in accordance with NZTA M/10:2020
c63608ec-a523-526d-a342-ec73cfa28bd5 | note | Record documents (QCP - Quality Control Portal) - Mix Design Report
1394a0b3-be84-5f04-b3da-222f8e5a0684 | note | Responsibility - Paving Contractor
3a423319-4369-5900-8638-a77e05456b4a | note | Project Specific Notes / Instructions - JMF expiry date and validation details in here
aaf85d45-9e27-5fa9-a8da-aeda8cefb5df | note | Designer - A
08209955-366a-520d-a6f1-f6679de97def | note | Eng. Rep / NZTA - I
8be9ca5a-71c9-5df1-8e21-9da544e0d573 | note | Contractor - R
1bb351a2-8b86-4aaa-bf1e-78bf3cf83c2a | signoff | AUTHORITY HOLDPOINT
e898b215-2ed6-4e5a-b732-4a9d8535bd6b | checkpoint | 1.2 - Site Conditions
62abee92-7754-5355-81dc-508adaad9bb2 | note | Detail of Activity / Test - Weather suitable, Site extents marked, surface suitable for paving (Depths/milling/cleanup complete etc), Environmental Controls in place
928c8e9f-c9ca-5fbc-ac6b-4cf9fd44d00a | note | Action (Hold, Monitor, Witness) - H
ccdfac58-d341-5372-9796-a074dfb8b39e | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
a3f79cbe-5d8a-55d9-9996-2f5b2971fdde | note | Inspection / Test method - Confirm requirements are followed
3d10cecd-a751-5534-a8ba-3a3f56e71a34 | note | Acceptance Criteria - Weather conditions and Site is suitable for paving
9a396126-d253-5652-a411-6fab87f85c22 | note | Record documents (QCP - Quality Control Portal) - Site Diary
91d6baad-5e95-53e0-89fa-f69baba2f57c | note | Responsibility - Paving Contractor
44b10304-3a37-5086-abf3-bba12b8a05cc | note | Project Specific Notes / Instructions -
9d205ba0-f01b-5d86-87f2-e765865c934d | note | Designer -
d66d6d24-2e28-5a38-a4c3-7eb36991fb36 | note | Eng. Rep / NZTA - I
0d6a08ca-b578-51f9-a2ed-a2787811d908 | note | Contractor - R
77316009-1b39-4c11-991d-78021c96eb5e | signoff | AUTHORITY HOLDPOINT
49a78727-947c-4b2a-98e0-34324dec437c | checkpoint | 1.3 - Traffic Loops
ce28a9d1-a3f9-5480-a5b2-123b6941a023 | note | Detail of Activity / Test - Communication with affected parties
de4bb566-fad1-5d17-8687-8f9bc5df9f8b | note | Action (Hold, Monitor, Witness) - H
eb3cb0ae-7a80-5a94-b02b-a1e4cd28be91 | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 7 days Before Works commence
749cedaa-caf3-58d8-b669-5630fc99b1c8 | note | Inspection / Test method - Visual
0a5e06f0-cd23-5a0c-82e6-518a232d5da1 | note | Acceptance Criteria - Notify RC at least 7 days before surfacing is programmed
e284b9e3-cf8b-5b7e-81f1-8041388706cd | note | Record documents (QCP - Quality Control Portal) - Communication
538f7624-389d-539b-bd37-0e571b45cd12 | note | Responsibility - Paving Contractor
840ebc77-7f3f-5edc-9601-8be9135d2b46 | note | Project Specific Notes / Instructions - only required where existing traffic loops are present
0d47b7fc-18f4-557b-bbcb-23f6247324f1 | note | Designer -
b74ed8a0-b6d4-58a1-95ad-56ebb43cba4c | note | Eng. Rep / NZTA - A
13f3ad53-2e6e-59a1-812f-37a20d801aa5 | note | Contractor - R
dd699b6a-c3b2-46f7-b665-38338dc6b2f0 | signoff | AUTHORITY HOLDPOINT
65cb1bc6-a8d6-4cd9-b62f-176a76d749c1 | checkpoint | 1.4 - Paving Plan
2a6f7782-6b90-52ea-83f8-3a7d18eb6b78 | note | Detail of Activity / Test - Paving Plan to be completed
64cea8fb-8cf1-5239-97cc-6c510d8dbd4a | note | Action (Hold, Monitor, Witness) - H
5e343a04-f860-5039-8f2b-a05b80962dac | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
0ef8a324-879a-5638-a2e4-ad3a63e41614 | note | Inspection / Test method - NZTA M10: 2020 Clause 9.5.1
1effdb7e-2858-544b-99fb-b1b78da8a5ab | note | Acceptance Criteria - Paving Plan to be completed for each shift with dimensions, location and type of (hot/cold) joints, areas and tonneages
e5551f58-7943-5852-9cf5-ca7053e839b6 | note | Record documents (QCP - Quality Control Portal) - String Sheet
99dff33a-37d6-5ebd-8290-6eb96d6a8a51 | note | Responsibility - Paving Contractor
a75312d6-7355-5270-a396-41024fde1cd2 | note | Project Specific Notes / Instructions -
80a5f9cc-e34a-54ca-b49a-ddfec812d19e | note | Designer -
fbabeab5-f8fe-51ac-875c-0ba947cef004 | note | Eng. Rep / NZTA - I
1aa4ceca-5475-5cbe-bb57-02b2e7f4250d | note | Contractor - R
d3df9e96-1a44-4dd9-bb18-1dc838625d46 | signoff | AUTHORITY HOLDPOINT
bc0f953f-a619-4691-ac1e-3fc4a6f2481e | section | 2.0. MANUFACTURE OF ASPHALT
0c7244b2-923f-47a0-a242-0d080474d559 | checkpoint | 2.1 - Temperatures
ce4d970b-8e56-53e0-bdae-307bcb14efd5 | note | Detail of Activity / Test - Mixing of aggregates and bitumen
9bbbdddf-1cc1-5101-a50c-787b42e9b396 | note | Action (Hold, Monitor, Witness) - M
4e8bc62e-9c02-5eae-9e0a-3202ae8121c2 | note | Minimum Test Frequency (Lot = 1 day’s production) - Constant monitoring of temperature by calibrated euipment
d6c303cf-7b28-5bb5-88a0-7d68de54dd99 | note | Inspection / Test method - Plant temperature probes
f0432a16-6cc0-5b93-8933-dabb6b3b9188 | note | Acceptance Criteria - PNZTA M10: 2020 states max. 170 deg.C
fbe8fd52-1857-552b-b792-520315793c5e | note | Record documents (QCP - Quality Control Portal) - Plant site diary
247c42c3-11fb-5b8a-8758-4702b75821b2 | note | Responsibility - Asphalt Manufacturer
01316407-50b9-5669-be8b-477825a63cca | note | Project Specific Notes / Instructions -
d09d848e-b17b-5ab3-9af5-ced072c1b358 | note | Designer - I
a9978c23-360a-567a-bc91-ed5b146c06b0 | note | Eng. Rep / NZTA - I
2954ed83-587d-555f-96f2-72b7039f7f10 | note | Contractor - R
bec1da46-a8a1-4cd8-90c8-b6fc2e2bb328 | checkpoint | 2.2 - Production Asphalt
b0b71f70-dd29-5b55-8011-3f1d4afe60b2 | note | Detail of Activity / Test - Particle Size Distribution
1a3872f0-19b6-53d3-8a2d-8505c8b37cf6 | note | Action (Hold, Monitor, Witness) - M
6ab624e6-2742-59a6-9785-46aa6b87150c | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
e7bca3d2-dc4e-551b-aa92-fc9df0cac727 | note | Inspection / Test method - NZS 4407 Test 3.8.1
cb6b40a2-cfe0-5078-bfee-4b35b18c0ae2 | note | Acceptance Criteria - NZTA M10: 2020, Refer to Table 5.3
b4948878-3d53-5d28-a488-1a6aab5bfc39 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
793ac005-4843-56e0-bffe-80cff5fdf029 | note | Responsibility - Asphalt Manufacturer
b5e33737-d01d-526a-9649-379d92f045e3 | note | Project Specific Notes / Instructions -
bb6d87f8-6c38-5d3e-bb9d-a7fa41e30323 | note | Designer - I
0633a35d-846c-56b9-a533-6391c891d440 | note | Eng. Rep / NZTA - I
9d6a1048-793d-575f-93b0-a1f480379853 | note | Contractor - R
37f3cb17-dbac-4a8f-b867-8ffa51b25360 | checkpoint | 2.3 - Production Asphalt
1e40f47e-c2ec-58e8-890c-5e177b952684 | note | Detail of Activity / Test - Binder Content
b1abd895-a9b5-5c26-9ea0-aa59fbc8980f | note | Action (Hold, Monitor, Witness) - M
1f0c99ef-f655-5595-aaff-2c7be2cd3883 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
b3038d3c-53dd-5583-b23d-969e124ba16d | note | Inspection / Test method -
ee3197fe-def7-5029-b5ee-411394038e7b | note | Acceptance Criteria - NZTA M10: 2020
92c1cee0-152a-50a2-8f3a-8c7922edb059 | note | ○ Individual Test Result: ± 0.5
ff413c72-7f4d-5e79-ae81-7309bba8170d | note | ○ Mean of Three Test Results: ± 0.3
744c5981-31d0-5036-900c-2f854270f39d | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
51d8be1f-bb47-5b3f-88c7-9e55551e124a | note | Responsibility - Asphalt Manufacturer
e1aa7d8b-4194-5b4f-b0b2-e4c56ce94295 | note | Project Specific Notes / Instructions -
4354b0e5-3afa-5fb8-8e0a-80a9cd89c683 | note | Designer - I
0aa2da75-7111-566b-ae82-d11b507a253d | note | Eng. Rep / NZTA - I
5915aa9c-06ec-5f39-b17a-a67254523258 | note | Contractor - R
03ac7fc0-c792-470b-993f-cf17f244aaca | checkpoint | 2.4 - Production Asphalt
1503fd7b-977b-5931-b2ed-f744fa429bae | note | Detail of Activity / Test - Max. Specific Gravity (MSG) of mix
3cd5eb7e-6934-5574-a24d-8381d40a8c94 | note | Action (Hold, Monitor, Witness) - M
04fe0c5d-8eaf-526f-8f49-d152f6161e1d | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
6b98af71-9cd4-5903-9f4b-ae1a22216b1e | note | Inspection / Test method -
2f26bfe3-88f1-5dc9-8759-cfa7f6308ee5 | note | Acceptance Criteria - Report
a899b043-12d4-57b0-a8de-779e79f4949a | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
0c9f6aea-d446-53c6-80e8-1a85bab52d08 | note | Responsibility - Asphalt Manufacturer
4afab9e5-220f-59bc-a8c7-3c6fa188a038 | note | Project Specific Notes / Instructions -
1d12e0ed-32f3-5dbb-9446-5167a9e3485e | note | Designer - I
594de825-6b15-5f3f-87c5-0eac4af9e638 | note | Eng. Rep / NZTA - I
4a6006ea-9b25-58df-ac81-ab73055b7273 | note | Contractor - R
a58a4f2f-5777-4a02-859d-940c2b34fae2 | checkpoint | 2.5 - Production Asphalt
70997ecb-993b-50ad-81ef-8282ed6da7bd | note | Detail of Activity / Test - Air Voids at lab design compaction
5b497140-0c37-5e11-9ad0-2153c8f7066a | note | Action (Hold, Monitor, Witness) - M
43ec8784-560d-5fe7-95ea-6ebb2a2cfbc0 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
85ce6a6d-c3e9-5d40-baad-ba3fd99cd4cd | note | Inspection / Test method -
4c73f2d5-e97a-5497-9240-95af99a07d97 | note | Acceptance Criteria - NZTA M10: 2020:
d3f2a88f-b26c-5092-a066-85a984532076 | note | ○ Individual Test Results: +2.0, -1.0
a365ed56-a2bc-5d44-a496-fe973300b148 | note | ○ Mean of Three Test Results: +1.2, -0.6
f2089bd4-d2c8-56df-888c-2e24a3d1dace | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
38008b9c-1526-57d1-a8fc-adbb5354db1a | note | Responsibility - Asphalt Manufacturer
64fa846d-dcac-5b04-862e-18646c810169 | note | Project Specific Notes / Instructions -
b227945e-4677-5cad-ac5d-54639af8d2e8 | note | Designer - I
94cc29b9-464c-50ca-a2a6-c0f51d348cc8 | note | Eng. Rep / NZTA - I
aa542260-e4b2-54d3-94ec-2f8e3cd0135a | note | Contractor - R
e638bcd2-d9fd-417b-acd8-80fcfb6e8a48 | section | 3.0. PLACING AND FINISHING
c03825f7-b493-4d38-aa1c-34a40a224227 | checkpoint | 3.1 - Membrane Seal
346bc99d-8cc5-5fc4-ab86-03976e81579f | note | Detail of Activity / Test - Application of Membrane Seal
44600590-d1f6-50df-8d31-53d79dcdb972 | note | Action (Hold, Monitor, Witness) - M
8c74f9f2-e55c-56ff-a666-103f2a4278d9 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
2c6a4aea-9df2-5d76-a0b6-ee064048db3d | note | Inspection / Test method - Sealing Records
dd5db99f-f403-5e5c-a635-5326d05d0392 | note | Acceptance Criteria - Application rate, chip type and binder as per membrane seal design
02ee728b-e3aa-5a19-a2ce-4a6660580fac | note | Record documents (QCP - Quality Control Portal) - Sealing Records
794311c8-470b-5c4a-9e1b-f2699d6e421c | note | Responsibility - Paving Contractor
44043ba0-f10e-5d25-a01e-f6bb0165e6fc | note | Project Specific Notes / Instructions -
35b95bb2-47e5-52bf-92fa-e2f7901575ce | note | Designer - I
18d592e4-a3e7-5ca8-bdb1-6066d2fdf469 | note | Eng. Rep / NZTA - I
89f6dcba-4f78-5221-96f1-6d100e3f274d | note | Contractor - R
81260d11-1ebd-4535-8104-e92f89b2a97b | checkpoint | 3.2 - Temperature
c1d96462-8eb5-57c9-a91c-5b2db624c1d3 | note | Detail of Activity / Test - Asphalt Delivery temperature
bbc31d72-09da-5f2f-8c49-f686c5ee0943 | note | Action (Hold, Monitor, Witness) - M
d718b407-8955-5bfe-aabd-434c8ca2e1a5 | note | Minimum Test Frequency (Lot = 1 day’s production) - Every Load on delivery to the Paver Hopper
e729efc0-728e-52c3-a65d-287950f66108 | note | Inspection / Test method - Temperature Probe
b4aa672f-167a-5463-b8bd-1a0084b54073 | note | Acceptance Criteria - Target ≥ 150 deg.C. in the Paver
8e8a130a-b70a-5f84-ac3d-1a1f75a67fad | note | ○ Min. ≥ 130 deg.C in the Paver
0e4f0d44-29a7-53f2-98a1-2c284854be63 | note | ○ <130°C to be Rejected
3840766f-7d5e-54ad-b6e0-d9c31e29b27e | note | Record documents (QCP - Quality Control Portal) - Site Diary
11ed1d6e-d5d8-5c49-aa80-05adcb21d160 | note | Responsibility - Paving Contractor
f82e87b2-7f15-5ac4-9a6b-9d275f905461 | note | Project Specific Notes / Instructions -
cfe717ed-6355-5582-b10d-af38df507df0 | note | Designer - I
1ef9fbc2-68b5-5542-bca8-9f551f3acfe9 | note | Eng. Rep / NZTA - I
97d810db-0d3b-593d-9aee-e870a570fe84 | note | Contractor - R
1868439a-8456-4c23-a9c9-f08e856986cc | checkpoint | 3.3 - Temperature
37ad2639-e9a9-531c-9b10-5658e173171a | note | Detail of Activity / Test - Compaction Temperature
ea9a1ef1-c05d-505a-a52a-204705d71f7e | note | Action (Hold, Monitor, Witness) - M
ed4d4efa-6dca-522b-a57b-cf1b35c63107 | note | Minimum Test Frequency (Lot = 1 day’s production) - During compaction
8adccbba-3a11-5744-94d8-6422f87146a9 | note | Inspection / Test method - Temperature Probe/Infrared gauge
4f160230-79df-5609-9a0b-57597d89eb42 | note | Acceptance Criteria - ≥ 125°C at commencement of compaction.
237d8ee1-bcad-5824-8f63-f2cf5a1712e5 | note | ○ < 80°C - Stop Rolling
25395825-502e-5a45-a7bb-e4aecb68da3b | note | Record documents (QCP - Quality Control Portal) - Site diary
b76e6c59-62da-57e7-8ec3-7124aa58e969 | note | Responsibility - Paving Contractor
833cf620-eea0-54e2-8e15-14071e08dd90 | note | Project Specific Notes / Instructions -
af1f0c1d-7d3f-57fe-b5d4-0b12792b64b7 | note | Designer - I
755dbe66-c000-5979-aff1-68db0a2366d9 | note | Eng. Rep / NZTA - I
c71ff951-f89e-5c74-85b6-1053796b8c83 | note | Contractor - R
d26850fa-78b3-498b-8ee3-2ed580c146e0 | checkpoint | 3.4 - Mat
09bc9ab0-71bc-5fc7-8609-da0e214d4516 | note | Detail of Activity / Test - Load Locate
2b27dfec-c515-5efe-a7ad-bf21c6e3278c | note | Action (Hold, Monitor, Witness) - M
873faef6-ec25-5ed2-84ee-5cb06db3b4fa | note | Minimum Test Frequency (Lot = 1 day’s production) - Each load
a84b0c17-3ea7-5c79-84b1-ef10f26fb234 | note | Inspection / Test method - M/10
0b494f3b-cfca-586d-b74a-83ed52a7767d | note | Acceptance Criteria - Each load can be indentified to a location using a diagram. Record includes:
131459c9-0a57-5ecb-ae59-7db8ade83424 | note | — Truck ID/Rego/Driver
fd11116b-ee68-560f-9c31-a70df5eb187c | note | — Depart Plant Time
e4da6b37-0029-5854-8882-5fdc31372985 | note | — Arrive Site Time
6b2a4a5d-497c-5c57-95ba-28c0059d5c59 | note | — AC Temp on Arrival
51c56fed-b509-5710-8bfd-799eb29b41c9 | note | — Tonnage
97c3f323-1c2e-5748-9884-25b25d2f72f7 | note | — Run Width
e31f3401-a90d-5092-919a-bcbac17ad233 | note | — Estimated Run Length
5a61688d-ce24-5e2c-80c1-494e3f942410 | note | — Calculated Area
d0320c71-4473-52f5-91b9-122bc24a0fdc | note | — Calculated Average Depth
c8d49925-924a-5715-800c-6a8e9fa70de7 | note | Record documents (QCP - Quality Control Portal) - Paving Run Sheet
5c12c902-fb97-5ca4-9707-84c2af77a19f | note | Responsibility - Paving Contractor
f8fea1f5-e251-5615-ad47-6b5630b0b53a | note | Project Specific Notes / Instructions -
6213902c-2e3b-5b9b-ac3d-473139c8b55e | note | Designer - I
d03c2057-9ca5-5592-a45a-5dec3e5f7a8b | note | Eng. Rep / NZTA - I
ebc797d0-92b3-57ce-a493-8b7e15b23661 | note | Contractor - R
47cde6fc-cc1e-42ed-984c-ab30b54c7dd8 | checkpoint | 3.5 - Mat
e2eb3d81-d052-5290-989e-b9ff2b7def23 | note | Detail of Activity / Test - Thickness Monitoring
d8c5f6cb-7704-5fc0-a21c-bc93dd74a15c | note | Action (Hold, Monitor, Witness) - M
04f7e27e-a7c4-5b98-b477-b2cffcdfd776 | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
32c372e8-0a36-5f92-bfe9-604e3d610d1a | note | Inspection / Test method - Dipping
6d191417-e12c-572f-9a52-aee061a13d9b | note | Acceptance Criteria - Target Loose Thickness -0mm / +10mm
0e0c58d3-4bbb-51e4-b575-c4e8000609fd | note | Record documents (QCP - Quality Control Portal) -
0a76ad5f-9bbd-5541-9a92-ab3690d2a941 | note | Responsibility - Paving Contractor
1b9c7637-4a6f-59fd-9466-babd54bcbc6d | note | Project Specific Notes / Instructions -
f53bd306-7900-5c51-b362-1b94bf28611d | note | Designer - I
eea89f2e-5f52-58e7-8d40-4b75d43e2ec5 | note | Eng. Rep / NZTA - I
fc552538-b41d-58c5-9ba4-bb58c3dee819 | note | Contractor - R
5651afe4-684e-4154-9e07-88cea980eccf | checkpoint | 3.6 - Mat
67e74765-b5bd-5ea7-8cb5-0ff3d280fe7d | note | Detail of Activity / Test - Compaction - NDM
183ce032-aeb3-5c79-933f-7b2f65d4b200 | note | Action (Hold, Monitor, Witness) - M
b8a66e55-f983-5004-b719-cd116e2e558e | note | Minimum Test Frequency (Lot = 1 day’s production) - Plateau to be completed on 1st run, thereafter monitor compaction/roller passes to achieve target density.
8a574568-3dad-58a9-8e5e-ba2e267275e3 | note | Inspection / Test method - Insitu density and air voids
bddfd38c-91a7-568c-acf9-67a19e77e1e7 | note | Acceptance Criteria - NZTA M/10: 2020 - section 9.9
e8f15166-6b6c-5a03-971e-e64cc15407b4 | note | Record documents (QCP - Quality Control Portal) -
134d33e9-8a04-5c39-a44c-7dd55be19682 | note | Responsibility - Paving Contractor
632336b5-3cd7-53ca-b6e2-62b0e3a63a3f | note | Project Specific Notes / Instructions - Use a calibrated NDM with established core correlation. Locate and mark cores, record NDM Bulk density by core location (including any offset used).
7e291600-0622-5b48-bd00-716f7757ba5b | note | Designer - I
6bb47220-b353-5856-8327-27ce572da3e2 | note | Eng. Rep / NZTA - I
b1127186-b0c2-55d0-ba29-4aa933bf19dd | note | Contractor - R
ea398524-c3c9-4f06-aeac-9e5ee6829255 | checkpoint | 3.7 - Mat
2520a482-8398-5687-afd0-0e8050a4228f | note | Detail of Activity / Test - Compaction
2333d167-78c6-50f1-854a-40ae9c9c4c9f | note | Action (Hold, Monitor, Witness) - H
0ddd32cb-1cb1-54a7-9840-e1bfc3d87f23 | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 1 mats and 1 joint
e7db4ecd-7be6-5193-8185-0a6d14fe7d54 | note | Inspection / Test method - Insitu density and air voids
4eb74a36-c066-5311-b066-1ac4b7c62124 | note | Acceptance Criteria - NZTA M/10: 2020 - section 9.9
57d8685c-f4f7-5e75-b08e-b893a68e93a6 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
2270f7d0-826e-5b60-8b89-82f7c00b7c58 | note | Responsibility - Paving Contractor
0204fd50-c550-5e84-80a7-86658ce855cd | note | Project Specific Notes / Instructions - A pavement lot shall be an essentially homogeneous section of work completed within a shift of production.
835e6ec1-706c-5d11-bde5-00152f452e93 | note | ○ The lot shall be divided into an appropriate number of approximately equal sub-lots and a core shall be taken randomly within each sub-lot. The Engineer or their delegate shall use a random method for locating each core position, such as ASTM D5361 or a similar process.
c2fc61be-5d78-5430-a917-0596a650be31 | note | Designer - A
1d6c869b-e84e-5755-997b-4462a25228ed | note | Eng. Rep / NZTA - I
cbdb1c52-d94c-5ade-8da9-927e8573b71f | note | Contractor - R
f690458a-3217-4676-bc37-09b3820795e7 | signoff | AUTHORITY HOLDPOINT
08dc0a1d-d35a-41f7-8b39-8e330d2bfbd4 | checkpoint | 3.8 - Mat
21833434-2e3c-57fa-8bdd-65e25d3a6869 | note | Detail of Activity / Test - Thickness
6513fa4d-20c1-5094-ae72-f22df7581b88 | note | Action (Hold, Monitor, Witness) - H
ae776c81-9edd-56cd-b5d7-b48b586279ed | note | Minimum Test Frequency (Lot = 1 day’s production) - Each load
9954574a-f845-5218-bcbd-11d6bf0e3914 | note | Inspection / Test method - M/10
555103e3-982d-5ba1-b4f1-c2dc0883454a | note | Acceptance Criteria - Calculated average Deth from run sheet
051f7a9d-43ab-5d57-b090-406634c1ddf3 | note | Record documents (QCP - Quality Control Portal) - Paving Run Sheet
e607b835-4e8a-539c-8742-1ee2a90a9a84 | note | Responsibility - Paving Contractor
06d27e14-c72d-5805-a438-b9ce32c05d4e | note | Project Specific Notes / Instructions -
bdd8e344-db29-5026-95d8-1f300f2fb526 | note | Designer - A
65ae840c-8b3f-5990-99f7-cd222860ff93 | note | Eng. Rep / NZTA - I
d924771d-b7dd-55a0-b802-133084cbbfff | note | Contractor - R
9b64a223-ea4f-4d4e-952e-c8dfa95cca4a | signoff | AUTHORITY HOLDPOINT
3b1c64cc-9bc4-48f0-be5f-ff8556c3063d | checkpoint | 3.9 - Mat
2d9b90f2-4d19-561c-843e-b688e538100c | note | Detail of Activity / Test - Shape
19151d33-8683-5678-b4bf-ef2d050c4b06 | note | Action (Hold, Monitor, Witness) - M
72ba2e28-3b86-5faa-9c5f-bd8617d62052 | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
60694397-cd46-55cf-be33-3e88de8ea501 | note | Inspection / Test method - 3m Straight edge
c157b2da-183f-5a17-89fc-2f98e9b1e9c8 | note | Acceptance Criteria - Where the length of the site or the geometry is such that a road roughness-measuring vehicle cannot be used then the straight edge can be used for checking the surface shape. Refer NZTA M/10: 2020 - section 9.8.
7aad95e9-708a-5b06-a6f1-39f3c20b0f9f | note | ○ Not more than 5mm under a 3m Straight Edge.
51802cc2-7ba5-5972-a80d-fb7a41e2f12a | note | Record documents (QCP - Quality Control Portal) - Straight Edge Record
c1f79ae9-f44b-51bc-9a1d-b12352331485 | note | Responsibility - Paving Contractor
d705078e-8d4f-57f3-ae63-2c017d6575e9 | note | Project Specific Notes / Instructions -
65412e33-6eb6-533b-9e38-5a1b9c86a4cd | note | Designer - I
d5d8585b-e57b-5529-8d00-441c1e7210f7 | note | Eng. Rep / NZTA - I
95f6bcce-5c8c-5129-b445-f5d55ab51cd4 | note | Contractor - R
45223f2b-1554-483e-a6f9-36f068a5f9ad | checkpoint | 3.10 - Paving Quality
40fba9f7-360b-546e-8a5b-64e3b74e2436 | note | Detail of Activity / Test - Level
9b7fa98c-37f0-51b1-bf52-69051d6c3f0d | note | Action (Hold, Monitor, Witness) - M
5c32fc53-5d89-5f1c-b8fd-489901ed1299 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site
e33301e0-722d-57eb-88c5-3626f04e760b | note | Inspection / Test method - As Built Survey
e97f5eeb-fedc-54ad-b4a2-2f02d2640285 | note | Acceptance Criteria - -0 < +5mm from Specified Level
e82c5381-1c34-55a5-99d7-53eb08486a74 | note | ○ Where there is Kerb and Channel shall be flush with or no more than 5mm above the LOC.
08aa07f5-ad40-5daa-aab5-6b19eb85b950 | note | ○ NZTA M/10: 2020 - section 10.2
77a32f17-af0d-57c6-ad9c-b311e0ce43bb | note | Record documents (QCP - Quality Control Portal) - Survey As builts
6210b903-12b5-5431-8793-ca3d1196ab8b | note | Responsibility - Paving Contractor
868885ae-4754-5239-beed-89d927790eb1 | note | Project Specific Notes / Instructions -
ce191980-ab45-5f84-b09c-0a940e8e33a8 | note | Designer - I
f0fe7239-6a4c-5b77-a518-35732c34d2ca | note | Eng. Rep / NZTA - I
18fd255c-8fd6-5f4f-86d7-94f83c922b01 | note | Contractor - R
b41d9bac-1a11-48a0-9cb6-b44484ca7ba7 | checkpoint | 3.11 - Paving Quality
c2aefaf0-3d03-5d1b-84f0-e8b93936ce7f | note | Detail of Activity / Test - Alignment
36a97288-b9c7-5261-b919-3591b268a6e2 | note | Action (Hold, Monitor, Witness) - M
93a5183b-ca4d-5528-bce8-f2b8d133218f | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site
4d00962a-e68d-5e23-a82d-bbe162acb19f | note | Inspection / Test method - As Built Survey
5e2eedfb-7c02-5e35-b898-9f33e99fe6f7 | note | Acceptance Criteria - Kerb to kerb
19c96890-7ebe-5c41-a2ef-f91c701f6a25 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
fde05ffb-7c9d-5b58-bdde-22be1a2f3e0c | note | Responsibility - Paving Contractor
723d0c35-68bf-5381-8206-fba71817379f | note | Project Specific Notes / Instructions -
b22f12e6-ac80-565a-934c-b1e72ece0b14 | note | Designer - I
b218f1dc-fcfe-5165-85ec-14bd75e6e98c | note | Eng. Rep / NZTA - I
d20d6831-29ea-5799-a5f0-016363d60074 | note | Contractor - R
c0d714d0-c460-4125-bc58-6b234f492c4d | checkpoint | 3.12 - Post Paving Completion Checks
95d30753-c56a-5efd-8f96-5b2f33350e18 | note | Detail of Activity / Test - Site clear and cleanup
0034cf6e-444a-52bd-8c3b-7d5480164ff3 | note | Action (Hold, Monitor, Witness) - W
baea3e21-0bf8-5d5b-acab-e4ab7557e1bf | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
d06d1201-582d-59ce-9936-85ab6df88b46 | note | Inspection / Test method - Visual
d23b6a82-8c24-5c0f-9914-7b61fc272acc | note | Acceptance Criteria - Site is cleared of plant (or parked in safe location) cleanup of all waste mix, paper and detritus is complete
1e03d3eb-ae52-563d-bec0-7e309e756e77 | note | Record documents (QCP - Quality Control Portal) - Site Diary
d8ff33ce-8afe-52e0-880c-2682f29777f5 | note | Responsibility - Paving Contractor
4c8bf693-0de0-585e-bd54-fead14d54f62 | note | Project Specific Notes / Instructions -
82fecd6f-9013-54c0-b481-92d49e69033b | note | Designer -
fb5b2628-2596-55db-9112-d94374036a7b | note | Eng. Rep / NZTA - I
43bd1c4b-7c98-5177-afb9-7730db576f45 | note | Contractor - R
d9800311-167d-4656-9de1-a3150eeca6d9 | section | 4.0. As Built Records
07eb4b61-66ce-42ff-abc9-d66de55e479b | checkpoint | 4.1 - Assessment of all test results for conformity
25cfcf35-758a-5b41-8c85-b32e84bfe994 | note | Detail of Activity / Test - Review against ITP Requirements
9f80bff9-3c9a-5069-959e-e493b6e054a3 | note | Action (Hold, Monitor, Witness) - H
5fd07f6d-4f87-5a85-bafe-53360ca256fd | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
19f571a3-d842-50f4-97c8-bca29749b4c2 | note | Inspection / Test method - Review
66d49c9c-dfdc-5748-9bf5-503424d22289 | note | Acceptance Criteria - Reporting of any non-conforming results to Engineer via NCR
ffd3090f-b3e8-556f-b79a-674d38bc5ae9 | note | Record documents (QCP - Quality Control Portal) - NCR
2ec1b18c-d13d-5c3a-8ad2-58fc827a97ae | note | Responsibility - Paving Contractor
e99e109a-0fcf-5c26-9eb8-7d509758333e | note | Project Specific Notes / Instructions -
bb417903-7bac-5629-9461-759e5cec6fe9 | note | Designer - I
9e77db7e-ac0d-53c1-a5fd-7ab26443ae37 | note | Eng. Rep / NZTA - A
e4298818-d021-5733-97f8-0faa7f8efbe2 | note | Contractor - R
dd82005b-89a9-4a85-b44c-73f0afc4cd27 | signoff | AUTHORITY HOLDPOINT
8a26f4ef-32a6-4ce6-9ead-87d69cb28e1e | checkpoint | 4.2 - RAMM pavement and surface records
29ad95d3-9108-513c-80f6-5fe78b72cb0d | note | Detail of Activity / Test - RAMM surfacing pavement data spreadsheet updated
91cfaab8-0a0b-53a7-8b33-964a594cb5cb | note | Action (Hold, Monitor, Witness) - W
30b1b609-59a0-55d0-bca3-5c1289068cef | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
ae1e1c20-d617-55ea-83f4-295a3e571791 | note | Inspection / Test method - Prepare Data
e1143cac-fcc0-5ab5-a59c-d48107bb8d4d | note | Acceptance Criteria - Over milled and Deep lift extents recorded and verified by Contract Engineer / QA
8184a084-4e0b-581c-996d-32eaa4bdb3ee | note | ○ Spray sheets for membrane area received by Contract Engineer from Sealing Team.
463a7305-ee26-599c-b170-f07234f77052 | note | ○ Surfacing layer extents recorded and verified by Contract Engineer.
12c8f716-b65d-5aa7-b02d-b1da92d26c5d | note | Record documents (QCP - Quality Control Portal) - RAMM Spreadsheet
1924c7be-bd1d-5ef6-a980-0776106ab646 | note | Responsibility - Paving Contractor
913db664-7f7c-5c99-995e-02f20514fee5 | note | Project Specific Notes / Instructions -
159f1ff9-6942-5a73-8b09-c7c0d743bd27 | note | Designer - I
8980d93a-a4fb-531c-b953-b5c5dde2eda7 | note | Eng. Rep / NZTA - A
d1005df8-83c6-5d1a-aef3-14082080a02a | note | Contractor - R
cbccb9ca-4eec-49b8-8a76-dbdeda936a22 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
c22867e9-1499-5475-9f6b-1e79ef5f87a6 | textbox | Contractor's Rep Name:
26fc4648-5575-52a9-be50-1408e3622d58 | textbox | Engineer's Rep. Name:
58835f08-3d22-5ce0-bce8-b50c5a47a516 | date | Date:
944413c7-c257-4341-9678-c55e654b66b7 | signoff | Add Signature
f53db032-4ab8-40bc-bc97-c7cfbbbc69dc | checklist | DN1210-012 ITP Utilities Rev 1 | itp | DN1210-012 ITP Utilities Rev 1
8e916c0c-5850-4ca0-aad3-d295c9619403 | section | 1. PRE-CONSTRUCTION (P&G / ESTABLISHMENT) - 1.1 GENERAL
4a66bb89-4063-48d7-ba64-2c8f3122a315 | checkpoint | 1.1.1 - Trench Profile
0bcb6d66-7e1e-522d-ba87-be9b0db6f981 | note | Detail - Tolerance of +/- 100 mm of the planned horizontal alignment and the maximum deviation shall be 1 in 20 in both the horizontal and vertical planes.
67dc9f3e-9171-50cf-b1b6-87fec1d0c3a6 | note | Acceptance / Conformance Criteria - Survey Set out
dd78f3e2-e03d-5227-a645-a1acee11c522 | note | Standard / Specification - PS 25.13.2 a (1)
40ba78fc-9e73-52b2-a54a-f9029e66caf3 | note | Verifying Document - Survey Data
20d912dd-83fb-52e2-b2fc-f85bf0271bb6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
9abec1dd-c417-52ff-a7dd-f5c2e029111e | note | Verification Activity - H
f2dfcbc7-c870-5849-aeca-006cd2d2d0c7 | note | By - ENG
d7f561a4-3e32-4b1a-9982-23753a93830f | signoff | AUTHORITY HOLDPOINT
25425128-8231-4e6d-aa60-7136a71593a6 | checkpoint | 1.1.2 - Underground Services
283dd870-0601-52e4-855c-ca1a319e14fe | note | Detail - Pothole all services within traffic management prior to commencement of trenching. Accurately record the location and reduced level of each service and forward Engineer.
e9093ccf-6692-5b86-aa60-478a2d8764e6 | note | Acceptance / Conformance Criteria - Survey Data/Existing utilities Drawings
c178e828-e156-5366-98fb-7c2b3ee5879b | note | Standard / Specification - Appendix V
afa0302e-7ad5-5f89-980f-717933ab154f | note | Verifying Document - Survey Data
999d0726-1342-5992-bf08-3221e0b8ecb8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
5195c12a-66bf-5ab3-be01-01228c27e530 | note | Verification Activity - H
917c7757-35c5-53a4-b610-1d5f602e77cd | note | By - PE/SE
af7a8933-9e5a-48a0-a05a-129fd15c5cc9 | signoff | AUTHORITY HOLDPOINT
39a6b05e-30a2-4740-ac86-41f6215e698b | section | 2. MATERIAL, PERSONNEL & THIRD PARTY APPROVAL - 2.1 MATERIAL TESTING
486cc648-29a7-46e8-87c0-82a4976fb1ca | checkpoint | 2.1.1 - Bedding and Overlay Material: Clean Imported Sand or SAP 7
4c6a5b85-12dc-57af-9f84-eb844b1a72b4 | note | Detail - Material grading:PSD
81d99318-3953-50b0-87a3-553626258b67 | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
842b2c18-b12a-55f1-ac5d-21652cdca29f | note | Standard / Specification - PS 25.13.2 g) & h)
110948ae-0e2c-51af-a67d-1197efab1263 | note | Verifying Document - Delivery Dockets/Material Certification
6d35a092-9e71-53f3-8366-f69dd71548b1 | note | Testing Quantity Required (based from schedule qtys) - NA
5b73eeea-f3c1-562c-addc-9e13da30056b | note | Verification Activity - HP
9a700353-5f28-57db-a746-62af3930586e | note | By - ENG
b1e0dc8e-de0b-4e74-a9aa-38a5ebc23b8a | signoff | AUTHORITY HOLDPOINT
44d83bac-76f3-42c4-8c5e-39b2257c0cec | checkpoint | 2.1.2 - Materials: GAP65-Backfill Material
23b3c69e-61c3-5c8d-b7c9-27e3a083e564 | note | Detail - Material grading:PSD
69982c10-640a-5c1d-b2c2-6349b69f27c9 | note | Acceptance / Conformance Criteria - Stockpile size over 4000m3 PS- 16.5.11 for GAP65
0d2e1224-6bdf-544e-8baa-647e3abc8c29 | note | Standard / Specification - PS-21.7.2 Table 21.9
89926f4d-431c-5a36-a4e7-5be287cc0f9a | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
538f58d9-8e96-5832-bd96-e69312922f9f | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 1000m3
582b6634-6b50-520c-8e89-1d5f35c4e7b7 | note | Verification Activity - HP
9569ed76-8c8e-598b-ac62-26995c7de055 | note | By - ENG
63d81330-269f-4298-9075-db67765b857e | signoff | AUTHORITY HOLDPOINT
0b6e92e6-b517-4dab-b57d-d9abacf69d0b | checkpoint | 2.1.3 - Materials: GAP65-Backfill Material
dead2c3d-8425-5ced-9f1d-c49fef0cedf6 | note | Detail - Weathering index:
10ac7968-b8ea-5b19-8b95-0f9febb656a2 | note | Acceptance / Conformance Criteria - AA to CA
f554ac44-d467-5ccc-847c-8f1390459f01 | note | Standard / Specification - PS-21.7.2 Table 21.9
987d8f4e-3f75-5e58-83e8-8420be2644fd | note | Verifying Document - Lab Test Report NZS 4407.3.11
8b7fa9c2-a910-5cc0-bdd6-f7af3e21259d | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
89b237ec-4d43-5544-857e-dccdc5cffbda | note | Verification Activity - HP
5eaf02df-d9ca-5f5a-8fa5-c343b8ec9cfc | note | By - ENG
464c66bc-6468-4260-b978-70b3310b1037 | signoff | AUTHORITY HOLDPOINT
09ef89c4-2afa-4d83-9697-447334c2113f | checkpoint | 2.1.4 - Materials: GAP65-Backfill Material
67aaf769-fcec-552c-9ed7-bf1a39112466 | note | Detail - Crushing Resistance
ffc49956-2e6a-5dd3-a304-40ece59ef931 | note | Acceptance / Conformance Criteria - >100KN
f76a0622-fd6e-5455-847e-d508fcacedbc | note | Standard / Specification - PS-21.7.2 Table 21.9
1a5aa289-6eaf-59a0-9437-a111b759d478 | note | Verifying Document - Lab Test Report NZS 4407.3.10
92ed5aba-43ea-56b8-a774-1a2293235f5c | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
b14c597e-8b01-5272-8ddb-301b10feb6bb | note | Verification Activity - HP
b5d26f2d-714e-521b-9a61-469d0abb98d8 | note | By - ENG
006c000e-da74-49b5-97af-9a1160001773 | signoff | AUTHORITY HOLDPOINT
0e80def9-0026-4998-a4ca-cde2b81a47e9 | checkpoint | 2.1.5 - Materials Approvals
a56af989-ca4e-5c53-a433-cd450e47f5e5 | note | Detail - All works and materials are to comply with the National Code of Practice for Utilities Operators' Access to Transport Corridors, and Individual Utility Providers Requirements
8895bb7e-c427-5901-a5aa-07751a808d3a | note | Acceptance / Conformance Criteria - Prior to Commencement and throughout construction
fdbe7567-dbbc-519b-80f5-59a9d0d58c39 | note | Standard / Specification - Project Specifications
5c389606-b39f-5d8e-8d26-163bf0f5146f | note | Verifying Document - Utilities Providers Approval/Material Certification /Delivery Dockets
3ddf2253-d8cc-5de2-81a4-28ced242fc94 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
ef51aec0-3acf-5b8c-814d-5627875e5648 | note | Verification Activity - H
1af29b68-624c-5b9b-b62a-c702c9fce0fe | note | By - SE
4ece6099-0f01-4b16-bde4-65c5945709fa | signoff | AUTHORITY HOLDPOINT
83f97cbe-b43e-4cbc-bc3b-729ae9f6c33e | section | 2.2 MATERIAL DELIVERY
ee48925a-b035-46ef-97b4-087f4ef5eabb | checkpoint | 2.2.1 - Pipe and fittings. Ducts
7db8345a-ba3e-58a1-ae6b-4d5f1a4d4028 | note | Detail - Duct Pipes shall be of the size, material and class nominated in Drawings. Ducts shall be high impact uPVC or High-Density Polyethylene (HDPE). Duct colours shall be to local authorities requirements. Duct colours for the different Utility Structures must be in accordance with the guidelines.
333fbb3f-f90e-5faa-ae0e-3ca9b54ed4ef | note | Acceptance / Conformance Criteria - Comply with Project Specifications
625baae0-854c-5ffd-9828-2611affb4ecb | note | Standard / Specification - PS 25.13.6 b)
51f875eb-7058-5199-9123-ccc9ee657e66 | note | Verifying Document - Delivery Dockets/Material Certification
497e2f66-3f6d-5599-b0d5-be28065d2a77 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5aa16fdc-5187-5a70-a7e8-62d24fd18fa9 | note | Verification Activity - H
78bc25dd-85bf-5421-be72-73f158f43e7c | note | By - SE
f97a8dfd-6853-5b80-b674-22bd03bdd93b | note | Comments / Closeout Details - Duct details will be instructed by service providers.
30b72118-4b36-4dd5-91c9-00414bc65ae7 | signoff | AUTHORITY HOLDPOINT
95fc4281-439d-4b9a-bfa7-e0f188d3b25a | checkpoint | 2.2.2 - Bedding material
349f055c-40d5-51ac-b330-812b78a35726 | note | Detail - Clean Imported Sand or SAP 7
52d5971e-85d0-5bd6-a4bf-6ae513e08feb | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
ac7553e4-090f-598d-93fd-a88a790432ad | note | Standard / Specification - PS 25.13.2 g) & h) & 25.13.7 b) ii
c7246019-cc11-595a-a5c5-ed534863d820 | note | Verifying Document - Delivery Dockets/Material Certification
da3558cd-d367-5395-806d-f6d08fba0c9f | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
13520fea-8f9a-58bd-94f0-b9d17b4cee98 | note | Verification Activity - H
bd332cbf-5d6b-5170-a45e-98515475dc80 | note | By - SE
e29ceea3-5f67-41be-9f64-7ba1ea194895 | signoff | AUTHORITY HOLDPOINT
d5398cc0-f040-422b-8e23-1339dfa1e2a1 | checkpoint | 2.2.3 - Backfill Material
775a8ca9-30b0-5457-92f9-21908aa5712d | note | Detail - Under roads, driveways and footpath - refer to pavement section for appropriate materials and layer thickness. Under berm or grass areas - site Won materials to be approved by Engineer or GAP65 to be used if site material does not meet Specs
b2e368c6-bc23-5da4-a48d-978978955761 | note | Acceptance / Conformance Criteria - Comply with Project Specifications
dc270cb9-cd17-59bd-803a-59e13c5cd7f6 | note | Standard / Specification - PS 25.13.2 h) i to iii & 25.13.4 a)
05583998-e4ea-505c-906c-b3681ae0bfd5 | note | Verifying Document - Delivery Dockets/Lab Test reports
b3465e16-1c11-5103-b922-723dc70f41a1 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
1524ee9f-d13e-5e50-87c6-a5e81f8459d0 | note | Verification Activity - H
9ba41559-439e-5d84-8fd8-cd22bd752862 | note | By - SE
7245ad1a-3400-43c7-aa67-5b628124c14c | signoff | AUTHORITY HOLDPOINT
a4d7cdb7-b059-4497-a17f-f892ba5d8756 | checkpoint | 2.2.4 - Pits Covers
b54dfeb9-8272-5c6a-9c91-dbe596f03cfd | note | Detail - Jointing and pulling pits shall have slip resistant surfaces.
6e129f47-6b34-5471-a0c8-52ff04f7831c | note | Acceptance / Conformance Criteria - Class A-10Kn. Class B- 80Kn. Class C- 150Kn. Class D-120KN.
f10b6ad6-3c89-5058-ba2a-5ab374cde17a | note | Standard / Specification - PS 25.13.6 c) AS/NZS 3661-1- 1993.
febba2d3-986d-5831-b1b0-a89896aa2976 | note | Verifying Document - Material Certifications. Delivery Dockets
8632adbf-8bac-5027-840e-de9d33e4f89b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
b523dd59-d9ee-5824-bcb7-d9730aa34ecf | note | Verification Activity - H
3c22d34c-297b-55df-9dc8-1e84a24caef9 | note | By - SE
12320b3f-a7f1-48e9-acfe-43a50c1746ea | signoff | AUTHORITY HOLDPOINT
2e80cf9e-cce2-4de5-a526-19b5f0b1c990 | section | 3. CONSTRUCTION ACTIVITY - 3.1
4473bcd7-a7bd-4e0a-b8c6-5007ed250edc | checkpoint | 3.1.1 - Trench Excavation
881014cb-a527-53b7-bee5-f8672fe67d26 | note | Detail - To be excavated to within a tolerance. Not more than 100 metres of trench associated with each site shall remain open at one time.
3e77300b-24e3-57d9-8d0c-54d09709df76 | note | Acceptance / Conformance Criteria - #ERROR!
12365ca8-56e6-5f1a-acee-ef8499fd5229 | note | Standard / Specification - PS 25.13.2 a) i
e5d1fb7e-67ac-59a5-9234-fe1d48f36ff3 | note | Verifying Document - Survey
39daa345-e591-50a6-9823-ea6a4c1e5c31 | note | Testing Quantity Required (based from schedule qtys) - Every time
6b035129-a403-50e6-a124-eafc4b6f86b9 | note | Verification Activity - M
b8e83467-db66-5745-9ff7-de536dd190a8 | note | By - SE
c560f64e-3631-49b4-b19d-a3becd6f68a3 | checkpoint | 3.1.2 - Unsuitable Materials
788da501-45e1-5204-b133-312faf493b0b | note | Detail - All confirmed unsuitable material shall be excavated down to suitable materials.
3b5a9fdc-7571-5cb9-8c38-a2295f4015fa | note | Acceptance / Conformance Criteria - Dig Down to Get Suitable Materials or get Engineers Approval.
8d8e26ee-a00d-5e92-ad99-5ebf580c87e6 | note | Standard / Specification - PS 25.13.2 b) ii
a32f42d3-0de8-5a1a-a4e0-0f297dd3fd71 | note | Verifying Document - Visual
eacc48f2-a624-5251-8847-87e6cddcb3cb | note | Testing Quantity Required (based from schedule qtys) - Every time
9d2893a1-8ed0-54ea-a3ad-ea1451cc7677 | note | Verification Activity - M
50c89cc8-28e1-5b9a-8865-40337e15e174 | note | By - SE
4a681e24-b46a-4441-9bd6-7e42252ebb01 | checkpoint | 3.1.3 - Foundation Compliance
9f3f9957-5265-56a7-8e28-baf2e6f1f334 | note | Detail - It shall be de-watered prior to installation of bedding material. If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
b4f5bf4b-5651-5370-9694-0525360b32f1 | note | Acceptance / Conformance Criteria - 50mm granular layer shall be laid and compacted before the bedding layer is laid.
70967d19-82ff-5029-93ac-e78b1e927194 | note | Standard / Specification - PS 25.13.2 c) and g)
bb29f6e5-6443-5910-892c-ab0fdd680881 | note | Verifying Document - Visual Inspection
d7b30555-ed23-54f5-971d-8f7663e42d70 | note | Testing Quantity Required (based from schedule qtys) - Every time
7f197952-ec14-51dd-a602-b43e97854998 | note | Verification Activity - M
f2e6e66d-882f-50c4-8a0e-428f0e065146 | note | By - SE
49179d62-20cd-451d-9cc5-4bdc9f49dc68 | checkpoint | 3.1.4 - Bedding
8614c5cc-5665-5fa3-ab79-3f8940785aa5 | note | Detail - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
0736aece-5d03-503d-8bd2-dc15e71dfe33 | note | Acceptance / Conformance Criteria - Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
119d2e5e-a84d-5440-9563-82cc8c9de3ac | note | Standard / Specification - PS 25.13.2 g)
f566dbf0-0c84-5db8-aa23-db97f0e0357e | note | Verifying Document - Visual Inspection
95c8247d-bef3-517d-afe5-71c62c023bcb | note | Testing Quantity Required (based from schedule qtys) - Every time
cf88f922-c00b-5c77-94ae-58ea7117c49b | note | Verification Activity - M
7af9af8b-6269-5b6b-9749-5e37f31ca339 | note | By - SE
78830cf9-10a2-4c5e-8550-200be233c777 | checkpoint | 3.1.5 - Bedding (Encased in concrete)
e2a882fc-91f0-5b73-ac67-4727ea84b5b1 | note | Detail - Concrete Bedding to be placed. Compressive strength of concrete used no less than 20MPa
e92735c5-112e-5f6a-ab41-56137c2c3ed8 | note | Acceptance / Conformance Criteria - 50mm
c925fb4c-df71-59d9-8612-f84c6aee1fad | note | Standard / Specification - PS 25.13.7 c)
aa502856-7f55-501a-8b7a-1cc391135779 | note | Verifying Document - Visual Inspection
15aa5f42-8a9c-5efd-8d93-0ae20c77a890 | note | Testing Quantity Required (based from schedule qtys) - Every time
99a33773-5ba8-5074-9c2e-001402773f08 | note | Verification Activity - M
b3c964ab-9694-5169-83b2-96437b72a933 | note | By - SE
dfc31b15-66cf-447e-b61f-2a1b0891b1c2 | checkpoint | 3.1.6 - Installation of Ducts
5b79e591-f8e5-5827-adaa-be34a18a3b89 | note | Detail - If more than 2 ducts are being placed.
a223bcd1-0b1c-5e32-beba-bb2d6eb87ff5 | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
deeb4f1c-8275-5660-ad84-a68effb8da42 | note | Standard / Specification - PS 25.13.7 b) iii
d86431aa-c70a-50be-a1cf-a63445223e1f | note | Verifying Document - Visual Inspection
24b5f92a-0d49-5a68-85cd-e4c7a023a435 | note | Testing Quantity Required (based from schedule qtys) - Everytime
4d7275e2-defa-5308-9cdc-0c13ffff8e33 | note | Verification Activity - M
4c27abcb-e832-5ed4-8489-e71afe910f15 | note | By - SE
a05dd518-a7e7-4a26-9f83-a8f2a44879cd | checkpoint | 3.1.7 - Draw Wires
5edb7e75-29a5-5246-b153-3b8dadcbedb7 | note | Detail - A draw wire shall be installed in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting.
9d659fb7-8cb7-5a1b-be14-7d781f814ada | note | Acceptance / Conformance Criteria - Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load. ≥20 years design life. The ends of draw wires shall be made fast within the pits and be secured to the duct plugs.
5c218fd5-e8d2-540a-9a00-2af658da7a07 | note | Standard / Specification - PS 25.13.7 e) ii to iv
f066a145-aaea-5c8d-a3ab-5f5869ec9dda | note | Verifying Document - Visual Inspection
8f57c5b6-de05-5c56-a867-4cffa95efeb7 | note | Testing Quantity Required (based from schedule qtys) - Every time
752d02da-2b6f-5438-b36b-7effcef8df65 | note | Verification Activity - M
d77a631e-2c4a-503f-aae3-306c4c26277e | note | By - SE
9d07cbba-54d9-488f-aaaa-b8959d513f76 | checkpoint | 3.1.8 - Caps
1bfdfd82-7fe6-5e68-9de7-b048819822ff | note | Detail - All duct ends shall be capped
ae5add1e-5d83-53f5-8d27-724134035025 | note | Acceptance / Conformance Criteria - Capped ducts
a3d7f628-012e-5ea4-b7c4-6f7f0f8c09e4 | note | Standard / Specification - PS 25.13.7 e) v
1b0dc8a4-1927-5f71-b1f5-72771fe7de73 | note | Verifying Document - Visual Inspection
387d27f1-087e-5ca4-aeaf-1624f5a7c315 | note | Testing Quantity Required (based from schedule qtys) - Every time
393cf3ed-7340-5bb4-9068-e6e079e4f5c2 | note | Verification Activity - M
57c7c6ec-efd8-5ea6-bda5-8e472b70ed9f | note | By - SE
b17ea8f5-9cdb-4403-a4d8-4c5f65d3300c | checkpoint | 3.1.9 - Warning Tape
fffcaef5-8628-5f0b-974b-849c726c921d | note | Detail - Warning tape to be placed above services.
51439d3b-16f0-5217-8a6f-2a24ba22fa89 | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the duct
e9c43411-659c-5c77-b569-388644d1a8ed | note | Standard / Specification - PS 25.13.7 b) iii & f)
fe08ade8-e822-5587-8394-f5dcc7688f8f | note | Verifying Document - Visual Inspection
00f192cc-e9dd-52d7-a66c-f6a410d5c154 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
66839ed7-44f6-50fe-a63f-4fcd43402bea | note | Verification Activity - M
5924d14b-7652-5653-ab92-1041568205ed | note | By - SE
e306fc1c-d395-46d7-a477-4d04ef77d232 | checkpoint | 3.1.10 - Overlay
c96c786d-a3ac-538f-bd2f-f7a7a9396209 | note | Detail - Clean Imported Sand or SAP 7 to be placed and compacted
bc7ad0de-793b-56a0-b539-d517e3b9bc52 | note | Acceptance / Conformance Criteria - 100mm thick Clean Imported Sand or SAP 7
a891bdad-70a0-52b3-aacc-ffe42aceab7b | note | Standard / Specification - PS 25.13.7 b) ii
1dd21f08-8d27-5bfb-b9e8-6a9f25e00417 | note | Verifying Document - Visual Inspection
127845bd-db3a-5def-b2b7-0a3acf4b4686 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
d556104c-2e88-5f64-9ae2-9701f3e1b8a3 | note | Verification Activity - M
b9d5c2fd-2a2a-5863-8989-b22e6624b3e7 | note | By - SE
3f3429b5-7132-4adb-b746-c9a7683a7539 | checkpoint | 3.1.11 - Overlay (Concrete Encased Ducts)
1f4429d8-f8a2-5bac-a86d-0813b9fde853 | note | Detail - Overlay and surroundings to be placed with concrete.
0b70a8f8-2690-5c27-8c4c-3c4c4fd010c2 | note | Acceptance / Conformance Criteria - 100mm thick on top of Ducts 50mm thick side of the Ducts
f9675d8c-79e1-56da-a27d-b43646e236b3 | note | Standard / Specification - PS 25.13.7 c)
010b256a-1588-58ba-9c39-62df9f4f7179 | note | Verifying Document - Visual Inspection
b34dbc84-d497-5c86-b2ce-8799a8d0f168 | note | Testing Quantity Required (based from schedule qtys) - Every time
d597156a-ed6b-5674-85c6-119be7aa2d64 | note | Verification Activity - M
236de8df-23be-5469-b74e-c361c55f82d8 | note | By - SE
0bae926a-9ce6-4858-9d51-9b2f9caa194c | checkpoint | 3.1.12 - Overlay Testing (Concrete Encased)
35e54c37-e0b1-598a-be0e-b1e2bb10136f | note | Detail - Placed Concrete needs to meet the strength Criteria
b074a358-5034-527a-bf77-2f7fbd297b7a | note | Acceptance / Conformance Criteria - >20 MPA
fa29de66-7375-50c6-8352-5c130ce9b7b3 | note | Standard / Specification - PS 25.13.7 c)
b0012925-f4cc-5a23-b915-ab5034f37dbe | note | Verifying Document - Concrete Dockets
91ed986f-a827-54fe-9a6b-7600723d8aa7 | note | Testing Quantity Required (based from schedule qtys) - Every time
9aacd20f-1f0f-508c-b1b7-468d26f1adbc | note | Verification Activity - H
90a5508c-f605-5494-9626-9395b1c0b5a6 | note | By - SE
0491c173-2aab-4592-86c2-67fcbec243f9 | signoff | AUTHORITY HOLDPOINT
5b6c2158-a99a-4448-ab3e-92552e8438d9 | checkpoint | 3.1.13 - Backfill
5bf88ea3-a40c-5c85-9bc5-bd9bc4a1e4e6 | note | Detail - GAP65 to be used if site material is not approved. NDM Testing to be carried out.
d007f31b-e980-5f51-b330-b26ba3ad43ae | note | Acceptance / Conformance Criteria - NDM Test every 250mm compacted layer Min 92% compaction rate and Average of 95%.
d72fe4f3-f5d8-5c87-ba13-19390696dae7 | note | Standard / Specification - PS 25.13.10 a) modified
b5333357-30a1-5679-9e39-f6a426589629 | note | Verifying Document - Lab report.
053515aa-9b3b-50c0-bfb4-56f808ca9c52 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
682f58e3-a6cd-56d3-ae35-8208fb6bbe45 | note | Verification Activity - H
3e64b478-e791-5aab-9131-020ba8bddd83 | note | By - SE
f4cf8649-25a9-4847-814e-28f6d264bf5b | signoff | AUTHORITY HOLDPOINT
aee89273-de10-42e4-89e7-889fa4ef10d3 | checkpoint | 3.1.14 - Pit Installation Location
78c4648b-49e0-5f28-8583-31e1f07bcca5 | note | Detail - Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid .
bfb37dbb-602a-54ce-865a-5f9bc9a9edc0 | note | Acceptance / Conformance Criteria - Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas. When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side. When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side.
1835a7c4-faa8-5498-b21a-52a635aa2845 | note | Standard / Specification - PS 25.13.8 a)
0708013d-51a8-535c-bd10-3d6f229329d2 | note | Verifying Document - Visual Inspection
950eab39-7f6f-598c-b4bc-b438a93cd9a9 | note | Testing Quantity Required (based from schedule qtys) - Every time
7c294134-4f12-5c05-a658-a9c7c627ad90 | note | Verification Activity - H
3f51bcd6-f532-5373-99ff-edace48712db | note | By - SE
b17ed789-fce9-5f0b-af6a-f65804704759 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
b30154a2-27cf-4399-9ebd-8961bb518b47 | signoff | AUTHORITY HOLDPOINT
4fede5a1-b426-4107-93fe-fbd3a4824ffd | checkpoint | 3.1.15 - Pit Installation Bedding
4ba50b52-7982-5304-a05b-b5ece97d1dda | note | Detail - Bedding with 150mm compacted GAP20 covered with 20mm compacted sand
f714ef28-6d1a-5fe8-b6e0-c8594a9f683b | note | Acceptance / Conformance Criteria - 150mm GAP20 covered with 20mm Sand
88a7d06c-e1cd-5f91-b95c-78a49a4d9b81 | note | Standard / Specification - PS 25.13.8 d)
f3588442-3583-5377-886f-1334bf1a0099 | note | Verifying Document - Visual Inspection
4a69ed86-2acf-5fb1-ba3b-a28f9a65b3be | note | Testing Quantity Required (based from schedule qtys) - Every time
9f492a93-7b7f-5b2c-bb98-924386c86df8 | note | Verification Activity - H
a4bd4db7-0e1e-51c1-b511-0cf4fb01e48f | note | By - SE
cdd9bd87-4c5e-595c-bae4-1b37f5494cab | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
0bd6e6a0-05f2-41ed-8cf5-802339320a6a | signoff | AUTHORITY HOLDPOINT
fe4a52eb-50ec-46b2-829a-261874d7888e | checkpoint | 3.1.16 - Pit Installation Backfilling
7d489dc7-5bbc-5fb4-9b31-a0f8163f708e | note | Detail - Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts.
500e8173-6802-5b17-a562-f5da50056f90 | note | Acceptance / Conformance Criteria - Min 92% compaction rate and Average of 95%.
ef7d94e5-4ee1-5d47-89e9-4f90d2138b3b | note | Standard / Specification - PS 25.13.10 a) modified
3e39b019-1e19-5ace-9f61-521efd6d31db | note | Verifying Document - Visual Inspection
72261735-3e57-5fe8-98e5-1f9fe9c01b44 | note | Testing Quantity Required (based from schedule qtys) - Every time
b747e77b-8f12-5546-96fd-5bdbf812d01f | note | Verification Activity - H
301bcfe1-402b-5b92-bc23-86c8a3fb4796 | note | By - SE
effe1658-db19-571c-b1eb-3597f1a6ecb6 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
81bc6170-8c9c-45f0-b620-12e1089e96ca | signoff | AUTHORITY HOLDPOINT
a1333581-120a-45d8-9b00-bb9c191658e9 | checkpoint | 3.1.17 - Pit Installation Clean up
cea66dc3-485e-5822-8e9f-c030703f0300 | note | Detail - Clean out all pit after completion of the work
ba3186df-c924-5b82-ac04-b2f5eae40ea4 | note | Acceptance / Conformance Criteria - Pit are free of dirty, mud,water and foreign materials
4a67d1d0-2cf3-5de9-aca4-16a4e0882ed1 | note | Standard / Specification - PS 25.13.8 e)
42dd3885-0376-5ec5-9b6d-c0db556cf49d | note | Verifying Document - Visual Inspection
bcdb6a29-93e7-5635-ac42-4cf1cfdf82ef | note | Testing Quantity Required (based from schedule qtys) - Every time
01606bd5-cb4b-5683-ba2d-65dbe816a496 | note | Verification Activity - M
c7db4af7-46f8-560c-8b92-e1d42d0b4448 | note | By - SE
4b3f379c-f817-5f86-b89e-9105a8b52a80 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator will clean the pit.
c508a466-171c-4f79-875c-c23e6a410c2f | checkpoint | 3.1.18 - Survey As Built
f986c5ac-7748-5e6b-b32b-c2a181dade03 | note | Detail - As Built every ducts joint before backfill
f9fbcc29-98d5-562e-84e9-57d1f7357dcf | note | Acceptance / Conformance Criteria - Completed as per drawings
108777ac-97dd-5670-b2fd-aa1ebb5ff775 | note | Standard / Specification - Standard Practise
c091fbf0-ef67-52e4-a28d-f14313c9f7ef | note | Verifying Document - Survey
449f69b7-8db5-5180-9127-5cd276569e69 | note | Testing Quantity Required (based from schedule qtys) - on going
0542d6c1-82c9-55fd-9307-73923cbeb027 | note | By - PE
8684bf06-73a7-4869-a78a-feab8acbd2f0 | section | 4. POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - 4.1 AS-BUILTS
2af294bc-bf87-484b-989f-db926cf70510 | checkpoint | 4.1.1 - Survey As-Builts
53cf4a25-16e2-5051-b5db-eb5ec3759817 | note | Detail - Quality Check on New Works based on the tolerances in RITS
83de8240-0fb0-5adb-8cdb-1750f0103661 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
b9ffad88-9cb4-57f8-b1b9-5dedfdde3f02 | note | Standard / Specification - PS-21.7.7
bbed9c01-fa35-530b-ab40-200efdd164d8 | note | Verifying Document - Red pen markup only
313a5680-5efb-513d-9f2e-dcdbdfe71f03 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
e4c858d1-5129-5530-baed-d20d31d20be2 | note | Verification Activity - H
9394f156-0b56-5a84-8b84-7ffc7787352e | note | By - SE
a072cf05-9802-47ac-9772-7070c5ba6526 | signoff | AUTHORITY HOLDPOINT
883bc83d-ede3-411c-818e-9c174952ad4f | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
1ca370eb-b058-595e-a9ed-d66f689435ee | textbox | Contractor's Rep Name:
5fe4ef1b-aeca-5f08-b1dd-a92b48753f25 | textbox | Engineer's Rep. Name:
db1422ec-6c03-598b-96e0-d0dfa9ae47fc | date | Date:
e3308bb4-14be-4adf-9e64-6431ddef9d3f | signoff | Add Signature
1f3c3fcb-78d1-4127-bc4a-8df8f2c3f654 | checklist | DN1210-013 ITP Surfacing EME Rev 1 | itp | DN1210-013 ITP Surfacing EME
90555150-c218-440f-9a27-547fcc3b4fad | section | 1.0. Pre-Commencement Activities
53e3d4cf-8e68-4ea5-bff5-ad16396d733d | checkpoint | 1.1 - Approved JMF for EME2 Base Course
d8726d28-6023-53e0-9607-f412c132e329 | note | Detail of Activity / Test - EME2 Whitehall V1 T24/3436
a0259e27-b134-5882-9a53-68930d4fa0cb | note | Action (Hold, Monitor, Witness) - H
2ddf311a-e1f1-52c2-815c-6c556231d46a | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
5acaf4cd-ddcb-5f41-96b0-68f3395c516d | note | Inspection / Test method - Confirm requirements are followed
544c89c1-772a-5b69-b023-20c65501354e | note | Acceptance Criteria - JMF Validated in accordance with NZTA M/32:2021
ae77f756-071f-5416-9d9c-d7596e9f02b2 | note | Record documents (QCP - Quality Control Portal) - Mix Design Report
562604a4-f3d1-5581-8f62-83f7c0aa26c3 | note | Responsibility - Paving Contractor
6d74af2c-9a14-58f4-8982-8ef88301a8aa | note | Designer - A
a1bdfa76-99c4-5dc0-9716-3e334b8f4909 | note | Eng. Rep / NZTA - I
425a57f8-d813-5944-8473-bc9bd40b4b63 | note | Contractor - R
7196002d-9f9a-430e-bc8a-1bda014ca31b | signoff | AUTHORITY HOLDPOINT
0a04a84d-8a66-4722-a8a6-bb4082803d33 | checkpoint | 1.2 - Approved Quality Plan/Renewal Quality Plan
d5128a0d-150d-58f6-9663-c0e32aed106c | note | Detail of Activity / Test - Prepare and Submit RQP
07d8607a-4c7f-5196-8bed-d1fc77850ee2 | note | Action (Hold, Monitor, Witness) - H
25fb6bf9-6f25-5de6-9049-2b161bf6aace | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
dacac2b1-9c2f-578b-8d6a-1571fb03b6ea | note | Inspection / Test method - Review /Acceptance by Engineer
ab1a1b04-199a-58c9-9736-ee8b4cdd2680 | note | Record documents (QCP - Quality Control Portal) - RQP
4f5278cd-2ec7-5efa-977b-6ce4762d1ada | note | Responsibility - Paving Contractor
633b2f25-8074-5441-b655-b8730c110531 | note | Designer - I
9a77d6ce-b865-5f49-b7a0-c4a88b51461b | note | Eng. Rep / NZTA - A
5dbd0480-aa40-5985-94fb-09b356baba83 | note | Contractor - R
3307b532-7d4f-4682-9932-e0cde264a8f4 | signoff | AUTHORITY HOLDPOINT
f3a79375-a4a1-48a6-a4eb-e524007283f8 | checkpoint | 1.3 - TMP Approval
9e8e04fc-9405-5e49-a04f-5abb4d65d006 | note | Detail of Activity / Test - Prepare and Submit TMP
74d84884-4964-5b23-9165-54eb1f1417db | note | Action (Hold, Monitor, Witness) - H
610d656e-daa7-5618-98e5-1cecb82dc5b6 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
e7d85e54-0c02-50ac-9df1-558f86322cf2 | note | Inspection / Test method - Review /Acceptance by TMC
8577cd9e-4bf0-5abc-8ed0-d463e88b84a2 | note | Record documents (QCP - Quality Control Portal) - TMP
bfa74ea0-3264-540a-a5d1-5d049e618ba0 | note | Responsibility - Paving Contractor
999b831d-1594-5567-bdd6-b3c9d1bbd2a8 | note | Designer - I
ef5e26a3-5a6a-5fdf-a491-db952d02813b | note | Eng. Rep / NZTA - A
3d9a3cd5-a53f-5f56-9c5f-f041455079e6 | note | Contractor - R
c13a1c7b-0774-4b60-b96c-b9130733e9f7 | signoff | AUTHORITY HOLDPOINT
071a64dc-464e-44c1-9d94-d9c110e1f0f2 | checkpoint | 1.4 - Public Notification
feb77416-6de7-5657-a0c9-8bb12c989748 | note | Detail of Activity / Test - Communication with affected parties
bae40a06-a77f-5feb-aecb-a65e4bd645dd | note | Action (Hold, Monitor, Witness) - H
699ccbff-67de-5f1b-b010-1cc261b0f771 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
c27368d6-c7a6-54cc-ad99-e9071d6f909d | note | Inspection / Test method - Media/Letter Drops/TREIS
3cd38d19-3da1-58e8-8f2b-250192c5aef3 | note | Acceptance Criteria - Letter drop to local residents/ Greater consultation as required
b9ed9752-5f30-5d18-8a90-3947bd32e4bf | note | Record documents (QCP - Quality Control Portal) - Letter
b07b45b7-8e69-5dc9-84bc-92b52fb6c462 | note | Responsibility - Paving Contractor
98d970c8-6d88-5b5b-b494-7c4c38918a85 | note | Eng. Rep / NZTA - A
a75c477a-c8e3-5737-aaf2-c62a276a6ad5 | note | Contractor - R
b5f63704-1ea8-456e-8692-417435fb8258 | signoff | AUTHORITY HOLDPOINT
fbe6a576-7bfc-4561-9f23-f24f64707716 | checkpoint | 1.5 - Crew Briefing Plan
f575b5ea-0176-55e0-93df-04066de84291 | note | Detail of Activity / Test - Prepare and submit CBP and VMP
dd77976d-5ead-52d0-bdf9-10c103fbcfa2 | note | Action (Hold, Monitor, Witness) - H
6924bb72-289e-5a14-88e8-712a3aefc2ee | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
ab0e6db3-b377-530d-937f-fd17db523e17 | note | Inspection / Test method - Written Plan
f336549c-98ee-5d8f-bad2-b5ddbbfbcfb3 | note | Acceptance Criteria - Approved by Responsible Manager
4c53c8bc-e59f-5381-b879-d021903fb88a | note | Record documents (QCP - Quality Control Portal) - CBP
c9554978-185e-50bb-9a0e-82c91b13a6b3 | note | Responsibility - Paving Contractor
d2fffa30-52a6-5165-8171-ca14a3225364 | note | Eng. Rep / NZTA - I
02d7c548-8dc8-5984-be17-6192172b73a3 | note | Contractor - A
77aee04a-1439-47a8-8e1b-8d62b9a0e092 | signoff | AUTHORITY HOLDPOINT
3e312c5b-8185-45e0-9e95-af333d2045b7 | checkpoint | 1.6 - Site Conditions
d02bb5aa-88df-54ce-b1b7-f2f5d6c73415 | note | Detail of Activity / Test - Weather suitable, Site extents marked, surface suitable for paving (Depths/milling/cleanup complete etc), Environmental Controls in place
f2dc5bf7-8254-5abf-9cbf-e3ab21d1ca63 | note | Action (Hold, Monitor, Witness) - H
3a1f252f-fc45-5c9f-b989-6b68a889abb8 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
ffcb4af1-cac0-51f1-8c2d-4a05054850b8 | note | Inspection / Test method - Confirm requirements are followed
9a4303f1-0b84-5153-8e35-2b7e89a59afe | note | Acceptance Criteria - Weather conditions and Site is suitable for paving
29fe3c73-89d5-5a81-9ced-310c6b190447 | note | Record documents (QCP - Quality Control Portal) - Site Diary/String Sheets
0269ac2a-6262-5f47-a364-5d03fc1c1d80 | note | Responsibility - Paving Contractor
b42129e5-73d4-5c69-a916-0e22308feafc | note | Eng. Rep / NZTA - I
7e7c7d70-c348-5f2e-a55c-b6c80525113c | note | Contractor - R
8ff84887-8f93-42f3-bb2c-056076ffd1bd | signoff | AUTHORITY HOLDPOINT
f23cdff8-3aa3-4588-9730-e53dda40ff35 | checkpoint | 1.7 - Traffic Loops
b38ba871-9610-563a-880b-6f3c1fcf3570 | note | Detail of Activity / Test - Communication with affected parties
cbaf637f-98f5-587b-bac2-a58e538dc7c8 | note | Action (Hold, Monitor, Witness) - H
f84478e9-4a8b-5064-9a96-04889435d858 | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 7 days Before Works commence
a5789dc4-203a-5c86-9aa4-18ebd00a8d0d | note | Inspection / Test method - Visual
f2f97555-fc28-50fe-8412-01fef6bf0fe1 | note | Acceptance Criteria - Notify RC at least 7 days before surfacing is programmed
91a9260f-5123-50fd-bac1-1196d154ff32 | note | Record documents (QCP - Quality Control Portal) - Communication
f991f379-2d7e-5b62-8e1a-88af229e5c6b | note | Responsibility - Paving Contractor
36f37b9b-88b1-5bcd-a1aa-69ac3c8f1518 | note | Eng. Rep / NZTA - A
6c2b6964-f14c-5e7c-b4d3-17dde35f6e27 | note | Contractor - R
749c3c97-2a7d-4d8f-9902-ecf5b1fc6a9e | signoff | AUTHORITY HOLDPOINT
ec493d14-6768-4494-ac98-49d871cf8473 | checkpoint | 1.8 - Paving Plan
2c13cb21-0ef4-5342-82a0-c606375ea05e | note | Detail of Activity / Test - Paving Plan to be completed
8963f05b-4476-553d-9cd7-034253e82f72 | note | Action (Hold, Monitor, Witness) - H
eee9a839-2ef2-52e5-93cc-00dc90bbcaec | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
cb5ab1f2-8f1e-5872-a0d1-b268943e9fbc | note | Inspection / Test method - NZTA M/32:2021 Clause 9.5.1
c7bfff1c-2019-5e53-aa89-98a217b40375 | note | Acceptance Criteria - Paving Plan to be completed for each shift
423ab632-a605-5599-afc1-63949239bce0 | note | Record documents (QCP - Quality Control Portal) - Paving Plan
fabf057e-2960-5991-b2df-74453edf1351 | note | Responsibility - Paving Contractor
f8f0cb95-09eb-542d-8438-e44940aca017 | note | Eng. Rep / NZTA - I
028ec8dc-f97b-578e-b1f4-7ef8655e44d1 | note | Contractor - R
6a4cdb7b-3b77-4c3a-a943-251ee6933f52 | signoff | AUTHORITY HOLDPOINT
2abf3f43-b7fc-4125-bb9c-6a2a703021d1 | section | 1.2. Mill and Fill (Only Applicable for pavement type 1)
ce226894-c4e2-4404-a957-5bde34a9eceb | checkpoint | 1.2.1 - Stringlines or equivalent
cdcd8dd9-7154-5b34-9e8d-49c9c4be78fe | note | Detail of Activity / Test - Stringlines or equivalent to check finished height of surface prior to Placement of membrane seal and EME
286f2f91-53f0-5dfe-aa3a-73be5bc72291 | note | Action (Hold, Monitor, Witness) - W
18525fb9-ce94-5334-9cb1-733c491586dc | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
c4602ad9-e0cb-5070-8645-267db21e56e7 | note | Inspection / Test method - As per Pavement Drawings for pavement type 1
f289b506-bf6f-5ffb-a46e-e8f04047df70 | note | Acceptance Criteria - (-15mm +0mm) (-235 from finish Surface )
5d564f00-eee8-52d0-9a09-1dc03c5effc4 | note | Record documents (QCP - Quality Control Portal) - Survey Sheet
b7bc509a-017a-5951-bb59-6dc77ae90295 | note | Responsibility - Project team
aa5d97d2-a054-570d-b43a-22985fece59d | note | Contractor - R
092e1b30-7b8c-434b-a528-72dc914c99bf | checkpoint | 1.2.2 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
7786eb31-a3af-509e-a84d-69ed51cfaa2d | note | Detail of Activity / Test - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
e5d5d569-0e44-5919-9463-f29713f30937 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 1m below the design basecourse level (-235 from finish level)
b3f96509-5c6e-5c5f-92b5-91b173029401 | note | Action (Hold, Monitor, Witness) - M
7426e1c5-eccf-5020-997e-89d764ebb6ec | note | Minimum Test Frequency (Lot = 1 day’s production) - Every 15 m
314a57dd-16f5-5177-81ca-552bf3c46053 | note | Inspection / Test method - As per Pavement Drawings for pavement type 1
6be60d69-3962-5156-a239-010ec609e5f1 | note | Acceptance Criteria - Minimum 3 blows per 100mm penetration
295e3fe6-e34d-56ca-8bea-c6b8623adb1e | note | Record documents (QCP - Quality Control Portal) - Scala Report
cbe95cf9-85e9-5a51-9174-c9fa33501ae9 | note | Responsibility - Project Team
ca7fb482-d2f6-5786-8798-b4d149b323a9 | note | Project Specific Notes / Instructions - Note: If the CBR is less than 6, Pavement type 1A ITP to be followed. Or An approved by an Engineer.
330af163-48d1-5c50-9a8f-15d82f882944 | note | Contractor - R
b6294803-740b-45be-902e-c30277a3a8ba | section | 2.0. MANUFACTURE OF ASPHALT
4eb7f6ed-4ae4-4a2e-b76a-ef73d952d804 | checkpoint | 2.1 - Temperatures
2615c758-329f-5e9d-8da3-47858c2be2e0 | note | Detail of Activity / Test - Mixing of aggregates and bitumen
dec099e4-2609-5edc-968f-48e03254bcc0 | note | Action (Hold, Monitor, Witness) - M
81232165-a0c6-536b-9032-6fb6da91bacb | note | Minimum Test Frequency (Lot = 1 day’s production) - Constant monitoring of temperature by calibrated euipment
4fc82854-f43e-5411-a9b6-763e9e678e84 | note | Inspection / Test method - Plant temperature probes
1a7a48fb-fd93-5792-9767-18f7b1325de0 | note | Acceptance Criteria - EME2 binder Mixing range 180 - 190°C
8ceee789-1d67-51ec-b564-67478fe46303 | note | ○ NZTA M/32:2021 states max. 190 deg.C
7f9c795a-9b86-572c-8e55-986e9ba4cc5f | note | Record documents (QCP - Quality Control Portal) - Plant site diary
81dacd1e-489b-5840-89f1-9aea0d36f2e7 | note | Responsibility - Asphalt Manufacturer
53fd666d-24ca-5d90-ab9b-9ed6f5a21df7 | note | Designer - I
9742246a-6389-54a5-882d-833b49f5c033 | note | Eng. Rep / NZTA - I
f33fe83c-3f5c-5938-815b-c3207daf1b02 | note | Contractor - R
c89eab6d-c269-49f5-8337-82e7c3162d8b | checkpoint | 2.2 - Production Asphalt
7213158e-ccdb-57c8-a32f-5dafe28f56bb | note | Detail of Activity / Test - Particle Size Distribution
5c18c652-91d1-5f60-a021-342c761cbc51 | note | Action (Hold, Monitor, Witness) - M
abccd3fe-60e4-5855-9245-9cb6b6ab1ef0 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
eba2d8ba-6aaf-504c-8057-0c7ae67c1b6a | note | Inspection / Test method - NZS 4407, Test 3.8.1
f623c518-d095-5ce7-b099-a113afa392aa | note | Acceptance Criteria - NZTA M/32:2021, Refer to Table 5.3
784b01b4-2ace-5518-83cc-994242418a66 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
24c6a835-3500-5f2b-9fdb-6964857010b7 | note | Responsibility - Asphalt Manufacturer
3c71d6fc-0041-5d58-adc4-14bdc2787eb1 | note | Designer - I
c0d361dd-62d5-5089-b4c0-e0e8d44551ec | note | Eng. Rep / NZTA - I
ac8bf286-f064-522b-969e-d29376d8a280 | note | Contractor - R
4f32417f-0be0-4c07-bf13-0f210274d929 | checkpoint | 2.3 - Production Asphalt
48e69e8f-81f2-52d3-84d5-2d17d790c844 | note | Detail of Activity / Test - Binder Content
ece8d70f-acf0-59d7-983f-7657cca9a471 | note | Action (Hold, Monitor, Witness) - M
3aadaa53-0c9e-5f07-92c7-4ae86dd23ce4 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
26c487a6-7d41-56a7-8dc9-7ebf74bb0675 | note | Acceptance Criteria - NZTA M/32:2021
353decd0-c16d-551b-bf90-be728a266a43 | note | ○ Individual Test Result: ± 0.5
1fa7fe09-9048-5050-a112-31f9c0d3c536 | note | ○ Mean of Three Test Results: ± 0.3
566da329-5c4e-5d55-ab9d-0ecc0ce9153e | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
b2e7ffd1-c6cf-5169-a96e-26df8a345ee9 | note | Responsibility - Asphalt Manufacturer
00cc3439-d13e-579d-b90a-82b86691e1df | note | Designer - I
dac685a3-58d7-597f-b247-2c584dfda06f | note | Eng. Rep / NZTA - I
426f4831-e6c8-50f5-953e-6e530d8ae5d3 | note | Contractor - R
9ba7a860-d5d0-42ad-bf3a-5f8c26ab497b | checkpoint | 2.4 - Production Asphalt
3cff7c88-507f-5f27-bece-3144a88a5814 | note | Detail of Activity / Test - Max. Specific Gravity (MSG) of mix
e79b0f8d-c5c5-5c68-864c-e7c4e6145d7d | note | Action (Hold, Monitor, Witness) - M
814ae9ee-5162-56d4-a19c-0435b73ef700 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
418f2633-1ca1-56cb-b0c1-193a764f0493 | note | Acceptance Criteria - Report
ea2a54f5-0df7-5c07-97ca-f04300a0e505 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
7e793629-01b3-5dd7-bfa5-e59c24246f45 | note | Responsibility - Asphalt Manufacturer
932ddc02-092a-5d77-8ec9-0744e99fba77 | note | Designer - I
ec683fa5-c9f0-5063-a211-5d376f50b48a | note | Eng. Rep / NZTA - I
41f1f310-729e-54bd-9f76-c0fa3e4f2e1d | note | Contractor - R
cb3fd138-6ec2-41ce-97e6-2d6459b2c682 | checkpoint | 2.5 - Production Asphalt
6959e388-4cf4-5ad4-aee0-b76996954a6c | note | Detail of Activity / Test - Air Voids at lab design compaction
9562c194-24eb-58af-8815-b04467bfd31e | note | Action (Hold, Monitor, Witness) - M
f41cc873-6542-5f9c-a00c-839f8deb49ef | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
74d924c6-7421-50e1-9809-cda1324648ff | note | Acceptance Criteria - NZTA M/32:2021
c1a23c1b-9995-5b8b-b95f-2c54489d7700 | note | ○ Individual Test Results: +2.0, -1.0
282cae58-b8d9-5700-a049-220d26f2ba4e | note | ○ Mean of Three Test Results: +1.2, -0.6
ac0af13b-c183-599b-8c92-9a2fd9b997e0 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
1f25d7a9-451d-54ac-b07f-7b73c0888e62 | note | Responsibility - Asphalt Manufacturer
033007df-8594-5a93-bfdc-f422cf3e05f2 | note | Designer - I
d2e87fc6-921f-5181-ac63-d3aafd2ffaf6 | note | Eng. Rep / NZTA - I
e3063d3b-abb0-57f7-8a66-7d58af286aee | note | Contractor - R
f020b356-945b-4863-9941-b5cdbe4e3f4c | section | 3.0. PLACING AND FINISHING
0afe85dd-be12-4a4d-b2ad-58b77a355f5e | checkpoint | 3.1 - Milling
4a843451-f2c1-5050-8cbf-1d5652740212 | note | Detail of Activity / Test - Surface strung to ensure milling Depth is achieved
73661ce7-c6b9-5dc4-a673-0beb864e9dcb | note | Action (Hold, Monitor, Witness) - H
1e433a86-846d-5625-a542-d523828e544a | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
3622c83a-5895-5b51-aa2f-b7aed56070f6 | note | Inspection / Test method - Confirm requirements are followed
2e1c0a9d-11e8-51fb-8902-89328e10a621 | note | Acceptance Criteria - Site is suitable for paving
1fb4e4d0-cf1e-5234-b3bf-5ecf47281e79 | note | Record documents (QCP - Quality Control Portal) - String Sheet
7a3f744d-1da0-500c-8cae-34b988f46b17 | note | Responsibility - Paving Contractor
639ed026-157a-53c1-85f4-c995ef265b82 | note | Eng. Rep / NZTA - I
fc4a27b2-8df3-5bdb-abf7-3526bc74bb23 | note | Contractor - R
6289d73f-2996-493e-aa7d-0f5e5c68c5e2 | signoff | AUTHORITY HOLDPOINT
78ac0994-cb3d-431e-80c5-a8dd1a27e59a | checkpoint | 3.2 - Tack Coat, OR
562f3869-e372-543a-a52e-62f124c3c6ab | note | Detail of Activity / Test - Application of Tack Coat
ab3330e8-20f1-520b-9f48-1afee9dc728e | note | Action (Hold, Monitor, Witness) - M
cd069770-0343-5dac-bd2a-5f6d92580c3e | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
8bd2bb74-3053-5de4-811d-26fd1d12c06c | note | Inspection / Test method - Dip bitumen emulsion tank before and after
fa9f5c51-0a8e-5c23-8bf0-608204749aef | note | Acceptance Criteria - Target Between 0.2l/m2 - 0.6l/m2 +/- 0.1l/m2 From Target Application Rate
7b33274a-0fb8-537d-82a0-684875c0fc99 | note | Record documents (QCP - Quality Control Portal) - Site Diary
94f3e780-6eec-55f1-96d2-c7535ece5e06 | note | Responsibility - Paving Contractor
d9c20d1b-6a46-52e1-ba63-906a4c9322da | note | Designer - I
1814b80a-c02c-5d18-896e-c708389ffae5 | note | Eng. Rep / NZTA - I
17f0fca5-1439-5be4-99b6-a4cba8d529ef | note | Contractor - R
8abc4c66-6b64-46b4-b244-ba873bc2d80d | checkpoint | 3.3 - Membrane Seal
25ae3c5b-71b9-5a7d-9510-91dd193b35b9 | note | Detail of Activity / Test - Application of Membrane Seal
7fcf3160-c877-52e4-9b20-1a794c967a0d | note | Action (Hold, Monitor, Witness) - M
8b7b1e3f-b358-5cd3-8e85-03f0059ef791 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
27efe21c-2945-593c-a1ed-2d6864dd264e | note | Inspection / Test method - Sealing Records
1067d2ce-3d3f-5bd7-b3b2-30aebc7f26de | note | Acceptance Criteria - Application rate, chip type and binder as per membrane seal design
436208ba-a97a-5064-bf6e-d223837fe6ac | note | Record documents (QCP - Quality Control Portal) - Sealing Records
65f28276-8531-5be1-968b-84e152525b29 | note | Responsibility - Paving Contractor
f003cb72-fb68-5edd-bf78-8355b8b62fa1 | note | Designer - I
7de6f0d0-0475-5d95-934d-b83bec7b2717 | note | Eng. Rep / NZTA - I
a1891846-ccc0-52c4-a071-3eb33bac9ad5 | note | Contractor - R
c646669d-81d4-40a0-ac50-84f8a79db178 | checkpoint | 3.4 - Temperature
95217190-faf9-5a52-b9d8-3507bcd3522b | note | Detail of Activity / Test - Pavement Surface
fdd852ee-b2b6-5666-b891-a1869865172d | note | Action (Hold, Monitor, Witness) - M
e50fdfff-7d89-518e-bf1c-f9515de93926 | note | Minimum Test Frequency (Lot = 1 day’s production) - Start of shift and every 1 hour until temperature rising
8ee086a9-e072-5a08-8f79-b1c694138236 | note | Inspection / Test method - Infrared gauge
d25c6950-59ae-5a7e-915a-15c8f0d6cd60 | note | Acceptance Criteria - ≥ 5°C for Structural, or as otherwise agreed with NZTA
b890e363-85c6-59d5-a530-7d6ba36ff2d6 | note | Record documents (QCP - Quality Control Portal) - Site diary
5e35e01e-1ca8-5202-b48c-7d2d3ff7e548 | note | Responsibility - Paving Contractor
f5901305-3f2d-5dd0-bfc7-ceafa5aa1ca5 | note | Designer - I
5c3e0b1f-95d0-5671-9eeb-968fc997ea3e | note | Eng. Rep / NZTA - I
d41c0f98-d8d1-5495-9216-ca5dc554f87c | note | Contractor - R
334f6c8a-6448-4b27-b01f-97c063964dcb | checkpoint | 3.5 - Temperature
5e0a760f-6341-5f35-b21e-25505bac942f | note | Detail of Activity / Test - Asphalt Delivery temperature
d3d23e76-331f-5ff6-a467-c7984297d1fe | note | Action (Hold, Monitor, Witness) - M
f9d5119e-552a-585d-b06f-08be6c77663a | note | Minimum Test Frequency (Lot = 1 day’s production) - Every Load on delivery to the Paver Hopper
3dfe43d7-c8a0-5aa2-9d48-6b6283e3eef0 | note | Inspection / Test method - Temperature Probe/Infrared gauge
e5aa21a9-eb6c-56af-bde7-665a9ff46798 | note | Acceptance Criteria - Target ≥ 150 deg.C. in the Paver
a80e5b70-4c28-513e-8e3f-5df6a8203bc5 | note | ○ Min. ≥ 130 deg.C in the Paver
90670339-ce3b-50c0-b053-7b5518669539 | note | ○ <130°C to be Rejected
a765937c-8cab-52d2-ac51-2352b35613fa | note | Record documents (QCP - Quality Control Portal) - Site Diary
b12dc223-82ee-5f31-8c07-0b33e3710b5d | note | Responsibility - Paving Contractor
d3448472-3296-5f4e-a518-3cee0678a2e7 | note | Designer - I
ed7ad57b-8972-52ae-b865-eabc95e37b63 | note | Eng. Rep / NZTA - I
ec9a2c3f-a9de-50e4-88cd-177af2bfff47 | note | Contractor - R
3edaccc7-63ee-43b9-a6fc-880169ba8a38 | checkpoint | 3.6 - Temperature
e01bcff1-f481-5f48-a054-102f8dbbb9f8 | note | Detail of Activity / Test - Compaction Temperature
a415ee66-9fe4-5ebe-baa9-7dc3e04cfa62 | note | Action (Hold, Monitor, Witness) - M
75aee3b3-9b36-5c47-b31c-b7aba8fd5f4a | note | Minimum Test Frequency (Lot = 1 day’s production) - During compaction
b3c6899d-99c9-58b0-8ea8-4c17c1f53bf4 | note | Inspection / Test method - Temperature Probe/Infrared gauge
7b451404-c914-58ff-a689-2d05dc81efc2 | note | Acceptance Criteria - 130-150°C at commencement of compaction.
e7d528ee-47f8-5a49-bb6c-9c21be0df107 | note | ○ < 90°C - Stop Rolling
dbf54ac7-b2b8-591f-b53a-d0368cc762e7 | note | Record documents (QCP - Quality Control Portal) - Site diary
af9c8e07-7fdf-5068-90ed-0f5006490044 | note | Responsibility - Paving Contractor
16b31812-d4c7-5e6c-9c66-5c72b7d4fcd4 | note | Designer - I
f41eddbe-72ee-5a19-8576-828f3db44bbc | note | Eng. Rep / NZTA - I
09181dff-7910-50fd-ba8e-1df21bf2e825 | note | Contractor - R
2fd1da07-faba-4555-bdaa-f6d3b6b2cb40 | checkpoint | 3.7 - Mat
5fa5a44d-8332-5f42-8472-d35c237f4b85 | note | Detail of Activity / Test - Load Locate
c227a8ff-6cae-5e83-802c-363ece352dbd | note | Action (Hold, Monitor, Witness) - M
2597f3af-5a9f-518d-8e1c-f83b279147b1 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each load
bfad18f5-bb0d-52e5-9c17-7c3100b6a318 | note | Inspection / Test method - M/32
f5a5ad0e-50ec-5efa-80b1-3afedaee6083 | note | Acceptance Criteria - Each load can be indentified to a location using a diagram. Record includes:
39a2a416-e2f9-5f57-a5a0-43433fee394a | note | ○ Truck ID/Rego/Driver
b198248d-12dc-521b-8543-a3a22e2ab362 | note | ○ Depart Plant Time
1436610f-f7d8-58b3-86ff-93ff57ed7da4 | note | ○ Arrive Site Time
61558398-60ab-5daa-b456-ac8746ce7ea6 | note | ○ AC Temp on Arrival
9ef3832a-e6be-5009-a8cb-877e53823d25 | note | ○ Tonnage
9f269cc9-9f8e-552f-ae36-9b06ed956def | note | ○ Run Width
108e94ef-e52a-5e12-9db9-e351054aea64 | note | ○ Estimated Run Length
083d8d05-c288-50ae-984e-a6fe1064df6e | note | ○ Calculated Area
e77aa0ee-b4be-5e7f-92d0-861cb1013091 | note | ○ Calculated Average Depth
933d947a-46ec-5a4c-90ab-73b2880f851c | note | Record documents (QCP - Quality Control Portal) - Paving Run Sheet
a936bc0e-8774-51bb-83e8-5b41dfb8018e | note | Responsibility - Paving Contractor
e5b72081-a1a1-5484-9a2e-349a53a1d290 | note | Designer - I
788c66a7-8a3c-5fae-935f-6aed67e9495e | note | Eng. Rep / NZTA - I
e3b1a323-ae15-5086-ba11-ae38fc400124 | note | Contractor - R
968eaf1b-1e1c-47fe-acd8-6072e978fd18 | checkpoint | 3.8 - Mat
ae0b8880-f6d1-5aa8-9526-4f800644b3bc | note | Detail of Activity / Test - Thickness Monitoring
aafb4e7c-dd21-5579-bcea-1589ccaffb96 | note | Action (Hold, Monitor, Witness) - M
a506507f-177c-5afe-b953-da7be95dc084 | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
f72d5af8-242f-5b15-bd28-135466ffc7cd | note | Inspection / Test method - Dipping
5ad6dcee-b595-5353-8619-9c7c0a6dbac5 | note | Acceptance Criteria - Target Loose Thickness -0mm / +10mm
9d22e03d-a5a0-5ab2-babf-3ee861ac8856 | note | Responsibility - Paving Contractor
dbfd62d8-82d5-53d7-bf67-561460ff6f6f | note | Designer - I
021f212e-7748-598e-b952-2e4bf941fa29 | note | Eng. Rep / NZTA - I
1c66b3d7-dda3-56e1-be4d-68726ec7ade8 | note | Contractor - R
9a05ea4f-7391-4c53-b648-c8459c06288e | checkpoint | 3.9 - Mat
b942f4e8-9034-548c-ae30-32bf9427a5d1 | note | Detail of Activity / Test - Compaction - NDM
524874c4-550b-5daf-ae69-9a4ee999f4dc | note | Action (Hold, Monitor, Witness) - M
b85e6050-9eed-5ac2-a7f8-347fa49fc3c7 | note | Minimum Test Frequency (Lot = 1 day’s production) - Plateau to be completed on 1st run, thereafter monitor compaction/roller passes to achieve target density.
cbd3f529-997b-5f89-bfa9-a86b26ff994d | note | Inspection / Test method - Insitu density and air voids
1bd41b7f-7c7f-57a6-9d23-ed3ad7aa6797 | note | Acceptance Criteria - NZTA M/32:2021 - section 9.8
fe9702f1-5112-5aeb-8456-7415e01186a4 | note | Responsibility - Paving Contractor
9470f193-b554-522d-8cb9-4ba685626fea | note | Project Specific Notes / Instructions - Use a calibrated NDM with established core correlation. Locate and mark cores, record NDM Bulk density by core location (including any offset used).
d3c9c2dc-52a8-5faa-8375-57a4ed017432 | note | Designer - I
e9aa7c58-4e32-5fb5-bd72-6c2f4e236acc | note | Eng. Rep / NZTA - I
99d8c54f-6ed1-50a5-9985-662e030d12a6 | note | Contractor - R
71186777-be05-4610-a80e-d2611934f6a3 | checkpoint | 3.10 - Mat
e9e3a49d-8e30-5899-b797-7fbe01c7fe6b | note | Detail of Activity / Test - Compaction
788e20d7-2ea3-5935-bb8e-2bb35846d93e | note | Action (Hold, Monitor, Witness) - H
5610e79e-4963-509a-a96a-00d46647db75 | note | Minimum Test Frequency (Lot = 1 day’s production) - Mat: 1 per 300m2/min. 8 per Lot Joint: 1 per 100m/min. 3 per Lot, In the event of a day's production being > 30t but < 2400m2, then it will be permissable to reduce the number of cores to; Mat: 1 per 300m2 with a minimum of 4 per Lot, and Joint: 1/100m with a minimum of 3 per Lot
3fb6cd59-e57d-5e6e-9987-51106a3a0e3d | note | Inspection / Test method - Insitu density and air voids
90663f86-c55c-5dac-a21a-8e1d6be3b71b | note | Acceptance Criteria - NZTA M/32:2021 - section 9.8
bf08307a-6902-5f72-b43c-2c573cf19ea9 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
53a71814-2d56-586f-b8e6-98193e33a134 | note | Responsibility - Paving Contractor
5f889082-360d-5995-998e-4c930f7df187 | note | Project Specific Notes / Instructions - A pavement lot shall be an essentially homogeneous section of work completed within a shift of production.
8411a3ef-a1c4-5409-aa73-7d6ce3107d95 | note | ○ The lot shall be divided into an appropriate number of approximately equal sub-lots and a core shall be taken randomly within each sub-lot. The Engineer or their delegate shall use a random method for locating each core position, such as ASTM D5361 or a similar process.
25e01f4f-2acf-554b-b773-c3d9b9765310 | note | Designer - A
744c2672-c0ba-593d-98b2-c601f2c53bdb | note | Eng. Rep / NZTA - I
3376e5c2-b508-5cfd-8f60-af84b8ac3ce2 | note | Contractor - R
d078e82a-81f2-48cd-a222-ea5cd1c17010 | signoff | AUTHORITY HOLDPOINT
ddd9fa08-683e-4fe7-bffd-f2f486ce467f | checkpoint | 3.11 - Mat
0fb4a213-863f-5327-addd-c9a522da3177 | note | Detail of Activity / Test - Thickness
9bbb6de5-68e0-57bd-8ebe-f6187aedd9e7 | note | Action (Hold, Monitor, Witness) - H
ec4b03da-e81d-5101-9d19-fe49e741e3bb | note | Minimum Test Frequency (Lot = 1 day’s production) - Average of 4 measurements per core
ae585f97-b4f0-5642-beea-118c15d0c3d0 | note | Inspection / Test method - Measure Cores
ed060c9f-b306-57a7-8ebf-6c7ae3ac1a87 | note | Acceptance Criteria - LCV ≥ Specified Depth (Minimum)
9a3ee352-e735-5382-b656-28462fe19b7f | note | ○ NZTA M/32:2021 - section 9.7
80d401a2-4cb6-5da5-89fe-59f66d7a584b | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
9ef7fc52-636a-5c3d-b51a-ad67271f9e97 | note | Responsibility - Paving Contractor
2ea9fc12-cf61-50a2-8fdb-c6a2b98e0a8c | note | Designer - A
580472ba-675a-5914-a9cb-a3dcbcb3a47e | note | Eng. Rep / NZTA - I
6639c178-51da-50f7-b9a7-8c372708e8d8 | note | Contractor - R
5e21e4b6-4954-4d8d-81f6-fd7e0c9f9dd3 | signoff | AUTHORITY HOLDPOINT
7e9a9732-bf3c-4791-b186-3268f88f4c41 | checkpoint | 3.12 - Mat
ce1a2a68-0ac9-5288-9335-f9093ee4f369 | note | Detail of Activity / Test - Shape
acf06b8c-2de4-5ff2-817c-772dfe78c6cc | note | Action (Hold, Monitor, Witness) - M
43bc0e08-e8b7-5e7e-b69d-544c44b0df2a | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
d7b19ead-f4d1-5f95-bfae-d6ee60c30454 | note | Inspection / Test method - 3m Straight edge
3cd9e014-6193-5ca6-aaa9-8a77885e898c | note | Acceptance Criteria - Where the length of the site or the geometry is such that a road roughness-measuring vehicle cannot be used then the straight edge can be used for checking the surface shape. Refer NZTA M/32:2021 - section 10.
c101c21a-5558-5dd0-b9b7-c59a0121ddf3 | note | ○ Not more than 5mm under a 3m Straight Edge.
4d48a6e1-94ac-5f80-8494-2293c727a1fe | note | Record documents (QCP - Quality Control Portal) - Straight Edge Record
89c90973-be41-5d27-bcaf-d9b1da193844 | note | Responsibility - Paving Contractor
1bffd564-6299-5c8a-b272-f9fb9be39169 | note | Designer - I
4684a047-d3b9-5c93-b442-1274d2a57ae1 | note | Eng. Rep / NZTA - I
252366b8-d479-5346-8b12-0ec89efbd64f | note | Contractor - R
3af14346-d6f4-4f35-95b0-c0d06fa395c6 | checkpoint | 3.13 - Paving Quality
895c3a22-7356-5fa3-adab-937e051fb827 | note | Detail of Activity / Test - Texture
2da5cbf3-22e6-525c-b839-94c5cb00720d | note | Action (Hold, Monitor, Witness) - M
d14557d1-208c-5b78-baec-5ed3b4c8e377 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site (If Required)
bcd42084-0a20-5d5e-be05-aceb5e5d5d16 | note | Inspection / Test method - Sand Circle or HSD
4cda6cb7-435b-535d-9304-6e655bc062c1 | note | Acceptance Criteria - NZTA T/10: 2013
a5e1e8d4-4852-5991-a96a-3414983343d5 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
3eef4fdb-8e29-5cc8-bfa2-5f95d23f5118 | note | Responsibility - Paving Contractor
cd0be239-07e6-5aef-a573-a7593786ca0c | note | Designer - I
8b3835d7-9c81-5717-8d4e-e228af1dff5b | note | Eng. Rep / NZTA - I
1b6599c5-d79c-5010-96fa-f4d11bc4a76b | note | Contractor - R
50989137-0893-40ae-a984-bd1f7cfafa9b | checkpoint | 3.14 - Paving Quality
a5c261e5-8775-566c-a5b8-89c0ede3ca19 | note | Detail of Activity / Test - Level
a9311866-dfc5-547d-b7dd-4c06ca07b2bd | note | Action (Hold, Monitor, Witness) - M
57d373fb-33ce-5f28-a8cb-6edfbd7aa58a | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site (If Required)
65849f2f-6f6e-5e68-8e88-00c11cdd9411 | note | Inspection / Test method - As Built Survey
d391c391-1eab-50e7-a229-537e3404e68d | note | Acceptance Criteria - -0 < +5mm from Specified Level
95d0ecd9-76e0-574e-8714-dc5eba73730a | note | ○ Where there is Kerb and Channel shall be flush with or no more than 5mm above the LOC.
aa803f4a-e0c5-56fc-a7bc-d913187c7dc0 | note | ○ NZTA M/32:2021 - section 10.1
846a1e3b-41d3-561b-89ed-45556b5c4813 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
dc06e6d7-25fb-5307-9f7e-570c57946141 | note | Responsibility - Paving Contractor
dddf07a1-9aec-5463-b100-21f02f705bec | note | Designer - I
e6a281af-80be-5224-9986-ca28c7c2eb07 | note | Eng. Rep / NZTA - I
995f947a-d740-5e35-bca7-e5eb78946bf4 | note | Contractor - R
251453e0-7425-46d9-83c8-df97a3dd1a07 | checkpoint | 3.15 - Paving Quality
70256339-1da5-5c1b-9a7f-8b483f230de7 | note | Detail of Activity / Test - Alignment
62fe077d-2eb3-5783-a070-7210031a2e4e | note | Action (Hold, Monitor, Witness) - M
5050a288-d3ef-50d9-86a6-9747e5c12108 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site (If Required)
283f952a-65b7-5c4d-8255-09f2137337d2 | note | Inspection / Test method - As Built Survey
643aa2cf-a1ad-57f2-847a-7c440352db01 | note | Acceptance Criteria - ±50 mm from drawings
b367acd9-220f-59c8-936f-a11b54a69b77 | note | ○ NZTA M/32:2021 - section 10.2
053e446d-67ab-502d-b980-2fcf4d12f05a | note | Record documents (QCP - Quality Control Portal) - Survey As builts
6ab5e81c-e066-5c72-be31-6cc7faa83574 | note | Responsibility - Paving Contractor
3cd52e42-2b70-52ef-a457-f22820fa6ae8 | note | Designer - I
688eaf10-35c4-5098-8ac2-05cfc62f188c | note | Eng. Rep / NZTA - I
9cfc1d29-0243-509b-bc1c-fd162c255ff4 | note | Contractor - R
537f248b-da6f-4dc6-b37b-284a6d357fec | checkpoint | 3.16 - Post Paving Completion Checks
042da5e3-28c0-541e-aaa0-04618547924d | note | Detail of Activity / Test - Site clear and cleanup
b304495a-c5de-5eb8-933f-fdcc7181957f | note | Action (Hold, Monitor, Witness) - W
86a8da67-30a1-5882-9f4d-bc6ed8839708 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
86eab0ef-ace2-5917-b4c4-1ea5cef304e3 | note | Inspection / Test method - Visual
32f39019-2580-5ecc-9cc5-0fb6696d98c0 | note | Acceptance Criteria - Site is cleared of plant (or parked in safe location) cleanup of all waste mix, paper and detritus is complete
05390f60-7c7e-5697-a61e-aa9b85fdfb7c | note | Record documents (QCP - Quality Control Portal) - Site Diary
e6d8fe28-1af5-5c2c-b9eb-1a39846b829c | note | Responsibility - Paving Contractor
1459f1d0-86fb-5a81-9bfe-af73910bc25c | note | Eng. Rep / NZTA - I
32fedf5c-adb4-5d37-946b-60644bfec5f9 | note | Contractor - R
e3930173-2a65-4451-9a09-2361ac0d84a9 | checkpoint | 3.17 - Post Paving Completion Checks
c0b4fbba-0df2-5d6d-ba6a-5cb5a7d5cdfb | note | Detail of Activity / Test - Pavement Marking
5a29dbda-1c60-5ce5-a07f-9de7668c5f00 | note | Action (Hold, Monitor, Witness) - W
14a8a08c-07f0-5532-8a12-67d42785d6d7 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
b95b260b-0b61-5eff-8a81-fdf3a445cc46 | note | Inspection / Test method - Visual
515ae211-1e31-5fb9-8957-08e7ba1ac816 | note | Acceptance Criteria - Roadmarking is complete
8ad7ae51-da02-502d-9f5d-a860e61586cb | note | Record documents (QCP - Quality Control Portal) - Site Diary
c542e157-eafc-5607-875a-33d72a621b7e | note | Responsibility - Paving Contractor
52a96869-fd8b-57d3-986a-4674932d09fc | note | Eng. Rep / NZTA - I
016eac2e-4387-5852-97e8-a30144b48fbd | note | Contractor - R
7a92ee2b-bd21-4bf3-87bc-d08de8a1c631 | checkpoint | 3.18 - Post Paving Completion Checks
ffbd31dd-4e6b-5761-ba4e-5d530021b892 | note | Detail of Activity / Test - Cold Joint Bandaging
ae708ba8-fe18-5587-95b7-12484191e1c3 | note | Action (Hold, Monitor, Witness) - W
a8319801-bb6b-5be9-be3e-2e6ef27eae51 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
30a509ec-69fa-529f-9f65-5294afcb2332 | note | Inspection / Test method - Visual
ed81bfc8-524a-57c0-a16d-12537f920d78 | note | Acceptance Criteria - Cold joint bandaging is complete
61efc8a1-5e69-5f42-a5ba-1efdb1fb9aff | note | Record documents (QCP - Quality Control Portal) - Site Diary
af5d2538-c49a-5de4-adc5-81e7a09a21a9 | note | Responsibility - Paving Contractor
f1a960de-7f78-50a4-9f81-32e1d26e6da1 | note | Eng. Rep / NZTA - I
b621d845-0b87-5ab3-b603-c7e1416adef4 | note | Contractor - R
aadcba3c-f82c-4fe8-85d2-77dd75b55ae6 | checkpoint | 3.19 - Post Paving Completion Checks
bd9e7b65-205b-544e-a111-ca6b653232fa | note | Detail of Activity / Test - Service Covers Checked
52ce8fe1-ba20-5c2c-a305-e51e4cbd2c78 | note | Action (Hold, Monitor, Witness) - W
37ad8222-eb9a-557a-a921-2591f95aa199 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
792d3c74-0106-565c-a8cc-38c781db5b16 | note | Inspection / Test method - Visual
cc862365-e62a-560a-8df9-935c192a7adf | note | Acceptance Criteria - Check that service covers are cleared and level with the pavement
83d78c26-9efb-58d7-ac13-b9e91831e61d | note | Record documents (QCP - Quality Control Portal) - Site Diary
817aa501-e367-546b-bfd2-c2b0e3004469 | note | Responsibility - Paving Contractor
4a9f71d3-7cd3-5bda-8496-089441ca77c3 | note | Eng. Rep / NZTA - I
5b8a1daa-7f25-508c-978b-c6eeb58463e8 | note | Contractor - R
1e2a6d01-db5e-4076-9c49-803c07882d2d | checkpoint | 3.2 - Post Paving Completion Checks
c557cfde-65f1-54da-ab10-61a4b4f60694 | note | Detail of Activity / Test - Traffic Loops Reinstated
91521bb2-932e-572a-9146-72b696128607 | note | Action (Hold, Monitor, Witness) - W
6d9039ad-9c41-55f8-afe3-94cd74d36ba9 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
dbc28b38-5c24-5cd1-bd12-537791789fab | note | Inspection / Test method - Visual
9e1ad543-650e-5dc7-8d9b-f3099e1c8b4c | note | Acceptance Criteria - Check that affected traffic loops have been reinstated
9ccb657a-704e-574c-bdc9-89b84d386188 | note | Record documents (QCP - Quality Control Portal) - Communication
43e29b9b-ad25-52a1-8b2b-2e029f0c566a | note | Responsibility - Paving Contractor
321cc5d0-6cf5-5fd2-b1f1-6979759b7f1e | note | Eng. Rep / NZTA - I
6f499201-c4d4-5405-8ed9-3ae8f87e90c4 | note | Contractor - R
1f1679b8-ff49-4d99-a587-1efcc9033d98 | section | 4.0. As Built Records
41dc27e2-9451-4a1d-bad9-c2f98cb145a3 | checkpoint | 4.1 - Assessment of all test results for conformity
748f5b46-8a82-52ac-a58e-d93856f234cf | note | Detail of Activity / Test - Review against ITP Requirements
89869b31-6ed2-541b-b1bb-ac77131e5a56 | note | Action (Hold, Monitor, Witness) - H
1db243b5-96cf-582e-8161-b5528478219a | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
0f6407bc-efa0-5797-9a10-e159d1dc62cb | note | Inspection / Test method - Review
71b2ef9c-f331-57fb-8a12-023c36f77429 | note | Acceptance Criteria - Reporting of any non-conforming results to Engineer via NCR
18b11731-1403-5816-afa0-82b6e503e701 | note | Record documents (QCP - Quality Control Portal) - NCR
d8c6a656-9566-5113-ad53-daaf784f0890 | note | Responsibility - Paving Contractor
481ea603-83e3-5077-ab93-a0b55d5ebfdc | note | Designer - I
d59daba7-0939-5345-bae1-bd1530e87121 | note | Eng. Rep / NZTA - A
6b08a26d-ff21-5bf2-ad8b-c05a473e8e12 | note | Contractor - R
5f7356e3-3ce9-40b8-9a34-8855188e9d7d | signoff | AUTHORITY HOLDPOINT
834ed3c1-bd73-4d68-844e-4ae54eb083d9 | checkpoint | 4.2 - RAMM pavement and surface records
ab1f1148-f782-59ca-b710-410a7298ba70 | note | Detail of Activity / Test - RAMM surfacing pavement data spreadsheet updated
c3c55026-bac4-5ae4-a3e4-183c8fdd2cf8 | note | Action (Hold, Monitor, Witness) - W
b928a0a8-e3b6-56b7-94f5-b119d8fc948f | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
21fbd7e8-50f7-5ab9-b7bc-39cf5554df8e | note | Inspection / Test method - Prepare Data
2fd6c45d-f0a0-5357-8039-72eb217c1d55 | note | Acceptance Criteria - Over milled and Deep lift extents recorded and verified by Contract Engineer / QA
e7f9a797-6de8-5abf-b494-5b4bb2150ceb | note | ○ Spray sheets for membrane area received by Contract Engineer from Sealing Team.
be46345b-1f2c-5919-8f14-6227d799a9b4 | note | ○ Surfacing layer extents recorded and verified by Contract Engineer.
9f1fcc2e-75b5-568d-bb3a-9d2d013c4fd7 | note | Record documents (QCP - Quality Control Portal) - RAMM Spreadsheet
da93a5b2-6d5b-506d-8ae7-de0e0d28bdba | note | Responsibility - Paving Contractor
539cc33a-333c-5816-9a0a-db300df41fcc | note | Designer - I
bcb61852-f5c4-5785-8fd7-cf782773ca46 | note | Eng. Rep / NZTA - A
0e9dd0fb-dd5a-5f15-a316-5ed5d7d949a0 | note | Contractor - R
ae6761fc-bd00-41ef-984c-c35f643b458d | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
dff2d346-1ad5-54db-8f8d-5238422640fa | textbox | Contractor's Rep Name:
1146c89c-cb0a-51a4-9b90-095d0d16b2d0 | textbox | Engineer's Rep. Name:
c10f1875-23b2-5ba4-bbd9-1d9ed9f388c1 | date | Date:
4b465f45-987d-418c-92b6-767bab679cb2 | signoff | Add Signature
3cce7847-2ef8-49ad-b2a3-f789806312b6 | checklist | DN1210-014 ITP Cycleway DG7 Rev 0 | itp | DN1210-014 ITP Cycleway DG7
08493a89-9b3b-4bb7-bf8c-f97cbdd074c5 | section | 1.0. Pre-Commencement Activities
e657350a-7c0e-4cb2-b577-cac6434f78d6 | checkpoint | 1.1 - Approved JMF for Asphalt Base or Wearing Course
dddf9439-dd95-5ddd-abfd-3fa0f489002e | note | Detail of Activity / Test - JMF reference in here
c00251c2-04c2-59d1-a195-16f0dabb52f8 | note | Action (Hold, Monitor, Witness) - H
a2ad9335-36c7-562b-818c-e53ebe557476 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
ad3ccd73-f631-5852-999c-5b30509f85af | note | Inspection / Test method - Confirm requirements are followed
1b0c6033-6837-5a67-a0d4-352b1257e367 | note | Acceptance Criteria - JMF Validated in accordance with NZTA M/10:2020
8dfd37a3-8b8e-5bd6-86b2-674ab7ec90ee | note | Record documents (QCP - Quality Control Portal) - Mix Design Report
f928aad4-6f35-5799-b5e0-915a49261ec1 | note | Responsibility - Paving Contractor
50fafb55-c206-5c63-851a-bd104e8f59d8 | note | Project Specific Notes / Instructions - JMF expiry date and validation details in here
6af9f981-b3cb-5c6f-99e5-4cc38474897c | note | Designer - A
8fa7bbc9-722e-5f08-b08f-8ae0bd7e6c33 | note | Eng. Rep / NZTA - I
b81becdf-22b6-5c3c-89b1-669f373695c9 | note | Contractor - R
60aa20e8-df3d-40b1-a683-61cf4f51f11d | signoff | AUTHORITY HOLDPOINT
82766399-6f2c-4d7d-9f97-e42e9c2b43f8 | checkpoint | 1.2 - Site Conditions
a2ad2b68-d062-5514-a5be-637129173dc1 | note | Detail of Activity / Test - Weather suitable, Site extents marked, surface suitable for paving (Depths/milling/cleanup complete etc), Environmental Controls in place
bff2ebb8-cbdf-57f1-b87f-4fc26777ebc3 | note | Action (Hold, Monitor, Witness) - H
4bdaad4d-08ea-5230-a3e0-868efdedca36 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
e64dea5d-d8b7-53d7-a758-d775270fb7e9 | note | Inspection / Test method - Confirm requirements are followed
8829157a-32b5-5aeb-8303-e9e41c5bfe5f | note | Acceptance Criteria - Weather conditions and Site is suitable for paving
bce0249c-f3ee-5d94-9019-952186764c5a | note | Record documents (QCP - Quality Control Portal) - Site Diary
fa3f82cd-af39-5199-8bad-edd1e428728a | note | Responsibility - Paving Contractor
d1482769-bf22-5691-b81b-af756325940d | note | Eng. Rep / NZTA - I
a0b665c3-2cbf-5d8b-8923-080bfe357b79 | note | Contractor - R
65bbe434-8b8a-4336-8299-5862cd01c819 | signoff | AUTHORITY HOLDPOINT
00bd3c5e-38e6-4976-b110-d78e5bf2aa04 | checkpoint | 1.3 - Paving Plan
f9081f0c-8c51-5481-9c5a-d4ace4039a99 | note | Detail of Activity / Test - Paving Plan to be completed
d4b14270-6c00-505f-9d5b-ccae919ae6db | note | Action (Hold, Monitor, Witness) - H
94abe736-847e-52b0-9d06-81c02e1e59c5 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
80c1cf8a-abb1-51fd-a7de-b7aa7574c0c9 | note | Inspection / Test method - NZTA M10: 2020 Clause 9.5.1
3a32de11-5a99-52eb-8051-0548fa8962b5 | note | Acceptance Criteria - Paving Plan to be completed for each shift with dimensions, location and type of (hot/cold) joints, areas and tonneages
ba63487f-f5d0-509d-b345-a5057155ba9d | note | Record documents (QCP - Quality Control Portal) - String Sheet
47571ce7-da52-5d7a-ad64-64f15980a474 | note | Responsibility - Paving Contractor
09608251-3db3-5c95-b3ad-61e873f6fc1d | note | Eng. Rep / NZTA - I
5fa3c4fa-87cc-57e9-964b-0ac63d52a71e | note | Contractor - R
71ba4805-736a-4913-8bfe-9ee507b86908 | signoff | AUTHORITY HOLDPOINT
264346a9-cf1c-4bbc-ba95-ce9e65585372 | section | 2.0. MANUFACTURE OF ASPHALT
669a5c04-e4ce-4827-8eb1-cb62babd8071 | checkpoint | 2.1 - Temperatures
6c7ff2bf-bb4c-5520-9384-35163cf1fc5d | note | Detail of Activity / Test - Mixing of aggregates and bitumen
3501dcca-f7b2-56d6-9ce0-08a35e2a5844 | note | Action (Hold, Monitor, Witness) - M
59a03ee0-aa8f-5811-9593-4c354f031f1e | note | Minimum Test Frequency (Lot = 1 day’s production) - Constant monitoring of temperature by calibrated euipment
cd1c3659-2b9e-59a9-9d35-d0ab1dfc4fe2 | note | Inspection / Test method - Plant temperature probes
ca80feeb-5e39-5c61-9607-60fe877b3caa | note | Acceptance Criteria - PG64H binder Mixing range 160 - 170°C
5304e0cf-4fbd-5e74-854b-7abc5232d9a6 | note | ○ PG64 V/E (Flexiplus Bind) binder mixing range: 170 to 190 deg.C
5d7ca439-18e4-57dc-af12-cc47856824d0 | note | ○ NZTA M10: 2020 states max. 185 deg.C
7dfebbf5-1fec-53a9-a9d2-b2bc6ae21dea | note | Record documents (QCP - Quality Control Portal) - Plant site diary
1cc058bb-4272-53b2-93cb-f940adccb83c | note | Responsibility - Asphalt Manufacturer
e6fc23ad-be64-589e-84d4-13ce5b468f86 | note | Designer - I
97fbf089-56cd-5f0e-8440-70abaa2baf58 | note | Eng. Rep / NZTA - I
e7823e99-27f3-5ba8-9787-a12fb9715dce | note | Contractor - R
37bb0000-123f-45ec-acec-63ee0726d4a7 | checkpoint | 2.2 - Production Asphalt
25e15fba-ca9f-5beb-b5cb-62e2260ac278 | note | Detail of Activity / Test - Particle Size Distribution
abdd93a9-6f46-56e3-b6a8-1b27b87eba6b | note | Action (Hold, Monitor, Witness) - M
93f61b36-d021-5ac7-a14b-09e93e28a305 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
ccc7357f-fe4e-5a75-bfc6-d06afe4416a7 | note | Inspection / Test method - NZS 4407 Test 3.8.1
9a3f087a-bfcd-5026-a90b-eadda6ef44c3 | note | Acceptance Criteria - NZTA M10: 2020 Refer to Table 5.3
f6a1c40e-d37a-5112-a876-c1669ea99fc7 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
f004e2f6-9dd6-5a42-8ed2-c8ae2b968bda | note | Responsibility - Asphalt Manufacturer
25ab9258-64e1-5e80-92ef-dd27034f4c42 | note | Designer - I
73cec4e0-b7fe-5506-a9fd-c88056e6e3c7 | note | Eng. Rep / NZTA - I
c75a5863-37dc-5232-a94e-7e0fddc5ff40 | note | Contractor - R
88a3319c-c7e0-41ed-bf71-cf3647af8418 | checkpoint | 2.3 - Production Asphalt
49a8602d-73e2-56fd-8920-9aceb45afdd7 | note | Detail of Activity / Test - Binder Content
69d7368d-92a7-5721-8fd0-ffed8c942d58 | note | Action (Hold, Monitor, Witness) - M
531a67df-88a3-54d1-a097-29f862634eb1 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
f9c3be7e-6dda-50da-b321-d008daec2de5 | note | Acceptance Criteria - NZTA M10: 2020
c060568e-8a6a-5813-be40-140e203126e4 | note | ○ Individual Test Result: ± 0.5
8a454878-0feb-5378-891f-8a35608e4414 | note | ○ Mean of Three Test Results: ± 0.3
8f81fad0-a95f-508d-a490-313adaf3f5aa | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
917cad62-97c3-51be-aeff-0625265024ee | note | Responsibility - Asphalt Manufacturer
4f0d441d-dc42-59a4-8590-9b7f3a60a31c | note | Designer - I
02568ea3-cd3f-572c-8914-90f489945903 | note | Eng. Rep / NZTA - I
e5a9c013-c7bb-5a8e-8d0e-01c9f81ac76b | note | Contractor - R
0f41190b-c71a-4f3d-8913-a7988c890d07 | checkpoint | 2.4 - Production Asphalt
58e3a90c-9154-569e-a546-28ba0d1be447 | note | Detail of Activity / Test - Max. Specific Gravity (MSG) of mix
3af7d235-4304-55a3-95a1-b7e60eb7b525 | note | Action (Hold, Monitor, Witness) - M
bda28791-2d7d-5124-ba76-a72ae33a41b5 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
4889f72b-a128-5ced-bdf9-100999f3a950 | note | Acceptance Criteria - Report
226e1468-189a-5cdb-a8b3-0d5010c0da02 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
78965120-9cef-5d6b-acf7-2a9f1cd2f878 | note | Responsibility - Asphalt Manufacturer
edbd5a7d-6ff9-5bb6-8e96-ad4e078a0357 | note | Designer - I
ab9fc0ed-8734-512f-97fa-44ad0987b570 | note | Eng. Rep / NZTA - I
9bb7c001-60fb-5e90-a0bd-a4e84fa282d9 | note | Contractor - R
36dfd0be-b776-435c-8f50-1f78d9bbc515 | checkpoint | 2.5 - Production Asphalt
af404a35-7127-5f10-aa8f-27f994e814b8 | note | Detail of Activity / Test - Air Voids at lab design compaction
c3ed2a86-f015-5536-9f46-6935a2454b86 | note | Action (Hold, Monitor, Witness) - M
d151db07-a818-5913-9537-1b734d0da6f9 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
b047d60c-ed2b-553c-9faf-a61524755dce | note | Acceptance Criteria - NZTA M10: 2020:
427b7180-cfe5-5ef3-a2ec-b27817645f8f | note | ○ Individual Test Results: +2.0, -1.0
c3a49040-5fbb-53cb-b5f2-f31e673935a0 | note | ○ Mean of Three Test Results: +1.2, -0.6
d8d13f2e-6ac5-5d12-ace8-a87fbe276abd | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
b88ea260-4473-511d-93a8-768e0da2e6b2 | note | Responsibility - Asphalt Manufacturer
c3389442-1be4-55a3-8dc6-01ae66927406 | note | Designer - I
28187933-aa43-567c-9d96-92b0f03aeb86 | note | Eng. Rep / NZTA - I
edcd6742-39de-52c5-b292-d257b7cbfa67 | note | Contractor - R
b68a03ad-abd5-4c2e-b2e4-dbd8c634b944 | section | 3.0. PLACING AND FINISHING
6e5f122b-135e-473f-b0fa-8a02efe5a981 | checkpoint | 3.2 - Tack Coat, OR
b7a430a7-9f02-521a-ab85-129aee2779d2 | note | Detail of Activity / Test - Application of Tack Coat
969319be-7b4c-5d43-a17f-27ca21c79711 | note | Action (Hold, Monitor, Witness) - M
8b37cecc-3380-5140-80e2-6ad42c09409d | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
9471d730-4d3b-5ad7-9ddc-7f43218f6df8 | note | Inspection / Test method - Dip bitumen emulsion tank before and after
c432fdd3-0759-561b-92b0-62533e3ffdf9 | note | Acceptance Criteria - Target Between 0.2l/m2 - 0.6l/m2 +/- 0.1l/m2 From Target Application Rate
b35ff0ff-42ab-5fea-8485-ca0f298526ff | note | Record documents (QCP - Quality Control Portal) - Site Diary
23704766-4c93-52c7-81c1-cc985ead8cf4 | note | Responsibility - Paving Contractor
8ab45bd9-d344-532d-9c69-af1869f62aeb | note | Designer - I
f234a238-74d1-5d2f-9f40-6ebed953e207 | note | Eng. Rep / NZTA - I
b31bd257-df42-5474-8cee-62b0cd77b1bf | note | Contractor - R
3f83ca8f-87a4-4f35-9dd7-58d562a81ccf | checkpoint | 3.3 - Membrane Seal
ace1f7b0-6986-53a3-91a2-63975c28a392 | note | Detail of Activity / Test - Application of Membrane Seal
760538af-6a37-57ab-b632-3c3869caeca3 | note | Action (Hold, Monitor, Witness) - M
2d70d989-0c9f-56be-a388-6a20a3db0b52 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
d842619c-b42c-577f-988b-c20009f90b51 | note | Inspection / Test method - Sealing Records
8ea676bd-7388-5d50-9435-faf711d85edc | note | Acceptance Criteria - Application rate, chip type and binder as per membrane seal design
fea20670-be9b-5258-ad5f-0df9176f2dc6 | note | Record documents (QCP - Quality Control Portal) - Sealing Records
87fb01bf-5433-5b17-b4d7-4a5f8f996154 | note | Responsibility - Paving Contractor
e294780b-2560-5b90-8fd8-f2db338fcc2a | note | Designer - I
ea34097a-23ee-5d30-882c-8bde520d133f | note | Eng. Rep / NZTA - I
b6f7d70f-94bc-5c3c-97eb-907d8ddf571a | note | Contractor - R
44b0e4e7-1417-4be0-a8e5-9eef4582d5c2 | checkpoint | 3.4 - Temperature
3a536085-79aa-5c6c-b32f-077d9e5cd890 | note | Detail of Activity / Test - Pavement Surface
b9ca07a6-3fe2-51fd-afa1-1bdab4a0967e | note | Action (Hold, Monitor, Witness) - M
0c801be6-274c-59eb-afdf-1dd8886d48dc | note | Minimum Test Frequency (Lot = 1 day’s production) - Start of shift and every 1 hour until temperature rising
b1728f85-b4e5-5790-8ab6-13d5917c3db3 | note | Inspection / Test method - Infrared gauge
04ceebe4-79db-5455-902d-809d1132255c | note | Acceptance Criteria - ≥ 10 °C for Wearing Course, ≥ 5°C for Structural, or as otherwise agreed with NZTA
823bcf63-30b4-5d19-8d87-89f4c7309eb4 | note | Record documents (QCP - Quality Control Portal) - Site diary
3534c086-b18c-5132-9129-d762eea0acd3 | note | Responsibility - Paving Contractor
fcd1014b-f3ab-5ece-9806-5852d5288796 | note | Project Specific Notes / Instructions - Must get NZTA approval if < 10°C for Wearing Course, or < 5°C for Structural
3a2a9b25-be76-5220-9969-51bf46eedb28 | note | Designer - I
0b6611ff-bd6a-53f2-b2d1-764cf776063d | note | Eng. Rep / NZTA - I
99e32150-1313-5261-a2a8-4d4a9bd33b3a | note | Contractor - R
85246f97-34b3-499c-9b07-f7317726230a | checkpoint | 3.5 - Temperature
5ee4f645-b3dd-5005-8148-10be8403bf0a | note | Detail of Activity / Test - Asphalt Delivery temperature
94e331b4-dba0-51b7-9768-5eb343a881ae | note | Action (Hold, Monitor, Witness) - M
cc286abd-d751-5928-a319-6d5c0c54f93c | note | Minimum Test Frequency (Lot = 1 day’s production) - Every Load on delivery to the Paver Hopper
291a1d22-8eb6-5a6f-9167-f7b3afc16f92 | note | Inspection / Test method - Temperature Probe
82a76f03-a94d-5cd2-bebb-98cf1769cb79 | note | Acceptance Criteria - Target ≥ 150 deg.C. in the Paver
18d6fd4a-6dcb-5989-8d97-bf8bdac9c720 | note | ○ Min. ≥ 130 deg.C in the Paver
fa5f772f-d24a-50ff-9b49-2dedfba99b94 | note | ○ <130°C to be Rejected
66af436c-e51c-51a2-aae8-78138f85d53a | note | Record documents (QCP - Quality Control Portal) - Site Diary
6f0ba38a-92ad-53c7-bbc5-b1ea5b0a2517 | note | Responsibility - Paving Contractor
fd2d2b61-87c9-5479-a9f7-b62f70ffa634 | note | Designer - I
d046b9bd-992f-5005-9e7a-a337fc421144 | note | Eng. Rep / NZTA - I
f53d2ada-1d20-58f1-bede-2c60e49433e0 | note | Contractor - R
c62ba254-6e9d-426e-8d35-64e6c55083a0 | checkpoint | 3.6 - Temperature
ce71e964-2043-5615-b9f2-a98df3bfa6b6 | note | Detail of Activity / Test - Compaction Temperature
f7d07e2f-a739-5f1b-9956-bdfdc396f046 | note | Action (Hold, Monitor, Witness) - M
bc999700-9718-5a6a-81f9-9105f8871be5 | note | Minimum Test Frequency (Lot = 1 day’s production) - During compaction
33caf021-fd96-55a4-ab25-be930c7c04cb | note | Inspection / Test method - Temperature Probe/Infrared gauge
dad8fe52-b5fc-5a5c-b059-336033790d33 | note | Acceptance Criteria - ≥ 125°C at commencement of compaction.
247caff1-c462-5f04-ab1c-ad06e2e29e77 | note | ○ < 80°C - Stop Rolling
0ce1ecdf-0b8f-5e2a-8635-bfb87074a773 | note | Record documents (QCP - Quality Control Portal) - Site diary
5d01a7c3-53b0-598e-a206-9eb0967ec6c8 | note | Responsibility - Paving Contractor
d121dcb8-c537-5b6d-a8e2-5605bd9cda14 | note | Designer - I
40413cb0-7e36-5df0-8574-26fba215f59d | note | Eng. Rep / NZTA - I
cb3d6e48-12de-55cb-9e1d-086dc691410f | note | Contractor - R
e63677b2-ac3a-4818-8d72-9a90ce0441d5 | checkpoint | 3.14 - Paving Quality
b8ddcd08-decb-51c6-a7a7-9d174a34ec56 | note | Detail of Activity / Test - Level
44ec3daf-1773-553b-8581-8b70de767442 | note | Action (Hold, Monitor, Witness) - M
9f3c1043-ba72-5a9f-a719-4026ac6dad0e | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site (If Required)
2b8f5e55-c8ee-5298-8e5b-fa094f3e50eb | note | Inspection / Test method - As Built Survey
8ac7258c-99a7-5a54-8165-76c89eb5abe4 | note | Acceptance Criteria - -0 < +5mm from Specified Level
6e919591-8f40-52a2-8f69-4fcacab13dd9 | note | ○ Where there is Kerb and Channel shall be flush with or no more than 5mm above the LOC.
2c2e93be-3900-5993-a7e0-c1e60c179a7f | note | ○ NZTA M/10: 2020 - section 10.2
fe93cfc3-d775-55b3-933a-fa5a0693fbb0 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
896c97bf-e2b5-55e6-9c57-1df61e64be73 | note | Responsibility - Paving Contractor
deace12f-8b66-5783-b555-420c86bf4676 | note | Designer - I
ddd52714-c658-5bcd-8c27-d4a6078f218f | note | Eng. Rep / NZTA - I
d629136a-743a-5804-9d0c-389e2abbd283 | note | Contractor - R
371cc436-2b42-49ec-a87f-9620c796c0ae | checkpoint | 3.15 - Paving Quality
7bbb0e40-bc16-5ba3-a7a3-614c26f71c7b | note | Detail of Activity / Test - Alignment
46d9d90c-ab3b-5eb4-80da-82f3b1ad28fc | note | Action (Hold, Monitor, Witness) - M
e942295a-93e5-5beb-8ac8-03a136b6320a | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site (If Required)
85e27116-47fe-5c63-bfef-fad17adde7f2 | note | Inspection / Test method - As Built Survey
5405fd50-1028-54e8-aa5c-b1664c879277 | note | Acceptance Criteria - ±50 mm from drawings
ba2b5f74-8d2b-5749-8dbf-312f02f14c27 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
f52250ce-f726-5a6a-9320-a432423677cc | note | Responsibility - Paving Contractor
61d005dc-850c-522f-ade0-7275aea318a2 | note | Designer - I
d0f02577-83df-5046-8c77-ea823bdb16cd | note | Eng. Rep / NZTA - I
93f27d58-04c1-541d-9fd0-bd41042363a8 | note | Contractor - R
805e8e1d-e9fb-4af9-882d-4c87b17edbc4 | section | 4.0. As Built Records
fe48a696-003d-4f66-a51e-bcd3d063abe8 | checkpoint | 4.1 - Assessment of all test results for conformity
893a1f49-9417-5cb0-b752-1e8f7efed98a | note | Detail of Activity / Test - Review against ITP Requirements
fe99537a-80b6-5d9e-8151-0e03b5c82bae | note | Action (Hold, Monitor, Witness) - H
e3a37438-8999-5452-9782-49b2a73fc26f | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
c527814f-79d1-514c-968c-dc6507783f5f | note | Inspection / Test method - Review
ec22d32f-754f-5c82-b1db-499791a722ad | note | Acceptance Criteria - Reporting of any non-conforming results to Engineer via NCR
9e926e94-4621-5f1e-bd43-aadbbbe5c538 | note | Record documents (QCP - Quality Control Portal) - NCR
cbc83aa3-bb00-5ecd-80d7-cb43cb2825b2 | note | Responsibility - Paving Contractor
ec0557b1-0d17-5d7f-ae95-d124e8dbf4f7 | note | Designer - I
18d4b632-e71c-51a8-9d6c-b4f4d43cbeed | note | Eng. Rep / NZTA - A
166a08ba-b708-5ad5-9968-dfbcfd21d810 | note | Contractor - R
e07b615f-93da-49d5-9ae3-4100f9099ceb | signoff | AUTHORITY HOLDPOINT
461aff98-05e6-4bc1-b595-80a146c79a48 | checkpoint | 4.2 - RAMM pavement and surface records
06c33aae-e12a-5a2c-a9aa-23b385751b5c | note | Detail of Activity / Test - RAMM surfacing pavement data spreadsheet updated
17d49d05-47cd-5240-b91f-503a417d4ffa | note | Action (Hold, Monitor, Witness) - W
e84c3c06-395d-594a-a6ac-cbe961803f6c | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
d88275af-af1a-5f85-8137-5c63c5e1819c | note | Inspection / Test method - Prepare Data
fc256ead-2b23-5e05-a214-d124ed844dfc | note | Acceptance Criteria - Over milled and Deep lift extents recorded and verified by Contract Engineer / QA
e9de92b1-38e3-5cf2-95dd-8bda7562c10a | note | ○ Spray sheets for membrane area received by Contract Engineer from Sealing Team.
19b2f7fa-1d23-56a2-925c-3c7658cd778a | note | ○ Surfacing layer extents recorded and verified by Contract Engineer.
e22fad4f-21fd-548d-9e64-0f17ca3d7ef1 | note | Record documents (QCP - Quality Control Portal) - RAMM Spreadsheet
69a65eb4-9b70-5043-858b-2218a9b992e4 | note | Responsibility - Paving Contractor
550a8be1-4996-5075-b9e8-3c4795db880d | note | Designer - I
1bed86f8-2b18-58f8-8fc7-bfe25712b107 | note | Eng. Rep / NZTA - A
629527c7-0b85-516a-a6c5-bb32a1d04a4d | note | Contractor - R
01f56a76-4cf5-4fa3-bde5-9beffb5d2381 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
9ef06f00-f16e-51f0-bb4d-2d13d0916972 | textbox | Contractor's Rep Name:
41e99f01-c2c6-54f3-8c15-4a46b86ce0ca | textbox | Engineer's Rep. Name:
5f482805-96e6-56f0-91b8-4db81f14b9cc | date | Date:
49975218-20b5-45b0-b967-9162543c0d05 | signoff | Add Signature
8693f360-eada-47f3-9a1d-f3381cf3ace3 | checklist | DN1210-016 ITP Fencing Rev 1 | itp | DN1210-016 ITP Fencing Rev 1
9dbf9507-d5c1-5f76-b0e9-632a875b7d7c | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
61faafb8-e067-5299-84f0-3fd60960e68e | checkpoint | 1.1.1 - Extent of Line Setout
2d49439a-3db5-5e85-9b0b-ca24f4b79ac2 | note | Detail - Ensure line and level of Fences has been marked out and agreed with Engineer in accordance with fence drawings.
29900d8c-108b-5bcb-ba90-3d2400fb1787 | note | Acceptance / Conformance Criteria - Engineers Approval
06e46e56-df76-5bec-90a5-c8ab5053aedd | note | Standard / Specification - Design Drawings
6e8489e2-fb2d-58f0-bf97-b57361fa463e | note | Verifying Document - ITP Sign Off
c1e300dc-eedd-5142-9f9a-1031ebfcf3b6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
9867705c-34a8-5fa4-ac89-8b325319a281 | note | Verification Activity: Activity - M
2597987d-ecc6-5af2-a423-671d0723a0f9 | note | Verification Activity: By - ENG
e9e8c2cd-2e34-5f02-8879-699288a9aa24 | checkpoint | 1.1.2 - Existing Fences system
f32c2d60-9006-5930-9f6b-c2059a7b2aec | note | Detail - Confirmation of existing Fence network.
8e482f4a-68fc-5545-8c52-941d9c8393af | note | Acceptance / Conformance Criteria - Survey Information's
15423d91-33c1-5772-b194-ca935acfe13d | note | Standard / Specification - Appendix V
a22b1324-349d-5388-b8f2-7cd6deed0be7 | note | Verifying Document - Survey data
06f131f8-2b9c-517c-8bf1-a86163db0679 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
2c553a08-9c29-57a0-b028-7b823682dc6c | note | Verification Activity: Activity - HP
455af034-9038-5f48-af09-f4980792f812 | note | Verification Activity: By - ENG
a071cef9-3b84-5a44-b239-8ada30897af8 | signoff | AUTHORITY HOLDPOINT
b2505ca3-943c-534d-afb7-23e310ef1e65 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
5032c6c8-1674-507b-9e9e-9ec0d09378eb | checkpoint | 2.1.1 - Timber (Rails/palings/battens) Posts
a81013da-d335-5038-9c3a-bf1ada791a78 | note | Detail - Treatment
c29adedd-6d0a-5c3c-af84-2548b36de425 | note | Acceptance / Conformance Criteria - H4
641c8d13-92c6-5734-a9f9-7a827bc2e863 | note | ○ H5 if touching ground otherwise H4
a8116ba3-05fb-5a11-a829-3fc17a982a24 | note | Standard / Specification - PS 27.5.5, NZS3607:1989
dc71efa7-cd41-5d29-a76d-db43d735b4d7 | note | Verifying Document - Delivery docket
d54ebcd7-a415-52f4-bb63-b53fb1780186 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
6dea0fbd-834c-5396-b585-29f6c8f5d8ef | note | Verification Activity: Activity - M
2cadf66d-84f1-567f-8b9d-b6ad000b32e5 | note | Verification Activity: By - SE
ff5686ac-35c4-536d-8305-ab342ed5957e | checkpoint | 2.1.2 - Steel (Wire/Metal fence)
471c13c3-334c-56e2-8a0b-e96c7e97c797 | note | Detail - Standard galvanised high tensile steel wire
75e50762-15d6-5b4a-9e79-d2ada755fd73 | note | Acceptance / Conformance Criteria - 2.4mm 12 gauge
6106274f-2944-5117-b75f-6a67e37f4337 | note | Standard / Specification - PS 27.5.1, PS 22.5.6
18e4522f-9002-5550-a9f3-e815c15dabdf | note | Verifying Document - Delivery Docket
55eefcb1-cdb8-56ea-b5ca-83b50390d83a | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
6da8dfdd-3e94-51cf-aa9a-d50d3657a29f | note | Verification Activity: Activity - M
1e6d896a-d77b-50fe-b701-9fa92a840bfc | note | Verification Activity: By - SE
489029af-ef0a-5f3a-b8fe-c98f2f8d59cc | checkpoint | 2.1.3 - Chain Link Net
fb315c75-5831-5ae8-838a-9490cc84d931 | note | Detail - Standard galvanised high tensile steel wire
75edb50b-7a66-5053-b343-dd5aaa97a314 | note | Acceptance / Conformance Criteria - 50*50 Max grid size
cb612150-a942-5284-9355-afa86e7fd150 | note | ○ Powder coated black finish
05b033fb-a4e9-593a-972f-af3ab8aeda25 | note | Standard / Specification - PS 14.6.1
b4ef8562-d5f3-5c66-94d7-614093dae351 | note | Verifying Document - Delivery Docket
dc0041d3-2301-51ce-bc4f-c9f15e7f8fb2 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
4e760af3-a526-5d2c-80d1-e5eb00863b05 | note | Verification Activity: Activity - M
8d4e7b06-7ee1-5d0f-95b9-b572a860eb13 | note | Verification Activity: By - SE
591f8625-e14e-5db2-9fa4-b5d19a067cc5 | checkpoint | 2.1.4 - Material (Fixings/fasteners/hinges/chains)
28e911e2-5198-5b13-a9be-af191a00da8e | note | Detail - Jointing
822cc2ce-04e1-5a67-b3e5-2148ab5ae88d | note | Acceptance / Conformance Criteria - Hot dip galvanised
01f9a961-8407-559f-a4b0-288c00dca841 | note | Standard / Specification - PS 27.5.1
f639d918-6f43-5577-84ff-6b2799ba0d07 | note | Verifying Document - Delivery Docket
3d59af60-6986-50ea-811a-cda0111e73f6 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
7806c0f5-e56b-58dc-93cc-ac50fd55c2ed | note | Verification Activity: Activity - M
e2935100-6616-5c08-9fbe-19fcfe7e7cca | note | Verification Activity: By - SE
9cc06a11-17ee-5f49-ac50-31c36fc22fcb | section | SECTION 3 – CONSTRUCTION ACTIVITY
4f3a473f-e466-5291-a795-4d0c92b1a2b3 | checkpoint | 3.1.1 - Wetlands Fence
f866857b-ce13-59f6-8fca-ccf773564bd7 | note | Detail - Install around the wetland
16be6173-c6ec-598a-80a0-bc506f5d4028 | note | ○ Black powder coated finish
02f97957-1b4c-5ba0-913e-2c6a46c4d6a9 | note | Acceptance / Conformance Criteria - 1.5M high
7878d232-a1da-53e7-8b56-551687b16305 | note | ○ Hot dip Galvanised
49455d3b-ce8d-5a0b-bb1d-4ee2f0059392 | note | Standard / Specification - PS 2-32735.02-WSP-DR-UDL-0407, PS 27.5.1, PS 27.5.2
b3e15b83-25bd-53c8-8724-0afc06f86748 | note | Verifying Document - Delivery docket
db100ae5-c88c-5953-bdac-afd6169ee08f | note | Testing Quantity Required (based from schedule qtys) - During installation
b54fff12-3021-50a1-a528-9d5e4e6811d0 | note | Verification Activity: Activity - M
8b1cfc15-3b30-5ee6-a294-a4d0f16103c9 | note | Verification Activity: By - SE
42ecb55c-639f-5bdc-a60c-8778e8f586be | checkpoint | 3.2.1 - Timber fence
d4316e81-867b-58ab-9596-b44287b1f3cf | note | Detail - Preserve timber exposed faces
5d5e9a2d-6a4d-58bc-9093-8643504d18fd | note | ○ Post imbedded in ground
8e9338f9-e7a9-5b7d-9ca3-3aa80ff61f31 | note | Acceptance / Conformance Criteria - 1.8m high
9508edf4-88d7-55ba-9ac8-e6968cf7b96b | note | ○ Exposed timber faces neatly protected with 2 coats of timber preservative (Metalex)
9623e987-c6f2-5d55-81fc-5622cb550839 | note | ○ 1800mm in ground with 17.5MPa concrete
4e0aa3d2-8b75-5ddd-8631-9598808c35b4 | note | ○ Minimum 100mm extend around the post
a685488e-d7f7-514d-942c-d745412a8f69 | note | Standard / Specification - PS 27.5.5
f6d7f996-c09b-5457-82a7-f73078527bb4 | note | Verifying Document - Delivery docket
7faebad8-8d34-5361-b428-2cbb50372b40 | note | Testing Quantity Required (based from schedule qtys) - During installation
4cc86542-9a5b-5660-882a-2b059e971f0b | note | Verification Activity: Activity - M
26b50076-ae91-5c35-8a91-c9991469d4f5 | note | Verification Activity: By - SE
0925a98a-cb05-53ed-bbcf-af284fac16fe | checkpoint | 3.3.1 - Post and Wire Farm Fence
a99eecce-1bd6-5757-ab09-4a0d680142a2 | note | Detail - 8 Steel wire
7db0eb80-7ddd-573a-9253-9f0367c508c9 | note | ○ Timber post located at max 5m centre and securely rammed
94b5ab92-09fd-549a-bbef-470b80a3ded6 | note | ○ Battens affixed to wire and timber evenly spaces
468bcdd9-c010-5727-bb03-23297570b593 | note | Acceptance / Conformance Criteria - Wire and ground distance < 125mm
a81f057d-2c0a-5b49-913d-da98849be607 | note | ○ Top wire to > 1m from ground
a6e655e0-1d7a-5e59-bdce-49e96ca95c86 | note | ○ Top of post > 50mm top wire
4fe274a8-f56a-5649-9772-9f3c0ea9eca6 | note | ○ Wires not attached on road side
79fcb05f-b14c-593e-9310-936c029d8ec0 | note | ○ First 3 wire separation 125mm
3819f83b-c1d0-5a7b-93fa-b09ec9bce062 | note | ○ Min 3 battens between posts
042662cf-7c8a-5cba-9f10-e32e166877c2 | note | Standard / Specification - PS- 27.5.6, NZS 2566
3418000d-3d38-57bb-9402-e322950b9a0a | note | Verifying Document - Visual inspection
ef05d5b9-bd63-5ba9-97f5-67cb63132ce0 | note | Testing Quantity Required (based from schedule qtys) - During Construction
cb8ceb04-16f5-57d6-9011-32b47bb8254a | note | Verification Activity: Activity - M
750bf047-2bb0-5ba5-b919-f85ad174c439 | note | Verification Activity: By - SE
94bb45d6-7c4a-5d34-9c38-ef50db464e25 | checkpoint | 3.3.2 - Strainer Posts
5eaa510d-3abf-564d-91e0-0687d7761430 | note | Detail - At new and existing fence terminations
51b392b8-abab-5567-87a5-77726bb2042c | note | ○ At each corner distance between corner and/or termination strainer exceeds 200m
d6c56c89-dfe6-5340-8dba-2e813b7fd5f7 | note | Acceptance / Conformance Criteria - Double footing and tight wire secured to the post using 4mm wire
b0a26b89-41ad-5167-af76-f10b58d3241c | note | Standard / Specification - PS 22.5.6.b
6ddd964e-1636-56b0-96f6-13d333cc1fd6 | note | Verifying Document - Visual inspection
5bf4e9fe-de84-5ef6-b6e3-19665fa1c039 | note | Testing Quantity Required (based from schedule qtys) - During Construction
9fd2937e-3755-58d7-ac9e-22f0494e473d | note | Verification Activity: Activity - M
d0bf2e5e-cac4-54d8-a3ed-5919040b7a75 | note | Verification Activity: By - SE
4067999f-5728-5587-8d89-7544a2a9c8b2 | checkpoint | 3.4.1 - Chain Link fence
49ccd8f6-152c-5be0-86c8-0816a13e7e1b | note | Detail - As per drawings
cf7d3ade-8d42-5a14-a50f-070e5a74f692 | note | ○ Headwall and Wingwall fencing
bb2211d5-3200-58fd-ab7a-1eb31f32ef4a | note | ○ Secured with posts and top rails
08ca82e7-f3c2-5580-985a-2e7f1364c65b | note | ○ Spacing between two post must be equal
66f2a5bf-d6be-5cb9-9bbd-d73b88e04d37 | note | Acceptance / Conformance Criteria - Tie wire on every second diamond
742f6d38-b923-5d12-b795-864bced588b5 | note | ○ Spacing < 2400mm
eb901cff-cee9-5f5c-97bd-5755a3be111b | note | Standard / Specification - PS 2-32735.02-WSP-DR-UDL-0407
cfbb4d20-0a62-51e2-83f7-f7e6f4f19055 | note | Verifying Document - Visual inspection
016b0d32-bd62-5a8b-8694-80f46c88f8c5 | note | Testing Quantity Required (based from schedule qtys) - During Construction
929a7432-3580-52b6-949b-87077a10bcf3 | note | Verification Activity: Activity - M
359818d8-98d8-5a2b-8d59-d3bb6f1a10b4 | note | Verification Activity: By - SE
801f7ada-618c-5ced-9ef5-1d9f7eae2d38 | section | SECTION 4 – HANDOVER
13049da8-dc5f-50e6-9653-61f13f53ec94 | checkpoint | 4.1.1 - Survey As-Builts
80835152-ec3b-5e5a-b659-35b7e243d274 | note | Detail - Quality Check on New Works based on the tolerances in RITS
6137f7ba-ad1a-5fce-8331-3e570fa5c5e8 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
5afaec36-5ff3-5d6c-8432-40d0ad8dea64 | note | Standard / Specification - PS-21.7.7
a9994d3c-d6bb-548a-a6b8-094cae2a1a95 | note | Verifying Document - Red pen markup only
02da7ac2-5c09-551f-b3e2-139dc087d778 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
44d84a42-1183-5ed1-aa30-431c32e958db | note | Verification Activity: Activity - H
9dd801c2-36c1-54bb-89d4-b13fc7e94d3a | note | Verification Activity: By - ENG/PE
9a1e2b98-f0f3-450f-8a5c-ba9bb3e1c1ba | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
8b5e7450-04e4-5aa3-bcc3-3784c4ee089a | textbox | Contractor's Rep Name:
70d8edb1-97bf-5c80-909b-6d716e3b5c77 | textbox | Engineer's Rep. Name:
1ab2ebb3-2c35-5f8a-bf3b-b6cfd57b39c2 | date | Date:
290d4bbd-090a-435c-b416-27d5ccad8496 | signoff | Add Signature
eb19ebab-a67d-4523-bf89-97e3bf27fc15 | checklist | DN1210-017 ITP Watermain Open Cut Rev 1 | itp | DN1210-017 ITP Watermain Open Cut
ea0170e1-4a69-48df-b393-8113b10f5a54 | section | SECTION 3 – PRE-CONSTRUCTION - P&G and ESTABLISHMENT
bcb18e91-dc12-48c9-9dbc-e7bcf7be05f4 | checkpoint | 3.1.1 - Pipe Laying
14e1b5d8-f64e-54ea-9bdc-dde1b63da1ae | note | Detail - Method Statement
6c0e6a46-295a-52a5-b5a0-6eae897980d0 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
25111f42-7f11-5111-9b66-f0b013cea86b | note | Standard / Specification - Appendix V
3e7c573c-8c7b-57f3-a523-e0aab92f1e0d | note | Verifying Document - Watermain Construction Work Pack- Open Cut Sign off
8a2aca51-394a-5c9d-bafb-09e3044fe80d | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
32ff296c-819e-57df-ba84-a3ff571d3164 | note | Verification Activity: Activity - HP
d31113f9-dab0-5fd7-9f3c-921cae7f8049 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
361fc99c-9d56-5f1c-8fc4-54b703c37e7e | note | Verification Activity: By - ENG
3c5be89d-02fa-4091-8620-dad3023ef6fc | signoff | AUTHORITY HOLDPOINT
83c39a72-c776-4e79-b60a-0a49a9787c85 | checkpoint | 3.1.2 - Butt-Fusion Welding
832905c1-51c4-56e2-9822-487fcfe04b1b | note | Detail - Method Statement
77637523-b37f-5552-b5a1-262e244afd61 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
6c720125-1d65-5f77-98d9-732696fddb72 | note | Standard / Specification - PS- 22.9.4
558e0cbc-59e6-5c76-9014-e0790c810e20 | note | Verifying Document - Watermain Butt-Fusion Welding Work Pack Sign off
3b16fc7f-199b-5ac2-9574-df6f6e96f2ba | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
02ca6ac4-f0cd-53c5-b851-31fe2927e878 | note | Verification Activity: Activity - HP
885660b7-cdc4-531e-945d-b8e65d43e1f4 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4ffcd019-d862-5178-8daa-02148ee053e7 | note | Verification Activity: By - ENG
516263b9-5f69-4bc6-8c3f-d2a06f625cae | signoff | AUTHORITY HOLDPOINT
35ae20cb-0437-44c5-9721-d381bcf67a10 | checkpoint | 3.1.3 - Electrofusion (EF) Welding
a8121126-3a79-504d-b25c-0bf06cf8567e | note | Detail - Method Statement
7ad89809-36b2-54ac-aafe-ec3d0498ace9 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
e2b478df-8760-5ae8-a5d4-efb56f359c9f | note | Standard / Specification - PS- 22.9.5
4946de42-1470-581d-985d-279144263c52 | note | Verifying Document - Watermain Electrofusion (EF) Welding Work Pack Sign off
780a6741-74e8-5733-9fb6-adade36d92b6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
d6e18d1a-5040-5edd-b421-ca1ad3538495 | note | Verification Activity: Activity - HP
3b5beead-0dbd-500e-8fe3-f81054a83126 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7df96f83-b657-5243-b73d-091101be83d2 | note | Verification Activity: By - ENG
712cb0c0-c413-4f62-a3eb-338c6a3549cb | signoff | AUTHORITY HOLDPOINT
68ca9bba-3372-46ba-ae0d-89df95bee9bf | checkpoint | 3.1.4 - Pipeline Pressure Testing
40dd89aa-819d-5271-b988-91ca648e24e4 | note | Detail - Method Statement
63cf7761-9553-52ed-aaca-24a6ed0ac420 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
e57bf052-f1f8-58d3-8466-acb7ceeb7534 | note | Standard / Specification - Appendix V
dace2b05-0d21-5626-b1da-b414aaca1f92 | note | Verifying Document - Watermain Pipeline Pressure Testing Work Pack Sign off
63cede62-7539-5e77-8842-accfb4e00489 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
e984deb7-8fa2-5132-b064-dabd5d8bf911 | note | Verification Activity: Activity - HP
7a7224ac-c6ad-5c00-968d-b745ebec0bba | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
acb12ca0-7f03-50d2-9f24-63b3c26c03b6 | note | Verification Activity: By - ENG
c040acff-7322-404c-9a20-cc3179e1ca9c | signoff | AUTHORITY HOLDPOINT
5a5738cf-d21b-41d1-8185-614d29903f20 | checkpoint | 3.1.5 - Water Disinfection
bd24db9f-cf0c-5861-87d3-b34bbcf2ab5c | note | Detail - Method Statement
9df2bb28-145b-556a-a217-8936872eeafa | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
e1d10d6d-1377-5872-9e3c-9bc4d7cc129c | note | Standard / Specification - PS- 22.8
ef503595-2c01-59a7-b8ab-d9aa8a26662c | note | Verifying Document - Watermain Disinfection Work Pack Sign off
dc83c5cf-06bb-5ee4-a667-5eeca5083523 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
78b2032a-ca0e-57b0-844e-b0eae7c0f19f | note | Verification Activity: Activity - HP
c766c577-f292-5ea6-bf52-ca123695debe | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4d8243fb-7a48-5267-85dc-b9a2b7f1d3cb | note | Verification Activity: By - ENG
0c8eaa88-f4c0-4987-b1ee-6a6129a38a9a | signoff | AUTHORITY HOLDPOINT
4c2799e6-e132-4746-a5f4-f414c34d3f6c | checkpoint | 3.1.6 - Extent of Line Setout
222c2b2b-a7c1-5428-a122-36f7ab320108 | note | Detail - Ensure line and level of watermain RM has been marked out and agreed with Engineer in accordance with water RM drawings.
2346af77-0611-5054-9af5-23503ae9efbb | note | ○ Identify any clashes before construction.
72cfafc3-fef7-51a0-a1ea-da94b462b001 | note | ○ LOT- markup
c9e3fb2c-8e4c-5b29-ab22-8051da4c3551 | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
b3d57b23-1b78-5ef8-84b1-dd2a2f3459a0 | note | Standard / Specification - Design Drawings
21f59368-f5d4-5d1b-9a65-fb7fc9086836 | note | Verifying Document - ITP Sign Off / Mark-up
94af1018-d925-5d39-bbf8-9f79c07f1f1a | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
6c4146d1-48fd-585f-a878-869a1ec403f6 | note | Verification Activity: Activity - HP
a1ed9958-1fb7-5e00-ad39-d77342114f05 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a4feb9e3-f3da-5e01-957e-caeb4a8676fc | note | Verification Activity: By - ENG
18f54a1f-a35d-42bc-88ed-ade36d5c053a | signoff | AUTHORITY HOLDPOINT
4614cba6-858c-42f9-9e41-e0e1d2f67c3e | checkpoint | 3.1.7 - Existing Watermain system (If any)
cc3e69ff-00b0-50e7-9fa2-e7ceb2a81379 | note | Detail - Confirmation of existing Watermain network.
671b2060-da20-5e1e-aa65-8e0a79a67f38 | note | Acceptance / Conformance Criteria - Survey Informations
60cb3df7-c841-589c-ac79-2208233dac75 | note | Standard / Specification - Appendix XI
714da5d2-175a-5de3-9f4d-587a668e012d | note | Verifying Document - Survey data
ad446d43-ead5-583d-a562-ba17ef53cf98 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
4a3f932e-c4c0-50f4-b5f1-3feb7e0ad7ef | note | Verification Activity: Activity - HP
116d8c0f-4791-5aa0-9f38-8f7b9debb1a0 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
682302c5-a272-5ab7-bf8c-4014ddb6fedf | note | Verification Activity: By - ENG
47c1a13c-3fc3-46a3-8e5d-6cbee827a794 | signoff | AUTHORITY HOLDPOINT
778f18f1-0af0-449e-b5dc-340c7e32baeb | section | SECTION 4 – PRE-CONSTRUCTION - MATERIAL, PERSONEL & THIRD PARY APPROVALS
c1d141a1-7c14-4d8c-aadc-a2804077b515 | checkpoint | 4.1.1 - Material grading: Alternative: PSD,MDD Embedment Materials
2d29984e-92dc-5715-9b44-5e190e267b15 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone compliance.
680e24a3-513b-50b2-8148-2a935681a591 | note | Acceptance / Conformance Criteria - Engineer Approval
80af4089-ef59-5541-b1cb-9f71f572bc60 | note | Standard / Specification - PS 22.4.5, AS/NZS 2566.2
52064956-cafb-5387-aa09-18a6f2d13ef3 | note | Verifying Document - Lab Test Report NZS 4407 3.8.1
9b176457-516f-57c3-baf7-ed143c9d0f8a | note | Testing Quantity Required (based from schedule qtys) - 1 test
4fa06d9c-5985-5772-a928-50660fd78839 | note | ○ 1 Test for each additional 1000m3
b061a47f-db3e-576c-82df-18356d4edf78 | note | Verification Activity: Activity - HP
f30892b5-212c-516a-a49b-3ca554f34a08 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6fdf89cd-5863-5553-9fc0-b126561870d5 | note | Verification Activity: By - ENG
02b61066-4913-417f-99bb-043591795b70 | signoff | AUTHORITY HOLDPOINT
f1a78ac0-e5c7-468e-8f23-bd4ba7b38630 | checkpoint | 4.2.1 - Material Grading - Materials for Backfilling
a7cc68aa-3bbf-5a67-ab20-45f831fbab75 | note | Detail - Tranch Backfill Material: Particle Size Distribution
b5801c27-2c43-5ac4-9141-f96ba75a9c8c | note | Acceptance / Conformance Criteria - Engineer Approval
efc90f4a-ae76-5fc4-a3bf-0e497e487332 | note | Standard / Specification - PS 22.4.5 AS/NZS 2566.2
4eb27cc3-ea0a-5d00-af15-2207971bcea8 | note | Verifying Document - Lab Test Report NZS 4402 4.1.3
1c632057-6162-50b5-ab3f-e32e4594d892 | note | Testing Quantity Required (based from schedule qtys) - 1 test
cfa831a7-4abe-5410-943e-58c3e1def9f4 | note | ○ 1 Test for each additional 1000m3
ce1163ee-da6a-53a9-9b7b-bbbcad43f12f | note | Verification Activity: Activity - HP
46a7e237-d915-54f8-b6f1-09dfffe37fe6 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a60e4344-11a9-5521-b4f8-fee838eaeab9 | note | Verification Activity: By - ENG
b12a8304-a9c4-49f4-84ba-ca046d90a3a9 | signoff | AUTHORITY HOLDPOINT
f5734a7f-6836-40f9-8c3c-55ac01421292 | checkpoint | 4.2.2 - Material Maximum Dry Density
d52890c9-0589-5b5d-a735-3dcc88d536a6 | note | Detail - Trench Backfill Material: MDD
b3b00323-6ca2-52e5-b633-3b44e37c5d69 | note | Acceptance / Conformance Criteria - Engineer Approval
eda7a35a-9373-55ba-9ca4-0706f52ad586 | note | Standard / Specification - PS 22.4.5 NZS 4402:1986, Test 4.1.2
83bb36bc-e2d4-59cf-9395-7fb6fd72fbec | note | Verifying Document - Lab Test Report NZS 4402 4.1.2
f79f0132-4d14-5e3b-abf8-8427adb28fa6 | note | Testing Quantity Required (based from schedule qtys) - 1 test per Material, per Source
8bdd9db7-9f87-557a-96c5-666ba074d6fd | note | Verification Activity: Activity - HP
41f90a51-aa61-5b8e-a8a1-cdca32ea9a9a | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
cfd8c561-d93f-5fe9-b680-9343eac738c4 | note | Verification Activity: By - ENG
cd331ca9-395e-49ac-a65d-c92e2ac48a06 | signoff | AUTHORITY HOLDPOINT
4285f1fb-bc35-4cc5-8964-e5e65d2a751a | checkpoint | 4.2.3 - Weathering index: Materials ( GAP65)
69401313-0e33-5a73-98f8-ffc139abbce1 | note | Detail - Trench backfill material, WI
4c3cd4c3-8d3f-5582-af22-880d332a33ce | note | Acceptance / Conformance Criteria - Engineers Approval AA,AB,AC,BA or CA
aa252f3b-4955-5496-a8e4-4d735f735759 | note | Standard / Specification - PS-21.7.2
06644b39-4a8d-5bcf-b0f8-b5909285afcc | note | Verifying Document - Lab Test Report NZS 4407 3.11
e5b0dd7f-d75c-5672-b64c-ced510fd77a9 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
828667a1-8184-545b-bd70-a188fdb1dfc4 | note | Verification Activity: Activity - HP
6e0b5d0f-c232-5e65-af8b-3ae39f8490c8 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
02676435-0e0f-577b-b837-101a49e0524d | note | Verification Activity: By - ENG
ae8b6701-96eb-4d7e-9aa3-08535dd6eee9 | signoff | AUTHORITY HOLDPOINT
7208866a-1907-44bf-bd5e-7c705b7d3494 | checkpoint | 4.2.4 - Crushing Resistance: Materials (GAP65)
7a2e8f80-3977-5d69-ba65-2427799c9bdd | note | Detail - Trench backfill material, CR
7b499ef5-e1f0-5b46-8281-ee6c657a3802 | note | Acceptance / Conformance Criteria - Engineers Approval >100kN
9260ccca-51bc-5e5d-8528-6aa9a8e30c55 | note | Standard / Specification - PS-21.7.2
8ac45d55-fb16-5de3-9c15-1975153aa1df | note | Verifying Document - Lab Test Report NZS 4407 3.10
298c100a-e7f7-5d3c-aa55-601cac922c91 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
0e36cdc5-7ee8-520b-a225-f7133810acf6 | note | Verification Activity: Activity - HP
bf9d6a9b-bc1c-5d0e-bb10-a8051d4a670d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7cf2eeef-3eb5-5d03-b4e0-558df9075e83 | note | Verification Activity: By - ENG
3c690882-7c53-4e3f-989b-65fe267f426f | signoff | AUTHORITY HOLDPOINT
b6f5739c-ec16-4fb9-990d-14a160013505 | checkpoint | 4.2.5 - Geotextile/Geogrid
d8cb7be7-8c74-5c81-a7bc-614e70406565 | note | Detail - Minimum Strength Class C & Filter Class 1 or TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
e90caa4e-9011-516f-a25a-69b60ec79df4 | note | Acceptance / Conformance Criteria - Engineers Site Representative to inspect trench.
add79e8b-99ac-502b-8ad8-630c2054f057 | note | Standard / Specification - PS-16.5.7
0566e3c3-73a1-592d-a6f4-b9148b246c4d | note | Verifying Document - Certification
ca0dc36a-ea41-598f-a8e1-6f470f7ed02a | note | Testing Quantity Required (based from schedule qtys) - 1 time
2ed65cec-f74a-5f06-a004-ec478ad76bb6 | note | Verification Activity: Activity - HP
89caedff-261d-5144-bf24-0b1e3bf61e47 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f42e917b-37f4-5f05-990a-acdb4126e2b7 | note | Verification Activity: By - ENG
ecdb98fd-6b32-4654-9a22-474c0c8625a1 | signoff | AUTHORITY HOLDPOINT
fc1a0167-6c2c-4f7c-84bd-50de6be5d995 | checkpoint | 4.3.1 - Pipes (PE/ Sleeve)
ec4acbdb-d745-53b7-ae3a-171b925fbf73 | note | Detail - Manufacturer's record and location of extrusion plants.
ab42057b-ec70-503b-923a-b6ecb70ddae1 | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
094ec16e-11e0-5c44-8930-d9abcb22bf19 | note | ○ Full Traceability information and certification of analysis for the resin batch.
aaf00832-bb82-5742-94ff-ca4e6143bacf | note | Acceptance / Conformance Criteria - Engineer Approval
eafd8275-7610-5f59-8a1b-00fface7de0c | note | Standard / Specification - PS-22.4.1 (d)
07bd8f9e-e38b-58de-9444-9a62959e8b84 | note | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets.
45d18c3b-26cf-5dd5-8bfa-b76d1cb92dd4 | note | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
84d9e2e8-ea32-5cf2-886f-ea320804fade | note | Verification Activity: Activity - HP
230c6552-1ed3-54ce-9202-2514726772b7 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4339aba8-afea-5593-bc5d-aee10536bd05 | note | Verification Activity: By - ENG
aad266b2-fa8a-4d10-9c20-13af6c46e43a | signoff | AUTHORITY HOLDPOINT
8e938e14-cc7c-4e68-b347-85f1360531eb | checkpoint | 4.3.2 - Valves, Adaptors, Flanges and Fittings
ea094425-19a7-5cc3-aad8-1182e3933dd5 | note | Detail - Have a pressure rating no less than the designed pressure.
32d16c53-7f86-55db-86ff-c0706bc38953 | note | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
1a7f02bb-a577-5a90-9e25-83c5d55de51e | note | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
4e5908ff-19f1-5856-9298-c003450a936f | note | Acceptance / Conformance Criteria - Engineer Approval AS/NZS 4129
93b9e295-b8b4-58b7-ae96-41e4c86b1f17 | note | Standard / Specification - PS-22.4.2
05afb50d-a915-5a2b-abae-a126c727bd76 | note | Verifying Document - Test Report showing pressuer rating and compatibality from the Material Suppliers
23ae8182-affd-5dfa-9163-73668634838d | note | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
424cbc98-51db-507c-92e4-c6fabd6bda14 | note | Verification Activity: Activity - HP
034243a8-ac5c-5ad1-8dd4-74742601176f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b0f12048-2849-5d89-a830-92d5344fc7d3 | note | Verification Activity: By - ENG
782dcda4-1e89-4f09-ad7e-8288b43b6a1a | signoff | AUTHORITY HOLDPOINT
568a0c1a-734b-44a4-9499-1471d5308cbf | checkpoint | 4.4.1 - Pipe and fittings (PE100- DN355 PN12.5)
d88a5c34-99ce-55b5-9ab2-1bdfcfeb3459 | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
d5f768c4-eba1-5616-b0a4-3b26cdbf5c7b | note | Acceptance / Conformance Criteria - As Per Drawings
72c706cb-6d1d-525a-91ad-1f9961df7cbd | note | Standard / Specification - Design Drawings
29a12935-19dc-554a-97c5-da44eb99680d | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
38b56f5e-0af8-569b-b226-7fe87e5f023a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
0c7fb807-9cc3-5be9-a006-513a855948d0 | note | Verification Activity: Activity - H
420a1834-19be-5e52-8848-ce4f14e38d7d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
25467ab5-5786-53ca-abc3-72a4aad7ca20 | note | Verification Activity: By - SE
faf58554-f118-4fa2-8019-8e9a75645518 | checkpoint | 4.4.2 - Valves, Adaptors, Flanges and Fittings
d1eb3f7c-7acc-5c61-9a3a-2ac51bde157b | note | Detail - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
2452a0cc-7bc4-5a4e-a83c-584f534e13ea | note | Acceptance / Conformance Criteria - As Per Drawings
5b695583-8691-5398-b5d6-e0f4c4ff3b00 | note | Standard / Specification - PS-22.4.2
4bf84a96-5022-50de-aa22-86742d799030 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
ad8b2c47-26df-5a6b-b368-1acdbbbb0e24 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
4109a400-bc55-5e93-a86b-9074309f7f42 | note | Verification Activity: Activity - H
b64e8b2c-5f96-5019-86ac-70e592a4d78a | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c83cd0f9-6cc5-59c6-b659-cf0b06695b74 | note | Verification Activity: By - SE
2bc6f17f-3890-46bf-ba50-34447fb3ec5e | checkpoint | 4.4.3 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
d6f4e404-94ad-58c2-832d-c50c6d9c51d5 | note | Detail - Confirm Specification and material in good condition.
13194e5a-55e9-5b45-8de6-caece67dbcbf | note | Acceptance / Conformance Criteria - Site Engineer Approval
b1d6314b-6942-5a35-a919-658ac38e072c | note | Standard / Specification - PS-22.4.1
2a512888-f819-50ab-a13d-027b18aec63e | note | Verifying Document - Delivery Dockets
f7b1ba62-b39b-568a-b97f-95821ae7f7ea | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
0d1803fc-de2e-5f6e-9418-2f135e9aff63 | note | Verification Activity: Activity - H
42c9774d-f3e8-5377-9863-fc8e40406a81 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b700a17c-6a44-5be0-961c-e0705795c69f | note | Verification Activity: By - SE
50876e46-92bf-4b5e-aae4-47b073513c9d | checkpoint | 4.4.4 - Bidim/Geogrid
e2cf9b7d-a448-563d-b2c5-1b00730a1b2d | note | Detail - BIDIM A29 Duragrid 30/30 or similar.
59690be4-823b-5f93-b16b-0e8c41bb8308 | note | Acceptance / Conformance Criteria - Site Engineer Approval
d4e4f404-db1c-5fff-b858-9328da8f3b60 | note | Standard / Specification - PS-22.4.1
0ba7a33b-0b1c-5fe5-9005-cd07bafe2cb9 | note | Verifying Document - Delivery Dockets
1b2cdeaf-f457-5b33-b5db-a09084382ee3 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
a584733f-7017-5dc1-862d-06b2afcc17d2 | note | Verification Activity: Activity - H
9f8e4b3b-f1dd-50b3-a82a-9d6239161a9a | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
90edd5b7-fb7f-59f4-a8e8-851166a49389 | note | Verification Activity: By - SE
4d767dca-e269-4130-89fd-287f5a4ead85 | section | SECTION 5 – CONSTRUCTION ACTIVITY
82053533-236d-4a80-96f1-7d6a6420f4e4 | checkpoint | 5.1.1 - Foundation Compliance
8e9a0d26-5c37-537a-adbc-4a1f6c386bf8 | note | Detail - On Granular or Cohesive Material
85c87151-aea4-5a3c-a3f4-178d9ce088ba | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
1b62fb80-d64e-513d-b048-7eba4affc8c6 | note | (Or)
ed855d40-8e15-5706-a8f0-16ad158d582b | note | ○ Cohesive Material: Vane Shear Strength 70kPa
4e966a63-1261-5ce7-b7fc-5207f4d4817f | note | Standard / Specification - PS 21.6.5 and AS/NZS 2566.2
332ad370-5d71-5224-ab2c-47f67daf2709 | note | Verifying Document - Scala/Shear test result
aa33a001-4b35-55ba-a9c9-8242f41d8147 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
39d77fd7-2da3-5fff-a376-49e884061acf | note | Verification Activity: Activity - W
7891129c-7182-5488-95e8-6e88990b9a90 | note | Review of text reports/records or other evidence of compliance
3219eb26-b4ea-5ac6-b9f3-ac3abf06a299 | note | Verification Activity: By - SE
ac9d18fd-22ef-4d3c-a2eb-095e62f6f3c8 | checkpoint | 5.1.2 - Undercut approval
91d9c49b-8c94-5280-8ed5-484374ad1612 | note | Detail - Trench Foundation
e3784ce4-7bc6-508c-9938-71d149dd3e80 | note | Acceptance / Conformance Criteria - 300mm Max cut
9fbb9c53-edcc-55ce-9ee8-990562a7f656 | note | ○ IFC Drawing Sheet 320
f4d26bc2-2644-5bea-8475-5a5b2c46685c | note | (Or)
d75a86aa-63c2-580d-a46d-74f9e289a6a6 | note | ○ Engineers approval
ad426d14-4b77-5479-b582-f6b4301806e9 | note | Standard / Specification - IFC Drawing WAT 0320. AS/NZS 2566.2/2002
5fb71400-0d9c-5cc3-b5a6-48185282f779 | note | Verifying Document - Lab Test Report / Watermainline record
2dbf0141-80e7-5d87-953f-9d4f86832db9 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
bce3024a-45b8-55f6-845b-ab6a83322ebf | note | Verification Activity: Activity - H
e6098477-409d-59d3-aea3-07fb5ebb38b5 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5a4bebfb-7481-5983-ab8f-fd4f4ca4a998 | note | Verification Activity: By - SE
08473596-6c78-4da0-9c0c-8c8e77d2de0d | checkpoint | 5.1.3 - Undercut Backfill Compliance
a991c6de-5b71-5e88-958c-a7e5e35fff1b | note | Detail - On Granular Material / On each layer as per specification / on the trench foundation.
f0c5427f-8c9d-568e-b956-2c63a6fec2d9 | note | Acceptance / Conformance Criteria - Visiual Inspection
65f1cabd-782f-5664-8d7b-bb79a4cfb4bb | note | Standard / Specification - IFC Drawing WAT 0320
597f1bb0-a74f-50ab-a628-0b4d5a498ab5 | note | Verifying Document - Lab Test Report / Watermainline record
58bbd019-8f31-5680-a97b-dc8ca2cc1618 | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
ec1b1ba8-d8e7-51da-a8d5-cab8c82de2bf | note | Verification Activity: Activity - H
87cd0a8b-8006-51c2-a5b5-9205043ed3bc | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
90363d68-0331-50ef-a303-648528b7afa5 | note | Verification Activity: By - SE
c676a675-7f22-4c1c-abe4-71669f66d673 | checkpoint | 5.1.4 - Bedding Zone Compaction Testing (PE Pipe)
a89265ec-d412-5c66-b7ab-0187ebf402e6 | note | Detail - On Granular Material / On each layer as per specification (Imported Sand or GAP20) NDM testing as per NZS4407:2015, Test 4.3
f3ee8cca-4830-5895-9cce-3016d68f4b68 | note | Acceptance / Conformance Criteria - Bedding Zone:
2b91181b-6f32-5505-a218-296ca60873ad | note | ○ 100mm minimum thickness (compacted) over the bottom of the trench.
e1600457-16bd-5b1e-84ac-27310a8e52c5 | note | ○ Minimum Compaction- Trafficable 95% MDD and Non-Trafficable 85% MDD
7508f66c-9b2e-5b98-85b2-be1ffbc9b2a4 | note | Standard / Specification - IFC Drawing 0320-1, AS/NZS 2566.2/2002
8270a176-f298-5d54-985e-35b86c9a1ff9 | note | Verifying Document - NDM:Lab Test Report
3f45f1cd-ff13-551a-b723-f29857ed7e9b | note | Testing Quantity Required (based from schedule qtys) - As per Water Specification. One test per 20m evenly spaced intervals.
bccad475-c28b-5de3-b317-e6bca1f3b7a7 | note | Verification Activity: Activity - H
5ce4e268-3ab6-55ac-bde4-18837390c82b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
9fe49360-e112-5897-ac7b-28894b4505f9 | note | Verification Activity: By - SE
7d647234-ca89-448b-87a2-4cb7fbd03193 | checkpoint | 5.1.5 - Laying of Pipes
5d98ba7e-6776-5871-ab8a-c9a596adeae0 | note | Detail - Lay in straight lines, beginning at the lower end of the line.
a7d5fe6b-722c-5dfd-b70e-19a26dbdba8e | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
56631ff9-59d9-5d49-88c2-b26d97283be0 | note | Acceptance / Conformance Criteria - As Per Drawings.
83e630e1-322e-5405-adf3-9376cf7f393f | note | ○ Facing upwards
b57adb26-047e-576c-999b-fd4fee7adcf0 | note | Standard / Specification - PS22.7.1 C
aadbdaa9-0bd6-552f-bf6b-0a639d15e1e8 | note | Verifying Document - Visual Inspection / Watermain line record
e93e2c3f-1a79-5c37-9053-0f5d8fe5b67a | note | Testing Quantity Required (based from schedule qtys) - Every Line
a240ed27-b1ee-5826-b504-738e3141bc46 | note | Verification Activity: Activity - H
884541ae-a73f-579c-a5ae-b4682dc9bd12 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
779f4014-4ef9-5aa9-a4ab-bdb145083aac | note | Verification Activity: By - SE
3fa45ade-08cb-47f4-beeb-c8d1f24a9f6c | checkpoint | 5.1.6 - Pipe Installation on Curved Alignments
5696e133-773d-5d8d-9ac9-417d7abbb4e0 | note | Detail - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
46e5d7ec-f9cd-5654-b92a-da75eabd0de5 | note | Acceptance / Conformance Criteria - AS Per POP 202
64171227-ed3d-5aab-a62c-b2e7bf71fef1 | note | Standard / Specification - PS 22.7.1 D
872f3d86-9dbf-5263-8bc0-9a1708f3bcad | note | Verifying Document - Visual Inspection / Watermain line record
5c61739c-50d0-5249-bf63-63e4d525e1ee | note | Testing Quantity Required (based from schedule qtys) - Every Line
848a8583-48dc-5c07-918e-12d688a585fa | note | Verification Activity: Activity - WP (Review of text reports/records or other evidence of compliance)
3291f0db-f9e6-515d-af94-583e8fa3cd93 | note | Verification Activity: By - ENG
c61db763-49df-4dea-9389-64f6b614e398 | checkpoint | 5.2.1 - Flanges
01263d85-da23-5dd6-b91e-f26f0393a10c | note | Detail - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
9504615e-502a-5e68-8b7f-b174ba661865 | note | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
26b9514e-ded8-5b58-82ef-3b09fa0abca9 | note | Standard / Specification - PS 22.7.5
c9186e8d-01af-5d78-a6c9-7f5c2cb0cc92 | note | Verifying Document - Visual Inspection
1552f7f7-ae06-5800-a54e-3cb470fa5353 | note | Testing Quantity Required (based from schedule qtys) - First flanged joint
ca19359a-4373-5d0e-9b71-7029ea789825 | note | Verification Activity: Activity - HP
2c9ddbf5-f2fa-56d0-8b22-bbf75e701e29 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0f46eb89-8089-5f25-84b4-e0400bc414cf | note | Verification Activity: By - ENG
65de76de-ed7d-4482-8bc4-b168cd872bd0 | signoff | AUTHORITY HOLDPOINT
49777ef0-0363-4b2b-a50c-0cc9b1342870 | checkpoint | 5.2.2 - Bends
e5df552d-8649-5bf1-b6bf-0d01099ccb3a | note | Detail - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
51a83b19-96da-56cc-81cd-afdbbf5f5ecd | note | ○ Fitting must meets the same PN rating as the adjacent PE 100.
09448f99-faaf-5844-8439-fd28290d73c3 | note | ○ Fittings must be suitable for producing the joints shown on the Drawings.
94f60a54-16d9-5326-811d-6d11cc4312c9 | note | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
ba8fae0e-70fc-5329-aada-16bfe8cf76c9 | note | Standard / Specification - PS 22.4.2
6628ea11-1002-5007-8ed9-dace5a8ee500 | note | Verifying Document - Visual Inspection
4659f703-60e5-5c57-bd6a-5fbaa24be9ab | note | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
b07ee3fd-c932-54b5-a8e2-2741ee44ad90 | note | Verification Activity: Activity - H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
666dffab-643a-5bd9-a52b-c0ad30763249 | note | Verification Activity: By - SE
0c2bb359-a787-44af-8797-d240d742223b | checkpoint | 5.3.1 - Butt-Fusion pre construction weld test
b8dc185b-2e35-59d7-b799-6c0394b1b665 | note | Detail - One weld on the most common size of pipes used for the project.
59a663ad-7b49-51de-b6c1-917e5085a13e | note | ○ One weld on the thickest wall (highest PN) pipe
1496afdf-cea2-5f2e-aba3-62aa41147ae2 | note | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode.
6721823f-a7fa-5d79-9052-3d52a70f9b6b | note | ○ WMS Report
afaad977-2119-5c54-9882-55b4b3656c04 | note | Standard / Specification - PS 22.9.6 (a)
21cead50-707d-5aeb-819a-5c35a568b5b7 | note | Verifying Document - Visual Inspection/ Test Reports
72063c72-6f76-5042-a84d-6891b938fb1f | note | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
e2c65ef2-8a73-51fb-8256-f1da55628b96 | note | Verification Activity: Activity - HP
9cfae568-6055-5439-8444-45372e164805 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
017a075d-0a75-5442-bad9-1c27badcb7e8 | note | Verification Activity: By - ENG
79f48858-7b99-4dcc-98e3-7aa46d2235af | signoff | AUTHORITY HOLDPOINT
68156762-b747-47f3-9d6d-9d43086bc66c | checkpoint | 5.3.2 - Butt-Fusion Welding
dfbad77e-2758-5f22-91c1-ce61ea710543 | note | Detail - Use only semi-automatic or automatic welding machines.
3b2ee552-08c5-524a-88af-8d25857f33eb | note | ○ Maintain a site record for all butt-fusion welds.
34cd90b9-5ab8-56b5-8bda-0d0a0e7ede28 | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
09bbd19c-1fb5-55f0-b13d-862cc7588cb5 | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
9a70c08e-8940-5286-b7e6-224d3878a68b | note | ○ WMS Report
c4dc7b91-a386-5af4-8e79-4b58f01493a6 | note | Standard / Specification - Appendix 22. PS 22.9.4 C
25a00752-b9e2-51f3-bd6b-8eae49ead483 | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report
55ecfb30-87a7-50a1-9681-1c9af152a540 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
6495d970-fdd5-5b3d-9789-ca47367a812b | note | Verification Activity: Activity - HP
81a8dfd6-4383-5f65-b594-2a1273ad5b1a | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
13dc2bed-b44c-53dc-8db3-77ec9a3c02f0 | note | Verification Activity: By - ENG
2962c4d0-b550-408c-ac87-4d335225be1f | signoff | AUTHORITY HOLDPOINT
0a0a9819-8bc7-4b56-8b0e-640728a24b8e | checkpoint | 5.3.3 - Butt-Fusion Construction weld test
12257571-e644-58b5-8536-78cbf895c794 | note | Detail - Test at least two welds from the first 50 welds.
32df6846-eb8d-55bd-ad9f-80823b481026 | note | ○ One of the welds to be selected by the Engineer for satisfactory result.
80f82be2-cac2-5d1a-b518-e06d030f3ac7 | note | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
c61a478d-242b-516b-9f41-2bec28c6ebec | note | Standard / Specification - PS- 22.9.6 (a) (iv)
b4826d77-fa37-56db-9274-beb15683f0ea | note | Verifying Document - Test report
03f018f2-51f6-52b5-87d8-c836922eee80 | note | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
6aa313e6-3bf7-5351-a5a7-61ccb542281e | note | Verification Activity: Activity - HP
0311b0ed-ca06-5389-8d27-b36d2ed50c0d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
92ee8729-bcd6-503a-b8ff-ce85f846a1ec | note | Verification Activity: By - ENG
ae9630b3-18f1-4294-93a5-204d7af4df76 | signoff | AUTHORITY HOLDPOINT
1048af9c-8d80-4e01-8e1a-4058c74e50ee | checkpoint | 5.3.4 - Survey
7a90cc35-e6c1-5676-b5fd-21d869e2a815 | note | Detail - Inspection of Pipeline Inverts
df09ced6-8288-51ea-9dfc-5eff5d165c86 | note | Acceptance / Conformance Criteria - Vertical design Setout:
bd048980-7c0f-5120-a889-bad7087603b2 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
71b9d4ed-ccfc-5dea-a750-0ff7f8948cf4 | note | ○ Pipes > 1% grade: +/- 20mm variance
1c27f186-91bf-5b94-8056-bbc3df1818d8 | note | Horizontal design Setout:
48c66168-e67e-56f6-87c5-20f07f3a2911 | note | ○ +/-30mm variance
619826e3-096a-5b07-89b7-02d8c0e7be68 | note | Standard / Specification - PS- 21.7.6, Table 21.15
d6a3ac2d-e899-549e-9a0c-cc67983b931f | note | Verifying Document - Survey Data / As-built record
64c338af-2f85-5099-8049-31a1175686ab | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
824a8cf4-1f11-55c7-9b31-89c6f6d5fa3b | note | Verification Activity: Activity - H
40d081cd-7286-5e5b-bf48-43a380bad3d5 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c8c85891-7291-58db-91d2-1c699172b5ed | note | Verification Activity: By - SE
036a8ffe-61e3-46ee-8066-07ded842204f | checkpoint | 5.4.1 - Electrofusion (EF) pre construction weld test
f5b5248b-bff8-5fa2-87c0-bba67d646263 | note | Detail - Use the designated welding equipment and the approved WMS.
eea5ec00-bf77-547d-bfc5-ff2a130aec08 | note | ○ On the largest size of PE pipe used in this Contract
64e81329-23c9-537a-95f2-2dd4e6ecc4d3 | note | Acceptance / Conformance Criteria - ISO 21751 (strip-Bend test) or ISO 13954 (Peel-decohesion test)
48eff62b-a241-5e27-8951-7c1b2e2bfb11 | note | ○ WMS Report
6e400a2b-b9f3-5d5e-a07d-82ea1041587d | note | Standard / Specification - PS 22.9.6 (b)
632939f8-c3ec-5fbd-8aeb-024f24e3160c | note | Verifying Document - Visual Inspection/Test Report
d2b898aa-fe56-544f-976a-1df2f23ea755 | note | Testing Quantity Required (based from schedule qtys) - One test welds per operative(Welder)
c434e9ae-5c05-5947-9eb2-6a2c66b09c9c | note | Verification Activity: Activity - HP
1561be26-44c1-50d4-8026-7df75f77905e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
07801683-2d7a-51e5-8790-c1a0a056aecf | note | Verification Activity: By - ENG
7ce0c5ab-1ada-4df7-9e51-6605a389edc2 | signoff | AUTHORITY HOLDPOINT
d731e839-bfa4-4887-85e7-837048ada425 | checkpoint | 5.4.2 - Electrofusion (EF) Welding
88e596a2-b411-5398-b4da-062374c96b8d | note | Detail - Required if Butt fusion welding cannot be perform.
74d45875-db6a-5b6d-8efd-9b94f6ecfca9 | note | ○ EF Jointing in accordance with PIPA POP 001.
7a8306c1-8692-5421-8df0-6f0555fc80f3 | note | ○ The lead welder or welding supervisor must verify on the site record form.
7e61ba9d-c2cc-5215-8dad-781168e8c34d | note | Acceptance / Conformance Criteria - WMS Report
d467032c-8e4f-514b-9ca9-5e2f206ce0ae | note | ○ Checklist (refer to CWP).
7d3d6ff8-6794-5e42-8965-abd6a0ea2446 | note | Standard / Specification - PS 22.9.5, Appendix 22
85b5bc57-6ca4-542c-a23b-fab93543b60b | note | Verifying Document - Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report
3eae3d40-3a33-5aed-8bca-387da6db2260 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
86cf2d0e-3d9c-5753-b062-ba32a18eee26 | note | Verification Activity: Activity - H
ec94f8c4-412b-5f9f-975b-fbd16fcdb1d7 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8383a8dc-9a40-52ce-a93d-87abc10d7eed | note | Verification Activity: By - SE
54d901d7-0903-4c6a-8c7f-c67522db93f6 | checkpoint | 5.4.3 - Electrofusion (EF) construction weld test
6c81d275-b53b-592c-a7d2-44806e675edc | note | Detail - EF weld quality to be maintained.
28622d62-70a2-50d3-8c72-21811280baeb | note | Acceptance / Conformance Criteria - EF coupler and EF saddle testing
32682a7d-c066-5c49-941e-2c783804bb06 | note | Standard / Specification - PS- 22.9.6 (b) (iv)
e8288422-2139-5608-80a5-26b9fb6d04ed | note | Verifying Document - Test report
d9fb5da5-f402-5465-89a2-bccd4192b732 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 5 welds
4d8e0da6-1ed1-5aee-96db-cfead1dff67e | note | Verification Activity: Activity - HP
899c1fd6-9d1a-5d13-ad72-da0806cc93ed | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
63314b99-5eae-5d3b-8724-08c0b75ec72f | note | Verification Activity: By - ENG
4bbd2062-bfb9-4619-9f17-0756ffedbe38 | signoff | AUTHORITY HOLDPOINT
0c9853fa-f754-44ac-9af6-5df8765fbfe2 | checkpoint | 5.4.4 - Survey
24082860-81c6-5466-94b3-ab2b284e7a3a | note | Detail - Inspection of Pipeline Inverts
b8bdd117-9026-5f50-9309-c219d62e792b | note | Acceptance / Conformance Criteria - Vertical design Setout:
f141f0dd-1cfa-5e69-8cd8-4a67751a4e2f | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
ae88a915-a830-50ed-9500-7accacc8b673 | note | ○ Pipes > 1% grade: +/- 20mm variance
825308dd-9ba0-52c1-b5b8-f139401a3fa4 | note | Horizontal design Setout:
002bc1ee-bdd5-5f2b-ab9d-467550963cfa | note | ○ +/-30mm variance
72c1e08b-fce2-5dda-a428-7ef421c27918 | note | Standard / Specification - PS- 21.7.6, Table 21.15
2e74f08f-bb64-508a-b127-005962f3cf24 | note | Verifying Document - Survey Data / As-built record
54b0c2b1-a1b0-57ee-a2ed-257fc82aaf8b | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
73a93f4a-0a28-5691-bf4d-331111910550 | note | Verification Activity: Activity - H
3e7546b1-1873-51b7-88e1-afb3cf247312 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0abd9862-245f-5ce1-9031-87df5ed5e677 | note | Verification Activity: By - SE
37023388-d70b-44ff-b0de-5b5bd3c257be | checkpoint | 5.5.1 - Emebment Zone - (Side Haunch Overlay )
a301f068-0d55-5567-8b84-10d4236ae5de | note | Detail - AP 20 backfill Compacted in 200mm Layers.
c7170dfb-4506-5821-a9ba-f5d09ef7a9b2 | note | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays .
db341517-a6df-564c-8e37-cc4a4f2cce4e | note | ○ NDM BS to be Carried Out
c51c893f-0958-5a0a-a6a7-9854f4611c91 | note | Acceptance / Conformance Criteria - in 200mm layers.
89c88dc1-7db3-5975-820d-a3e3d469ff86 | note | ○ More than 85% of MDD.
2c57eea4-e1a5-5922-801a-42830c234860 | note | Or
67b5d8d9-3fa9-550b-be01-6791b083999c | note | ○ Minimum Compaction- Trafficable 95% MDD and Non-Trafficable 85% MDD
052d35f3-508b-52be-9172-629d6acd3984 | note | Standard / Specification - NZS 4407:2015 Test 4.3 Nuclear Moisture Density Gauge; BS
fc4064c9-a6cd-5c1c-9620-8f00621c5de1 | note | Verifying Document - Lab Report / Watermainline record
e8b60c12-d025-55ba-8f15-c4741901bff0 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals. 200mm lift
a426835e-96b9-5e3a-81fd-a273a8e1834a | note | Verification Activity: Activity - H
af835de1-aad3-5b2d-9c43-4521038995f8 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
becc822f-386a-5dca-a8df-47ecdb432e90 | note | Verification Activity: By - SE
d050736c-4e5c-438b-bd26-6109436b06f3 | checkpoint | 5.5.2 - Pipe Markers
14d15fd9-3cc2-5fa4-bc34-0edd05cbfff6 | note | Detail - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
93b74fb3-6afa-5870-ae3f-c7911e2fb95a | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
3a9bdcc4-2be8-5f99-ad1f-e9045ff80373 | note | Acceptance / Conformance Criteria - AS Per Drawings.
6fcb2a59-118f-5f3d-92b2-d95edbc778b5 | note | Standard / Specification - PS 22.7.3 a
8abedf07-645c-50da-b610-9298891bc3e1 | note | Verifying Document - Visual Inspection / Watermainline record
bedb66d6-3a95-5623-a710-4629ece5a1cc | note | Testing Quantity Required (based from schedule qtys) - Every Line
77b45c69-4a96-586c-bc68-e4d15cf89d25 | note | Verification Activity: Activity - H
bca1fab2-bc8a-562b-a308-5ed873ef1cc3 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ab079233-6a53-5431-8203-4775026df4b3 | note | Verification Activity: By - SE
825dee0f-1828-4f92-a4b3-54f7746e596f | checkpoint | 5.5.3 - Backfill Compaction Testing
901e6a0a-7a81-557f-84f1-9c7f11d313f3 | note | Detail - GAP65/AP65/LRAP65 Backfill Compacted in 200mm Layers.
8c9595b4-7fce-59fa-a129-b60362b775a4 | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
a4761f8b-fa79-5e34-919a-ff33c522c6eb | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers.
2f549fbe-2659-5117-a6f7-d743c84c8183 | note | ○ Testing to be completed on maximum 200mm lifts of backfill.
4012adc2-6190-59d7-b9e4-b9b8870b32de | note | ○ LRAP65- achive 90% NDM on Grassed Area and 95% NDM on Shared and Carriageway.
926b11c6-a7fd-596a-bf04-df84af6bc1d0 | note | Standard / Specification - PS- 22.13.5, NDM Standard 25832, NZS 4402 Test 4.1.3
22b07b8b-9466-5db2-8faa-05c94c447559 | note | Verifying Document - Lab Report / Watermainline record
90df1755-10cd-5d04-8425-61dc3d74e2c5 | note | Testing Quantity Required (based from schedule qtys) - As per 200mm lift. One test per 20m evenly spaced intervals.
4497c566-00bb-5a1b-ae4e-822a5ad0a098 | note | Verification Activity: Activity - H
49013a28-8f88-5a6b-9abc-2f8dda307176 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4bce3e34-fe96-5b91-abc5-32783867a220 | note | Verification Activity: By - SE
2fc2f76e-862b-4b68-9dc5-b8857255ea03 | checkpoint | 5.6.1 - Pipe Inspection
1a1cd0b5-2dd2-54b0-b376-ff03e5a6c24f | note | Detail - Inspection of Water Rising Main line
42cbc36c-8626-5835-9cab-c6169918f451 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
21ca437b-1912-5ee9-a9e0-f19e75edaa5b | note | Standard / Specification - Internal
016c2fda-ebfb-53c0-8f14-1722593a670f | note | Verifying Document - Watermain line record
5a95ac5e-a80e-5efd-8eb8-d8f306a27e71 | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
2264c1d4-3c9f-5ab9-aef6-0d840057ec84 | note | Verification Activity: Activity - I
d3c8b41e-b0f9-5869-8ca1-debc98dbf784 | note | Formal inspection activity to be undertaken and recorded.
101535de-8c33-54d6-a575-9bf0ce6ff57b | note | Verification Activity: By - SE
15ae9e1e-6e2f-4306-b909-d02523bef6e0 | checkpoint | 5.7.1 - Pressure Acceptance Testing
8e6b98d2-8efd-5cc4-9754-4014b349a625 | note | Detail - Backfill/cover with embedment before testing
a239db14-0cc4-5c3f-8f61-20be17a7d2f0 | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
498c6837-ea00-59d0-8bd0-ecf0187418c9 | note | ○ Thrust Blocks installed- backfilled and concreted.
301d7020-11b7-58fe-be79-dc8ba9138ef7 | note | Acceptance / Conformance Criteria - WatermainRising Main Pipelines – 1250kPa
5ebddd3c-b93a-5cbb-9b01-4ad609681b0b | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
643b799c-d229-509d-9132-6d015ddb6bab | note | Standard / Specification - PS 22.7.4, PS 22.7.12(d), PS 22.7.13(b)
29b5183e-ce79-5dec-8edd-2ea298ab0ddc | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
acae643f-857a-5fd9-8b51-e947cff69d7c | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
eea10ab7-5a15-543a-93b5-4762946c9cfe | note | Verification Activity: Activity - HP
4a188d00-0c33-5376-a83a-a6e5430f0495 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
fab8f820-53eb-5b52-a46e-ad36f49cfe29 | note | Verification Activity: By - ENG & TPI
1144c958-6e58-4a71-b13c-c36d16ab3687 | signoff | AUTHORITY HOLDPOINT
76887398-829d-49ff-9231-7525bfb03b2b | checkpoint | 5.8.1 - Watermain Disinfection
d9ae749f-6d27-53c4-9b5f-a2319a36d92c | note | Detail - Introducing a solution containing a free available chlorine (FAC) residual of 15 – 20 mg/L (ppm)
2b6bdf8b-d7b9-5bd0-b1e0-55fc561e5c07 | note | Acceptance / Conformance Criteria - At the end of the disinfection time the Free available chlorine (FAC) in the water being flushed from the pipelines must be at least 5 mg/L.
a7100c87-46ab-5c57-a99f-f1f5c68d5b3a | note | Standard / Specification - PS22.8
0ffb2d28-12b7-5ebb-a096-64ab93eece3f | note | Verifying Document - Observation and monitoring of disinfection solution on site by Engineer.
42ff0d8b-77fb-5b7c-9759-7673d395682f | note | Testing Quantity Required (based from schedule qtys) - Once for Watermain pipeline
c84e4db4-2f25-574d-bf05-fc77c82dde20 | note | Verification Activity: Activity - HP
0e6e099b-db03-56cd-a8d9-3771cc29e785 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
bfa3ba3e-bcf6-5ede-87f5-f1c3c3d3e9fd | note | Verification Activity: By - ENG
5de0d5da-f3f1-4513-b29a-60facf06e093 | signoff | AUTHORITY HOLDPOINT
bf36d203-088b-4bb2-9af8-470639760fc7 | section | SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - ACCEPTANCE BEFORE COMMENCING DISINFECTION WORK
683e7344-c787-470d-ad0c-229d1ccd045d | checkpoint | 6.1.1 - Survey As-Builts
35ec82d9-aa79-55ab-88f4-b3f689e1621d | note | Detail - Quality Check on Nee pipeline and structure based on the tolerances in RITS
6699b658-1272-563d-b736-00efd4430f11 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
2e3a941b-63bc-504c-b61a-818806e630e1 | note | Standard / Specification - Project Specifications
ff429bc2-e2d5-5330-a3bc-307420ae70cb | note | Verifying Document - CAD File as per PS12.3 and Red pen markup only
adc38286-fa84-55aa-bb27-5deee4106164 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
b69b4873-20fd-5f99-8dd0-c2d01258c103 | note | Verification Activity: Activity - H
ab622969-3460-5d54-add1-a5548325b54b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5f7b3d79-f371-57ec-ac10-af7ea47bbe55 | note | Verification Activity: By - SE
ec88217f-887e-49ba-a501-14d3ac99caf9 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
3189193e-22ac-5462-9c8c-71fd04a42f57 | textbox | Contractor's Rep Name:
4f5c39b7-2afd-520b-88ca-f4784e75011c | textbox | Engineer's Rep. Name:
31ccc46e-7866-546d-8f17-459cb94f1b6a | date | Date:
adcffc03-b1ba-4812-a87a-8fb38bb06adb | signoff | Add Signature
07d8a1e0-2c78-4fa6-b014-c940d056ff4e | checklist | DN1210-018 ITP Gas Protection Structure Rev 0 | itp | DN1210-018 ITP Gas Protection Structure
f562b102-101d-45c5-963e-45b1179ae6f0 | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
e5a0b618-fefa-4aa8-b863-e9fc53e38c33 | checkpoint | 3.1 - Reinforcing steel and Strands
085d15ef-8083-5e19-9bc0-30714412849d | note | Detail - All Reinforcement bars and strands used in structural concrete to be approved by the engineer prior to construction.
c035c7f2-d3fe-5ee8-9ee9-e7422ce27d4f | note | ○ Post tensioning strand to be high tension ASTM galvanized and complying with AS/NZ standard
0a03338c-2f50-585a-b04d-43362e7a963a | note | Acceptance / Conformance Criteria - Test certificates shall be obtained from the manufacturer for all strand, cable and bar to be used in the work and copies shall be forwarded to the Engineer at least one week before the programmed commencement of any work incorporating these materials. Test certificates shall be traceable to the batch of material supplied to the work.
96d20958-0458-57bf-a9ee-f1da5f6f36c5 | note | ○ High yield steel, Grade 500E, Seismic MA.
6dd24b9e-b1c8-583f-94de-fbff02db660a | note | Standard / Specification - PS 18.3.3, 18.5.7 and 19.13.1
623be45b-df8b-5424-a450-49d9d6e12f01 | note | Verifying Document - Supplier data sheet/ Mill certs
4a2830a4-6575-5aaa-a038-34b4801be9fd | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
25355fb2-0a33-5fe3-a5fe-263408c39ccb | note | Verification Activity: Activity - HP
a0fb09ca-9c1e-557b-bb15-202d4791072a | note | Verification Activity: By - ENG
0ebe80cb-4f79-4c0c-94e8-8b4c8a484c01 | signoff | AUTHORITY HOLDPOINT
fe70bfd6-beb2-4f4f-bb23-6a902fb0fb07 | checkpoint | 3.2 - Concrete mix design
1e273088-7561-5615-86e9-ea12220c667d | note | Detail - Approved mix design - Concrete shall be of the class as defined by NZS 3104 have a minimum 28 days compression strength as specified for various members: for Gas Main protection structure in-situ pour: 40mpa
9ef9e248-bffd-58ca-90d7-6e2e7974a788 | note | Acceptance / Conformance Criteria - 28 Day concrete requirements:
12d25260-ed92-5cb0-b880-6c69d7049c5e | note | ○ In Situ Footing and stitch pour for Gas Main Protection structure: 40MPA
ddc8be09-0305-5975-8a4a-99dd814c68e3 | note | ○ Screw Pile Shaft filled with 40Mpa Concrete
358d96b3-6347-5ffb-9fc5-ba8add4f19a6 | note | Standard / Specification - PS 19.3.3
2b840fe2-9c58-59f0-b8a5-039b8895693c | note | Verifying Document - Approved Mix design
7378ab80-1b6c-5352-a72a-f09bfadead3a | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
ea96f2e6-413f-53a9-96de-76fa664f837a | note | Verification Activity: Activity - HP
9d492b42-20ac-5f93-bbec-27b90f8f0d25 | note | Verification Activity: By - ENG
a2132987-d7b5-4f04-8dec-329934710455 | signoff | AUTHORITY HOLDPOINT
e84be5ff-201f-47a8-9fc4-24e08f3ab795 | checkpoint | 3.3 - Shop Drawing Approval
bd677266-9079-522c-96ab-d03125d10201 | note | Detail - Shop drawing review and approval from Engineer and Production QA Records to be submitted
e5d416dd-06f1-5533-8911-1735fbe69966 | note | Acceptance / Conformance Criteria - Send shop drawings to the Engineer for review, at least 14 days prior to manufacture of any pre cast members. Any variations between the Drawings and shop drawings shall be clearly identified and brought to the attention of the Engineer.
704102cf-3897-531b-9cc7-94d684545f4e | note | Standard / Specification - PS 19.12.6
f4b3aa88-8fba-5f88-ab9a-74110419bd53 | note | Verifying Document - Shop Drawing Approval, QA records
b236a2dd-ded9-5c68-b5b3-ebbbc741e86b | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
8210f29e-71a3-523a-af34-8d6b6c608f90 | note | Verification Activity: Activity - HP
23bc716c-5f7f-5722-87be-4603b4e25411 | note | Verification Activity: By - ENG
63ff8a59-e290-49a0-92fb-8cad583e2aa8 | signoff | AUTHORITY HOLDPOINT
af62ff11-a592-4d35-b357-359b0d900420 | checkpoint | 3.4 - Joint Sealing and Waterproofing Sealant
10859afd-9b94-52b5-a7ce-fc1cf3bc32d2 | note | Detail - Pre approved joint sealant meeting the specification requirements
c887028b-8d2b-5690-8547-40a8fcc1b6dc | note | Acceptance / Conformance Criteria - Joints are to be sealed using a fuel resistant, multi-component polysulphide sealant designed for horizontal and vertical joints in concrete and is joint sealant pourable or gunning grade as appropriate.
e4e54cdc-c451-5a68-90a6-115a87ba48a4 | note | Standard / Specification - PS 19.12.6
8962ef0b-bcb3-5a2a-9af8-d3f73fff41f4 | note | Verifying Document - Delivery dockets and supplier data sheet
63aa635e-a260-56d9-b456-8c40def50e4b | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - Engineers approval
01eabd3b-1ce8-5b78-a7aa-0357b7805238 | note | Verification Activity: Activity - HP
21cd0882-e6a7-555d-9ff1-a26136874158 | note | Verification Activity: By - ENG
758ef49a-b1b7-4a76-8803-f4aa296c698d | signoff | AUTHORITY HOLDPOINT
08d5b30d-8ec5-486a-9ef2-74b0c86d2296 | checkpoint | 3.5 - Screw Piles
f98025dc-0aeb-5798-859a-dd145b852171 | note | Detail - The Length of the Screw Pile delivered to the site will be long enough for both, Type 1 pile (dia 168mm, 6.4mm thick) and Type 2 pile (dia 273mm, 12.7mm thick). Need to be 11.95m long with Helix as indicated on Spiral Drillers shop drawing of the pile. Helix to be 450mm dia 15mm thick for Type 1 pile and 750mm dia, 25mm thick for Type 2 pile. The External Bearing Ring for Type 1 pile should be 250mm and 41mm thick. For Type 2 pile 350mm and 39mm thick
308f772d-a2de-59a5-9af7-16a9fca975d1 | note | Acceptance / Conformance Criteria - Site Inspection
529458a8-2648-523b-a9b2-83cbc8351cc8 | note | Standard / Specification - Spiral Drillers Pile Details, Drawing No. 1
2704dfd7-dab6-5821-bb9f-15276afeb95e | note | Verifying Document - Delivery dockets and Visual Inspection
d53f2dd9-0ba7-57c7-a36d-671ad433e847 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
30196f09-8358-5e55-bb50-7ce2e729707f | note | Verification Activity: Activity - HP
55ad4c28-7391-5755-9cf3-2925fcff7f56 | note | Verification Activity: By - ENG
f30fbc66-0487-42b3-a5bc-f9d3a024bed5 | signoff | AUTHORITY HOLDPOINT
eaac5dbd-5f91-41f6-a73b-2beab62649f2 | checkpoint | 3.6 - Compressible filler board
686b6894-7457-5daa-9730-755937db9306 | note | Detail - Compressible filler board specification to meet the project requirements.
9b924b04-603c-5c31-bfa9-525e4c520350 | note | Acceptance / Conformance Criteria - Details of the compressible filler board proposed to be used as a construction joint shall meet specification requirements.
e135c071-73b4-5f61-971a-d14edb868248 | note | Standard / Specification - PS 19.12.6
fda3ea32-618f-512b-9b27-dccefdded2d0 | note | Verifying Document - Delivery dockets and supplier data sheet
7f0196c6-bf60-5e53-96c0-2d8718868274 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
2ed93483-f17c-52df-a3e6-80add553c209 | note | Verification Activity: Activity - I
412fdb85-22ff-560c-8fc3-f8f9909d6ac4 | note | Verification Activity: By - SE
bd7cf1dd-1e59-4764-8a10-f1df966bb3f9 | section | SECTION 4 – CONSTRUCTION - EARTHWORKS SUBGRADE
d1168374-45d8-4533-bfbd-a02c582700f5 | checkpoint | 4.1.1 - Cut Subgrade Inspection
1dc2120f-f7e5-5036-a3ee-0b2553d73109 | note | Detail - Engineer to inspect all foundation surface inspections
4360cb08-9ad2-539d-9857-874a680ac986 | note | Acceptance / Conformance Criteria - Engineers Approval
35b72f6d-e722-5ac3-93e6-2e399e3b8e44 | note | Standard / Specification - Appendix V
b4f98d9a-5bed-510d-b809-cdf6cd7e2a0b | note | Verifying Document - Visual Observation
35ef5fb9-efb7-5357-9972-9c4c53022cb8 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
c1f04d40-a804-50ce-aee3-da79cc999533 | note | Verification Activity: Activity - HP
9220883c-9159-535e-9d7b-df6c7b3d4dc8 | note | Verification Activity: By - ENG
8e5e8d39-2ef0-4777-a2c6-33d4e267a6b1 | signoff | AUTHORITY HOLDPOINT
982684e0-53b7-4ad4-af65-4c156112d871 | section | SECTION 5 – CONSTRUCTION ACTIVITIES - SCREW PILING, INSITU POUR, PRE-CAST CONCRETE
fa509067-825c-48e6-b4de-d1282ee4e00a | checkpoint | 5.1.1 - Survey Set out
79244f73-6f63-5517-b9e3-452eae47aa44 | note | Detail - Pile heads must be within +-75mm of the specified plan location. Pile heads must be within +-20mm of the vertical level indicated on the drawings
3ca14e4c-08dc-52fa-a106-8c1b3421eb7f | note | Acceptance / Conformance Criteria - The verified data is within tolerance as specified
522ce4fc-6304-5811-8bd4-9015fa60e751 | note | Standard / Specification - AoS Design Report
8f2fa738-dbc2-521f-b414-af3f8201ca14 | note | Verifying Document - Survey data
1044ea12-3300-5c42-b3cf-10ea978a5742 | note | Testing Quantity Required (based from schedule qtys) - Post construction
4d703bc2-08e2-5467-aa1a-3693f93c9223 | note | Verification Activity: Activity - D
e2bd2671-906d-57c8-b01e-2ec7f5fc0f4d | note | Verification Activity: By - SV
fc2ad01e-0a0e-45d3-97a2-ccbdd3a61c08 | checkpoint | 5.1.2 - Installation Torque
10eca628-fff6-5cad-a91c-1623c457bd05 | note | Detail - The minimum pile founding depth for all helices shall be 9.5m below existing ground level AND Target Installation Torque 168mm dia shaft= 15000NM Target Installation Torque 273mm dia shaft=45000Nm Note: Max allowable Torque 168mm dia shaft=70000Nm Max Allowable Torque 273mm dia shaft=120000Nm-However on-site digger will allow Maximum Torque of 90000Nm
769e659b-3a6c-5f56-8621-395f55005bbd | note | Acceptance / Conformance Criteria - Site Inspection
c9548b36-cea3-5a21-9f53-a1156aab5c16 | note | Standard / Specification - Spiral Drillers Pile Details, Drawing No. 1 and AoS design Report
a0013dbf-1bbd-5e7f-947b-4ce526cebb71 | note | Verifying Document - Site Inspection
4d9a337d-3b97-568a-a38f-dad42ea96c43 | note | Testing Quantity Required (based from schedule qtys) - 2 Site Visits
003d1541-97df-5dc3-a7d8-de993e245182 | note | Verification Activity: Activity - HP
13c2d40f-2829-5c2d-9baa-ea1d2db5524d | note | Verification Activity: By - ENG
b5bf62b4-709a-4181-a9cc-50b8d374f80d | signoff | AUTHORITY HOLDPOINT
1dc6fac6-cdb0-4228-8742-aa9bbda07735 | checkpoint | 5.1.3 - Concrete Infill
70aa42b0-a405-579a-8b97-bb71fc4e8c22 | note | Detail - Pile Shaft to be filled with 40Mpa Concrete
a1ef2fb2-05f5-5dc5-ac99-9381f9da6151 | note | Acceptance / Conformance Criteria - Pile Shaft to be filled with 40Mpa Concrete
23d433c1-548b-5c7f-90d3-dc535b1ad0e9 | note | Standard / Specification - AoS Design Report
14018413-2a0a-549b-a133-20352373b496 | note | Verifying Document - Concrete Delivery Docket
4393bc56-23e5-5971-97e1-d241c5eab81c | note | Testing Quantity Required (based from schedule qtys) - Post Construction
2018bac9-2f24-5428-b42b-88869519a05d | note | Verification Activity: Activity - R
c85d3efa-37a6-54c3-84c2-94b5097c4df8 | note | Verification Activity: By - SE
078aad9f-fd51-4cb2-8052-c74590fc3c8c | checkpoint | 5.1.4 - Top Plate Install
c5a71cc6-fb5f-5b28-890d-fadf6683fbc4 | note | Detail - The bearing plate will be lowered over the top of the screw pile to its design height (200mm from base of abutment/wingwall cap). Once at height it will be tack welded in position. Bearing plate and stiffening ring to then be welded using a partial penetration butt weld.
8f10f110-43a5-5c36-a86b-50c3bd0f2127 | note | Acceptance / Conformance Criteria - Site Inspection
41da61b2-8635-57b3-9488-deaf2ef00eb3 | note | Standard / Specification - AoS Design Report
d0abbaa9-43bc-5684-8108-29969adf0310 | note | Verifying Document - Site Inspection
c2610756-e82e-547f-b7a0-95880b1bcb7c | note | Testing Quantity Required (based from schedule qtys) - Post construction
0a08fedc-79eb-5527-91e6-150a9d8a4260 | note | Verification Activity: Activity - HP
00e060e2-f8c8-5452-9824-ea3be92b7b33 | note | Verification Activity: By - SE
6138b92e-aef3-496c-bc87-b61ea9701ba8 | signoff | AUTHORITY HOLDPOINT
92201a53-f4a8-456d-958c-3fa3327645e3 | checkpoint | 5.2.1 - Pre Pour Inspection
d2958012-dfde-59db-b995-5de548096dc7 | note | Detail - Pre Pour inspection to check:
1b2ee065-f35d-5c71-af26-a16a2083e87a | note | — Reinforcing
9e8b4052-da73-5917-8ff8-7e18133cfaa0 | note | — Moulds
a446e581-b2d1-5367-945e-f98363a45c85 | note | — Cover Spacer Blocks
4ec8d991-c394-5520-bf9a-d1a95791ba82 | note | Acceptance / Conformance Criteria - The Engineer shall be informed 8 hours prior to the casting of any unit, to allow the Engineer to attend the pre-casting plant to inspect before and during production of the units.
dfebef22-9c18-5eb6-89d5-8b0e3f25f16f | note | ○ Reinforcing shall be pre assembled wherever possible into rigid cages using a template or jig. Reinforcing shall be tied together with wire unless otherwise accepted by the Engineer
bf4f4635-38e4-55c3-adf9-bc57cc5cb6c7 | note | ○ Confirm correct type and location of cover block is used.
9bb8140d-0bd5-5e10-ad3c-ef0cc1816ac0 | note | Standard / Specification - PS 19.3.2, 19.4.3 & 19.12.3
6280fbfc-d06f-5cc0-bd5d-c3680cebe10b | note | Verifying Document - Pre pour inspection checklist, Manufacturer QA records
06ca04ab-132f-5c0b-ba80-55fe4d958721 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
1c825be8-7342-5f75-8115-221dbcb9ed16 | note | Verification Activity: Activity - HP
4e71a649-afa3-5b32-be7a-8ec2c75eae81 | note | Verification Activity: By - ENG
84bf072d-0f47-4312-86a8-b083160ce559 | signoff | AUTHORITY HOLDPOINT
a7888c56-3ad0-44c3-9ce4-bdf330f89196 | checkpoint | 5.2.2 - Concrete sampling and testing
ab4d725f-46fb-581b-bc1a-ef6cbdabe409 | note | Detail - Pre cast Methodology from Pre co to submit to Engineer and Compression Test Report
5f775cca-599f-5f18-8ef9-c48d296df4b4 | note | Acceptance / Conformance Criteria - For pours under 150m³: three standard cylinders shall be made for each 50m³ of concrete placed, or part thereof, for testing of 28 days compressive strength in an approved laboratory.
9b12f60b-84b1-5560-bd24-5c574b69db13 | note | Standard / Specification - PS 19.4.3
cafa9e89-2b7b-5487-8201-caa610cd7d14 | note | Verifying Document - Slump Test/ Compressive strength test Report at 28 days/Pre pour inspection checklist
36e41caa-b264-5b3f-af0f-a4f8c0298ccf | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
8f1cacee-e3fd-5638-a3df-03bae15c26d5 | note | Verification Activity: Activity - HP
ebc597f1-09f7-52f5-9a08-0f7c31a1e299 | note | Verification Activity: By - ENG
3ad9f916-b230-4359-ba0d-51ef50efa4c2 | signoff | AUTHORITY HOLDPOINT
6a8ca925-849f-4ea0-b7dd-19bd27f12a5d | checkpoint | 5.2.3 - Post Pour inspections
047e726b-254d-5808-979d-15edb091024b | note | Detail - Post Pour inspection
ca1b86d1-5ef9-5c33-ba8a-867349013bc2 | note | Acceptance / Conformance Criteria - Following the concrete pour and stripping out form works: the concrete shall be inspected for Size, Shape, Features, inserts, reliefs, and Finish against the drawings.
0631d7f6-5b99-5593-b686-14d6a141b081 | note | Standard / Specification - PS 19.3.1
69b2567f-670d-5301-a0dc-30e32439d82e | note | Verifying Document - Visual Inspection / Post pour checklist
454f346d-67ac-5fa7-9261-76d190310fa5 | note | Testing Quantity Required (based from schedule qtys) - Each Pour
2328fd34-2780-5c67-ab2b-c9180dfea70b | note | Verification Activity: Activity - I
ed627049-f146-56ab-94a8-caf8c6dbe8c1 | note | Verification Activity: By - ENG
5928ad52-a052-4687-a596-37f23fbabd6c | checkpoint | 5.3.1 - Forms and Moulds
7a956c78-651b-5b3f-906d-3fa013cd7f58 | note | Detail - Tolerance on the placement of internal forms and moulds shall be +-5mm
cc0b6cfa-1e44-5a88-bc44-88f37a104581 | note | Acceptance / Conformance Criteria - Moulds shall be rigid accurately formed and of sufficient strength and stiffness to prevent distortion under vibration.
a920e5a5-0829-5ea3-aafe-b8d769e52446 | note | Standard / Specification - PS 19.12.5
8e7843da-b152-534a-ae08-07a885999539 | note | Verifying Document - Manufacturer QA records
f5fbf86c-1ae0-536c-a46e-b55616b1eb6b | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
e4181dd7-ba11-51c8-9a41-6d892a7d9360 | note | Verification Activity: Activity - I
68606d61-ecda-5367-bc4f-32d0006c53ff | note | Verification Activity: By - SE
c1fc09cc-d97d-4294-bdd3-216724442539 | checkpoint | 5.3.2 - Pre Pour Inspection
7f9d6c2f-4565-537f-9b5c-bbe6512618a2 | note | Detail - Pre Pour inspection to check:
e9c55fc3-1427-5523-a3f2-6eb8dce88ec7 | note | — Reinforcing
4659b308-c349-547a-8254-d06befdd3c6e | note | — Moulds
35bdeb0e-2b8b-560d-8f96-0c8da0efba09 | note | — Cover Spacer Blocks
d44fe543-9f72-5df6-894f-87a22418a811 | note | Acceptance / Conformance Criteria - The Engineer shall be informed 8 hours prior to the casting of any unit, to allow the Engineer to attend the pre-casting plant to inspect before and during production of the units. Pre pour inspection for 1st pour, there after every 3rd pour
e94da072-b456-5906-8493-dbc8f3e8b673 | note | ○ Reinforcing shall be pre assembled wherever possible into rigid cages using a template or jig. Reinforcing shall be tied together with wire unless otherwise accepted by the Engineer
6d2532a4-4244-59ed-8c6d-193ce0941616 | note | ○ Confirm correct type and location of cover block is used.
88a24498-9520-50e6-aa24-1e0650c37b00 | note | Standard / Specification - PS 19.3.2, 19.4.3 & 19.12.3
799995e9-aed3-5b62-85a7-15a024653f88 | note | Verifying Document - Pre pour inspection checklist, Manufacturer QA records
d1064926-c562-5abc-b4aa-1bcd00fef92a | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
5b5ae979-80ff-50cb-846c-62c4371fe385 | note | Verification Activity: Activity - HP
da45c694-bce9-58e6-b9a2-73ad882a39f7 | note | Verification Activity: By - ENG
a492f02f-3a33-4941-acf3-67c7eada17b4 | signoff | AUTHORITY HOLDPOINT
be9a1d3b-11bb-40b3-b8b4-2c07518852f1 | checkpoint | 5.3.3 - Concrete sampling and testing
e6e831d1-a5d7-5357-a03a-db6de4655845 | note | Detail - Pre cast Methodology from Pre co to submit to Engineer and Compression Test Report
8a998d98-792c-5be3-8f66-e500a65aa7a8 | note | Acceptance / Conformance Criteria - For pours under 150m³: three standard cylinders shall be made for each 50m³ of concrete placed, or part thereof, for testing of 28 days compressive strength in an approved laboratory.
86b7d350-54a2-5d72-a0b6-3dbb25cfd1a7 | note | ○ For repetitive precast underpass units with 6.42m3 each pours undertaken on a regular basis, three standard cylinders shall be made for each of the first five pours of any one type, and thereafter three standard cylinders shall be made for every fifth pour of that type for testing of 28 days compressive strength in an approved laboratory.
6794757f-1144-5049-84e6-6285927c0ef1 | note | Standard / Specification - PS 19.4.3
0a286742-071f-5d47-99f1-ee37db8396a7 | note | Verifying Document - Slump Test/ Compressive strength test Report at 28 days/Pre pour inspection checklist
e9a32069-4357-51dd-8f7d-e8d612fadc0e | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
977e863f-745f-5d95-9f58-dafcd6a76b7b | note | Verification Activity: Activity - HP
b6f3b3b2-c632-5d57-a0cb-18124850ed44 | note | Verification Activity: By - ENG
30efd315-fa97-4302-8dff-ea2ede4350e0 | signoff | AUTHORITY HOLDPOINT
cfe702dd-0046-454a-b9a8-dad0105f2921 | checkpoint | 5.3.4 - Post Pour inspections
265aef9d-097d-54e2-ab04-2117d6933ba6 | note | Detail - Post Pour inspection
9e6a1d3c-8c77-5358-8a26-af7f9e85c03a | note | Acceptance / Conformance Criteria - Following the concrete pour and stripping out form works: the concrete shall be inspected for Size, Shape, Features, inserts, reliefs, and Finish against the drawings.
12d33f0a-66f5-56be-b826-546359afe913 | note | Standard / Specification - PS 19.3.1
efcff6b4-fec3-59b1-9121-1d4b9d0ba143 | note | Verifying Document - Visual Inspection/ Post pour checklist
dffc12f6-e772-566f-a921-aa8177d51a93 | note | Testing Quantity Required (based from schedule qtys) - Each Pour
e309ff2a-44f6-551d-ab08-905734cfc092 | note | Verification Activity: Activity - HP
0d53c098-8010-5b60-b85c-b0e7abcff5b8 | note | Verification Activity: By - SE
85a73e6d-5bae-4757-a8b8-351456c675c3 | signoff | AUTHORITY HOLDPOINT
acfb3765-7deb-4afd-b7c5-3dc2188f8ae8 | checkpoint | 5.3.5 - Joint Sealing of Pre cast members
bc3f0d78-dddf-5d47-b354-53d3ccd5835b | note | Detail - Joint sealing of pre cast members
17e88322-80b2-5099-9062-5209def0dff2 | note | Acceptance / Conformance Criteria - Joints are to be sealed using a fuel resistant, multi-component polysulphide sealant designed for horizontal and vertical joints in concrete and is joint sealant pourable or gunning grade as appropriate.
43e1499f-e61f-5f47-9b05-cc3896766a81 | note | Standard / Specification - PS 19.12.6
d75d93c0-1629-5e7f-b66d-97fe2a16b916 | note | Verifying Document - Post installation inspection check list
d83eafff-93bf-5e67-b5a7-49d76fec1bd9 | note | Testing Quantity Required (based from schedule qtys) - After placing pre-cast units
3721e4a3-d55f-573e-a93d-5ba758a56eed | note | Verification Activity: Activity - I
e189b1e7-76dc-5248-b5d6-63d627e54f3d | note | Verification Activity: By - SE
2fee44f1-4b18-4883-8419-1f874802eecd | section | SECTION 6 - BACKFILLING WITH IMORTED STRUCTURAL FILL MATERIAL
8e7cfc9f-6528-42af-8d5e-b7c11d453039 | checkpoint | 6.1 - Backfilling of Gas main protection structure with imported hard fill
f0a7f7fc-161c-56ad-8e95-ef1a612fc907 | note | Detail - The backfilling on top of gas main protection structure to meet the earthwork specification and testing requirements. Compaction-Clegg Hammer
c9ea5169-d6fe-5702-8aca-3a89f42cbe93 | note | Acceptance / Conformance Criteria - Structural Fill
4a645952-77d5-5779-8af2-384452d7f6d7 | note | — Min CIV 18
edd2196a-ed1b-5ea0-918a-cc900d450033 | note | — Ave CIV 20
eb302cb2-7c01-53de-8dbf-a19206a9c4af | note | ○ Non-Structural Fill
df032376-1447-53f7-bfa2-cc66c6d7a741 | note | — Min CIV 10
f7a4544f-e9d0-5628-ae5b-a0d0a374c07b | note | — Max CIV 12
0c054f4a-2878-5656-8d5d-c1664e1a5254 | note | Standard / Specification - Appendix XVIII
7e23b439-db32-5b3e-b684-5c7b57839d73 | note | Verifying Document - Clegg Hammer Report
7b877280-e6c5-549f-bb50-481eb2be3c36 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
457980c0-fc6d-56c2-9605-8befb4d561b5 | note | Verification Activity: Activity - I
3e85ef6d-6fc9-58ea-a4e1-164dafb76de7 | note | Verification Activity: By - SE
def366e7-a456-439b-ab8b-d7baa66ef5e6 | checkpoint | 6.2 - Backfilling of Gas main protection structure with imported hard fill materials
06207c2d-2007-5957-8ad1-76d9136baa92 | note | Detail - The backfilling on top of gas main protection structure to meet the earthwork specification and testing requirements. Compaction-NDM
f3b0c01a-c0e0-5eb7-aaff-6261f1cde5e0 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
e4a4de02-737c-567e-a56f-ad9f1549a8af | note | — Min >92% of MDD
64eaa438-a8ff-5407-b996-52225b57bb57 | note | ○ Non Granular Material
cbf1721f-b48f-5f41-8b63-182be5d7248b | note | — Max Air Voids 8%
d5dcb0b5-c0a5-55ea-b67f-21e3a9165e70 | note | Standard / Specification - Appendix XVIII
ca2735e2-6440-50f7-8d6c-3ffb16ff7e36 | note | Verifying Document - IANZ Accredited Report
9343f1c7-b391-518e-9b6c-56085faf50c9 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
6b4715f7-e9f2-5ddd-bd9c-0fef44ebb450 | note | Verification Activity: Activity - I
78f726d2-0a2c-55ef-b295-6ad998d08ca1 | note | Verification Activity: By - SE
c3ac5bb0-1529-4403-b649-7d04fc062a46 | section | SECTION 7 - AS-BUILTS/ REDPEN MARKUPS
4fdf7d49-e8c5-4006-81e8-2bb437a1edfc | checkpoint | 7.1 - As-Builts/ Red pen markup
9e1bdc75-dbd5-5925-8261-40e07d65517a | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
1fbebef9-3d20-5a3e-9920-56919a4e6d1f | note | Acceptance / Conformance Criteria - As built drawing red pen markups
36b48a41-1896-56a9-b301-fc72fc6b990f | note | Standard / Specification - PS 16.7.6
10611cd3-b4cf-5659-bbf5-eafb6b44af2a | note | Verifying Document - Red pen markups
98099b17-dd13-5d8c-8a63-95b6df531796 | note | Testing Quantity Required (based from schedule qtys) - During construction
7e869bc5-317b-5cc4-aebe-cf344c865a1d | note | Verification Activity: Activity - D
a13a9762-e4ba-53a8-9703-0544ad042122 | note | Verification Activity: By - SE
665d94d3-f08b-4c49-a0a2-e6fb02752456 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
5bc8728d-9199-5d04-81f5-e30dab1eb8bf | textbox | Contractor's Rep Name:
b6364fb5-f2e2-5f4c-a0e6-e500bd19626d | textbox | Engineer's Rep. Name:
711e1d73-183c-52b0-9fdf-6ce046f4d26a | date | Date:
f24e1c5d-6129-4eb0-9b65-8f6dafc1a483 | signoff | Add Signature
34f9d7c8-49ba-48d2-925d-9f33b2cd0ec2 | checklist | DN1210-019 ITP Traffic signals Rev 0 | itp | DN1210-019 ITP Traffic signals
23ee718f-f009-4990-89d1-82e56e4bdc29 | section | SECTION 3 – MATERIAL, PERSONEL & THIRD PARTY APPROVALS
45852fb8-132e-4f35-9d69-7037e040d08e | checkpoint | 3.1.1 - Underground Services
bd7e22a9-707a-5e3b-8575-6c0c6f9a6274 | note | Detail - Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage.
0f2797f9-18b0-54ed-ad20-2c279d9d85c1 | note | Acceptance / Conformance Criteria - All underground services marked on site before pot holing or excavation
19f3fc4d-2547-52ce-87a2-8a3463416b47 | note | Standard / Specification - PS23.5.3 b)
1013309e-a1bd-5c7d-b94d-8e4ef5b6d724 | note | Verifying Document - Survey Data/Site Photos
d747511a-1c52-5d31-bfd0-4a8b82725f8e | note | Testing Quantity Required (based from schedule qtys) - Pre Excavation
ec8b5a3c-6b33-5be7-9a75-3b2cff9789a1 | note | Verification Activity: Activity - H
e5cad257-30e4-5305-847c-2babcae35ca8 | note | Verification Activity: By - PE/SE
c5b0b8e4-990d-4da4-801f-98f6c383fa18 | checkpoint | 3.1.2 - Ducting and Cabling Route
f4667313-ced5-5d1d-9a17-b92ec5c01639 | note | Detail - Confirm on site the exact location of cabling routes before trenching.
7206a939-1611-5361-8e9c-63a8f7c5c5f5 | note | ○ Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system.
f1d5d829-45f5-59e2-b5b3-1e03daa6da0e | note | Acceptance / Conformance Criteria - Markings match design drawings
ad796f50-bfbb-59df-a67b-e2d287ec8415 | note | Standard / Specification - PS 23.1.5 p) & 23.5.3 a)
63239c8b-5cfc-5159-821e-7680a019c8c4 | note | Verifying Document - Survey data/Comms with Client
6c2c38e8-a2ed-5b3f-b73a-ab0712a88c7b | note | Testing Quantity Required (based from schedule qtys) - Prior to Installation
a9d7f37b-affe-5895-81b1-257fd8ac693a | note | Verification Activity: Activity - H
a7036b81-36e5-56d0-8713-19ee775799f7 | note | Verification Activity: By - PE
06f5753b-b11d-4e94-b998-4e96f240d6d6 | checkpoint | 3.1.3 - Location of Signal Poles, Cameras, Cable Pits
8bacb124-2c09-5f5b-a75a-6e5d589e919c | note | Detail - Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation.
b851e114-87fe-57ac-b805-e1ae32085b2d | note | Acceptance / Conformance Criteria - Survey Records/Checks
7d91e937-dd6d-566b-a2ae-ebcccb8ba058 | note | Standard / Specification - 8287
5c567f28-df74-5e62-9ede-0310bece2491 | note | Verifying Document - Survey data/Comms with Client
a955f088-f28c-56b0-b3ca-54df7523c38a | note | Testing Quantity Required (based from schedule qtys) - Prior to Installation
ffbbd18f-425d-5660-b7e6-186254f2732c | note | Verification Activity: Activity - H
6b1a88e5-d3a8-5479-b807-f7d60d37412a | note | Verification Activity: By - PE/SE
6c49e182-7021-4277-b615-84f9b880b88e | checkpoint | 3.1.4 - Bedding and Overlay
3af010f7-1724-5387-90c9-e2c79ab9331d | note | Detail - Bedding and overlay material for the ducts will be coarse sand
1cacde88-91fe-5ded-a785-fcdd00d880cc | note | Acceptance / Conformance Criteria - Coarse Sand Visual Inspection
8c0568cf-5698-5bec-a3a2-bf3ae9e62cfc | note | Standard / Specification - PS23.11.8.a) ii-iii
f43d839a-d5ec-5bf2-8a1e-0895a6786fcc | note | Verifying Document - Coase Sand - PSD Report
5d2b4671-e730-54dc-b57b-bf31465e5c18 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
81f89811-2716-57f5-ac56-98358f1c8790 | note | Verification Activity: Activity - HP
d4841154-a930-557c-994d-bd3cff6a40f7 | note | Verification Activity: By - ENG
2688d1d8-870b-4114-bae5-c78f867bb772 | signoff | AUTHORITY HOLDPOINT
b0403297-2ff4-490a-83c2-42c7f3044200 | checkpoint | 3.1.5 - Backfilling of ducts, loops, cable pits
5b469c3c-09dc-58eb-9543-2ed0a94de3b8 | note | Detail - Under roads and paved areas: Coarse sand, controlled low strength material or fine crushed rock.
5e3552aa-b3c6-50a9-8d11-5779d2f76ce4 | note | ○ In topsoil areas: Complete the backfilling with topsoil for at least the top 50mm.
4eb1fa97-b874-59ed-a477-b38fa469b7cd | note | Acceptance / Conformance Criteria - Visual Inspection
a7aab036-b729-51ec-bbd7-0b08fe4f5283 | note | Standard / Specification - PS23.11.8.a) ii-iii
5a5e32ad-43d1-5a31-939d-8d51300cc4f0 | note | Verifying Document - Material data sheet and Engineers Approval
98719db6-572b-50b5-bd06-c1801f417170 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
335930c7-f276-57a9-8742-3a29affe99a8 | note | Verification Activity: Activity - HP
f19ff46f-fa1f-531f-99fb-ab908ce26b70 | note | Verification Activity: By - ENG
6da55b42-2595-4098-b8bf-f78364d8e0c1 | signoff | AUTHORITY HOLDPOINT
2aafc886-fd4a-416d-908f-300ff2e8526b | checkpoint | 3.1.6 - Ducts and Fittings
6aeec989-f642-52f6-9225-3835708636f1 | note | Detail - Use heavy duty HD PVC for underground services.
8fa284ca-8c16-530a-aa18-99b5c0ee9ef0 | note | ○ Use best practice PVC where possible.
d3d7c6bc-5f54-5bfd-b2b6-8c1bb5531b32 | note | ○ Orange colour for all conduits containing consumer mains, sub-mains or final sub-circuits cabling
0a3b0db4-588d-5fb3-9e90-ac97de009e71 | note | Acceptance / Conformance Criteria - All the materials meets the specification requirements and Engineers Approval
66036a98-c435-5f76-ab69-a09ded80fd1d | note | Standard / Specification - PS23.11.8.a) iv
57f1e26c-0584-588b-a9ae-dc5119503a6f | note | Verifying Document - Material data sheet and engineers approval
918e85d6-0671-557c-8f71-2d92ba2a6831 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
e82a8634-b1e4-5634-b43d-43bdef10b59b | note | Verification Activity: Activity - HP
1c3ddab7-0e06-53fc-a153-5a900732b021 | note | Verification Activity: By - ENG
387dc4cf-80b3-4069-92e9-28bccfc4604f | signoff | AUTHORITY HOLDPOINT
7efa8952-aa84-435d-b829-14064ad9d228 | checkpoint | 3.1.7 - Cable Pit
ce8f9fbc-4ea6-5f74-b7ad-2857e2f5e0b3 | note | Detail - Aco Cablemate Polycrete "type 66" Dimension: 665mm x 665mm x 620mm with heavy duty steel lid.
36a3a941-ac29-570a-ba3d-c481759a6cf0 | note | Acceptance / Conformance Criteria - All the materials meets the specification requirements and Engineers Approval
a06d1bec-2f0d-5ca8-ad9d-faa592f16f27 | note | Standard / Specification - PS 23.1.5 d) & Drawing 0122
6cdcd713-bf77-5cc4-98f6-70fa2f3f6e21 | note | Verifying Document - Material data sheet and engineers approval
c8906d4c-e0a6-5b3c-95b0-8d09c30ae7b7 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
126bbbcb-218e-5342-b519-a85f5532cbaa | note | Verification Activity: Activity - HP
1841c719-91f8-5c4c-8489-4ade35899a3b | note | Verification Activity: By - ENG
7e07693c-4d74-4fd8-8df1-8f824042d9a2 | signoff | AUTHORITY HOLDPOINT
46cfb142-283c-4b13-8153-56db8679cd77 | checkpoint | 3.1.8 - Signal Poles
6c1220c9-1d90-567b-8a3f-34f9992716f5 | note | Detail - The design requirements for all traffic poles shall be in accordance with AS/NZS 4677 with Design working life 50 years. Pole shall be finished internally and externally in accordance with AS/NZS 4680. Ready galvanized steel, Spray on galvanising or thermal zinc will not be accepted.
dcd2e82a-ed94-5dbc-b5f5-2624489109c6 | note | Acceptance / Conformance Criteria - All the materials meets the specification requirements and Engineers Approval
0ffe5d66-7286-5f4c-9a45-7598f56be0e1 | note | Standard / Specification - Section 24.2.1b (Project Specification PS ) NZTA P43
b630c04d-c561-5cd9-bb2e-c6c6d6e7f07c | note | Verifying Document - Material Data Sheets/Test Results/Eng approval
18ec32b2-d1ae-5082-b20b-f5ec4a7a0059 | note | Testing Quantity Required (based from schedule qtys) - 100% of critical materials
4766048a-de1c-55b2-bc6e-44e6d0caf934 | note | Verification Activity: Activity - C, W
e75df707-d20b-5dca-8a19-d6a42ba17c17 | note | Verification Activity: By - QE, PE
bd730177-8906-4305-a11a-7db265d590fa | checkpoint | 3.1.9 - Aspects/ Displays/Visor
6df6d0a5-0eeb-53c4-add7-1a54c3f56dac | note | Detail - All LED lanterns, visors, louvres and target boards shall comply with NZTA P43. In addition LED lanterns shall have an independent NZTA certified laboratory report confirming compliance with AS/NZS 2144. This must be supplied to the RCA traffic signal Engineer on request.
7f8524e2-3a3b-5705-9417-27776e6c4120 | note | Acceptance / Conformance Criteria - Materials meet specified quality standards
ab9fb50b-ced3-5987-8178-5721ee043767 | note | Standard / Specification - Section 24.2.1b (Project Specification PS ) NZTA P43
5803d945-18a8-5fa2-b15f-31b8cf69bb44 | note | Verifying Document - Lab report and confirmation from sub contractor
7e34afa4-f060-537e-9225-b291ac3d617a | note | Testing Quantity Required (based from schedule qtys) - 100% of critical materials
468fef0a-afbb-5837-9307-39366935be09 | note | Verification Activity: Activity - C, W
5721196d-1265-5894-89ba-7a306ec5871d | note | Verification Activity: By - QE, PE
5b36fee8-06a1-4025-ae4f-ad7646a0da20 | checkpoint | 3.1.10 - Cycle and Pedestrain push button assemblies
dabac0e1-a282-55c4-9cf7-e838c5305218 | note | Detail - Pedestrain push-button assemblies shall contain audio and tactile facilities and shall comply with AS 2353. in addition it requires 1. The call box with audible locating and walk signal 2. The audible locator shall incorporate ambient noise control 3. the tactile function shall be continually operational, however the audio signal should be able to be muted.
4cf3b5fe-0232-5e22-bc37-bc5536b3f355 | note | Acceptance / Conformance Criteria - Sub contractor's installation MS confirming Waka Kotahi P43 standards
013672c4-005c-57a5-9602-2871df16f828 | note | Standard / Specification - Section 24.3 (Project Specification PS)
3d5879a3-6846-53e3-89fd-8cc05ab8afe7 | note | Verifying Document - Installation MS
91513584-63f8-541f-9ade-c967927ae147 | note | Testing Quantity Required (based from schedule qtys) - Once
3c0c50bd-54ea-50ea-8c2e-afd2fef5a2c1 | note | Verification Activity: Activity - I
3cfe6c08-0f55-5772-9537-a3d2c46c180d | note | Verification Activity: By - PE
eeb98122-b662-4274-a354-5535725941ac | checkpoint | 3.1.11 - Signal lanterns
78cbb057-e433-52fd-bcbb-60f962f15387 | note | Detail - The technical requirements for traffic signal lanterns including cowls, visors, and louvres shall be as stipulated in AS/NZS 2144, including amendments as issued from time to time. The signal size of pedstrain and general purpose signals to be 200mm. The size of extended range signals as refered to in 3.3 of AS/NZS 2144 shall be 300mm
e34b55fe-817a-5b7a-bbc0-cba774ce7252 | note | Acceptance / Conformance Criteria - Sub contractor's installation MS confirming Waka Kotahi P43 standards
f2ceaa5f-7cdd-529e-a2d6-54815b9cf3a3 | note | Standard / Specification - Section 24.3 (Project Specification PS)
299c93e8-aa71-5e3b-8d8c-1eda0093f240 | note | Verifying Document - Installation MS
55c6d834-72b9-5e80-b747-772c07430ad8 | note | Testing Quantity Required (based from schedule qtys) - Once
d2a78b4d-164f-5c45-840b-059fcbf71985 | note | Verification Activity: Activity - I
aaa64be3-56d4-56e5-a0ab-7b3ee44854a0 | note | Verification Activity: By - PE
8990ab6a-8073-43a4-ba36-7573c65306a1 | checkpoint | 3.1.12 - Controller personality software
6d067580-456c-5931-bb01-032bcf39ec98 | note | Detail - In case Signal installer needs assistance from TCC
6c82d75a-cebd-5d66-9b5c-b1f34de1b5bc | note | Acceptance / Conformance Criteria - Discussion and agreement with TCC
5ce6d735-70f5-5fe5-83b3-ce779c55a151 | note | Standard / Specification - Section 24.2.1 (Project Specification PS)
246ab632-3be9-56ff-b190-25ba984c8c0b | note | Verifying Document - Meeting and agreements
8f208bde-8b0c-51fa-9ff3-8d564351fcf1 | note | Testing Quantity Required (based from schedule qtys) - Once
5469e533-1aaf-5471-8624-96174b14c8fa | note | Verification Activity: Activity - R
edf3cb25-6537-5d08-85e3-ce402fdf1c3a | note | Verification Activity: By - QE, PE, ENG
c7f8a570-33f4-42ea-bcf8-8432e848534b | checkpoint | 3.2.1 - Delivery of Materials
141bcb2f-7df8-564a-9685-aa290b25e289 | note | Detail - Ensure materials are delivered as per project schedule and specifications meeting P43
0bcbd142-3274-524e-be12-05a792685587 | note | Acceptance / Conformance Criteria - Materials delivered in good condition, within specified timelines
7d197a91-3aba-5f8c-87f0-af319ff79028 | note | Standard / Specification - Section 24.4.1 (Project Specification PS)
a8a0e20f-92da-5d7c-87b9-521802be547a | note | Verifying Document - Delivery receipts, inspection records
6c86d78a-9f8f-57f8-bb25-d50b64086c95 | note | Testing Quantity Required (based from schedule qtys) - 100% of material deliveries
f55efdf2-5b60-5ac4-9178-e595d9f8e1b2 | note | Verification Activity: Activity - I
052f2ba7-e51c-5dad-b66a-840d20b80b71 | note | Verification Activity: By - SE, QE, SUP
9913d7fd-4330-4db3-ab8f-27c967c810c2 | checkpoint | 3.2.2 - Storage of Materials On-Site
b56519b9-1481-52fe-a861-e893b38986ff | note | Detail - Verify that materials are stored properly to prevent damage
9bb65996-b8ed-5c5a-a1e6-abb44d2c587e | note | Acceptance / Conformance Criteria - Materials stored according to safety and handling requirements
edf11133-8eca-5e6b-9806-f7172899f9d1 | note | Standard / Specification - Section 24.4.1 (Project Specification PS)
fc4f567f-9b6f-5e0e-9262-a05a09489196 | note | Verifying Document - Storage inspection reports
d564cb7a-58b1-5730-b935-3002d2c9feba | note | Testing Quantity Required (based from schedule qtys) - 100% of materials on-site
8ce29566-c1d6-534f-ba3a-0e65d98af27c | note | Verification Activity: Activity - I, V
5d0a7044-e977-5ea3-9b31-b35d5f748e0c | note | Verification Activity: By - SE, QE, SUP
dfa85078-6043-4df1-9803-7f96e9a2f475 | checkpoint | 3.2.3 - Joint Use Poles (JUSP and JUMA) Painting
d59b98d0-f3f0-52a9-b60e-60f528bae470 | note | Detail - Ensure that JUSP and JUMA poles are painted yellow as required
4460339e-8291-51d8-acaa-3d0c69172a33 | note | Acceptance / Conformance Criteria - Poles painted and installed as per project specifications
c0764753-cb5a-5423-a838-b8d1b004b8d2 | note | Standard / Specification - Section 24.2.1f (Project Specification PS)
8d816d53-1d47-5186-a0d3-a82682692397 | note | Verifying Document - Painting and installation inspection records
2c8cbf1e-c590-554c-b598-2534b21da483 | note | Testing Quantity Required (based from schedule qtys) - 100% of JUSP and JUMA poles
126abdb7-ec5e-5611-98b1-471c41c0a8f3 | note | Verification Activity: Activity - V, C
20b23fa5-27a7-5d1e-8297-8fdb69f43554 | note | Verification Activity: By - SE, QE, SUP
a70ad95e-8044-45dd-924b-328a80f17b5d | section | SECTION 4 – CONSTRUCTION ACTIVITY - DUCTING, CABLING PIT, CABLING ROUTE, SIGNAL POLES AND LANTERNS
4cd0224d-24ce-4eb3-963b-3fb72a9a1ff5 | checkpoint | 4.1 - Foundation & Bedding Compliance
f88f5c14-9b1b-5d4e-ae83-2a997047e662 | note | Detail - Keep trenches free of water
5a5f17da-abbd-5e4d-9baf-c7f2b825b9a8 | note | ○ No sharp projections, roots and other obstructions.
c6f4e7ec-71d3-526a-b8d3-0b542decdd97 | note | ○ Then bedding with sand for 50mm
237606e5-3fff-5b53-8bb7-fb2eae02ecc6 | note | Acceptance / Conformance Criteria - Visual Inspection: clean trenches, smooth trenches and bedding material placed
54fc614d-e0e4-508e-899d-76ae93d857f7 | note | Standard / Specification - PS23.11.8.a) ii
b1fc2cdb-6990-58b9-898f-71a29d2efb5d | note | Verifying Document - Photo/Visual Inspection
c09b4664-8551-5023-857e-3fedc560326e | note | Testing Quantity Required (based from schedule qtys) - Each excavation
2d97c481-b517-5db7-8d6a-8443a4e54508 | note | Verification Activity: Activity - V, C
4d943210-9b5e-55cf-a773-0f1400b1cee8 | note | Verification Activity: By - SE, SUP
af3ff14e-f4fb-4517-9e55-32a463a3acf2 | checkpoint | 4.2 - Ducting
535b6523-a5bc-5738-b153-6785ba24405a | note | Detail - Minimum 50mm separation from other conduits; Also follow separation requirements by utility operators when in shared trench.
fef0fad9-1408-55af-905b-0c78b04cd74c | note | ○ Depth as per drawing (survey data):
75257031-f97b-5a37-af5c-a10b3ef08b26 | note | — ≥900mm under Roadways, ≥600mm under Sidewalks/Berm;
901dd8e6-4b88-5fb9-bf22-dc96191e08dc | note | — Or Client Instruction on site.
7dc98d57-be6d-5184-a1fe-a19c00440654 | note | — Where services cross, install electrical conduit at the topmost
373ff247-7f5a-5c82-a9ed-4d6ec54bc568 | note | Acceptance / Conformance Criteria - Visual Inspection: 50mm separation from conduits, depth check as per specification
f13b8adc-7acf-5cb9-a06a-cbd8a76dab50 | note | Standard / Specification - PS23.11.8.a) v
16cecc7f-f22b-5966-9f32-0e1d3ed23b1f | note | Verifying Document - Photo/Visual Inspection/Comms
babe838f-326f-5717-85f5-b34159cd7dea | note | Testing Quantity Required (based from schedule qtys) - Each installation
ece87548-7684-5765-95b8-51e9e3988188 | note | Verification Activity: Activity - V, C
206e6876-eb73-5a1e-85e6-0eaaf4dae110 | note | Verification Activity: By - SE, SUP
1903c272-7fe6-4208-8f7c-d59ef1d2a7c1 | checkpoint | 4.3 - Sealing Ducts
ccd8d589-d20a-57b0-9fbc-1bcd913a804e | note | Detail - Seal buried entries of ducts and conduits using waterproof seals and/or conduit fittings.
3e9fc738-6741-529d-a474-d183b70ee9ec | note | ○ Seal spare ducts and conduits immediately after installation and seal other ducts and conduits after cable installation.
645757be-e3b6-5581-b02b-3fa71c924b9b | note | Acceptance / Conformance Criteria - Visual Inspection: checks for waterproof seals
536d0779-cad3-59cf-b568-6264c32d5c3d | note | Standard / Specification - PS23.11.8.a) vi
bd665131-145a-5177-8570-cd97705083f3 | note | Verifying Document - Photo/Visual Inspection
01cd0889-94fd-5af0-9da6-bde5d69598db | note | Testing Quantity Required (based from schedule qtys) - Each installation
3fd9910a-744b-50aa-a957-141aa7ba2cb2 | note | Verification Activity: Activity - V, C
32166709-ca84-507a-ac40-696603bfd73f | note | Verification Activity: By - SE, SUP
9254ae22-45f7-405d-b357-a1b1483f1db2 | checkpoint | 4.4 - Backfilling
6141bffb-4e65-5970-9936-6d4d80284005 | note | Detail - Backfill trenches as soon as possible after approval of laid and bedded service.
bc7ac13f-e72d-54f2-a3de-60da498e3841 | note | ○ Place the backfill in layers < 150mm thick and compact to the density which applies to the location of the trenches to minimize settlement.
97c0a4ce-d01c-5cd5-8c1b-43cd8d5f2c3c | note | — Under maintenance pad, Clegg test will be used, with target CIV 25 for GAP65.
6ece739d-ba75-537a-bde9-138f97895590 | note | — Under berm area, no test needed on topsoil.
ec27a4d2-7a13-580a-993e-5efef5cab86b | note | Acceptance / Conformance Criteria - Visual Inspection: checks for specified materials for backfilling
85142c73-4bfc-5eca-b160-e2ccaa3e8151 | note | Standard / Specification - PS23.11.8.a) iii
f3fc3e3d-d6fa-5407-98af-ff3a8d4f28d0 | note | Verifying Document - Photo/Visual Inspection/Compaction result when under Road or paved areas
c68f0817-f98e-5e14-a38b-124ff973ea52 | note | Testing Quantity Required (based from schedule qtys) - Each installation
6180b06a-2fbb-5705-885a-55c146af43bd | note | Verification Activity: Activity - M
e8d4e7f5-ce4f-5cde-b30d-0293082f1c99 | note | Verification Activity: By - SE
a1735f46-4cab-4409-9c2a-8d9129634bfd | checkpoint | 4.5 - Cable Pit
281e51f2-27c0-5995-8824-763550730bc0 | note | Detail - Install cable pits as detailed on the drawings.
f8008515-d93c-5022-aacb-09075f5675b2 | note | Acceptance / Conformance Criteria - Visual Inspection: checks for specified cable pit location as per dwg
8aabd475-904a-5e42-b7f9-7c72981e76d5 | note | Standard / Specification - PS 23.1.5 d)
ccb84f17-2d61-5829-a0ce-30e623907b75 | note | Verifying Document - Comms with WSP/ Photo/Visual Inspection
87fddfd5-46fa-5095-b92c-da191adea48b | note | Testing Quantity Required (based from schedule qtys) - Each installation
c39cf6ee-ba9b-5e18-9d6b-356fcd502434 | note | Verification Activity: Activity - W
8a8b7da7-3cac-5bed-ae20-2ac82019fda4 | note | Verification Activity: By - ENG
c6eba7a8-3255-43a6-b919-ef8fd77f0b1b | checkpoint | 4.6 - Installation of Poles and Lanterns
a9f1bde3-35a1-547c-9410-cb45ee1c3e96 | note | Detail - Verify correct installation of all poles and lanterns. All lantern mounting barckets,bolts,nuts and mounting hardware shall comply with section 3 of AS2339, all lower lantern nut and bolt assemblies shall be installed complete with a locking mechanism.
1df62f41-eec2-59e2-a8c4-7a9cceeeda05 | note | Acceptance / Conformance Criteria - Installed per design, stable, operational, as per Waka Kotahi P43
16a6a3ad-110c-509e-872c-da8d81d26153 | note | Standard / Specification - Section 24.3.1 (Project Specification PS)
3d90b20a-3f19-5d31-acd9-5d3256b10583 | note | Verifying Document - Installation checklists, as-built drawings
e7920921-c5b9-5849-af80-4d395c83cd43 | note | Testing Quantity Required (based from schedule qtys) - 100% of installations
3044034f-fe31-590b-b870-238273b5997d | note | Verification Activity: Activity - I, W
b27d0c17-2261-5f5f-aa08-a70b56608857 | note | Verification Activity: By - SE, QE, SUP
16a02995-92cc-40a5-9def-6e67ea238bbc | checkpoint | 4.7 - Ducting and Access Chambers Installation
3571c382-0fe8-53a6-954c-57e619d06cf8 | note | Detail - Ensure correct trenching, duct laying, backfilling, and reinstatement
45ab2942-6a6b-5edb-a3d2-9fd29df7670d | note | Acceptance / Conformance Criteria - Ducting installed as per design, trench reinstated properly
5b909b16-61da-59f5-8717-91899c87c64e | note | Standard / Specification - Section 24.3.2 (Project Specification PS 1)
d9ca1ae7-2c83-53c2-8a10-4eee4970019c | note | Verifying Document - Duct installation logs, inspection reports
18b5cacf-1727-595e-94ca-e873a3715c53 | note | Testing Quantity Required (based from schedule qtys) - 100% of ducts and access chambers
6dd4d662-7231-5f5a-b16e-52e5cf6f1a60 | note | Verification Activity: Activity - I, C
ca9a6421-7ae4-5146-bca3-319d574e7c0a | note | Verification Activity: By - SE, SUP
c47423f0-7496-4ab6-b179-6d3058dcefe9 | checkpoint | 4.8 - CCTV and ANPR Camera Installation
0a35a74e-fa4c-51e8-a6e1-0822d51fe6de | note | Detail - Verify correct installation and operation of CCTV and ANPR cameras
eb8299af-6bf4-5dc1-bc6d-53da60702a08 | note | Acceptance / Conformance Criteria - Cameras operational, meeting field of view and accuracy requirements
4211b8bd-5473-5d2d-a160-e0cb897e3fe6 | note | Standard / Specification - Section 24.4 (Project Specification PS)
b8230a9c-73b5-58f2-9689-2f196c35e966 | note | Verifying Document - CCTV & ANPR installation checklists, test results
e93f9ce1-8539-5a80-89ee-3e29cb034ec2 | note | Testing Quantity Required (based from schedule qtys) - 100% of camera installations
4a6fa814-90c2-5bc5-92b5-30c0b9a64a32 | note | Verification Activity: Activity - I, W
dad92e07-836c-5f60-b0e2-bf19172f8294 | note | Verification Activity: By - SE
0450f6a0-6930-4b40-8ab4-38261d1265f2 | checkpoint | 4.9 - Signal Controller Installation & Testing
e9a7ad54-5bdc-5ab6-9087-3ba87a5f84ae | note | Detail - Conduct pre-commissioning checks on signal controllers
1090773a-9d17-58bf-96cb-3a82be4c5153 | note | Acceptance / Conformance Criteria - Controllers installed and operational, tested successfully
df77582f-028a-564e-ae00-1b4d96244247 | note | Standard / Specification - Section 24.7.2 (Project Specification PS 1)
6eb27a71-afca-536e-aee8-fe0fb33ad2d9 | note | Verifying Document - Pre-commissioning reports, bench test results
2ad05974-8d06-502a-ac0d-239b99f8b9ef | note | Testing Quantity Required (based from schedule qtys) - 100% of controller installations
35361c9b-df35-52f6-9202-599471e853f7 | note | Verification Activity: Activity - C, W
08f2ad29-e392-55cd-926c-ce284baba8b6 | note | Verification Activity: By - ENG, SE
b1c0cbae-0ca1-48a5-8a7d-c416f1f5ec62 | checkpoint | 4.10 - CCTV Camera Field of View Verification
cb03fd5b-17b0-5fee-9779-b1e6c178c969 | note | Detail - Verify CCTV field of view before foundation construction
7d5a90a5-397e-5706-b74e-5dfdc8fd4085 | note | Acceptance / Conformance Criteria - Field of view meets design requirements, photos taken from proposed camera height
dbfcd3d7-e1bb-5a1c-973f-921343a5543f | note | Standard / Specification - Section 24.4.1 (Project Specification PS)
3c02f225-105f-55fc-a147-4d755af4751d | note | Verifying Document - Field of view verification reports, site photos
f897e0f3-5a14-58e0-9351-dd42ce43a010 | note | Testing Quantity Required (based from schedule qtys) - 100% of CCTV installation
2ecdcaf2-9537-5647-9783-beab503c99c3 | note | Verification Activity: Activity - I, H
a80efaf5-d66f-50bd-9f50-97f348dc9a62 | note | Verification Activity: By - SPEC, ENG, SE
0c651bff-5df7-4183-831a-5674f145dc70 | section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
e5c7ca13-f18e-486e-9e43-fbf2df7c6eee | checkpoint | 5.1 - Final Inspection and Audit
4e89449d-906e-5135-8eb0-65e2ab2018ae | note | Detail - Conduct final inspection and audit of all installations
f8eb6ae2-f000-5e55-8964-e77b977c2157 | note | Acceptance / Conformance Criteria -
cf6d0925-c594-53d1-a1a7-192e57625a3a | note | Standard / Specification - Section 24.7.4 (Project Specification PS)
26f872c8-3157-57bc-97e8-c2539a8aec71 | note | Verifying Document - Final inspection reports, Certificate of Electrical Compliance
1a8a6cef-d5fe-5e79-9ffa-9861e2b01dcb | note | Testing Quantity Required (based from schedule qtys) - 100% of installations
9c8e0aa2-4e6b-5a3b-8803-31925d9597c0 | note | Verification Activity: Activity - R, HP
612b3c2f-5a3f-55bc-b27b-54c79b8675ad | note | Verification Activity: By - ENG, SE, CR, QM
4f757029-a79a-46c8-a658-20ffb1db1bc8 | signoff | AUTHORITY HOLDPOINT
fddf058c-8951-4f8f-8375-f42f9fc4e0a6 | checkpoint | 5.2 - Final Inspection and Commissioning of Traffic Signals & ITS: Electrical Certificate of Compliance (CoC) and record of inspection Electrical Safety Certificate(ESC)
4b4dec99-64cb-5cc6-8906-14f90c32e75e | note | Detail - Conduct final inspection and audit of all installations;
4d71439f-995f-5c9d-8830-354f5746cae6 | note | ○ Ensure signals and ITS equipment are fully operational and integrated with SCATS
d7fe6f4b-468e-5a7d-84e3-1155066c4924 | note | Acceptance / Conformance Criteria - Installation meets all design and safety standards;
049627c9-64ee-5fdf-b7ff-c1a9113b354d | note | ○ Fully operational, integrated with SCATS, accepted by Waka Kotahi/TCC
3f502ea9-f3ca-56a1-bebd-752edef68194 | note | Standard / Specification - Section 24.7.4 & 24.7.5 (Project Specification PS) ITS-01-010-202008-STD-DUCT
9e1d834b-cc33-5133-ab87-8c4b46cba690 | note | Verifying Document - Certificate of Electrical Compliance;
7a82f4e5-6d88-5978-8eb8-25ab0c350199 | note | ○ Commissioning reports, SCATS integration logs
51710168-750a-5f39-a6ca-454b6753596d | note | Testing Quantity Required (based from schedule qtys) - 100% of signals and ITS installations
46008caa-99fb-5005-bfa7-b20682bff6a8 | note | Verification Activity: Activity - R, HP
794877ad-87f7-50a8-bf32-76be9c1c6c11 | note | Verification Activity: By - SPEC, ENG, SE
cf32f4b4-959e-4191-8f14-596169a128f3 | signoff | AUTHORITY HOLDPOINT
9be94bdb-d246-4034-9eb8-61ca15237485 | checkpoint | 5.3 - Handover Documentation
c30da3e7-ea20-513d-94c2-fa99ce6b1ab1 | note | Detail - Submit all required as-built documents and records
6abfef99-8a4c-5ac3-8d75-4df610728d7b | note | Acceptance / Conformance Criteria - Documents complete, accurate, submitted as per schedule
0f7ba529-3272-513e-b57a-93ca056342d5 | note | Standard / Specification - Section 24.7.6 (Project Specification PS)
d1042bd8-8dcc-59be-be52-f15aa8bdcf0a | note | Verifying Document - As-built drawings, system schematics, manuals
3b1a808a-f8d9-529d-b7fe-34dc7828b891 | note | Testing Quantity Required (based from schedule qtys) - 100% of system component
7835cb52-fef2-56f4-a6f4-d2dbb25ed928 | note | Verification Activity: Activity - R, HP
613543aa-22ff-5b2f-9776-7a45a4a155b2 | note | Verification Activity: By - PM, ENG, QM
7214c438-8765-4a5c-85e2-4d846d405139 | signoff | AUTHORITY HOLDPOINT
737a7471-9bc3-4e25-b586-25dfd332160b | checkpoint | 5.4 - Warranty and Maintenance Arrangements
4c3f49ea-5c4d-5126-9579-5793bcd05a24 | note | Detail - Establish warranty and maintenance protocols post-handover
27c5c413-9115-5201-861e-8ae793eb2708 | note | Acceptance / Conformance Criteria - Warranty and maintenance agreements in place, responsibilities defined
4e701006-26c5-543e-8768-5368a2d98b20 | note | Standard / Specification - Section 24.8.1,24.8.5 (Project Specification PS)
fdbd85ad-bfc9-529e-a106-e82e8fc86355 | note | Verifying Document - Warranty documentation, maintenance agreements
a34e879d-8a7c-5cb2-aed3-37629b540747 | note | Testing Quantity Required (based from schedule qtys) - 100% of installations covered
f49ad4f2-f522-59c7-9fbe-691aec8d94af | note | Verification Activity: Activity - R, W
c2d5d93b-5d56-59ff-93f8-5acfbe26360b | note | Verification Activity: By - ENG, PM, CR
d6db08ed-98a8-4e5c-ac67-06670b3f404e | checkpoint | 5.5 - Battery Backup Systems Testing
f33088ac-54b1-5ba7-871a-5a8a8bd6302e | note | Detail - Test battery backup systems for CCTV cameras
ef6c9e3f-c7b0-5e2e-a7fe-b55a03593ef4 | note | Acceptance / Conformance Criteria - Backup systems functional, providing images during power failure
2825392d-0468-5224-b109-dcaa51ef8cc4 | note | Standard / Specification - Section 24.4.1f (Project Specification PS)
2ad6982f-c86e-510c-b26c-eb26d50529f1 | note | Verifying Document - Battery backup test results, operational logs
ae1e21cf-fb6d-5a2a-88d0-9ab34689496f | note | Testing Quantity Required (based from schedule qtys) - 100% of CCTV installations
4a4367a0-ecd4-567d-a5e2-f6f46377719e | note | Verification Activity: Activity - I, C
0cc07610-e082-5494-8b02-cafc1bfa89f5 | note | Verification Activity: By - SPEC, ENG, QE
93035453-0b0c-4574-8694-a48545e0f236 | checkpoint | 5.6 - As built and RAMM Requirements
d983e04d-23be-5942-9183-bb0722f8ac1a | note | Detail - All ITS and signal equipment, including software shall be recorded in electronic format into the RAMM database. As built drawings are required in advance of the 80% walkovers prior to handover.
36c33a69-c08a-5277-9851-9cbd47b9c92c | note | Acceptance / Conformance Criteria - Final As built as per Waka Kotahi ITS specification Testing, commissioning and handover (ITS-10-01)
dbcbe14e-e65d-565b-9909-6ff8f9fae9e0 | note | Standard / Specification - Section 24.7.6 (Project Specification PS)
8b906636-8a52-53c9-9f0b-5f4e1d9deea5 | note | Verifying Document - As built reports
3fb6ef96-8243-5def-b403-6810fc919552 | note | Testing Quantity Required (based from schedule qtys) - 100% of CCTV and Signal installations
ef005b78-d300-5ed1-b704-0267438677d3 | note | Verification Activity: Activity - R, HP
75c2d2cf-d267-5717-9fa4-ddcabd92ab0b | note | Verification Activity: By - PM, ENG, QE
9c5565f6-424f-41b3-9720-3e4c98db5e31 | signoff | AUTHORITY HOLDPOINT
9680336b-d034-40eb-8aa4-dccfa1f80f14 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
e3af727a-dcbf-533a-8e4e-b603b2b23e41 | textbox | Contractor's Rep Name:
c49db5e1-36cd-52dc-9260-bfb101403122 | textbox | Engineer's Rep. Name:
dedfd772-4001-51a6-a34e-6ceaac47129a | date | Date:
ea6b01a2-9f25-4539-8c61-826b04f0533e | signoff | Add Signature
4fd5e986-db36-4e90-a338-c7d6f55ac51c | checklist | DN1210-020-001 ITP Kerb & Channel | itp | DN1210-020-001 ITP Kerb & Channel
0c8c6f82-2e9f-4692-9ac5-2b7e9c8e34cb | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
e6daf850-0de4-4c7c-8439-9f111b5921f9 | checkpoint | 3.1.1 - Crushing Resistance
fe9c9d3b-fe16-554b-9262-621494ab0e27 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
3a59e58a-abd0-590c-863e-2d833cad9b18 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of minimum of 100kN
f0fbfd8c-e6ab-5e21-9d87-a5b120d43366 | note | Standard / Specification - NZS4407:2015 Test 3.10
5cf202d9-cbb3-5cb1-8ab6-6c45a8262414 | note | Verifying Document - IANZ Accredited Report
900ca516-8685-5424-84f6-0c40bb353566 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
11300c42-b16a-5543-9c6f-9f4bf35e16e4 | note | ○ Results to Engineer 2 wks before importing
653dd3e9-33f7-5b92-8ef3-3bfd69e999a4 | note | Verification Activity: Activity - HP
09a41b47-f8fb-5320-bb0a-4109947acb65 | note | Verification Activity: By - ENG
8c056dcb-07b9-4bf6-bcb0-4d1751525de9 | signoff | AUTHORITY HOLDPOINT
3635f740-3ec0-478b-bd95-ccce79be368b | checkpoint | 3.1.2 - Weathering Resistance
37f53d1a-004c-5886-bacb-84417064e3c4 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
31847e01-5228-5e92-aec0-82e737046507 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
3b2300d7-7225-5656-a9c0-40fa5cfbdb65 | note | Standard / Specification - NZS4407:2015, Test 3.11
1cedcc4d-9e71-528b-b1bf-caa3f78aa872 | note | Verifying Document - IANZ Accredited Report
affcb6ff-46b3-5ef5-81f4-9c3595ac2c95 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
2d915f99-8563-5737-a6e6-9d44cd471a5a | note | ○ Results to Engineer 2 wks before importing
bddd146b-96a6-54fd-90b4-a0a8785c694e | note | Verification Activity: Activity - HP
17e2a53d-062d-5d4a-878c-3be732d2b3d8 | note | Verification Activity: By - ENG
9e37c1c0-1d6e-4b8e-97ce-f8612ff53ca3 | signoff | AUTHORITY HOLDPOINT
69cd36bf-d8af-43d0-aa0d-03c9a12ba9d4 | checkpoint | 3.1.3 - Particle Size Distribution
0b5975ca-dd29-5cc9-8ee3-72339b3ebb88 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
6e2d41be-7e9a-5682-b969-5cf65db2d639 | note | Acceptance / Conformance Criteria - Fitting within standard AP40 grading curve
f62fea29-cd16-572a-b65d-3df99a924ced | note | Standard / Specification - NZS4407:2015 Test 3.8.1
aa274350-c62a-550a-a2a6-332146a45baa | note | Verifying Document - IANZ Accredited Report
ce91096c-25d0-53da-9ccf-c2aea4d5b37f | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
663ed0bc-e0c6-50ad-80d2-b5e4c301411c | note | ○ 0-400 - 2 tests
8f30bb1f-73d9-53ca-a35c-4050662233de | note | ○ 400-1,500 - 3 tests
3e2a3206-0d55-5430-bd8d-5588f097db2a | note | ○ 1,500-4,000 - 4 tests
ee7385c9-97b2-5141-8fba-90b38a1909f6 | note | ○ >4,000 - 1 test for each additional 1,000m3
139e0ff4-1a4f-525c-8aba-e6ce608fdcd6 | note | – Results to Engineer 2 wks before importing
7b7dfcbf-8364-571f-be9d-16a2d7312142 | note | Verification Activity: Activity - HP
8fde49c1-4836-55e8-a91f-38d3d132ef94 | note | Verification Activity: By - ENG
b389de57-8a92-4e81-bd4f-2b35ab4c41ab | signoff | AUTHORITY HOLDPOINT
d850adc1-ca28-4c76-a66f-2c6058bdbe86 | section | SECTION 4 – KERB & CHANNEL PREPARATION - INCLUDED IN PAVEMENT ITP
458b59b3-5dc8-46fc-8bf2-7a807b0fd6dc | checkpoint | 4.1.1 - Pre-pour inspection
9755bf20-49b8-5721-8b06-b41adba87fef | note | Detail - Subcontractor string line to be checked by Site Engineer to ensure horizontal and vertical smooth transition and to ensure the channels flow towards the catchpits
33fdb29d-e2df-566e-8344-8e2f2b0460c6 | note | Acceptance / Conformance Criteria - Tolerances are
51be7d69-3396-5744-91e0-84158c538c45 | note | ○ +/-5 mm variance to vertical design setout
b3f77e95-eebe-5146-87e5-73f5a078da45 | note | ○ +/- 10mm variance to horizontal design setout
c32e70cd-6bd4-55f4-8ecc-46d77c20ae4f | note | ○ The deviation from a 4.0m straight edge shall not exceed 3.0mm.
82430e7d-ca05-5dec-9e26-af7dab0fdcdb | note | Standard / Specification - PS21.7.6
60d1d25d-afa0-551a-a860-e55620f0a864 | note | Verifying Document - Kerb construction record
5eb7e41d-96b4-57eb-b43f-6c948a57a88b | note | Testing Quantity Required (based from schedule qtys) - Before every pour
c06e007f-87b9-522b-b507-f7921b4e5bcf | note | Verification Activity: Activity - I
80611284-b782-538b-b4d0-ed687a89d98d | note | Verification Activity: By - SE
61583889-ff60-4d70-ace6-88048506e3c3 | checkpoint | 4.1.2 - Concrete
508927a4-0206-5bb7-8a76-8b9d5c98c93b | note | Detail - 17.5 Mpa Concrete
a6ec2ca8-b9ff-5d16-a6b2-cd16311bf0e6 | note | Acceptance / Conformance Criteria - Delivery Dockets
a89c499f-f350-560d-a865-408c59aa6616 | note | Standard / Specification - PS 26.7.3
ff160c9b-ff66-5bfd-b0b7-57495e6d663c | note | Verifying Document - Concrete Delivery dockets and concrete test results
7f78aea1-761e-5585-8c6d-5094378604a6 | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
83c2ef25-ec80-5103-9d65-3e77dfbaa01c | note | Verification Activity: Activity - I
42247d7d-2129-5705-bb72-d9a25983f524 | note | Verification Activity: By - SE
06314508-255d-407f-bcaf-c1bd4e6b44c5 | checkpoint | 4.1.3 - Control Joint
e1fe74aa-b47e-53fb-9c59-a99276b0e90d | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
cb47c201-dbba-5b9d-832d-6d47f1428e10 | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
051b6944-7eca-527f-9cd6-35243d7afd00 | note | Standard / Specification - PS 27.4.5
c9dda678-9220-5460-b2c6-58d1bc87d0d5 | note | Verifying Document - Post Pour Checksheet
1c2a46c3-3a74-5b26-bcbe-630939c044e0 | note | Testing Quantity Required (based from schedule qtys) - After pour
d384c3c2-53f3-510f-9150-208ba5e2b660 | note | Verification Activity: Activity - I
3da6e281-ce68-51a2-a061-a46b2a5cceba | note | Verification Activity: By - SE
e5d04f56-ce48-49bc-a87f-d05ff8f2e4ef | checkpoint | 4.1.4 - Final Finish
780256d8-db30-5cb0-82c7-b52424108445 | note | Detail - Slip form kerb and channel
cd03d3d7-4ea2-503b-90ee-e75fea89d35d | note | Acceptance / Conformance Criteria - Slip form kerb and channel
bcf8bc5c-a218-552a-a894-1a1650f3434b | note | Standard / Specification - PS 26.7.3
669d0b43-8c9c-58e2-bd5f-5891336d4183 | note | Verifying Document - Post Pour Checksheet
cfa21740-eada-57ed-b293-d8a464f04718 | note | Testing Quantity Required (based from schedule qtys) - After pour
e0aa7daf-ff83-5315-8f53-dc071d425427 | note | Verification Activity: Activity - I
42fd8519-32e2-5ede-80ed-845472b8bcdd | note | Verification Activity: By - SE
703f457c-49d2-480a-bbf7-26af5ea32494 | section | SECTION 5 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
12f9f48f-ccf7-4a28-ac8b-46ac2ce74fa1 | checkpoint | 5.1 - Final Inspection
46337664-cb68-5ea3-bf6f-f63b21bd5fe4 | note | Detail - Final inspection of all concrete work.
c298b2f2-696b-5c49-b594-e4ad975a1d5e | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
147cc2f9-fedb-54c6-8506-88cc9c394e18 | note | Standard / Specification - NZTA P39: 2013
be62610a-1221-58b1-a79e-34c19f9d4cc5 | note | Verifying Document - Final inspection report
84e161fe-ed72-5264-bdc9-e508d35de70f | note | Testing Quantity Required (based from schedule qtys) - 100% of works
270346be-0ac3-5660-8094-3653720ad5d9 | note | Verification Activity: Activity - HP
6ddcd574-d507-5609-b061-ddffe63ff56f | note | Verification Activity: By - ENG
295e872d-23f6-4f19-82f7-cd729a960a9c | signoff | AUTHORITY HOLDPOINT
9200ad16-aabd-4f51-855d-df164986a044 | checkpoint | 5.2 - As-Builts
90ce837b-56ec-5b21-9af8-1696ce1625e4 | note | Detail - Final inspection of all concrete work.
b368dbb0-3f98-559a-b157-d6adf58767c1 | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
52b2ec10-4947-5554-bbc4-031484719bbd | note | Standard / Specification - PS 16.7.6
00ce4584-e404-5950-89b5-cbf336e2c1b0 | note | Verifying Document - Redpen markups
715f47ba-c339-5891-886a-ae09fc60031d | note | Testing Quantity Required (based from schedule qtys) - Completion of works
4e271cda-52ad-5fcf-91e5-cc88e1b0a2b5 | note | Verification Activity: Activity - D
79eae1ca-5883-5d72-b4c3-1422a33d7c7a | note | Verification Activity: By - SV
1096c77c-a064-4e72-9ee0-5dc5ee7ec464 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
d14d904b-19df-57a1-bc2f-9c5cc1080f91 | textbox | Contractor's Rep Name:
618f7d6b-a1a6-52cb-88c8-f787041c7896 | textbox | Engineer's Rep. Name:
f20c5675-16c5-5bae-a7c9-303d39bfe8e3 | date | Date:
7c4e652c-861e-48b2-bb70-716fcc50a64b | signoff | Add Signature
c6f424fc-909f-44de-b081-cf32ac6b571a | checklist | DN1210-020-002 ITP Shared Paths, Maintenance Pads & Traffic Islands | itp | DN1210-020-002 ITP Shared Paths, Maintenance Pads & Traffic Islands
3692138c-96a8-459c-8137-a3fde6cb20e5 | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
1d798aca-fdad-4e86-b153-4b97527b189e | checkpoint | 1.1.1 - Crushing Resistance
4619ffca-54e6-54b8-ad78-7057dff4d671 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
b452037e-f520-5761-8879-46274e27ad44 | note | Acceptance / Conformance Criteria - >100KN
f35102fe-161d-51e2-9506-a3221361f5f8 | note | Standard / Specification - NZS4407:2015 Test 3.10
29dee9be-7e1f-56cf-8ab8-b1c4eccce982 | note | Verifying Document - IANZ Accredited Report
e0076496-c257-5222-a562-8775b50a0c16 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
6974cd1c-d4e3-5105-8364-e11871d78707 | note | ○ Results to Engineer 2 wks before importing
4fb930b4-ce93-5c53-971a-444d3fee86cf | note | Verification Activity: Activity - HP
18b1b6c4-1a84-5bc4-aa6e-3b924991d7cc | note | Verification Activity: By - ENG
92ad212a-2867-43ac-aee8-115d271e255b | signoff | AUTHORITY HOLDPOINT
40a8404a-40bc-4206-97ee-0b203424b7f0 | checkpoint | 1.1.2 - Soaked CBR
9853980c-2d99-5db8-8735-df9b8bcaab78 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
d02f45c2-8601-5ffc-92a3-22679fafcfa6 | note | Acceptance / Conformance Criteria - Minimum soaked CBR of 25%
889a02f5-f152-5ff3-b06c-2e434956e457 | note | Standard / Specification - NZS4407:2015 Test 3.15
6adecfa7-49e2-55d1-9b9d-efc6d9b3b481 | note | Verifying Document - IANZ Accredited Report
555fdc0e-519d-5eed-a3ff-86a5ec41e8fd | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e41c4a2f-bc3a-5ff1-b9ec-1e9b55844a2b | note | ○ Results to Engineer 2 wks before importing
0e549f2f-5479-5533-84de-c75f52da4f2a | note | Verification Activity: Activity - HP
d84e32af-f7d3-53ce-8ec5-70233a70d0cf | note | Verification Activity: By - ENG
14479391-3d0e-4a44-8f95-a7b8d9418671 | signoff | AUTHORITY HOLDPOINT
446204cd-6d95-426c-bad9-97450daf8a8d | checkpoint | 1.1.3 - Weathering Resistance
ec31ece6-a527-5e51-958e-99589149bdb9 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
4e330acd-6897-5de9-847f-ddae8d6d08b6 | note | Acceptance / Conformance Criteria - CA or better
659deeca-e1e5-549a-a1fb-93f139a59185 | note | Standard / Specification - NZS4407:2015, Test 3.11
3138626d-2f05-5282-895b-9560cb5de774 | note | Verifying Document - IANZ Accredited Report
8a147be7-026b-5297-a023-725029c91274 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
a11909c8-0560-5e76-a064-449f8dec7d02 | note | ○ Results to Engineer 2 wks before importing
bb2e041e-71f8-5511-8907-1f260698c9db | note | Verification Activity: Activity - HP
70361cab-e491-5ed4-a03a-3b9b13826177 | note | Verification Activity: By - ENG
176b05fa-a1c1-4970-ac82-4f463d595edd | signoff | AUTHORITY HOLDPOINT
157c3e23-df56-42af-ba87-77f2df86ef95 | checkpoint | 1.1.4 - Particle Size Distribution
f35baf9d-ab72-5eaa-a7a3-cde2a8ba107d | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
e87bab87-458f-5c24-9ea3-2932253304fe | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
ea0c62e4-c661-5748-a972-e7a90fce7a3c | note | 63.0mm ¦¦ 100% passing
6b839a4d-27a0-5a88-8cc0-9e2e77fcab74 | note | 37.5mm ¦¦ 68-90% passing
cd2f959a-939e-5541-9d53-4bee115caa12 | note | 19.0mm ¦¦ 42-76% passing
1d6d16b9-5168-5c87-84f1-dde78ea4e88d | note | 9.5mm ¦¦ 26-58% passing
195d4e69-ad2e-5cba-93fd-be70b137d1e3 | note | 4.75mm ¦¦ 16-44% passing
4a367762-8bc9-556a-92df-b987b5ef8604 | note | 2.36mm ¦¦ 10-33% passing
aa622ff9-8831-56c0-ae52-0b267cbf3cf7 | note | 1.18mm ¦¦ 6-24% passing
30fef4f0-1c59-5c81-9091-c436a436cdea | note | 0.425mm ¦¦ 3-14% passing
8f11645e-29c1-5b2b-80e5-786c2f0941ce | note | 0.075mm ¦¦ 1-6% passing
069af935-aab2-54c9-8250-24d84c3c11a7 | note | Standard / Specification - NZS4407:2015 Test 3.8.1
b93bc630-e854-50e5-8a98-ea4bbb78d93e | note | Verifying Document - IANZ Accredited Report
4ee0c1e9-7b41-5bf8-9952-8b284bf8f70e | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
2a12c00d-6b08-5df5-be6b-6590c923c0c7 | note | ○ 0-400 - 2 tests
7216a228-d978-5aaa-8e58-5807662ad023 | note | ○ 400-1,500 - 3 tests
9d0ed928-9884-596f-8921-b631f19eabdc | note | ○ 1,500-4,000 - 4 tests
4d715870-0375-5b30-8b98-9e7797e5a5ca | note | ○ >4,000 - 1 test for each additional 1,000m3
e6cd6c43-22ed-5c73-85ec-f554544d0ef7 | note | – Results to Engineer 2 wks before importing
5f1f1197-2ba0-57e8-ba1f-c78194678543 | note | Verification Activity: Activity - HP
e237bfa2-9b4f-5cb2-b9d9-4a51cbc7c9c9 | note | Verification Activity: By - ENG
611e525a-035b-4423-9783-7d7ffa82d113 | signoff | AUTHORITY HOLDPOINT
d3aeaca3-219c-4f56-b49f-543b79980418 | checkpoint | 1.1.5 - Maximum Dry Density and Optimum Water Content
05aee957-3d9f-5a5f-93a1-342337984bca | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
c2212c80-bb58-54f0-b097-adc12e0220a4 | note | Acceptance / Conformance Criteria - Report Value Only
0294e485-5d51-5bb3-b90e-0078389f38ff | note | Standard / Specification - NZS4402:1986 Test 4.1.2
83d02e8e-6e71-5f36-baa9-4cf6f58a2419 | note | Verifying Document - IANZ Accredited Report
91d50116-3cc7-5478-9e76-de81b9ee6366 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, PerSource
e05fb3a9-d0bc-5d5a-81f3-286b75451946 | note | Verification Activity: Activity - HP
a83da929-d0c9-5c46-b608-ac8390885ebf | note | Verification Activity: By - ENG
9a7aadd3-fced-4da6-a4b6-1c331ab19621 | signoff | AUTHORITY HOLDPOINT
a6c29d1f-b7b3-4020-8634-f4cb290ceeec | checkpoint | 1.1.6 - Sand Equivalent
a81b2c58-675b-51b0-a3e2-378e7079e0f6 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
1a473bd1-1d90-54a8-86a6-bbcf896f2b41 | note | Acceptance / Conformance Criteria - >25
f2518fbe-587d-5e2b-9e82-e7e585e35764 | note | Standard / Specification - NZS4407:2015 Test 3.6
429fb2a1-6ce9-5c05-a227-b3c2fe95baca | note | Verifying Document - IANZ Accredited Report
f9c2d81b-f1f8-5da2-9d1f-8588db1b2432 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
ffd30849-ee3e-58e7-b70b-e0796f04804e | note | ○ Results to Engineer 2 wks before importing
c627426e-4d5b-5cff-a4fb-d0b1c11379dc | note | Verification Activity: Activity - HP
3d321dc0-5b8b-5d00-917a-2c81ef684648 | note | Verification Activity: By - ENG
10455672-7420-48dc-a8de-f3e603e9af02 | signoff | AUTHORITY HOLDPOINT
e1818c7f-2325-49e9-879f-9222d3915201 | checkpoint | 1.1.7 - Clay Index
4e325b0c-98b5-5a94-8359-59916cce0e22 | note | Detail - NZS4407:2015, Test 3.5 - Clay Index Test Report
39fc1f67-8109-5688-bb77-6e61245b2b91 | note | Acceptance / Conformance Criteria - Report Value Only
f44f7475-ec5d-5cf2-a74e-866213ddd1bc | note | Standard / Specification - NZS4407:2015 Test 3.5
c57caaf5-709d-52dc-8bc1-6f61d526c5ea | note | Verifying Document - IANZ Accredited Report
b78c3984-ad13-5b02-8061-569d8917b8a5 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e38944a3-8620-5523-9ea7-0c5eb83e3e34 | note | ○ Results to Engineer 2 wksbefore importing
e9432655-35da-51aa-8779-337df359bcd7 | note | Verification Activity: Activity - HP
4f61f101-4647-5e56-8946-3c55ff124909 | note | Verification Activity: By - ENG
e60f74f9-a64b-44f8-ab66-665565d4023d | signoff | AUTHORITY HOLDPOINT
ffe1b2c7-0001-48e8-936a-db4a04de3537 | checkpoint | 1.2.1 - Crushing Resistance
5e7dc93a-4824-51e1-99a6-a9cd82332886 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
b46ee7e5-d30c-506a-849d-82ba29715575 | note | Acceptance / Conformance Criteria - >100KN Minimum
7b6475b9-420d-52d4-9bcf-3e7929c3a2ae | note | Standard / Specification - NZS4407:2015 Test 3.10
fcaba796-5a1f-5148-b085-de3b17d8b119 | note | Verifying Document - IANZ Accredited Report
b94a02dc-7a0a-548f-bbb7-db86e6f468df | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
f0d04de1-a3bc-57e2-b9d2-26587b36f315 | note | ○ Results to Engineer 2 wks before importing
d3dd315b-6b3a-5161-95c0-20bc3f0cac31 | note | Verification Activity: Activity - HP
5d852471-9bbd-5182-a444-25b96e4620e4 | note | Verification Activity: By - ENG
2814329d-7d6b-4fe0-b401-b5610814834e | signoff | AUTHORITY HOLDPOINT
a4610c5b-a104-4e08-a941-2b86dec9d654 | checkpoint | 1.2.2 - Soaked CBR
ff1e4bec-a4f2-508d-9798-40761dbba053 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
38c8f081-5a23-5a54-934e-9e7f62a5e22b | note | Acceptance / Conformance Criteria - Minimum soaked CBR of 25%
3f2f1842-76db-5d0f-95f7-d7fa176138f1 | note | Standard / Specification - NZS4407:2015 Test 3.15
4c772b43-8181-528f-90e0-d587cd82a2ce | note | Verifying Document - IANZ Accredited Report
309dfcdc-f3b4-5562-ba57-b2a892517ae2 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
33e75093-962c-52b0-9d3a-68dc18776f4d | note | ○ Results to Engineer 2 wks before importing
c457fe84-541f-54b2-98f6-401783664311 | note | Verification Activity: Activity - HP
66093549-d337-5499-b376-e3572c6163c0 | note | Verification Activity: By - ENG
25f40c6e-6bcf-4fc8-8862-1afe0c3167ad | signoff | AUTHORITY HOLDPOINT
1eb671c1-040f-4d95-b2c5-95c127788986 | checkpoint | 1.2.3 - Weathering Resistance
4b85dad2-41c5-52e0-be8c-1cff90a63335 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
c72690ee-63bd-5bbb-9c02-750a01675db7 | note | Acceptance / Conformance Criteria - CA or better
b7afbd6b-14c0-5697-828e-bef0324352d4 | note | Standard / Specification - NZS4407:2015, Test 3.11
fc02d181-afff-51f6-8cf5-3b18a3d1b893 | note | Verifying Document - IANZ Accredited Report
9dd9504e-c922-5549-bccd-f404925b34a5 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
1e440f1c-fea3-5987-bf79-df4f05d2c59f | note | ○ Results to Engineer 2 wks before importing
2f744791-197c-596f-b70e-ee0519510adc | note | Verification Activity: Activity - HP
e23e8a2d-925b-5f4c-8c16-f006adbdd4eb | note | Verification Activity: By - ENG
294246ed-2105-4481-b552-24a48cb79d6b | signoff | AUTHORITY HOLDPOINT
b6aa7bf4-5cec-4c53-86ab-b98cf15d9233 | checkpoint | 1.2.4 - Particle Size Distribution
c46a086e-3282-5b82-bd62-37eb9206a090 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
7b1b1431-d7a1-5d16-8392-708f9dd92c33 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
1b149671-6205-59e0-8815-8c0b74c5aa9d | note | 37.5mm ¦¦ 100% passing
32d15221-17a7-58c9-9d3d-f8e3342d54a7 | note | 19.0mm ¦¦ 60-75% passing
f020c1f5-6071-5b04-a113-57addbdb8146 | note | 9.5mm ¦¦ 37-50% passing
924ec757-1fd5-5dc2-ad38-7f0b9b4f0edc | note | 4.75mm ¦¦ 20-35% passing
b66b9463-1cb4-537c-a4e3-69b8344ef60d | note | 2.36mm ¦¦ 12-28% passing
fdef56a7-6395-599c-9a3f-07a80cb509f1 | note | 1.18mm ¦¦ 9-20% passing
0671285d-c948-52b2-923d-13ee68b9dd6b | note | 0.600mm ¦¦ 7-12% Passing
338390db-ee12-513f-9a31-6d417e099cbc | note | 0.300mm ¦¦ 3-10% Passing
1f0926f9-0b3b-54d3-86d0-f65a03c77c45 | note | 0.150mm ¦¦ 0-5% passing
bab1cc18-554a-518f-b779-eb5374751e73 | note | 0.075mm ¦¦ 0-5% passing
aa4d02d8-6614-5fd9-9b90-d5b97d8136a7 | note | Standard / Specification - NZS4407:2015 Test 3.8.1
bd474bdf-db10-5cb8-8aa2-4584859878b0 | note | Verifying Document - IANZ Accredited Report
f53d66db-3524-52b5-8b2b-f3005f33f7a9 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
007be748-b3f1-5c03-8371-db41237cf461 | note | ○ 0-400 - 2 tests
380da09a-952e-53db-9d86-b309e22dab32 | note | ○ 400-1,500 - 3 tests
3935c69e-cdd4-57af-8ba7-9a57e9b0d3cc | note | ○ 1,500-4,000 - 4 tests
343c0ada-d1d5-5c57-91b3-05cdb6998ed6 | note | ○ >4,000 - 1 test for each additional 1,000m3
ea7cc390-0392-5d68-82f9-617d5c86945b | note | – Results to Engineer 2 wks before importing
1cea707c-8a6f-51c5-b7c9-9c4cd54452e4 | note | Verification Activity: Activity - HP
96f8b471-f2b1-5bd0-a33e-2c501f255751 | note | Verification Activity: By - ENG
20f9fd2b-7871-4078-9249-4a9adfb7df0e | signoff | AUTHORITY HOLDPOINT
ad4dbcb7-0de3-4378-9c4f-20588dc0b0c1 | checkpoint | 1.2.5 - Maximum Dry Density and Optimum Water Content
e9bb2f0d-5017-51be-9952-8c7edc5c99d1 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
ad7e7154-36af-5c5b-aed3-8561a75d5e0c | note | Acceptance / Conformance Criteria - Report Value Only
ef43ea90-e924-57a7-a7df-18a6f4f6967e | note | Standard / Specification - NZS4402:1986 Test 4.1.2
b55c5a11-97e3-5df1-a3a2-c82bbce2358c | note | Verifying Document - IANZ Accredited Report
c3195efd-8b0c-54c5-83b3-7b830eabc093 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, PerSource
4c235328-72c5-5e6b-b548-aa7ed0461ca4 | note | Verification Activity: Activity - HP
162924dd-9ff8-5ac0-8a83-466ad8884bac | note | Verification Activity: By - ENG
47492c3d-f393-41d2-a938-5e63ff70446a | signoff | AUTHORITY HOLDPOINT
8c4e3130-446e-4bc6-a3b7-2dd9f233ae44 | checkpoint | 1.2.6 - Plasticity Index
5b4dc68a-b20f-5154-92ea-3e5ecfa17763 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration NZS4407:2015, Test 3.4 Plasticity Index
68f5eeaa-556a-5446-9a15-fbaaa80ae1f2 | note | Acceptance / Conformance Criteria - <30, <8
fd543870-4119-50a6-be9c-3385e791865d | note | Standard / Specification - NZS4407:2015, Test 3.2
2138a299-4e09-58e6-9e14-8c1c1c96000d | note | ○ NZS4407:2015, Test 3.3
2d6e9ce1-bdd8-5152-a90f-0b83d6975ca2 | note | ○ NZS4407:2015, Test 3.4
fb8af2da-af9c-50c2-aee9-20c88ea6e710 | note | Verifying Document - IANZ Accredited Report
73ab46f9-9b22-5d08-a992-70252be0c60e | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
0fd24aad-14e9-5fd3-8150-dc65c9975868 | note | ○ Results to Engineer 2 wks before importing
d0a53718-9f02-5102-893a-10847c633822 | note | Verification Activity: Activity - HP
7d57d8be-9e35-5ce3-9ae1-602d6695144d | note | Verification Activity: By - ENG
141c726a-6f81-4545-bc86-0d21c564cc07 | signoff | AUTHORITY HOLDPOINT
0c98d8a3-2021-445b-8e6a-b440fccea6f4 | checkpoint | 1.2.7 - Sand Equivalent
396ebefc-1d29-55e4-95c7-c7e8d26e0c3b | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
25ef6dde-90a9-5994-afc8-242121d9ea68 | note | Acceptance / Conformance Criteria - >40
a7523743-02ac-5d91-8566-5b99c0822dbe | note | Standard / Specification - NZS4407:2015 Test 3.6
71b7344c-bed7-5627-a12c-2d56e0b925a4 | note | Verifying Document - IANZ Accredited Report
d582f322-ff89-527e-8c91-ff41a828f611 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
af2a5601-d171-51fb-8379-60e958d16971 | note | ○ Results to Engineer 2 wks before importing
64824af7-dec2-50ec-a5bf-d46ef687d993 | note | Verification Activity: Activity - HP
775b506d-c95e-5d3b-acb9-c96d98a849cc | note | Verification Activity: By - ENG
fe1a3ec3-8abc-4c03-9e92-d8b39d4375bc | signoff | AUTHORITY HOLDPOINT
e914ec86-78af-421e-85f3-ba00d6e5c600 | checkpoint | 1.2.8 - Clay Index
f6a97e19-6b30-5c76-976c-c1230d8b495d | note | Detail - NZS4407:2015, Test 3.5 - Clay Index Test Report
d54a4ac6-f6f9-568a-98e9-27345cb65970 | note | Acceptance / Conformance Criteria - Report Value Only
e54ae1ea-415f-5822-861a-e0d6dea7a983 | note | Standard / Specification - NZS4407:2015 Test 3.5
24514cd7-54bf-5c91-b7c8-2ccbac49fd8f | note | Verifying Document - IANZ Accredited Report
4ee64f8c-d53b-59d9-afff-d0c7d977cdb4 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e6fcf953-07f2-5b06-b5db-647611b4c6d7 | note | ○ Results to Engineer 2 wksbefore importing
8f495c76-1b9d-5b13-a476-2d994820cd6e | note | Verification Activity: Activity - HP
5910c778-f748-5eb8-9100-4e970c557319 | note | Verification Activity: By - ENG
b4b07047-35b4-4add-b852-7de9c45eafef | signoff | AUTHORITY HOLDPOINT
a2faa7f3-880c-46ff-a254-7d53eab84aa4 | checkpoint | 1.3.1 - Crushing Resistance
f46681b8-c010-5b0a-9978-739965c04017 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
3a297d1b-aade-54ee-bc4c-49fbc9893d0a | note | Acceptance / Conformance Criteria - >100KN
f633c57d-78ee-5934-8078-ec3fa1537bd8 | note | Standard / Specification - NZS4407:2015 Test 3.10
ef1a9d21-e8e4-5ecf-bc34-3df5d6c69520 | note | Verifying Document - IANZ Accredited Report
45b85e40-472d-5fd0-bfa0-4e290acc339d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
4bd1cd7e-aa0b-559b-8808-27a1c17386ba | note | ○ Results to Engineer 2 wks before importing
1b78fff7-71c0-518e-bafa-86c36131623d | note | Verification Activity: Activity - HP
36232fe1-db21-5f97-bd51-b68a177193a0 | note | Verification Activity: By - ENG
28d508d2-ed0f-4223-83a5-a3fef9fc116b | signoff | AUTHORITY HOLDPOINT
10133793-6622-4c5e-9c80-6b897bd066c0 | checkpoint | 1.3.2 - Weathering Resistance
2d83bf39-680f-5413-acd2-2ca70dbbde4e | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
8691daea-bf86-59d6-8272-5cf69464aab1 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
5ecda9c3-9237-5c38-9a5b-2e260e99baca | note | Standard / Specification - NZS4407:2015, Test 3.11
0b4e787e-fc13-5d64-8469-2efe9b7b0473 | note | Verifying Document - IANZ Accredited Report
e143359a-bdd2-5fec-b563-a96d930eb732 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
9ad60cfa-dd03-514e-b309-3735ca889526 | note | ○ Results to Engineer 2 wks before importing
dde56b5b-0903-5860-b66d-6cfd87118df4 | note | Verification Activity: Activity - HP
96c06018-ddc0-5934-bc1f-7ee9008574c0 | note | Verification Activity: By - ENG
4d6b169d-37f8-423b-9ea4-0ae781206f3c | signoff | AUTHORITY HOLDPOINT
159dbfa5-2f34-427e-8a80-b8c25b4d43f5 | checkpoint | 1.3.3 - Particle Size Distribution
6419b1f9-a457-52f4-82ec-3afb5c011898 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
f60b9861-0704-523e-85ab-5ee325cb4ef6 | note | Acceptance / Conformance Criteria - Fitting within standard AP20 grading curve
ca30727a-db58-5f1a-a616-60d7bbf7dda2 | note | Standard / Specification - NZS4407:2015 Test 3.8.1
bdaaeeee-d8c8-564d-bc52-c9d21d8d4be5 | note | Verifying Document - IANZ Accredited Report
344e42fb-78df-5b14-a94a-80124daa14fb | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
808bbd19-c82a-5a7c-8b88-a2b5e25dfd32 | note | ○ 0-400 - 2 tests
4551bbf3-f4e6-5a67-9f73-1b2ce8e7b733 | note | ○ 400-1,500 - 3 tests
885420a5-8626-5794-bd5a-4b9d8b7089d4 | note | ○ 1,500-4,000 - 4 tests
f3b46a13-89b3-5929-adf3-e906af7ca9e0 | note | ○ >4,000 - 1 test for each additional 1,000m3
f708fc24-0771-5209-8b6f-f59bd46ed3ea | note | – Results to Engineer 2 wks before importing
b29ee523-8ef5-5792-957b-e85ef3e4028d | note | Verification Activity: Activity - HP
6b75bdef-315a-5c48-ae76-b51fd1399249 | note | Verification Activity: By - ENG
fbb05bba-2651-44d6-9a93-fba568af2cac | signoff | AUTHORITY HOLDPOINT
897634ef-0664-4d10-b350-6dbb8814bab7 | checkpoint | 1.3.4 - Maximum Dry Density and Optimum Water Content
9f11bb51-a4dc-53c4-8ff3-3408cb090a8f | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
1e23d068-c69e-523b-8f0b-d68081d2c614 | note | Acceptance / Conformance Criteria - Report Value Only
f9beaa05-e392-530e-8b83-5091d31f12c8 | note | Standard / Specification - NZS4402:1986 Test 4.1.2
c31d661d-3241-5f33-bffc-892cfabec121 | note | Verifying Document - IANZ Accredited Report
fb675986-d11b-5d8a-b656-baa8f660868a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, PerSource
1bfc0e21-5b1c-5399-a677-8e2703c991e4 | note | Verification Activity: Activity - HP
c370c34c-82f4-5750-9d44-be49fb458780 | note | Verification Activity: By - ENG
041ee7aa-b81b-46ef-b9b4-e16f7af3974a | signoff | AUTHORITY HOLDPOINT
28168727-9e02-4e15-8f6a-734dfbcea18e | checkpoint | 1.4.1 - Sample panel (1000 x1000mm)
d9c59f67-dd67-5494-9e0f-a4fc583bdd9d | note | Detail - Contractor to provide a sample panel (1000 x1000mm) of the exposed aggregate specified finish before commencing work
257f3b34-5d7e-5325-a22a-77beef35feeb | note | Acceptance / Conformance Criteria - To NZS 3121:2015, use crushed aggregates or rounded coarse gravels for exposing. Allow a mixture of nominal 10-20mm aggregates consisting of a mixture of grey, black and brown colour tones that represent a riverbed, Autumn or Sunrise mixes. Mix design to be confirmed by the Engineer
f5dcdffb-6264-5c34-9335-50fed56f4406 | note | Standard / Specification - Project Specifications 27.4.5.e
c0eb2d91-bdc4-569e-9b7b-89f0b2494dcc | note | Verifying Document - Visual Inspection
eb8e0f53-a3dd-5fe8-a11a-e210748f9e28 | note | Testing Quantity Required (based from schedule qtys) - 1 Sample Panel
d7046495-6698-554b-898b-a2235924ff00 | note | Verification Activity: Activity - HP
176b75c2-1785-5990-bad8-e3929d80efa9 | note | Verification Activity: By - ENG
997ab9b0-af78-4421-beaa-53240c241f14 | signoff | AUTHORITY HOLDPOINT
20dd0d35-b5ce-45c1-baa5-04633b5b868f | checkpoint | 1.4.2 - Slip resistance
ae1465d7-d10e-5b6c-b17f-e01602a28e7e | note | Detail - Test sample to comply with NZBC D1/VM1, NZBC D1/AS1
9cada0b1-5845-5455-9513-9a92e70fbb03 | note | Acceptance / Conformance Criteria - Level access routes: 2.0 Slip resistance for ramps :3.14
14a074c5-7f4a-556f-ba02-dc604c7ff5cd | note | Standard / Specification - Project Specifications 27.4.5.e, AS/NZS 4586:2013
dce292db-78e1-53bb-a26a-b1cfe4f38b0d | note | Verifying Document - British Pendulums
8430b09c-74be-5c44-8d7c-a1474ca57692 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
9d1d8a0c-3d2a-569e-b8b6-3ae4865c645d | note | Verification Activity: Activity - HP
c1d2cf4e-14b2-5921-b517-1410c2aebd11 | note | Verification Activity: By - ENG
db4c5227-00ed-494f-b4e5-d4583c1f4c16 | signoff | AUTHORITY HOLDPOINT
85fa58a3-ae1f-48da-8f8e-81636e24db3c | section | SECTION 2 - CONSTRUCTION - PREP GENERAL
d25a4520-7a5f-47ef-85d6-63e3b3745caf | checkpoint | 2.1.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
2f3b9c44-4219-5c4f-87bb-844a6c521b25 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
d72a9180-7b52-5527-acd0-45cfd995e037 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
9d60261d-6ba6-5d3c-8628-a0512f359502 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
125b6c75-1dc4-5887-b822-4221634e6d98 | note | ○ CBR: >7
26e77e45-91ee-5968-a13d-db57c1233bbe | note | ○ Single Test Min SU: >50kPa
99e923ab-d04a-5745-9dbb-c34bf1d1abae | note | Standard / Specification - Appendix XVIII
7edd1994-2e75-5cbf-ab91-0c0eacbf3a31 | note | Verifying Document - Shear Vane Report
f340637b-a28a-5e22-854a-62f5bc69c51d | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
b81a7fb9-1fcc-56b8-9553-1a007b436f7d | note | Verification Activity: Activity - I
0a3a57ae-6af3-52d7-bed3-dad52cd09089 | note | Verification Activity: By - SE
70acbdf4-ea07-48af-8fab-30f3d180821b | checkpoint | 2.1.2 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
d5a5320e-85cf-52e7-a903-235d5465b7b9 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
18985a8e-69da-5cea-970f-605bf50fb2ef | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
953c2133-b1db-52d1-8db3-5ccc8d33f6ee | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
7842aea1-033b-5531-b4ee-466a8543a60c | note | Standard / Specification - Appendix XVIII
ba416f88-8229-5102-9c49-edb08cfd812c | note | Verifying Document - Scala Report
a0c0b250-58c2-59f7-b5d3-384b6d91049b | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
d3add1d2-3f65-59a7-94b6-799dea295881 | note | Verification Activity: Activity - I
bdd1a255-9e12-5e0c-ab32-a529094c8f39 | note | Verification Activity: By - SE
27997550-870a-42c8-a3c6-bf760a3f06d4 | checkpoint | 2.1.3 - Proof Roll Subgrade
a870a0d0-e511-57e7-98e6-3d66ec98a51b | note | Detail - Visual Inspection of Proof Roll
35f1e3d8-b98f-5b04-9cce-114db751a34c | note | Acceptance / Conformance Criteria - Visual Inspection
215e5423-d3ca-51e0-971e-76361f7e0ac8 | note | Standard / Specification - Appendix XVIII
be95674b-475e-537c-9d48-0badc57783bb | note | Verifying Document - Visual Site Record
9c73410d-4b59-5701-9802-2f39f1f82ded | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
80482f35-d08d-5f88-a436-a7fd430d1896 | note | Verification Activity: Activity - I
510f9d62-23ef-5bb0-af34-ce19acddac0c | note | Verification Activity: By - SE
85703be7-f70c-4276-8add-52d7aff5e64e | checkpoint | 2.1.4 - Final Subgrade Heights
4b8f428e-a350-5ece-a85a-95674ea9c668 | note | Detail - Excavated to the required subgrade level
cb0b4692-8e0e-532f-a55d-f135ee8dd13e | note | Acceptance / Conformance Criteria - Using survey pegs as hights and placement. Measure from stringline for depth. Tolerances as follow
d3157b67-fb29-5f2d-8fda-1f66f778de1f | note | ○ Vertical: -25mm +5mm
9e41f8d0-4a6b-56e7-be4e-1abcd13ff394 | note | Standard / Specification - drawings 232735.02-WSP-DR-UDL-0405,406 -TNZ B/02: 2005
4bcc5a02-6dc1-5d34-a60f-604a9aeab8c0 | note | Verifying Document - String Check Sheet or Equivalent
fdb33dbf-b184-540f-a489-1134ee907203 | note | Testing Quantity Required (based from schedule qtys) - Every 15m
ae599e29-2a94-5e3b-b5ca-4536313e033e | note | Verification Activity: Activity - D
4c555ce5-e435-5900-be55-ffa0c043562b | note | Verification Activity: By - SE
fdc0782b-13f5-459b-937e-ebac3e897f7b | checkpoint | 2.2.1 - Stringlines or equivalent
db4e7eb9-fb46-54a6-951f-0bf79b50424d | note | Detail - Stringlines or equivalent to check finished height of surface is below 225mm.
2569a014-7e16-561f-b63d-6253b409be89 | note | Acceptance / Conformance Criteria - -0mm + 20mm
8ef44ed3-f238-57c5-b383-7806d5801430 | note | Standard / Specification - Standard
3a458e34-9465-5897-9d0f-c6dcf355e6de | note | Verifying Document - Check Sheet
0ec2e7c1-c8f6-51a4-ab03-345b76e82330 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
3e201cd2-b407-5b88-8b4b-2163cfae82ec | note | ○ 1 set = 5 tests
9ab97534-7bd0-59af-844e-a62c148cfd56 | note | Verification Activity: Activity - I
a8758595-fc33-51e7-b314-926d893b9238 | note | Verification Activity: By - SE
3238bb34-0b5e-4e6d-b2ae-0ea5dc3e681b | checkpoint | 2.2.2 - Compaction - NDM
4614d7b8-ebdb-5a86-940e-4484e5ecdc13 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
a3cec897-7208-537c-b77a-e83ff2932d7b | note | Acceptance / Conformance Criteria - Ave >95% of MDD
c92a67b1-3aab-5653-b226-7bd64286efeb | note | ○ Min >92% of MDD
6a9697a1-21f5-56d5-b1a1-dde16047824c | note | Standard / Specification - Standard
96d0380d-4b34-5880-9452-9acc259b6ef4 | note | Verifying Document - IANZ Accredited Report
ba7cd886-36dd-5e6a-8a58-e5ce004df881 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
9742c0f0-7466-5d97-9c27-285f97499a50 | note | Verification Activity: Activity - I
dfa51c55-8fbd-53a2-a014-3c655f734d91 | note | Verification Activity: By - SE
a651c24f-87bb-42d9-ba98-1844c288b740 | checkpoint | 2.3.1 - Stringlines or equivalent
842cec0a-7c3e-5590-8f46-cdc170aedbc7 | note | Detail - Stringlines or equivalent to check finished height of surface is below 125mm from finished height.
be4c270c-9159-54b5-b310-7b1f447fc746 | note | Acceptance / Conformance Criteria - -0mm + 20mm
53d808f7-a4a3-577f-bd70-47fb18ebfd5a | note | Standard / Specification - Standard
09b8a216-8183-5f84-9111-4aab78032fc2 | note | Verifying Document - Check Sheet
4c14f10d-c349-5c4e-b5da-56840195dd5a | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
ab08153a-9400-5e39-95dd-46501bdf8236 | note | ○ 1 set = 5 tests
c0e0765a-c7e8-5730-bf1f-2d8b4e0c2625 | note | Verification Activity: Activity - I
d2418b93-ed6f-5f5a-99ff-170f72444c51 | note | Verification Activity: By - SE
628a2666-f186-4b69-99b4-4369803cc603 | checkpoint | 2.3.2 - Compaction - NDM
9c75ec1e-2ccd-5eb5-b932-1d907a42e6ed | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
9dc85293-3ca9-546b-b9a0-6928e563dbbe | note | Acceptance / Conformance Criteria - Ave >95% of MDD
2606d97e-bf3a-51a9-91a5-4fae8393655f | note | ○ Min >92% of MDD
483a669f-b1d2-5da7-9388-478996cdaccc | note | Standard / Specification - Standard
1dc210a6-4b0c-512b-bbe5-d4734d768aa9 | note | Verifying Document - IANZ Accredited Report
7fd78d08-74d3-5afb-8911-22cafb7d6383 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
08ef993d-f4ce-54b0-ae73-95590233c3ba | note | Verification Activity: Activity - I
583ba1af-ed07-551a-a45b-239f29b48ab1 | note | Verification Activity: By - SE
d9e3cb8c-8b0e-443d-9446-d59bbc3faf11 | section | SECTION 3 - MAINTENANCE PADS AND SHARED PATHS
4c0287b6-6a6d-44d6-b1a3-e8d478a2e428 | checkpoint | 3.1.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
72c04df4-5078-5a79-b373-a9b396ddfe48 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
e3205afd-3e05-5c2f-9124-1c076be5972e | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
d8793717-2550-512a-91f0-363c2bad13f6 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
32fd2d23-453e-5071-bbba-5ddca4ea95ba | note | ○ CBR: <7
2264d593-450e-566c-bd0e-21a77f5d2d18 | note | ○ Single Test Min SU: >50kPa
6e7c9281-963c-5df5-98cc-6a592b2308a6 | note | Standard / Specification - Appendix XVIII
caa78b12-d7d6-5aa9-8b10-30462e0fd07b | note | Verifying Document - Shear Vane Report
a8e1cd24-b708-5f71-bc97-933b09cf46f2 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100M2
83e4ef1c-a0f7-50e3-9bb8-6146dd60c713 | note | Verification Activity: Activity - I
b0727597-da1a-5d6c-91cf-eb080f4f6c3a | note | Verification Activity: By - SE
1a6336df-6cd5-4704-a8d1-288d1b697142 | checkpoint | 3.1.2 - Cut Subgrade Testing - Granular Scala Penetrometer
01837c63-b896-530a-8ff5-7498c4d6389d | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
d8a46197-2778-5e82-96be-1c12d13e00e9 | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
458fb63e-0ec6-52f1-8f50-ba9792330b76 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
65a16184-1e75-588f-bcd3-bd84e5ee60d5 | note | Standard / Specification - Appendix XVIII
8828fe7f-806b-56c8-b061-53ad2c3dca1e | note | Verifying Document - Scala Report
e964d4e9-dc81-5126-94fc-a55102ab0d79 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
7b49719e-9224-5d1c-baeb-cbe9c064753b | note | Verification Activity: Activity - I
9f7d02dc-73a5-5a04-8754-bdd7f34d6487 | note | Verification Activity: By - SE
1dca9d8f-e58d-475e-8c65-ab043eafc51c | checkpoint | 3.1.3 - Proof Roll Subgrade
6f20e008-b4a1-59f2-8062-64e65e58e630 | note | Detail - Visual Inspection of Proof Roll
f625f8a9-0f88-5231-8ed6-714557b51e63 | note | Acceptance / Conformance Criteria - Visual Inspection
90bcb70a-a963-5dbf-ab71-553a82121f04 | note | Standard / Specification - Appendix XVIII
84fc629b-d327-5e11-93fe-3f753fa6387c | note | Verifying Document - Visual Site Record
85a43f07-a7aa-5bdb-85b3-362d4f30821b | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
d77cc5f6-ca35-58b1-b1ab-08081f781d58 | note | Verification Activity: Activity - I
5d7481a8-692d-550c-943c-ec8a8e5e67de | note | Verification Activity: By - SE
9866e942-8363-4571-9de0-819fd88ce592 | checkpoint | 3.2.1 - Stringlines or equivalent
aa730a6a-b6cb-587e-9fb8-6a552928b829 | note | Detail - Stringlines or equivalent to check finished height of surface 225mm Below From Finish Height
92b3557a-5e02-5465-ac76-3ecdd88b9d15 | note | Acceptance / Conformance Criteria - -0mm + 20mm
557953a4-e63d-5b3b-8fba-66993e32a707 | note | Standard / Specification - Standard
0570d856-ffaa-5125-8ffd-a5a294e8d0f7 | note | Verifying Document - Check Sheet
3d7552ea-dd73-5983-b7bc-20c660020025 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
94e29bad-e759-595e-b8a7-32335ad44164 | note | ○ 1 set = 5 tests
b68e5cf8-72ca-5203-9716-5435574d9d0f | note | Verification Activity: Activity - I
3257e526-e8d8-5e8a-ae02-e5bc8311035a | note | Verification Activity: By - SE
9ae09d81-ea76-4be2-82ae-a0b8cc1a9fc8 | checkpoint | 3.2.2 - Compaction - Clegg Hammer
03b62280-7f02-5ec3-92dc-128828eba795 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
f50bb3a0-b31d-5c6d-a1d8-9bbcf62690f1 | note | Acceptance / Conformance Criteria - Min CIV 18
ae885d8c-446b-5f5d-b6af-e40e0bd5cc20 | note | ○ Ave CIV 20
b29caf3e-3d2f-55c0-9a67-dc28fd283c0f | note | Standard / Specification - Appendix XVIII
01cdd487-371b-5426-989a-df7016ee0ae6 | note | Verifying Document - Clegg Hammer Report
7685c8ac-4fc0-51ef-bb4b-252138a85a30 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
cf9b5d43-6f43-5adc-834a-f4771477e4d0 | note | Verification Activity: Activity - I
f9a6dcc9-0c26-5ec4-9bac-863553988f5f | note | Verification Activity: By - SE
b208a383-643b-412c-8284-a949c048e932 | checkpoint | 3.2.3 - Compaction - NDM
21510923-897f-5844-965c-90446c81b6ff | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
56a15cc6-d5be-5400-befb-c283139861f8 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
1727149f-bbeb-5151-9d85-50ed2f29c921 | note | ○ Min >92% of MDD
6058fab9-8778-59c4-af5c-41fa04c94cda | note | Standard / Specification - Standard
8eff1124-4436-5a9f-9520-a49b373c2e39 | note | Verifying Document - IANZ Accredited Report
f1efed7a-f913-52a0-b79e-5b298c3918e4 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
0bed155f-a0ac-5e04-90e0-edfa181235d8 | note | Verification Activity: Activity - I
8a6e8c27-77f9-5916-900a-f8b87971f57d | note | Verification Activity: By - SE
9f33fd73-c604-4ed5-a4b5-31bba61d0595 | checkpoint | 3.3.1 - Stringlines or equivalent
307dbc96-3a1c-5118-9548-c401fd44a34a | note | Detail - Stringlines or equivalent to check finished height of surface
9ac38c82-fc97-5094-9d44-661eaa5a754a | note | Acceptance / Conformance Criteria - -0mm + 20mm
f6066707-9c4e-5b8e-ae01-9d2a44854eb9 | note | Standard / Specification - Standard
e690d9e8-e889-5c13-aecf-31e0e8bca67d | note | Verifying Document - Check Sheet
9f4b1b0d-2f83-58dd-8c03-633f1236e129 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
a3dbaff0-0081-5314-aa86-fe23606fc7e0 | note | ○ 1 set = 5 tests
30b54305-e5c8-5af3-8199-1797e4a7b22b | note | Verification Activity: Activity - I
79d9d6dc-3cb1-5f0b-a882-718ff9726793 | note | Verification Activity: By - SE
e5bc3925-e26b-484f-9111-d3c9eb4d0d90 | checkpoint | 3.3.2 - Compaction - Clegg Hammer
96c9822a-037d-5816-a21a-4fac3db7e1ea | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
7c95c259-a6e6-5a95-aae1-9790198e02ca | note | Acceptance / Conformance Criteria - Min CIV 18
bb686f34-12ba-5d48-9ec1-029e140a718d | note | ○ Ave CIV 20
26988cf7-84fb-518b-83c4-ad940fd34c7f | note | Standard / Specification - Appendix XVIII
89a7c465-16bd-5173-97e7-181ca9d37567 | note | Verifying Document - Clegg Hammer Report
1fef6aab-7a0a-5a01-8c77-b50c52aa7d67 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
5b210126-7672-5967-83ab-c8cedf1f5c3e | note | Verification Activity: Activity - I
99a9e98d-0545-57aa-b4a8-be6389c4dd78 | note | Verification Activity: By - SE
436dfa8f-b54d-4a86-96a5-c839ac2e212e | checkpoint | 3.3.3 - Compaction - NDM
ae3994ff-0790-58ad-b290-9ac8a566c127 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
12a78dcd-2461-5af4-a49f-a85c379eb239 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
f50d3620-d491-5cd3-b899-7ae023418427 | note | ○ Min >92% of MDD
c72f6844-340c-59e1-b47e-141cb2145cff | note | Standard / Specification - Standard
5b386554-e2d9-5a8c-bb3c-6bb7323c70da | note | Verifying Document - IANZ Accredited Report
e87df91a-66fc-5247-acd8-2c9eb2446620 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
fe3cf561-1d59-5d9e-9c66-52965eb81676 | note | Verification Activity: Activity - I
60494a4f-329f-53b8-8661-c801c5ffbf2e | note | Verification Activity: By - SE
66e9178d-bb7d-478b-91bb-e9433f7a056b | checkpoint | 3.4.1 - Surveyor check
3cf20d50-88fd-5579-83ee-621daef26f91 | note | Detail - Equivalent to check the position of the formwork
953cb1b0-4bf4-51fb-bfef-b5e6788aafa8 | note | Acceptance / Conformance Criteria - +\- 100mm of design
fe9f026a-b224-59bc-a9e5-ec7bed693e84 | note | Standard / Specification - NZS 3109:1997
25ca51f1-9f51-5c2c-8d1f-d968c283e9af | note | Verifying Document - Check Sheet
739da0b2-f831-5e71-a337-a37b499d10af | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
e122dc59-a295-51c8-b7a0-ca8fd2c6382e | note | ○ 1 set = 5 tests
390772b3-0c21-5e18-98bd-7ed00c68275c | note | Verification Activity: Activity - I
b0d42c73-7ba8-5dd2-b62c-cfc57146954b | note | Verification Activity: By - SE
1910391f-7aeb-49a0-99ce-2b63ef6b542d | checkpoint | 3.4.2 - Surveyor check
e8b2011c-da54-5a6b-9a09-facfa2cdbd2f | note | Detail - Equivalent to check finished height of framework
393d4e4f-1141-59f1-8185-fa9e17e6aa8f | note | Acceptance / Conformance Criteria - +\- 10mm of design
90162288-9853-5d9c-b6ba-4deabc6872c0 | note | Standard / Specification - NZS 3109:1997
72ea192f-e905-5831-8cca-b038ff468e36 | note | Verifying Document - Check Sheet
ddd83f04-32af-5dfc-a93c-ca2a60b4b6ad | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
640b3662-1986-593f-b88d-bbe7c3167f19 | note | ○ 1 set = 5 tests
93e20c36-4205-5bc9-92b6-48cdd84dfec3 | note | Verification Activity: Activity - I
431c59d2-1c1e-5105-8247-53b788260260 | note | Verification Activity: By - SE
7fa06933-9dfb-4f0a-a758-3c938788a9cf | checkpoint | 3.5.1 - Reinforcing Mesh Check
1e9e2bdb-7248-5d23-8f2b-f295463a648e | note | Detail - Ensure the right mesh
14288e1d-b253-5304-9f0b-0904d281cf6a | note | Acceptance / Conformance Criteria - 665 Reinforcing mesh
39957a03-f005-5693-b339-8102623b5800 | note | Standard / Specification - Project Specifications 27.4.2
1d965cd6-c37b-5982-8ead-573e62fdbac9 | note | Verifying Document - Dockets
fc48b28e-78d1-56a4-8587-f40f17896c4b | note | Testing Quantity Required (based from schedule qtys) - Measurements
b1784ec4-2684-5de9-8cf3-5e0ba3084516 | note | Verification Activity: Activity - C
692760c0-ed56-565a-957e-eb9d896b2676 | note | Verification Activity: By - SE
57e1407c-0ced-4e2e-be9a-95b908fc401d | checkpoint | 3.5.2 - Reinforcing Mesh Check
b41a5053-da06-5ac7-8226-c3cb6728724e | note | Detail - Ensure that overlap and clearince from edges
726544b6-c659-5a1f-b13a-178d6a75a6c6 | note | Acceptance / Conformance Criteria - 666 Reinforcing mesh
ec7e49ad-c32f-54d3-8851-59bbd9c896b0 | note | Standard / Specification - NZS 3109
008c2320-cb51-526f-b68c-70396ece45ab | note | Verifying Document - photos
a9235e17-a979-5a85-ba95-35150efe39b7 | note | Testing Quantity Required (based from schedule qtys) - Measurements
22efac26-02a0-5cc8-849d-adc20290058b | note | Verification Activity: Activity - C
265d379c-cc89-5daf-8669-fdc32b0968f1 | note | Verification Activity: By - SE
6c6f4ac2-7cce-4d79-9d91-2c30961fce9f | checkpoint | 3.6.1 - Concrete
aa10fd1d-d524-5fbd-b29f-7f9093f67350 | note | Detail - 20.0 MPA concrete. 4kg/m3 black oxide (2.5%)
6dc65310-4e9f-524c-9c40-4447064ee3b6 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 20MPA
768aec2b-7e10-5cae-a99d-b2be4ec19324 | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405
0c97f914-3536-5a05-a38b-9a52b2537095 | note | Verifying Document - Concrete Delivery dockets
4ed81fdf-43e7-5453-9336-adad46ad70fd | note | Testing Quantity Required (based from schedule qtys) - During construction
df48181e-5051-5f38-b05d-07b7bd20d362 | note | Verification Activity: Activity - I
7e583b55-c649-5dfd-b3aa-a8622da8d939 | note | Verification Activity: By - SE
38063ddf-a5c8-4e08-9c06-40f6bd41dc25 | checkpoint | 3.6.2 - Control Joint
f8e609e2-0073-5938-9f97-b8ed401aa759 | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
211a47ae-bbde-506b-92d9-5154c01263b5 | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
61f2c44d-9776-5ae2-bb01-713e7f71231d | note | Standard / Specification - PS 27.4.5
97f17f0a-5f88-5f4f-b520-dbffc83a381c | note | Verifying Document - Post Pour Checksheet
1c621658-cc3b-5d15-aea7-43836f3164c3 | note | Testing Quantity Required (based from schedule qtys) - After pour
b5602494-2419-5309-954c-d9183241ba55 | note | Verification Activity: Activity - I
8a688b28-2af6-5cb6-8ee8-bf9210c5d1ef | note | Verification Activity: By - SE
5021aea5-17f6-494b-b8e7-9d6be6fc61d9 | checkpoint | 3.6.3 - Final Finish
b7c595ca-1c2e-5060-9695-e5b63aa76336 | note | Detail - Finish to be either:
63f2f6cd-8832-5636-83e2-be4a4cf814e8 | note | – Rough broom finish
528d4544-2ac8-58f6-8463-5ca722bbcf38 | note | – Exposed aggregate finish
0b6634a4-79c1-5e5e-b8e9-8883f9a98b19 | note | Acceptance / Conformance Criteria - U5, U5E
5d56b1a3-1514-5fe4-bb8a-e2116e592f38 | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405
0192477d-caad-56c4-953f-92c8f9be93d7 | note | Verifying Document - Post Pour Checksheet
2d0f9210-bfc8-5657-8a27-290487f79c1f | note | Testing Quantity Required (based from schedule qtys) - After pour
359b30fb-e45b-567c-845e-12e97dc78ce4 | note | Verification Activity: Activity - I
18c61468-eb09-5fcd-9e9e-cfa84c0930b5 | note | Verification Activity: By - SE
d8890db4-ac9a-4843-a7a8-121590dfa4ab | checkpoint | 3.6.4 - Slip Resistance
ae379e8b-6c79-53ac-bf71-7a54c4d07a44 | note | Detail - British Pendulum testing
1b95d662-bb99-57aa-8832-f2dc6a604031 | note | Acceptance / Conformance Criteria - Level surface: mean coefficient of friction (µ) not less than 0.4.
59d3f088-c2f0-54f2-942f-47cf460677f7 | note | ○ Slopping surface: mean coefficient of friction (µ) not less than 0.4 + 0.0125S (S = slope of surface expressed as a percentage).
1b938d1a-65e5-5f9f-8434-5e3d9f129f08 | note | Standard / Specification - Project Specifications 27.4.5.e, AS/NZS 4586:2013
207a5da3-2dca-54d5-9d0d-71ba52f5546a | note | Verifying Document - Britsh Pendulum Test Results
2ab49df4-885a-5901-b7e7-532c4aa698af | note | Testing Quantity Required (based from schedule qtys) - Every 20m
836ae2c6-2012-54d7-afbd-7b64d22fe78e | note | Verification Activity: Activity - I
f21c765e-111d-5b97-97a7-7ddd803c8cb0 | note | Verification Activity: By - SE
dae12519-c8b7-4587-ab48-84bb121a6762 | section | SECTION 4 - TRAFFIC ISLAND INFILL
7197728c-57b1-454e-b301-44204eff1b43 | checkpoint | 4.1.1 - Stringlines or equivalent
5f242d27-52be-5c36-ac6d-aafd7344c745 | note | Detail - Stringlines or equivalent to check finished height of surface
dd9fdfa9-0c4c-5ff3-85f8-08563be68c1e | note | Acceptance / Conformance Criteria - -0mm + 20mm
00191ec3-13fd-5cfa-bfb5-e1d1a1ccb6e4 | note | Standard / Specification - NZTA B/06 8.2.2
e24ad0fd-7f97-5950-9383-ff7f18094188 | note | Verifying Document - Check Sheet
8fc623c0-c7c7-59fa-88ba-c2d4df86c744 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
46ae3ec0-42c1-506e-8119-cb95c8b85d2c | note | ○ 1 set = 5 tests
77d9713f-e00c-5d54-ac99-379bf0f487a4 | note | Verification Activity: Activity - I
36fe757c-f553-573c-94db-499dfb85c143 | note | Verification Activity: By - SE
f419c2dc-88cd-4555-a94e-7787c1df773f | checkpoint | 4.1.2 - Compaction - Clegg
6a02fa33-2bd3-5e21-ab0b-7e0c0cf246ed | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
c76ab4a1-b75f-5586-8bd8-b89f2128c2ac | note | Acceptance / Conformance Criteria - Min CIV 18
97539810-cd23-5319-af6a-5999a0460a25 | note | ○ Ave CIV 20
abeede5f-be57-527c-a016-d23ea5f4e844 | note | Standard / Specification - Appendix XVIII
efb03d70-67e8-5781-83c3-7e0c434ef98d | note | Verifying Document - Clegg Hammer Report
71c482d9-17d4-5272-8e5d-7b4189ac9b14 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
e956049c-2a77-5d9b-8e35-38e3cc09077b | note | Verification Activity: Activity - I
b02ddc1b-0b3f-5a3e-a6ce-35139e7b8443 | note | Verification Activity: By - SE
6f688b65-c4da-4b02-b956-1e0bedbf21c5 | checkpoint | 4.1.3 - Compaction - NDM
0ae23cf6-4d8b-5bcc-8745-a1c421c6d2e8 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
9938ed66-bfd4-59a1-9b4f-0141bb0e587a | note | Acceptance / Conformance Criteria - Ave >95% of MDD
21131c39-8ab4-5ada-ac84-026e2656e952 | note | ○ Min >92% of MDD
ba577605-0e72-5161-b4e5-58af50397b26 | note | Standard / Specification - Standard
12b0917e-32bd-51dc-a39a-8c9e03267aae | note | Verifying Document - IANZ Accredited Report
cbdcbf14-a71c-5cd4-b638-64c1a957b580 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
4f590d76-6375-5b0e-9c78-d9292af77df0 | note | Verification Activity: Activity - I
203c464b-fb90-5145-a99f-be8649cf3c3e | note | Verification Activity: By - SE
7cb3ea5e-7d19-4ce2-91ab-4c4d5dbfe0c4 | checkpoint | 4.2.1 - Concrete
c2b2d559-08c4-57ed-b9aa-ce35ae0b9bb3 | note | Detail - 2.5% black oxide by weight of cement
a52d8c64-e62c-56ce-b95a-78fae574afbc | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 20MPA
19d59f23-d26c-5b76-996c-184a9a8d6f14 | note | Standard / Specification - PS 27.4.6
69d371be-8893-583a-aa7e-9ae2fac0804a | note | Verifying Document - Concrete Delivery dockets
275b35f8-b363-5e97-937f-2a605e36d951 | note | Testing Quantity Required (based from schedule qtys) - During construction
9423b85f-ae24-528f-8c06-d48d232f78a4 | note | Verification Activity: Activity - I
89335873-c0c2-5975-baa9-401d5c0a1086 | note | Verification Activity: By - SE
411c97f3-46d4-4b7f-82b4-317498f4e427 | checkpoint | 4.2.2 - Final Finish
69d74643-b8f8-5ee4-ba51-e229771ca92a | note | Detail - U3 Finish
b84df24b-3568-5b96-b553-941b8146ed5c | note | Acceptance / Conformance Criteria - U3 Finish
b6c5ddb8-4d3c-5768-9511-7981eaca2c5c | note | Standard / Specification - PS 27.4.6
ba811caf-eb65-5efc-8ec7-c60ec2d44545 | note | Verifying Document - Post Pour Checksheet
bc015065-af8c-5a19-a3d3-473327168345 | note | Testing Quantity Required (based from schedule qtys) - After pour
cbdf1f4a-7035-5632-8e17-6313b516e317 | note | Verification Activity: Activity - I
6efb3d0b-a686-5cef-bbc7-70635246fdd1 | note | Verification Activity: By - SE
db352c6e-5f8d-428f-8489-6832386ba688 | section | SECTION 5 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
7ef9cb80-2ba4-42f0-86f6-68541501885b | checkpoint | 5.1 - Final Inspection
cc1951c3-ba5a-5206-9842-eacb927d52cb | note | Detail - Final inspection of all concrete work.
bcf059a5-989f-554f-a653-4aa069634195 | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
85609c1f-b321-5755-88b9-4e26af27236e | note | Standard / Specification - NZTA P39: 2013
48e1d444-1dc0-530d-b7f4-e5b7cd76b778 | note | Verifying Document - Final inspection report
ac2ba76a-1bc6-553a-a5e3-ee8ec45475b2 | note | Testing Quantity Required (based from schedule qtys) - 100% of works
071b6b68-9490-5fa4-ba32-434bc922d3de | note | Verification Activity: Activity - HP
517b1723-e9d4-53a6-85ce-3350fbdfac92 | note | Verification Activity: By - ENG
1c24d26c-c095-41f0-97f1-c01267769aa0 | signoff | AUTHORITY HOLDPOINT
42655801-5e7f-4ad2-89bd-bbaab819364b | checkpoint | 5.2 - As-Builts
988a7cdf-76ae-5bb0-8f52-481b8565a637 | note | Detail - Final inspection of all concrete work. Red Pen Mark up.
58eb4188-8a7d-5f86-b4d5-67416cceb549 | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
644a46fe-d8b5-53b7-9c1a-a8f561d6a6d4 | note | Standard / Specification - PS 16.7.6
09e02c7b-e479-5eb5-930b-ddeef6387286 | note | Verifying Document - Red Pen Markup
c6286ece-ff8d-59e8-8e1a-c2666f0bf548 | note | Testing Quantity Required (based from schedule qtys) - Whole Work
2f66b20f-876e-5b4d-b767-e138614a23d6 | note | Verification Activity: Activity - D
85944407-c7c9-5ef3-ac3a-a562c2b1d905 | note | Verification Activity: By - SV
b15f6b49-59de-4647-85a7-e05f92c28b71 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
44a30cf7-dae3-55eb-be19-0187357b6423 | textbox | Contractor's Rep Name:
95fbc56a-93b3-5730-aab6-800fdcd4e030 | textbox | Engineer's Rep. Name:
511fcbc0-a1f7-5b9a-ae87-e50de805180e | date | Date:
3ce9702d-23fe-47a8-b56a-60d833f914c6 | signoff | Add Signature
399eec96-b2bf-4177-b569-de9e318de6b2 | checklist | DN1210-020-003 ITP Roundabout Apron & Riverstones | itp | DN1210-020-003 ITP Roundabout Apron & Riverstones
ef0ab627-f1c7-4d55-ba3b-846d1fe5490a | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
c3018cc9-8578-4917-926a-133ce3ec2108 | checkpoint | 1.1.1 - Crushing Resistance
90ad8044-ae41-5cd2-98b4-c1739895bce4 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
6b8b7231-0db6-5b9f-aa89-256bdc244204 | note | Acceptance / Conformance Criteria - >100KN
b38b6c23-18e8-58ce-ac8d-2107c1358c90 | note | Standard / Specification - NZS4407:2015 Test 3.10
466854f4-89d9-54e5-8f3a-f8c71eb21438 | note | Verifying Document - IANZ Accredited Report
544cab5a-1307-5ba5-86ea-24366a2b9b36 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
0ac54d21-894a-56a1-8fbc-20a6e0c19023 | note | ○ Results to Engineer 2 wks before importing
f0c07168-fcf8-58ec-8f6d-732063976808 | note | Verification Activity: Activity - HP
1cc3504c-ed2b-523e-ab46-1db6033b044e | note | Verification Activity: By - ENG
c08a1b96-26a9-46fc-8fe6-ba2416026cc7 | signoff | AUTHORITY HOLDPOINT
11dfba15-087a-40bc-8758-945482f73127 | checkpoint | 1.1.2 - Soaked CBR
45624f17-2638-54d6-9fd9-8162899a99d9 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
25b61483-3f50-5dd6-b951-189cc7834e30 | note | Acceptance / Conformance Criteria - >25%
2324b573-aa47-560c-890b-0036f5d8cf4e | note | Standard / Specification - NZS4407:2015 Test 3.15
3087ac23-0cf3-570f-9e0a-61eb68510d30 | note | Verifying Document - IANZ Accredited Report
41d4b849-a4e8-5329-a307-d363a14d200b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
56fec474-2715-5a01-808d-90e231a143f1 | note | ○ Results to Engineer 2 wks before importing
dfde4e39-8191-59a3-b6de-dba2101c6415 | note | Verification Activity: Activity - HP
07948e46-d28f-52d0-9906-9a3143f12e4b | note | Verification Activity: By - ENG
06df4d76-4815-4739-9fc4-a48f5e5d36c0 | signoff | AUTHORITY HOLDPOINT
776ca60b-02fa-4bfc-86ac-9d4f918f463b | checkpoint | 1.1.3 - Weathering Resistance
6d81bffa-ceca-554e-90a5-3dfe5b050196 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
439a1d8b-552a-5e40-9d6b-77f4d38149d2 | note | Acceptance / Conformance Criteria - CA or better
b9b12d24-30a9-50db-adbe-c4ff79cec570 | note | Standard / Specification - NZS4407:2015, Test 3.11
ec61276f-ac27-5256-bfff-a04434aaa7ea | note | Verifying Document - IANZ Accredited Report
d9aeff26-0ebc-538b-ad4c-dc1a931cd84f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
dc3a0dfb-d913-522a-a397-86fea3d3de61 | note | ○ Results to Engineer 2 wks before importing
7982e793-11dc-5207-a30a-cbfb545d16a8 | note | Verification Activity: Activity - HP
aaee3a1f-5b5f-50d6-8001-6eac6dbe66d6 | note | Verification Activity: By - ENG
5202378b-c50b-4865-ab44-ff71d84ff6d9 | signoff | AUTHORITY HOLDPOINT
195f7743-b6f5-4f04-932a-1c0181374322 | checkpoint | 1.1.4 - Particle Size Distribution
46615842-db8d-5251-aa9a-1ec0a690e717 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
80284c6d-f376-5f2b-973f-1dcaa493dccf | note | Acceptance / Conformance Criteria - Fitting within standard GAP 65 grading curve
935ab6cc-794c-5ace-a8b3-d27f60ccd588 | note | Standard / Specification - NZS4407:2015 Test 3.8.1
ac900865-e15c-5286-8381-9c451af93169 | note | Verifying Document - IANZ Accredited Report
0c4f5891-198c-5609-ba35-eb3555d2572a | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
baf61c5f-5820-50b7-906f-4bffb083814d | note | ○ 0-400 - 2 tests
83aeccd6-dc27-5695-bb8e-340e397460b9 | note | ○ 400-1,500 - 3 tests
6f3de228-bdef-5108-b60b-b98dd18d6339 | note | ○ 1,500-4,000 - 4 tests
02abdc65-c79e-55ff-a1cc-2fb4d1a059d2 | note | ○ >4,000 - 1 test for each additional 1,000m3
2974a435-7e9a-5ab4-b90c-6fa59c47b1ed | note | – Results to Engineer 2 wks before importing
9f0d36f6-ad21-5c9d-83eb-73ad8b2db4dc | note | Verification Activity: Activity - HP
bd602f59-e952-592a-aeb7-f1f41a914779 | note | Verification Activity: By - ENG
d52fbf68-c821-4146-bc80-b062148c8268 | signoff | AUTHORITY HOLDPOINT
8fcfd3b8-9f41-47f0-b006-2080aaf07032 | checkpoint | 1.1.5 - Maximum Dry Density and Optimum Water Content
1a20dd93-cfcd-5d74-8a3c-4c04b09ef9d5 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
ea7f4383-d1be-55f4-902a-5bb91645e467 | note | Acceptance / Conformance Criteria - Report Value Only
a9d6ebf1-16c4-5b63-a59f-f0796ca931b2 | note | Standard / Specification - NZS4402:1986 Test 4.1.2
a5e835a5-8bf3-599a-b0e6-5ed5b5dcd813 | note | Verifying Document - IANZ Accredited Report
be609a27-0ecf-5715-9b02-2058d7f3fd42 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, PerSource
19a442ad-c91c-59f5-ad4e-0f1ee7ce48cf | note | Verification Activity: Activity - HP
bd52d708-2d88-5e89-b3cb-8b94ef4c06d3 | note | Verification Activity: By - ENG
4291235a-f6b2-4615-9a39-f0ad5253dbca | signoff | AUTHORITY HOLDPOINT
f94631d4-f27d-4b3a-b651-1c732287a5b2 | checkpoint | 1.1.6 - Plasticity Index
2e7a6aac-6fe1-52d8-a11b-71cbef3af379 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
14149837-35ba-5809-8ee4-bc12ff6fafa0 | note | ○ NZS4407:2015, Test 3.3 Plastic Limit
07a05152-97d3-5d14-8cf3-7bb9ce992cad | note | ○ NZS4407:2015, Test 3.4 Plasticity Index
18d1c1b0-5cfb-5181-8693-e057bcf40dd2 | note | Acceptance / Conformance Criteria - NP
79c0cf14-2940-5ae7-a3dc-c5ffe785fb82 | note | Standard / Specification - NZS4407:2015, Test 3.2
e4e59479-d967-50db-8e11-4861eae6e8d2 | note | ○ NZS4407:2015, Test 3.3
2f1a45e3-8bbc-55a1-a888-eb4efe93f895 | note | ○ NZS4407:2015, Test 3.4
7d1eb018-83b6-5d29-867b-22606a6573f2 | note | Verifying Document - IANZ Accredited Report
856df372-2650-509b-a529-baf10b402c73 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
46d6b818-9ee9-514c-accb-c26b7b69b306 | note | ○ Results to Engineer 2 wks before importing
12c0a2bb-e790-5257-b7cf-f9c1189ab525 | note | Verification Activity: Activity - HP
27fbfe00-1a67-57c5-89dd-571c1e6c65dc | note | Verification Activity: By - ENG
0e71995d-82a5-473b-a107-2da644e6804e | signoff | AUTHORITY HOLDPOINT
fcb6843c-a211-468c-9ae6-539f9c88f926 | checkpoint | 1.1.7 - Sand Equivalent
74093e3f-3fa2-5302-9000-95484903beae | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
9789a2c3-fefb-5b96-a963-1e6b09855335 | note | Acceptance / Conformance Criteria - >25
0964d503-b441-5f65-b4e0-9d634f77e7a3 | note | Standard / Specification - NZS4407:2015 Test 3.6
4dcbfb08-460f-5114-af7e-7fec2136e9ab | note | Verifying Document - IANZ Accredited Report
9ae91d46-948c-567c-bd2e-2eed904157b6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
2b5a5baa-b8b3-5426-9468-6aed134ce36e | note | ○ Results to Engineer 2 wks before importing
4c09a2d8-cff5-5e25-9e80-da9925e99597 | note | Verification Activity: Activity - HP
600efda2-7184-5dc1-a6f7-199216949e63 | note | Verification Activity: By - ENG
2c369707-6112-4533-8a85-f28fd809a568 | signoff | AUTHORITY HOLDPOINT
e10a845c-767e-4e2e-a329-44807438cb92 | checkpoint | 1.1.8 - Clay Index
ce39556c-6b24-5258-8dc0-df0bb3beba69 | note | Detail - NZS4407:2015, Test 3.5 - Clay Index Test Report
79f57f49-0b72-5c44-b77a-31450744e216 | note | Acceptance / Conformance Criteria - Report Value Only
1c554c80-9d65-5a8d-a898-665476352126 | note | Standard / Specification - NZS4407:2015 Test 3.5
7561ef45-bbeb-5633-8356-d0fcbad7be3a | note | Verifying Document - IANZ Accredited Report
8091b8ab-705a-5433-9b13-148f24d87e1c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
37f4adbd-e071-5ef0-bfb7-4b8c41880dae | note | ○ Results to Engineer 2 wks before importing
27362019-a559-5044-8fb0-ed419da555be | note | Verification Activity: Activity - HP
56389858-662a-5709-ab24-017143626469 | note | Verification Activity: By - ENG
aa0d167d-cf30-4dda-ac8f-ffe7617acdef | signoff | AUTHORITY HOLDPOINT
bbce4c35-99e7-4a7d-a617-2c142c0bbf28 | checkpoint | 1.2.1 - Crushing Resistance
9c183b99-fe38-598e-b22f-b84a3abc6fde | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
9e78601c-7291-5376-b9ee-e00c9ec46a84 | note | Acceptance / Conformance Criteria - >100KN
861b98f5-3b27-560e-9d3d-25a938f2ef6d | note | Standard / Specification - NZS4407:2015 Test 3.10
18c190c5-62d9-5e2d-8959-0219394a54c8 | note | Verifying Document - IANZ Accredited Report
dbcefa3e-a7bb-5f9e-8567-fa0f9ecaa1c7 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
58d592b1-c92b-575f-a547-ad78b2c8ebe5 | note | ○ Results to Engineer 2 wks before importing
c6942f2b-2dbe-5c05-890c-107590a197e1 | note | Verification Activity: Activity - HP
b90a6bc9-f38e-5791-833a-28ab4352500f | note | Verification Activity: By - ENG
8a58de6f-083b-438c-8aa3-94594754a399 | signoff | AUTHORITY HOLDPOINT
74cf70cf-3102-4aff-91db-43736fa136e7 | checkpoint | 1.2.2 - Soaked CBR
2b60380e-6f13-5af4-8635-080d0d7d59b9 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
a5fd174d-caa2-57a2-9506-f7eb1efcb7c6 | note | Acceptance / Conformance Criteria - >25%
47065cd2-7de0-5617-b7d0-c8bfe1561857 | note | Standard / Specification - NZS4407:2015 Test 3.15
2aea8b0d-3999-5a8f-a062-bbc6f5c6261e | note | Verifying Document - IANZ Accredited Report
f49243a3-8453-588d-832d-12ac724dcb1e | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
b2ae56fa-a43d-5279-a179-52ff25b0e989 | note | ○ Results to Engineer 2 wks before importing
f30e673d-2436-59dc-8deb-687750d4024d | note | Verification Activity: Activity - HP
ce19c34d-a3d3-5738-b524-f3099adf6c75 | note | Verification Activity: By - ENG
125a1d7f-2e8e-4983-a228-0e9ba15dcbe6 | signoff | AUTHORITY HOLDPOINT
51036ec8-8362-41cd-826e-4a7bbb170739 | checkpoint | 1.2.3 - Weathering Resistance
b7d4ecd4-63f6-5773-8f6a-bc690a0c3fb6 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
0e51f922-8406-50cf-89f0-8f3425964e5b | note | Acceptance / Conformance Criteria - CA or better
c608b9dc-b4af-548a-b3a3-89550472cb9f | note | Standard / Specification - NZS4407:2015, Test 3.11
b1eeaef2-fb0a-554d-94aa-4f330e111e23 | note | Verifying Document - IANZ Accredited Report
ed3f6bbf-9ccc-5589-b934-f3fce50a94cb | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
c4ef7d29-78d8-584a-a90c-4eb0bf472b75 | note | ○ Results to Engineer 2 wks before importing
736cea2f-e49b-5ee6-864f-5467773a2af0 | note | Verification Activity: Activity - HP
28b52c60-a783-5123-ad4c-82eef9a0a49e | note | Verification Activity: By - ENG
ee1a08d0-dba2-4221-85e0-f5c4086e713f | signoff | AUTHORITY HOLDPOINT
819970cd-13c5-48fc-9719-a721c8a20067 | checkpoint | 1.2.4 - Particle Size Distribution
c26a9488-8d7a-5b35-987b-17793d073856 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
67895126-42c2-5015-8362-aedbb4fc9d4e | note | Acceptance / Conformance Criteria - Fitting within standard AP40 grading curve
3dc898a5-8fb5-5638-beed-a67c8d8759f5 | note | Standard / Specification - NZS4407:2015 Test 3.8.1
18591a69-ccb7-5541-bc85-9e5e4ff75381 | note | Verifying Document - IANZ Accredited Report
879e8d78-0e63-57ca-98ad-f6b63967a097 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
1933bb2f-bf69-59f1-a5de-0fd0858d99f4 | note | ○ 0-400 - 2 tests
9d7cd78d-1814-5c5f-91a6-b123bcd5687a | note | ○ 400-1,500 - 3 tests
586b8910-2fe5-5ba7-b933-f6df3ec3edfc | note | ○ 1,500-4,000 - 4 tests
9c8cfb5f-389f-56c5-b492-ab884c3972ca | note | ○ >4,000 - 1 test for each additional 1,000m3
f65e9f12-1e82-5711-add8-92829ac1f839 | note | – Results to Engineer 2 wks before importing
17ebb78c-2677-5cbd-bb1a-f02664f43091 | note | Verification Activity: Activity - HP
fc6e3e36-37c3-5d3a-9d88-8b8c25c8c20c | note | Verification Activity: By - ENG
9afc9113-ee7c-4de4-90a2-d49734d83295 | signoff | AUTHORITY HOLDPOINT
c3a55388-299c-44b8-b8e2-213891355559 | checkpoint | 1.2.5 - Maximum Dry Density and Optimum Water Content
fe6e2ab0-77aa-5527-ac16-9b612bc7ffa1 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
dd4c1dfa-b23e-5c9d-b2be-354042672229 | note | Acceptance / Conformance Criteria - Report Value Only
a888d5b6-3b26-5532-be15-3ab41fea710a | note | Standard / Specification - NZS4402:1986 Test 4.1.2
1da5004b-d8f3-5dd0-ae93-e0eea23159b0 | note | Verifying Document - IANZ Accredited Report
2e7a7f40-01e4-587d-a328-cf255ca5a1f7 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, PerSource
1cbee1a7-73f6-591a-a9de-c8dc928ab1bf | note | Verification Activity: Activity - HP
629ebd98-4278-5541-adf0-bd5da150f6e8 | note | Verification Activity: By - ENG
7eedf74c-38ff-4acd-ac43-2445907a50b1 | signoff | AUTHORITY HOLDPOINT
5e1dbb33-06bb-4156-8cc0-8a33cce89b10 | checkpoint | 1.2.6 - Plasticity Index
9334df15-a9fe-537d-a12a-1a2b22dd60e3 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
b5143efa-f9fe-59cd-86af-da57d495a59f | note | ○ NZS4407:2015, Test 3.3 Plastic Limit
da53189e-6cf3-5e7b-adba-733f8d3ee2cc | note | ○ NZS4407:2015, Test 3.4 Plasticity Index
4f4a24be-202f-5754-ae0d-27999d5bda34 | note | Acceptance / Conformance Criteria - NP
f4da463a-ea50-51bc-9a4b-6d8ae79c68fd | note | Standard / Specification - NZS4407:2015, Test 3.2
6ef926b9-23fd-52fe-95de-511e264a41bd | note | ○ NZS4407:2015, Test 3.3
13dfddf7-d9a7-5a5a-97f5-5714adda8fc0 | note | ○ NZS4407:2015, Test 3.4
80eb71e8-4acc-5fb0-93ad-efade3acaa0a | note | Verifying Document - IANZ Accredited Report
010e8f2c-c3af-5740-9ed7-bb471bbb0cb5 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
27c4a9f5-a968-5c29-b23a-3ad4785971b5 | note | ○ Results to Engineer 2 wks before importing
1c60bd5d-007c-5639-bc82-82e94b6ac6f8 | note | Verification Activity: Activity - HP
b53a2a17-126b-58b6-b892-57c8cf03132c | note | Verification Activity: By - ENG
de1f425f-b673-4cc0-b43c-ce8885c28eb6 | signoff | AUTHORITY HOLDPOINT
620b9bdf-7af0-4dea-93e6-325257f9a35a | checkpoint | 1.2.7 - Sand Equivalent
105e9406-17ee-507f-9f0c-7051e16de148 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
179ada16-04ad-5e47-8efe-1ddd0fa65416 | note | Acceptance / Conformance Criteria - >25
c4b555cf-9da5-5b02-a708-3a30ba68b4ee | note | Standard / Specification - NZS4407:2015 Test 3.6
e06bc168-c6e4-5f39-af00-d520f5af12d4 | note | Verifying Document - IANZ Accredited Report
dab81360-8767-52eb-897b-ed7f78f735c1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
9359e74e-dcc2-5bca-9326-530df91f5f6d | note | ○ Results to Engineer 2 wks before importing
3bc38e50-9b0b-55ab-8df3-f6ced0aa9854 | note | Verification Activity: Activity - HP
c3756362-6ee3-5045-b690-064ba5cf544a | note | Verification Activity: By - ENG
0662e87a-8c2a-4697-bcfe-dad67aa5cd52 | signoff | AUTHORITY HOLDPOINT
ef19c27d-3b4e-413b-9287-9091a4fd3cab | checkpoint | 1.2.8 - Clay Index
e9dedb06-6f5b-54a1-87ef-6a90a70b12d4 | note | Detail - NZS4407:2015, Test 3.5 - Clay Index Test Report
17554c1c-ec16-5dc4-9b06-8b2e0d26a38b | note | Acceptance / Conformance Criteria - Report Value Only
c4d05b3b-957c-56f1-a276-316a40db781a | note | Standard / Specification - NZS4407:2015 Test 3.5
1342ccf6-78a3-5680-b1ed-aacc2ce4ed13 | note | Verifying Document - IANZ Accredited Report
ae7ed2aa-0b2b-5b06-8514-38c1947b2d63 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
6c2b8ea7-2e2c-5d1d-8b04-cb02089bd383 | note | ○ Results to Engineer 2 wksbefore importing
864097d2-a253-5926-8451-1c9220aef2f4 | note | Verification Activity: Activity - HP
b1c3ceae-7ff9-5fa0-9af6-56447357a771 | note | Verification Activity: By - ENG
e6f5252f-2a9c-483b-9d76-9d0642df97cb | signoff | AUTHORITY HOLDPOINT
7cf7e680-5ee4-4075-a917-037ef135b01f | checkpoint | 1.3.1 - Crushing Resistance
62574e73-1864-5947-aeae-73ecce9b1056 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
760d5bfd-7e2e-520f-b680-510ccba10a93 | note | Acceptance / Conformance Criteria - >100KN
c845521b-138a-5409-b877-817aa763114c | note | Standard / Specification - NZS4407:2015 Test 3.10
ad8b3712-0c0e-5e8d-a2fd-4c2ce89daa78 | note | Verifying Document - IANZ Accredited Report
2b93663e-f8b7-58d0-b53c-80bca207cd6c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
8fd6e43d-a81e-5923-bacb-189204ee10ce | note | ○ Results to Engineer 2 wks before importing
86191f13-19e8-5490-8c34-6a69adc677a2 | note | Verification Activity: Activity - HP
3b6fe05b-7467-5983-be0e-e0e733752a33 | note | Verification Activity: By - ENG
45ebe7e1-c5c9-4a56-a1e7-721ace5ee64c | signoff | AUTHORITY HOLDPOINT
aff59f80-ebf1-4fdb-b73e-d919f15d9ed1 | checkpoint | 1.3.2 - Soaked CBR
7152e540-752e-54c6-8e56-d3f9f2e38f60 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
76b9d97c-55e8-5322-98b3-e67d5d757b46 | note | Acceptance / Conformance Criteria - >25%
8bdecab5-444d-57ae-9a1c-3dc488232c22 | note | Standard / Specification - NZS4407:2015 Test 3.15
ee6b595a-af36-56f2-93d0-dab7253ddfab | note | Verifying Document - IANZ Accredited Report
3b3a3d14-acf1-5802-a940-d9c9206a0cb9 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
f8b5cb44-4ba4-5c79-bd91-997097e81788 | note | ○ Results to Engineer 2 wks before importing
94ab65f0-b557-5aa8-ab79-72f3cbb888c6 | note | Verification Activity: Activity - HP
166a62fa-cb43-508a-a422-6f638a202a46 | note | Verification Activity: By - ENG
ba563efa-bd8b-4d6f-9851-7489d8d445ed | signoff | AUTHORITY HOLDPOINT
d9f59b41-f26e-461f-9757-7aeee2992fc3 | checkpoint | 1.3.3 - Weathering Resistance
21c7422f-9843-5fe9-b7da-6b522d11e194 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
71ef4c7a-39e0-550f-93fb-e18e4c830dd9 | note | Acceptance / Conformance Criteria - CA or better
3216550f-1224-5741-bc60-8b4816b3f249 | note | Standard / Specification - NZS4407:2015, Test 3.11
43d2ac13-61cb-52c6-b1f0-438180201733 | note | Verifying Document - IANZ Accredited Report
cc631a03-de9f-51fe-b990-03eca7eaba9b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
c39265b2-8d34-5498-8f40-cb6a5352fae5 | note | ○ Results to Engineer 2 wks before importing
dc36ed30-2224-5fe5-906a-704777807852 | note | Verification Activity: Activity - HP
e2904b03-9d5b-57fc-8112-c2ded59ad49b | note | Verification Activity: By - ENG
7c1072d9-9211-4eb3-a333-3a374b491666 | signoff | AUTHORITY HOLDPOINT
e549bcab-f8b4-4c4b-89aa-0f2b18a2535a | checkpoint | 1.3.4 - Particle Size Distribution
21905074-233a-5c29-bd22-0f6c5312f8d1 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
17817cc4-65d6-559d-bf51-ebe36e1db7dd | note | Acceptance / Conformance Criteria - Fitting within standard AP20 grading curve
d5d48fa3-2405-599a-987f-9839f49ca5ff | note | Standard / Specification - NZS4407:2015 Test 3.8.1
3bc44567-e051-53fc-8b23-cb54c00cde20 | note | Verifying Document - IANZ Accredited Report
eb95b3c4-a946-5795-bec2-d3a10ef36982 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
96210d56-2db6-5e0a-8621-177091d1cba9 | note | ○ 0-400 - 2 tests
fa2b0541-0133-5614-989e-15f20141ed8a | note | ○ 400-1,500 - 3 tests
85e44496-15eb-5526-bd7a-404220b60ea9 | note | ○ 1,500-4,000 - 4 tests
89a3f0f4-4824-5e8c-a3d7-416de95906e9 | note | ○ >4,000 - 1 test for each additional 1,000m3
3696ef95-c465-5ac8-a1f3-7d84b14699ce | note | – Results to Engineer 2 wks before importing
3e8fe53a-158a-5827-95aa-875f3f84624c | note | Verification Activity: Activity - HP
4470d900-b21b-5d0b-ae51-15f482a01e31 | note | Verification Activity: By - ENG
aa116de3-04e5-404e-89d8-13a03848a4cf | signoff | AUTHORITY HOLDPOINT
36755419-248e-4956-975a-8e9f6b2b56a2 | checkpoint | 1.3.5 - Maximum Dry Density and Optimum Water Content
3998ef8e-7a6d-5c90-901e-aea76ed8b597 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
cc8ebb79-ef65-5efc-a1c8-f382572924e0 | note | Acceptance / Conformance Criteria - Report Value Only
0747fab1-01c5-53d5-9903-e8e5ef508f68 | note | Standard / Specification - NZS4402:1986 Test 4.1.2
367b8787-7c59-50c4-867f-22596dc378d4 | note | Verifying Document - IANZ Accredited Report
6287b3e0-8044-5254-9685-8cb542f53a5a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, PerSource
492354e7-04de-546c-9244-d6177a768ac1 | note | Verification Activity: Activity - HP
826c7aab-30d3-5e6c-a3d3-91d7b1af16c3 | note | Verification Activity: By - ENG
384c4ceb-8fa0-4ece-b9de-28810c1c3082 | signoff | AUTHORITY HOLDPOINT
6e01f1e6-b1f4-40f6-8c39-ee96a1acd94d | checkpoint | 1.3.6 - Plasticity Index
645ff30e-c8fc-5bd5-ac0c-05ade350bb56 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
deec702f-fd3e-530e-9ac7-3d06a4fdb336 | note | ○ NZS4407:2015, Test 3.3 Plastic Limit
ac33ce72-b2ad-5cfb-8ac1-4e0eb8b2c217 | note | ○ NZS4407:2015, Test 3.4 Plasticity Index
90bb13b6-662b-5db8-8efe-5d424a4e427f | note | Acceptance / Conformance Criteria - NP
1880f645-9c61-5500-8c5e-cb97d0527d8f | note | Standard / Specification - NZS4407:2015, Test 3.2
42bcba65-0a93-5721-915b-8990b17d425a | note | ○ NZS4407:2015, Test 3.3
dda38271-c5ec-5e74-9ec2-45d4a5ecfc23 | note | ○ NZS4407:2015, Test 3.4
7384f4dd-a0bd-5ac2-b30e-1761389dbb9c | note | Verifying Document - IANZ Accredited Report
487899e5-4be9-5bfc-b894-f0fe7d55f1f6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
73ed4fb2-4d90-5e7f-ac5b-0a415c80841d | note | ○ Results to Engineer 2 wks before importing
601c0fee-85db-5378-a24f-c42aa6ff89d4 | note | Verification Activity: Activity - HP
31dac406-c163-5b24-8eec-fb2bb00dd3a1 | note | Verification Activity: By - ENG
d8c17930-d3c3-40eb-ae42-45879b1d4aad | signoff | AUTHORITY HOLDPOINT
73d9d1fd-53c1-4bd2-a22e-b67e8893c0af | checkpoint | 1.3.7 - Sand Equivalent
906ab5b6-efdd-58c5-81de-fb742190ea8b | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
5202b9e0-af87-51ad-abe1-d2a4ab87f19e | note | Acceptance / Conformance Criteria - >25
d1b8705c-a5c1-5f39-a173-bad6db5642b3 | note | Standard / Specification - NZS4407:2015 Test 3.6
fba379c2-6445-5240-a08c-ccf6390aa6de | note | Verifying Document - IANZ Accredited Report
d1faf77b-3553-5a7b-86b9-b5541c44a440 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
adb9a3d7-5f26-5e95-9eea-bd9f3e51602e | note | ○ Results to Engineer 2 wks before importing
0a76c7ab-5525-5fa4-ba97-0b5c08a8a7e2 | note | Verification Activity: Activity - HP
f27bcfb6-8bab-56c5-a8ae-5233b6128749 | note | Verification Activity: By - ENG
7efc9f38-58fd-4370-8f59-b456a753df84 | signoff | AUTHORITY HOLDPOINT
6eb1e21b-7524-48b8-bcb4-be9086a0f51e | checkpoint | 1.3.8 - Clay Index
e6e9976f-d269-53d8-9948-ade5a4c46be1 | note | Detail - NZS4407:2015, Test 3.5 - Clay Index Test Report
a204544a-9655-5eaf-8ae0-94c23050bf7e | note | Acceptance / Conformance Criteria - Report Value Only
ed66666a-939c-5d6b-80d4-ebbdfc80ee0c | note | Standard / Specification - NZS4407:2015 Test 3.5
13cce37e-9d7e-5f89-9cd8-1ca0086ecbc8 | note | Verifying Document - IANZ Accredited Report
97ec8565-a4c3-59fa-a9d5-af38e45a33e6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
171904a2-078e-5140-a621-507fe60265b9 | note | ○ Results to Engineer 2 wksbefore importing
ead4b109-9236-5e1f-8539-8ae9339484ed | note | Verification Activity: Activity - HP
ba43689f-7a12-52f4-9db0-1438ca6b5fdb | note | Verification Activity: By - ENG
14a33225-72a5-4aef-94f4-065633cc2a8a | signoff | AUTHORITY HOLDPOINT
e14214a1-854e-4049-be87-594c92750a1a | section | SECTION 2 - CONSTRUCTION - PREP GENERAL
6bda0229-254c-467d-aa84-8b6e68365e3f | checkpoint | 2.1.1 - Excavate to final depth
099a8847-fdc4-5969-b4bd-b6e8dab4d0bd | note | Detail - Subgrade Level
cd6f173e-f384-533f-afc0-c0be24fa37f8 | note | Acceptance / Conformance Criteria - Using survey pegs as hights and placement. Measure from stringline for depth. Tolerances as follows
dfb7b117-2821-5c1f-b2ff-ba872e54e516 | note | ○ +0mm -30mm
167d764e-d07b-5612-bd48-1db08dc42222 | note | Standard / Specification - drawings 232735.02-WSP-DR-UDL-0405,406 -TNZ B/02: 2005
2a904c15-54b7-5bba-a205-f4e7d4651e63 | note | Verifying Document - String checksheet or Equilavent
24a6e875-2088-5344-bd02-3e24ede26f37 | note | Testing Quantity Required (based from schedule qtys) - Every 15m
6144fa86-6d3b-5f06-96f0-88e1297e7166 | note | Verification Activity: Activity - D
fa5a3da4-f4b5-58bb-8feb-0f75835450ef | note | Verification Activity: By - SE
476bc088-8b5b-45b3-a336-cf6de1ea4be9 | checkpoint | 2.1.2 - Cut Subgrade Testing - Cohesive Soil Shear Vane
99dc2a57-1890-535c-9a57-cdcc2a3bb1fd | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
40cde751-46dd-5369-9b38-dae43fd189ea | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
3476fd0d-65b2-5a68-a78d-dea5990c735f | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
e4faae25-80f7-56ae-ad64-2d59e4f8602f | note | ○ CBR: >7
7bc137ea-19ed-5fb6-afd0-0bb4baccf464 | note | ○ Single Test Min SU: >50kPa
fe696828-f631-51e9-afe9-f2f452e97e4c | note | Standard / Specification - Appendix XVIII
c19280a0-1a04-5686-89c9-bbee60efac00 | note | Verifying Document - Shear Vane Report
b052f06c-1e89-5482-8332-458fb8f85525 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100M2
b9fa0108-1c9e-586a-9b02-e89c1f57fa46 | note | Verification Activity: Activity - I
1763fba1-d96b-5379-a39c-563ac8374656 | note | Verification Activity: By - SE
dfca1497-7053-4add-9af6-3e1fcad5f6ed | checkpoint | 2.1.3 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
5a41174b-92e3-553f-afcd-a68cf039bb53 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
c5c246fc-1bc4-517f-8db1-f1717ab81e83 | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
f0e0bb6c-4658-5456-8d2f-db2c318114dc | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
dbfc5a8d-4ac8-5ecf-9f14-11f4ce5d46c6 | note | Standard / Specification - Appendix XVIII
8986de9a-ac63-525e-ad76-c9eb9880d11d | note | Verifying Document - Scala Report
bccd3fd0-a534-5d70-bc22-f7ad7dfdedd9 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
4a2b4cf5-182e-53f7-af2c-5b27db15d956 | note | Verification Activity: Activity - I
0d2a9e8e-e62a-548a-8b21-0905bc25ea97 | note | Verification Activity: By - SE
b0538da9-3e9b-498f-8ca3-92ca0ee66542 | checkpoint | 2.1.4 - Proof roll
90b368d2-464b-5b97-a776-24c62107b76e | note | Detail - Visual Inspection of Proof Roll
09a8b521-ae80-5408-ba75-773e3f826509 | note | Acceptance / Conformance Criteria - Visual Inspection of Proof Roll
485f334a-b973-59b5-8a5b-ae208e558ef7 | note | Standard / Specification - Appendix XVIII
03cce3f3-e61a-514a-944b-24c40c04691b | note | Verifying Document - Visual inspection/ Photos
0dd0577e-1bba-515a-84f4-035fb19d5fe3 | note | Testing Quantity Required (based from schedule qtys) - Across Whole are
e94572c3-3e86-5f05-94ae-422ae385806b | note | Verification Activity: Activity - I
6edb14ba-4342-54f0-9b32-9fb2793f2ab3 | note | Verification Activity: By - ENG
05382cdd-8a95-4b15-ae25-7ed99ecbd77f | section | SECTION 3 - ROUNDABOUT APRON
f956c9a4-9632-4bfb-8eb9-d8e4ea9b870e | checkpoint | 3.1.1 - Surveyor check
d2af62d5-ba7e-59ff-8c10-171e2565a33c | note | Detail - Equivalent to check the position of the formwork
ba44c744-bfd7-5d9c-a80c-b139c295808c | note | Acceptance / Conformance Criteria - +\- 100mm of design
c9336583-e5a1-5b11-ac8a-de94e27d88e7 | note | Standard / Specification - NZS 3109:1997 (PS 27.4.5 Viii)
ecaee153-38ba-53a0-8786-2cf99a90a98b | note | Verifying Document - Check Sheet
109c9ecc-dd34-53ee-a752-3086acb31059 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
e865c47f-858c-5c66-9cfe-1996d7f4b869 | note | ○ 1 set = 5 tests
5e9b5f4f-9adc-5fd6-bcb4-572941d7ba2f | note | Verification Activity: Activity - I
69adfa43-e771-5f9a-bdd9-54eda71cd369 | note | Verification Activity: By - SE
cc1bc987-4fdf-4974-9bd1-ebdf738f80fc | checkpoint | 3.1.2 - Surveyor check
929fe70a-2371-5d77-8464-69dd26868ebd | note | Detail - Equivalent to check finished height of framework
8369205d-46af-52d7-ac1e-3ecef244ffc8 | note | Acceptance / Conformance Criteria - +\- 10mm of design
a023f643-7c39-50a1-8f25-a0b30ed3fc28 | note | Standard / Specification - NZS 3109:1997
0b5521a6-4a27-501a-be5a-e04d0d9dde2c | note | Verifying Document - Check Sheet
02a82dfe-ae01-5a24-afa0-47cecac1eefc | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
6943b9a5-f892-59f2-841a-47fbdc4c4c36 | note | ○ 1 set = 5 tests
5222ab7f-55fd-5b0a-b9ee-e8236b25ad33 | note | Verification Activity: Activity - I
10ecd07f-cc4c-55a2-b3bc-3f1767552181 | note | Verification Activity: By - SE
eb4e2bf7-7639-4b5d-9e86-08ddcb596adb | checkpoint | 3.2.1 - Concrete
1d9ba44a-f0a0-5fe8-bc6c-883b59a0c878 | note | Detail - 20 MPA: Include a mixture of nominal 10-20mm aggregate comprising grey, black, and brown-colored stones, resembling a riverbed
4d1ea62b-0ef4-5fa9-adb6-f6db30455244 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 20MPA
6c788c13-6a92-56b4-84b5-6214c12d9345 | note | Standard / Specification - PS 27.4.5
10466246-dafd-53bd-8aa1-7d6e66030cf2 | note | Verifying Document - Concrete Delivery dockets
42fe5bb4-076f-5e25-85d2-02e72dfee8a5 | note | Testing Quantity Required (based from schedule qtys) - During construction
b7ffb0dc-3eea-5a1d-abd4-5ddb0f259a98 | note | Verification Activity: Activity - I
18a4ac17-2fab-55bf-838f-e93a4dd5acc9 | note | Verification Activity: By - SE
300fd900-5235-448f-865d-373b26ee604e | checkpoint | 3.2.2 - Control Joint
6b3a54f8-760c-52c6-a392-79358c27f6eb | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
4c23f0ad-12dc-56c1-9ca4-30a32b546b3d | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
3ec6100b-51f7-5960-936c-93daf51b5207 | note | Standard / Specification - PS 27.4.5
be78c2e5-036f-55e1-9c75-a88461f10d83 | note | Verifying Document - Post Pour Checksheet
e7cc746c-7f6c-58c3-b416-75274d2c2931 | note | Testing Quantity Required (based from schedule qtys) - After pour
d24aae11-7580-5f91-bae1-4ae1d8c5924a | note | Verification Activity: Activity - I
fc7b5b0c-3daf-5c65-b2fe-343f23f8d45d | note | Verification Activity: By - SE
ba704168-e215-404c-b269-2b095e1ad581 | checkpoint | 3.2.3 - Final Finish
4cb3c4ce-dc9e-5952-8bf4-69c906b37b7a | note | Detail - U3
48d8ffec-7811-573b-b4e2-8c4c1c954fda | note | Acceptance / Conformance Criteria - U3
9904362b-e753-515f-aaa5-8d1c1aa5baba | note | Standard / Specification - PS 27.4.5
0ce723e6-204d-5019-95be-0f8d7fa62937 | note | Verifying Document - Post Pour Checksheet
8c985695-48b7-5042-be55-305ed423ccc4 | note | Testing Quantity Required (based from schedule qtys) - After pour
1551efce-d5d6-5ced-93cd-ce597fdaa2b2 | note | Verification Activity: Activity - I
65c55a87-55ce-5f35-aa60-c562d5ecfb09 | note | Verification Activity: By - SE
eb43b7dd-6a6f-4464-b529-cb007482569d | section | SECTION 4 - ROUNDABOUT RIVER STONES
4f5807cb-e5bf-4d67-88b5-f4b029dec27c | checkpoint | 4.1.1 - Surveyor check
50a00c49-0054-50df-896e-089d3d537230 | note | Detail - Equivalent to check the position of the formwork
4916dcba-b71a-52aa-8dac-5a8733090ff1 | note | Acceptance / Conformance Criteria - +\- 100mm of design
5ae2aa0f-cbb1-52ba-84c3-468e92253e30 | note | Standard / Specification - NZS 3109:1997
a99cc85a-0e2c-59b7-9809-fb68e2454dbe | note | Verifying Document - Check Sheet
2c1c2671-20f9-56fb-bdb5-5b373a9813a8 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
ac361a4d-677d-5e74-820b-2a4b97169de8 | note | ○ 1 set = 5 tests
bd38304b-2e76-518e-be13-5c3e59913f57 | note | Verification Activity: Activity - I
16fbf902-7fbc-5474-bb46-397dee690f16 | note | Verification Activity: By - SE
1667ec25-52cd-49f2-b69e-1493594b2d9e | checkpoint | 4.1.2 - Surveyor check
f18a26f9-5eda-53f7-87b3-8b56c91dd147 | note | Detail - Equivalent to check finished height of framework
b338ead5-eb91-560b-9b05-826db96e386f | note | Acceptance / Conformance Criteria - +\- 10mm of design
eca88fff-b6e1-52d8-bd86-fef493273a69 | note | Standard / Specification - NZS 3109:1997
4aa509b0-cb3d-5c2d-907b-d3e1e6aa6a2e | note | Verifying Document - Check Sheet
e3bc4eb9-efd3-54e0-9ee1-d680efae205c | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
814b8502-0e2b-5842-b03a-132dfb65cba5 | note | ○ 1 set = 5 tests
cf79e5b9-dc4b-5000-834c-cb34ac8e429a | note | Verification Activity: Activity - I
d73bab97-96dd-54cf-b000-249c00c1a11d | note | Verification Activity: By - SE
886c4573-0d6b-4c30-9836-f6c7dc4c2491 | checkpoint | 4.2.1 - Concrete
e00cbba4-defd-582f-b772-03f6988b24c8 | note | Detail - 20 MPa unreinforced concrete
dc23a0fc-a15b-59d9-bcc6-7877117a9fd7 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 20MPA
9db58c13-8735-5d3f-a82d-4fedc197cfb3 | note | Standard / Specification - PS 27.4.6
ed13d637-3ec8-54b3-99ee-f115c2803d8f | note | Verifying Document - Concrete Delivery dockets
ef0f98ec-7f63-5a06-aac0-d20a4afb53e8 | note | Testing Quantity Required (based from schedule qtys) - During construction
bc2b9e2d-aa8a-591e-b094-4db71721ffdc | note | Verification Activity: Activity - I
7aef2ae0-bb75-56b0-878e-a18cccbc4ba3 | note | Verification Activity: By - SE
2c7268bc-6851-4689-9442-3401b1055289 | checkpoint | 4.2.2 - Final Finish
0f27e145-12c2-5a9c-b5d6-663b188c38d9 | note | Detail - Riverstone from a selected local quarry, with a diameter of 150-250mm, will be set into the concrete. The stones must be embedded at least half their height into the concrete for stability. Place the stones closely, ensuring gaps between them do not exceed 50mm.
20fec73c-72c5-576a-85fa-186e7a26999d | note | Acceptance / Conformance Criteria - The protruding portion of the stone to be 50-75mm above the finish concrete level.
c4779584-be4b-51d5-8e4c-aa3086018c28 | note | Standard / Specification - 232735.02-WSP-DR-UDL 0406
b0d95f44-fc73-57a8-8023-e4b7f710db79 | note | Verifying Document - Riverstone delivery docket & photos
bbca0c65-ef1a-5a80-940e-56b2b7056954 | note | Testing Quantity Required (based from schedule qtys) - 150-250mm Riverstone protruding 50-70mm gaps 50mm
e89fe579-26f7-52ef-a92e-4147a06e3303 | note | Verification Activity: Activity - I
e577fbf4-7051-53ea-8539-b125ea447e09 | note | Verification Activity: By - SE
cd1994cb-e228-428f-b3e1-c050b7a5284c | section | SECTION 5 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
e58d69ef-48e3-4d37-bc39-47092fac2b8b | checkpoint | 13.1.1 - Final Inspection
8ab94d08-4ea7-5986-877e-5e688feb0fb8 | note | Detail - Final inspection of all concrete work.
8095e6e5-7b25-5550-8083-5744002099fa | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
8e383182-5383-5141-beeb-819c65466d8d | note | Standard / Specification - NZTA P39: 2013
d724ce8e-5c2a-55c3-800b-eed53ae88aad | note | Verifying Document - Final inspection report
3f6367d0-f4a4-5301-9477-d9d73b738c9a | note | Testing Quantity Required (based from schedule qtys) - 100% of works
ec1c366f-1920-50fe-91cc-5efad46c9adc | note | Verification Activity: Activity - HP
4a38cef9-f660-5aa5-9611-d20c8831892f | note | Verification Activity: By - ENG
8fd723f4-664d-4321-b26a-4bb8e4dce35c | signoff | AUTHORITY HOLDPOINT
4c2c66f7-26fb-4f17-9d45-46986db70cb3 | checkpoint | 13.1.2 - As-Builts Red Pen markup
f3f12ed6-5cc0-5b6d-9aa2-f7352f127e69 | note | Detail - Final inspection of all concrete work.
63c88875-43f6-5413-9c92-87c23d2b4509 | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
39eb8325-9eb0-5919-885b-bdf00361b07c | note | Standard / Specification - PS 16.7.6
e30b6d68-d3db-5546-afd0-b3a19c906ee5 | note | Verifying Document - Survey Records, Red Pen Mark up
4c63e240-f743-5628-bc40-9a8ec37b65fd | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
9480740c-0aba-5868-bbb6-02e0c15e0ac5 | note | Verification Activity: Activity - D
cd5af709-aff4-5b84-a621-b24a4931d7bb | note | Verification Activity: By - SV
4505003c-1c52-4b59-8def-f9c0230c11e3 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
29878b6f-eb0b-5113-93e0-5156a241082a | textbox | Contractor's Rep Name:
3b80f30d-084e-5b29-8316-b288a5a72264 | textbox | Engineer's Rep. Name:
1294135c-9e75-50da-841c-9858d7a4960a | date | Date:
b611c4d4-85ba-4345-a7a8-f935e6b93a1f | signoff | Add Signature
5f13b3f7-6ac6-4e75-83c0-1346780bb34f | checklist | DN1210-021 ITP AC14 Surfacing Rev 0 | itp | DN1210-021 ITP AC14 Surfacing
d6be62dc-cdc2-4b5e-9d64-9133eb395e31 | section | 1.0. Pre-Commencement Activities
35b5ccfb-12c5-4cf2-8e41-40386a858184 | checkpoint | 1.1 - Approved JMF for Asphalt Base or Wearing Course
e6941523-351b-5251-902e-89dfe46ac7f9 | note | Detail of Activity / Test - As Per DN1210-WSP-GCO-0160
01c94187-c20b-58e3-ae06-b4488b56f0b1 | note | Action (Hold, Monitor, Witness) - H
9d9a69ee-d601-51bc-a5dd-760b7dc72c7c | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
387d8efc-dc62-54ad-b49a-c02f418d39d3 | note | Inspection / Test method - Confirm requirements are followed
2b1916e4-cf10-5382-80a3-0674eaf7c903 | note | Acceptance Criteria - JMF Validated in accordance with NZTA M/10:2020
928e220c-a370-55d6-8fed-422aa14db513 | note | Record documents (QCP - Quality Control Portal) - Mix Design Report
d35323cc-23ee-51d8-889f-13310cffb953 | note | Responsibility - Paving Contractor
d3318a0b-0b35-50e6-a907-46bd437f63af | note | Project Specific Notes / Instructions - JMF expiry date and validation details in here
92ef250c-c967-5efe-8f19-67235aa3c6fe | note | Designer - A
6c39cccf-c064-50f5-80b5-34dd18c9a655 | note | Eng. Rep / NZTA - I
2356e515-1591-53b6-8e88-2039f30a72ff | note | Contractor - R
490d4c84-643d-4954-bf9f-6a5ff5d1ab26 | signoff | AUTHORITY HOLDPOINT
52d48c4f-4b59-4664-9ab5-98b5ece55c94 | checkpoint | 1.2 - Site Conditions
8d112c55-196f-54be-8cad-f3a2eb68e215 | note | Detail of Activity / Test - Weather suitable, Site extents marked, surface suitable for paving (Depths/milling/cleanup complete etc), Environmental Controls in place
4e873c1d-2402-5ab3-8cbc-b8018074a08f | note | Action (Hold, Monitor, Witness) - H
39008e32-9e09-5235-8f62-f3390aaac2cb | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
b28a48ee-c695-53ba-96d0-8ee9d2cd6aff | note | Inspection / Test method - Confirm requirements are followed
fa1da597-cac2-5fd5-834d-63a148db3d0b | note | Acceptance Criteria - Weather conditions and Site is suitable for paving
e3ed865e-9e11-5d42-a043-ee40787ae8e6 | note | Record documents (QCP - Quality Control Portal) - Site Diary
51f3901f-c83b-5cf2-8bfd-ccd498c51ef8 | note | Responsibility - Paving Contractor
c045ce09-abb8-5f09-a87c-8364614133b5 | note | Eng. Rep / NZTA - I
0852d866-664c-564f-b02c-21f380661616 | note | Contractor - R
f7bd631d-688c-4226-8504-f7e27365ee87 | signoff | AUTHORITY HOLDPOINT
af97e48f-4ab9-4059-8d93-13d40c8c5cb6 | checkpoint | 1.3 - Traffic Loops
2b8e9162-4523-5a60-a595-2a32b4face7c | note | Detail of Activity / Test - Communication with affected parties
88039f4c-1c73-513b-89e6-ff12f4fc2a3e | note | Action (Hold, Monitor, Witness) - H
dc3f9cc1-fe3a-5620-9417-5d23eb440b4a | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 7 days Before Works commence
88825b0a-7589-5fbd-bb1d-f374549a802d | note | Inspection / Test method - Visual
4b4b3c01-0eec-5d27-8710-83f529d8159a | note | Acceptance Criteria - Notify RC at least 7 days before surfacing is programmed
dabd54ed-031e-529f-b132-e532a3af5937 | note | Record documents (QCP - Quality Control Portal) - Communication
e3c7d56d-d12c-5563-bc8b-1e5fc8f66f93 | note | Responsibility - Paving Contractor
bbbae925-4997-5f18-9e5e-460c56529ac5 | note | Project Specific Notes / Instructions - only required where existing traffic loops are present
5f1770dc-08ff-5d0d-adfa-78fe850c2a9b | note | Eng. Rep / NZTA - A
7f854da6-fe6b-5676-ae6c-5b51e44be32d | note | Contractor - R
becf5e44-2891-4cf4-a65c-52e88ae7c32a | signoff | AUTHORITY HOLDPOINT
f23f9df8-c813-4806-9e33-f99a254cb552 | checkpoint | 1.4 - Paving Plan
1f704cd8-6e33-5691-b23a-cdd23273b846 | note | Detail of Activity / Test - Paving Plan to be completed
6e00be73-3013-5290-8a88-8db285905cc3 | note | Action (Hold, Monitor, Witness) - H
7cb35ac4-e96e-5666-829d-59bf3425b304 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
13a91a9f-8313-5ec7-a11a-7a216c41ed68 | note | Inspection / Test method - NZTA M10: 2020 Clause 9.5.1
80f03de5-664e-584d-9afc-e58fb5dc53b7 | note | Acceptance Criteria - Paving Plan to be completed for each shift with dimensions, location and type of (hot/cold) joints, areas and tonneages
25ad6f0d-548d-5834-98f2-c77205f412ae | note | Record documents (QCP - Quality Control Portal) - String Sheet
00528317-e316-5bd1-a0a3-63fee63823d6 | note | Responsibility - Paving Contractor
803d0b3e-25e8-5d76-9b8a-6e4c639e1c07 | note | Eng. Rep / NZTA - I
8b0f7422-ae71-5ec7-9309-367b33e7b47f | note | Contractor - R
4e4226e7-b0f0-49c9-8035-bd02c4e9ca79 | signoff | AUTHORITY HOLDPOINT
f080feaf-f742-4747-840b-609daa0abcae | section | 2.0. MANUFACTURE OF ASPHALT
ca31d17d-221c-4656-93e2-9d47cbdf9b82 | checkpoint | 2.1 - Temperatures
b90c0c5d-4671-54e3-84fe-a433e1a2e825 | note | Detail of Activity / Test - Mixing of aggregates and bitumen
d7750391-c691-5526-9ae3-ecdc3c33365e | note | Action (Hold, Monitor, Witness) - M
5e20cc49-cbde-50bf-a736-5a8e29f3961c | note | Minimum Test Frequency (Lot = 1 day’s production) - Constant monitoring of temperature by calibrated euipment
39dd64b2-a24c-52cd-a351-c635c2bbce16 | note | Inspection / Test method - Plant temperature probes
5b252a87-6e0f-5af2-a312-a6fe9de44952 | note | Acceptance Criteria - PNZTA M10: 2020 states max. 185 deg.C
9fa9f57a-6390-5f66-b99e-fe7b4cd83f33 | note | Record documents (QCP - Quality Control Portal) - Plant site diary
06a43304-5f7f-5ddd-b358-765f4a866036 | note | Responsibility - Asphalt Manufacturer
5f49785e-1171-53e7-bed7-324a6cde6d0b | note | Designer - I
286e200b-f455-5a2c-bb4e-5bef3fc6d429 | note | Eng. Rep / NZTA - I
b7253c08-9aff-5d66-ada4-3a81eb661c3f | note | Contractor - R
354cf9f4-c635-400f-be35-bccb2242cb15 | checkpoint | 2.2 - Production Asphalt
f9177c07-b050-5ca1-a969-2741a7d7f84c | note | Detail of Activity / Test - Particle Size Distribution
366e31e7-60d2-5964-b81b-cc68f9049c4d | note | Action (Hold, Monitor, Witness) - M
c457ff2a-8719-551b-a35e-658580d649bf | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
45f7c15b-0030-54a0-8740-a874f21c89e3 | note | Inspection / Test method - NZS 4407 Test 3.8.1
1a52e594-5f7a-5320-b2bd-d78534df3f8f | note | Acceptance Criteria - NZTA M10: 2020
91576850-c543-5c62-8b5f-3cabf35b02bd | note | ○ Refer to Table 5.3 (Refer to CWP for image)
6bd7090d-61e3-5373-bb3e-63f9390d3918 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
0472b718-4aeb-5b0f-8712-7746118a5d55 | note | Responsibility - Asphalt Manufacturer
6fe4ca11-e7a7-5de7-8f61-c567017252bd | note | Designer - I
90c292c9-d0cd-5b48-9432-853b9923cfbe | note | Eng. Rep / NZTA - I
d9bec883-55ec-5b13-b2c0-a8f727288101 | note | Contractor - R
ea1656bf-964c-4c5f-a774-d09992059fe5 | checkpoint | 2.3 - Production Asphalt
0bc282a3-fe03-5262-a0f2-727dcc8bf697 | note | Detail of Activity / Test - Binder Content
f9ec9f15-876a-5849-91fe-21b24b463559 | note | Action (Hold, Monitor, Witness) - M
9c0a1947-bd0f-5be9-9345-978eb0abfdb6 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
fd1d1422-2da2-5b55-92f2-a3af48b2c444 | note | Acceptance Criteria - NZTA M10: 2020
42a57765-15a4-52db-ac76-6ec8940b8cc0 | note | ○ Individual Test Result: ± 0.5
f3046e03-6ff7-5ab2-b63e-63b0aba5c76c | note | ○ Mean of Three Test Results: ± 0.3
730f58f3-faf1-5b17-984d-df65024c9d31 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
3eefc2c2-82ee-504e-bcb5-43a994c838c9 | note | Responsibility - Asphalt Manufacturer
fc00c326-51c2-57cf-887c-684d6cfa8e6e | note | Designer - I
37c1cf31-30df-593f-b2a5-1d981ddea4b6 | note | Eng. Rep / NZTA - I
4ce93999-0116-5227-8993-74a063e62a62 | note | Contractor - R
c9b0813c-af91-4447-8a17-99cf3529ee1c | checkpoint | 2.4 - Production Asphalt
38bd32da-9ac2-53dd-9afe-a5828232746e | note | Detail of Activity / Test - Max. Specific Gravity (MSG) of mix
e40d3e99-bc1f-5154-968e-73d2f13d3a93 | note | Action (Hold, Monitor, Witness) - M
052a0ee2-4045-56fe-b5db-51ef7734985f | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
64ad79c1-5488-5bb2-9c32-47cf4ff612e4 | note | Acceptance Criteria - Report
6204e37a-0519-5272-9779-6afba53157a7 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
4b91d436-3025-577f-8fef-daff65e7bb27 | note | Responsibility - Asphalt Manufacturer
6c5fc4ce-56c1-5300-8b70-d39db864360b | note | Designer - I
1b0bed92-7557-5e07-9ab4-ea8ecc0661f9 | note | Eng. Rep / NZTA - I
cb28d9c1-2280-5537-8740-e08a8241fdb4 | note | Contractor - R
866c0702-1f86-45ae-9b5a-48d58c67d8a3 | checkpoint | 2.5 - Production Asphalt
6f143446-88b4-5a40-bc15-69031669977b | note | Detail of Activity / Test - Air Voids at lab design compaction
473df85a-9d32-53de-a3a2-fbcbbdbf687f | note | Action (Hold, Monitor, Witness) - M
b1646479-908e-5b63-8eb0-dad37c1ab8d2 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
382f5f3b-9cce-594f-ab83-f447838498d3 | note | Acceptance Criteria - NZTA M10: 2020:
1f885684-7f82-5ed7-bdc6-cf5481950904 | note | ○ Individual Test Results: +2.0, -1.0
30bf49ef-6e6f-5592-9ae0-dbb986b7633d | note | ○ Mean of Three Test Results: +1.2, -0.6
0e82cdcd-5c6d-5ddb-9831-825c24fa42c3 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
4e7ac522-f48e-58cf-96e7-5ac20cfb6850 | note | Responsibility - Asphalt Manufacturer
b0ee6981-3364-51e9-8556-dbdba8d9845e | note | Designer - I
7e7fcdcb-2bed-53ad-97ef-65fed15b599f | note | Eng. Rep / NZTA - I
86a99dc7-1f61-5121-a6a7-8538e65f8746 | note | Contractor - R
e0bdd83f-fbc7-45e7-b47a-865462cee1f1 | section | 3.0. PLACING AND FINISHING
7ab700c5-b157-42db-abc2-5d6319b9bbf8 | checkpoint | 3.1 - Membrane Seal
26c9de9e-9d4f-5005-b7cd-7dc7fad71406 | note | Detail of Activity / Test - Application of Membrane Seal
3d97afda-bf7b-5261-aa24-abf810fb8660 | note | Action (Hold, Monitor, Witness) - M
362b7d05-b221-556f-9e0b-518ea2469aad | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
fde437ec-ee02-5a6b-acd7-f2dfa70e9e05 | note | Inspection / Test method - Sealing Records
338804ac-085e-5cfb-bb32-a2e1f85cdf2d | note | Acceptance Criteria - Application rate, chip type and binder as per membrane seal design
1d30ac5f-1888-58d7-90cc-0ab351a916b4 | note | Record documents (QCP - Quality Control Portal) - Sealing Records
c51017f5-69fa-5532-86cf-8d36dbc9c456 | note | Responsibility - Paving Contractor
1e255417-0ec7-519f-87cd-b06da6d846d2 | note | Designer - I
726d0e23-9675-5fc5-93eb-c0873d4da700 | note | Eng. Rep / NZTA - I
7ebd93e3-4b97-58d1-96c2-d03ab85766ea | note | Contractor - R
915c5e54-9648-4ea8-9186-0b5ea06af445 | checkpoint | 3.3 - Temperature
81895b9f-d01d-5d0f-9634-c0e13ab8ceb0 | note | Detail of Activity / Test - Asphalt Delivery temperature
84e38848-2445-5a4d-8726-2c3f8035270c | note | Action (Hold, Monitor, Witness) - M
bc4e31bc-f5f0-5e66-9f36-abe37b1756f9 | note | Minimum Test Frequency (Lot = 1 day’s production) - Every Load on delivery to the Paver Hopper
ddc57c2d-3090-5bb0-aca6-5c668978f649 | note | Inspection / Test method - Temperature Probe
f4fa3ba7-567d-548b-b1dd-af812f91d9fd | note | Acceptance Criteria - Target ≥ 150 deg.C. in the Paver
1c3d4289-6b47-5e76-bdb0-6deb0abfa3e9 | note | ○ Min. ≥ 130 deg.C in the Paver
bf03fae7-f970-57e9-b380-d839ca7684c2 | note | ○ <130°C to be Rejected
38a01c7c-ec4b-5bea-99e9-7c2f85665cc8 | note | Record documents (QCP - Quality Control Portal) - Site Diary
3f189313-e16d-5ff9-9f4f-0d41e904b585 | note | Responsibility - Paving Contractor
bf7be3a5-6008-540a-8aa5-6e3dbbdbdb02 | note | Designer - I
430c91de-fd51-5f9d-b1a0-049aaa4c44a9 | note | Eng. Rep / NZTA - I
3333f010-068e-595c-a48c-7abeba817bab | note | Contractor - R
89fdd906-cbbf-4c3d-b22a-5ee064ef953d | checkpoint | 3.4 - Temperature
4e95d422-f093-5dd7-b57c-735a30782c10 | note | Detail of Activity / Test - Compaction Temperature
ed056f01-90af-5d28-b17e-66f68a7a4c14 | note | Action (Hold, Monitor, Witness) - M
56f933e3-65a2-53f8-8800-458ea2b17159 | note | Minimum Test Frequency (Lot = 1 day’s production) - During compaction
4e6d1d7e-fa0a-5bbf-a9f7-018ba2edddd7 | note | Inspection / Test method - Temperature Probe/Infrared gauge
60d0248a-4502-5299-b415-518232e4670a | note | Acceptance Criteria - ≥ 125°C at commencement of compaction.
722b0f7e-0b1e-58b0-aa15-3da965836e24 | note | ○ < 80°C - Stop Rolling
ddcc815a-9dfc-5c74-941e-3d663bac16fc | note | Record documents (QCP - Quality Control Portal) - Site diary
47941e3c-32b4-5688-97c3-9af1a21e7e02 | note | Responsibility - Paving Contractor
48bc3c09-4c3b-5977-975d-552c7005deea | note | Designer - I
f834589c-87ed-58c3-b204-e63923d286c9 | note | Eng. Rep / NZTA - I
c870bc04-aab2-5e23-a297-54862dbb6bb3 | note | Contractor - R
43d4698c-c59e-451f-9a94-588f4c854f8f | checkpoint | 3.5 - Mat
d2f77fed-0253-576d-b4a0-da04da63a9ec | note | Detail of Activity / Test - Load Locate
1dd8638b-ce8e-5dc2-a6ed-8bbb1edc0491 | note | Action (Hold, Monitor, Witness) - M
6158e486-2050-5bb7-bcf8-2e720fc42706 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each load
3046449f-3cf9-59ff-8c03-dce996f96403 | note | Inspection / Test method - M/10
b43470b3-4bc7-58dd-a859-ecb2fb4f8d16 | note | Acceptance Criteria - Each load can be indentified to a location using a diagram. Record includes:
b7c320ae-252f-58c0-9153-40f5ff367b5a | note | ○ Truck ID/Rego/Driver
d8050cfe-0811-5777-bbf1-4d92271f201b | note | ○ Depart Plant Time
7aed7eac-8165-51d4-83e7-62e13da3a592 | note | ○ Arrive Site Time
2c9da7ad-6ccf-5448-8eb3-c93af3d470f6 | note | ○ AC Temp on Arrival
bb6fc437-0466-5e95-a459-8f19b1a595e8 | note | ○ Tonnage
74abe666-8343-57c6-aa27-d1fe585bb194 | note | ○ Run Width
382f9596-830e-5f87-bb25-92094196c025 | note | ○ Estimated Run Length
855dd588-5e85-5532-b974-bce3e2b06699 | note | ○ Calculated Area
790803f4-6689-5ac8-9f14-398916e5d91e | note | ○ Calculated Average Depth
f0d1f1d5-cd04-502c-b991-d9ea92363ca9 | note | Record documents (QCP - Quality Control Portal) - Paving Run Sheet
bfd0e11f-acbb-5a53-a9f0-f68d66674f6e | note | Responsibility - Paving Contractor
9e286fe5-aef7-56e2-bfcf-620de23a83fe | note | Designer - I
d4cf0d2b-2579-5801-a165-9a752d36164c | note | Eng. Rep / NZTA - I
bb713f0f-9592-5c18-bcc0-0f8309b903db | note | Contractor - R
e9b6077a-d7bd-41fa-88c7-3457488bb680 | checkpoint | 3.6 - Mat
fedcbb8f-1750-5d40-8657-bb244d43b34d | note | Detail of Activity / Test - Thickness Monitoring
b241d227-acf4-5601-af64-ee2cff753677 | note | Action (Hold, Monitor, Witness) - M
d3682024-afc3-5a1a-86c0-34f806c2ff79 | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
03bed458-a941-548f-9a67-3e46bd4e1811 | note | Inspection / Test method - Dipping
197723a7-0c7c-51fe-87e3-3a0c4d9f959f | note | Acceptance Criteria - Target Loose Thickness -0mm / +10mm
ae2dfd0a-4ef4-5b31-99fc-01d6ea43e924 | note | Responsibility - Paving Contractor
f2992b7d-89ac-5e1f-b964-98d78a1b9852 | note | Designer - I
5f072418-b5a0-5f7f-9344-5291f03d6037 | note | Eng. Rep / NZTA - I
01764861-5e7c-56d1-b33c-b3acfee771fd | note | Contractor - R
315bc808-5a57-4306-8b2c-d1451a6d3370 | checkpoint | 3.7 - Mat
2c52fd98-2725-50c8-b94c-4bbcf4571786 | note | Detail of Activity / Test - Compaction - NDM
1689ec91-04cf-5248-a0e3-fdc6494d14e8 | note | Action (Hold, Monitor, Witness) - M
22928dc8-4749-5f2a-be00-d1bed3b851fd | note | Minimum Test Frequency (Lot = 1 day’s production) - Plateau to be completed on 1st run, thereafter monitor compaction/roller passes to achieve target density.
bf249e1b-4eea-55a6-9267-75b1836ad7ba | note | Inspection / Test method - Insitu density and air voids
2c596da7-6c65-564e-8485-781b3ae07d3c | note | Acceptance Criteria - NZTA M/10: 2020 - section 9.9
e0eb5dc0-e5fa-532d-aada-b0e9346dfe7b | note | Responsibility - Paving Contractor
be666b0e-af9f-55ab-8727-f366011ec1a9 | note | Project Specific Notes / Instructions - Use a calibrated NDM with established core correlation. Locate and mark cores, record NDM Bulk density by core location (including any offset used).
fd05ee86-b3a6-56d7-9f3a-9fa2347e9677 | note | Designer - I
fe0eda0f-1553-5d04-b4bc-b645b9fb608b | note | Eng. Rep / NZTA - I
b347783d-407d-55bc-b8d9-678e91ca7a79 | note | Contractor - R
937eeb84-f724-4b5a-a835-086f9fa3d032 | checkpoint | 3.8 - Mat
0e675824-722b-5212-a09d-e6816bada809 | note | Detail of Activity / Test - Compaction
13e38e60-87aa-59f3-a60c-bf9f9ccab32b | note | Action (Hold, Monitor, Witness) - H
cb1b5a4a-d79f-5cac-9f5f-e4de560ca31a | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 1 mats and 1 joint
661510e7-9a8d-55b1-8390-811f0bb0e2d2 | note | Inspection / Test method - Insitu density and air voids
bdf47283-4326-5ddc-9568-abe3ab0db046 | note | Acceptance Criteria - NZTA M/10: 2020 - section 9.9
04216aaa-58ef-526b-88ee-61149cbd7580 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
860e64a1-665e-539f-8641-d1cecab3dce1 | note | Responsibility - Paving Contractor
0cbd9ccd-f72b-5f81-ae06-de70f433c52f | note | Project Specific Notes / Instructions - A pavement lot shall be an essentially homogeneous section of work completed within a shift of production.
6f9e4b52-da54-5b73-8fa1-18d019437b30 | note | ○ The lot shall be divided into an appropriate number of approximately equal sub-lots and a core shall be taken randomly within each sub-lot. The Engineer or their delegate shall use a random method for locating each core position, such as ASTM D5361 or a similar process.
7f62098e-be6d-57ff-b80b-4f553ab4d58e | note | Designer - A
4db7f61a-3b11-5921-8911-155591d39ef3 | note | Eng. Rep / NZTA - I
e305f1e5-e891-5446-90f5-ec267ab17392 | note | Contractor - R
ea3b19cc-95c5-4695-8500-5ab6471835fe | signoff | AUTHORITY HOLDPOINT
bda8b1a0-182c-484c-bd21-b0f2c0c3b39c | checkpoint | 3.9 - Mat
ccfae955-7c4f-5ae5-8f7e-f1cfc4e8d4aa | note | Detail of Activity / Test - Thickness
ea9c1258-5691-599c-901c-b12cefd8ab2b | note | Action (Hold, Monitor, Witness) - H
5e95e77e-e99d-5b96-857b-e9f95de077af | note | Minimum Test Frequency (Lot = 1 day’s production) - Average of 3 measurements per core
3dabc6c4-f1d7-5198-830d-43121d2c5186 | note | Inspection / Test method - Measure Cores
a4bd2118-d712-57cc-afd0-950f32147442 | note | Acceptance Criteria - Average Thickness > Specified Depth (Nominal)
2c5bb38c-5767-58d5-8677-a09a1f68a4f7 | note | ○ NZTA M/10: 2020 - section 9.7
9b2cc3e5-487a-5df5-bd83-5f6bc1fddcec | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
2fcbceab-b984-5fdc-9b06-13dddc469e28 | note | Responsibility - Paving Contractor
b3d12e15-a6a6-53ae-a36d-11f69c077946 | note | Designer - A
4863bc80-6e67-5423-aac1-98c7e0981169 | note | Eng. Rep / NZTA - I
d4e8ea53-d1a4-5da4-9963-4989d6f1c371 | note | Contractor - R
215d0012-60ae-4e8e-aa38-1c497bb73cd5 | signoff | AUTHORITY HOLDPOINT
1ae1c02e-0d4b-4144-8177-ccdee6c033b4 | checkpoint | 3.11 - Mat
435c79d4-b345-5bbb-87b0-fe1ce07e8da3 | note | Detail of Activity / Test - Shape
566c1562-8d64-5a9e-bb02-b387caa59717 | note | Action (Hold, Monitor, Witness) - M
585bd2bb-78ae-5636-b66d-f424d9838e79 | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
38a2a5c3-9c47-5da5-b8a2-f24f34caca60 | note | Inspection / Test method - 3m Straight edge
ba82ffa0-38ee-5172-85e6-8fd679e4f672 | note | Acceptance Criteria - Where the length of the site or the geometry is such that a road roughness-measuring vehicle cannot be used then the straight edge can be used for checking the surface shape. Refer NZTA M/10: 2020 - section 9.8.
fb74bd17-23c3-5bad-b4b7-fdb329b8069c | note | ○ Not more than 5mm under a 3m Straight Edge.
18d3dc1a-c0eb-5553-9c15-c37f6da06f03 | note | Record documents (QCP - Quality Control Portal) - Straight Edge Record
d2f33e2c-4498-559c-8993-55fd842ab6e0 | note | Responsibility - Paving Contractor
0cd1bfcb-3b79-598a-b7da-571c8f96a8ae | note | Designer - I
db6e1a32-7059-58e8-ba11-78338ab2813f | note | Eng. Rep / NZTA - I
24196802-9ca0-59b3-9d3e-dab77a4b10e2 | note | Contractor - R
ce429907-72e2-4aa1-ae79-73b90e52a3dd | checkpoint | 3.13 - Paving Quality
6f896ab4-226c-56e8-8174-d89b1111dfd1 | note | Detail of Activity / Test - Level
ad43e35a-7d98-56fd-ac75-8fc72aa4a7ac | note | Action (Hold, Monitor, Witness) - M
2a987c72-235f-57f9-9f6b-257662a50b5f | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site
6fccf511-2225-5c93-afbe-d677abbd8749 | note | Inspection / Test method - As Built Survey
b6ef1287-ec06-559d-b963-8574e7a0af2a | note | Acceptance Criteria - -0 < +5mm from Specified Level
d62f2f5d-02db-5ff9-89cf-c4c09e37079c | note | ○ Where there is Kerb and Channel shall be flush with or no more than 5mm above the LOC.
a8241c7f-4d1e-5d69-99bf-d81eb08d6a8c | note | ○ NZTA M/10: 2020 - section 10.2
094d69d3-2680-5ff0-916a-0dcb5208670f | note | ○ Note: Minumum 55mm not nominal 55mm.
9796ac3a-2f57-5072-966c-4fd931643466 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
e657cff9-1c2b-5aaa-8eb9-e5efc84fe488 | note | Responsibility - Paving Contractor
2776e57e-bc51-530f-8185-e2cc86906b7f | note | Designer - I
01edd3ee-385b-5e5f-a00d-d436865efa3c | note | Eng. Rep / NZTA - I
8b1db29a-d5f3-533d-ad20-48d96b408f38 | note | Contractor - R
d083cdc9-0d0c-46e5-a9e4-e6859af8e624 | checkpoint | 3.14 - Paving Quality
20e16404-21cd-53a8-aa1d-ba7196b9a9a6 | note | Detail of Activity / Test - Alignment
d8eb17da-a969-5f40-97bf-015ee6dc8b5c | note | Action (Hold, Monitor, Witness) - M
159aed3d-6e63-5912-8019-f3d0e01d3bb3 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site
37bf6818-5c0b-5a24-9165-21271462e239 | note | Inspection / Test method - As Built Survey
739dbd29-a9bf-5bc8-bc6b-8cb3ca747abf | note | Acceptance Criteria - Kerb to kerb
9b8f82b5-0430-555f-9225-29911a6bfebe | note | Record documents (QCP - Quality Control Portal) - Survey As builts
64b3ad22-46fe-504e-bff3-2275bfc2afcb | note | Responsibility - Paving Contractor
476a40be-64a8-5cb5-8e9f-7b45369bd658 | note | Designer - I
b437269e-b03f-5d40-ba21-4a68b7c95cc0 | note | Eng. Rep / NZTA - I
c9826fe5-3137-5046-a24d-69106c0e0754 | note | Contractor - R
49a39d5c-8b46-4003-8d4f-ff38d36a58b5 | checkpoint | 3.15 - Post Paving Completion Checks
6cf91122-30b4-59df-9548-5ccfa6f98cd9 | note | Detail of Activity / Test - Site clear and cleanup
772a13f5-9c18-5045-a8f8-886a1594bfe6 | note | Action (Hold, Monitor, Witness) - W
e97579f9-76b0-59a9-896b-ecbf29469532 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
39c595e1-e6ce-54df-a9fa-9c1ee993927a | note | Inspection / Test method - Visual
103e4ab5-0c9f-51eb-9243-efa80f7d4046 | note | Acceptance Criteria - Site is cleared of plant (or parked in safe location) cleanup of all waste mix, paper and detritus is complete
b94e86f3-a664-5a8f-b450-357ac4c986e5 | note | Record documents (QCP - Quality Control Portal) - Site Diary
0b552cd0-a4b1-5aaa-b7b4-6a7142669cfb | note | Responsibility - Paving Contractor
3f07393d-eaf0-524d-9b2d-b8ccf2fff836 | note | Eng. Rep / NZTA - I
dfa04d84-4f6c-570c-876d-6b223a95850a | note | Contractor - R
2635f859-d21f-4777-a53c-87c6ea5ef402 | section | 4.0. As Built Records
66a35960-0612-4e8d-a027-d73adc6a5956 | checkpoint | 4.1 - Assessment of all test results for conformity
bca6ea3e-288a-50aa-9d2b-a0df8ae1cd2f | note | Detail of Activity / Test - Review against ITP Requirements
9d44ae4f-bcb4-50c6-9656-13acb57396ec | note | Action (Hold, Monitor, Witness) - H
042b2f11-186f-587c-a4b4-2d47306b3e0e | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
7acedc6c-114b-54ef-b800-2d4fb0b3b8d8 | note | Inspection / Test method - Review
951f9f20-5a77-5c2b-84bc-ead3ba0dc7e2 | note | Acceptance Criteria - Reporting of any non-conforming results to Engineer via NCR
827327d4-4c52-5575-9743-54d7f755f099 | note | Record documents (QCP - Quality Control Portal) - NCR
15c10a72-73d0-5d6d-bbb6-370114d115f8 | note | Responsibility - Paving Contractor
a25b9fdc-f04f-578c-aa1e-0ae60345eb75 | note | Designer - I
829c6417-4ca6-50fc-9c32-b3925eaee143 | note | Eng. Rep / NZTA - A
d87bc92f-2c85-5e80-a640-5502fa550ac4 | note | Contractor - R
3afc4415-1a3d-4e47-abe8-4d6a22a4cf07 | signoff | AUTHORITY HOLDPOINT
25c66f12-86f5-4ef7-bc8f-48475f59ea82 | checkpoint | 4.2 - RAMM pavement and surface records
09b1bd58-4391-5f23-8cad-87a361a77b4e | note | Detail of Activity / Test - RAMM surfacing pavement data spreadsheet updated
7025f10e-c133-5585-81f5-b9aad7ae6692 | note | Action (Hold, Monitor, Witness) - W
7fdcf9e9-7527-5c25-bdc3-0f39eb1614c0 | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
1f1dbe45-2b6f-5cfe-8600-5e59363aa816 | note | Inspection / Test method - Prepare Data
f64ac8d3-f752-5780-bca1-38491a0b3101 | note | Acceptance Criteria - Over milled and Deep lift extents recorded and verified by Contract Engineer / QA
a55c15c7-3d4c-5567-a5e3-5ecb97b1b838 | note | ○ Spray sheets for membrane area received by Contract Engineer from Sealing Team.
90312022-6596-5fed-a8f4-35110dd9c489 | note | ○ Surfacing layer extents recorded and verified by Contract Engineer.
81761d2d-27c0-53c9-a5e7-a10c136049c6 | note | Record documents (QCP - Quality Control Portal) - RAMM Spreadsheet
d0a3f71b-ad80-5182-884d-a7c94101edcf | note | Responsibility - Paving Contractor
13607bca-00dd-56fd-8445-a4d9fd2eed88 | note | Designer - I
3966ca8d-436a-5125-9f76-f030699b5941 | note | Eng. Rep / NZTA - A
73574074-ca24-527c-a3a4-8ce9f4eb974b | note | Contractor - R
49d45665-41d6-48e2-8985-22dbf0c79b23 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
b9167e74-edfd-5f2b-95af-742f738d1a5f | textbox | Contractor's Rep Name:
6bad32df-6d90-53c1-b5d0-53fa37fe712f | textbox | Engineer's Rep. Name:
f021a4f3-8ec5-5184-8ab8-a08da07608fb | date | Date:
91699f12-e44a-4436-bf94-8674dd286b65 | signoff | Add Signature
7252aecf-d5c8-477f-9144-f3addebda6d2 | checklist | DN1210-023-01 ITP Traffic signs Installation Rev 0 | itp | DN1210-023-01 ITP Traffic signs Installation
8d024a50-ec1c-4d30-9387-4583d3279106 | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL, PERSONEL & THIRD PARTY APPROVALS
0005bf3e-df3f-43e7-9dd2-cb97cb5e4549 | checkpoint | 3.1 - Underground Services
deb7a66b-8975-5623-a5cc-ea2227b21efc | note | Detail - Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage.
44613fe5-ad80-5162-86b0-3f1a2f407887 | note | Acceptance / Conformance Criteria - All underground services marked on site before pot holing or excavation
02099c89-ccbb-5c9d-8a22-629120b5ce5e | note | Standard / Specification - PS23.5.3 b)
60483119-a67f-5082-ad9e-0b6c02be79b9 | note | Verifying Document - Survey Data/Site Photos
71474ad0-3f2e-5002-a934-41ac606c82e8 | note | Testing Quantity Required (based from schedule qtys) - Pre Excavation
81a63444-f204-5fb8-bdb0-078f5004bfe8 | note | Verification Activity: Activity - H
fbc31589-df73-57b1-ae0a-e911ea0d10d9 | note | Verification Activity: By - PE/SE
a77d1bc9-4f57-4fed-a434-3e1554205b10 | checkpoint | 3.2 - Sign manufacture
afd6bf58-3589-573d-84f6-cb40720ebe3c | note | Detail - Ensure sign products and systems are listed in NZ transport agency's accepted products and systems table in Appendix F of P24
054aa313-2332-5874-8d5a-0eb76ac6e1d0 | note | Acceptance / Conformance Criteria - Listed in Apendix F of P24: specification for permanent traffic signs
62a59120-a82b-59df-b9d6-8007ff32fc23 | note | Standard / Specification - PS26.3.2
ce704b92-812e-57fe-afe3-f0d6a0070988 | note | Verifying Document - Appendix F
3632b1b9-f608-531e-a577-f51811483731 | note | Testing Quantity Required (based from schedule qtys) - Prior to installation
1f192b3b-06e4-5e03-bd7e-651419bea59b | note | Verification Activity: Activity - HP
1f35be33-7f39-5816-b7c6-d8796809cee1 | note | Verification Activity: By - ENG
513a62cc-de8d-4280-bf35-8779697a3091 | signoff | AUTHORITY HOLDPOINT
39a9f4a0-94f6-4e2e-8b94-a57039d06cf7 | checkpoint | 3.3 - Sign Retroreflective sheeting
846e55ac-d8ad-5dab-a6c7-03f1ba729bf5 | note | Detail - All signs be reflectorised with Class 1W sheeting, and must be turned about 5 degree away from the driver's line of sight.
1c21a512-5983-504b-861e-cf5b090afe06 | note | Acceptance / Conformance Criteria - Visual Inspection: Manufactrur's confirmance
e1adfc4e-c6d3-5279-9b03-d33eb5731dc5 | note | Standard / Specification - PS26.3.3
f13749bb-d418-5c97-a422-a1c463ae9470 | note | Verifying Document - Photo/Visual Inspection
03c188b0-acb4-572d-9dbb-23093714c096 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction and after installation
29a2ec04-4420-50e4-a75a-a69948c0e132 | note | Verification Activity: Activity - HP
95de3936-fa36-51d1-9ea5-1b3af067729a | note | Verification Activity: By - ENG
020bddb9-9b5a-40b2-8044-84dd6a8e0358 | signoff | AUTHORITY HOLDPOINT
c1251ccb-08f3-4925-9329-2d56699ebb9b | checkpoint | 3.4 - Delivery of Materials
ff83fa34-5154-5d1f-9788-fcabad06a932 | note | Detail - Ensure materials are delivered as per project schedule and specifications
75369cf4-c471-5a8d-98e4-6d36f1d3f606 | note | Acceptance / Conformance Criteria - Materials delivered in good condition, without damage to anything
b1e20ec7-6e36-5264-a32c-ec5655b36adf | note | Standard / Specification - Section 26.3.4 (Project Specification PS)
3e5c0716-7ddc-5bbc-9341-205e861fe5e6 | note | Verifying Document - Photo/Visual Inspection
274eb381-5fab-54ca-9a82-8a16ad362960 | note | Testing Quantity Required (based from schedule qtys) - 100% of material deliveries
88f3b247-748b-5080-94c2-3deead67d75b | note | Verification Activity: Activity - I
c0111213-fe97-5640-b217-85860c72621f | note | Verification Activity: By - SE, QE, SUP
7f4c2320-7d81-4796-84b2-cd047a46a763 | section | SECTION 4 – CONSTRUCTION ACTIVITY - W-Section GuardRail Installation/Sign Installation
1152dced-ca66-41c9-8cd9-0e2410f001c1 | checkpoint | 4.1 - Set out of Traffic Signs
8fd51000-2cbc-51db-b205-9cb5c7b074a6 | note | Detail - Set out to be done as per IFC drawings/design Specification, if there is no model and position for sign post to mount on grond: seek Engineer's consent follow the installation schedule as per WSP-DR-RSA 0326
3057d9e9-55fb-5161-99a7-4f57c027cf62 | note | Acceptance / Conformance Criteria - Visual Inspection: checks for appropriate position for sign to install
24726cfc-51b5-5155-a9a8-054584d82e8e | note | Standard / Specification - PS23.11.8.a) vi
b26f5512-4ede-5f8c-80d4-65d493302cc1 | note | Verifying Document - Photo/Visual Inspection
3b44492f-32f3-51aa-89eb-9279180ff464 | note | Testing Quantity Required (based from schedule qtys) - Each installation
2c778b87-6e51-52fe-aefc-a0782409085f | note | Verification Activity: Activity - HP
1931d74d-0188-5a08-a1a4-a316301c4a6e | note | Verification Activity: By - ENG
4b46a412-91b0-4c3a-8b54-c08e191c923a | signoff | AUTHORITY HOLDPOINT
7155f5e9-9d6e-45d0-a68a-89b73fe23ffd | checkpoint | 4.2 - Installation of small traffic signs
06d3119b-e121-5122-bfcf-2935bc67d8b2 | note | Detail - Sign installation follow standard method as indicated in specification and drawings
0da5b86b-ac63-503a-a3ee-acd7d044787c | note | Acceptance / Conformance Criteria - Visual Inspection: checks for appropriate position for sign to install
3e6b69c1-796d-5298-8e26-b7a49f2806c5 | note | Standard / Specification - PS23.11.8.a) vi
c993d605-6e19-5e63-a916-2ceef06812c1 | note | Verifying Document - Photo/Visual Inspection/Checksheet
693ba9f3-7e1a-5e77-a959-642c69fbc3ed | note | Testing Quantity Required (based from schedule qtys) - Each installation
d8ac2ab2-44a6-53ee-9de4-dbd4a46679ea | note | Verification Activity: Activity - I
2aa4e858-995c-5d11-bc3a-7a799c633af5 | note | Verification Activity: By - SE
179b9aa2-4ae6-47cd-8350-0a6d27161379 | checkpoint | 4.3 - Installation of large signs with face area more than 4.7m2 Specific design
236c790e-bea9-54c1-b6a6-badcf7b255b5 | note | Detail - The foundation for post need to be 3500 deep with 750mm dia
218f3d95-f0fc-5ac9-8c90-48f6053fac12 | note | Acceptance / Conformance Criteria - Foundation as per design and drawing
005fdbaf-5856-5575-b28b-624742fda7a5 | note | Standard / Specification - WSP-DR-RSA 0336
a73ab335-0c0e-59fc-ad02-6b7e98cd0254 | note | Verifying Document - Photo/Visual Inspection/Checksheet
f5d5b9a1-933b-54da-beb3-b8a45c3f014e | note | Testing Quantity Required (based from schedule qtys) - Each installation
1e4ecd99-b8ed-5ad2-868e-70f22da3f24c | note | Verification Activity: Activity - HP
1865a298-25b9-5d8b-a636-df1179e408cc | note | Verification Activity: By - ENG
2a56950d-49e6-4622-8726-85111ac88c41 | signoff | AUTHORITY HOLDPOINT
1addf32e-9138-46d6-963b-3b4dce20fbc8 | checkpoint | 4.4 - Installation of large signs with face area more than 4.7m2 Specific design
e04c88a9-bc3b-5a7a-b43d-d8d20973623d | note | Detail - The foundation for post need to be 3500 deep with 750mm dia, 75mm cover all over: 12YD16 longitubinal bars with YR12@200mm spiral.
9f61c3d7-56b2-5701-8409-d5f843e82b1b | note | ○ The concrete to have minimum 30MPa
316d1921-770d-5e7f-af19-12e0c6c2b3df | note | Acceptance / Conformance Criteria - Foundation REO as per dwg 0336:
98f1e475-d25e-58f7-88c4-f77638a42490 | note | Standard / Specification - WSP-DR-RSA 0337
920d7607-9dd5-5c9a-9273-0b5f3b845c6b | note | Verifying Document - Pre Pour inspection/photo/ Concrete Docket
7f2e4d8a-4c5b-57bf-a08b-6cf942baff34 | note | Testing Quantity Required (based from schedule qtys) - Each installation
50cc65c5-047e-5dce-bb8e-ed97c4586b0b | note | Verification Activity: Activity - HP
8dea56a0-418b-514a-88f0-d0a768fa00ff | note | Verification Activity: By - ENG
807cb5af-897b-4934-bce2-3e80d2e0a046 | signoff | AUTHORITY HOLDPOINT
770bed58-853f-4c85-b7f6-99ad8304bbad | checkpoint | 4.5 - Installation of large signs withface area more than 4.7m2 Specific design
c48dfdd6-4ac3-5288-a528-6025fab3f0d5 | note | Detail - The Foundation post pour inspection
980d441a-ffee-5df5-8677-883651031435 | note | Acceptance / Conformance Criteria - Engineers Approval
f7f31d74-4449-541b-b43a-795012b32869 | note | Standard / Specification - WSP-DR-RSA 0338
b104de13-79f4-5463-a703-198ea26843f3 | note | Verifying Document - Post Pour inspection/photo
8d8bbb35-9295-5ee3-8159-18dabd45201b | note | Testing Quantity Required (based from schedule qtys) - Each installation
df2770d4-59fb-5e94-bcd2-cb0bf7f5e64e | note | Verification Activity: Activity - HP
bfb9e90a-511a-5e65-9c19-c0b05bf1a290 | note | Verification Activity: By - ENG
d11d6310-2a3f-42c7-a02b-e9495dff2920 | signoff | AUTHORITY HOLDPOINT
efe1217d-f574-4c70-bdcf-72275fd7bc8c | checkpoint | 4.6 - Installation of Retroreflective sheeting
bde5f00c-4062-58d5-ac7e-f2f7a71e2f57 | note | Detail - All signs be reflectorised with Class 1W sheeting, and must be turned about 5 degree away from the driver's line of sight. The chevron boards beed to be turned about 10 degrees away as per section 1.10 from MOTSAM part 1
5944aa7d-8a47-560c-bd85-afe603b1db68 | note | Acceptance / Conformance Criteria - Visual Inspection
61303fca-b94b-541b-95a2-55e27607d42d | note | Standard / Specification - PS26.3.3
1fb60084-1022-523f-bf2c-fd6e414a904d | note | Verifying Document - Photo/Visual Inspection
572da0c1-35b3-57e5-9356-a3063e213ee8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction and after installation
fd95d2d0-60f9-501c-a4a1-6cfb8a2b4bb2 | note | Verification Activity: Activity - I
75eb1259-5e04-500e-a42f-f76ff8fafaff | note | Verification Activity: By - SE
b707ba22-13a2-4ca5-b724-9927b1f9e55e | checkpoint | 4.7 - Foundation Embedment depths for signage posts
6b97e8e0-d4a7-5679-b54c-603f02225d92 | note | Detail - The depths provided in the schedule do not include the topsoil, total depth below surface of the signs shall be the embedment depths plus the topsoil depth
e724317b-16e4-58b5-97c8-8d2cb103c3be | note | Acceptance / Conformance Criteria - Visual Inspection: checks for specified embedment depth
c2a539c0-c95f-5c6c-ad78-42657a6d06fc | note | Standard / Specification - PS26.3.4 g, III
54247b63-c95b-540f-9bbc-b8bdd1c448d2 | note | Verifying Document - Photo/Visual Inspection/Checksheet
b4b348d4-7e0b-5d31-b2c2-4855702632c7 | note | Testing Quantity Required (based from schedule qtys) - Each installation
9331c396-a7a0-56af-9ef5-b4d03f51e11b | note | Verification Activity: Activity - I
5904ce42-bc45-536a-ae52-6c48fc13c322 | note | Verification Activity: By - SE
23be3f24-b872-49e5-a973-1eb4f8116c75 | section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
69742da1-df6a-4056-9fb7-4bc40a7042ef | checkpoint | 5.1 - Final Inspection and approval of installed signs
a0d6f6be-ab8e-5388-9ea0-3904b48bcab4 | note | Detail - Conduct final inspection and audit of all installations
8c5dde05-0dac-5eaa-b899-094f57fa245a | note | Acceptance / Conformance Criteria - Visual Inspection
998f9ff3-2807-5e9f-a41f-d93a48982313 | note | Standard / Specification - PS26.3
cc7782a1-9f60-5cd3-87ce-b243043419d4 | note | Verifying Document - Final inspection reports, Compliance Sticker from the installer
8c221627-616d-585f-8410-323e20be0924 | note | Testing Quantity Required (based from schedule qtys) - 100% of installations
9f40a96c-5180-56e5-ad81-f8311051b09c | note | Verification Activity: Activity - R, HP
465f9a85-4e0b-5535-bb7d-3f298f251242 | note | Verification Activity: By - ENG
a6c6d12e-0fde-465b-9d77-d6fe140f5f32 | signoff | AUTHORITY HOLDPOINT
a71f2988-1a97-4710-864d-a7daee4d06b6 | checkpoint | 5.2 - As built and records of installed signage
03ff7595-d1ea-52b6-b0c0-346fc39d6196 | note | Detail - As built and record of installed barriers
4bbb2ee5-6364-59c7-b055-4822d7ad7675 | note | Acceptance / Conformance Criteria - Survey/Records
4d393cd2-b76e-5827-bc28-a9c247a41065 | note | Standard / Specification - PS
866a478d-b88e-5eaa-b2aa-3d8af0c4ccc9 | note | Verifying Document - As built records
12cb47fc-eae0-51f9-8006-47069da8f82b | note | Testing Quantity Required (based from schedule qtys) - 100% of installations
73643178-3699-5bee-af83-2ba426cddb17 | note | Verification Activity: Activity - SV
fb67a096-8f7b-5691-a33d-ba32722e1033 | note | Verification Activity: By - Surveyor
4f2c129e-8ccb-437e-b0ff-b725fc27fd96 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
d2cb2109-7a6c-566a-9902-02ed322368dd | textbox | Contractor's Rep Name:
9ef0bc7c-b90b-5a05-a6f0-3e4c8c157eec | textbox | Engineer's Rep. Name:
03e9e638-c05e-511d-814b-3712817a9671 | date | Date:
bbe855fa-1674-48f5-b639-3485121ddf77 | signoff | Add Signature
e06a4c01-5f37-411d-b658-61462934c5a8 | checklist | DN1210-023-02 ITP Barriers Installation Rev 0 | itp | DN1210-023-02 ITP Barriers Installation
dc3e4dc8-1d29-44ac-bc50-497e7b43ac75 | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL, PERSONEL & THIRD PARTY APPROVALS
e4b59101-76e0-4869-94c3-ad82ee358ec4 | checkpoint | 3.1 - Underground Services
d85b7520-c13f-5f32-a449-e1ea5801ae87 | note | Detail - Set out new and existing services and identify clashes with design
5f565e19-c2d4-592f-8f34-2221991e8471 | note | Acceptance / Conformance Criteria - All underground services marked on site before pot holing or excavation
b4bfc4e6-5b20-5ed1-ade0-31cdcb70f4e0 | note | Standard / Specification - PS23.5.3 b)
2a94f8d9-2883-51a3-a937-57c18e134ac8 | note | Verifying Document - Survey Data/Site Photos
0008bd33-c2de-5988-9d97-9f005bdbb26d | note | Testing Quantity Required (based from schedule qtys) - Pre Excavation
bce30ea1-9a58-558d-bced-512769daee7d | note | Verification Activity: Activity - H
5b56106e-2fdc-5cdd-8c78-c40047e0eae1 | note | Verification Activity: By - PE/SE
4650ec39-d704-459e-9c11-64ca4b55d34e | checkpoint | 3.2 - Materials for W-Section Gurad Rail
a3968dfe-ff24-589f-af1c-7415a1d4226e | note | Detail - Confirm that the W-Section barrier meets the specification and NZTA M23 specification
04203221-5b27-59d7-8942-189d044c1c56 | note | Acceptance / Conformance Criteria - All the materials meets the specification requirements and Engineers Approval
236b4feb-063e-59ee-84e4-9bb6bae4e22d | note | Standard / Specification - PS 26.5.3
cc9b4c39-a14c-5dd1-9ce3-9815cc4b82a9 | note | Verifying Document - Material data sheet and Engineers Approval
952a56cc-9d56-5a07-8a2b-87f577e291e6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Installation
066d3b38-747e-56fc-b813-76d03647676d | note | Verification Activity: Activity - HP
2717c18d-201d-5c40-b807-efddad3b4f39 | note | Verification Activity: By - ENG
610f944b-32aa-4e5c-b4c6-14d999fdc06e | signoff | AUTHORITY HOLDPOINT
53bbfaed-23f1-4c44-9294-1fb4c0576580 | checkpoint | 3.3 - Road Safety hardware system performance
47fd51ee-bafa-5bf6-a464-35e86ac60160 | note | Detail - The minimum performance level for permanent road safety hardware systems installed on SH for side is MASH TL-3
561ba9cd-5900-5928-88cc-86ff5679a927 | note | Acceptance / Conformance Criteria - All the materials meets the specification requirements and Engineers Approval
4dcef88b-81e9-5339-8fdc-69b2200cf7a5 | note | Standard / Specification - PS26.5.4
d54394b1-3a9a-5b30-936d-d3b0c59dc80c | note | Verifying Document - Material data sheet and engineers approval
81497a30-3763-5ae5-94dd-1e4b6f25a7b8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
31bd4b8c-1f73-573d-8ccf-3133d619d6a6 | note | Verification Activity: Activity - HP
0233b80e-9097-5630-988d-c94f5d523555 | note | Verification Activity: By - ENG
d9f19417-9208-4e4c-851a-24aec31ddd12 | signoff | AUTHORITY HOLDPOINT
8106e8f0-5903-4455-b4bf-7a9dae8e9e9b | checkpoint | 3.4 - Delivery of Materials
da5ccfd4-0910-5e9b-b095-15baa0c9edc9 | note | Detail - Ensure materials are delivered as per project schedule and specifications
039752d4-86e9-5e93-9876-9dfdd4a948f7 | note | Acceptance / Conformance Criteria - Materials delivered in good condition, within specified timelines
c0f1029a-6c20-520b-abce-be3e7dc6f350 | note | Standard / Specification - Section 26.3.4 (Project Specification PS)
d23158dd-f483-52d1-9018-85293b5fa69e | note | Verifying Document - Delivery receipts, inspection records
82ecba26-2215-5d93-99c2-33380d4f3809 | note | Testing Quantity Required (based from schedule qtys) - 100% of material deliveries
480bbaa0-56d5-59f3-aa73-705650ed52bb | note | Verification Activity: Activity - I
d97f74b0-1b23-52ed-93a3-d2db4773ba6e | note | Verification Activity: By - SE, QE, SUP
2b2c64d8-4184-47ef-8fa3-6d31ab961462 | section | SECTION 4 – CONSTRUCTION ACTIVITY - W-Section GuardRail Installation/Sign Installation
b4213767-accd-44f4-8d51-4bf4b85a3bea | checkpoint | 4.1 - Set out of W-section barrier
2e4dc67b-6561-543c-b9ae-a77352e9ad6f | note | Detail - Set out to be done as per IFC drawings/design Specification
177e371e-d16a-5314-b4e3-721ce529f743 | note | Acceptance / Conformance Criteria - Visual Inspection:and verification as per latest dwg
7ce2b6df-a5b5-5239-91a4-186fd56f9452 | note | Standard / Specification - PS26.5.2
f117cced-27ed-5e06-a606-a80ad60d86dc | note | Verifying Document - Photo/Visual Inspection/Checksheet
cea866a3-3569-549f-838b-e6037b63674b | note | Testing Quantity Required (based from schedule qtys) - Each Barrier Installation
6fbec9b4-ed1b-5145-9fd4-91f75fef73cf | note | Verification Activity: Activity - HP
76339bb3-0fa1-5707-97fc-8a97291f5f29 | note | Verification Activity: By - ENG
ec8a7df6-06bf-4c70-b0af-b064d1912d2e | signoff | AUTHORITY HOLDPOINT
13400a68-482c-43a7-9b9b-88e3f5e5a52a | checkpoint | 4.2 - Set out of Entry and Exit Terminals
f2f7c270-df12-5060-a44b-e12950807610 | note | Detail - Set out to be done as per IFC drawings/design Specification
1d102fd5-9852-5023-93a4-597e666c5e54 | note | Acceptance / Conformance Criteria - Visual Inspection:and verification as per latest dwg
f3c82aeb-2e2c-5b42-afce-524bc3dc805c | note | Standard / Specification - PS26.5.3
5fdf040c-750d-5347-8a8d-33b7abb8b7ba | note | Verifying Document - Photo/Visual Inspection/Checksheet
63b97e67-5567-57b5-959f-f884ba8156eb | note | Testing Quantity Required (based from schedule qtys) - Each Barrier Installation
d6134d71-d5aa-5de8-866a-eed778be2a8e | note | Verification Activity: Activity - HP
7b342b8e-22d9-5e22-aff4-f2fcf4f3188e | note | Verification Activity: By - ENG
73601c68-952d-4012-a5fc-241b54bf36f3 | signoff | AUTHORITY HOLDPOINT
5aa0a677-0da9-49aa-a6e6-93c3bb0aaf04 | checkpoint | 4.3 - Installation of W-Section barrier as per AS/NZS 3845
8ce17463-61d8-56e7-9f02-c7cd12202683 | note | Detail - Set out to be done as per IFC drawings/design Specification, and installation to be done by competence person
fa59d26b-3e5f-5239-a4a3-c213c7fd64af | note | Acceptance / Conformance Criteria - Visual Inspection: checks for appropriate Installation following standards
dd1f83c0-9e57-53a1-8a97-0e1e5e3dafda | note | Standard / Specification - AS/NZS 3845
74481325-7d8a-5124-b652-0e5e1eb01cba | note | Verifying Document - Photo/Visual Inspection/Checksheet
c84c1051-c6fc-58ce-87db-821b5d4a8c01 | note | Testing Quantity Required (based from schedule qtys) - Each Barrier Installation
cad4c0ea-106a-5531-94f2-36931bf42bc4 | note | Verification Activity: Activity - V
04779767-0c73-5386-8860-fa042c649bfb | note | Verification Activity: By - SE
eaa64532-57e9-4e4d-995e-ab0647c06a31 | checkpoint | 4.4 - End Terminal and Thrie beam installed as per AS/NZS 3845, M23 and Project specs
1b81c911-b874-5f7b-9e3d-d984fcb8c682 | note | Detail - Set out to be done as per IFC drawings/design Specification, and installation to be done by competence person
70914b77-cd43-5753-82f2-f5501cd73ff9 | note | Acceptance / Conformance Criteria - Visual Inspection: checks for appropriate Installation following standards and QA checklist from suppiler
6ae2e456-e4c8-55eb-b652-1cd7d5a9d3de | note | Standard / Specification - AS/NZS 3845
2dbde663-7fcf-5fdf-b8e7-ccfad493c8e5 | note | Verifying Document - Photo/Visual Inspection/Checksheet
123104b3-0736-5fc8-808e-4fc38b554b7a | note | Testing Quantity Required (based from schedule qtys) - Each Barrier Installation
f90f0c2e-a14e-5f9a-826e-756f923e6c3e | note | Verification Activity: Activity - V
7e4b4acb-e9c2-5cfc-a197-6b82857dffa5 | note | Verification Activity: By - SE
89d53f1c-6ff1-4954-8d33-ec3cbb72a4bd | checkpoint | 4.5 - Lapping of Rail in direction of Traffic
046c51f5-2ee6-58dd-8aa0-2ec51e4367a0 | note | Detail - Lapping of W-Section barrier to be lapped in the direction of traffic
6105f32b-518c-53ea-83b4-a2613a92574f | note | Acceptance / Conformance Criteria - Visual Inspection
2b562876-af9f-5b93-847e-0ebaec2af8ab | note | Standard / Specification - NZTA M23
02f50a4c-c1a3-58e3-a995-ed87bd1c748f | note | Verifying Document - Photo/Visual Inspection/Checksheet
6e57584a-e259-5105-ae3a-3cda47e9a4e0 | note | Testing Quantity Required (based from schedule qtys) - Each Barrier Installation
7fb2bac4-da3b-57a2-b54b-3b5fe8bd702e | note | Verification Activity: Activity - M
a125aa2d-0529-5f06-8a2d-d08e2f3be53a | note | Verification Activity: By - SE
c7dbbb66-8225-4fc4-9d02-821975270daa | section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
7a59bf0f-fec0-49dd-b731-b9a2e2d8fdfe | checkpoint | 5.1 - Final Inspection and designer's approval of installed barriers
5d92f934-3ba7-56a8-8c33-ce57c65786d7 | note | Detail - Conduct final inspection and audit of all installations
75d457aa-fca2-51a2-9e5c-3029a5a62041 | note | Acceptance / Conformance Criteria - Visual Inspection:
3eeb8b2d-13b1-533d-82d3-f257a48279b3 | note | Standard / Specification - Section 26.5.4 Vi (5) (Project Specification PS)
9020a40b-4107-52f3-a28a-b1b6bf25bd54 | note | Verifying Document - Final inspection reports, approval of installed bariers with tolerance -0mm, +20mm
0726bbba-5892-5e4c-b257-2c0808965720 | note | Testing Quantity Required (based from schedule qtys) - 100% of installations
4a74f100-7f75-506a-b936-07a85dcceab6 | note | Verification Activity: Activity - HP
283da55d-a5b5-5d04-b525-e08bb2f44541 | note | Verification Activity: By - ENG
60803457-d975-468a-9943-2e5975422bc1 | signoff | AUTHORITY HOLDPOINT
36936dd0-07ce-44d8-b43a-2f76461c882c | checkpoint | 5.2 - As built Records
08de100c-ec76-50b3-b0a4-61db7d96f893 | note | Detail - As built and record of installed barriers
e7a1f3ba-447e-54b4-a310-c36c06e3690e | note | Acceptance / Conformance Criteria - Survey/Records
7ed558ac-f875-518a-abad-49d3d078ba18 | note | Standard / Specification - Project Specification
ec5919cd-f3ba-575e-982f-3a679b4a78cf | note | Verifying Document - As built records
46688ed6-6a46-52cc-937e-a32a10df9c5c | note | Testing Quantity Required (based from schedule qtys) - 100% of signals and ITS installations
1f6f86ea-2f21-5224-9f2d-b1fe60298f1d | note | Verification Activity: Activity - SV
b8224994-4c84-51b9-8c98-1f16ec23214b | note | Verification Activity: By - Surveyor
344f80cf-9a01-441a-b618-140b87deb781 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
08de0083-0fb3-50e5-a4d3-6363a0726122 | textbox | Contractor's Rep Name:
23dcfff6-b3b7-582f-b25f-fdd6400e46df | textbox | Engineer's Rep. Name:
b3294781-6fb3-59d7-acdc-e45181f92c39 | date | Date:
0d3b679e-3a95-4bde-b799-f38599fc9716 | signoff | Add Signature
775f5cb4-abb8-411d-9cca-796fb845b696 | checklist | DN1210-024 ITP Permanent Line Marking REV 0 | itp | DN1210-024 ITP Permanent Line Marking
33a87482-5620-43c0-ae61-d43a08714805 | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
6f338c62-8228-48e3-9dce-8a5c4f9f591b | checkpoint | 3.1.1 - Paint
1d310112-9a43-57b6-92f9-0af0e560ca0c | note | Detail / Activity - comply to TNZ M/7, TNZ M/20 and TNZ M/24 requirements as applicable. It also must be the brand and type currently approved for use on State Highways.
0e297a2f-8c80-5fa8-9c46-9b726ae52e15 | note | Acceptance / Conformance Criteria - Engineer approval
cd6e8278-36e5-5e10-b41c-ada9510a49ea | note | Standard / Specification - PS-26.4.4
06cd938c-f078-5c76-abaa-3f11cc45d876 | note | Verifying Document - Data Sheet
2628dd65-0460-5611-a8e5-de5900558ddb | note | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
b712f55e-71a4-552a-af8e-90e0882f7e60 | note | Verification Activity: Activity - HP
31274d6e-0f4d-5bee-89e7-2ab22abd1e0b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
203abe74-1ed8-59cc-8f43-4f1de57d6eef | note | Verification Activity: By - ENG
e12c391c-b66c-4b69-8b0e-423996be0c94 | signoff | AUTHORITY HOLDPOINT
1bc0bd72-e514-4066-9a44-17f5c75b8ae5 | checkpoint | 3.1.2 - Glass Beads
439b7aee-cae1-5706-baa4-b82a688fa4a3 | note | Detail / Activity - As per NZTA P/12:the Glass Beads must comply with the AS2009:1991
5d7976ac-2309-54a6-93ee-fecc4d3440fc | note | Acceptance / Conformance Criteria - As Per Specification Requirements and NZTA P/12
f64a86e0-3bf2-5080-adc9-efd00746c070 | note | Standard / Specification - PS-26.4.4
a466bfe2-7728-55ea-ae09-d2879b9de0e3 | note | Verifying Document - Data Sheet
a45f24d8-12cd-5b58-b9ba-7ced280d4060 | note | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
2c652e21-68c9-5072-ad21-840b25befc75 | note | Verification Activity: Activity - H
008ee893-d035-5f7d-a2f8-20ada19eb396 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
2553ea5e-9706-5eb3-a008-15b1e5452192 | note | Verification Activity: By - SE
e6aa49ab-7dc9-49d0-b407-5123631eb961 | checkpoint | 3.1.4 - Paint Applicator Testing
d6d0ccb7-5055-5960-b8b8-78295eb9e26f | note | Detail / Activity - All applicator plant/equipment shall comply to requirements of the NZTA specification T/8 and must have a certificate of Compliance as per TNZ P/12 Specification
51502e1c-ceac-5896-a088-0e524f14de71 | note | Acceptance / Conformance Criteria - As Per Project Specification
bc43fea8-6dab-5719-9f3d-ce7ae578465e | note | Standard / Specification - PS-26.4.4
4c478777-2594-5ed4-97f5-0cdc05e782d3 | note | Verifying Document - Test Certificate
2f70498e-7928-515f-ad75-fbd9bed08f6e | note | Testing Quantity Required (based from schedule qtys) - Once per paint applicator
ba487a2b-e8d3-56cd-ab0d-baf3b7c3d077 | note | Verification Activity: Activity - HP
7a18bbc5-ff45-587b-be4b-7eb37e24534a | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
39bf485b-8ad7-5503-88c2-08e1db29085c | note | Verification Activity: By - ENG
c08e79b3-3f22-4f45-b771-a655120fa7ac | signoff | AUTHORITY HOLDPOINT
9a50e0d0-d7b2-454a-a003-d720f7ffb12d | section | SECTION 4 – CONSTRUCTION ACTIVITY
ef9c9c32-1e2f-4054-bba7-05263160b665 | checkpoint | 4.1.1 - Survey Set Outs
70946bfe-8667-5c7d-84a8-e646a9b2edd2 | note | Detail / Activity - Survey to set out edge,centre line at 20m interval on straight sections and 10m intervals on curves. Ensure setout is from the latest CAD file.
ab8a6b5c-95a4-589c-81c8-44b5401f2ce2 | note | Acceptance / Conformance Criteria - Prior to commencement of line marking.
45c127f8-0870-5561-b6f1-877c5e729666 | note | Standard / Specification - IFC Drawings
69d1d5fa-814b-58a5-a79a-336dc6ebfe6e | note | Verifying Document - Visual Inspection
c24b4b8a-c4b3-54ce-a220-63069b7acc1c | note | Testing Quantity Required (based from schedule qtys) - For each shift
e3f90d94-3c4b-5cea-9721-0de8590eb411 | note | Verification Activity: Activity - W
94db4750-cee2-52b6-8610-22c082e65014 | note | Review of text reports/records or other evidence of compliance
9342c264-e787-5868-8a5e-ca19ad35cc51 | note | Verification Activity: By - ENG
e482c57c-79c2-453d-b025-de7e0899090d | checkpoint | 4.1.2 - Paint Marking tolerances
b94379dd-ae0d-57e0-92ee-4b4eb8abe211 | note | Detail / Activity - Paint marking tolerances shall be accordence with the section 10 of P12 requirements. and as per PS26.4.6 for transverse location +-20mm, Longitudinal location +-50mm
d65c719d-2d4b-5e17-8af0-5064531ee27e | note | Acceptance / Conformance Criteria - Picture
8559733e-1648-5318-8d3d-9a5e593822be | note | Standard / Specification - NZTA P12
6e2dbee2-5aa9-55e5-9fc7-6c0f78135c51 | note | Verifying Document - Visual Inspection
d2243001-8ac7-5678-839a-d4411f7498bf | note | Testing Quantity Required (based from schedule qtys) - For each shift
00660c0f-291f-5cb2-8f28-3a97fec7ddfe | note | Verification Activity: Activity - V
f8f9c5b5-7b5d-55cf-9e39-23956360f8e3 | note | Visual Verification
84348698-da87-5362-9ad8-e46eafbb23b7 | note | Verification Activity: By - SE
c2f99d6c-ef81-4314-b34f-1131ab83c8e6 | checkpoint | 4.1.3 - Features, Arrows and Letters
925605e0-d7e2-5ab8-adbf-764523466ab7 | note | Detail / Activity - Painting of Features, Arrows, Symbols, Letters etc shall be in accordance with industry best practice. Works shall conform with the requirement of TNZ P/12 specification.
669308dd-5f9b-589d-9f5a-d6bea0f95395 | note | Acceptance / Conformance Criteria - Paint Marking meeting the project specification and NZTA P/12
42cf50fa-9c6c-5079-8ac3-6f2455935528 | note | Standard / Specification - Detail as per IFC Drawing following PS 24.4.3
03f330a6-74f3-5fb2-b1b9-04168299ce39 | note | Verifying Document - Visual Inspection
5e46e855-d78e-5f9a-8720-3d7af07f6224 | note | Testing Quantity Required (based from schedule qtys) - For each shift
3dc655d7-c24a-5fd5-969e-d891d6c46e0c | note | Verification Activity: Activity - V
342b230e-fc3f-5fd8-a90a-5743cd1ee234 | note | Visual Verification
9fd0385e-9f73-5f3d-90d4-093edca89f75 | note | Verification Activity: By - SE
a3c3850a-5e3c-4bdd-a3d5-5df7d07c1e1c | checkpoint | 4.1.4 - Application Rates
a901ea79-bf23-51ca-aab0-99a6e2d8f8a6 | note | Detail / Activity - For paint the finished dry film thickness shall be 150microns or greater. Film thickness is measured on steel plates
8254e646-9027-54de-8f7a-83859db5cdd5 | note | Acceptance / Conformance Criteria - Paint Marking meeting the project specification and NZTA P/12
3e31fe80-0f41-54ff-8adf-86b6c4df6d4b | note | Standard / Specification - PS-26.4.4
360eb2cf-b836-5ce1-9f9d-7cc161b2472f | note | Verifying Document - Visual Inspection / Test Plate Certificate
79b3cf55-8176-5932-8100-77fab0f0edec | note | Testing Quantity Required (based from schedule qtys) - Min of 2 per day after pressure or speed settings are changed.
0e9ab139-2cd8-5e75-b8b0-8745efdae9a0 | note | Verification Activity: Activity - V
a4eafdf8-bf0b-546c-a480-75c1e3262e32 | note | Visual Verification
b8f25879-ad10-5287-813d-fb44716f440f | note | Verification Activity: By - SE
103e0d6a-9ac7-4379-aa03-b48e5bc74911 | checkpoint | 4.1.5 - Thinners
c0f9837c-bd28-551b-870f-6ea4640231dc | note | Detail / Activity - Thinners, when used in conjunction with paint application, shall be added according to the manufacturer's instruction.
3ce04981-8648-54b2-943e-2966ae0adf66 | note | Acceptance / Conformance Criteria - As Per Specification Requirements and NZTA P/12
bf203395-fc82-5e8a-a6b0-7566782d46b1 | note | Standard / Specification - PS-26.4.4
03116e66-5589-59f2-9ea3-810f340a0536 | note | Verifying Document - sub-contractor's QA Record
3e1f728a-a294-578d-b53c-bf3d2e27ea05 | note | Testing Quantity Required (based from schedule qtys) - As required
a65904f5-8141-5d06-aed5-16ab801cdc95 | note | Verification Activity: Activity - M
ff4d676b-7a77-5355-b66a-20c5f32b4b4e | note | Monitor
05a6b1d1-d6bb-5cd8-982d-155ea739b6b1 | note | Verification Activity: By - SE
0b85e4db-8ce1-4654-9666-d9361b327a22 | checkpoint | 4.1.6 - Road Reflectorised Pavement Markings (RRPM)
6e2e0ccb-77d1-58e3-b39b-4735b476defa | note | Detail / Activity - RRPM's for lane lines and edge lines shall be monodirectional, while RRPM's for centerlines and flush median border lines shall be bidirectional, as per MOTSAM requirements
89ea3c30-bbb5-5f64-9afa-f81366419512 | note | Acceptance / Conformance Criteria - Paint Marking meeting the project specification and NZTA P/22
f38cf27c-be16-5e16-90a4-1b646cbe2882 | note | Standard / Specification - PS-26.4.4 (I)
f0d315ef-7261-51e0-b76a-38fdfe7e8416 | note | Verifying Document - Visual Inspection
15caab2d-851f-51f7-82d3-a76d04449250 | note | Testing Quantity Required (based from schedule qtys) - As per DWG, RSA-0333,0334
8e755d38-08a2-59de-9251-e4daa8217ab6 | note | Verification Activity: Activity - V
4d463039-51ad-5a6d-9d2e-0fe1c920fc2f | note | Visual Verification
4ceebe02-e694-53ab-b584-036f525d756c | note | Verification Activity: By - SE
847366c4-9bf8-4b74-804e-4c9ef0944f06 | checkpoint | 4.1.6 - Dry Reflectivity
9771fc80-b146-5b27-8655-b7dc60fb1abb | note | Detail / Activity - The reflectivity is measured using a suitable photometer or reflectometer. 5 readings are taken and the results are avereged.
312f352f-da51-5eea-a3be-8972a911d2a7 | note | Acceptance / Conformance Criteria - Paint Marking meeting the project specification and NZTA P/22
7a93b5a4-9bd4-5fb1-b6f3-19a9febc1d7b | note | Standard / Specification - PS-26.4.4
1b60180f-129c-5639-8e47-d11ccf5669a2 | note | Verifying Document - Visual Inspection / Test Certificate
037a5249-01a7-50e4-9019-68b36c7be9a5 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 1km to a maximum of 5 tests
70dd898d-4a84-5ba4-87b4-356d21404c6d | note | Verification Activity: Activity - I
382544c9-194c-58fe-9a31-eda5b89a54c4 | note | Inspection
9655fc72-54dc-5ba8-af7b-fc21be65a267 | note | (Formal inspection activity to be undertaken and recorded)
8d380a0c-0859-5dbf-b772-93127546e8a6 | note | Verification Activity: By - SE
31bc281f-5cd4-41e7-a3cc-29c03aeabe3c | section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
941ea75b-e2c3-4e1e-8cbc-82bac8f12526 | checkpoint | 5.1.1 - Post Line Marking Inspection
989f32fb-d7f3-5409-bd94-2e1fc9224ce1 | note | Detail / Activity - Complete visual inspection of linemarking
6ce85eda-ba84-5184-b96c-3ff69c55223e | note | Acceptance / Conformance Criteria - Accepted by the engineers representative that it is visually appealing
0bcc020f-35ac-57e3-a812-97023c3fa96e | note | Standard / Specification - Project Specifications
cd86245a-43a7-5e6e-9643-47b126105069 | note | Verifying Document - Site Instruction
0003d74c-dd67-5b49-9e45-8b451b99ea8f | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
9e416043-c8cc-585d-9972-aaf2708a1331 | note | Verification Activity: Activity - H
a82b9edf-4139-5367-a133-8a3a7555a81c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
74f903dd-3edf-51d4-8074-8902029b02a9 | note | Verification Activity: By - SE
3142e4a2-dae9-4b84-8165-876379949754 | checkpoint | 5.1.2 - Survey As-Builts
ca6b08da-ad42-58d3-a15d-cd91fd302ea0 | note | Detail / Activity - As built records of the finished line marking
d35be51a-0db2-5718-9328-d8abf20d2050 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
3fb872b3-a772-55f9-8014-09d8faa7bd24 | note | Standard / Specification - Project Specifications
2055b220-46da-55bf-9ecf-e26017be8ce8 | note | Verifying Document - Red pen markup
037ee26a-0948-578e-8cb6-914e919b4acb | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
c7fd4540-5cb5-5832-94aa-70842446ca9b | note | Verification Activity: Activity - R
edb9b96a-ff13-5d53-9f58-cba7e5d8a0d5 | note | Review Redpen markup
d4c60d1e-31bf-504d-9365-be0d55b87764 | note | Verification Activity: By - SE
91b0a275-017d-47ce-945d-6b00e28775c3 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
7e9438ec-d016-5741-bc07-c7ce3a23112c | textbox | Contractor's Rep Name:
a348e9e0-9d5b-5357-acf4-54b621d83e75 | textbox | Engineer's Rep. Name:
12e8cd69-28bb-5c1a-8e82-2eb83a0a7cd9 | date | Date:
021d407c-1a2a-4461-8b1f-02d4631ecaa6 | signoff | Add Signature
073b10ce-c426-4196-b2a0-264fdc283285 | checklist | DN1210-026 ITP Pavements Type 1A Rev 1 | itp | DN1210-026 ITP Pavements Type 1A
9423c4d7-5e91-4454-a4fb-e0b52df0008c | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS (MATERIAL & THIRD PARTY APPROVALS)
31899494-833c-499a-9e66-2e51a2c3d529 | checkpoint | 1.1.1 - Geogrid
ded6c325-2294-5443-9c32-71b1ad231a93 | note | Detail - The Contractor shall submit the full details of the geogrid they propose to use to the Engineer for approval prior to installation.
735b1237-751e-5cc3-8a79-74a60dda6111 | note | Acceptance / Conformance Criteria - Engineers Approval
58e5b285-e7b9-57b6-a94e-e2b2fa07b8fe | note | Standard / Specification - PS 20.5.2, PS 16.5.13
c25bf4ff-a01a-5f1a-a28b-bb0457a7c6b6 | note | Verifying Document - Data Sheets and Approval
e0079757-f159-518e-9320-092d690f6881 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
34fb81af-2717-597b-bf9a-76cbeb0196c8 | note | Verification Activity: Activity - HP
fb6becc4-e1b0-5bc5-96ad-dc7f79311b67 | note | Verification Activity: By - ENG
b959828d-0294-406a-ae8f-fe1020601e16 | signoff | AUTHORITY HOLDPOINT
db5b4f51-e280-40d9-85c7-dc9c1ba1b465 | checkpoint | 1.1.2 - Geotextile Fabric
843c99ea-a3dd-552d-8c0b-95bb59f3d87a | note | Detail - The Contractor shall submit the full details of the geotextile fabric they propose to use to the Engineer for approval prior to installation.
3576f768-9e51-5ed7-be1a-9127cca15254 | note | Acceptance / Conformance Criteria - Engineers Approval
afea997f-891d-5185-b066-9728e85b5105 | note | Standard / Specification - PS 20.5.2, PS 16.5.14
b418ec99-492b-572e-93b1-8d734906e40f | note | Verifying Document - Data Sheets and Approval
19a4308c-fc7a-58ff-b6bc-1e6639f5eb84 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
5858b1d7-19a1-555a-8213-169cdbce71d0 | note | Verification Activity: Activity - HP
e8990a0c-20b3-5238-a169-f3329d2ecccf | note | Verification Activity: By - ENG
7e0034ec-ff5d-4174-8b0d-90f2c7d3b601 | signoff | AUTHORITY HOLDPOINT
0acfebc3-02f0-4f37-89b3-0297d827a514 | checkpoint | 1.2.1 - Crushing Resistance
cd846756-c97c-59bc-83bc-4c99bdd580aa | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
1a870996-30fb-59f6-87ea-f617456a3b0d | note | Acceptance / Conformance Criteria - >100KN
dff4a9f2-b2dc-59e0-ac17-0e0b20080baa | note | Standard / Specification - Appendix XVIII
38df10d6-451b-59df-b16c-0d42c9b101a4 | note | Verifying Document - IANZ Accredited Report
8341cbcd-c356-54a3-8092-e83e3a7ef8a4 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
a565fa9d-668d-5011-bb2b-4545e1cf0135 | note | ○ Results to Engineer 2 wks before importing
2f4c4742-87ab-5f3a-b888-512f26f5a438 | note | Verification Activity: Activity - HP
ab1ebaaa-592c-5646-9c24-2771faab8fbf | note | Verification Activity: By - ENG
ad91d7af-3d94-400b-af06-6d8a432dec06 | signoff | AUTHORITY HOLDPOINT
c3f22bfa-d315-4da1-9bbc-409895ebd19f | checkpoint | 1.2.2 - Particle Size Distribution
87af45bd-a393-5e94-b4af-e08d3e519557 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
fc66d116-2471-5d0b-bff1-ded67868bcdb | note | Acceptance / Conformance Criteria - Max Particle Size 53mm
c5eb30ae-24e4-5a8e-addb-2b34a15d44eb | note | ○ Max 10% passing 13.2mm sieve
842ccf6a-af8b-5a15-9c18-e6805c513d33 | note | Standard / Specification - Appendix XVIII
2564b50c-921d-5fdb-87f8-c1b947469520 | note | Verifying Document - IANZ Accredited Report
fafe5ffd-9db7-5853-824a-caebec7113eb | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3
15cfafdc-27f1-5655-90d1-c009c7c9fe20 | note | ○ Results to Engineer 2wks before importing
d9a89a56-b410-5c8d-98e4-9569d16d07e2 | note | Verification Activity: Activity - HP
6ff47114-ce91-5c58-ade0-5aae80f2877f | note | Verification Activity: By - ENG
e1e4b2ec-9f97-4d7f-bf36-278feba5717b | signoff | AUTHORITY HOLDPOINT
98d842e5-af51-4d61-94c7-ec48faeb3a4a | checkpoint | 1.2.3 - Weathering Resistance
a6a9f7ea-fc27-5723-b693-53ca25b298ca | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
54a2fba2-5d76-5de2-a38e-adaa3ea203cd | note | Acceptance / Conformance Criteria - CA or better
daa24e72-6091-57f4-9678-c891ea216a8f | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
4b412552-7da3-5f8f-b56f-9995e676c9cb | note | Verifying Document - IANZ Accredited Report
6bdb912b-b0e9-5fae-9760-fe8f7a6e77f8 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
cc9480f7-e180-5182-a601-2012a6d95cd2 | note | ○ Results to Engineer 2 wks before importing
26177c3d-1a08-53ea-bd24-0109386535df | note | Verification Activity: Activity - HP
d8999b98-9e21-5c35-815e-8aaafb52cede | note | Verification Activity: By - ENG
75836ba6-f9c0-4aea-b425-8709f2e3a2fe | signoff | AUTHORITY HOLDPOINT
501f8326-f9a3-41b0-898c-e5f5e213e13b | checkpoint | 1.3.1 - Crushing Resistance
d0e7b228-20e1-59e0-8814-628e1656b682 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
6ebd5384-676e-5118-9d5f-860839f20479 | note | Acceptance / Conformance Criteria - >100KN
44061de5-5b0b-5d45-bab8-4df81027368d | note | Standard / Specification - NZS4407:2015 Test 3.10
89a1b701-1ec6-52a4-9bef-33aad0b59c35 | note | Verifying Document - IANZ Accredited Report
4a370797-1287-5d14-b617-9296a1c399b0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
3d105fe9-c9ff-5554-87b9-d67f2a6c2077 | note | ○ Results to Engineer 2 wks before importing
de348323-9ab0-5d18-a86b-3021169b48f7 | note | Verification Activity: Activity - HP
fb660106-a94d-533a-ad90-e7adb513256e | note | Verification Activity: By - ENG
998124dc-c242-4c0c-ad03-0f3c68e21358 | signoff | AUTHORITY HOLDPOINT
35f33a25-0906-49d9-a9e5-4f4bec4954c5 | checkpoint | 1.3.2 - Soaked CBR
10820a39-af1d-552f-a08e-af2c196a535e | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
7d495b1d-a91d-5e30-a230-d5763bc03465 | note | Acceptance / Conformance Criteria - >60%
4211831e-d23b-5e97-894d-c458f88d8a0b | note | Standard / Specification - NZS4407:2015 Test 3.15
0a9f7dc8-b024-5bf1-9ddf-7e852dc33574 | note | Verifying Document - IANZ Accredited Report
dc48b22b-314e-580e-b143-1295c43d7acc | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
b15bfe46-837a-553c-aae8-d04fa0e1f13f | note | ○ Results to Engineer 2 wks before importing
3c32e5c4-5175-56d0-9088-d124ca970a64 | note | Verification Activity: Activity - HP
4874f395-b7fb-5608-9e67-0908ff86cec4 | note | Verification Activity: By - ENG
0b1ba297-373c-4c6e-be73-ed6584192583 | signoff | AUTHORITY HOLDPOINT
daa3ba95-18bb-414d-a8f3-23a474eb0d74 | checkpoint | 1.3.3 - Weathering Resistance
9f35029a-0f44-55cb-8b71-eedafec63145 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
f92d2c71-b4b8-5fd7-8e0a-21744b2ca99e | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
05ac6d7c-369f-5850-bc89-8574c6d4be21 | note | Standard / Specification - NZS4407:2015 Test 3.11
4e87f8dd-a799-5cf4-84b8-937d409bf65f | note | Verifying Document - IANZ Accredited Report
b68312e4-559b-5e3e-88b6-1b1fbad1d99b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
449033d8-7276-50cb-83da-8323643dc8ae | note | ○ Results to Engineer 2 wks before importing
0c91779d-f8da-55a1-8da5-7cb8a3dc7dde | note | Verification Activity: Activity - HP
174804d4-cc54-5fc6-b23a-8cc790a83f26 | note | Verification Activity: By - ENG
4f160e28-3252-42be-ad19-6481cdc9434a | signoff | AUTHORITY HOLDPOINT
9c6814ac-05e2-439a-90e7-68cb0a3d0552 | checkpoint | 1.4.1 - Particle Size Distribution
22ef05de-8fe1-55ae-92c4-62b33cabb926 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
d3e01e1a-6bda-51fb-b1e2-fae0595ac2eb | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
1d95b49c-57a7-5089-ad79-4051bd5e9e05 | note | 63.0mm ¦¦ 100% passing
491a1c30-4a92-5379-a781-3bf7d6f04f9d | note | 37.5mm ¦¦ 68-90% passing
9824003d-c186-50b5-9663-28d935979ee4 | note | 19.0mm ¦¦ 42-76% passing
bb8a749d-7c03-5d75-8b28-fcd68178e4dc | note | 9.5mm ¦¦ 26-58% passing
ef0c3a15-df4f-51ab-a978-b792c776da13 | note | 4.75mm ¦¦ 16-44% passing
d20b3017-9cf8-54e0-8341-e0d7c529e36e | note | 2.36mm ¦¦ 10-33% passing
08ea3c8f-ee2e-59f0-ab39-7d466ddeddda | note | 1.18mm ¦¦ 6-24% passing
d5efc050-0a90-54ca-86a7-b0aa9c062b8e | note | 0.425mm ¦¦ 3-14% passing
04bf9098-77e5-5913-a568-f18d07582849 | note | 0.075mm ¦¦ 1-6% passing
87eada81-2263-5e85-94a7-7d678d0e059d | note | Standard / Specification - NZS4407:2015 Test 3.8.1
ec7e0857-d147-5bb2-ae3f-9faee0ce3bc1 | note | Verifying Document - IANZ Accredited Report
65ff0ea8-87a7-5bf1-8a93-3e1ff6c81367 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
7dec627e-bd20-563a-a3d3-825aa107276d | note | ○ 0-400 - 2 tests
dbc6e8ed-3758-56c5-9cec-a0b4d63ca4ab | note | ○ 400-1,500 - 3 tests
b14e88b4-3098-514a-bb90-d13c2aed7e81 | note | ○ 1,500-4,000 - 4 tests
4a991e70-9dc2-5ac4-b6bd-b4e4219f00a3 | note | ○ >4,000 - 1 test for each additional 1,000m3
24452072-c00e-5749-986e-40eed674c36b | note | – Results to Engineer 2 wks before importing
c517d451-5841-55cd-8481-98733ef3da86 | note | Verification Activity: Activity - HP
807fb9de-a3ec-50f4-b23e-428e04fbf8e7 | note | Verification Activity: By - ENG
726ec3b4-b49b-4ebf-9214-23aafe32e47e | signoff | AUTHORITY HOLDPOINT
18767c54-986d-47cf-82ee-669cd53203f3 | checkpoint | 1.4.2 - Sand Equivalent
3bd18539-0f91-54e1-9694-a1e7227d7997 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
a136de90-608c-5763-be13-f8eb395d376d | note | Acceptance / Conformance Criteria - ≥ 25
a78bbb31-3f45-5543-acde-16e3d0c7224e | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
c233776c-5dfd-524e-b284-dc3b0e01569c | note | Verifying Document - IANZ Accredited Report
48ae8898-00a8-5a57-87c2-9e9be4560b6b | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
a05b7ba6-7b67-50ff-b651-15a0ad6e8b18 | note | ○ 0-400 - 2 tests
f61d6566-0018-523f-b94d-c8fb879527b9 | note | ○ 400-1,500 - 3 tests
961252a8-55ee-542b-9948-3b3cc86ae754 | note | ○ 1,500-4,000 - 4 tests
6026bd10-09d5-56ae-8211-bf7308e4e275 | note | ○ >4,000 - 1 test for each additional 1,000m3
fde6525e-cfcc-5963-922b-36a50bf874ab | note | – Results to Engineer 2 wks before importing
18777131-6d23-5b08-8936-e893a3821a56 | note | Verification Activity: Activity - HP
475aafbe-613b-5eba-af68-a058490e9a57 | note | Verification Activity: By - ENG
4299503a-616b-4ff8-be1e-8b79f22558d3 | signoff | AUTHORITY HOLDPOINT
7ad9c416-17d0-46c8-9257-ca4804133b13 | checkpoint | 1.4.3 - Maximum Dry Density and Optimum Water Content
6ab93145-cf9c-5671-89e7-fbc59debbafb | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
26429510-4069-52e9-8327-24314b54219c | note | Acceptance / Conformance Criteria - Report Value Only
4aea692a-ea8e-53aa-8b76-10456c19e9f7 | note | Standard / Specification - NZS4402:1986 Test 4.1.2
d5ddaae6-d286-5ffd-9fae-d1493db86ae0 | note | Verifying Document - IANZ Accredited Report
2b739195-56d7-51cc-9ecd-190a6a5d061f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
4c6aa23f-cadd-5c3d-8ccd-0364ac600238 | note | ○ Results to Engineer 2 wks before importing
d90a5713-5369-5e31-af17-aa9a730edcf4 | note | Verification Activity: Activity - HP
b02136a4-dfb3-57f0-939e-6bbed172532d | note | Verification Activity: By - ENG
47bfbabb-4409-4a70-b28a-33c6e8858d13 | signoff | AUTHORITY HOLDPOINT
6ce595d4-24f5-41de-8631-549951d08907 | checkpoint | 1.5.1 - Crushing Resistance
2f5c97f9-e61b-56a2-aa5e-712c4d142422 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
21fa532e-a380-5b78-a213-6f676f360fb3 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
5f5296f2-c965-51b6-9713-b4ecbda358bf | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
59732cff-e5ab-5ed6-8b0c-4148ecd5ec02 | note | Verifying Document - IANZ Accredited Report
df6c20a7-927e-53c8-a293-3cb8ea188560 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
019b1669-7b1e-5fc1-8c51-968320b132ba | note | ○ Results to Engineer 2 wks before importing
a742e342-70e7-5327-93b3-873f59938850 | note | Verification Activity: Activity - HP
81b20f15-0347-55d4-a88b-49108c3fecdf | note | Verification Activity: By - ENG
00b5475b-2bc6-4cee-9bde-169b44e962b7 | signoff | AUTHORITY HOLDPOINT
57ffac27-2515-4376-a9ab-690cc094a5ce | checkpoint | 1.5.2 - Soaked CBR
fd3a4d97-16b7-5111-899b-aa24ca340f0c | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
8143c1f2-16ba-5e94-aed7-8524ed3c4d43 | note | Acceptance / Conformance Criteria - ≥ 60%
c3fb71f3-678e-5c3a-be8c-e7e8521ae832 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
de1bf16e-241e-5a54-91e0-e2bbae475ba6 | note | Verifying Document - IANZ Accredited Report
03ed405d-ada8-5d5e-9365-43212d062929 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
ffd42fb2-6d1f-5fe5-9438-6db3e4fb0d30 | note | ○ Results to Engineer 2 wks before importing
11197fe7-8bea-5ba7-9861-c598c88eb6bb | note | Verification Activity: Activity - HP
bb3ec055-4aea-543e-b22b-468bc16e8746 | note | Verification Activity: By - ENG
27adf4c9-d477-4ae1-9a6e-8a2cf3d73235 | signoff | AUTHORITY HOLDPOINT
b0e646b4-849d-4ee6-8f9c-e81803555daf | checkpoint | 1.5.3 - Weathering Resistance
8b015982-eff8-552d-b435-7a6e84af5a69 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
d5826536-29b0-59d5-a855-997aa524492f | note | Acceptance / Conformance Criteria - CA or better
2fee8da2-4cd7-5c43-bc8e-d6555e5d0562 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
76479d2f-f684-56b5-99b3-32acffcb422f | note | Verifying Document - IANZ Accredited Report
06309d18-34be-5ae3-9d31-a7767407e4e4 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
285c4865-7b1a-5b6c-989f-84af103c4335 | note | ○ Results to Engineer 2 wks before importing
c896e17f-8bbc-5908-b379-44eae06e8369 | note | Verification Activity: Activity - HP
d4ae2fa0-85cb-5fe4-ab4e-59c1c422522a | note | Verification Activity: By - ENG
6aa6cf9c-63a5-421f-b3ea-581381f517e8 | signoff | AUTHORITY HOLDPOINT
fded66f6-b112-4887-bbd3-66430d1f5ac4 | checkpoint | 1.6.1 - Particle Size Distribution
acb572d6-1968-5c91-8f63-d20b89c539d7 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
d3dda28a-5286-51c5-aea2-fac01bfb9dee | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
2b9f1bb2-f9f9-5291-81f5-ed641622b0db | note | 63.0mm ¦¦ 100% passing
61ec1f11-4e23-582a-ba59-32c7f6b95739 | note | 37.5mm ¦¦ 55-85% passing
50c30b7c-2ddc-5246-8405-534c0b6549e0 | note | 19.0mm ¦¦ 33-65% passing
6c76e1a5-7825-5667-aedd-f18d543d91ca | note | 9.5mm ¦¦ 20-50% passing
71f87ecd-8ac7-5ab1-8bf6-5330a2f4d633 | note | 4.75mm ¦¦ 10-36% passing
fea8a055-6333-5469-9436-678a22a713c8 | note | 2.36mm ¦¦ 5-27% passing
53ad37f6-4504-5391-8ae1-6b53ee891c76 | note | 1.18mm ¦¦ 2-20% passing
2f70f343-586d-5a6b-b049-65fe4ff75921 | note | 0.425mm ¦¦ 1-13% passing
a25b79e2-242f-5228-aa9b-39d52c42f375 | note | 0.075mm ¦¦ 6% max passing
be27b6f0-72b5-5aad-aec8-87038e9991d5 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
60243f69-84f3-5a25-bd57-09440d06ba2d | note | Verifying Document - IANZ Accredited Report
7c336808-e982-5e8d-9bdc-513ec75ccc44 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
327f9bcb-fb75-5c7e-b412-a6b0498c082a | note | ○ 0-400 - 2 tests
beaef7ca-311b-531e-b818-db0bf0008f0c | note | ○ 400-1,500 - 3 tests
8c9392e4-9c01-559d-ba41-085666e170bc | note | ○ 1,500-4,000 - 4 tests
0141e8e2-ae0b-5170-adec-a005e628527c | note | ○ >4,000 - 1 test for each additional 1,000m3
6115f220-9cf0-590d-bbf8-d163c364237a | note | – Results to Engineer 2 wks before importing
203f2751-d6c1-5dad-938a-c3720ec24231 | note | Verification Activity: Activity - HP
6df4f987-9c3a-5c7d-9219-4bff2c5ff131 | note | Verification Activity: By - ENG
d9fad559-30af-4748-8dd5-d6ee8c90ab4b | signoff | AUTHORITY HOLDPOINT
e4f45488-db64-4900-9961-2aba6b945c3d | checkpoint | 1.6.2 - Shape Control
8f3dd964-179b-54ee-979b-2677917141be | note | Detail - Tolerance allowed from approved grading curve (%)
f74c73a9-333c-5384-8fc5-664f4e942dd1 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
9dab7c3a-8338-5d76-9c17-d1b3afe9577a | note | 37.5 – 9.5 ¦¦ 34-50%
7d888140-8815-5fa3-b0ce-d592530e4e71 | note | 19.0 – 4.75 ¦¦ 18-40%
0c4e86c5-c57f-5f20-931e-6b18db5787f2 | note | 9.5 – 2.36 ¦¦ 12-32%
865da25e-4b48-5eb2-956a-560a6b542cea | note | 4.75 – 1.18 ¦¦ 6-24%
3595dbc6-49aa-508d-8fc0-b101414ea547 | note | 2.36 – 0.6 ¦¦ 2-20%
d2faacb2-5a42-5b9c-8e16-aa2645ee4b4f | note | 1.18 – 0.3 ¦¦ 0-15%
af435bff-b935-5365-8581-f013288dbc18 | note | 0.6 – 0.15 ¦¦ 0-12%
2ed25dd8-dd19-5deb-8994-fba0bba91a42 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
bb6d1f68-9da6-53dc-98dc-6b7aee1e059f | note | Verifying Document - IANZ Accredited Report
ca41b2fe-cf46-57ac-9825-c4f0d666cc92 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
f3b29147-b73a-5f1f-a03e-27009b11deea | note | ○ 0-400 - 2 tests
9bc69d86-59e1-5148-a57a-226e115429b7 | note | ○ 400-1,500 - 3 tests
dc21575e-f061-52ef-997d-51fcd5c67a75 | note | ○ 1,500-4,000 - 4 tests
6ac96ba3-6d54-5d79-94d4-2985f619c85c | note | ○ >4,000 - 1 test for each additional 1,000m3
4c3a4d22-88ea-56ca-a81c-522051ec71c9 | note | – Results to Engineer 2 wks before importing
7cd55c7c-36ca-5c6d-8cec-350a6ce06f68 | note | Verification Activity: Activity - HP
d4786860-4e8c-5b4c-b8a4-561699b35082 | note | Verification Activity: By - ENG
28955505-62c9-454a-b205-792c6f14b0b1 | signoff | AUTHORITY HOLDPOINT
35161628-0315-4014-83b5-141c4f57ee5e | checkpoint | 1.6.3 - Sand Equivalent
d292bbb5-95fe-5be8-9420-62455f453fdb | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
da183d42-e710-5f6d-86f6-b2557f92871d | note | Acceptance / Conformance Criteria - ≥ 30
d966c876-928f-5b97-8a4d-b8ff2fe89b82 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
e9a08cd8-e0d3-5f4d-a962-5071d0fbde76 | note | Verifying Document - IANZ Accredited Report
75b1e418-5040-540e-bdca-534512f5ff24 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
f7a1b7d8-23b8-59b3-9be6-6fe1ae1f150e | note | ○ 0-400 - 2 tests
52e6d77b-6415-5ff1-843b-ce5906112b29 | note | ○ 400-1,500 - 3 tests
efcd6bfb-fec0-5778-a8f7-c9ec4bcdfc06 | note | ○ 1,500-4,000 - 4 tests
127aee68-748a-5b6b-aa90-b69f4f6405e6 | note | ○ >4,000 - 1 test for each additional 1,000m3
c49e3845-8b22-5aa0-9df4-f7b2f9e1b43b | note | – Results to Engineer 2 wks before importing
7afd9db4-a896-514b-aed8-2129f8175936 | note | Verification Activity: Activity - HP
f4d7778d-f21b-5b1d-b61e-0456b0c8271f | note | Verification Activity: By - ENG
5b0dd7e1-2e53-4597-b2ed-62a35c4a788d | signoff | AUTHORITY HOLDPOINT
1245373b-8c14-49aa-9aa9-e39a3c2690e0 | checkpoint | 1.6.4 - Cone Penetrometer Limit
aa99ebef-7e4c-5ccb-a734-3ddcb34b3ab2 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
6a960e67-6a93-5b74-8c8d-34be2372aec6 | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 25
5d7f54ca-de96-5606-a16f-0e74dd037bda | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
770cb8fb-be6b-5bf4-b285-aa5685d73e97 | note | Verifying Document - IANZ Accredited Report
95f92f5c-e435-548d-80ee-0953e9a06712 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
1c5bcd3f-d495-5456-ac9e-7026b205d614 | note | ○ 0-400 - 2 tests
8389b67d-6e81-5770-af56-6502b00a89c5 | note | ○ 400-1,500 - 3 tests
f23c8f4f-ec26-562d-98c9-53aedcaee6a8 | note | ○ 1,500-4,000 - 4 tests
87256890-4bfa-5b42-874e-16f32d34bb69 | note | ○ >4,000 - 1 test for each additional 1,000m3
7873f697-d04c-5a49-b228-1264e818eb7c | note | – Results to Engineer 2 wks before importing
21df9621-98e9-5652-88c9-84862adeb8b8 | note | Verification Activity: Activity - HP
0bdf335a-9d61-5bf4-ad89-92de6b43bca6 | note | Verification Activity: By - ENG
f41ddc94-dbc1-4c3a-a3af-707df3298de9 | signoff | AUTHORITY HOLDPOINT
66e6a11f-1391-4671-bed9-e4a169ae5e1c | checkpoint | 1.6.5 - Plasticity Index
afb454e9-2605-5346-8210-967d9408ac7e | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
91eb8072-583d-5fb7-9851-e2532386adea | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
c5b73234-c77f-56b8-9ae7-5958c88ac396 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
eb053cfc-dab7-573d-8cca-45e45ee204a8 | note | Verifying Document - IANZ Accredited Report
0e96ab00-fd63-53b4-9a59-460ed1d5baff | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
4fe85226-0903-5604-855f-83374d2e42a4 | note | ○ 0-400 - 2 tests
3c891fdf-8d61-56cf-91c6-0bdaf545a501 | note | ○ 400-1,500 - 3 tests
be053d42-f2e0-56a5-8bd6-9039a88798a7 | note | ○ 1,500-4,000 - 4 tests
70829659-bb62-52ff-95ae-2d62f4dbfd83 | note | ○ >4,000 - 1 test for each additional 1,000m3
eb5ec36c-87af-55ef-8c77-5601a0f10d1f | note | – Results to Engineer 2 wks before importing
9dab3aaa-13d2-50f9-8d4e-85c8dee3de2f | note | Verification Activity: Activity - HP
e0f9e6ce-7881-5975-bb4d-bae8f1f4850d | note | Verification Activity: By - ENG
dae8bf9f-c8f7-48ad-a225-658aa90a852e | signoff | AUTHORITY HOLDPOINT
7f2f26c6-e87d-4bd0-998c-c36b5bb09ece | checkpoint | 1.6.6 - Accelerated Weathering
6e90061a-8b40-52bb-8b8d-86fed545a863 | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
cf34ac93-421d-5f5f-b07b-f02f3e0f7045 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
ff4e36fd-7594-5b3d-a010-9984fb6c2813 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
0589cbe9-e464-5f6b-8671-6918f67e5f8e | note | Verifying Document - IANZ Accredited Report
0d48fdde-cc3b-5ae6-b422-ff5efaad14cb | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
ddb398bb-a8c3-5ce7-a810-4cbf8d430def | note | ○ 0-400 - 2 tests
bc1ac96c-3f63-5aac-9171-9cb207556db5 | note | ○ 400-1,500 - 3 tests
89250bb8-adfd-57c2-8b12-4d6afb3bcffe | note | ○ 1,500-4,000 - 4 tests
f720ddc8-f62c-57ba-abca-fe66c2588121 | note | ○ >4,000 - 1 test for each additional 1,000m3
31fa3ae2-0d5f-51e2-85a9-e668afc85151 | note | – Results to Engineer 2 wks before importing
68d274c2-0389-5a9f-9340-0127ae9e4694 | note | Verification Activity: Activity - HP
7d90a44a-44c2-5c1b-9cd3-41306fcdf6f1 | note | Verification Activity: By - ENG
df813c86-ab3c-4f55-b0d4-86f7e9ac03c1 | signoff | AUTHORITY HOLDPOINT
101909de-fa2a-46b4-bb42-4529af2109fe | checkpoint | 1.6.7 - Maximum Dry Density and Optimum Water Content
1497bd29-46a7-57d0-9cb6-a226a23d3823 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
4a32f38d-65bb-56ff-a894-4f678752764b | note | Acceptance / Conformance Criteria - Report Value Only
694e0aec-67b1-5586-b72e-0f9b1930f3a7 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
c4129a88-5707-51ef-95e7-9200ace85e89 | note | Verifying Document - IANZ Accredited Report
49406ced-0fa8-565d-a35e-9bb49d573fba | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
67cbb732-cca2-5763-871b-5e8d9782b8f5 | note | ○ Results to Engineer 2 wks before importing
0d577e2c-5924-51f1-a35f-250bc51fd0b0 | note | Verification Activity: Activity - HP
92502d25-e1ce-5843-be22-7f2394019665 | note | Verification Activity: By - ENG
f682b319-bef7-4004-834b-f6143e5421d9 | signoff | AUTHORITY HOLDPOINT
780209b1-3381-499d-aa8d-440077a1bbcc | section | SECTION 2 – CONSTRUCTION - SUBSOIL DRAINS
c9a0f44d-bbbe-4658-996c-d3e6ce7a04d7 | checkpoint | 2.1.1 - Subsoil Drain inspection
0f03e87a-4ce5-5006-beb7-b2c7197df617 | note | Detail - Subsoils to be placed below kerb lines and inspected by Engineer
f0b15acc-cecf-5945-9904-788938a3504e | note | Acceptance / Conformance Criteria - Engineers Approval
c0211aa7-fb02-566d-8776-49f0885a3c13 | note | Standard / Specification - PS 17.6.3
c6cd9127-3730-530b-b691-47cf1f61a206 | note | Verifying Document - Release of hold point
bd994b9b-ab3e-5496-b86c-61ddf3d46115 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
34075fb3-d281-5f91-a8e0-b49e9b2ecde8 | note | Verification Activity: Activity - I
602319d9-51b5-5f91-bcbb-8a158fa9c746 | note | Verification Activity: By - ENG
18fff7d2-e88b-4e4c-ab5f-7aaec5ad4aee | checkpoint | 2.1.1 - Excavation
e0596ef8-e6bc-525b-86c7-10e1051579bf | note | Detail - Excavtion of Trench should be within tolerances.
01c4e9c6-9fa2-56b2-bf71-f935ff6c5798 | note | Acceptance / Conformance Criteria - 335mm deep x 300mm wide
f01b08d2-d0d1-5070-8312-f97b6798ead9 | note | Standard / Specification - Drawings
14096404-c34c-5aa5-8eae-29f4cef9e6dc | note | Verifying Document - Subsoil Checksheet
1e721651-bad3-5b53-8218-3aff30f1d6ed | note | Testing Quantity Required (based from schedule qtys) - During Construction
1e71cb5a-cd1d-5a5f-b81e-5eaf8ed25616 | note | Verification Activity: Activity - M
19a975a3-ceba-5ac2-9fa5-e8068a22d5e6 | note | Verification Activity: By - SE
cd630c77-4f2a-42c3-8ea1-1ae60dc34070 | checkpoint | 2.1.2 - Placement of Bidim
94c9ddb9-6dc5-5512-b21e-208a16a44a72 | note | Detail - A29 Bidim to be placed andd wrapped around Trench.
6c878745-84f3-51b4-8e02-e5d5b256e925 | note | Acceptance / Conformance Criteria - Minimum Width 300mm.
4628c80d-36c1-5aaf-9df9-bab54a0c81dc | note | Standard / Specification - Drawings
95257eea-5bb9-5ccc-a538-4261e613d173 | note | Verifying Document - Subsoil Checksheet
2f746bb9-06fc-500a-8dc8-8960c1811550 | note | Testing Quantity Required (based from schedule qtys) - During Construction
de3c0783-edef-51eb-883d-6493299d6502 | note | Verification Activity: Activity - M
dfb7c90c-c81b-5699-9907-e139fe6eac2c | note | Verification Activity: By - SE
4dacafe2-6213-4b59-aa22-f9adf31c08a6 | checkpoint | 2.1.3 - Cushion (Bedding)
b1c65d51-c6cd-5cca-acf8-517573d911d1 | note | Detail - Pipe must have 75mm of Cushion. Drainage 20:40 Material to be used.
558cf078-1664-537a-bb52-5e2bbe3aeb47 | note | Acceptance / Conformance Criteria - Minimum 75mm
e009158d-0192-52c8-b801-1dad981d7cd7 | note | Standard / Specification - Drawings
5cb1b3bd-e626-54da-88c7-30589059ec97 | note | Verifying Document - Subsoil Checksheet
05f61b71-6706-5c9d-8dbe-516c98bc7078 | note | Testing Quantity Required (based from schedule qtys) - During Construction
932f058d-d32c-58ff-8869-7db8518c2da6 | note | Verification Activity: Activity - M
10233c1d-f7f4-5ccb-83a0-9a5af93e75e7 | note | Verification Activity: By - SE
4ef045cd-8899-498d-b411-10d7bb038397 | checkpoint | 2.1.4 - Placement of Pipe
95c275ea-dda0-5b97-9fd0-7c4992b5894f | note | Detail - 110mm Perforated Pipe to be laid Down
21236585-cf9b-5d4e-b9f5-b465a0a8d258 | note | Acceptance / Conformance Criteria - As Per Drawings
37587856-e947-5a89-9ab2-78a84a1d25af | note | Standard / Specification - Drawings
53a05ca3-14c2-5dea-b708-2ac490bb29d6 | note | Verifying Document - Subsoil Checksheet
59743d09-80d9-5757-b9f2-84b8ddad9dc6 | note | Testing Quantity Required (based from schedule qtys) - During Construction
81a2f73e-1a2d-51be-8b4f-1851b582dab9 | note | Verification Activity: Activity - M
cf02a88b-a773-575a-b5b9-6551a62cdcac | note | Verification Activity: By - SE
a7abf62b-adfe-49c6-9b35-3778c10196d4 | checkpoint | 2.1.5 - Backfill
6851d909-e696-57c7-8f96-e8e8ac62c83a | note | Detail - Pipe Must have a 150mm cover from Bottom of Pavement.
e6111ff7-1a06-564a-bedf-2e734e83d4d7 | note | ○ Drainage 20:40 Material to be used.
fa995c9a-936e-56ea-a6da-7cf861d3d795 | note | Acceptance / Conformance Criteria - >150mm Cover
a6083ea5-b17b-51a6-ac29-067d28b4a1c1 | note | Standard / Specification - Drawings
732bde75-7050-5385-bd99-cdb140b15580 | note | Verifying Document - Subsoil Checksheet
11323b96-df18-511b-9b2f-9c6007d28dec | note | Testing Quantity Required (based from schedule qtys) - During Construction
c809d460-2eee-5d9f-b4a8-e4cce32c5fee | note | Verification Activity: Activity - M
1f2f20e0-4412-598b-9d84-37c8951b9acd | note | Verification Activity: By - SE
508a3d7d-c8bf-41c1-8eef-c75b6a2e2536 | section | SECTION 3 – CONSTRUCTION - PLACEMENT OF GEOGRID AND GEOTEXTILE FABRIC
0732ff46-0f8e-4d78-8d68-4746707e341d | checkpoint | 3.1.1 - Placement of Geotextile Fabric
c66e4071-e591-5122-b996-6ee241d0ce3e | note | Detail - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
186b53b9-2e05-5c21-87ef-da772d1d7ca2 | note | Acceptance / Conformance Criteria - Visual inspection
f33c2fcc-965d-519a-b236-1add7f5ebfeb | note | Standard / Specification - NTC0097
7163238f-bb09-5afe-b3c4-2ed2e843063b | note | Verifying Document - Visual inspection
84a43778-2257-5475-b88b-85c9a9965bfc | note | Testing Quantity Required (based from schedule qtys) - During Construction
d85dd530-711a-5d5e-85db-f30828ae2579 | note | Verification Activity: Activity - WP
09bd55a4-d788-52d1-885d-c29af9dbaeb1 | note | Verification Activity: By - ENG
338c6efd-e82a-4f78-9c2b-7c61229059e6 | checkpoint | 3.1.2 - Onsite Check by Engineer on Geogrid
f175aafa-ff75-5530-bff0-b1b29e410842 | note | Detail - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
ee3f5e08-ae98-5477-9f94-56515cd76db8 | note | Acceptance / Conformance Criteria - Visual inspection
e15cce84-4569-5ce6-b0bc-42974134ec8e | note | Standard / Specification - NTC0100
8bb1afa1-98c4-576d-85a2-7f5b55878970 | note | Verifying Document - Release of hold point
8a8e3eb0-7550-547d-b9ea-f80ad85d7cb8 | note | Testing Quantity Required (based from schedule qtys) - During Construction
f188a9ad-9203-57f2-9d4e-f068cf2dd6ed | note | Verification Activity: Activity - HP
ee8c54a6-cfe4-5402-a6ea-d934289b2cb5 | note | Verification Activity: By - ENG
ebca47be-adf2-42cb-b0e8-1d79226d4e89 | signoff | AUTHORITY HOLDPOINT
c71f9c33-c3bb-4a16-9c09-576dc5c93a6d | checkpoint | 3.1.3 - Placement of Geogrid
14c883c2-6149-57dd-b9c6-fef5343dee17 | note | Detail - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
ecd73193-6ed2-5356-a5c7-bc99d432fe3d | note | Acceptance / Conformance Criteria - Visual inspection
f172ec27-ef2c-563a-8454-2ad283febd0c | note | Standard / Specification - NTC0100
4cfb6987-4676-509f-b9c0-6ce88b7949ce | note | Verifying Document - Visual inspection
cc829193-e4dd-5054-a211-f594b6bb7488 | note | Testing Quantity Required (based from schedule qtys) - During Construction
0ce068f0-90d2-5737-85b7-1c0c5afc5f97 | note | Verification Activity: Activity - WP
3a8f6cb4-dd80-5562-99b5-6a9e6d825953 | note | Verification Activity: By - ENG
fbcbf2b1-81f7-4986-8cd1-26a9f961891f | section | SECTION 4 – CONSTRUCTION - SUBGRADE IMPROVEMENT LAYER TESTING
1704f5f3-813a-451b-8350-6539109f8764 | checkpoint | 4.1.1 - Plateau Density Test
d20b8454-0a71-5b5d-9de6-a8bc0783abc8 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
1906fb20-dfd8-5164-8055-a601639d0293 | note | Acceptance / Conformance Criteria - Plateau Density Report
3899a4e8-dbed-58bd-a5c4-c06bdd7c599b | note | Standard / Specification - NZTA B/02 7.5
7dee8da4-3abd-5333-b01e-ca920e02aac2 | note | Verifying Document - IANZ Accredited Report
49c7d788-8bdb-5ba4-aa55-f4e91ee23a83 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
11bd93fd-033a-5aba-88b0-007a807fbdd3 | note | Verification Activity: Activity - I
90266214-703b-59a4-98e3-ec252004b543 | note | Verification Activity: By - SE
4b261cdf-29bb-4ba6-8410-636087589e2d | checkpoint | 4.2.1 - Stringlines or equivalent
acd4d31d-35cf-5476-802b-26d4e9ab0061 | note | Detail - Stringlines or equivalent to check finished height of surface
1390d1aa-dd4e-5791-bc2b-86202a05902a | note | Acceptance / Conformance Criteria - -25mm + 5mm
222be1c3-0989-585f-b36d-8e91fa834747 | note | Standard / Specification - NZTA B/02 5.1
026430b0-f816-5c71-8d42-dad78643623c | note | Verifying Document - Check Sheet
9e4f3e48-0eed-5a1e-82e7-acb2695d94ca | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
3106f911-17ec-5914-a2f7-5f0d4121ac93 | note | ○ 1 set = 5 tests
abac6be7-1b1b-5b26-b889-78975326050e | note | Verification Activity: Activity - I
f683f145-337e-538b-8790-cd36b0a0815a | note | Verification Activity: By - SE
557190b8-78ed-4a1b-848c-9aae1f23200c | checkpoint | 4.2.2 - 3m Straight Edge
30ab32ee-126f-5e5f-ac4f-d04babf3b550 | note | Detail - Formation to ensure Surface is Smooth
cb8b92dd-33e8-57de-bd35-363f38337111 | note | Acceptance / Conformance Criteria - 10mm (-/+)
6b757d8b-cc88-5c54-83de-fca6fdca3f88 | note | Standard / Specification - TNZ B/2 7.7
2f23cf18-39af-562e-b235-3c32687466cd | note | Verifying Document - Checksheet
0ffbd940-f8af-5f60-b80d-fb802e616a33 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
f3ebe210-1b2a-5f61-b8f2-c295a9089e58 | note | ○ 1 set = 5 tests
2e14658f-0dc5-5925-9921-977da8f356f7 | note | Verification Activity: Activity - I
f25bcbcd-404d-50c2-8753-e2ccf470adc8 | note | Verification Activity: By - SE
8be63174-fd88-450a-95c3-4dac90f9fd6b | checkpoint | 4.3.1 - Compaction - NDM
717a34f7-6bee-5e34-9696-e96e9862abd2 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
43809d09-f875-5aca-8a76-06c43f717d9f | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
54197f0c-5f9c-5ddc-a409-2a0cdf749d6d | note | Standard / Specification - NZTA B/02 7.6
09c94633-54d1-558a-8c0c-0ae5721a2af2 | note | Verifying Document - IANZ Accredited Report
3764b5a7-c79d-5993-8dcb-8c23b881457f | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
789f8aed-98b1-5e2c-8f38-c55a6b10c38d | note | Verification Activity: Activity - I
875c8ad1-936f-58e2-8c1e-071a7ce15554 | note | Verification Activity: By - SE
a19a27c7-a9ef-4277-b0a7-692c153fc285 | checkpoint | 4.3.2 - Benkelmen Beam
3294d61a-787c-55d1-a25d-0bbd6ca63eb1 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
d6beeffd-da45-5ec7-a03f-f0080a10ce7f | note | Acceptance / Conformance Criteria - Engineers Approval
ccec9286-6f1e-5a9a-b1cd-503c58bce4a8 | note | Standard / Specification - NTC0160
10858f74-8d79-5369-bd4c-bed2c91f1154 | note | Verifying Document - IANZ Accredited Report
2d697e00-3da5-5e21-81ff-f49da10ed5dd | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
7f81cd92-dd78-5e67-85c5-8864953fe165 | note | Verification Activity: Activity - I
13638ca2-63e4-572d-8f0c-d21f90c66d82 | note | Verification Activity: By - SE
9738961a-32d5-48e4-8dce-4600f1cc52fc | section | SECTION 5 – CONSTRUCTION - SUBBASE LAYER CONSTRUCTION
63bd97ee-d1aa-4e34-b364-c47f2e0d3a74 | checkpoint | 5.1.1 - Plateau Density Test
4c14623e-087a-5003-b580-83605dd345a0 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
9e13c42f-712f-590e-af6d-afde073c31c2 | note | Acceptance / Conformance Criteria - Plateau Density Report
b413c405-6334-5b84-b7f8-757eb970bccf | note | Standard / Specification - NZTA B/06 7.6
aaa98e93-236c-52c3-afc7-ea42fc8a6969 | note | Verifying Document - IANZ Accredited Report
dcc00793-da02-5953-bc0d-8095bd646f4a | note | Testing Quantity Required (based from schedule qtys) - 1 Test
3e7445c1-f9a9-501f-bbd3-713df8c3de3f | note | Verification Activity: Activity - I
cbf471ca-fd30-5ced-9480-1ea3fda7b378 | note | Verification Activity: By - SE
e5de0bc4-6402-439f-b2b2-d70d4f4dff91 | checkpoint | 5.1.2 - 3m Straight Edge
e0062508-838a-55ac-a444-2d7b2b12a864 | note | Detail - Formation to ensure Surface is Smooth
adc187d7-3ac4-559a-a33a-560d596a78f3 | note | Acceptance / Conformance Criteria - 10mm (-/+)
b5bc08ea-9248-5f27-a41e-191aa2f302f9 | note | Standard / Specification - TNZ B/2 7.7
f0cab3b9-cb57-592e-9eb2-542b3ae44641 | note | Verifying Document - Checksheet
b481e96a-6596-5012-91ff-fe122552dec1 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
b69d0fa3-b75c-5777-bb56-72d36b99f810 | note | ○ 1 set = 5 tests
ea758b56-768c-5ae4-8db6-708bac46ad42 | note | Verification Activity: Activity - I
523e7a28-255b-53a2-9e1d-4b6de3df4239 | note | Verification Activity: By - SE
699bb454-a9af-40da-b774-cf979b2de58b | checkpoint | 5.2.1 - Stringlines or equivalent
4dcfed96-99c9-56ee-b967-194e1481bf56 | note | Detail - Stringlines or equivalent to check finished height of surface
f768d0a3-9501-5099-a153-c2edd7b7482b | note | Acceptance / Conformance Criteria - -25mm + 5mm
a2afbe27-e29b-5c9b-8a8a-389f6a93359d | note | Standard / Specification - NZTA B/02 5.1
7e84b04e-ec1a-5622-81da-a3ffff5d294d | note | Verifying Document - Check Sheet
4288ed40-e6d3-52e5-bd37-35ab5e9f9de7 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
ffd61f7e-7a81-5216-8f48-bf2cc6c86d0d | note | ○ 1 set = 5 tests
8022486e-46ab-535e-bb9f-204837cc058e | note | Verification Activity: Activity - I
6e076803-dc5b-5e56-957a-c5348ba3f75b | note | Verification Activity: By - SE
5ead6841-8b6e-4765-b03f-e66a46bd9b64 | checkpoint | 5.3.1 - Compaction - NDM
9883deee-6625-5220-b4a4-8f8fed8a9a8c | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
40418678-dc6f-5c87-941a-16d35afbdc54 | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
7aef05f9-7877-5335-9f51-cdb62c94aece | note | Standard / Specification - NZTA B/02 7.6
3d5b493d-0b87-56f4-a9aa-b5cb1b965587 | note | Verifying Document - IANZ Accredited Report
b4c7bafa-4a35-5bc6-ab63-18b6c74caa26 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
2144d8b0-692e-50da-bd0d-19b640e6f682 | note | Verification Activity: Activity - I
28c9a76f-0dbb-5ee7-b2c8-c55846dbdb02 | note | Verification Activity: By - SE
742d5d2d-bcbc-4c61-b8d8-9c21cae16026 | checkpoint | 5.4.1 - Benkelmen Beam
99e0bd81-202c-56ae-8928-5d60a134559d | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
585fb1f6-7545-595f-9644-04fdcbaf6ee1 | note | Acceptance / Conformance Criteria - 90th Percentile: 1.65mm
459bdca6-9fe4-55b4-b320-d07e54e0cb4a | note | ○ Maximum: 1.82mm
a5a3e3f4-c218-5e64-bccf-8d1d839b47ee | note | Standard / Specification - PS 20.14.5, NTC0160
6016dbba-230b-5b61-8b52-0645f3f92644 | note | Verifying Document - Test Report
828d0f2a-f3dc-5334-8f1d-65e7eac400fb | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
da3bd737-4b0f-5728-ae44-5c4539220c2e | note | Verification Activity: Activity - HP
456c958b-1442-5619-9e54-341c65e634db | note | Verification Activity: By - ENG
6404f98d-2b4e-42f6-abfa-e0616be5a8e4 | signoff | AUTHORITY HOLDPOINT
9c66bbe8-e2dc-4215-a2cc-f8febe1ac75a | checkpoint | 5.5.1 - QA Submission
09edb72e-e3f5-578a-8698-3cf344255300 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
b57d9c15-f27c-5941-a209-dfbb77a4eb52 | note | Acceptance / Conformance Criteria - Engineers Approval
2e19410d-6613-5a01-95b6-65c191d2f435 | note | Standard / Specification - Appendix V
ce10e081-cb19-5203-a909-f4ab6e1a88bc | note | Verifying Document - All test reports
7cf858a4-53a5-57f8-97ab-43b7f58dbb33 | note | ○ Material Test Results
10af2f79-b9e2-5f4d-9f67-c1f0942f1567 | note | ○ Laboratory MDD
13882438-a99f-5834-a88f-e9657b0604f8 | note | ○ NDM results
e94205f5-053e-52e4-a4fd-b7c941a83ec7 | note | ○ Proof Roll - hold point release
bbe0949e-dd4b-52f0-9f06-611216241e4f | note | Testing Quantity Required (based from schedule qtys) - Once
077a59ca-7715-55d2-8546-c08060cfaa2a | note | Verification Activity: Activity - HP
9072c04d-ff29-5a1d-bafc-74a05664e877 | note | Verification Activity: By - ENG
9ec6aac2-84e6-481b-a785-a4280d55de09 | signoff | AUTHORITY HOLDPOINT
cf4fcf3a-db8a-46f3-8d15-a01e45a57941 | section | SECTION 6 – KERB & CHANNEL PREPARATION
899b90e0-68ad-4db5-afe2-ab3565534027 | checkpoint | 6.1.1 - Stringlines or equivalent
1023fa29-0365-5640-a125-4b9194fda1af | note | Detail - Stringlines or equivalent to check height of surface prep
09836910-0b50-565e-b7c4-7c6d7294dd18 | note | Acceptance / Conformance Criteria - +/-5mm
ff906209-dc1d-5eec-ac42-ca17aba1b273 | note | Standard / Specification - PS 21.7.6
2df1ed5f-7510-5e59-8fdc-d0b88ab03ac0 | note | Verifying Document - Check Sheet
03ba536b-388d-5815-a7aa-9046fe85c9ee | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
adca65cb-4597-59d3-a134-190229d2b318 | note | Verification Activity: Activity - I
22f45d27-0a35-51e9-a8b5-650f4b954a32 | note | Verification Activity: By - SE
56062c06-c70f-4339-9c2a-9f50d3e46d4e | checkpoint | 6.2.1 - Compaction - Clegg Hammer
593dd740-efe5-5ca1-a813-9a0ac77a8f7d | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
c686f1a3-ff3f-5c5c-8364-7e157e3bd27c | note | Acceptance / Conformance Criteria - Min 25 CIV
3adf654a-51e1-5788-924e-c63c8dc7dd63 | note | Standard / Specification -
0a712ddd-b43d-5a7a-b9e9-6210807354db | note | Verifying Document - Clegg Hammer Report
c8a23c6e-0465-5d8f-94f4-dc94b617e42d | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
120b7062-749b-595b-a801-fdb79ce0ec77 | note | Verification Activity: Activity - I
94ef0de0-2e6e-51c8-b163-2f386f98d2fa | note | Verification Activity: By - SE
34d44896-ab9f-4e6d-8198-14c0b0ff4f7e | section | SECTION 7 – AS-BUILTS / REDPEN MARKUPS
4426daa7-0945-4c5b-b2d2-a9e07780d211 | checkpoint | 7.1 - As-Builts/ Red pen markup
e497ebc3-4169-51d7-8384-c2936a11240c | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
f018c892-11c1-564f-b62a-498f545fe7d9 | note | Acceptance / Conformance Criteria - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
bc21b89a-3b01-5d23-9d50-8461234324a3 | note | Standard / Specification - PS 16.7.6
f3ac0088-aa92-54af-be63-f134c925a8bd | note | Verifying Document - Red pen markups
7ea5d3fe-3c3a-5225-9a9d-0c262c9f8c4e | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
f02dda16-b68a-5242-b10b-93792cc26ec2 | note | Verification Activity: Activity - D
f7524803-8c31-53aa-98a4-663b27aabb3e | note | Verification Activity: By - SV
f51cc6b0-67e6-4391-8af4-ec53016ad791 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
a35e0753-1be5-5fb5-b671-f795abe98c53 | textbox | Contractor's Rep Name:
21ac8f41-6f1c-53d1-8199-539e5db86886 | textbox | Engineer's Rep. Name:
663b7691-31f8-5c72-b576-0f8d31f79366 | date | Date:
f72d9537-a070-4711-97d7-ea25994662b5 | signoff | Add Signature
cda9932b-ac1b-4772-9aa5-423b40cc628b | checklist | DN1210-027-001 - ITP Streetlighting - Ducting and Cable installation Rev 0 | itp | DN1210-027-001 - ITP Streetlighting - Ducting and Cable installation
de41dceb-1eba-4755-a9fe-fb19da227a02 | section | SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
e85a41b8-9815-4cf1-a721-a76fbdfaaa20 | checkpoint | 1.1.1 - Underground Services
4e9b1bba-a133-53d9-87a1-71cbc1f38772 | note | Acceptance / Conformance Criteria - Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage.
7491f41f-e10c-5fd6-ba4f-49a14aaf197e | note | Standard / Specification - PS23.5.3 b)
74bd2f4e-4037-535d-9df2-b3ad089ef470 | note | Verifying Document - Survey Data/Site Photo
44f1b69b-e68a-52e3-b5d3-f16761c1744b | note | Frequency - Pre - excavation
80bf52b3-ae1b-5e47-8189-1eddc4be31a6 | note | Verification Activity: Activity - H
d6e806e2-a42f-5bb4-8178-2d26fd80dbad | note | Verification Activity: By - PE/SE
a8cce687-381a-4319-a625-34dd5ca7d744 | checkpoint | 1.1.2 - Ducting and Cabling Route
550dde91-3495-515d-bde7-0f06a0adcd00 | note | Acceptance / Conformance Criteria - Confirm on site the exact location of cabling routes before trenching.
70d1cfff-aeab-5062-9cc6-a061e14765ea | note | ○ Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system.
30bc0823-fa11-5f94-b218-bf7327f5098a | note | Standard / Specification - PS 23.1.5 p) & 23.5.3 a)
85ee32be-7b2c-577b-99e2-0a42c3936170 | note | Verifying Document - Survey data/Comms with Client
1c328b6b-ce6c-525c-a2b5-0a4b1b0a7358 | note | Frequency - Prior to Installation
2e34b99f-40c9-54b4-a181-ffcd54c15448 | note | Verification Activity: Activity - H
5b40b32d-be33-5639-899a-72a6aba5b975 | note | Verification Activity: By - PE
007973af-bbe5-47c0-a4ea-396c43afe7ad | checkpoint | 1.1.3 - Location of Lighting Poles, Cameras, Cable Pits and Montrose Boxes
90cedc3d-1681-588b-96e9-53d4a9d36b83 | note | Acceptance / Conformance Criteria - Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation.
4b555aa0-e1e2-5bfa-ad9d-43e0ffb8900e | note | Standard / Specification - IFC Drawings
efb72eaa-4474-5799-bf1b-8e9a3c06141a | note | Verifying Document - Survey data/Comms with Client
e6cd1b17-4dcc-5e4b-a346-beeac539ca9b | note | Frequency - Prior to Installation
e1a6783b-bcf9-5ab8-ab8b-f42fcfa056d4 | note | Verification Activity: Activity - H
84debf06-7893-558b-81bb-ef33898e6b59 | note | Verification Activity: By - PE
9c1f6af6-3ddd-47c5-92ff-144fdc7a102c | checkpoint | 1.2.1 - Bedding and Overlay
a73dbb60-04b9-503f-b1bd-8acee4e1a3f7 | note | Acceptance / Conformance Criteria - Coarse Sand
8e974097-b1aa-51b5-b7b5-03cf9865c31e | note | Standard / Specification - PS23.11.8.a) ii-iii
a5a64bfd-da14-5e0d-abb7-0527934f52c1 | note | Verifying Document - Coase Sand - PSD Report
f46e85b9-d22c-5343-8731-fc9f97748546 | note | Frequency - Before construction
1d3e376e-a1e5-5199-94d0-eb2e88140fe8 | note | Verification Activity: Activity - H
baff00af-dcec-550f-8ce1-083087bc8bbe | note | Verification Activity: By - ENG
b35184d4-2af8-450e-8792-4d4cadbd7f28 | signoff | AUTHORITY HOLDPOINT
3a0af91f-19e6-4537-8817-51fefcc8729a | checkpoint | 1.2.2 - Backfilling
103fb9ab-e550-5061-b71e-f289a69e1782 | note | Acceptance / Conformance Criteria - Under roads and paved areas: Coarse sand, controlled low strength material or fine crushed rock. In topsoil areas: Complete the backfilling with topsoil for at least the top 50mm.
b797d306-8478-5817-b6b9-df491a685fdd | note | Standard / Specification - PS23.11.8.a) ii-iii
9982a1ad-c8e6-5fdc-a303-2aecd74f5ca8 | note | Verifying Document - Material data sheet and engineers approval
d2dd468a-e234-5b96-8f0a-dad9c8d9e1c9 | note | Frequency - Before construction
6bb61d78-1785-56b5-aa0c-53a9e5d0a04a | note | Verification Activity: Activity - H
428f594c-6563-51a3-b17e-4393c4ab6840 | note | Verification Activity: By - ENG
9462cfd0-6178-5a87-a4ad-901329e05571 | note | Comments / Closeout Details - Backfill materials will either be site excavated GAP65 which had been approved at Earthwork stage) or Soil
573d34d7-434b-4b0e-a5f4-bcafb9804297 | signoff | AUTHORITY HOLDPOINT
f0d94e98-46a3-4c9c-af9f-09d44aabf23f | checkpoint | 1.2.3 - Ducts and Fittings
75e234bd-dbcb-5fbc-a8b4-aedeed6ea892 | note | Acceptance / Conformance Criteria - Use heavy duty HD PVC for underground services. Use best practice PVC where possible. Orange colour for all conduits containing consumer mains, sub-mains or final sub-circuits cabling
67a631d8-662d-5b56-b083-787b70a6656e | note | Standard / Specification - PS23.11.8.a) iv
4cab70ac-9048-5e49-a685-1d74ae5a84e3 | note | Verifying Document - Material data sheet and engineers approval
d965e798-5c34-5f80-8cf4-81e9a43b4396 | note | Frequency - Before construction
39c49a5c-0ae6-5654-b0ba-ed3b832603eb | note | Verification Activity: Activity - H
a0fa6f64-c1ec-5fc1-8ff7-6bc730429afc | note | Verification Activity: By - ENG
3dc33307-a2e1-50c3-9a52-9a2f763b20f3 | note | Comments / Closeout Details - Same power ducts applied as Utility works
c952038e-288c-4a69-8353-265f07992068 | signoff | AUTHORITY HOLDPOINT
bb8606fa-34c6-403b-a59e-7252b72f5fb8 | checkpoint | 1.2.4 - Cable Pit
f6c48225-5bbf-5eb0-a21b-b625d604ef55 | note | Acceptance / Conformance Criteria - Aco Cablemate Polycrete "type 66" Dimension: 665mm x 665mm x 620mm with heavy duty steel lid.
36d15b1b-fe49-5985-84fc-3a1e4f30352d | note | Standard / Specification - PS 23.1.5 d) & Drawing 0122
fa61a229-8fcc-5b76-af06-62ce74a03f91 | note | Verifying Document - Material data sheet and engineers approval
dcba5a9b-1d92-5090-acc9-51212169a891 | note | Frequency - Before construction
36e932ee-9cb1-5e12-a96c-280a2953dd2c | note | Verification Activity: Activity - H
7ac91d64-edfd-5e6d-8c2e-a5dde8cd8f60 | note | Verification Activity: By - ENG
74b76730-fce7-400d-b2aa-d15f6c74b197 | section | SECTION 2 – CONSTRUCTION
6fb88986-845d-449d-af80-8bfeda2c1216 | checkpoint | 2.1.1 - Foundation & Bedding Compliance
95cb4dc5-7952-5cf7-bb45-75b3421a2fad | note | Acceptance / Conformance Criteria - Keep trenches free of water
8c97a95d-24da-5304-bec2-cdcd1bcfb796 | note | ○ No sharp projections, roots and other obstructions.
02d90c7a-562d-59af-aa67-44a2f288ff57 | note | ○ Then bedding with sand for 50mm
51592d24-67f7-5c5f-a728-a83b2f89e297 | note | Standard / Specification - PS23.11.8.a) ii
ce6e4d7e-b32a-5c83-8bd0-19ce7edb66fd | note | Verifying Document - Photo/Visual Inspection
2d4a60c4-fa48-5a38-a93f-0d03085de5f4 | note | Frequency - Each excavation
9f4c7af1-058b-5865-9be1-1140db9bb0ce | note | Verification Activity: Activity - C
4ca9d4e9-4e0b-5db5-94e2-37465fc24d65 | note | Verification Activity: By - SE
a44264bf-3198-44f1-bf2a-fe973bacee0b | checkpoint | 2.1.2 - Ducting
642607d8-0df0-52bd-a992-dd1aedc82901 | note | Acceptance / Conformance Criteria - Minimum 50mm separation from other conduits; Also follow separation requirements by utility operators when in shared trench.
0db3b1bf-21c9-51de-bab9-c0c17bfa84ca | note | Depth as per drawing (survey data):
a8fc9d96-a57a-55f2-b5a3-baeb749a8215 | note | ○ ≥900mm under Roadways, ≥600mm under Sidewalks/Berm;
c312ec67-c5a7-52ce-b3f6-3bb92e90135e | note | ○ Or Client Instruction on site.
95da64a9-1aa1-5f1b-a08f-16c201970c64 | note | ○ Where services cross, install electrical conduit at the topmost
714f410c-3d23-5820-b48d-419cd5d5f94c | note | Standard / Specification - PS23.11.8.a) v
e913771f-a004-5a84-935b-d8805efb79ab | note | Verifying Document - Photo/Visual Inspection/Comms
adfcf36a-160d-591c-a2e0-92423f6ffe83 | note | Frequency - Each installation
5a6fa599-b834-590a-a52a-664a36a4d178 | note | Verification Activity: Activity - M
790150c1-59dc-57a0-8469-c4a9b183f3dd | note | Verification Activity: By - SE
dab78477-1d9a-4c38-98d2-95047a01b499 | checkpoint | 2.1.3 - Sealing Ducts
d390e0e6-c76a-5848-8e8b-195e3048a9ae | note | Acceptance / Conformance Criteria - Seal buried entries of ducts and conduits using waterproof seals and/or conduit fittings.
8f82a5b6-e7aa-5ea3-ad4b-ba8dbbc6d0b5 | note | ○ Seal spare ducts and conduits immediately after installation and seal other ducts and conduits after cable installation.
035b358c-f3d8-5ba7-8281-ed7573395e68 | note | Standard / Specification - PS23.11.8.a) vi
fea256a4-3b51-5cfd-8608-8b2e5a3af5a2 | note | Verifying Document - Photo/Visual Inspection
5871317f-a190-57ca-b8d0-cf4d9d3e9f38 | note | Frequency - Each installation
71ec54fa-edc2-5046-9975-515f27288a3a | note | Verification Activity: Activity - M
2cb0ef48-0281-5fbc-96f6-e9ad2ee36674 | note | Verification Activity: By - SE
139ad055-f017-4ace-9891-9c81d7fd4962 | checkpoint | 2.1.4 - Survey data for ducting routes
60ccc0e3-485d-5720-8b92-613f7863e25f | note | Acceptance / Conformance Criteria - As built every ducts joint before backfill to accurately record the routes of underground cables.
c8f6fb56-cb2d-5095-b76e-c3e42b5591bf | note | Standard / Specification - PS23.11.8.b)
c43bc785-6152-5620-ac16-f37b28d73ad4 | note | Verifying Document - Survey Data
81bf0e29-f500-557f-8d17-71bd9b3ec2a2 | note | Frequency - Each installation
75391b0e-7e2f-5fbb-80c1-93a2b19369d4 | note | Verification Activity: Activity - H
14840e0b-14c2-5370-b1a6-eb251df634ff | note | Verification Activity: By - SE
c5f24295-a2f0-4c54-91d6-f620c1c3a24b | checkpoint | 2.1.5 - Marker Tape
d3446902-51aa-5aad-ad12-5bf32dbb1594 | note | Acceptance / Conformance Criteria - Install orange marker tape at 150mm or 50% of the depth of burial, whichever is greater, below finished ground level.
a46c9170-5fce-570c-97b3-0135295e3d98 | note | Standard / Specification - PS23.11.8.b) ii
4b0a0490-949a-5dd5-87d1-dccc3bcda281 | note | Verifying Document - Photo/Visual
2c40df16-8f9d-5f02-ab58-b113e995dd72 | note | Frequency - Each installation
d16bebb3-2631-5b76-a31e-0856beae25db | note | Verification Activity: Activity - M
9f7ab748-6850-5f23-aa5e-27bb842d6065 | note | Verification Activity: By - SE
2f082ed6-b78b-4b2e-8165-141f21faad76 | checkpoint | 2.1.6 - Backfilling
7356f8a7-a04d-520e-bd38-c83090b0edad | note | Acceptance / Conformance Criteria - Backfill trenches as soon as possible after approval of laid and bedded service.
76d3b08c-6456-5ff0-9baf-81f835b761f6 | note | ○ Place the backfill in layers < 150mm thick and compact to the density which applies to the location of the trenches to minimize settlement.
5e9e8913-7aae-5454-a77c-26250bf66b21 | note | — Under maintenance pad, Clegg test will be used, with target CIV 25 for GAP65.
06ce0253-7f64-530a-b3ff-19384ba0e3dd | note | — Under berm area, no test needed on topsoil.
02c91981-2bb2-58bc-a7f0-c9bc3be24591 | note | Standard / Specification - PS23.11.8.a) iii
01e11107-e2d7-523d-ad66-10a638573954 | note | Verifying Document - Photo/Visual Inspection/Compaction result when under Road or paved areas
aa01b1ad-658d-504a-95c4-b398174b5219 | note | Frequency - Each installation
b2a52398-9f05-5b64-92b6-9116a576eb6d | note | Verification Activity: Activity - M
04bed1c6-528f-5375-9cf3-d43e6ba64b2a | note | Verification Activity: By - SE
b6decc3c-3c45-4a51-913e-6f7a5825b795 | checkpoint | 2.1.7 - Cable Pit
b577b272-193c-5d89-ba59-dbd65dcd42e7 | note | Acceptance / Conformance Criteria - Install cable pits as detailed on the drawings.
0b49d719-18ff-58f2-baad-af45df0d8be6 | note | Standard / Specification - PS 23.1.5 d)
49e243b3-4435-50b9-abb3-f4f110db5f1d | note | Verifying Document - Comms with WSP/ Photo/Visual Inspection
f77d5da3-7b11-52c9-8de5-7f015328b68e | note | Frequency - Each installation
8a8b9026-3f26-5f67-b522-c77652054dd7 | note | Verification Activity: Activity - W
71ab1403-f5bc-5fc9-bdc1-53726111b30f | note | Verification Activity: By - ENG
dca3d85a-c93f-494b-843d-6984cf5b638f | section | SECTION 3 – POST CONSTRUCTION ACTIVITY
8b9bf5b4-1434-4002-9b49-c124e559b406 | checkpoint | 3.1 - As-Built
2c2259f1-7447-5847-8d94-febbfc45affe | note | Acceptance / Conformance Criteria - As-built drawings with
d192fa6c-3ce4-52fe-a29d-5c71b836192c | note | 1) ducting routes.
ea265cbd-505f-5dc9-816b-d9b76f629128 | note | 2) control groups,
10786deb-c6fb-5c17-bade-cd8a8d00580e | note | 3) scene settings
e2192fdd-2457-502b-a272-28bb630e10ce | note | 4) override sequences,
1b58c0dc-d922-5abf-9e58-c7fd7d4abd9e | note | 5) luminaire and pole locations,
8b49b0d7-8982-5b68-ba51-d832e9a8d666 | note | 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes.
3796fc4e-a8a5-51e7-8732-291f2e2e6408 | note | 7) All changes to design to be noted, highlighted or markup clearly.
fbde06aa-efb2-5325-a444-941e3e34fb2f | note | Standard / Specification - PS 23.1.5 h) & 23.8.5 a)-b)
265ec1e7-fc99-592f-a010-ecde5285a792 | note | Verifying Document - As-built Drawing/Survey Data
d6c9f86f-860d-5024-9ccc-890cee876245 | note | Frequency - Post construction
8e419d11-901a-56e8-8435-1075dba76678 | note | Verification Activity: Activity - HP
764c9fa3-5d7e-529c-9592-775b92cd275d | note | Verification Activity: By - PE/ENG
bd77a42e-8bf2-4e57-9936-b83f42e44247 | signoff | AUTHORITY HOLDPOINT
cfb8f18c-e017-46ae-9e89-bce686a00648 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
c64c23f4-ae28-5d08-baaf-29af316a04ab | textbox | Contractor's Rep Name:
0937ba13-5e22-56b8-ac66-6e87161e3fce | textbox | Engineer's Rep. Name:
72408430-0c69-55e1-b00a-a40458ec2605 | date | Date:
892a2472-8102-4f2f-bde6-0dac9c1b16fb | signoff | Add Signature
c6af23e9-715b-4f07-826f-f62980190cbe | checklist | DN1210-027-002 - ITP Streetlighting - Luminaire @RAB Rev 0 | itp | DN1210-027-002 - ITP Streetlighting - Luminaire @RAB
2e43f5a8-3f1b-409f-b95f-2def447c7faf | section | SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
5fda5ef3-4776-4757-94f4-71c17840c0d6 | checkpoint | 1.1.1 - Underground Services
15d03ebb-ed62-53c3-997d-aac1d86ea1d5 | note | Acceptance / Conformance Criteria - Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage.
39fe2ddb-99e7-5d61-9552-58ea5aef8378 | note | Standard / Specification - PS23.5.3 b)
d0b48e5f-8e29-5911-adf7-8fdb1e589301 | note | Verifying Document - Survey Data/Site Photo
25b33ccf-c804-502e-ac4b-8d4c409fba4c | note | Frequency - Pre - excavation
9e2ee90e-c345-547c-bd69-afcc16b73bc7 | note | Verification Activity: Activity - H
a308d4a5-4988-541d-af55-e5cf811ebf3b | note | Verification Activity: By - PE/SE
b33e8e26-30d6-4a52-8688-8a97357baed0 | checkpoint | 1.1.2 - Ducting and Cabling Route
2f12a254-47b8-54ce-9a1e-356222780c78 | note | Acceptance / Conformance Criteria - Confirm on site the exact location of cabling routes before trenching.
6bd89240-17bd-5e6c-9abb-c7587d1c17fd | note | ○ Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system.
94f5e947-2b3f-572f-9c2d-039799bfe52b | note | Standard / Specification - PS 23.1.5 p) & 23.5.3 a)
e0e4125c-c6b5-5a76-a9d8-dcb890305dc4 | note | Verifying Document - Survey data/Comms with Client
7e6f01c9-9ea5-59c6-9659-bd9378816174 | note | Frequency - Prior to Installation
1c7fb30b-e121-5e64-a833-f280bfde92a0 | note | Verification Activity: Activity - H
1874d2a9-3c7e-5972-9db4-150eb28e2cf7 | note | Verification Activity: By - PE
f6b25012-2605-4958-83d1-a8ea0b1b8a24 | checkpoint | 1.1.3 - Location of Lighting Poles, Cameras, Cable Pits and Montrose Boxes
e269dea3-3855-56b4-8639-24c2f9d157ee | note | Acceptance / Conformance Criteria - Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation.
8839152a-e1e0-5857-93f3-0eb24fd3ab98 | note | Standard / Specification - IFC Drawings
d62a8826-86d1-5def-9d41-48f5a2d19da8 | note | Verifying Document - Survey data/Comms with Client
47ed8d59-f73f-5ab1-9734-c506cc6fd000 | note | Frequency - Prior to Installation
e87ec0a2-bc08-5e4e-9667-2f3f34856530 | note | Verification Activity: Activity - H
da2eeaca-2dd4-532d-a629-c34a6950a65a | note | Verification Activity: By - PE
6fbfc24a-1f4a-47e7-b70d-3137d97df71e | checkpoint | 1.2.1 - Montrose Box
b0b2f6be-c607-5fb6-9be4-30af0edc96ab | note | Acceptance / Conformance Criteria - Provide MSB-NMB shop drawings complete with wiring schematics for review and approval by the Engineer prior to construction.
6b360d98-ea7d-5b90-8316-dbc31f308596 | note | Standard / Specification - PS 23.1.5.a) ii
48203735-48bf-5fe2-b9a8-11c683794ab9 | note | Verifying Document - Shop Drawings and engineers approval
2d138412-197d-56e2-a21d-e599af7c6071 | note | Frequency - Prior to Purchase
40278a55-4e98-504e-8f68-dc15994e7107 | note | Verification Activity: Activity - H
1a8b9a8c-06ae-577c-938f-a2d3a3766bdf | note | Verification Activity: By - ENG
566858ab-ea1a-4ea3-bd21-d36a01c0707d | signoff | AUTHORITY HOLDPOINT
891ed4de-f3f4-4b99-b507-9e9e6ae7956c | checkpoint | 1.2.2 - Pad, Hasp and Staple
b856e668-7dd1-53bb-93e8-4b8167901f98 | note | Acceptance / Conformance Criteria - Supply new Montrose Boxes on concrete plinth as per Electrical Services drawings. Box need to be fitted with a stainless steel hasp and staple brackets to allow for Waka Kotahi to fit their own padlock onto it.
4ca65941-269a-538d-beff-e1f9ee344780 | note | Standard / Specification - PS 23.1.3.b) & 23.1.5 a) ii; Drawing 0413, 0411, 0412.
cdca47ce-d97d-5c8e-b8d1-f3778aecdd66 | note | Verifying Document - Material data sheet and engineers approval
4063baaa-8a9f-5ff7-83e6-2a342309a93e | note | Frequency - Before construction
feeb956f-96bf-55ec-a888-9a02b0aaefad | note | Verification Activity: Activity - H
fe18ee69-ff3f-5b1d-a9b1-eb990aad6011 | note | Verification Activity: By - ENG
fa1b597a-d360-455d-b17f-28a3f8ab1a3b | signoff | AUTHORITY HOLDPOINT
bf02e8f5-5481-4d68-a216-901a158f0294 | checkpoint | 1.2.3 - Luminaires & Poles -WK & TCC Redwood Ln RAB
6d2f41a4-e804-5f1f-8849-586d1da10e2f | note | Acceptance / Conformance Criteria - Luminaire and Pole types shall be supplied and installed as detailed on the drawings or as per instruction of Client
84b640d2-09c9-53e8-b3d3-cb259099052f | note | ○ Luminaire Controller - PDL- 56SS10.
d534375c-faa6-5267-b136-2a56b93bbf1a | note | Standard / Specification - PS 23.1.5 g) & Drawing 0411, 0412
74542dea-5a0e-5e07-a9c9-58bd697cf944 | note | Verifying Document - Material data sheet and engineers approval
3a7bfa31-5d87-57cc-8eb7-66e3eba46e9b | note | Frequency - Before each Installation
fd9af9f1-6ab7-54db-bba6-51fd0253838c | note | Verification Activity: Activity - H
0c75e3a4-fe2a-578b-ad46-073af3067627 | note | Verification Activity: By - ENG
11be8082-514f-5a28-a435-b16f55bf83bb | note | Comments / Closeout Details - Purchase of Luminaires/Poles already approved by Client.
0127fc11-9bb4-51e5-a394-e2507671ef07 | note | ○ PE/SE need to check on site to guarantee right type of luminaries and poles are installed at specific location.
6ac274a0-820e-49dd-885c-380ec8ae8aea | signoff | AUTHORITY HOLDPOINT
0150cb71-47ab-46b2-a541-f679a86d15b7 | section | SECTION 2 – CONSTRUCTION
0f9b3a97-4f61-4ba6-a747-10d166870d25 | checkpoint | 2.1.1 - Pad, Hasp and Staple
f287d67a-c274-52cc-b4a2-2242700a2cfe | note | Acceptance / Conformance Criteria - Install new Montrose Boxes on concrete plinth as per Electrical Services drawings.
a74996ea-2c7f-54a5-9817-f271bf97d9c0 | note | ○ Install stainless steel hasp and staple brackets to allow for Waka Kotahi to fit their own padlock onto it.
fde379f0-76cd-5e8b-95c7-db1c53d7b261 | note | Standard / Specification - PS 23.1.3.b) & 23.1.5 a) ii; Drawing 0411 - 0413.
ec384d6c-f028-5f9a-b445-f44ca72a0e90 | note | Verifying Document - Photo/Visual Inspection
47522002-7527-5e7c-ba79-6665b879f5f8 | note | Frequency - During construction
255c750a-0336-5d72-bdd0-933f57063eb9 | note | Verification Activity: Activity - I
226ed708-4c54-54d1-8d36-337494f01dfa | note | Verification Activity: By - SE
4fd45516-c903-420d-a8e5-b33ad1a8cff9 | checkpoint | 2.1.2 - Earthing, Bonding & Surge Protection
f6fcab18-79a4-54a3-801c-917237934b3b | note | Acceptance / Conformance Criteria - Install an earth electrode in accordance with the AS/NZS 3000. Install new Earth Bar and Neutral Bar c/w MEN link;
747c85a3-fcff-508e-90cb-021d848e380f | note | ○ Install Circuit Protective Devices as specified in Drawings;
0a7b565a-e179-5f22-bfcf-050fde55e63d | note | ○ Install Switchboard as per details in Specification.
a2bd8fe7-9c18-5a0e-888d-b8c071a7d10b | note | Standard / Specification - PS 23.1.5.a) ii & iii
c899b116-67ac-5f40-bf97-71b6bd3f9a6a | note | Verifying Document - Photo/Visual Inspection
387dc988-1e67-5935-8246-0f72f946a3b0 | note | Frequency - During construction
f6b85ad4-5580-5323-b5a4-d4a7bbb71bc2 | note | Verification Activity: Activity - I
addf7b1d-cc0f-5982-8fed-ec23e9408b67 | note | Verification Activity: By - PE/SE
bcd259b8-a1ea-46bf-95e9-2e2e234393a1 | checkpoint | 2.1.3 - Metering Compartment
84d1f349-feb4-59f8-8ddb-249df762c588 | note | Acceptance / Conformance Criteria - Liaise with the client’s electricity retailer for the installation of their three-phase meter within the metering compartment of the new Montrose Box.
365a122f-fba7-5c21-829c-cd799139e9f6 | note | ○ Metering Agency supply of low Voltage meters and metering current transformers.
473539db-316f-5858-9c2b-6f7a9a149007 | note | Standard / Specification - PS 23.1.5 a) & 23.3.1& 23.9.4
b487001e-fe85-54a8-af73-48866e5a8276 | note | Verifying Document - Comms and Photo/Visual Inspection
7467c176-96fc-586d-8cae-da7af095a32c | note | Frequency - Prior to Installation
3343916b-98e3-51ff-8d26-55013b02a48d | note | Verification Activity: Activity - H
c8aaedfa-efff-5348-a6c9-6be1f12aac28 | note | Verification Activity: By - PE
58d8f734-1b3a-4134-9518-7aac4dcec6b3 | checkpoint | 2.2.1 - Luminaires & Poles (WK & TCC @ RAB)
54c9a83d-b846-59ce-96a5-7f8bfa9c327d | note | Acceptance / Conformance Criteria - Types of luminaires and poles shall be installed as per details on the drawings or as per instruction of Client
80e80b39-c372-57de-a86f-89442c477def | note | ○ Luminaire Controller - PDL- 56SS10.
2890729c-f372-59d8-8a0b-a29566036664 | note | ○ Luminaires shall be fitted with Shorting Caps.
c7a3fed1-a6e2-57e5-918a-3129d4060d16 | note | Standard / Specification - PS 23.1.3 c-d); 23.1.5 f-g) & Drawing 0004, 0407-0409,0413
8c45191c-b8ee-54a7-96ee-809d2048e9b9 | note | Verifying Document - Photo/Visual Inspection
6abcce20-01df-538d-99e0-1a34f56420bb | note | Frequency - Each Installation
88aa0b64-5acb-5ac8-a38a-338b58002f69 | note | Verification Activity: Activity - I
cff33fb6-4ccd-56a5-a41b-bfee60f5268e | note | Verification Activity: By - PE/SE
01831604-7e2a-4f98-b75a-20f12dfb0ef4 | checkpoint | 2.2.2 - Circuit Cabling (WK & TCC @ RAB)
63432621-7708-5dc2-ac8f-9b7c145c1e40 | note | Acceptance / Conformance Criteria - Supply and Install final circuit cabling to Luminaires from the Montrose Boxes via underground ducts and conduits as per Drawing - proposed circuiting layout.
be729d5f-7647-5a3e-ae6f-8679092729b0 | note | Standard / Specification - PS23.1.3 g); 23.1.5 e) & Drawing 0131 -0135
b80e8548-10cc-5f94-bccc-11a69261c0ad | note | Verifying Document - Photo/Visual Inspection
1cf0ef6e-4052-59bf-8657-20509deb3df8 | note | Frequency - Each installation
f32bf408-2332-5fa5-a391-9ed6412055d4 | note | Verification Activity: Activity - I
1ed13e40-d0e4-5a9c-94dc-57bd475e642a | note | Verification Activity: By - PE/SE
40c68e2a-abff-46c9-9048-87a808acd41d | section | SECTION 3 – POST CONSTRUCTION ACTIVITY
5514a5df-e404-43b4-974a-968bc518a79f | checkpoint | 3.1 - As-Built
ae7a2a9c-c466-5a02-aad8-2585aef55566 | note | Acceptance / Conformance Criteria - As-built drawings with
47bbf7d8-0a41-588d-81b7-ef40a46e2ab9 | note | 1) ducting routes.
e98a5052-5639-573b-99f1-cd3f88dc462e | note | 2) control groups,
516b6bea-b31d-504c-b447-46ff367bf2bb | note | 3) scene settings
75e3a9be-d11b-5f97-a023-f1e54bdee439 | note | 4) override sequences,
092da9fd-7e98-5105-abaf-dc95bc47eaa7 | note | 5) luminaire and pole locations,
b9fe3885-a14c-544d-a0cf-b107ed8f08ea | note | 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes.
e43fd52a-eae2-5735-b3a2-6b9cef2f5813 | note | 7) All changes to design to be noted, highlighted or markup clearly.
6c82e042-f3d6-5c0f-a662-6bdcc545c184 | note | Standard / Specification - PS 23.1.5 h) & 23.8.5 a)-b)
4b53b9b1-eea6-5bd4-aee0-9c4347f129b7 | note | Verifying Document - As-built Drawing/Survey Data
58780e00-ca3f-5cff-b5d3-6b43e4ba1a4e | note | Frequency - Post construction
e3b79c0b-1a5d-5d45-8080-7ba711d0c5da | note | Verification Activity: Activity - H
8a52682e-011f-5f5a-a8d0-b0d13c06e933 | note | Verification Activity: By - PE/ENG
72241c9f-8480-491d-8086-209ccb1f2a7b | signoff | AUTHORITY HOLDPOINT
30dc6e8c-5f3c-4b0c-a432-8ec650abd1e3 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
46a5bfaa-a2e2-5cb4-b370-0a0c187ba722 | textbox | Contractor's Rep Name:
0cdac6fd-837a-54c5-a5c3-d2b8f5575d9e | textbox | Engineer's Rep. Name:
ef4cc762-669f-5bf9-94a6-e638680151a5 | date | Date:
b06349d4-cd6a-42e8-9fbe-80f96a1cb25c | signoff | Add Signature
24d120c4-20ea-4e57-b58c-1cf5aeb94f26 | checklist | DN1210-027-003 - ITP Streetlighting - Luminaire and CCTV @underpass Rev 0 | itp | DN1210-027-003 - ITP Streetlighting - Luminaire and CCTV @underpass
0f6c99e4-49c6-4854-910f-4ab60b021834 | section | SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
fe1b3228-f69a-43d5-828a-5181c37a8b24 | checkpoint | 1.1.1 - Underground Services
7c775439-35d6-56c2-bc04-eff2db4b1d80 | note | Acceptance / Conformance Criteria - Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage.
dcfda641-dc82-5bc7-8a11-cade1fe66634 | note | Standard / Specification - PS23.5.3 b)
8e26989c-28b3-5314-8609-0294028cf47b | note | Verifying Document - Survey Data/Site Photo
bdd60f43-1770-5a05-a766-4bfd9b61295a | note | Frequency - Pre - excavation
3165dc40-4188-5349-bd34-5b8c34ff638c | note | Verification Activity: Activity - H
a5e38fd3-98dd-54b0-b1f4-b9d1c5c38079 | note | Verification Activity: By - PE/SE
8ffebfd1-4d30-40ae-8e6b-3b979e40525c | checkpoint | 1.1.2 - Ducting and Cabling Route
317afe80-93d4-5d53-96a9-8707e6dfdfb9 | note | Acceptance / Conformance Criteria - Confirm on site the exact location of cabling routes before trenching.
1a804e43-aa43-5a9d-a570-0ed3abc2549a | note | ○ Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system.
36f844de-a61f-57a0-aaa5-1c1775791b42 | note | Standard / Specification - PS 23.1.5 p) & 23.5.3 a)
765e9173-1eb2-5ad2-9417-8659aa8f6fd8 | note | Verifying Document - Survey data/Comms with Client
ad9d7c7a-41ac-5034-8fcc-008782caf63c | note | Frequency - Prior to Installation
bc79b36d-524e-5b1c-a3ab-b909c0f18239 | note | Verification Activity: Activity - H
42124d8c-d893-5b9f-bbf0-e65ac086e9a7 | note | Verification Activity: By - PE
1c2dbdca-0bfd-4f31-b935-124e308b4180 | checkpoint | 1.1.3 - Location of Lighting Poles, Cameras, Cable Pits and Montrose Boxes
8e3b3f13-1efa-5525-87e8-74bb5d402310 | note | Acceptance / Conformance Criteria - Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation.
564ff9ab-2250-5add-8dc3-d441ce4114ea | note | Standard / Specification - IFC Drawings
1b16e267-5c2b-5de9-85d7-886e584d89bd | note | Verifying Document - Survey data/Comms with Client
19d56848-cea8-58f1-9a56-06102d121c6d | note | Frequency - Prior to Installation
42d06f16-2a77-5b68-9ed7-d5f9990b9ec5 | note | Verification Activity: Activity - H
d91f171e-b21e-594d-bb15-7721352e7aac | note | Verification Activity: By - PE
1cccabad-59e9-4bbe-9ae5-e7654d7bfbbe | checkpoint | 1.2.1 - Luminaires - Underpass
f2c62957-19d2-58ae-bcae-aad742f94b05 | note | Acceptance / Conformance Criteria - Luminaire and Pole types shall be supplied as detailed on the drawings or as per instruction of Client.
dd787517-afde-5f8f-9fcf-0bb1e7802b6b | note | ○ Luminaires Controller - CASAMBI "CBU-TED" procured directly from Energy Light NZ.
6cf79f03-0cbf-589a-9ad8-9afdcd7b35cb | note | Standard / Specification - PS 23.1.5 g) & Drawing 0412
06591aab-ed1e-58ef-9074-5d45fac1f3c5 | note | Verifying Document - Material data sheet and engineers approval
d6eba0a6-53fa-50bc-836d-e87cc79a1db4 | note | Frequency - Before each Installation
5c23be33-d57e-5450-9f33-3a507eb7340c | note | Verification Activity: Activity - H
797b1075-a602-5988-baae-05d93daf6fb3 | note | Verification Activity: By - ENG
6ff270c2-bcf3-555f-9b3b-5ffe2f19e1ed | note | Comments / Closeout Details - PE/SE need to check on site to guarantee right type of luminaries and switch are installed at specific location.
cb1bb416-79e8-46d5-a030-5986c5026d4c | checkpoint | 1.2.2 - CCTV Cameras and PoE Switches
d81cc660-2334-5ee9-9648-25edaeaf5c2d | note | Acceptance / Conformance Criteria - TCC Approved IP67 IK10+
5718eb24-84df-5186-bbb8-6b126055f482 | note | ○ With Weatherproof Housing , Vandal Resistant and PoE Dome (HD1080p, 2MP), Sensitivity down to 0.01 lux
4eda383d-e4fe-55b9-84d7-e54e9eb2097f | note | ○ Have intelligent auto exposure to offer front and back light compensation.
2522ddbc-a2ca-57f7-9bc7-656966146745 | note | ○ TCC approved Power-over- Ethernet (PoE)
75e738f2-ea8f-55a1-bffb-4f7204614f94 | note | Standard / Specification - PS23.1.5 n)
1beabf9c-f38d-535c-81af-8f3a4180671c | note | Verifying Document - Material data sheet and engineers approval
eeab5288-61c3-50da-b64e-6da7a5a1deda | note | Frequency - Before each Installation
6ef5c06f-fb52-519d-a47b-848ef782a97e | note | Verification Activity: Activity - H
de6000dc-be0f-55d2-92ab-7d96aed7aab3 | note | Verification Activity: By - ENG
620af39f-d21c-4417-91bd-2408040d8f83 | section | SECTION 2 – CONSTRUCTION
d3f1e878-500f-4d9b-9ea1-7a2d805fcb71 | checkpoint | 2.1.1 - Luminaires - Underpass
10949904-5e58-5ee5-aacd-4d93aa207873 | note | Acceptance / Conformance Criteria - Types of luminaire and poles shall be installed as per details on the drawings or as per instruction of Client.
2d9bb4fa-99db-5f94-af54-bb8d1adfd73d | note | ○ Luminaire Dimmer Controller - CASAMBI "CBU-TED".
ccc18197-d0f3-57ed-878e-764b8b065193 | note | ○ Time and Dimming percentage be adviced by Light Engineer WSP.
298757ba-f751-5892-bd3a-accddf2734d2 | note | Standard / Specification - PS 23.1.3 c-d); 23.1.5 f-g) & Drawing 0415
7ddf6137-a93f-5097-b0b8-f8725e404f33 | note | Verifying Document - Comms and Photo/Visual Inspection
61adebf4-c8d9-5a31-9084-58f489c831e3 | note | Frequency - Each Installation
b94614cd-8850-5aa0-b1ba-53dace19ec68 | note | Verification Activity: Activity - I
1ba91e17-d70f-52bd-9925-8864367f437c | note | Verification Activity: By - PE
8a0276a7-e3b6-441e-aee0-00a0f4b4e0f4 | checkpoint | 2.1.2 - Circuit Cabling - Underpass
7e5d740b-c57c-564c-9f03-6ba1a5e07b6b | note | Acceptance / Conformance Criteria - Every second luminaire shall be on separate circuit (MSB-TC-NMB/R3 and B7) as per Drawing and terminate into a CASAMBI "CBU-TED" Dimmer Driver Controller via individual 230V-rated Switches.
dd8fa15d-afec-570e-b9b1-1604bbaaec30 | note | Standard / Specification - PS 23.1.5 g) & Drawing 0405,0415
35cd9eb9-df8f-5353-86f6-172893340048 | note | Verifying Document - Comms /Photo/Visual Inspection
284c11e2-a502-5646-9184-de48300a9261 | note | Frequency - Each Installation
9f97f10e-5fd3-5f76-a2cf-feece0d6bafa | note | Verification Activity: Activity - I
121227fe-f554-50dd-8e79-7b417324ed95 | note | Verification Activity: By - PE/SE
b063be56-f675-4490-8a16-53db7b82ecd9 | checkpoint | 2.2.1 - Camera and Cabinet Location
e915143e-0fc8-5e40-9fdf-7516e9e75acb | note | Acceptance / Conformance Criteria - Cameras mount at high level on chamfered edge of underpass or the underside of the sealing if no space after lighting installation.
e2d27d81-33ee-5b93-8efe-b608942d9f2e | note | ○ Lockable CCTV Cabinet mount at high level underneath the chamfered edge of underpass.
f3c92b01-3020-58e1-9e88-dfc1220fc257 | note | Standard / Specification - Drawing 0406
1e4cedd0-528d-552e-b73b-2c4d0b8ee639 | note | Verifying Document - Photo/Visual Inspection
0b394d4e-a804-5c7a-8715-9abe2f062213 | note | Frequency - Prior to installation
1865906f-c851-5626-b4fd-89ad0d6cad9d | note | Verification Activity: Activity - H
194b6b22-1aed-51a4-a8b8-c1d916ede81f | note | Verification Activity: By - PE
0b71134c-d5be-4377-83ef-837a898dcbd7 | checkpoint | 2.2.2 - Circuit Cabling
66b71de8-36bc-5582-b343-64cdeca46705 | note | Acceptance / Conformance Criteria - Cabling from cabinet to camera through ridged conduit.
7e989d85-3277-5398-a852-ef7f8c6a0464 | note | ○ Between Montrose Box(MSB-TC-NMB/R7) and Cabinet - Tight buffered outdoor OM4 Optical Fibre
489f0c8c-11a9-564a-a6ab-0bc5b7271966 | note | ○ Between Cabinet and Cameras --CAT6A U/UTP Cable in 25 mm conduit
0be7e87e-c44e-5dd2-a131-7b21ce6b9c02 | note | Standard / Specification - Drawing 0414
ff9fa0a2-7c64-54cc-90c3-bb0b336bb487 | note | Verifying Document - Photo/Visual Inspection
2616562c-852f-5f3f-9e38-2a0ebce68f1c | note | Frequency - Each installation
9cacd7e6-7251-5c77-b484-9fd9fbbb000e | note | Verification Activity: Activity - I
7d8e14b8-8758-5cd9-a9e2-59bfcf6db2dd | note | Verification Activity: By - PE/SE
a0083817-1556-4587-acc3-bf4dcc2bd12a | checkpoint | 2.2.3 - IP Addressing, Programming of PoE Network Switches
56b32c1c-09c3-56dd-be93-85d6eb215218 | note | Acceptance / Conformance Criteria - Liaison with TCC for IP addressing and Programming of PoE Network switches.
9dd5f8f8-ce29-5a1a-a5ee-79b9e68105ef | note | Standard / Specification - PS 23.1.4 m)
81954df5-8d89-530c-b908-be6fdd519b89 | note | Verifying Document - Comms Record
997144eb-5020-5f87-8525-46f4aabf0125 | note | Frequency - Prior Installation
965544b8-efa2-5d8c-a9c0-c6994d86b8a3 | note | Verification Activity: Activity - H
615c918c-ae00-5a8c-8f2f-a3107647a918 | note | Verification Activity: By - PE
1c6c7e48-9f0c-41d0-ae0a-ef19665437cf | section | SECTION 3 – POST CONSTRUCTION ACTIVITY
3395a398-1b3b-482d-98d2-b84a394a410d | checkpoint | 3.1 - As-Built
133bd4b6-592f-5f8e-a872-54b1cb97c3e3 | note | Acceptance / Conformance Criteria - As-built drawings with
8716f3f2-b678-5a9b-b753-7f220d16aa3a | note | 1) ducting routes.
a00c56b3-b05a-5b28-8b7d-ca1a059ac869 | note | 2) control groups,
860a8347-b9ae-5dbd-8170-c336bdae131e | note | 3) scene settings
50ebbd75-e5dd-5504-a5ea-f0d8bce34130 | note | 4) override sequences,
87918af6-6519-514f-b088-7a1966f723b5 | note | 5) luminaire and pole locations,
960cb8e3-264b-5bec-9cfa-665d23092dc5 | note | 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes.
4bbb1e13-3187-5ec6-9f47-f1cb67a48f6d | note | 7) All changes to design to be noted, highlighted or markup clearly.
c5623a26-c482-5674-ae71-8d5f788e534a | note | Standard / Specification - PS 23.1.5 h) & 23.8.5 a)-b)
314fa020-1d07-5ac4-af19-b4dd04398324 | note | Verifying Document - As-built Drawing/Survey Data
ef4b166a-565a-548d-9129-8f3bb8846e4f | note | Frequency - Post construction
4e4f93c8-90a4-53c8-bdd8-79714ae1260a | note | Verification Activity: Activity - H
ab46085a-fcb0-5bbf-ade5-2e9d98651b17 | note | Verification Activity: By - PE/ENG
bd2ce875-61cb-4fa7-9c1a-a350f3f9b229 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
b7037b27-9ce4-5152-b99e-a9019666911c | textbox | Contractor's Rep Name:
854f02ff-b1ee-5f1a-add8-864a53e6c886 | textbox | Engineer's Rep. Name:
e5c8bd08-2378-566e-9f4d-e3fa744291c3 | date | Date:
9ebc3636-61b3-4bc2-b2ff-198d7a2e8aa7 | signoff | Add Signature
71a08376-c4f1-4923-886a-bdee89cd1615 | checklist | DN1210-027-004 - ITP Streetlighting - Commission and Post Construction Rev 0 | itp | DN1210-027-004 - ITP Streetlighting - Commission and Post Construction
23106e99-6141-4aa2-bb2e-336fe9a249dc | section | SECTION 1 – Commissioning and Testing
aa0106d2-ba61-4a3e-adf9-edc5d8bcd42d | checkpoint | 1.1.1 - Commissioning - Luminaires (WK RAB)
8428ac16-6430-5146-88a3-80c4c349ea87 | note | Acceptance / Conformance Criteria - Carry out full commissioning of the Light Controls as detailed on the drawings.
16611aed-b1da-5526-af65-44c96deadf1c | note | Standard / Specification - PS 23.1.5 f) -g)
6d3ce8ca-222d-54d9-8473-bde375970bdd | note | Verifying Document - Photo/Visual Inspection and Commissioning Records
7c6a7b40-59ae-51f5-9e46-e111a75b4069 | note | Frequency - Each Commissioning
f18ffb76-5b22-5c49-8a35-b4223d06833a | note | Verification Activity: Activity - I
5243d129-f18b-5860-a18a-b44987930637 | note | Verification Activity: By - ENG
46ed1f36-1633-4494-b449-92ec398c42d7 | checkpoint | 1.1.2 - Commissioning - Luminaires (TCC RAB)
a8d15b5d-6699-50ad-b113-d963f38ec602 | note | Acceptance / Conformance Criteria - Carry out full commissioning of the Light Controls as detailed on the drawings.
54837bc2-637b-52e3-8eab-450ced94b1ad | note | ○ Also record "Benchmark" energy meter reading from the lighting switchboards of all levels to demonstrate power consumption when ALL luminaires are running at 100%.
f6fed076-4c87-556d-9ef9-fb501bbb979f | note | Standard / Specification - PS 23.1.5 g) & h)
d4c36518-c9f0-56d2-8780-5be7b842d685 | note | Verifying Document - Photo/Visual Inspection and Commissioning Records
32c480d0-99b2-5685-9fd9-d58bcea38655 | note | Frequency - Each Commissioning
ee790ede-9680-524d-8408-9f98f9627a79 | note | Verification Activity: Activity - I
1ff8bf28-2ad7-542c-a97a-5ea5660077b5 | note | Verification Activity: By - ENG
08b301e2-b52c-47f8-9b01-64916865693f | checkpoint | 1.1.3 - Commissioning - Luminaires Underpass
e7e61091-532b-5bff-afce-8a0fefcac5c1 | note | Acceptance / Conformance Criteria - ON/OFF Operation + Dimming Function etc. on each Lighting Circuit under direction of Energy Light NZ utilising Calibrated Lux Meter.
7c22aa7c-4980-5040-86de-84f9cebf788d | note | Standard / Specification - PS 23.1.3 e); 23.1.5 g) & Drawing
ecdefd89-8bf6-51e3-b908-00207c443b88 | note | Verifying Document - Photo/Visual Inspection and Commissioning Records
47782710-ca43-50e1-91ff-c0bcc4cefd3d | note | Frequency - Each Commissioning
658f2694-7216-5b15-a799-fb3d06a06f4d | note | Verification Activity: Activity - I
02bf9827-1563-5ab8-860f-731d5c612090 | note | Verification Activity: By - ENG
b331e5e1-e579-4678-b0a6-92900a5e4409 | checkpoint | 1.2.1 - Cameras
a21da11c-3215-50ab-9a62-19aed7cc9c1e | note | Acceptance / Conformance Criteria - Testing Optic fibre fromTCC Montrose Cabinet to underpass CCTV Cabinet;
58114293-0e63-592d-b3d1-4f8590adfe46 | note | ○ Testing CAT6A U/UTP Cabling from CCTV Cabinet to each CCTV Camera.
b57424d2-a1bd-55c5-af27-4f7ff5844ebd | note | ○ Liaison with TCC for Commissioning and Testing including camera adjustment to achieve the desired FOV.
e83d0ab4-6dab-519c-a6fc-b527125550ba | note | Standard / Specification - PS 23.1.4 m)
245067f9-3c30-57e4-adf9-580ad3125528 | note | Verifying Document - Testing/Commissioning Record
95505b69-d0c8-5e2c-afeb-3c75bc2fe22b | note | Frequency - Each Testing/Commissioning
7c459355-178d-5f93-af5b-3f221d964407 | note | Verification Activity: Activity - H
c6757eaa-cd25-5778-8b77-51158790f864 | note | Verification Activity: By - PE
aaee6909-ecb4-48d1-9ca9-0221115c73a6 | section | SECTION 2 – POST CONSTRUCTION ACTIVITY
945d217d-c00e-4679-b91a-3a7cb48e4749 | checkpoint | 2.1 - Electrical Certificate of Compliance (CoC) & Electrical Safety Certificate (ESC)
fd7cb60c-40d0-5436-b8b6-a6f2c700ecbe | note | Acceptance / Conformance Criteria - Obtain final certification of the installed systems by an independent electrical inspector approved by the Electricity Workers Registration Board.
f54454ce-a7c5-5531-b379-3ec19e568fee | note | Standard / Specification - PS 23.1.5 p)
ef77920b-aae7-5731-87f6-8385dee0a34e | note | Verifying Document - CoC and ESC
4a592b71-8dd0-55b3-b609-0b8f2220a052 | note | Frequency - Post commissioning
1aeb0efc-28d0-5357-a0dc-ed3fde8b4459 | note | Verification Activity: Activity - R
5daa58ec-5057-5879-a438-a1f61514c144 | note | Verification Activity: By - PE
a0146ede-0d96-4c5f-9540-31d8d3b26b16 | checkpoint | 2.2 - As-Built
35f56536-c984-5986-a81d-ca85ad4ee174 | note | Acceptance / Conformance Criteria - As-built drawings with
183ee0d8-80c4-5eb6-996f-6137d851d05a | note | 1) ducting routes.
03913006-55c6-55ef-ac19-cfb526bce9d0 | note | 2) control groups,
fbec7588-a78f-5c4f-a680-8d76eb0a84bf | note | 3) scene settings
8d9376c9-fbc7-52eb-9493-7e0b32cc2d75 | note | 4) override sequences,
a6848f2e-92fb-5e44-a60d-cb64d00c2ef3 | note | 5) luminaire and pole locations,
6419ea4e-dbce-53fa-8315-0efe56b5f6d0 | note | 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes.
1deb3e53-cf13-523b-a36d-93a814c7e597 | note | 7) All changes to design to be noted, highlighted or markup clearly.
746db38a-5bad-5d7d-96b1-77b5ab93ca39 | note | Standard / Specification - PS 23.1.5 h) & 23.8.5 a)-b)
bb67dfd2-51fb-5ac9-8e0f-ee33909cdd0c | note | Verifying Document - As-built Drawing/Survey Data
63811469-df17-59ae-9c3e-74036d214c30 | note | Frequency - Post construction
79e7c2dc-cd36-55f1-b7f1-a8d53d9f475f | note | Verification Activity: Activity - HP
881671d3-a022-53b1-a427-eea5a1eafc94 | note | Verification Activity: By - PE/ENG
8e51f2f5-5cd9-4fa6-8d15-8f5cbb85530e | signoff | AUTHORITY HOLDPOINT
af3a0527-f28e-4ee2-96aa-0c3b95dfb069 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
453ed43e-a111-5c36-9793-8924d3103697 | textbox | Contractor's Rep Name:
52a40e73-4326-560f-8ec5-4050a0e74f54 | textbox | Engineer's Rep. Name:
45070d55-ada5-59d1-9589-609e774442bc | date | Date:
0398820a-2def-4fe6-bf51-059bcfb5829a | signoff | Add Signature
e82a1e0e-6b6c-47cd-8acd-35b7da870bd4 | checklist | DN1210-028 ITP Pavement Type 5 Rev 2 | itp | DN1210-028 ITP Pavement Type 5
e230adfa-d435-4643-b8ab-e4f0c182ad2e | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
4c851fcf-5164-4c85-802c-7d1c6927b012 | checkpoint | 1.1.1 - Geogrid
336ba9ed-3189-573a-bacc-2fc5c23bd750 | note | Detail - The Contractor shall submit the full details of the geogrid they propose to use to the Engineer for approval prior to installation.
eab57fad-37e4-517c-9dcd-2ac923314346 | note | Acceptance / Conformance Criteria - Engineers Approval
49157f89-34d3-5c40-ad3d-75659b17de46 | note | Standard / Specification - PS 20.5.2, PS 16.5.13
5156f74a-881b-5a4e-9c34-e2a8f1bb9a9c | note | Verifying Document - Data Sheets and Approval
54c55482-c9e1-5c8b-ace2-780dfc8aec6b | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
dc69a006-3962-539d-8b5e-52c69f2e302a | note | Verification Activity: Activity - HP
18fb85c0-c52d-5879-932e-ad77a1a99767 | note | Verification Activity: By - ENG
a9a12b28-72b4-40aa-b571-8e3bc9138164 | signoff | AUTHORITY HOLDPOINT
c6889cc9-570c-4770-a484-af7748978204 | checkpoint | 1.1.2 - Geotextile Fabric
c2245fef-46e2-5f4f-8bd5-005a5b756c5e | note | Detail - The Contractor shall submit the full details of the geotextile fabric they propose to use to the Engineer for approval prior to installation.
98a41817-28b8-50d7-ae06-0fb82626f6a7 | note | Acceptance / Conformance Criteria - Engineers Approval
f76fade0-9a13-57fa-8ec6-4434815a6b32 | note | Standard / Specification - PS 20.5.2, PS 16.5.14
e452f2aa-d051-5fdb-88dc-ed3f4caeea30 | note | Verifying Document - Data Sheets and Approval
07a2c415-e088-5bac-81f3-33aee0563a9d | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
b56c305e-1399-5c28-9aa5-cd3c496011b2 | note | Verification Activity: Activity - HP
74b04655-7d19-5598-b8bc-bec449938eeb | note | Verification Activity: By - ENG
6ca7c749-7ad0-4aff-99b9-2dc1504ee4d5 | signoff | AUTHORITY HOLDPOINT
705cbee1-5da5-433a-bef7-550bb6715b0b | checkpoint | 1.2.1 - Crushing Resistance
a6893831-a21d-5fa4-a136-285d1da4c4f3 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
9da06033-01f6-5347-9bc1-09b868cdfe09 | note | Acceptance / Conformance Criteria - >100KN
fac78bb8-b8e4-5527-bc07-06617579ff81 | note | Standard / Specification - Appendix XVIII
a6342979-9c3a-5697-af8b-4cbe9f925343 | note | Verifying Document - IANZ Accredited Report
6e5d8363-1f4c-5cd8-bd5e-352783d61aa6 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
224e1c06-82c7-59a8-b3d2-097491670b9c | note | ○ Results to Engineer 2 wks before importing
6eed00ff-4b58-58d8-be8b-815e73f783b7 | note | Verification Activity: Activity - HP
0328c571-7195-5a4d-b8b6-128ad584dd4e | note | Verification Activity: By - ENG
ae0b9558-335d-4e19-842d-679596bec709 | signoff | AUTHORITY HOLDPOINT
319fa415-207c-4095-8b91-2073f2c26ba4 | checkpoint | 1.2.2 - Particle Size Distribution
e4dd1e60-ac04-5148-a151-d9ea3a7d67f3 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
26112aa8-55a3-58e8-9daa-6eac87f76e7b | note | Acceptance / Conformance Criteria - Max Particle Size 53mm
962c96c7-4a88-5618-b8d1-2fc112cb0e99 | note | ○ Max 10% passing 13.2mm sieve
41ac4789-6c98-5a59-af27-a544218dec9a | note | Standard / Specification - Appendix XVIII
2bff8fcc-2436-51c2-a78c-287f3bce8da6 | note | Verifying Document - IANZ Accredited Report
d5b1e52a-3658-51e4-97c6-68af5dda798d | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3
788dcb74-a3c9-5efe-8b5d-594243763afc | note | ○ Results to Engineer 2wks before importing
3445a18a-35b3-5cea-9352-8d37e55eab04 | note | Verification Activity: Activity - HP
ae9fea48-6ed8-56cc-9519-6e595428b968 | note | Verification Activity: By - ENG
955b3f38-9681-447d-bacd-eb36e5cf1329 | signoff | AUTHORITY HOLDPOINT
302a30bd-91e2-40f6-a5dd-8b9908ba9490 | checkpoint | 1.2.3 - Weathering Resistance
b5b918d9-91c4-560c-a79d-df089fddbace | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
9c6d0cbb-09cb-59b9-9a96-28531534640e | note | Acceptance / Conformance Criteria - CA or better
04a9dde3-4c55-5b61-b88a-a030aa5ddc25 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
bb2f0ddd-979a-521b-8f38-f912130f0dfc | note | Verifying Document - IANZ Accredited Report
dfd15723-44ea-5e0b-b9f4-0f5444f493c1 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
d4deea57-d940-5a81-a436-f1cedf5b71b8 | note | ○ Results to Engineer 2 wks before importing
c6c04fbb-f8af-508a-b619-e4f8a7777d2c | note | Verification Activity: Activity - HP
ab3eceb8-e2a8-55c7-8264-a90f99cb78a0 | note | Verification Activity: By - ENG
5da8bcdb-192c-4e62-b84e-764977656084 | signoff | AUTHORITY HOLDPOINT
850dfeda-3637-4105-8952-97e215200e0e | checkpoint | 1.3.1 - Crushing Resistance
0279a956-0469-5072-9137-5d99265d8fb1 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
c45db7d7-b7db-5bc9-8f81-4d8bf63d0234 | note | Acceptance / Conformance Criteria - >100KN
dc5a5762-4b6f-5853-8b09-77de8bed8859 | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
5286c518-4cef-5051-84e0-89d3cdae0866 | note | Verifying Document - IANZ Accredited Report
52dc2363-5183-5caf-b1c5-7c4012968a26 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
fab33388-c3d8-5591-96f8-dbba6d4e2a77 | note | ○ Results to Engineer 2 wks before importing
138d99f5-1c32-5d8d-8b9e-f5b3e1b582f1 | note | Verification Activity: Activity - HP
496fc70d-c708-54a3-8044-051609c65604 | note | Verification Activity: By - ENG
cc9fa1f1-144d-4051-810a-9228a6dc9e61 | signoff | AUTHORITY HOLDPOINT
ba0f85fa-576c-4323-a580-f3257ea832c3 | checkpoint | 1.3.2 - Soaked CBR
96bf1d96-b555-5a0f-886a-d427ca2712eb | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
411a3d69-7fd8-5cf1-be73-568c6174f574 | note | Acceptance / Conformance Criteria - >60%
82c3a599-60b3-5afc-8987-57346ce42f88 | note | Standard / Specification - NZS4407:2015 Test 3.10, IT-4.7.1
809842bd-96ab-5880-9e1a-dda9997ec88d | note | Verifying Document - IANZ Accredited Report
c993ab84-3b7f-5875-bc56-b97c511afedd | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
02172d24-e024-514e-814b-de86c28255d3 | note | ○ Results to Engineer 2 wks before importing
53aa4f81-5f5b-55d4-9b0a-ea554d8c5816 | note | Verification Activity: Activity - HP
6d59e6ba-578d-5f45-958f-533b511903e4 | note | Verification Activity: By - ENG
3f26c264-fa8b-4a1f-82a4-9f4500336c74 | signoff | AUTHORITY HOLDPOINT
2f5afed7-3592-45d7-b192-4ca2d0052cea | checkpoint | 1.3.3 - Weathering Resistance
8ac2c049-9b22-54bd-8215-19afb28c741a | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
70531716-c4c7-5aaf-8151-2cd9bd296ce9 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, CA or CB
fe3bdc97-c4b6-5f65-b007-bb8351452469 | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
79adf7f0-d212-5760-a2fb-a505c7714e3a | note | Verifying Document - IANZ Accredited Report
b85421ee-4000-55f7-843e-98d41ae1a648 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
04f87804-cff3-5a18-a322-c3a8835c3f7c | note | ○ Results to Engineer 2 wks before importing
9c5e8ae0-e29f-5710-97aa-e6fbaf41add1 | note | Verification Activity: Activity - HP
deb6d883-e31a-5d16-9074-88088b54a006 | note | Verification Activity: By - ENG
2989476a-99d8-413a-99ca-7c4588774337 | signoff | AUTHORITY HOLDPOINT
9342458d-77b7-43ae-a264-a6c3bc534f91 | checkpoint | 1.4.1 - Particle Size Distribution
913d4d04-be34-593e-9449-9a4e4d2b07e0 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
36e97cc3-383c-55f7-8021-bb44e9fa9ff1 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
66ce5b43-e527-56a5-9338-6d02a5f0d832 | note | 63.0mm ¦¦ 100% passing
8c769ed4-2533-5801-b48b-92591665721d | note | 37.5mm ¦¦ 68-90% passing
c87bbe0e-06c5-52d4-968f-08058dc8bb99 | note | 19.0mm ¦¦ 42-76% passing
57cdc55b-828d-5a7c-94e3-77975047d2e3 | note | 9.5mm ¦¦ 26-58% passing
cf46dabb-6c43-5ba4-9c20-95f20bd52d71 | note | 4.75mm ¦¦ 16-44% passing
f2a48e10-eb0b-5dbe-b282-baf977829b37 | note | 2.36mm ¦¦ 10-33% passing
d036d343-e037-51e0-a618-ce68e4448d22 | note | 1.18mm ¦¦ 6-24% passing
d330109d-a923-5dc2-a7ce-2b3a60facf66 | note | 0.425mm ¦¦ 3-14% passing
e623e3fe-9505-52bb-bdd0-25226ce71dea | note | 0.075mm ¦¦ 1-6% passing
0677343e-028f-59f3-9b55-22fdf455a865 | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
b38c0b3e-0ed4-5713-93fc-3e3472d79a18 | note | Verifying Document - IANZ Accredited Report
ed977273-1ded-54ac-b621-4425c74b94b5 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
e570ad46-7015-52b7-b5b9-feacc82adfc2 | note | ○ 0-400 - 2 tests
cb310c55-849e-50ff-a024-55249c0be125 | note | ○ 400-1,500 - 3 tests
0e79cb6d-be12-5cbf-a8ff-80d86de51e0a | note | ○ 1,500-4,000 - 4 tests
bd88e5d8-cd6e-5408-ad87-19d1d6ead8f4 | note | ○ >4,000 - 1 test for each additional 1,000m3
8dc731e5-230e-5012-84eb-b7ab81889b9a | note | – Results to Engineer 2 wks before importing
f0a08848-5832-57a5-966a-fe8eecf7352c | note | Verification Activity: Activity - HP
880d8829-86fc-56fb-8cb6-b983aef27066 | note | Verification Activity: By - ENG
9bb758d2-526b-46cc-aa91-9f2a32b6dbd5 | signoff | AUTHORITY HOLDPOINT
e716a136-ed83-41b0-bd9c-8615cafc139f | checkpoint | 1.4.2 - Maximum Dry Density and Optimum Water Content
6b3016c6-9aad-5154-a851-f43645fff76c | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
92f6b6ea-26c9-5085-b94f-38392e5fa246 | note | Acceptance / Conformance Criteria - Report Value Only
ee5cf5b1-56b3-5abb-8bc6-9c2b04ce0a7f | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
ca386bda-c565-58aa-8e90-ad8f3e40e15a | note | Verifying Document - IANZ Accredited Report
f72a127e-fc3f-573c-ac22-c6e617b3d666 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
dd26ff9e-a7e4-5307-b94f-e9b387c7c6a7 | note | ○ Results to Engineer 2 wks before importing
a0d6aa16-76bf-5aa8-a15b-7baef652a06e | note | Verification Activity: Activity - HP
e8d71c13-2e90-529c-8875-4382e486f423 | note | Verification Activity: By - ENG
f43a95ea-c73b-41a4-b98d-42842d006cf3 | signoff | AUTHORITY HOLDPOINT
0c32b14a-b34f-4cfb-afce-0f5aa995784d | checkpoint | 1.4.3 - Plasticity Index
c9d215f7-e90e-5a02-8a8b-b45e273ef03f | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
266bc1f8-0ada-5cc5-8791-13c045c3fdd5 | note | ○ NZS4407:2015, Test 3.3 Plastic Limit
882f8122-2081-5441-9aa4-4cf23ed22eae | note | ○ NZS4407:2015, Test 3.4 Plasticity Index
031e8c80-60f1-59d9-b586-85ea817f32f7 | note | Acceptance / Conformance Criteria - <8
74e2d39f-4c67-5d36-bda8-5f7670fc6bd8 | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
5835feb4-a6f9-5563-8a90-6dd51d3b2250 | note | Verifying Document - IANZ Accredited Report
6adbde6e-ce5b-5f5d-a0d4-625948abd336 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
5d2752f3-88c0-51ea-b421-e9ab6974750d | note | ○ Results to Engineer 2 wks before importing
b025b5ab-3604-5525-947f-db1de9241844 | note | Verification Activity: Activity - HP
ceb065c2-cccf-5fcd-82dd-356dac949672 | note | Verification Activity: By - ENG
e8d4c144-c682-4770-9377-6fe35f1dd77f | signoff | AUTHORITY HOLDPOINT
07e028bc-e7e1-4cf1-b9f9-1f8225a6663b | checkpoint | 1.4.4 - Sand Equivalent
ef4f7dd3-1fb0-5371-a776-24b550e0a137 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
5e5a1e33-85d3-52c7-a331-af0bfac0dadb | note | Acceptance / Conformance Criteria - >25
433c81bb-e1f3-566d-afc0-55243fb2c1f9 | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
9d9d9659-e428-50ff-9f86-09b86cc5e699 | note | Verifying Document - IANZ Accredited Report
792790ce-b232-5b72-be67-1e62cde3f3d4 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
62c415b7-458c-560a-9b29-2c23f0f36fe8 | note | ○ Results to Engineer 2 wks before importing
f94eb75f-5b49-5dcb-9b56-5eb43278716c | note | Verification Activity: Activity - HP
562e60fa-c769-5132-b5b7-1e2c8fcac41b | note | Verification Activity: By - ENG
a0d5eb00-d424-4cce-a8f4-c822d18e5d3d | signoff | AUTHORITY HOLDPOINT
10d10a2e-9a4e-493c-892f-18547b2007b8 | checkpoint | 1.5.1 - Crushing Resistance
100ac725-662d-5223-bff2-16ba1282e4cd | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
28f19aad-ad90-534c-80d1-88fe633c3671 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
9c83e184-ca23-570a-ba59-51dacab34267 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
08625e76-e2b5-5a95-8238-e455c90ee8ef | note | Verifying Document - IANZ Accredited Report
753d970d-3708-5c6d-b35b-acc779709bab | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
ee112722-fe8f-5423-ad4b-e32b83348316 | note | ○ Results to Engineer 2 wks before importing
a5dbbbfe-d237-5041-919f-20afec4be0be | note | Verification Activity: Activity - HP
2c2fea67-3edf-5236-96d9-c8221b622083 | note | Verification Activity: By - ENG
9d0f97cc-70ca-45fd-9388-17fb0eb14a56 | signoff | AUTHORITY HOLDPOINT
d4dddad3-c0fa-4d8d-9455-febc6796d6a5 | checkpoint | 1.5.2 - Soaked CBR
f2746106-187d-5370-b68c-4446620a840d | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
4245c60a-518d-5f9f-8079-b0d7f70640f0 | note | Acceptance / Conformance Criteria - ≥ 60%
7a2ee47a-fe9a-5459-866f-2471cca83192 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
fa2597ed-194f-5c8b-8565-43105b41652d | note | Verifying Document - IANZ Accredited Report
b179e1aa-6405-5c59-ae14-34d8a92ecd9f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
903b464e-af79-5266-92b3-e2b3af2f342c | note | ○ Results to Engineer 2 wks before importing
5b48e244-02c5-5542-904a-bf1f0a1e6ab2 | note | Verification Activity: Activity - HP
4d230c20-62da-51d6-a5e4-366218f259a9 | note | Verification Activity: By - ENG
47ce82fd-c7da-4fac-8a01-32c61faac2ef | signoff | AUTHORITY HOLDPOINT
05ddd0dd-fdfe-4887-9133-b6591c1dd020 | checkpoint | 1.5.3 - Weathering Resistance
211c67d3-4c93-51cc-9f8a-62a1c9338ec0 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
98722dd1-7a86-5cc2-be56-a078b8a34c39 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
41b30600-bbb2-58e3-8054-082fab9d8e3c | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
d3b27197-e9e5-5249-9266-918c09ead963 | note | Verifying Document - IANZ Accredited Report
f2f6cdc7-cd82-5125-a432-c75877849d5c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
8a5f0680-35e3-5a73-b727-98105e358ed6 | note | ○ Results to Engineer 2 wks before importing
642b6121-42e2-52de-930d-11dd4d9d2b3e | note | Verification Activity: Activity - HP
aa3d3cbb-171b-5f04-82fc-d0622017c31c | note | Verification Activity: By - ENG
88ac0847-31c4-4876-a181-f6e976ad926e | signoff | AUTHORITY HOLDPOINT
a86bad5e-2deb-4256-9dfb-abbbae4869fa | checkpoint | 1.6.1 - Particle Size Distribution
f68e0509-005d-5167-9734-52439d1c72bf | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
fe6cbcea-43b2-5604-bd3d-753da0a52a22 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
2902b786-eb3d-5917-8a7e-c9c0e2ed1aca | note | 63.0mm ¦¦ 100% passing
dafd505d-2a41-5c33-996e-9dd4adb214f8 | note | 37.5mm ¦¦ 55-85% passing
60cb7209-59f8-51cb-aa3a-60155aacaff6 | note | 19.0mm ¦¦ 33-65% passing
509f8124-fd7d-5bff-b217-676e2ea10ecf | note | 9.5mm ¦¦ 20-50% passing
dbcd20f2-1419-54d6-8b19-5cd85f9c8f36 | note | 4.75mm ¦¦ 10-36% passing
e0164a27-e6f1-51a0-9d8d-c58b257697d7 | note | 2.36mm ¦¦ 5-27% passing
f24e1b9e-94f5-56e4-8148-31db2ad5edcb | note | 1.18mm ¦¦ 2-20% passing
5c2c7364-0a68-5fff-abed-9d5db228c265 | note | 0.425mm ¦¦ 1-13% passing
f4626395-53e0-5e57-8548-48ca84f3c8fa | note | 0.075mm ¦¦ 6% max passing
7475f022-4547-5246-8175-f25cb81e6f41 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
74dbce0f-438b-57b8-8e83-465838f221d3 | note | Verifying Document - IANZ Accredited Report
3314ff60-f48b-5c96-ab6a-bfb5922ecdfb | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
1e81ceb7-6850-5e13-b801-b351b78935ba | note | ○ 0-400 - 2 tests
498adebf-4758-5449-b3c9-8110dab1aa15 | note | ○ 400-1,500 - 3 tests
9f29e3c3-0e34-5c98-8701-77ace048f34d | note | ○ 1,500-4,000 - 4 tests
f9979b20-c870-5dab-b8e8-254c4b677164 | note | ○ >4,000 - 1 test for each additional 1,000m3
ac178340-39bd-5631-805b-d893c5d999f9 | note | – Results to Engineer 2 wks before importing
9062697d-34ae-56e0-a830-e3a7c77c1095 | note | Verification Activity: Activity - HP
7d45a0b8-8e07-5ce8-82f5-087a0f28fd8c | note | Verification Activity: By - ENG
cfd0f743-dd05-4705-8530-335f3bd10ad7 | signoff | AUTHORITY HOLDPOINT
b13a28c2-e6b8-45b9-a07b-01e8ffc424c9 | checkpoint | 1.6.2 - Shape Control
659e7739-1739-5821-a4ce-c337f13e4f3e | note | Detail - Tolerance allowed from approved grading curve (%)
1afdedb8-fe89-549d-b4c7-439b96a02581 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
716b2897-8dd6-5c9c-aae7-ccc220766499 | note | 37.5 – 9.5 ¦¦ 34-50%
b1858afc-f7bd-5637-85c2-89002967591d | note | 19.0 – 4.75 ¦¦ 18-40%
d13cdc4a-2457-56a8-b92c-d21ea74e9259 | note | 9.5 – 2.36 ¦¦ 12-32%
78543c2a-ac3f-5091-b432-1b937ac9377c | note | 4.75 – 1.18 ¦¦ 6-24%
6da80a4e-2543-5cf8-9a2f-31540b9c1dee | note | 2.36 – 0.6 ¦¦ 2-20%
74ecbfa2-5b6d-5814-888c-8522f017ed89 | note | 1.18 – 0.3 ¦¦ 0-15%
ba4451e2-26e3-5acf-83ae-4122f483830e | note | 0.6 – 0.15 ¦¦ 0-12%
bdbe6536-9f9c-5632-9768-96b712a29d51 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
9edd8831-4d61-556d-8e6c-268085ac8246 | note | Verifying Document - IANZ Accredited Report
2d2cc45b-a25a-57e6-9b31-7b3639855284 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
024b877b-0f8a-56c6-85c5-984fa278b804 | note | ○ 0-400 - 2 tests
859593f5-bd2b-5727-9795-6af7e6ec5cd3 | note | ○ 400-1,500 - 3 tests
981c2f6a-a9f3-529f-af23-c29d055f6821 | note | ○ 1,500-4,000 - 4 tests
296752e0-0e42-592a-8cd8-dd78e2bff2de | note | ○ >4,000 - 1 test for each additional 1,000m3
86b42248-6510-5f8d-8ed8-7f343c7ec0f5 | note | – Results to Engineer 2 wks before importing
03682961-2c04-5685-9633-98e2049deb6c | note | Verification Activity: Activity - HP
7fed3be5-cd80-5db8-a698-d168693f3ba2 | note | Verification Activity: By - ENG
93c9222d-15e1-4120-b7e4-84284c33a070 | signoff | AUTHORITY HOLDPOINT
c6ce0c90-d92e-42cb-b0b8-e5e22ba48c78 | checkpoint | 1.6.3 - Sand Equivalent
fcda5e2e-0059-57af-a654-6a4b7ab81b13 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
c431a3a3-991c-59da-9dac-66a72f08c956 | note | Acceptance / Conformance Criteria - ≥ 30
7ab2b2e4-0814-54c5-8f63-be63baee2c84 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
13a3ec96-7782-5b67-9186-05cfe5d4cbfc | note | Verifying Document - IANZ Accredited Report
3735038e-1a99-5a8e-81ce-cf21cc7523dd | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
3673cef9-a72e-552d-a1fd-d1bd3416ca4e | note | ○ 0-400 - 2 tests
0d0cf124-fa50-5ed6-914e-066531eac649 | note | ○ 400-1,500 - 3 tests
0c28ab68-66b6-54b1-a013-7976b176553e | note | ○ 1,500-4,000 - 4 tests
4805aafd-45b7-55ce-9214-60205189ce4c | note | ○ >4,000 - 1 test for each additional 1,000m3
71d70278-ed77-559e-8825-53a69ab87ec0 | note | – Results to Engineer 2 wks before importing
381e1278-1082-5048-8584-71037e806d98 | note | Verification Activity: Activity - HP
37e550e9-f458-5908-beaf-44d06e1121d4 | note | Verification Activity: By - ENG
92d99614-66ed-4287-a021-1e81fb026b0a | signoff | AUTHORITY HOLDPOINT
dc591e55-2597-4d08-bb8f-21a762c9a9c0 | checkpoint | 1.6.4 - Cone Penetrometer Limit
7ec99c43-9bc1-5ab2-9b7f-f68e2c7bca43 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
e2f6f541-4a28-57c0-af64-3954b419bb50 | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 25
ea7b9989-bb6d-5455-aab8-b2aa0208e52d | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
948d22cd-4793-5f4d-bd4f-57b4eb206162 | note | Verifying Document - IANZ Accredited Report
28a70497-ed90-507e-8da3-66ada2d5e32f | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
9ef0c4e9-ad74-52bd-ab66-136e9b5defe0 | note | ○ 0-400 - 2 tests
9fedf64b-8623-5f54-8404-0968be26ddb8 | note | ○ 400-1,500 - 3 tests
83f99519-cd4b-57da-be02-76e6530901fb | note | ○ 1,500-4,000 - 4 tests
fce6ed45-082a-5b36-af3a-27c22ed340bd | note | ○ >4,000 - 1 test for each additional 1,000m3
93f8eee0-8637-5c92-8def-20bc30fd9187 | note | – Results to Engineer 2 wks before importing
c9cb5c19-de4c-5aa2-9bc6-ec9b627a8ea9 | note | Verification Activity: Activity - HP
4adae0da-7fd7-50e0-89e9-f75003883a35 | note | Verification Activity: By - ENG
80d75a23-e0e8-4635-8d48-2181498a3be1 | signoff | AUTHORITY HOLDPOINT
0d0c38d7-5ab9-40f2-b855-79aeb4c3c2b4 | checkpoint | 1.6.5 - Plasticity Index
80467335-8bc4-5ea3-8f05-486b764ce4c5 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
5fca8321-3338-5522-a821-529cc10e49ba | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
070698ed-f99b-5629-bfef-3bd5aa4f75a4 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
e817796a-3d71-52af-9e3c-8592fea28174 | note | Verifying Document - IANZ Accredited Report
8e912c14-d8f8-5c01-85a7-3d09935e245c | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
45671849-4fcd-5b3a-a5bd-852df648fe3a | note | ○ 0-400 - 2 tests
d0e3508e-1bf2-516d-8ffd-953f5d730ce2 | note | ○ 400-1,500 - 3 tests
6380d7eb-2ec5-5201-a818-1f6933e3e7df | note | ○ 1,500-4,000 - 4 tests
8c8fdbb5-4426-51c5-833e-7dcd924c3e92 | note | ○ >4,000 - 1 test for each additional 1,000m3
acbd4953-1923-53ac-9e89-c285e76e6ae2 | note | – Results to Engineer 2 wks before importing
109c6203-b646-53ef-b061-0a9df6bba530 | note | Verification Activity: Activity - HP
67e39763-4755-5854-b4be-822ec9736f6d | note | Verification Activity: By - ENG
52867599-0183-44fc-847a-94a785998c48 | signoff | AUTHORITY HOLDPOINT
210e44a1-cd9a-4525-aa4b-52f19390737e | checkpoint | 1.6.6 - Accelerated Weathering
b324322d-61f7-5935-b226-a47a51f5f0bc | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
b5593a1f-981a-586a-9b3a-84f30c06891f | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
72a96da1-b365-58bf-8378-56ae22c5bc52 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
ad4178ee-50f3-5fcf-be92-c9eea7c2f273 | note | Verifying Document - IANZ Accredited Report
bfd62b08-d2ac-5b3f-ae9e-bde2d07b636f | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
0bc0ac2c-fdfb-5afa-93ba-f51aafd12648 | note | ○ 0-400 - 2 tests
3170c1e5-5e0b-5b6a-92fd-f380dac49be6 | note | ○ 400-1,500 - 3 tests
3f44dc10-1124-5f28-a4ca-ebe80b7e38bd | note | ○ 1,500-4,000 - 4 tests
f5864cdd-e6fe-5998-a779-89610d4899e1 | note | ○ >4,000 - 1 test for each additional 1,000m3
b18c7f91-fe3c-57e0-a89e-99557fae28e9 | note | – Results to Engineer 2 wks before importing
4e215c1c-5438-5550-b477-af372acd6d71 | note | Verification Activity: Activity - HP
75e2cf3f-420b-5e37-8dfb-c466c18967d7 | note | Verification Activity: By - ENG
d72474fd-d394-4cff-b374-56efbcd1bcbc | signoff | AUTHORITY HOLDPOINT
3228785c-b93c-463b-b464-1fbf67ae924d | checkpoint | 1.6.7 - Maximum Dry Density and Optimum Water Content
2166d7d2-0cf7-5a94-9de2-f8bde7048efb | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
f2a321d0-e4b8-51e7-bd85-df859960cecf | note | Acceptance / Conformance Criteria - Report Value Only
96db7b59-b35a-50a3-9dc4-2c664256b06d | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
cf9c358a-b4b6-5b68-991b-e60ff17c07ef | note | Verifying Document - IANZ Accredited Report
564eab38-da7c-5b2a-8eae-135f15f53547 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
6f4fdb7d-ff68-5a4b-9370-73fa4afe3dba | note | ○ Results to Engineer 2 wks before importing
f1843c92-4973-59fe-9aa6-75af003c64f3 | note | Verification Activity: Activity - HP
a567922e-5c79-56b2-b7de-0c4aabca7850 | note | Verification Activity: By - ENG
8f70b105-3e6d-40d4-a330-a5243a953133 | signoff | AUTHORITY HOLDPOINT
2e408549-6755-41bd-9a86-5141669fdec1 | checkpoint | 1.7.1 - Crushing Resistance
90b10a10-f699-5a1e-ae9f-f2bbf335c00c | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
c3aaf88d-3ccc-5a0c-ae19-bbc346108e85 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
d606d056-0003-5d0e-a457-4c897341a5ff | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
cd9c6d6c-3e84-574e-ad5a-67ffcde308ea | note | Verifying Document - IANZ Accredited Report
d043c238-ecb1-51bc-9e2e-bfdcc33e1210 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
ca48e7e5-0511-534c-a807-b981f2a910d2 | note | ○ Results to Engineer 2 wks before importing
df2b6f12-7ebf-5799-ae82-5a09c78e932e | note | Verification Activity: Activity - HP
e9744f75-6196-5bfd-bde1-073b92f2e992 | note | Verification Activity: By - ENG
3b38f3e8-46d0-42d8-8cf3-e9f3633034ae | signoff | AUTHORITY HOLDPOINT
7981f53d-cf01-46dc-8b46-f3e9465c0180 | checkpoint | 1.7.2 - Soaked CBR
0757bff8-64d4-54ba-93c4-69de06c61d03 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
2e1c7e37-bc6e-53ec-a79e-4a71f84f7b6f | note | Acceptance / Conformance Criteria - ≥ 80%
e9a5c2fe-87b5-54d2-8f6f-639aa30c778c | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
950bfb7c-70a4-56df-be7b-f491ea042abe | note | Verifying Document - IANZ Accredited Report
c4a591d8-7de8-5e62-8f12-7c66cbbdd98c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
bf9b5e88-4ff6-52c3-be4c-0a94a29eb2c4 | note | ○ Results to Engineer 2 wks before importing
11c6c9f5-0dd6-50c3-b91f-34a2124916ef | note | Verification Activity: Activity - HP
3c06772a-70a8-5405-b9ed-3689e1dc4a09 | note | Verification Activity: By - ENG
19a6be2b-e2a8-49fe-8a93-4d8669a6cfd3 | signoff | AUTHORITY HOLDPOINT
b6471655-5cb7-476c-8a6a-2f2b48ad92c3 | checkpoint | 1.7.3 - Weathering Resistance
7b6205f4-125c-5348-9f18-cf2db9a4f569 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
d2e9f57c-7f57-57e3-be1e-6eec1f556b51 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
15bc977e-1319-5f03-9648-55b04a3a2f58 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
b4a1666f-0d4b-59f2-a786-3b6d96fa6841 | note | Verifying Document - IANZ Accredited Report
60697ee2-4121-5149-92ec-9002e16eb564 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
520e3623-1bb9-5351-bdc8-4ed9e7f98481 | note | ○ Results to Engineer 2 wks before importing
23000daa-fd2f-5467-95de-7fde44a26ea1 | note | Verification Activity: Activity - HP
f6f09b52-6fcc-5383-91f5-06d7ae2587b0 | note | Verification Activity: By - ENG
e2b5e8f0-62e1-404d-8e72-e6750bdfcac1 | signoff | AUTHORITY HOLDPOINT
621f139c-b066-4a78-bd18-79232f272187 | checkpoint | 1.8.1 - Particle Size Distribution
fb0e9928-6834-5fd4-90bf-a1a170288161 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
81788831-11d2-5fa0-945e-78a33b22f562 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
4dc0b81d-d22d-5cc8-9b98-6fd6f5d2de15 | note | 37.5mm ¦¦ 100% passing
cd7e6553-e0c9-5089-a95c-7d7846792c22 | note | 19.0mm ¦¦ 60-75% passing
4efaded8-4d72-5bdd-8e39-0723ada17e95 | note | 9.5mm ¦¦ 37-50% passing
1f2d0734-979e-5b4e-b495-fc679df1b3e5 | note | 4.75mm ¦¦ 20-35% passing
baf0a415-d02b-57a2-85ac-7f89ea37170b | note | 2.36mm ¦¦ 12-28% passing
0462a5cb-90e3-53af-bd39-77c5b5f3f8dc | note | 1.18mm ¦¦ 9-20% passing
1b4b4c75-0f17-5845-b937-f8bd918ad270 | note | 0.600mm ¦¦ 7-12% passing
20730bcf-80c1-5470-871f-b57d70b50a28 | note | 0.300mm ¦¦ 3-10% passing
c35269ed-f6f2-5a3c-9454-a50f415e6468 | note | 0.150mm ¦¦ 0-5% passing
4e4ca48b-3df7-5bba-86ef-9bf0c8e223a2 | note | 0.075mm ¦¦ 0-5% passing
0bdfdb6e-66ad-528e-b8a0-ac699fa971a1 | note | Standard / Specification - TCC-IDC IT-4.7.2
8e5a1051-0c10-52ba-b251-695af572f13a | note | Verifying Document - IANZ Accredited Report
33cb877f-5796-5eb4-be0c-93151a2d7be4 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
225a9b76-a626-5ec2-9db5-cb7d646290e7 | note | ○ 0-400 - 2 tests
4e60222c-577a-571d-b3ce-f11fe6b537da | note | ○ 400-1,500 - 3 tests
5d6751b3-1dd2-5b53-aeb6-127055ad4407 | note | ○ 1,500-4,000 - 4 tests
8c8eaaf8-5899-5e4d-87c5-c7035a159ea7 | note | ○ >4,000 - 1 test for each additional 1,000m3
bf06e8e5-4766-5d11-9de4-e23100f4e0e8 | note | – Results to Engineer 2 wks before importing
0f1e96aa-a0f8-545a-8026-0ec49c1a199c | note | Verification Activity: Activity - HP
4cc54cb1-bdcb-56fc-9fa1-259e59db77ee | note | Verification Activity: By - ENG
14fd2ff0-af95-4fbb-81d8-731dafed52e9 | signoff | AUTHORITY HOLDPOINT
7511e3f8-1f82-4d5b-9e3d-7233bf21c423 | checkpoint | 1.8.2 - Shape Control
de208439-5691-5644-8435-9efdf90f3236 | note | Detail - Tolerance allowed from approved grading curve (%)
e1e6ade3-c5ca-550c-9e85-cb7c8a5a1288 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
845ccdc4-0e81-54b7-aefe-59093cf2e17e | note | 37.5 – 9.5 ¦¦ 28-48%
4372fcd0-ddab-5c90-9ca1-073408cb5ec2 | note | 19.0 – 4.75 ¦¦ 14-34%
044fa588-2342-568a-8bef-99435783d71a | note | 9.5 – 2.36 ¦¦ 7-27%
f6f561dc-f5a2-522f-9887-0a991a91648f | note | 4.75 – 1.18 ¦¦ 6-22%
c8280773-9f6e-5000-a4ae-103f8e435ef6 | note | 2.36 – 0.6 ¦¦ 2-20%
b1b8f494-c5db-569c-8107-6945ff926683 | note | 1.18 – 0.3 ¦¦ 5-19%
73bbfb38-a0ba-539f-bcb5-657dba3c7f20 | note | 0.6 – 0.15 ¦¦ 2-14%
a8403498-8dab-5ee4-8451-eee98df19e0a | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
463b467d-ed82-5221-a40b-b893437c1f97 | note | Verifying Document - IANZ Accredited Report
b98c8e4c-be60-5480-a294-53b0e9abab9d | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
dc7d78d6-2234-50d5-b557-9c0b95d46601 | note | ○ 0-400 - 2 tests
3f09a4fe-2a9d-5a8a-9b84-dd6bf64741f2 | note | ○ 400-1,500 - 3 tests
2f10974a-0c2b-5206-8b4d-b60cfe8f5359 | note | ○ 1,500-4,000 - 4 tests
165d4876-7198-56d7-b175-f867dd125d40 | note | ○ >4,000 - 1 test for each additional 1,000m3
ee70b370-374d-5b9b-be83-430858df52f2 | note | – Results to Engineer 2 wks before importing
2031e863-c4e3-5ef9-b022-156cf733d573 | note | Verification Activity: Activity - HP
3c376ec4-64fd-58dc-9ef2-594dfcbcbe79 | note | Verification Activity: By - ENG
939bc362-9391-4308-bdb8-c170fe303349 | signoff | AUTHORITY HOLDPOINT
aec7a5b7-ab1d-4421-94a8-aa9fd75d4620 | checkpoint | 1.8.3 - Sand Equivalent
4734c455-2ab2-5c14-b922-d944ce5cbb3d | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
2bed91fc-529c-59c1-af56-9bda658722f8 | note | Acceptance / Conformance Criteria - ≥ 40
813e9b31-91a1-52a6-b074-9e0e6f5e06e0 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
75a544a5-8ef6-5f9c-9a4f-ab9caf780513 | note | Verifying Document - IANZ Accredited Report
9c5d6fe6-cf0c-5187-96ec-f4e1d08e5474 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
46bfbcc1-6629-59a2-9aa9-925c85a22ff4 | note | ○ 0-400 - 2 tests
d3f09484-3710-5dce-becb-6c225bd6e3fa | note | ○ 400-1,500 - 3 tests
c7bf67d5-4575-5432-9665-09e140483b63 | note | ○ 1,500-4,000 - 4 tests
dd72594c-be75-54b1-89b7-12b2ac2617a9 | note | ○ >4,000 - 1 test for each additional 1,000m3
c6f63231-a1b5-5f13-99a7-0e0f2cd0aa1d | note | – Results to Engineer 2 wks before importing
86e4f1db-0e87-5f21-8869-2f2258505866 | note | Verification Activity: Activity - HP
ceb1a9b5-6794-521e-97f7-824810e18b6e | note | Verification Activity: By - ENG
604ab0cc-cf80-4ed7-a7c8-e0eceb492e51 | signoff | AUTHORITY HOLDPOINT
766261d8-e67b-40f4-a643-2ffcc3e692aa | checkpoint | 1.8.4 - Cone Penetrometer Limit
c3b6b94c-ecaa-5fa8-9c50-7ec224c6f575 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
b6776f54-321a-523f-9bb8-ed52f5ab010a | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 30
e240aaef-769c-5b3d-8cf1-60836e1af553 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
44e5c191-28b7-5baa-9c21-d6b09bd4eee8 | note | Verifying Document - IANZ Accredited Report
9a177e1e-6487-54d3-b548-319e453810e8 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
a3fbd76d-ed88-5579-8152-8a64e491d894 | note | ○ 0-400 - 2 tests
496e067b-fcb3-5518-a644-54687cbabf34 | note | ○ 400-1,500 - 3 tests
90117e4e-fc6a-5bcb-b68a-0f387605a4c8 | note | ○ 1,500-4,000 - 4 tests
f1011cd5-a3c9-56f7-af77-0a1ce6250864 | note | ○ >4,000 - 1 test for each additional 1,000m3
afd7816f-93ca-5671-90d2-99c99143c5bb | note | – Results to Engineer 2 wks before importing
c4ee350f-05e2-5b09-8e49-9dee62d1ee31 | note | Verification Activity: Activity - HP
60591213-4b44-57c8-aea0-484a52e2b44f | note | Verification Activity: By - ENG
8dd07927-2a7e-41c3-8ad5-5c2fb8b112aa | signoff | AUTHORITY HOLDPOINT
0524a25d-f076-4cac-940f-8a04b4551d8d | checkpoint | 1.8.5 - Plasticity Index
ed4a618b-af90-5e66-b3f3-56e4afd85332 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
4e252b2d-3aef-570b-bd1e-a04d9e6c0c75 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
1a7297f8-80d7-56c6-a31b-ac3e4485f41d | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
b765fbad-29fc-59c1-a80b-7fbe5c165be9 | note | Verifying Document - IANZ Accredited Report
92d183d4-9b73-5d7f-87e6-82d4ec537532 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
1d656ea9-dfc6-5671-a482-20b525253832 | note | ○ 0-400 - 2 tests
0124400f-1272-5efd-bc7a-38a61866cd2b | note | ○ 400-1,500 - 3 tests
9ea56e5b-41d7-55d8-b523-317726eaa00c | note | ○ 1,500-4,000 - 4 tests
bcdf04f7-7a0f-5d0c-9d86-53f47dd07115 | note | ○ >4,000 - 1 test for each additional 1,000m3
9b1a6658-b166-5be0-8009-7fc0058d63dd | note | – Results to Engineer 2 wks before importing
7688e179-a45c-5358-ae92-f65f0e73fbc4 | note | Verification Activity: Activity - HP
1c5ab553-3f8a-51c6-a2e7-855317605431 | note | Verification Activity: By - ENG
97751f37-f2b5-464b-8898-e12cca3fb6f7 | signoff | AUTHORITY HOLDPOINT
6711d234-882f-4385-994d-e6ee27cc5f47 | checkpoint | 1.8.6 - Clay Index NZS 4407 Test 3.5
8d02947f-2d14-53c7-b2f4-82ebd1f6cd92 | note | Detail - Clay Index NZS 4407 Test 3.5
33a28590-7958-5abe-a9fd-ad4da34cc081 | note | Acceptance / Conformance Criteria - <5
fdf840a5-2e93-536a-b86a-d97dc5db1da6 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
37e87a4c-cba8-5d5f-976f-77b7190a2497 | note | Verifying Document - IANZ Accredited Report
ba909619-20da-5fcd-8247-94f3e2c425d5 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
9aef66d1-ca12-5872-9edb-b91ce1a71b9a | note | ○ 0-400 - 2 tests
a5c6e997-59ee-5220-9c9b-d693ebf153fd | note | ○ 400-1,500 - 3 tests
7427963c-8431-5b13-97c9-450eff628f26 | note | ○ 1,500-4,000 - 4 tests
99b13abe-5c34-5f94-8a00-61c5ecb4711e | note | ○ >4,000 - 1 test for each additional 1,000m3
d16fffc9-b611-5c32-9078-0b209d249050 | note | – Results to Engineer 2 wks before importing
55c19460-8578-5dd3-8be5-bb202e0fe7f5 | note | Verification Activity: Activity - HP
9e064852-f564-59f0-b618-f0536b7449a9 | note | Verification Activity: By - ENG
4a0a0d6b-4308-40bd-afb5-a6bb655df906 | signoff | AUTHORITY HOLDPOINT
c948a93d-5c77-4188-979b-a174d4b2414a | checkpoint | 1.8.7 - Accelerated Weathering
a58f15be-8cd5-5e9f-94a4-4280b6df2830 | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
524ab205-163a-57c1-9247-681c26c167c3 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
f1f95192-3da3-5f27-be2f-5d8155c9496b | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
0e19de73-00a3-508b-ae32-16c740e5f428 | note | Verifying Document - IANZ Accredited Report
1c1f5376-8d59-51b4-aad5-b7231010a761 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
b415b75c-e525-5a74-976b-0845cf576b25 | note | ○ 0-400 - 2 tests
b10399d0-4d9d-53cd-a035-8dc4c230abbc | note | ○ 400-1,500 - 3 tests
caf4b8d5-4010-58f9-b388-9018c308c948 | note | ○ 1,500-4,000 - 4 tests
d8e44eb1-ec4a-52b5-b56f-cc66beec2ae8 | note | ○ >4,000 - 1 test for each additional 1,000m3
bdfd0f3f-0b75-5332-b701-749b01ea5cb0 | note | – Results to Engineer 2 wks before importing
d2c5e963-c443-5d8f-91d3-03420a157f91 | note | Verification Activity: Activity - HP
84eeb6bd-4f70-5801-93e1-b993c580c5ac | note | Verification Activity: By - ENG
ef8d50fb-dc82-4c31-a97f-447a936699f1 | signoff | AUTHORITY HOLDPOINT
bf89fd2f-35c9-437a-8ba6-438d173722b6 | section | SECTION 2 – CONSTRUCTION - SUBSOIL DRAINS
9bc8b022-8eb5-4cae-9579-cbf21e3a7b24 | checkpoint | 2.1.1 - Subsoil Drain inspection
454282fa-ab16-5d64-a092-9d6cb06ad420 | note | Detail - Subsoils to be placed below kerb lines and inspected by Engineer
5c8a6d0a-6011-5bad-85e2-4b346f4a9f09 | note | Acceptance / Conformance Criteria - Engineers Approval
04868d0a-2d21-5f6f-bacb-e31901f9e7e8 | note | Standard / Specification - PS 17.6.3
81c2c6ec-3ad2-5365-8bdb-f9747a6369af | note | Verifying Document - Hold point released
6b7899ef-9ba9-5a3e-b52a-a5cbe03a8f82 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
7f38251b-2b47-5973-a101-dd6fdd6a2f76 | note | Verification Activity: Activity - HP
3b7e46b4-2929-5c21-b810-cb1d8309ce18 | note | Verification Activity: By - ENG
3dc4cb24-8a48-4538-bbe4-3a89f7e84b2b | signoff | AUTHORITY HOLDPOINT
e7b630cc-aafe-4da6-9c4b-b0b1bfdcf53b | checkpoint | 2.1.1 - Excavation
b3e0ba96-5186-57bb-9100-c7a31d966fa5 | note | Detail - Excavtion of Trench should be within tolerances.
23c6e656-4a71-5451-ae8c-6d668a651aed | note | Acceptance / Conformance Criteria - 335mm deep x 300mm wide
e1538e53-a3bf-5a80-81dd-6f8b9931a435 | note | Standard / Specification - Drawings
50da2fe3-03b7-5760-86eb-938f6d639f06 | note | Verifying Document - Subsoil Checksheet
6b48943b-9dc3-5a36-ad31-a6b5b1233a2d | note | Testing Quantity Required (based from schedule qtys) - During construction
84ab2e51-7be6-5bc7-9a4d-06068997baa4 | note | Verification Activity: Activity - M
394c4edc-2f5e-581f-b4b9-6fac500f4e82 | note | Verification Activity: By - SE
2adc3dc6-1f6f-45b4-9b2b-95a157b290de | checkpoint | 2.1.2 - Placement of Bidim
9ede821b-6b3e-5ee7-8696-61cf67c0044b | note | Detail - A29 Bidim to be placed andd wrapped around Trench.
546b5a06-98c6-52fe-ac18-9a335dfeecb4 | note | Acceptance / Conformance Criteria - Minimum Width 300mm.
c6b5a53f-69c1-5612-8e63-632141c5ed95 | note | Standard / Specification - Drawings
74bbdbc7-b116-517e-b849-b3530602fb66 | note | Verifying Document - Subsoil Checksheet
84936c86-703e-5522-b979-4405fa4e7172 | note | Testing Quantity Required (based from schedule qtys) - During construction
777e011f-1ff7-5bb4-9ead-9fdced610b08 | note | Verification Activity: Activity - M
9958d2e3-8cb9-5b0e-b40d-6af2929b2f24 | note | Verification Activity: By - SE
6f0c39ac-50e8-4f39-a384-5930eebe8e5a | checkpoint | 2.1.3 - Cushion (Bedding)
471ffe35-2322-53ce-8818-449f0dbe092e | note | Detail - Pipe must have 75mm of Cushion. Drainage 60:40 Material to be used.
62026e4b-090b-5496-bd45-fc484ef7c624 | note | Acceptance / Conformance Criteria - Minimum 75mm
446eff34-b422-579f-93ae-2f932f23b352 | note | Standard / Specification - Drawings
a947c901-8420-5ab3-b172-66cb398c4d6e | note | Verifying Document - Subsoil Checksheet
ad4faa99-09c5-5c8e-92bc-187a05323335 | note | Testing Quantity Required (based from schedule qtys) - During construction
34f54eb6-a006-5012-a729-109266e32224 | note | Verification Activity: Activity - M
0f11fc34-7714-5003-ab78-cdfa0d9bcf2a | note | Verification Activity: By - SE
c00bbabf-e2ca-4771-89b9-e1beb64387f3 | checkpoint | 2.1.5 - Placement of Pipe
04b0b817-b4b6-5f49-ac5d-11384150a0fd | note | Detail - 110mm Perforated Pipe to be laid Down
d27e600a-61aa-59fd-8951-80411bde1f7e | note | Acceptance / Conformance Criteria - As Per Drawings
4c49739f-5a98-58b2-ab8e-df49873197b9 | note | Standard / Specification - Drawings
319c6d77-2fdb-55fa-87dc-1bd30d1b6777 | note | Verifying Document - Subsoil Checksheet
057ec02e-7d84-5581-ba82-b71ec684614e | note | Testing Quantity Required (based from schedule qtys) - During construction
af3a061a-0524-597d-a45f-90009d796b12 | note | Verification Activity: Activity - M
11c2b2cb-3772-56d6-b3b3-65100e635684 | note | Verification Activity: By - SE
6a2cc404-b57c-4d3a-b59a-40c723c09350 | checkpoint | 2.1.6 - Backfill
8d65d731-9300-58b4-88d4-aca07e017a88 | note | Detail - Pipe Must have a 150mm cover from Bottom of Pavement.
d222a4c3-a39a-5c5c-927a-42a8bac69937 | note | ○ Drainage 60:40 Material to be used.
9336073e-9e1f-57e6-8c6e-0bec651e37ed | note | Acceptance / Conformance Criteria - >150mm Cover
44ec0930-24ab-5029-bddc-770089b3c129 | note | Standard / Specification - Drawings
58369a61-eb6a-5398-9531-8cf58e07edc1 | note | Verifying Document - Subsoil Checksheet
b44cead0-2d15-596e-9546-4888a576ba91 | note | Testing Quantity Required (based from schedule qtys) - During construction
af991cad-3097-56ae-9f08-4a049c630cfe | note | Verification Activity: Activity - M
8fd05b15-c70a-540f-a9d6-64e3e3a4c321 | note | Verification Activity: By - SE
b4540cb8-c2b1-46a6-af3c-38b819982012 | section | SECTION 3 – CONSTRUCTION : PLACEMENT OF GEOGRID AND GEOTEXTILE FABRIC
d2a3dba9-b9cb-47e2-aa78-c87a7954d88d | checkpoint | 3.1.1 - Placement of Geotextile Fabric
6df789f7-bfee-5789-b611-4432fc127dad | note | Detail - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
98ad861d-6a96-5718-bbe1-c5db99667e50 | note | Acceptance / Conformance Criteria - Visual inspection
af902383-b04c-58b6-b1e1-005883604008 | note | Standard / Specification - NTC0097
a31152c7-9692-56b1-ac2c-27d6e0ee95de | note | Verifying Document - Visual Inspection
9059c401-41e1-5b96-9c62-d4ff169a8afe | note | Testing Quantity Required (based from schedule qtys) - During construction
e6e33450-1a45-5ee8-b6ca-63d0fa5af91e | note | Verification Activity: Activity - WP
19355e42-aeb0-50ce-878b-89ce080e4d00 | note | Verification Activity: By - ENG
a7281051-e533-45c5-a766-a49a2fe38e1b | checkpoint | 3.1.2 - Onsite Check by Engineer on Geogrid
b48a66f9-e6da-5b4d-b988-2af5ec5b1a8f | note | Detail - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
2f370e1f-4f86-5a96-beec-6f289e4aef08 | note | Acceptance / Conformance Criteria - Visual inspection
c87b98a7-509e-5ead-abef-755cf505f3e5 | note | Standard / Specification - NTC0100
f00e7431-b47d-5303-87ff-b7c730888d26 | note | Verifying Document - Visual Inspection
19143b28-600f-5ad7-a683-99f466097d90 | note | Testing Quantity Required (based from schedule qtys) - During construction
6021e670-2738-5306-a3b0-95a60eaffb3c | note | Verification Activity: Activity - HP
28859638-2467-5cd7-a1d6-9b21608bc7b8 | note | Verification Activity: By - ENG
44655d65-18d1-4da2-8bea-395f6941965f | signoff | AUTHORITY HOLDPOINT
07832c6d-9351-415b-a971-82cce129cf0f | checkpoint | 3.1.3 - Placement of Geogrid
96268d09-1354-55e2-8257-2980d3f1db6e | note | Detail - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
30717041-d3b6-566c-bc37-de9cc43197e0 | note | Acceptance / Conformance Criteria - Visual inspection
20b2b631-af06-5803-8dda-704be3574b7c | note | Standard / Specification - NTC0100
fda06ca9-03c9-5133-90e0-8eb787f75d21 | note | Verifying Document - Visual Inspection
b373eafc-d6bc-5fdf-bad8-ae6dfb2caf63 | note | Testing Quantity Required (based from schedule qtys) - During construction
94c6da75-9bfa-5cb8-b6cd-2a6713dc162f | note | Verification Activity: Activity - WP
87dd6597-1633-5d72-9d4f-06175e297cf7 | note | Verification Activity: By - ENG
108c18e3-636e-4c4f-90fc-114435b78b19 | section | SECTION 4 – CONSTRUCTION : SUBGRADE IMPROVEMENT LAYER TESTING ( AP65-2)
b671884f-3e8f-471a-bb19-d64e10d4fc09 | checkpoint | 4.1.1 - Plateau Density Test
072e09f8-7dee-5c42-a36a-39ff228c2e47 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
44fb90d8-bc68-5ade-b2c7-c8dd7f28b246 | note | Acceptance / Conformance Criteria - Plateau Density Report
64f5a45f-0aa1-5ab4-8c24-9747ef665237 | note | Standard / Specification - NZTA B/02 7.5
c497b2d7-6040-5237-a9a1-19fe06dea15f | note | Verifying Document - IANZ Accredited Report
730a6b65-c7ee-5d92-a26b-243881b0cc37 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
2b2d0139-915e-5c70-ab7b-5fe570c4d1e3 | note | Verification Activity: Activity - I
7ab2d4b8-0fe2-5fc0-ae80-beb03a34a2ea | note | Verification Activity: By - SE
4f6ea550-6f56-4765-9c7b-292c01de7f6d | checkpoint | 4.2.1 - 3m Straight Edge
eadbb648-de8d-575b-9d98-16c6f811bda6 | note | Detail - Formation check to ensure surface is smooth
aec5e88f-a5de-5caf-8a5a-147ce606f8de | note | Acceptance / Conformance Criteria - +/- 10mm
b069e9e8-425e-535e-92a7-c94d33d08318 | note | Standard / Specification - TNZ B/2 7.7
c4662eb6-690d-57ae-b9a1-c21bd1ef0481 | note | Verifying Document - Check Sheet
dd3bbeb2-0165-5568-abe4-49fc06c7b640 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
5d54e442-84ab-5888-8446-5dba1fd97a42 | note | Verification Activity: Activity - I
c5a6be66-875c-534a-b9e2-f35f820db4df | note | Verification Activity: By - SE
a49b93b0-16ae-49e2-ac5b-29e1c3f6fa1c | checkpoint | 4.3.1 - Stringlines or equivalent
387c226f-ff0c-5864-bb4d-b5039b14e31f | note | Detail - Stringlines or equivalent to check finished height of surface
cbed4b5d-1bb1-51a6-b33b-f721ee2f6dc9 | note | Acceptance / Conformance Criteria - -25mm + 5mm
988de439-cb52-520d-905a-96ebfb9b614e | note | Standard / Specification - NZTA B/02 5.1
938e3694-a387-53d1-a4b8-d5701aa02740 | note | Verifying Document - Check Sheet
74c19353-6f48-5b35-bb4a-489bc7a25113 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
32f72a6f-7744-55c7-8abd-9f6eac0c6757 | note | ○ 1 set = 5 tests
29702b2e-46fa-5e73-a3e7-f6c69d5161ad | note | Verification Activity: Activity - I
7e3d8079-8df8-52be-97cd-2db704e4fb8e | note | Verification Activity: By - SE
7d95e5fd-2c7f-4644-8f21-4b3233a052eb | checkpoint | 4.4.1 - Compaction - NDM
71d91cfa-dc4c-5287-9b82-afc6a69d9248 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
e846d025-61f5-5634-bb41-7fd7eaa62fbc | note | Acceptance / Conformance Criteria - Ave >95% of MDD
5bda8b61-e483-5f8d-a391-e8aaf924d67a | note | ○ Min >92% of MDD
74509f53-9020-5881-b0f5-787bbffd85e6 | note | Standard / Specification - NZTA B/02 7.6
c82eb608-e8de-583f-bbe8-3766fe41c4f1 | note | Verifying Document - IANZ Accredited Report
571f06da-e408-54ab-a910-b239d032a4ef | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
da0641db-2ed5-5dfa-be48-e9e64d2e4ab6 | note | Verification Activity: Activity - I
a4b3608a-2262-5f2f-bb58-ac1d3dec1bb5 | note | Verification Activity: By - SE
3a615086-bff4-40da-ae04-2289b00af3ec | checkpoint | 4.4.2 - Benkelmen Beam
1ea9e246-cae9-57bd-8e00-06073e1c6c9a | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane. Unbound layer.
d375c02d-8544-577f-86ca-0df9dda943de | note | Acceptance / Conformance Criteria - 90th Percetile: 1.90mm
524a9f3f-846a-5e4f-b8c1-c75605011499 | note | ○ Maximum: 2.34mm
48dfcdbb-88f5-5554-9e07-c8bf66ff10e6 | note | Standard / Specification - PS 20.14.5, NTC0160
89eb0a36-3256-5473-9270-61d4e5c95398 | note | Verifying Document - IANZ Accredited Report
e2b6b740-7ca2-5d38-9195-bfb62f3e5447 | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
e856428c-34c8-5701-9c2b-4c2b5b5eb502 | note | Verification Activity: Activity - HP
ec4e4cff-e0d7-5987-85c7-68701f91707c | note | Verification Activity: By - ENG
d934aff8-0f49-4641-a0b1-3592acc90c76 | signoff | AUTHORITY HOLDPOINT
4ad79ee1-5a8f-44ea-a222-0e7ceb5079d1 | section | SECTION 5 – CONSTRUCTION: Subbase Layer Construction (AP65-1)
2b54d7ad-42f2-4dcf-ac92-d7d1ae27bf2f | checkpoint | 5.1.1 - Plateau Density Test
10ff17b6-cc03-5ff2-b2cb-d1f6070ef390 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
dcab0b4e-32c3-502d-b99d-9efec63afad0 | note | Acceptance / Conformance Criteria - Plateau Density Report
a0edc13d-27fd-54bc-a726-8e2c348bfb8f | note | Standard / Specification - NZTA B/02 7.5
cc75a222-1ba9-5443-a1ec-ecf4f5275165 | note | Verifying Document - IANZ Accredited Report
027c734c-abd9-5aff-a54e-7daa79564216 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
1df54d4a-1952-5dd7-8e64-2680ab1b2b4e | note | Verification Activity: Activity - I
27dfbcb9-8ff9-5e06-8bc4-586159c1193c | note | Verification Activity: By - SE
0d9dd8f1-babc-47c1-af98-c396f5a09811 | checkpoint | 5.1.2 - 3m Straight Edge
92c94e8d-2fd9-50a5-bc24-54237390202d | note | Detail - Formation check to ensure surface is smooth
2e751bab-b8a8-5729-8a99-aa251adeff7c | note | Acceptance / Conformance Criteria - +/- 10mm
bd108313-46ac-5196-af5d-7a379ae362d3 | note | Standard / Specification - TNZ B/2 7.7
ecc51f39-28cc-531f-94c2-666394706b84 | note | Verifying Document - Check Sheet
64fe7b88-52cc-5535-9f08-3dd38968c906 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
b678566e-e9b4-51de-b148-8d01827c7edc | note | Verification Activity: Activity - I
cd07e881-477b-5caa-8736-b8f37cce5e94 | note | Verification Activity: By - SE
c19e0d74-ad6e-490b-ae4c-d1a75df62c8c | checkpoint | 5.1.3 - Stringlines or equivalent
6ae82037-0fed-5bdc-9746-5f66d74c9ab8 | note | Detail - Stringlines or equivalent to check finished height of surface
17e65358-37aa-52d6-b774-31854507c71f | note | Acceptance / Conformance Criteria - -15mm + 0mm
87a377e1-9599-5145-83a5-e79ca88949a8 | note | Standard / Specification - NZTA B/02 5.1
b69a8077-b193-54ab-b827-be454dbb8de2 | note | Verifying Document - Check Sheet
be73f4b8-1ba7-596d-b151-0dfa07c48968 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
73caabab-72d7-51cb-b3fb-77f9bf012b1e | note | ○ 1 set = 5 tests
2f05399a-5128-52ea-a207-12cb32ef1372 | note | Verification Activity: Activity - I
1514e247-f5dd-593b-a5c1-77a1774443fb | note | Verification Activity: By - SE
b3878906-4116-4560-9d89-a23580cb02ab | checkpoint | 5.1.4 - Compaction - NDM
ba2bc629-e278-51f7-a275-1f511b135c92 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
1dcac20b-3982-54d9-bb53-5168b86d7db7 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
9d7e047b-ff4f-55ed-876c-69060875499d | note | ○ Min >92% of MDD
1a96b206-6f42-52e7-bc54-95ecd95cbb61 | note | Standard / Specification - NZTA B/02 7.6
8087c3b3-d363-5186-ab36-dbcb44b81e8c | note | Verifying Document - IANZ Accredited Report
d9f2372f-38fa-5367-86ef-96b3f1fe842a | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
f25cb4b3-acc1-5e3e-9626-8a6b91d061f2 | note | Verification Activity: Activity - I
357b0b45-891e-53c4-aa64-8497e9ebd542 | note | Verification Activity: By - SE
82809645-7538-4a37-bd95-00663a2a424f | checkpoint | 5.1.5 - Benkelmen Beam
52dfe179-7f57-5040-86c2-f8a504cea140 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
dd28708c-0356-5f6d-87aa-8caa207a502d | note | Acceptance / Conformance Criteria - 90th Percentile: 1.39mm
a05939f2-5564-56a4-be83-e366702cec41 | note | ○ Maximum: 1.70mm
2b66b0ab-d0e3-565c-85d4-4ef2f23c1abe | note | Standard / Specification - PS 20.14.5, NTC0160
1205535a-353e-511b-bbf8-7c55d51c20e1 | note | Verifying Document - Test Report
86c7f71c-f4a6-5a7c-9fe1-ce1957c286ec | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
2e0e1c04-ba8f-5151-a3ca-2ca3738e2727 | note | Verification Activity: Activity - HP
019c4677-47d7-5311-b9e7-84d2ae359fe5 | note | Verification Activity: By - ENG
f74389bb-0609-49b3-a654-1d0a29f9535d | signoff | AUTHORITY HOLDPOINT
88fe4122-7666-4abe-82c3-e4ea5d5c5d36 | section | SECTION 5.2 – CONSTRUCTION : Subbase Cement Modification - (AP65-1)
be2add53-291e-451b-9971-16612774bf80 | checkpoint | 5.2.1 - Mat Test
f28cdc06-b47c-5a80-908e-3ce5740d9616 | note | Detail - 1m2 Canvas - used to check the (13.3kg as per lab report) of cement being used per m2
746f1957-0959-5aef-b75b-24f32fd0fc59 | note | Acceptance / Conformance Criteria - Visual inspection, check sheet
9c1a15bf-8d94-5a08-8d8d-18bc87216636 | note | Standard / Specification - NZTA B/06 7.3
981e9142-7ead-51a6-84c8-0adf5c2fd3eb | note | Verifying Document - Stabilisation Check Sheet
471ebdb9-05d9-5a09-a8ab-115bd077fab7 | note | Testing Quantity Required (based from schedule qtys) - Every 400m2
877f4c1e-89c0-54c4-b4bb-b40380d5addf | note | Verification Activity: Activity - I
bf0ae4e8-1997-5a13-b3ec-6811eb1e3d31 | note | Verification Activity: By - SE
a9c1379d-844a-440c-b622-c7ae3033159c | checkpoint | 5.2.2 - 3m Straight Edge
23a57573-6272-5b62-9923-dc05d41eeb7c | note | Detail - Formation check to ensure surface is smooth
289143d2-971c-506f-8605-8a713ad3472b | note | Acceptance / Conformance Criteria - +/- 10mm
5920dca6-33ef-5df2-ac13-293391582627 | note | Standard / Specification - TNZ B/2 7.7
afa5e34c-347d-5d06-b48e-f46f7e248932 | note | Verifying Document - Check Sheet
d6002b22-2cd5-57ad-9589-8519c692b184 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
5de27584-247f-5f12-943b-50e7369948f7 | note | Verification Activity: Activity - I
28aa959a-d2d2-57de-98ba-47a25053da4e | note | Verification Activity: By - SE
f78d7eb4-ccb0-4447-be0b-cf45743958f7 | checkpoint | 5.2.3 - Stringlines or equivalent
d6c7fa27-bf4c-53cc-813e-8ce71741c769 | note | Detail - Stringlines or equivalent to check finished height of surface
330af192-5a15-579c-8055-bc75ad77e5f7 | note | Acceptance / Conformance Criteria - -15mm + 0mm
ecb928b2-6443-5af5-920d-46a7ea162044 | note | Standard / Specification - NZTA B/06 8.2.2
10550c92-295c-54c7-872c-c428cd7fb846 | note | Verifying Document - Check Sheet
75ec6dbc-7c16-5116-b1b3-8848273d84c8 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
7ebaa216-b23b-58b6-b5b3-8ee9373ec411 | note | ○ 1 set = 5 tests
4d7882a5-ff86-56a0-ab85-32400710884e | note | Verification Activity: Activity - I
5e26c6d3-5c6f-5fe0-825c-2345a9209db4 | note | Verification Activity: By - SE
b64b6f27-6a70-440b-86c9-18d7d2d13230 | checkpoint | 5.2.4 - Compaction - NDM
398fbef9-3262-5bab-8257-8db87584bc2a | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
2508f6b0-8f8a-5752-a50c-5422bba5967f | note | Acceptance / Conformance Criteria - Ave >95% of MDD
bf822851-383f-550d-b061-5617ede3f7cf | note | ○ Min >92% of MDD
81029c66-3865-544a-90d5-a83fcd541e6c | note | Standard / Specification - NZTA B/06 8.1
d345ecd7-02ba-5544-bd85-3eeb83e54039 | note | Verifying Document - IANZ Accredited Report
7efbc78c-614e-5e58-b82c-ea2ff52b46da | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
181bee23-416f-5fe8-94a1-410b6b838b13 | note | Verification Activity: Activity - I
1f891247-1967-59a1-8512-bcce864c560e | note | Verification Activity: By - SE
065b120a-3586-46bd-b93f-b96e15a5f196 | checkpoint | 5.2.5 - Benkelmen Beam
bd7afd3f-9c0a-518e-8850-80b9c1632a17 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
7265da99-077a-51b4-a672-0e543a8d2e70 | note | ○ Unbound layer.
984f1429-0c1a-5eb1-bd3d-918255d8d1b0 | note | ○ Cemeneted Layer.
58b58d78-2044-5230-a04a-abe93584ab17 | note | Acceptance / Conformance Criteria - 90th Percentile: 1.39mm
c03e55cc-94e2-513c-9ad0-1482fe41963d | note | ○ Maximum: 1.70mm
d2aebde6-0f9d-53e8-b22d-a919f029311f | note | Standard / Specification - PS 20.14.5, NTC0160
5839504b-b7f3-55c9-b815-9e402e803857 | note | Verifying Document - Test Report
c07cae09-5bf2-5c1a-9105-b05838cb98b9 | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
9ffbe83a-cb18-50c3-a376-a6d276dd7e39 | note | Verification Activity: Activity - HP
c9738bba-2dbe-5298-8fbd-f36de9998d5c | note | Verification Activity: By - ENG
3fffedee-2702-47ea-8493-eb5da29ad6dc | signoff | AUTHORITY HOLDPOINT
f9cf6e4c-0c50-4c89-a0ec-7e82a67efe90 | section | SECTION 6 – CONSTRUCTION : Basecourse Layer Construction- (AP40-1)
f87cb97a-fa60-41fc-8c06-78067d13f261 | checkpoint | 6.1.1 - Plateau Density Test
eb7e065e-7ac2-51e3-bfd6-3663ba28fe22 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
76581955-3525-5ea6-b84b-54473a484e98 | note | Acceptance / Conformance Criteria - Plateau Density Report
872ca81b-9f02-5ad8-9cd9-9c9bd2827af1 | note | Standard / Specification - NZTA B/02 7.5
d15266ef-08ed-5341-bde4-c2f49ef3449d | note | Verifying Document - IANZ Accredited Report
0f5bc925-cd08-5672-9c8b-e73fcef3347c | note | Testing Quantity Required (based from schedule qtys) - 1 Test
fd870261-e7ef-5135-9a1e-deaaeaf9fb3d | note | Verification Activity: Activity - I
ae176a82-fdd7-547c-9a54-05e18a50b44d | note | Verification Activity: By - SE
28fb9724-c144-49c3-ab45-3aa6f6f080cd | checkpoint | 6.1.2 - 3m Straight Edge
36e8292b-0c87-5f5c-997e-b9a0de697785 | note | Detail - Formation check to ensure surface is smooth
b2a9032c-662e-5663-a6be-04a005c754ff | note | Acceptance / Conformance Criteria - +/- 10mm
9c996e72-74fd-5fbf-8f38-a1f03d55a4fb | note | Standard / Specification - TNZ B/2 7.7
2b087cbe-c93e-5ec9-ad27-f15dfd1b0866 | note | Verifying Document - Check Sheet
d132cd33-cba0-5c67-afeb-f7b49de98f32 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres
99206281-ed22-5834-b74f-b7c325d42e31 | note | ○ 1 each lane
907649fb-c25e-5f7f-acbd-eacbf02355a1 | note | Verification Activity: Activity - I
788d398d-5243-5d93-978a-bd7fca3034e7 | note | Verification Activity: By - SE
1f0252fe-eb27-48fc-a4dd-7837280998b3 | checkpoint | 6.1.3 - Stringlines or equivalent
6aaf83f3-1c69-5425-afb3-7f6d02b1d1a2 | note | Detail - Stringlines or equivalent to check finished height of surface
2c0c37ef-3a5d-574a-b29a-8c8ea6a1a6f9 | note | Acceptance / Conformance Criteria - -15mm + 0mm
b138f7b7-bd1f-53a1-aece-bf2e689360bd | note | Standard / Specification - NZTA B/02 5.1
3e4e64c0-bee0-52fa-beff-7112b71bcbaa | note | Verifying Document - Check Sheet
24c04727-4160-589e-9406-25cdb51fcbcf | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
8fedf556-8aa4-5068-938e-4dd68576e69f | note | ○ 1 set = 5 tests
09d312d5-522c-5333-8173-56d7c7d36f8c | note | Verification Activity: Activity - I
e9b2e20c-5730-5457-84bb-d02af2354a77 | note | Verification Activity: By - SE
1834b22e-6393-430e-add8-cec2b84ee924 | checkpoint | 6.1.4 - Compaction - NDM
aa1f08aa-5ae3-5b18-9f04-8094c2552e31 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
c01a8e83-8cce-5063-a186-8355c4575d56 | note | Acceptance / Conformance Criteria - Ave >98% of MDD
43bbc7cd-12da-5acc-8338-8fd1943ee157 | note | ○ Min >95% of MDD
ebac6831-8f14-585a-b2e9-888dc171e02b | note | Standard / Specification - NZTA B/02 7.6
cbaa8fd4-d8e0-5271-904b-77f23194ad63 | note | Verifying Document - IANZ Accredited Report
d3063928-26eb-5e16-b52c-c51e1eec82d6 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
47f703ea-7368-5ed4-a1b9-6deaeb9c141b | note | Verification Activity: Activity - I
f2889d23-34bb-58d7-a7c5-42b77a688926 | note | Verification Activity: By - SE
bb07fbf4-c522-4443-9288-bb9462379239 | checkpoint | 6.1.5 - Benkelmen Beam test
e71108de-9d54-5776-a5a0-ab1070373847 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
9f6cc4bb-c001-565b-8f2d-812ad928df7c | note | Acceptance / Conformance Criteria - 90th Percentile: 0.90mm
bc486a9d-5efb-501f-90e2-8d547d64a5e3 | note | ○ Maximum: 1.00mm
90f3d672-4733-5a6b-a0fe-73fc14dfc159 | note | Standard / Specification - PS 20.14.5, TCC IDC 4.8
bedb32e4-5bb8-5b95-9ed4-511ae5d3e028 | note | Verifying Document - Test Report
4db8cfc3-d2f1-53d7-8892-4b90b0e4a440 | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
1050d603-6156-531d-a461-37d1b78187fd | note | Verification Activity: Activity - HP
3310f9f2-0e4e-5b53-8ba1-436bc1c75d04 | note | Verification Activity: By - ENG
29634773-04b9-4557-9429-5ad2714a0eb1 | signoff | AUTHORITY HOLDPOINT
58421bc1-e33c-4b7e-a31a-dc628e9f73bb | checkpoint | 6.2.1 - QA Submission
ef5cc7f4-6fa5-5165-b611-755851217175 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
7ab18a1e-c2e8-5443-bed6-8b9395fd59af | note | Acceptance / Conformance Criteria - Engineers Approval
35c3471f-0a87-509d-a720-45110e329f2b | note | Standard / Specification - Appendix V
9060aeb3-5e60-5f06-8a5d-42f887b28834 | note | Verifying Document - All test reports
cdb084d2-9ca9-5853-9e8c-5ed13c657065 | note | ○ Material Test Results
af98cada-4ef1-5213-a819-eb6837e9887a | note | ○ Laboratory MDD
de5d317a-b926-5213-951d-0885f0623be8 | note | ○ NDM results
5ecfe9e7-3f89-51e4-b5c9-8352b29031c6 | note | ○ Proof Roll
bf889641-2923-50cd-9206-e06140dc492b | note | Testing Quantity Required (based from schedule qtys) - Once
a667fdd2-20dd-502e-8d13-9c73a6f24b74 | note | Verification Activity: Activity - HP
95cdc64d-29fa-5b27-9a31-9246fd9f8182 | note | Verification Activity: By - ENG
122a4191-9f49-4d65-bf83-49c4dedd4634 | signoff | AUTHORITY HOLDPOINT
6097308c-8ff6-4cf2-95f2-7e66fd341f63 | section | SECTION 7 – CONSTRUCTION: KERB & CHANNEL PREPARATION
d109f8e3-e555-4501-be7f-7ccc620ef819 | checkpoint | 7.1.1 - Stringlines or equivalent
f4752ae2-bae2-5082-8e7a-fd3563d642ce | note | Detail - Stringlines or equivalent to check height of surface prep
b9ec9230-f8e4-58ab-8584-389ea961a22a | note | Acceptance / Conformance Criteria - +/-5mm
b1bc853f-2440-5ed4-bca2-7595e54eb074 | note | Standard / Specification - PS 21.7.6
40c61f18-a9a1-56cb-a54a-78a87f36362e | note | Verifying Document - Check Sheet
808e2986-94be-5b44-b7ff-2d2550519bd7 | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
30a7bbfb-9ab7-5595-8415-8ad92ab9e3d8 | note | Verification Activity: Activity - I
a03faac2-6d55-5589-89d6-1eb4dabbaff6 | note | Verification Activity: By - SE
aa11b864-ff11-48fc-a0a6-ab8143b803bf | checkpoint | 7.2.1 - Compaction - Clegg Hammer
97294872-8e6f-5e2f-b6f6-c6723f7e8e58 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
107e071e-3ed3-5dc0-ab63-1e63706a6f4d | note | Acceptance / Conformance Criteria - Min 25 CIV
cf63eaa7-a301-5a1f-a17a-168b1aac5978 | note | Standard / Specification -
d40ae453-2851-5ac5-a01c-11d257003eb6 | note | Verifying Document - Clegg Hammer Report
6285351d-0161-5100-ba53-286a0164c1c1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
35b09c36-1484-57fd-a187-ce62b69fd9d7 | note | Verification Activity: Activity - I
0d0a934c-e707-54f4-82e0-25db57bc9e3e | note | Verification Activity: By - SE
ef507bab-ebab-40e5-87f1-b50f7d05aa81 | section | SECTION 8 – AS-BUILTS / REDPEN MARKUPS
a1b8d841-b633-44d7-a41b-412dae2113a5 | checkpoint | 8.1 - As-Builts/ Red pen markup
e3293e4d-e669-589c-a30f-c6ed7494b49d | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
0c90b9ee-9b27-5d28-8b54-f5836ff8868d | note | Acceptance / Conformance Criteria -
83f4dfae-7183-54c5-9ce0-e6c1446b22ba | note | Standard / Specification - PS 16.7.6
703cd00f-1d15-568c-86a6-f466e97185a2 | note | Verifying Document - Red pen markups
917a6c1a-7859-5bbd-95f6-70f4c64ba129 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
d788762e-23ef-579b-a4d5-3b493318adfd | note | Verification Activity: Activity - D
786ac0c9-6051-599c-b62b-2bfe815d00bd | note | Verification Activity: By - SV/SE
f4d093d0-2e52-4e45-a6d4-f83cbca97bc9 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
b9ddd635-4346-5ef3-b9e2-8585f03113a4 | textbox | Contractor's Rep Name:
ca70f1d1-99a1-5e85-a31a-1905e2a1a1f2 | textbox | Engineer's Rep. Name:
5be1330d-5c3e-566e-ae07-d648292dbb95 | date | Date:
c0813f0b-bc62-43b9-ba48-01d95fd3b83d | signoff | Add Signature
6c1d0992-3f74-4514-a9e2-da5ca87fb96f | checklist | DN1210-030 ITP Pavement 8 REV0 | itp | DN1210-030 ITP Pavement 8
aca0e09d-a0c6-428d-825f-d09e37dfd20c | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
dabf2517-48da-4d79-9b9b-3884a64aac12 | checkpoint | 1.1.1 - Geogrid
eacf1861-a0ff-53da-ab93-7216807250e4 | note | Detail - The Contractor shall submit the full details of the geogrid they propose to use to the Engineer for approval prior to installation.
1a78301d-7731-52d4-876e-a571b42c3184 | note | Acceptance / Conformance Criteria - Engineers Approval
75749727-3a29-5e75-b6c4-b4b3955a2491 | note | Standard / Specification - PS 20.5.2, PS 16.5.13
d8d7436f-fcf7-5e01-a2c3-8f38219056aa | note | Verifying Document - Data Sheets and Approval
58b4bbb6-da9c-5a59-90f4-b23d0c6f27ee | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
3be26a8b-172d-5710-a41b-4febd91b3b4e | note | Verification Activity: Activity - HP
260a3ab0-8a5b-5896-801e-ab2136fc28e4 | note | Verification Activity: By - ENG
d1dea125-82e6-4f7c-96ee-7fcabcab1282 | signoff | AUTHORITY HOLDPOINT
c539f5f2-5129-4128-bd58-efd9e01c9786 | checkpoint | 1.1.2 - Geotextile Fabric
d5505466-da96-5a8f-97e9-da096b009d22 | note | Detail - The Contractor shall submit the full details of the geotextile fabric they propose to use to the Engineer for approval prior to installation.
8bf42caf-dae9-53dc-b16f-e53d91c74651 | note | Acceptance / Conformance Criteria - Engineers Approval
2387a287-c093-5689-b230-4c0d46b142af | note | Standard / Specification - PS 20.5.2, PS 16.5.14
f932d502-492c-5afc-b621-a17076d88481 | note | Verifying Document - Data Sheets and Approval
840d52bb-7f2e-5a21-a214-30b839350824 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
237c4871-9285-58f7-9b94-e425db6f383c | note | Verification Activity: Activity - HP
cc63423e-c30b-51e7-a41d-68afe79e51f6 | note | Verification Activity: By - ENG
daa71d35-d1fb-4456-9d84-611493f2ad11 | signoff | AUTHORITY HOLDPOINT
4e310427-d553-4d73-bcc3-fdb142fbffc8 | checkpoint | 1.2.1 - Crushing Resistance
79cd2ed1-4005-5c04-8efc-aee611e794b9 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
449af382-ed19-522b-b04c-2b1945629693 | note | Acceptance / Conformance Criteria - >100KN
e5d020b2-aaee-51ad-8db9-fcc035adf3ba | note | Standard / Specification - Appendix XVIII
de769e98-8220-5148-9b2e-67bccd921d7e | note | Verifying Document - IANZ Accredited Report
8f01ae13-0cbb-53f7-92b8-96a3ef737d23 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
1de789ea-8753-5515-ad7e-dadc06c5ff95 | note | ○ Results to Engineer 2 wks before importing
045e4a88-f27a-5c85-899d-f92bf9149c22 | note | Verification Activity: Activity - HP
3582e24a-9d94-54cf-a6e5-4d7b8741b8bc | note | Verification Activity: By - ENG
ec02315f-22f1-41e7-983b-87c926534eab | signoff | AUTHORITY HOLDPOINT
b22fd2dd-d108-4996-90aa-b2bd7612e287 | checkpoint | 1.2.2 - Particle Size Distribution
b356494a-e936-55f5-be5f-50bcf2984cfd | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
7e7146e3-18ac-5c66-8b60-b75f7e8b4fee | note | Acceptance / Conformance Criteria - Max Particle Size 53mm
7d61ac95-f7ae-5c74-b6a1-507cf75b02cd | note | ○ Max 10% passing 13.2mm sieve
3a325305-f98c-53ad-bf23-d70a58404d43 | note | Standard / Specification - Appendix XVIII
207674c1-3e78-5d0b-a8a7-f5f3ceb4f2e5 | note | Verifying Document - IANZ Accredited Report
dcfa0954-a085-53df-9e9c-0e88bbef5d1e | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3
3dc8a4f1-7c02-5467-9240-da12e06b5289 | note | ○ Results to Engineer 2wks before importing
bcda2145-a79a-5b3e-8339-cde709f63107 | note | Verification Activity: Activity - HP
75e4e80d-3a92-50a5-826d-7a2f6fc6ed08 | note | Verification Activity: By - ENG
ba53df63-fb4a-4e3b-8424-95cce1ea3468 | signoff | AUTHORITY HOLDPOINT
89b7ee7b-4815-4ee2-9cee-f2918dd866d4 | checkpoint | 1.2.3 - Weathering Resistance
4959fe18-a012-5713-b324-513de1487149 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
2653e0dc-eba3-5045-a63a-0b8605d96bb2 | note | Acceptance / Conformance Criteria - CA or better
ae02cabe-848f-5f3d-81e1-c0290c1a56db | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
77c87968-bd6c-519b-b78e-45f3a23a33f0 | note | Verifying Document - IANZ Accredited Report
8d5ebb06-bfbd-546e-ae04-002e2910b56e | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
74b2f8b0-7efa-54b2-bc5d-c35a71fce43c | note | ○ Results to Engineer 2 wks before importing
aea79779-205d-579e-9d80-3fa6016cc0e0 | note | Verification Activity: Activity - HP
43fc89a4-3844-5f3d-a4d0-555a25457480 | note | Verification Activity: By - ENG
aabfa5b6-e884-45f5-9a45-294c8c5170a3 | signoff | AUTHORITY HOLDPOINT
74d9c903-f7b7-4efc-979a-e061b1e85e9c | checkpoint | 1.3.1 - Crushing Resistance
6e21854d-0361-563b-82f7-2c011be2bcb4 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
7da715b5-4b39-59b2-b4d2-323424eec897 | note | Acceptance / Conformance Criteria - >100KN
a91de2db-c5fc-5791-b24b-817f27e7ce94 | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
5bc64ecb-092e-5744-8a9b-e4fef3df0e83 | note | Verifying Document - IANZ Accredited Report
c52072da-85ef-57ab-97e5-fa8852d6cd5c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
7072307e-6e71-533b-a79a-2a6d5047d085 | note | ○ Results to Engineer 2 wks before importing
d43ec809-9f1e-57e2-bcc1-11645ebcc396 | note | Verification Activity: Activity - HP
f75eca3f-ab13-5d98-bb10-bd33cb9df071 | note | Verification Activity: By - ENG
882dbc8d-756f-4910-b6b7-5e9f78058aef | signoff | AUTHORITY HOLDPOINT
7f076dd6-c239-4d78-b969-a3c145f646a2 | checkpoint | 1.3.2 - Soaked CBR
1fdf6168-caf3-5adf-be7b-1d8894ee3dbd | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
abd524c2-c910-5021-8fd6-0ad855b0c112 | note | Acceptance / Conformance Criteria - >60%
9c45fe6c-4a38-50d2-a1ad-43fce0c14d1c | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
bd6ce960-0a45-5dfc-84b6-ef827409b4a3 | note | Verifying Document - IANZ Accredited Report
fa5d4ae3-5f1a-5fcc-aab1-f14aaa164bb1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
338745d5-4cb5-5791-b20d-6ff8346d4c08 | note | ○ Results to Engineer 2 wks before importing
9d7c3b1d-afe6-5a43-b390-e429e1fa844e | note | Verification Activity: Activity - HP
2492c7cc-a6ed-54cb-ae77-e677e929f0f9 | note | Verification Activity: By - ENG
b9f8fad2-c057-4a9c-9da6-e73194a77adc | signoff | AUTHORITY HOLDPOINT
c5fbfee4-9f56-4ae4-a17d-96d6515cd7aa | checkpoint | 1.3.3 - Weathering Resistance
e4d3b22c-e03e-5924-9d04-ef45fb4d19a6 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
9975fd90-4125-53af-b3e0-5b032e8f055e | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, CA or CB
9a8cbc00-d703-5bb2-bf37-2c612f13ca78 | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
49fbddc2-8ae6-58ea-9037-fca09a5a3f17 | note | Verifying Document - IANZ Accredited Report
2d01e3e6-3979-5213-a22a-01e858b9f12e | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
12fdc44b-c78d-5396-9996-405fc87e7eb7 | note | ○ Results to Engineer 2 wks before importing
af513736-3bf0-5ce3-ad8f-3a5b490deced | note | Verification Activity: Activity - HP
3e4140e2-6dde-5486-891b-ffabda7a58f2 | note | Verification Activity: By - ENG
b0a57ce0-f5de-4eba-91d6-a9c0e152c6b2 | signoff | AUTHORITY HOLDPOINT
84ce937f-00d8-4f0f-980f-1996834e6477 | checkpoint | 1.4.1 - Particle Size Distribution
7895f2cd-90de-5c0f-a39b-aaa9f632f343 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
5c238bf8-3f81-5a20-817e-c874590061b0 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
4c30c0e5-1300-5360-a4cc-2cba52787d99 | note | 63.0mm ¦¦ 100% passing
715912a0-c8b9-58ac-9302-8e3d69e67578 | note | 37.5mm ¦¦ 68-90% passing
5e1cc847-e2fa-5fd9-8770-831febf63afb | note | 19.0mm ¦¦ 42-76% passing
c16a9865-a98f-50a0-9c56-a052a80d5702 | note | 9.5mm ¦¦ 26-58% passing
d1a2c189-dd5d-56fc-9004-6e9cafe896c7 | note | 4.75mm ¦¦16-44% passing
dd193eb7-7aa9-5d5d-8fd9-c42ef65190ff | note | 2.36mm ¦¦ 10-33% passing
43041df6-c37b-5839-a0ab-ccb82a79b757 | note | 1.18mm ¦¦ 6-24% passing
a8016350-987c-5a14-b675-b4a1c7c13174 | note | 0.425mm ¦¦3-14% passing
dc58cefc-5612-55a9-9b1c-801690d6d9cc | note | 0.075mm ¦¦1-6% passing
f9d90ebc-e576-5c22-aedd-1c95423e8424 | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
74975767-7df2-5fe2-a437-040a22694471 | note | Verifying Document - IANZ Accredited Report
aa95280a-72d5-5878-ad12-8802ef11ebe9 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
e547be75-040d-57a9-b86b-1e920d5a64f1 | note | ○ 0-400 - 2 tests
e4832fac-892d-5a21-b53d-799b4333dba5 | note | ○ 400-1,500 - 3 tests
889b332c-bb80-5a77-add4-96b8a20f80d5 | note | ○ 1,500-4,000 - 4 tests
458bdc50-a1a1-5ca4-9f25-4b7ed321d5eb | note | ○ >4,000 - 1 test for each additional 1,000m3
2887f123-c576-53a8-ad6a-81605eca05d3 | note | – Results to Engineer 2 wks before importing
ef75cc4b-4bb1-5ae8-a9cd-3853581ad2b6 | note | Verification Activity: Activity - HP
757ec61a-e269-5393-a0b1-ffe8cd1ec785 | note | Verification Activity: By - ENG
6cd596a1-8c1c-46b8-9ffa-056b4335015a | signoff | AUTHORITY HOLDPOINT
aaa833a9-8f35-4b49-b5b0-b6f0b52eaf7b | checkpoint | 1.4.2 - Maximum Dry Density and Optimum Water Content
d61f12ba-820a-5faf-b030-3012aa44ddbb | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
7d4d3917-e5dc-53ac-ad7e-e98861fd9c94 | note | Acceptance / Conformance Criteria - Report Value Only
0f7af876-fed9-54fd-9824-4f869a9e3640 | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
37a77de1-fa1d-5851-af5f-ec58d17a0511 | note | Verifying Document - IANZ Accredited Report
06f890a9-2ee3-5765-9add-f8c7f528aac3 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e4475203-b60b-50c4-b14a-38e9736b8f39 | note | ○ Results to Engineer 2 wks before importing
63c9111a-aed9-5c0c-917e-6dec5cefd079 | note | Verification Activity: Activity - HP
fed05df6-ab17-543c-81de-8dfe3b00f90c | note | Verification Activity: By - ENG
d52eefad-8999-43c3-b9bb-1fc50f15a647 | signoff | AUTHORITY HOLDPOINT
5bbea343-4579-4e6b-b55e-c155885e6a79 | checkpoint | 1.4.3 - Plasticity Index
819b93e2-3dc7-5439-95d6-bac2a2da5779 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
9c416763-66a0-5111-a8a5-15e6f7abf4ae | note | ○ NZS4407:2015, Test 3.3 Plastic Limit
176298bd-7a4a-5fce-a39b-aa344471e846 | note | ○ NZS4407:2015, Test 3.4 Plasticity Index
934bf26d-74ae-582b-9d11-3b8c8fda4589 | note | Acceptance / Conformance Criteria - CHAR(LESS)8
31db2b27-276b-5e3a-a33c-1cfc6d52a58a | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
ed21fa5e-829c-5df3-9dc1-8b2d86272526 | note | Verifying Document - IANZ Accredited Report
abd87235-7204-5023-a60c-8896b50bf5fb | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
f93d2264-e2bf-54bb-8e05-926e485dff20 | note | ○ Results to Engineer 2 wks before importing
1e886391-77d8-53ec-8f32-ae58dd5142a1 | note | Verification Activity: Activity - HP
e362c0d5-f50f-52d6-845c-e7cf159c60af | note | Verification Activity: By - ENG
5ca28087-c2fb-407a-8b1d-23be67ec9cc3 | signoff | AUTHORITY HOLDPOINT
75eef8d4-2e1a-4c33-861c-e44fa2400e7b | checkpoint | 1.4.4 - Sand Equivalent
877ce2e8-cdcf-5920-b064-e2a264c7384c | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
f72728df-4d9d-5757-8be0-a2ab7b0774f1 | note | Acceptance / Conformance Criteria - >25
6900cf37-4af9-5f45-b9de-7449944f105a | note | Standard / Specification - NZS4407:2015, Test 3.10, IT-4.7.1
caf85dc8-d453-5fb8-8868-eb7ad52e9847 | note | Verifying Document - IANZ Accredited Report
c57e853e-8efb-5bbe-acff-71756a940a84 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
f831fedc-bd2b-5023-ba23-1ba1fe03fcb3 | note | ○ Results to Engineer 2 wks before importing
8770783b-fda9-5be0-b752-94103b313c13 | note | Verification Activity: Activity - HP
ae7d3eac-5542-5f7f-9c6d-8a1d8f31ca50 | note | Verification Activity: By - ENG
942b247d-abf0-43fe-99af-8ddc3c2b6681 | signoff | AUTHORITY HOLDPOINT
6e34fa20-8afc-4f8a-96f0-3d72b26cef67 | checkpoint | 1.5.1 - Crushing Resistance
e131fe21-d024-55c3-8fac-a52c1d2afb3c | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
815deff8-fe97-5108-b094-bb86c700ef6a | note | Acceptance / Conformance Criteria - CHAR(LESS) 10% fines passing 2.36mm under a load of 130kN
61959e39-60eb-5a2d-83a1-4eb4ff389639 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
45821b02-4a10-5a32-8768-3b3a1eb47f1a | note | Verifying Document - IANZ Accredited Report
c285e0a1-2646-5e4b-958f-924fe7ce73f9 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
cc3a6725-dff4-573e-a858-b800618ab98e | note | ○ Results to Engineer 2 wks before importing
1b26618f-733b-5ac0-a7cd-d0a5f838ee44 | note | Verification Activity: Activity - HP
ecdc51b4-5b0a-511f-9ec3-04ddb6b79d48 | note | Verification Activity: By - ENG
c891821a-b577-47b7-ad6d-1f866a52f607 | signoff | AUTHORITY HOLDPOINT
9c0100b4-082b-4378-bf5f-fdee2aa240e1 | checkpoint | 1.5.2 - Soaked CBR
7285ffb3-29e2-5026-9a07-adacbb762321 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
ca4daf93-e0dc-510c-a4b9-d1e57ee69b90 | note | Acceptance / Conformance Criteria - ≥ 60%
c9ee7e47-1006-562b-93b3-5cef453f70c4 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
745bf7e0-0f20-5599-a226-fde9f569de87 | note | Verifying Document - IANZ Accredited Report
de253071-5829-5d6f-bb84-dd3370ff70bd | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
2c3b7a13-8646-58aa-b9bf-b5882c1ec16f | note | ○ Results to Engineer 2 wks before importing
20249e05-c006-55c4-a38e-e6ee52cbbd02 | note | Verification Activity: Activity - HP
b08de8d5-8263-5e1d-a862-375557c202ed | note | Verification Activity: By - ENG
a95ad7a2-7cb2-4625-b0a1-3b814a209c21 | signoff | AUTHORITY HOLDPOINT
2ce9721c-1ef4-4a53-a187-4b54ff81963e | checkpoint | 1.5.3 - Weathering Resistance
2ddae53d-ec4b-5df0-9a45-43851f8f0ce5 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
7b01dd84-503f-5bc8-864a-f63e1d4a9620 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
bfab5628-7e5e-5c86-aaf8-f5f3af3f700f | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
6c6473df-f7ef-5662-ae40-e932a47be81e | note | Verifying Document - IANZ Accredited Report
3de58d73-e005-5a79-bdc3-9b3f0f973bf8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
97c614b6-096f-521d-afba-069b6e834296 | note | ○ Results to Engineer 2 wks before importing
1e8db603-97bd-50cc-a65b-db72f790dcf6 | note | Verification Activity: Activity - HP
16c13235-f0d3-58a8-9e05-880cf595c445 | note | Verification Activity: By - ENG
7e20329c-d56c-4c2f-9dde-4d88ad62c48e | signoff | AUTHORITY HOLDPOINT
d74123dc-76c7-4b62-91c3-ecb763f0f063 | checkpoint | 1.6.1 - Particle Size Distribution
2dbd4b84-0056-50ab-bbd5-6aaf28328942 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
24fb828a-a638-559d-b51d-51a3425a0b0f | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
6ab5732f-1c42-53f8-ae69-63ee9cd9b459 | note | 63.0mm ¦¦ 100% passing
ed0e2f50-57bf-529c-b0c3-fe0c0792eb5a | note | 37.5mm ¦¦ 55-85% passing
71a26dd5-dfb3-5c72-869f-9a8e2b5535ce | note | 19.0mm ¦¦ 33-65% passing
6807465c-b479-5050-8f14-fe7edd56061a | note | 9.5mm ¦¦ 20-50% passing
98d8d3b7-537d-5097-9ce8-9892ac87e850 | note | 4.75mm ¦¦ 10-36% passing
9b43b857-c1d8-5157-a763-8ac8478ad5e2 | note | 2.36mm ¦¦ 5-27% passing
3f1de623-7ea0-5e7f-992d-4fe451a65ca1 | note | 1.18mm ¦¦ 2-20% passing
457d716d-b795-5972-9680-37cdc3dc2ec4 | note | 0.425mm ¦¦ 1-13% passing
c585e5f3-f22a-51b4-a136-ea6f6b2d81e7 | note | 0.075mm ¦¦ 6% max passing
216cf3a9-0701-59e6-8ec6-a350a09b1174 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
646308dd-560a-5f48-b383-90789b7d9df0 | note | Verifying Document - IANZ Accredited Report
7fb4e3e7-17d5-516d-8668-a2cffcd73255 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
8e50c704-3834-54fc-a7ee-f89fc6956d40 | note | ○ 0-400 - 2 tests
1650012b-de4d-5d8e-a4b7-400f1159d7ef | note | ○ 400-1,500 - 3 tests
efccbeb7-a1e9-5330-88f8-4e13bc1e62e7 | note | ○ 1,500-4,000 - 4 tests
8cef93e3-b9af-5497-8c69-146cbd3b4854 | note | ○ >4,000 - 1 test for each additional 1,000m3
f8c92a58-6c5e-565f-8c52-df76e216d5c6 | note | – Results to Engineer 2 wks before importing
d4dd0be3-8f94-5da0-9a89-5577570e0272 | note | Verification Activity: Activity - HP
4b76a864-0685-5d93-bbb6-dd76ea1d4883 | note | Verification Activity: By - ENG
5a550892-1755-497f-8e7b-8236a83bca49 | signoff | AUTHORITY HOLDPOINT
75c3ef89-4abe-4ba2-aef0-ce1acc08854f | checkpoint | 1.6.2 - Shape Control
766ee7a7-8b0a-53f0-806c-60ab553496ff | note | Detail - Tolerance allowed from approved grading curve (%)
7662daaa-27b8-5ab8-8d7e-9de356fcaf96 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
5a28c09c-82d6-5dc9-9113-e0bfc0f11d1d | note | 37.5 – 9.5 ¦¦ 34-50%
404df8b9-a435-5381-b532-6958bbffdb9c | note | 19.0 – 4.75 ¦¦ 18-40%
678b4f38-4ba1-573e-89e3-dff5a60fb052 | note | 9.5 – 2.36 ¦¦ 12-32%
6df99e9d-7fcf-5389-b27e-7968758c305f | note | 4.75 – 1.18 ¦¦ 6-24%
c612298b-9636-5e4f-9f1c-067b8eba122a | note | 2.36 – 0.6 ¦¦ 2-20%
3cdaea46-fd87-5da8-9210-00dc5c2364b3 | note | 1.18 – 0.3 ¦¦ 0-15%
dbee2eaa-570a-56c1-930e-40bb07738853 | note | 0.6 – 0.15 ¦¦ 0-12%
3536d19c-824c-5f37-afe8-05a8da200a0d | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
a5da914b-87c8-52fa-95ab-a4269a482600 | note | Verifying Document - IANZ Accredited Report
190b042e-a684-51df-8b80-267cc5137979 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
be335fd4-55e2-5db5-8ea7-09124f3a9e3a | note | ○ 0-400 - 2 tests
b37b0c8c-597d-5f8d-973e-37e33eaa3e35 | note | ○ 400-1,500 - 3 tests
e3421f9d-081b-58de-b39e-5e50d4772f73 | note | ○ 1,500-4,000 - 4 tests
f658218d-6ab6-58e8-89d0-0439968fe94c | note | ○ >4,000 - 1 test for each additional 1,000m3
c2f4d4fe-72f1-56d7-91a0-e4a56366b626 | note | – Results to Engineer 2 wks before importing
b891d7f6-b6a3-51c0-8c73-ac0b3cf4557a | note | Verification Activity: Activity - HP
39c92ca0-a9d5-5340-8df9-d6c525979dfa | note | Verification Activity: By - ENG
78aefa48-4f50-403e-9d75-8413bae2141e | signoff | AUTHORITY HOLDPOINT
e9f3d5c3-f804-4665-a6b2-85e6773ca7cb | checkpoint | 1.6.3 - Sand Equivalent
729288d4-16c5-570b-9acf-ae86f051450d | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
af7134d4-c827-5a37-a31e-8b8325155900 | note | Acceptance / Conformance Criteria - ≥ 30
eb3a043b-c01d-59fa-ae80-5598f2bb1846 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
8b4407c7-c542-5bbd-8995-83771d975697 | note | Verifying Document - IANZ Accredited Report
e51a6f0f-983d-504f-9906-7bdd3dbb6894 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
e305e4b5-2405-5597-b4cc-8fa7eec59f56 | note | ○ 0-400 - 2 tests
95c28d4c-aa63-5668-b397-6e333a3b5438 | note | ○ 400-1,500 - 3 tests
f921661b-4568-5c64-a70e-55678150883c | note | ○ 1,500-4,000 - 4 tests
d85cf8d7-58f7-5031-ba91-e5fd88d8f8e1 | note | ○ >4,000 - 1 test for each additional 1,000m3
61b07e47-99a7-5bfb-8790-5b0fc3fcbfb7 | note | – Results to Engineer 2 wks before importing
a6b456a2-08c2-583b-ac05-cf38ddd117f6 | note | Verification Activity: Activity - HP
30fc6d25-5ce7-536b-9b86-930fe6a2abe0 | note | Verification Activity: By - ENG
b19cadc7-8354-4b65-a3d7-b8d3b1dfe3c8 | signoff | AUTHORITY HOLDPOINT
be69c8ea-2203-482d-a4e1-dbdedf629bfd | checkpoint | 1.6.4 - Cone Penetrometer Limit
ea9baf95-08db-5622-9df7-24f2c3cb34e2 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
31199459-71aa-599f-ba0d-511abbac28a3 | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 25
33c35720-c487-5df4-b59d-e3e47ec78dbd | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
cf2a18f6-5464-55e5-b844-1c248fcffd6a | note | Verifying Document - IANZ Accredited Report
3e04041f-56a3-5e5b-b44e-b9614aaebd02 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
48fdf0d8-3361-5838-ba79-7ffb0ddd6ff2 | note | ○ 0-400 - 2 tests
f245e0dc-ebc7-5adf-9c6d-8d7c8fda76fc | note | ○ 400-1,500 - 3 tests
ed88dd84-59e6-5cb1-a02f-8f63149e818c | note | ○ 1,500-4,000 - 4 tests
16862536-f9b3-54a1-9ec7-47c12c8ff998 | note | ○ >4,000 - 1 test for each additional 1,000m3
025e0db2-4801-50ce-b727-09fa2e157fe7 | note | – Results to Engineer 2 wks before importing
7596e727-8373-5f59-ae2f-6192137d09b0 | note | Verification Activity: Activity - HP
78326b0c-7cf4-5b90-8eaa-34c18c587824 | note | Verification Activity: By - ENG
01ac2316-2846-4144-87f2-984d2b9d923b | signoff | AUTHORITY HOLDPOINT
6f7ef984-f38f-4003-ae84-c1b22b0ab6c9 | checkpoint | 1.6.5 - Plasticity Index
1b535943-bfd6-5c37-bc31-33ffa43efab8 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
1d9996d0-840c-5f8a-952e-a7f28a8ec081 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
580de0e9-0255-5e72-bb28-fab1ad777875 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
f34f1f45-1588-5b42-b28e-c9a02820a9e1 | note | Verifying Document - IANZ Accredited Report
0375bba4-84ee-5374-b475-35aafe236724 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
a9efc352-2aa0-5d3c-9287-dc19a4a0ee0a | note | ○ 0-400 - 2 tests
2d4e3180-db8e-531a-9596-5b05443099f1 | note | ○ 400-1,500 - 3 tests
f0b276b3-58d0-5392-b73a-94885173e70c | note | ○ 1,500-4,000 - 4 tests
33d5a6b8-495f-5d6b-8084-b5464432b810 | note | ○ >4,000 - 1 test for each additional 1,000m3
d1de1a9d-b989-5724-a506-bcc0ef76d346 | note | – Results to Engineer 2 wks before importing
80955355-f0f5-55a1-bf21-dcd43fdfec0a | note | Verification Activity: Activity - HP
890aec0b-ec30-5870-b52f-d2ab566e4b10 | note | Verification Activity: By - ENG
7a1ee926-b44e-481a-9bef-fc911869b1ff | signoff | AUTHORITY HOLDPOINT
8535c52a-0900-4528-a550-e3fb264c4bdf | checkpoint | 1.6.6 - Accelerated Weathering
ab64b827-62e8-5803-8056-ebcb7eeaf84f | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
99a6536d-1471-53d1-b5cc-027ee7878db9 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
60b9ef9c-310a-5a90-b1a6-cd10f36855fd | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
a32608b1-05a3-55a2-8827-a69dda621bc9 | note | Verifying Document - IANZ Accredited Report
ede01c5d-c682-5fc9-835f-34c20f748685 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
dedf45b9-67a4-57c8-b4d9-b0f2ea8e5f95 | note | ○ 0-400 - 2 tests
1aa0aed2-e551-5a26-8064-4930d2b89c46 | note | ○ 400-1,500 - 3 tests
b878bf86-39e0-5c46-b828-146c16ef6850 | note | ○ 1,500-4,000 - 4 tests
fe6b291b-8d74-5410-ac62-4961d285d7b3 | note | ○ >4,000 - 1 test for each additional 1,000m3
9691aa25-da65-5f10-89b8-324a6e9eaee9 | note | – Results to Engineer 2 wks before importing
014b3b48-b6ca-57d8-8c4b-dc9beaf3cc91 | note | Verification Activity: Activity - HP
215df7e7-b777-5145-bb8d-6af0a34133df | note | Verification Activity: By - ENG
af5f685c-2a60-4bf8-abfc-82d217ca3bfa | signoff | AUTHORITY HOLDPOINT
15b24c65-31a5-4a91-87da-0fad4814f92d | checkpoint | 1.6.7 - Maximum Dry Density and Optimum Water Content
e8a10689-b9b5-56ef-8bed-9042d6bb4972 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
2c68ad20-be87-5874-8807-729c290bd1df | note | Acceptance / Conformance Criteria - Report Value Only
dfd62d76-6d41-5dd3-b6ae-41d9ffc548fb | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
3d28f036-b43c-5198-b700-533dba745aec | note | Verifying Document - IANZ Accredited Report
669a4d7f-1fdf-5b02-adb9-b101702ae95a | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
44c4a8b7-7d9d-5f8c-a997-300cb0b02f9d | note | ○ Results to Engineer 2 wks before importing
18c12bca-ec0e-568e-9af7-ee5409e4fb3e | note | Verification Activity: Activity - HP
28f3b49c-2c6b-540a-b084-ba619027b62d | note | Verification Activity: By - ENG
164788f3-9178-453f-81d4-c21269535162 | signoff | AUTHORITY HOLDPOINT
ce265187-cc45-4380-a141-486a6aa2633d | section | SECTION 2 – CONSTRUCTION - SUBSOIL DRAINS
59ab6bea-5ce1-45c2-ad66-c2040dc8db29 | checkpoint | 2.1.1 - Subsoil Drain inspection
faca462f-9803-5643-ac3f-f29372355fb6 | note | Detail - Subsoils to be placed below kerb lines and inspected by Engineer
b53f623e-ffe5-57a3-8034-0018195d05d7 | note | Acceptance / Conformance Criteria - Engineers Approval
913d0a5b-006e-58d4-a66b-129b4e742f86 | note | Standard / Specification - PS 17.6.3
187e0a76-de29-54b0-aaa2-4985a86b69dc | note | Verifying Document - Hold point released
6a61b150-9342-5fb0-99e5-c2df3bca6480 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
be0c05c7-3118-5dee-a150-7f40d693b642 | note | Verification Activity: Activity - HP
6dfc7da5-8e20-5e64-8de3-8b46445bfe08 | note | Verification Activity: By - ENG
baf18c65-8bcc-47db-87a0-b01157244acd | signoff | AUTHORITY HOLDPOINT
0548486b-c272-4340-8d46-31d80128c615 | checkpoint | 2.1.1 - Excavation
9d7ef01c-faa4-51bd-ace2-c50711548d48 | note | Detail - Excavtion of Trench should be within tolerances.
a2d0fa21-1c83-562d-b77c-0c3a71ac0648 | note | Acceptance / Conformance Criteria - 335mm deep x 300mm wide
55295b82-55cd-5cfd-b352-de0f14d9dcbc | note | Standard / Specification - Drawings
d81915a4-c4f0-50ff-8d09-e96eac1448f0 | note | Verifying Document - Subsoil Checksheet
674646a0-38a5-545e-9840-9f4e60ae95be | note | Testing Quantity Required (based from schedule qtys) - During construction
ba187616-da5f-59fc-a82c-947093d56084 | note | Verification Activity: Activity - M
4ae2a69c-f028-5445-bd91-0fc0630cd33d | note | Verification Activity: By - SE
6dba4ca6-03d9-4c7a-8a91-a502f644a4c3 | checkpoint | 2.1.2 - Placement of Bidim
37b02e52-a039-573a-a97e-df204e3bda0d | note | Detail - A29 Bidim to be placed andd wrapped around Trench.
3de1ee50-e990-5679-a9a7-7f55d38cce92 | note | Acceptance / Conformance Criteria - Minimum Width 300mm.
86e50d23-acac-591c-8c81-81dfddae6399 | note | Standard / Specification - Drawings
a8705621-13be-5ee4-b53a-c8406c267014 | note | Verifying Document - Subsoil Checksheet
9d58f436-d701-5bc1-a1c3-14b022782c73 | note | Testing Quantity Required (based from schedule qtys) - During construction
3d4afc35-1f1c-55d3-b01b-1e9f399aa40a | note | Verification Activity: Activity - M
cf954825-31bf-5971-9381-c56fb1cff531 | note | Verification Activity: By - SE
7d4a2fe9-9c55-45a3-88d9-6e572c6a433b | checkpoint | 2.1.3 - Cushion (Bedding)
63f42823-9144-5a07-94f6-5bf7c5577480 | note | Detail - Pipe must have 75mm of Cushion. Drainage 60:40 Material to be used.
482f1343-77b3-5156-8294-395b74972f0b | note | Acceptance / Conformance Criteria - Minimum 75mm
3146895f-40db-5558-9b96-a9f3f14c8106 | note | Standard / Specification - Drawings
d649a585-2c49-5f1f-a40d-fdea5a7cc56d | note | Verifying Document - Subsoil Checksheet
f9d4e642-f8bc-5e38-998b-43fdd87f750b | note | Testing Quantity Required (based from schedule qtys) - During construction
c01c3f83-121a-55c9-a18e-d187f0f45b36 | note | Verification Activity: Activity - M
1566b6a0-4f13-585a-9583-79b3ff4c7079 | note | Verification Activity: By - SE
dcca4c19-b510-467a-b0c6-28b34bc9050a | checkpoint | 2.1.5 - Placement of Pipe
04a24fd1-ed8a-5f16-b38f-16945a92d4f7 | note | Detail - 110mm Perforated Pipe to be laid Down
cb157a35-c38f-5125-946d-2a56c47105df | note | Acceptance / Conformance Criteria - As Per Drawings
4cd6747a-4117-5014-83f6-836a7ea6ba56 | note | Standard / Specification - Drawings
ecb7ee78-d900-5b6d-a5dd-81048be8b0b0 | note | Verifying Document - Subsoil Checksheet
acfcce70-bf84-54d8-9ad4-3694890b2f3c | note | Testing Quantity Required (based from schedule qtys) - During construction
0ea57d40-11e3-5789-b4b0-066ed77b6e24 | note | Verification Activity: Activity - M
02174d0b-7d56-5cde-8117-80282644b510 | note | Verification Activity: By - SE
7c9651a7-5dad-497d-a8bb-44dd3e8581a0 | checkpoint | 2.1.6 - Backfill
61814940-665e-518b-bab0-bb7966501e2f | note | Detail - Pipe Must have a 150mm cover from Bottom of Pavement. Drainage 60:40 Material to be used.
094e5138-e4b5-5fb9-a3f4-83a76067adf9 | note | Acceptance / Conformance Criteria - >150mm Cover
3e6456c9-7d7f-507f-ab91-1572ea5dc898 | note | Standard / Specification - Drawings
b6c3feea-86e3-500e-a2b0-428e048ac5ce | note | Verifying Document - Subsoil Checksheet
639259b5-5660-5f46-8232-6e01064662f9 | note | Testing Quantity Required (based from schedule qtys) - During construction
1dda0991-50b8-584b-8df2-d35ab84024c3 | note | Verification Activity: Activity - M
c2fa25d6-ee17-56d9-8963-74e610174324 | note | Verification Activity: By - SE
9e2e06b9-af76-4d45-9311-b275fc28da08 | section | SECTION 3 – CONSTRUCTION : PLACEMENT OF GEOGRID AND GEOTEXTILE FABRIC
7991c873-b9be-4435-9f4d-1e21b9e46f63 | checkpoint | 3.1.1 - Placement of Geotextile Fabric
9a907af2-9548-51b0-be36-559c0d62dc81 | note | Detail - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
79f48c76-a3d1-5f24-8459-87a892c65294 | note | Acceptance / Conformance Criteria - Visual inspection
e280bc28-cb21-50e6-9857-d8141263f843 | note | Standard / Specification - NTC0097
a9186e75-2a6e-5fca-8fd0-6b3e8fcb3b36 | note | Verifying Document - Visual Inspection
c4bf1a07-5893-515e-ae2b-4c5cff8bbb2e | note | Testing Quantity Required (based from schedule qtys) - During construction
0b522e71-bbd7-5eef-b1da-0cc15a2c7954 | note | Verification Activity: Activity - WP
7f6900e5-9453-5fc0-a64d-074e0d17c2a9 | note | Verification Activity: By - ENG
521f4fcb-397d-4cd5-98c5-a461954c95a6 | checkpoint | 3.1.2 - Onsite Check by Engineer on Geogrid
7442b31b-c22d-5807-8df5-73f6ab7725a4 | note | Detail - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
497a9a94-1631-5460-b1d4-97ee080fcee4 | note | Acceptance / Conformance Criteria - Visual inspection
f5e79a15-600b-5719-9efa-362ba4446fe9 | note | Standard / Specification - NTC0100
79851e56-4b8c-53b5-9669-4cb52b1fd9f4 | note | Verifying Document - Visual Inspection
f5765e3d-edfc-57dc-b508-c5bb6335e348 | note | Testing Quantity Required (based from schedule qtys) - During construction
7d486efc-a8f9-5d82-a0ac-18fcea7e6617 | note | Verification Activity: Activity - I
9327f636-8b72-5d30-95fa-d359d1ee6409 | note | Verification Activity: By - SE
ddbf0b1f-45f3-4af9-8c23-eb50d2dbe92d | checkpoint | 3.1.3 - Placement of Geogrid
c259e048-c281-5c02-a570-98cd9ab0125c | note | Detail - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
23bee63b-bd16-5f2a-9fa2-269061f1b7d9 | note | Acceptance / Conformance Criteria - Visual inspection
295df77c-09ea-58b4-8405-f747782d8c0e | note | Standard / Specification - NTC0100
aab10a6a-7500-5883-9e0c-80c950e780d7 | note | Verifying Document - Visual Inspection
7a386830-7710-512f-8d0d-7f1960c6fe7c | note | Testing Quantity Required (based from schedule qtys) - During construction
5600a4f3-afce-5298-8817-e3bebf0baf7a | note | Verification Activity: Activity - WP
1392d6ca-ad34-5050-9ff5-f9b1679cb9df | note | Verification Activity: By - ENG
127964ec-2d7d-4066-b123-cae87630484a | section | SECTION 4 – CONSTRUCTION : SUBGRADE IMPROVEMENT LAYER TESTING ( AP65-2)
30647f85-816d-4d73-b5e5-de15e1376bc0 | checkpoint | 4.1.1 - Plateau Density Test
0886119a-1ac9-5e41-b700-ab6f79df9098 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
a167bd44-bf22-57f7-a4dd-9e1979700a41 | note | Acceptance / Conformance Criteria - Plateau Density Report
d61ea61a-471a-5d92-b617-723f1fa84c45 | note | Standard / Specification - NZTA B/02 7.5
eb285d5f-ccaf-582f-a7a0-19678ee6906c | note | Verifying Document - IANZ Accredited Report
24d66a6a-46fe-5e96-94ee-ee447e9c18f6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
7f6acdc5-d56d-52a2-a6cc-90a5d9c53417 | note | Verification Activity: Activity - I
ef14d3b8-92ad-577b-9982-9820e9c9b32d | note | Verification Activity: By - SE
a889ff4c-198e-4a73-9b07-4a35ff46d2fb | checkpoint | 4.2.1 - 3m Straight Edge
4d3eb178-4c22-50bf-922b-f0765d9ecb65 | note | Detail - Formation check to ensure surface is smooth
e4fce76b-0c39-5d45-94ee-a9775b4a0743 | note | Acceptance / Conformance Criteria - +/- 10mm
e4a13044-de2a-5d5c-8bd9-2d69327185b7 | note | Standard / Specification - TNZ B/2 7.7
34a34e3b-ba6e-5a70-922c-89d87e9f508b | note | Verifying Document - Check Sheet
41bc21cd-ca03-5ffc-b70d-dcdd35b7724b | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
de517fb1-9b20-5bac-9e94-d1483834f7dc | note | Verification Activity: Activity - I
e7af078e-9830-5c65-a977-39bb90b5b356 | note | Verification Activity: By - SE
67300741-e8bf-4e28-8327-6a96f65d640c | checkpoint | 4.3.1 - Stringlines or equivalent
e22da69b-9dd4-5c5c-927a-88f262eadfd7 | note | Detail - Stringlines or equivalent to check finished height of surface
21eff9a9-ff5b-53a3-96f0-b0016d42b719 | note | Acceptance / Conformance Criteria - -25mm + 5mm
cade9a84-3bfd-5a78-bdec-59becb1d8d21 | note | Standard / Specification - NZTA B/02 5.1
e6af0be1-9ce0-531c-b736-4e1f96c38be8 | note | Verifying Document - Check Sheet
d2cdf6a9-fb11-56dc-9417-78f10d6b4df1 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
b25f9948-f884-535b-8871-376a1f922f6b | note | ○ 1 set = 5 tests
01284851-227c-582e-9c3c-6499c8297a0a | note | Verification Activity: Activity - I
f5f5e12d-5e3f-537d-b121-8032db6c25df | note | Verification Activity: By - SE
bb2bdfbc-b609-4d05-bf45-9a711a384098 | checkpoint | 4.4.1 - Compaction - NDM
4f98f7a1-73f5-5106-b925-4bf7956a8839 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
6f23e39f-2d32-55b2-b258-cbcd3c60eafe | note | Acceptance / Conformance Criteria - Ave >95% of MDD
3b96606b-943c-5de0-bff8-248aa11085c3 | note | ○ Min >92% of MDD
6597f7a4-3609-579e-b4aa-0e34cccd4250 | note | Standard / Specification - NZTA B/02 7.6
f9187bec-9979-5637-a406-fcc782dfec68 | note | Verifying Document - IANZ Accredited Report
c5763032-e4f2-553f-95ce-e75bba484c22 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
14a81efb-6104-53fc-a2de-980945766b72 | note | Verification Activity: Activity - I
32dddbea-7dfc-5f65-bca0-e807956e2d6b | note | Verification Activity: By - SE
22463005-60ab-4690-9a2b-9720a9e56133 | checkpoint | 4.4.2 - Benkelmen Beam
a0c99f7e-efc7-5a30-b8ee-244b9fb9634a | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane. Unbound layer.
b7ac8255-4b25-52af-a041-79d1a0192e0b | note | Acceptance / Conformance Criteria - 90th Percetile: 1.90mm
2b90ccb4-ad01-5e6c-a4e2-3e66ab798cc2 | note | ○ Maximum: 2.34mm
49d8d7a8-c6d2-5a1a-b643-f681d2e35091 | note | Standard / Specification - PS 20.14.5, NTC0160
2a8947c9-0121-557f-8d1b-c3acd94a17e0 | note | Verifying Document - IANZ Accredited Report
31fcaa89-b896-56a3-858a-7dc896239f1c | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
c95951fc-390a-51ea-8e47-421f2c902d78 | note | Verification Activity: Activity - HP
f415f5d8-cc6d-5f97-aa03-b762b5d0b021 | note | Verification Activity: By - ENG
0c5b877d-4710-476d-8382-a4b41e887097 | signoff | AUTHORITY HOLDPOINT
22c49809-8fd8-4ddc-b99d-605c1af55ae3 | section | SECTION 5 – CONSTRUCTION: Subbase Layer Construction (AP65-1)
5c5a3154-3479-4f5e-ac5c-ec0bce4a35f9 | checkpoint | 5.1.1 - Plateau Density Test
99d6db84-15d4-51bd-8989-4c21a311a909 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
c2ed500f-8757-50f0-be29-38c246210e42 | note | Acceptance / Conformance Criteria - Plateau Density Report
9f386eab-91ef-5899-a70c-4c7376d59846 | note | Standard / Specification - NZTA B/02 7.5
8974ff98-8c42-5594-90d0-830e0703f17f | note | Verifying Document - IANZ Accredited Report
f6c6765e-09f2-5ec2-ae25-e6c5db607482 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
0a8d73fa-da94-509d-99bc-e2fd8af2f787 | note | Verification Activity: Activity - I
e8088411-f21d-5748-bbf3-f2e7522654c4 | note | Verification Activity: By - SE
ea9f20ff-1376-4558-98c7-c96aa07c3728 | checkpoint | 5.1.2 - 3m Straight Edge
1e8599ee-c773-52fb-8e05-5d40837e7842 | note | Detail - Formation check to ensure surface is smooth
4e453819-783a-5fd1-a305-8413c27f87da | note | Acceptance / Conformance Criteria - +/- 10mm
55700783-70d6-550f-a0fb-b0af625d2740 | note | Standard / Specification - TNZ B/2 7.7
f3c56a9a-97f8-51ea-946f-fdcc35159f9c | note | Verifying Document - Check Sheet
d10f7368-a30f-574b-92e2-f909e56222cd | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
b4966300-b4d0-5368-8e4a-96ab89a9e418 | note | Verification Activity: Activity - I
0e6dbd8e-17f6-5ac3-a80b-d73718f1e6f9 | note | Verification Activity: By - SE
b7695ffe-cd35-44e3-a32e-4a77f1a7fae9 | checkpoint | 5.1.3 - Stringlines or equivalent
399a769b-3da1-54a4-b5e8-0f585494c6db | note | Detail - Stringlines or equivalent to check finished height of surface
4a44ecf9-7fd6-5495-886c-9cc1bd6a8459 | note | Acceptance / Conformance Criteria - -15mm + 0mm
dd162c8c-7443-5592-80b6-7745c4bb096e | note | Standard / Specification - NZTA B/02 5.1
4d65d49c-21f5-582d-9cf7-447ffb9cc67b | note | Verifying Document - Check Sheet
c440f52c-9f3c-580c-844c-33fdfd46c55f | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
075c2f45-5e03-531c-92fb-d499b2214671 | note | ○ 1 set = 5 tests
d0c82b06-6562-538b-abef-968ea2889b6a | note | Verification Activity: Activity - I
472c0ba3-2388-5eaa-8f41-504897c7197d | note | Verification Activity: By - SE
4e594c7e-76b1-44f8-8365-718799b782a8 | checkpoint | 5.1.4 - Compaction - NDM
a38890e9-e297-5a17-821d-f46d225ccc6d | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
1c0d9664-0925-5f2e-be8d-45a7acaeba83 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
d5b0b29e-b37a-55b5-9b3c-fce9a642c45b | note | ○ Min >92% of MDD
45f9fdbc-47ea-58ca-ac69-6b94be8f1865 | note | Standard / Specification - NZTA B/02 7.6
114a1a30-1d31-5909-b05d-0109d2c08113 | note | Verifying Document - IANZ Accredited Report
94d7509d-7ffc-5970-b6cb-b64c76797817 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
caf6f3a2-3f4f-56b5-a96c-71928848e941 | note | Verification Activity: Activity - I
0f2bbfc2-deb6-5728-80db-05c245ad021a | note | Verification Activity: By - SE
c7dc3d62-ebec-4026-8629-a44848b00f11 | checkpoint | 5.1.5 - Benkelmen Beam
07271896-fbb4-5d14-a257-5df4ede19ada | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
b823be12-d796-562b-b746-c7b2a9f5f8e0 | note | Acceptance / Conformance Criteria - 90th Percentile: 1.41mm
ce561325-24f5-5a7a-95a2-6de09e129fe0 | note | ○ Maximum: 1.74mm
de6ad317-9bed-51e8-9efe-f712b4384988 | note | Standard / Specification - PS 20.14.5, NTC0160
2d0234cf-94ed-5427-9522-eefbb0de73f1 | note | Verifying Document - Test Report
22ae926e-782b-54bf-9dff-4ecab429c063 | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
be3b192a-b4ab-539a-bb5b-b10249c7b00f | note | Verification Activity: Activity - HP
ffe3cdbd-17bc-55d5-9cfb-063b0025fd64 | note | Verification Activity: By - ENG
9ca0fc90-401f-4d2e-8661-3a7133a34e68 | signoff | AUTHORITY HOLDPOINT
6d987937-8701-4daa-88ed-618cafecb40c | section | SECTION 7 – CONSTRUCTION: KERB & CHANNEL PREPARATION
90bb50b4-95dc-47f0-b3d0-be2000405aaa | checkpoint | 7.1.1 - Stringlines or equivalent
566db037-c02f-5aa4-a519-14d2858fc93d | note | Detail - Stringlines or equivalent to check height of surface prep
b7382724-0fb2-56eb-9a7e-c1295507c74e | note | Acceptance / Conformance Criteria - +/-5mm
0bc39c8c-895b-5e0a-9fff-2db6720190bc | note | Standard / Specification - PS 21.7.6
70935406-c954-5296-88f1-7badc108bf2b | note | Verifying Document - Check Sheet
316a824c-ebb4-5ddf-8e10-e7d8a96142bd | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
6e4661b2-6d17-535f-a227-63bcc2a75305 | note | Verification Activity: Activity - I
354e6d99-ae1d-5b7e-995f-eb20eb90505a | note | Verification Activity: By - SE
dad30302-8c1c-4648-a966-afb02d086c58 | checkpoint | 7.2.1 - Compaction - Clegg Hammer
03fc92ec-d697-50de-8298-8b9fba84c2ad | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
9542bd9f-29a8-52ea-9792-13d1a8396662 | note | Acceptance / Conformance Criteria - Min 25 CIV
569d2542-3809-5e13-99e7-8b7180a548c1 | note | Verifying Document - Clegg Hammer Report
552824d6-6e09-5e54-9a83-912b6fdeb585 | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
14a0f89e-c422-5b55-87cb-5388d842e9f5 | note | Verification Activity: Activity - I
65afc6cd-f933-5186-94bf-f143b459707f | note | Verification Activity: By - SE
067d5f7c-96a8-4979-b8f3-564f4888c7d9 | section | SECTION 8 – AS-BUILTS / REDPEN MARKUPS
504e3c2b-8cf7-4f8b-8898-43d7bf470649 | checkpoint | 8.1 - As-Builts/ Red pen markup
d2272896-8680-5340-9c8c-6a44db1c05a4 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
e8ad02cc-b365-5a56-8bbc-a01bd4c525e6 | note | Standard / Specification - PS 16.7.6
e9e480c4-1a06-540a-9b97-def5732cfe6c | note | Verifying Document - Red pen markups
bfc3ebb4-e7f0-53d6-9e1d-79d6d1d6c80a | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
c2db5e3f-55b6-59a8-8ce9-7df11ffe8eb2 | note | Verification Activity: Activity - D
ffa58b21-0009-571d-ab96-ba5fdd357150 | note | Verification Activity: By - SV/SE
84cc4b15-6033-4e9f-ba85-2f9ed807ab99 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
5ca6d8ca-4340-51a5-abc3-d3a5e1dadecf | textbox | Contractor's Rep Name:
f398ed0a-dcd3-557c-9b74-1cdd5a448c0c | textbox | Engineer's Rep. Name:
788cf626-77b0-5d44-a4e0-8b04028a8532 | date | Date:
35fff924-87c2-4177-8721-3171169aa9ee | signoff | Add Signature
33b12352-cf45-45fc-b625-49e1f039a882 | checklist | DN1210-031 ITP Pavements Type 09 Rev 0 | itp | DN1210-031 ITP Pavements Type 09
0536b4a9-98cd-4e3f-a47a-41885fa7aa51 | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
c5f5486c-02dd-4574-9ee3-b437383575b1 | checkpoint | 1.1.1 - Material grading: PSD Materials GAP20
61952d65-874a-59a5-a452-a27e84d6934c | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
01045525-500e-5910-9668-f859348952bc | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
b81e5cbb-35c6-5a07-89b1-b0d3b13418ed | note | 19.0mm ¦¦ 100% passing
7af807ce-6a0e-539f-8b38-07bdbad793ea | note | 9.5mm ¦¦ 52-76% passing
324cb925-4415-51ac-b95b-4ade144cc043 | note | 4.75mm ¦¦ 33-57% passing
a07c1d85-4ba0-5068-890e-a29c357196ed | note | 2.36mm ¦¦ 20-44% passing
cce6c9e8-d837-575e-b281-cfe484bdcd9d | note | 1.18mm ¦¦ 12-35% passing
134fa116-4938-5f53-9d79-3fdf85c34736 | note | 0.600mm ¦¦ 7-25% Passing
c802abc2-10a8-5b21-8e6c-dde320b498b1 | note | 0.300mm ¦¦ 4-20%Passing
e4e54688-8f23-531b-8a96-f2070456f2c8 | note | 0.150mm ¦¦ 0-12% passing
11ba6571-aaf4-5827-b45c-4202821c3fe3 | note | 0.075mm ¦¦ 0-8% passing
1459fb11-1294-57d9-8c7e-4e5532e49d24 | note | Standard / Specification - NZS4407:2015 Test 3.10
493517ba-debb-5e35-b563-943bfe60bd6c | note | Verifying Document - IANZ Accredited Report
03f075c8-a09c-541f-99d8-898102de724f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
5b45e722-7208-5085-b31f-15ff3c82d886 | note | Verification Activity: Activity - HP
58ee7560-c8fc-5c78-acf8-9f03d4b78b58 | note | Verification Activity: By - ENG
a7caa989-7911-4224-87fe-942b1ab9532d | signoff | AUTHORITY HOLDPOINT
f24ab076-a803-4cc4-bd8a-265e264fd823 | checkpoint | 1.1.2 - Weathering index: Materials GAP20
670e07f7-1a33-57f5-8aec-d851b713940e | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
d89690c5-623a-507e-ba1a-7445968c28ad | note | Acceptance / Conformance Criteria - CB,CC,CA.
be0a0ddf-268a-5f03-afac-f3bb2bb2b176 | note | Standard / Specification - NZS4407:2015 Test 3.11
133f7827-fd17-5aa4-b5fb-0ac507ce786c | note | Verifying Document - IANZ Accredited Report
640f8d57-c32f-5394-bd8c-3f528ebf2f5c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
e777cb51-2732-51e7-9873-e3320f20aace | note | Verification Activity: Activity - HP
c36c852d-daf7-547c-a336-c6e854fab248 | note | Verification Activity: By - ENG
79cb9f89-9596-4fe4-9b0e-4bb8e8da1958 | signoff | AUTHORITY HOLDPOINT
bdf0438e-5436-4232-b94f-a0cca40972b5 | checkpoint | 1.1.3 - Crushing Resistance: Materials GAP20
7c4b1b6b-d980-5b0f-8925-0f23bbe140e8 | note | Detail - Pavement layer on top of underpass
d614080b-223c-5ee1-815d-13fbea5a9789 | note | Acceptance / Conformance Criteria - Engineers Approval >100kN
befc619e-d075-5e97-a70a-6579400ab51d | note | Standard / Specification - PS-21.7.2
f0511766-15a6-5bc4-8241-295f9b80792f | note | Verifying Document - IANZ Accredited Report
c980e8f0-0d0e-58c8-ac81-08c0f745c189 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
c38b5cd8-ea97-5500-abeb-7bf28f08616d | note | Verification Activity: Activity - HP
fabd6ff9-dd27-531d-b9e6-74dd2261522e | note | Verification Activity: By - ENG
42f6d513-d1ab-482b-a60b-6362f9997ae4 | signoff | AUTHORITY HOLDPOINT
68191c50-04e6-4983-b7e1-0faf1a20c4cb | checkpoint | 1.1.4 - Maximum Dry Density and Optimum Water Content
d51243dd-f1f7-5ec4-8e63-68a2424d3daf | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
ba5a47fd-9ab9-5b94-848e-fc3179b88a5b | note | Acceptance / Conformance Criteria - Report Value Only
7d5d52de-561b-58bd-8e85-76e9b49b71ad | note | Standard / Specification - NZS4402:1986 Test 4.1.2
721270a3-1342-5ce3-be54-1ff90c493349 | note | Verifying Document - IANZ Accredited Report
a4260284-2e6b-5fb8-9aff-29e2172cde2a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
5f047645-78ab-5da9-856a-dd9bb9530177 | note | Verification Activity: Activity - HP
0e46b9e6-05f8-5ecf-ba89-a53741458084 | note | Verification Activity: By - ENG
9c929cbd-ee6d-4473-8c9c-89de010f4a56 | signoff | AUTHORITY HOLDPOINT
19935587-7c90-4739-a3a9-96fd1d60393e | checkpoint | 1.1.5 - Geogrid
41653efb-4f7e-5a62-bfb4-15b03590eb6d | note | Detail - Triaxial geogrid to be laid on top of the sand layer extending it 1m on both sides
82ae3ca0-5be8-58a0-9955-b6ba96b6f58a | note | Acceptance / Conformance Criteria - Engineers Apprvoal
673473c8-e90d-5ca5-b4d3-c833f906939d | note | Standard / Specification - WSP-DR-PVS-0401
783552b2-756d-597a-9071-4688379b195a | note | Verifying Document - Engineers Apprvoal
1197da18-817d-5b70-936b-5d0b172a7911 | note | Testing Quantity Required (based from schedule qtys) - Once before works commence
ec94e2aa-9c48-5a2c-965d-a024ff40c55e | note | Verification Activity: Activity - HP
d982c0b7-57db-522f-b8d4-389ed333febd | note | Verification Activity: By - ENG
ffa4ca81-0a4d-4f42-a06f-9375e3e60dc0 | signoff | AUTHORITY HOLDPOINT
ece50be3-692e-442a-b0f3-dc18807e3fd7 | checkpoint | 1.1.6 - Mix Design
70c64968-b0d5-5ade-b379-e4b5ad6c265b | note | Detail - Concrete Mix Design needs to be Sumbiited to an Engineer.
eb25552e-0f12-5fa9-b1aa-ab80377c6368 | note | Acceptance / Conformance Criteria - Engineers Apprvoal
ba5c7eae-d7cb-5d18-b63e-d338e35a8d5c | note | Standard / Specification - WSP-DR-PVS-0401
ec99d257-d39a-58fe-bb25-85088ad9f13e | note | Verifying Document - Engineers Apprvoal
477b3067-90a0-5037-95be-790574510499 | note | Testing Quantity Required (based from schedule qtys) - Once before works commence
79109956-5a34-542b-a70e-989055f077c2 | note | Verification Activity: Activity - HP
751a9157-b62b-53f8-ac52-c1b3d3e8c899 | note | Verification Activity: By - ENG
c94fa583-ae30-4eda-b68a-2d53c144e863 | signoff | AUTHORITY HOLDPOINT
8e59152b-a1ed-47cb-b0f7-a9056beb8195 | section | SECTION 2 - CONSTRUCTION OF UNBOUND AP20 LAYER
1e7b6478-c023-4424-9417-63ff6dc5e468 | checkpoint | 2.1.1 - Install 2 layer of polythene sheet on top of underpass
51ee30e9-dbf4-5faa-9558-f8ea88e8044e | note | Detail - Installation of Polythene to be directly on top of underpass precast unit 2 layers of polythene to be laid to prevent the puncture of the water seal during compaction
fa264f2e-3c7d-5108-bb56-0ce4aca99c29 | note | Acceptance / Conformance Criteria - Visual Inspection
b4d0589a-bd3a-5465-8660-69e8aa1f83a8 | note | Standard / Specification - WSP-DR-PVS-0401
46b24f25-0423-5692-8d73-20b03bbaf0bc | note | Verifying Document - Visual Inspection
3b15c0de-fad2-5d5b-8e2a-f745ff205f98 | note | Testing Quantity Required (based from schedule qtys) - During Construction
7c307018-9c98-5cad-a941-e28bd9d17268 | note | Verification Activity: Activity - I
b93c88f3-551a-516e-88f3-e1f1317c433b | note | Verification Activity: By - SE
36523137-1266-4132-b427-46cef01085e1 | checkpoint | 2.1.2 - Sand Layer
710031ae-6dba-5d0f-a219-6ab733103b08 | note | Detail - 20mm sand layer to cushion the polythene layer
b22225b4-08e8-59ca-ba28-dd676103078d | note | Acceptance / Conformance Criteria - Visual Inspection
531ceecc-9165-540c-a2ea-e3f386c84e5d | note | Standard / Specification - WSP-DR-PVS-0401
ca9876ea-c4ea-5471-8b55-5a5333548e7c | note | Verifying Document - Visual Inspection
b77c74d7-fc80-5bf4-8247-7ee15a151776 | note | Testing Quantity Required (based from schedule qtys) - During Construction
61027747-7954-543a-ad85-d048d4b461b8 | note | Verification Activity: Activity - I
555c3462-1cb0-58f5-b40e-67952ee9a038 | note | Verification Activity: By - SE
c76101da-5757-4905-a0aa-f78e7bb80d36 | checkpoint | 2.1.3 - Place Triaxial Geogrid over underpass extending 1m on both sides
bb55be34-b55a-5a64-b48e-b53f9387d4ea | note | Detail - Triaxial geogrid T600 to be laid on top of the sand layer extending it 1m on both sides
8d7c8fb4-1fc4-54ed-9062-8de9df2b29f6 | note | Acceptance / Conformance Criteria - Visual Inspection
3642a613-5d36-5be0-9bc5-fc9f42d689fb | note | Standard / Specification - WSP-DR-PVS-0401
3c456756-7bf1-51e0-9796-e42a97c464cb | note | Verifying Document - Visual Inspection
d6ff198b-0e55-50c8-be80-9bf58afbc135 | note | Testing Quantity Required (based from schedule qtys) - During Construction
2dce0d68-67fa-5f33-b3a6-e52fbb9bde48 | note | Verification Activity: Activity - I
2ba80529-6583-5998-9e69-1fecd0aa1bb6 | note | Verification Activity: By - SE
b5888067-d162-4a68-9022-6006a901e714 | checkpoint | 2.1.4 - Stringlines or equivalent
a807edf7-aa01-578d-85b5-f49d66b4ae0a | note | Detail - Stringlines or equivalent to check finished height of surface
a0a261a0-841e-55ac-b0e2-132720932f31 | note | Acceptance / Conformance Criteria - -20 + 0mm
bf55da09-a3db-551f-aa26-7d3e37f4db99 | note | Standard / Specification - NZTA B/06 8.2.2
cdcb2fed-bfda-5ed0-925d-c3f565a6d4a1 | note | Verifying Document - Check Sheet
387b7e1d-cc01-512c-9eff-28f7be917232 | note | Testing Quantity Required (based from schedule qtys) - During Construction
e43c0689-8999-598b-b43e-8b98c386047b | note | Verification Activity: Activity - I
38ac8d60-8cbc-5fa7-9a72-970c4b0c0918 | note | Verification Activity: By - SE
5d8dbc45-0c77-45c8-bc39-48ebe979acf4 | checkpoint | 2.2.1 - Compaction - NDM of AP 20 layer
bb208037-5a28-5897-adeb-3ac2291130ae | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
366d3bce-09ef-5ef7-8eb6-c11bccc9636d | note | Acceptance / Conformance Criteria - Min >92% of MDD
80092e7a-647e-537b-8ab5-172efa2d392a | note | Standard / Specification - NZTA B/06 8.1
e1943092-a6a1-5e24-a2ed-1695b16b9cc2 | note | Verifying Document - IANZ Accredited Report
5e8ae482-89f4-5c89-961e-807d48426c6f | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
075cc21e-65b2-591c-9db1-b40317c4bdcb | note | Verification Activity: Activity - I
f8a1e19b-3e39-5d9f-964b-825974336cdc | note | Verification Activity: By - SE
9199d6f7-6eab-49a6-bd14-ad05b79d5464 | section | SECTION 3 – CONSTRUCTION - 10Mpa LEAN MIX CONCRETE
e5355835-bbce-47fb-b061-1e087cebd451 | checkpoint | 3.1.2 - Pre pour inspection to be done before concrete pour, Check delivery dockets
efa6cca4-02d6-5adf-bb1b-4454a523c6e1 | note | Detail - Pre pour inspection with designer to verify the surface is clean and all works has been finished before pour which will stop concrete from flowing outside the pouring area
a2e0347b-3d19-5436-afa2-6fc53ac19169 | note | Acceptance / Conformance Criteria - Visual Inspection
82150845-d5a3-5a64-ab31-47388f90e0b5 | note | Standard / Specification - WSP-DR-PVS 0401 Rev 3
b64a9bc8-85ef-52bb-9369-753ce6181570 | note | Verifying Document - Pre-pour Check Sheet, Visual Inspection
a6926b48-ff5a-5d37-9785-427b37fe66d1 | note | Testing Quantity Required (based from schedule qtys) - Each pour
97c1155b-559f-5847-88f6-ef8d5b620ed7 | note | Verification Activity: Activity - HP
ff60d397-a6fc-5930-9b22-b09716798134 | note | Verification Activity: By - ENG
c7571f85-fa00-4603-a108-21a4236c9b52 | signoff | AUTHORITY HOLDPOINT
a655130e-f72a-4a81-83fd-bcb010567354 | checkpoint | 3.1.3 - Slump test and compressive strength test of concrete
afd3e845-1752-5001-b77f-9c8e0a9a9965 | note | Detail - Ensure lean mix concrete with slump 40-80mm and take samples for compressive strength test
87e94db7-7e16-56c1-8ac6-0ca9d3bfcb1f | note | Acceptance / Conformance Criteria - within tolerence: +20mm for slump test and minimum compressive strength of 10MPA @28 days
99711ae0-2c52-5fdf-b4ff-38127a4aff76 | note | Standard / Specification - WSP-DR-PVS 0401 Rev 3
6f32fbd0-e4b3-5f0c-8f01-a43937b23e88 | note | Verifying Document - IANZ Accredited Report/ Concrete delivery docket
36f4d1f8-95bc-5e6d-bf04-86facd25e88c | note | Testing Quantity Required (based from schedule qtys) - Each pour
5d503e40-ceaf-5652-93e2-94c2a4d428b1 | note | Verification Activity: Activity - I
46e98197-8621-5343-9969-da868c2dd8c5 | note | Verification Activity: By - SE
226f6015-8406-4248-9c05-52afec4ac811 | checkpoint | 3.1.4 - Stringlines or equivalent
2c8799ac-2bc2-5246-8e76-f44b9fb970ba | note | Detail - Stringlines or equivalent to check finished height of surface. 235mm Below
47f53d8b-20f9-5bf6-8a00-f7dfc65f3ded | note | Acceptance / Conformance Criteria - (-15mm +0mm)
b70a64f4-2508-51e6-92ba-ff97db8d8f96 | note | Standard / Specification - NZTA B/06 8.2.2
f7fa7a27-ec7c-5285-912b-339972ddb4a7 | note | Verifying Document - Check Sheet
ffcccae1-f19f-53f1-9934-4c5130a69c73 | note | Testing Quantity Required (based from schedule qtys) - During Construction
b41e3088-3175-51bd-a4a7-92916b1e46ad | note | Verification Activity: Activity - I
d8976c54-8fa1-579c-9089-0891a6a30e0a | note | Verification Activity: By - SE
2e6f5ac8-09a0-4b4e-b5b5-9a81e55d84b1 | section | SECTION 4 – KERB & CHANNEL PREPARATION
caf9913b-b4b3-4641-aba0-d9f93723d9dc | checkpoint | 4.1.1 - Stringlines or equivalent
a260cb67-287b-5e73-8e67-3d22bd5b040a | note | Detail - Stringlines or equivalent to check height of surface prep
4276a9bd-e3ab-57cb-89da-d7f0f63819ec | note | Acceptance / Conformance Criteria - +/-5mm
3a54af1a-472c-559b-9178-96efc41dfec2 | note | Standard / Specification - PS 21.7.6
1df7d0cd-0af8-5b51-adc8-4b99f878214d | note | Verifying Document - Check Sheet
ea361712-49c9-5f22-b0f0-169afdb8fdec | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
ee6593db-9c2c-57d0-9f1c-f218a47662df | note | Verification Activity: Activity - I
971aeabe-b744-527f-a02a-c900cbb54191 | note | Verification Activity: By - SE
d608f81f-f5fd-4414-ba95-0529baaa113f | checkpoint | 4.2.1 - Compaction - Clegg Hammer
c8c60fb7-e1de-55fe-97e1-6c8a64126169 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
16d111a3-8484-5906-8d17-ac00c9a385cb | note | Acceptance / Conformance Criteria - Min 25 CIV
eebff5dd-4e7c-50ed-bd84-5058a4f841bf | note | Standard / Specification -
15d7b4bd-154b-54ad-a732-247eeb646021 | note | Verifying Document - Clegg Hammer Report
0024dcf5-5e77-5755-85b6-d7bdc074af5f | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
5b5d0596-46b3-53b1-936a-2c35fdfbedae | note | Verification Activity: Activity - I
03aa364c-8c40-50a5-bc53-99a17da5280e | note | Verification Activity: By - SE
b98aca88-c7b1-4e45-8b88-c1eba4e256fb | section | SECTION 5 – AS-BUILTS / REDPEN MARKUPS
ca5cb986-bbc5-426d-bc71-35cb298e1046 | checkpoint | 5.1 - As-Builts/ Red pen markup
c9de22c1-3c8a-5f68-94eb-551c9846897f | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all the changes been made different from design.
c53b8180-f89a-525a-aa51-c46f4d1aac3e | note | Acceptance / Conformance Criteria - Red pen markups
ce1ffcfd-e0a7-55b6-9e66-276d704e3631 | note | Standard / Specification - PS 16.7.6
52353db6-1861-59dd-a6fa-59e590fa2d14 | note | Verifying Document - Red pen markups
52a5bfb1-3e47-5444-a53b-1d42cc357392 | note | Testing Quantity Required (based from schedule qtys) - During Construction
bf94d5ad-5a60-5851-abae-d8e4769f2f35 | note | Verification Activity: Activity - D
578dfc26-a502-5162-b04b-f7ddc7271757 | note | Verification Activity: By - SV
abee857f-1a6c-42e3-889e-c271566a0847 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
dbc70f68-185b-5018-a049-8c6e5de14afb | textbox | Contractor's Rep Name:
c3a3cc9b-c48f-56c3-8503-ef4a00bf7341 | textbox | Engineer's Rep. Name:
67b39dcc-03ef-52ad-be44-eff7b3d22675 | date | Date:
983bc151-d3c4-4b4f-8f17-720652d364a1 | signoff | Add Signature
459be8cc-d324-4840-bd37-c6f59fed126c | checklist | DN1210-034 ITP Wetland Maintenance Track Rev 0 | itp | DN1210-034 ITP Wetland Maintenance Track
f64680e7-d963-4fd6-87c5-4bf50459b3a6 | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
e049f50e-4b6a-4877-841a-09d600e08a35 | checkpoint | 1.1.1 - Crushing Resistance
551d9188-40bc-51bd-991f-d552b6f5bb8b | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
56b6ba43-9beb-53e8-925f-deaa801b5590 | note | Acceptance / Conformance Criteria - >100KN
862a1f29-2a88-517e-a313-6e19a3081fcf | note | Standard / Specification - NZS4407:2015 Test 3.10
dd72c922-3438-52b6-8301-335bee4d1f58 | note | Verifying Document - IANZ Accredited Report
853b0770-679f-5361-88b2-7a2e33f5f14c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
90af5f12-78d2-5cbe-9e85-19c1fe1985a1 | note | ○ Results to Engineer 2 wks before importing
7987eff2-5cdd-5a1c-a5fc-d44c1725f8dc | note | Verification Activity: Activity - HP
04e4c42f-2793-5360-9ba1-ca5d42a6dceb | note | Verification Activity: By - ENG
abe54e2a-7fb9-4e36-ac39-70a94f91e846 | signoff | AUTHORITY HOLDPOINT
3b1fb7f6-2235-4a4c-aa3e-2836fea343fe | checkpoint | 1.1.2 - Soaked CBR
5a3360bb-41df-59f2-8f9b-f6a60e0aec67 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
289a9d55-07d2-5008-9634-89f0b31de642 | note | Acceptance / Conformance Criteria - >60%
79ce244a-d460-5a62-abc9-db6aa9499717 | note | Standard / Specification - NZS4407:2015 Test 3.15
e17a6d73-23ba-5e17-9d82-5326d601ac4b | note | Verifying Document - IANZ Accredited Report
80c3c181-3ef1-58e7-8811-5878c6a3480f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
ff0d45e0-f3ef-5ef0-b249-84e19c49cb7e | note | ○ Results to Engineer 2 wks before importing
8080229a-650c-55c8-a216-dc51187bf0a8 | note | Verification Activity: Activity - HP
068bfa4b-a6ab-5498-9b31-d05428372c69 | note | Verification Activity: By - ENG
e24bb0b4-b321-441b-aad6-26fb0a4ed2cf | signoff | AUTHORITY HOLDPOINT
fb2c285f-431e-4d79-af35-2a44ddd78bf0 | checkpoint | 1.1.3 - Weathering Resistance
0d4e5420-993c-5b7f-8e3b-70e001525ba8 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
89fe3710-e9b1-5bfd-a77c-abd4d649a1d0 | note | Acceptance / Conformance Criteria - AA,AB,AC,BA,BB,CB or CA
017b70f0-587c-5149-9949-4a5eb82281d9 | note | Standard / Specification - NZS4407:2015 Test 3.11
49f7f7a9-c52c-5195-b43c-216b99e0326e | note | Verifying Document - IANZ Accredited Report
0d99065a-0ae6-58ca-9272-a45cea77ee5b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
99062ba1-bc3f-56f8-a3d8-b6847ec0f0b6 | note | ○ Results to Engineer 2 wks before importing
dfe0ba70-90a4-57bb-b9dc-0c5efa6e2ac3 | note | Verification Activity: Activity - HP
5974a46e-e38b-5936-a724-e2cf12367a29 | note | Verification Activity: By - ENG
3dabb55f-46e2-4f9b-8699-d8c689d6f1de | signoff | AUTHORITY HOLDPOINT
24d848c8-2038-48d7-befd-21e48e13e8a1 | checkpoint | 1.1.4 - Particle Size Distribution
04ada0bb-6c6a-50cb-a77c-92b4898cea13 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
08297905-7e9e-51f3-ad8f-8afdadcdaa6d | note | Acceptance / Conformance Criteria - Sieve ¦¦ Percentage Passing
bbaedd6d-03f2-5edb-b432-fca7ace526ef | note | 63.0 ¦¦ 100%
dc221a25-a908-5fbd-9558-85004b858305 | note | 37.5 ¦¦ 68-90%
a7909bd2-bc40-543c-a51e-0ac91f0a2575 | note | 19 ¦¦ 42-76%
f400cabc-d309-58f8-9ba6-e7f492352d60 | note | 9.5 ¦¦ 26-58%
3b5a4a55-123d-56d9-9a7e-6238b98d9827 | note | 4.75 ¦¦ 16-44%
0d040445-b817-5772-bc7d-468f6b7c2cee | note | 2.36 ¦¦ 10-33%
54431799-1821-5e27-9cef-1f8bb9a20e16 | note | 1.18 ¦¦ 6-24%
8c99f769-7d39-5e05-b2ba-e9382b633355 | note | 0.425 ¦¦ 3-14%
fe181241-75b6-5d49-844d-afc4eea1b3c7 | note | 0.075 ¦¦ 1-6%
d3c48d63-5778-534c-883c-9df3d1ab14bb | note | Standard / Specification - NZS4407:2015 Test 3.8.1
12896dc7-09bd-534d-9f92-1c7dbb40f8af | note | Verifying Document - IANZ Accredited Report
932cc835-5940-5e90-b64c-b5f6c16cff46 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
2be5247e-b3d0-5856-a2d6-f57d8e2d36a0 | note | ○ 0-400 - 2 tests
5a46d6fb-317f-5521-a397-7146d43f1312 | note | ○ 400-1,500 - 3 tests
fe2d24ec-2d26-5330-949f-cc42130c6d81 | note | ○ 1,500-4,000 - 4 tests
32bcabd5-c7f0-52c3-901b-7aa2a66472e1 | note | ○ >4,000 - 1 test for each additional 1,000m3
b68b8d59-2590-5790-9775-ee71f87cc5a6 | note | — Results to Engineer 2 wks before importing
c9bb871d-1b05-58d0-a073-502691b47f4a | note | Verification Activity: Activity - HP
d722ac35-003c-5cb3-9517-62237533592a | note | Verification Activity: By - ENG
a37126e4-0da2-4be9-8de5-f9f2df114ccb | signoff | AUTHORITY HOLDPOINT
ec586bd6-d87a-43f2-9b1c-36dabf02dd23 | checkpoint | 1.1.5 - Maximum Dry Density and Optimum Water Content
038f0c4a-d9d0-5e66-8d60-f2ac30507f77 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
83a8733b-5301-5465-8fe0-ab338dae04d1 | note | Acceptance / Conformance Criteria - Report Value Only
25c5b61c-92a1-5567-8079-627ca3e33b47 | note | Standard / Specification - NZS4402:1986 Test 4.1.2
a9223604-66ac-59ed-bd73-9a6065742324 | note | Verifying Document - IANZ Accredited Report
9f9e9b77-2e39-59dd-88a0-57956b0224af | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, PerSource
f8b338ac-431c-5042-97b7-d2f6f1a16d4c | note | Verification Activity: Activity - HP
36913f6c-d4a7-5f10-a48a-6ecd9c3d25fb | note | Verification Activity: By - ENG
c10fa2ab-0d0d-448c-8cc0-a00551a9aa02 | signoff | AUTHORITY HOLDPOINT
824cf3ec-7047-4a08-b13e-9d828492e1be | checkpoint | 1.1.6 - Plasticity Index
43a02864-d30e-5a49-a047-37d0fb21c45e | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
081a5c27-5001-5bb3-af85-793104d5ae83 | note | Acceptance / Conformance Criteria - <8
9b8430c9-ccfa-5d36-b231-363507be53fd | note | Standard / Specification - NZS4407:2015 Test 3.4
07f67512-48b5-5352-b673-3caa22bc7eeb | note | Verifying Document - IANZ Accredited Report
75cb3874-81ca-5eda-a181-c238aa7ada84 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
bae455ed-e9f1-5526-b01f-fc3010da818a | note | ○ Results to Engineer 2 wks before importing
8952dcf7-ce6f-5e33-92d9-f728f6778a3d | note | Verification Activity: Activity - HP
107cb349-e2ea-5844-aac3-cae6e1194a31 | note | Verification Activity: By - ENG
9ae752b3-03d7-480b-9b53-7656a564a6f5 | signoff | AUTHORITY HOLDPOINT
a50618bd-c727-4d69-8cad-e5c89d7675bd | checkpoint | 1.1.7 - Sand Equivalent
1b4b162e-ee13-5736-8b3b-45e5ec36a8bc | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
8815711c-5d2e-5947-8d87-3d9a44a4107d | note | Acceptance / Conformance Criteria - >25
fc8ca2dc-6960-52bd-a120-0b0662cfd66e | note | Standard / Specification - NZS4407:2015 Test 3.6
8f53b29c-0469-52a4-84f9-161da1134571 | note | Verifying Document - IANZ Accredited Report
ac38f4a4-a7de-5529-9e43-db5b1d1b3168 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
4a5e08f4-cf7f-5c4b-a5f1-7122be109d15 | note | ○ Results to Engineer 2 wks before importing
3c5c4926-348b-53d4-aac7-3064734ed49e | note | Verification Activity: Activity - HP
06f40f3f-b8f1-5fde-9313-c248ec8e12cb | note | Verification Activity: By - ENG
bb4bd5e4-441f-4825-bb7c-ab803aa0081b | signoff | AUTHORITY HOLDPOINT
e4e3594f-b543-460b-ad12-1954a49d5f5b | checkpoint | 1.2.1 - Crushing Resistance
7dfaa38c-e1ef-5fde-a57f-5cce7b483521 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
3f3210e8-1bec-5aff-bfac-e52a72024505 | note | Acceptance / Conformance Criteria - >130KN
9b6ee661-7db3-524c-80fb-236974487e83 | note | Standard / Specification - NZS4407:2015 Test 3.10
f95f4b25-f23f-517a-8535-f3943ecb6486 | note | Verifying Document - IANZ Accredited Report
6e12f52d-da90-5ef6-b1b3-2d5e91ad9fa8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e95ec37e-5435-5079-b44c-d2042742d4ec | note | ○ Results to Engineer 2 wks before importing
23c3cf35-1b89-5c1e-8f16-4a0bab74183f | note | Verification Activity: Activity - HP
ceae5222-1af7-5f26-bdb6-315252b20c2b | note | Verification Activity: By - ENG
b939ad98-6823-4b63-9c97-5c108f03f37e | signoff | AUTHORITY HOLDPOINT
d998ad0f-270c-4212-b0e1-86c98554b0d0 | checkpoint | 1.2.2 - Soaked CBR
364d2d3a-45e7-5a7f-834f-b9c1ba636fad | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
0c0c8611-b35e-523e-8cf6-dcb97981576f | note | Acceptance / Conformance Criteria - >80%
757a3c84-e400-5890-9ab6-9f41e5934761 | note | Standard / Specification - NZS4407:2015 Test 3.15
90c31c7b-c19e-5cc9-b823-87469cb502fa | note | Verifying Document - IANZ Accredited Report
7842f115-86f8-5269-a08a-bf25b750abe0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
2e7fd914-9ee0-5353-a3a2-8e0432d6447a | note | ○ Results to Engineer 2 wks before importing
8387536e-141b-54a2-b48e-e48ab528d1e3 | note | Verification Activity: Activity - HP
580f2a0b-fa2d-57f6-becb-a36d12b2b11b | note | Verification Activity: By - ENG
0af17fc1-6b70-46aa-9ae6-fb462074d5e1 | signoff | AUTHORITY HOLDPOINT
014df9ff-de67-4c08-be1c-5b2355575a1c | checkpoint | 1.2.3 - Weathering Resistance
6c38f3f0-d421-59c0-8865-7ed383a0126a | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
fca334a9-0228-5e63-98a8-0778c10320c4 | note | Acceptance / Conformance Criteria - AA,AB,AC,BA,BB or CA
bb8ba673-bc02-547d-bb4f-ebb7f51c72ff | note | Standard / Specification - NZS4407:2015 Test 3.11
06184d34-c0d6-55e0-abdf-47875034a764 | note | Verifying Document - IANZ Accredited Report
6694db0c-1a61-549c-a413-f45b67876455 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
d61f5c53-1f13-51d3-8fe6-21c065c080ce | note | ○ Results to Engineer 2 wks before importing
8f7521c6-5e19-58c7-acbd-5bb9e07dc575 | note | Verification Activity: Activity - HP
c8c5cf86-6620-5b58-8630-e9bf2e418d0e | note | Verification Activity: By - ENG
f88f854b-101c-4484-b8c3-d43d8cd5fa03 | signoff | AUTHORITY HOLDPOINT
918c25b8-96f4-4560-aa85-450acf3e9169 | checkpoint | 1.2.4 - Particle Size Distribution
770335b6-1060-5d1a-be24-3a2c35de677d | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
9ee44f4f-267f-5fc2-af3a-6731eb367d7b | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ Percentage Passing
fecbe906-26a1-500b-86f4-ae96a7c69c69 | note | 37.5 ¦¦ 100%
a249b0fb-11aa-5cfd-9b44-8f52e1b99bcb | note | 19.0 ¦¦ 66-81%
def2dd35-4638-5e94-a7ee-8358edfc08c6 | note | 9.5 ¦¦ 43-57%
2a032b85-0975-5562-b597-66253265b93d | note | 4.75 ¦¦ 28-43%
61ec1427-7e2b-5493-ad8f-dc99e98eeae7 | note | 2.36 ¦¦ 19-33 %
292ac0b4-fd0a-5d89-9b6d-c7ecb3f5024a | note | 1.18 ¦¦ 12-25%
5daa15c5-4bb2-53fb-8863-8d3fa8e063b5 | note | 0.600 ¦¦ 7-19%
8b4eae72-02a9-5230-9118-66a41f9d636f | note | 0.300 ¦¦ 3-14%
52bf0590-0265-5a53-8b49-41a2f4e91035 | note | 0.150 ¦¦ 0-10%
39add1a7-282d-5cbe-8cdc-3d2a033a236f | note | 0.075 ¦¦ 0-7%
65a2b234-531b-5d91-a17e-80937093a954 | note | Standard / Specification - NZS4407:2015 Test 3.8.1
7f24ec21-9a10-50ec-b8c1-788222644528 | note | Verifying Document - IANZ Accredited Report
0643964f-1e23-5815-85f1-f64d23c7550f | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
918b9e46-9a3c-5715-9b47-0198766851a4 | note | ○ 0-400 - 2 tests
50e26ed3-4474-585a-98ee-0b8a03a38d8c | note | ○ 400-1,500 - 3 tests
08b6d593-ba1e-5b4d-b027-12b5b016e30b | note | ○ 1,500-4,000 - 4 tests
840e76d9-1e79-53f5-8300-0d41e20b7bcb | note | ○ >4,000 - 1 test for each additional 1,000m3
4e4bf27c-73c7-58aa-89df-c9b28238a676 | note | — Results to Engineer 2 wks before importing
f08d7751-dff3-5109-bd01-3eff5720e62e | note | Verification Activity: Activity - HP
7d010658-38ec-59b0-a004-d583296abdf5 | note | Verification Activity: By - ENG
caf43ebb-8e39-4d67-b238-aa0dfed12e95 | signoff | AUTHORITY HOLDPOINT
140dcab6-8b22-4fd1-b4c0-e64cdf48c55f | checkpoint | 1.2.5 - Maximum Dry Density and Optimum Water Content
fbc5146e-250a-5519-aa65-425c2a7855f2 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
7702bdf7-6aca-5dca-b619-364e9225cbf0 | note | Acceptance / Conformance Criteria - Report Value Only
1172828c-578c-540c-8688-4f7022e41c93 | note | Standard / Specification - NZS4402:1986 Test 4.1.2
552cca15-3e6e-50ed-b870-ad28c16d4368 | note | Verifying Document - IANZ Accredited Report
292a9d68-5577-51de-a24c-f89b5d1ff967 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, PerSource
eb725b1b-4f1b-50bd-b8ab-0f579cc03ba1 | note | Verification Activity: Activity - HP
ccc4d362-3509-51b3-a35b-b361ce601616 | note | Verification Activity: By - ENG
dfb14fa2-aa83-49fe-9607-319d107e3eca | signoff | AUTHORITY HOLDPOINT
7ee005ef-0787-4c2c-ad3b-c0f3dc7e84eb | checkpoint | 1.2.6 - Plasticity Index
b6c88848-8aff-51b8-a71f-9e529454809d | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
99d5fbd5-6bfe-591e-b9db-fe8adcb8f318 | note | Acceptance / Conformance Criteria - <8
63608f24-d509-5cf3-a8fc-e4bbe3c1bb0a | note | ○ If SE is <40
d4fba987-7b7d-559e-99dd-9a781f2c95a3 | note | Standard / Specification - NZS4407:2015 Test 3.2
f9a41828-014d-5e27-94ea-747bc8a9cdd0 | note | ○ NZS4407:2015 Test 3.3
6a55b7b4-6926-5e8e-8a87-60f293cbf66e | note | ○ NZS4407:2015 Test 3.4
67b37d61-e9ed-519b-9e2b-ff63331c4542 | note | Verifying Document - IANZ Accredited Report
9bc47301-3da3-5319-b81d-5f57b12b6a95 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
cf552ae4-c944-50e9-acfc-446c66234258 | note | ○ Results to Engineer 2 wks before importing
150dfd9d-5c04-5484-9384-aa70e268d03b | note | Verification Activity: Activity - HP
503c8a25-47fb-5636-9a18-66afd81cb103 | note | Verification Activity: By - ENG
48eb7c18-406a-4825-9435-dd80fccf6374 | signoff | AUTHORITY HOLDPOINT
47dc234d-14b5-4a47-9f08-756fc946560f | checkpoint | 1.2.7 - Sand Equivalent
41aa3462-e63b-5b0d-9d5a-6606f0cbfad5 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
76251cf6-3555-5497-8b77-09137c67ee8d | note | Acceptance / Conformance Criteria - >40
32ca73a8-22cc-54f4-be76-41c7ddfdbfb0 | note | Standard / Specification - NZS4407:2015 Test 3.6
ab098109-a647-5328-bb0e-697bf6a875f8 | note | Verifying Document - IANZ Accredited Report
518a1804-52ec-5a14-9b37-6fe6b8096b4f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
d0ed7717-06da-562a-a957-cc1738ac2b88 | note | ○ Results to Engineer 2 wks before importing
5b50fa24-6f79-596b-aaf1-239d62dfaa9e | note | Verification Activity: Activity - HP
79ce82a2-c7b5-5cc2-923f-2ff5ee076867 | note | Verification Activity: By - ENG
de1c7dc2-17bd-481f-a93d-fcd4adb28a37 | signoff | AUTHORITY HOLDPOINT
e0db9963-51c0-4092-b692-e423e8386571 | checkpoint | 1.2.8 - Clay Index
02d6238f-cb64-5ea2-9bf2-a5dba3ff4120 | note | Detail - NZS4407:2015, Test 3.5 - Clay Index Test Report
6e9630bd-473c-5940-bcf0-574f94a94c58 | note | Acceptance / Conformance Criteria - <5
72e06647-740c-5694-b705-ae4901e82dde | note | ○ If SE is <40
88a38388-78c5-53e4-8048-b72fe91b27c8 | note | Standard / Specification - NZS4407:2015 Test 3.5
55739e58-1ed5-5b20-a67f-97726337705b | note | Verifying Document - IANZ Accredited Report
888b7241-31b8-5639-b852-c33cbf416927 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e4cc9e50-9602-5325-8999-1d08ebbd4074 | note | ○ Results to Engineer 2 wksbefore importing
51349178-dc5e-5b55-8f17-72964c1a186a | note | Verification Activity: Activity - HP
c5cc6084-8d30-5858-afe7-9356d16eb450 | note | Verification Activity: By - ENG
4ec5bfaf-64c6-466c-acf0-9e0fce7b499c | signoff | AUTHORITY HOLDPOINT
18ee7813-4114-4dbf-a9d7-f54c5f1d4a6b | checkpoint | 1.3.1 - Crushing Resistance
b8d3bd96-253d-51f8-999d-ad8405be45c3 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
0d51f8b2-037c-5e87-ab7f-4a1a2f8a278c | note | Acceptance / Conformance Criteria - >80KN
6c0df41e-3dea-5284-8547-44662833d85f | note | Standard / Specification - M04/4.4.1
670408dc-85f2-5e98-9cee-2c81342f868b | note | Verifying Document - IANZ Accredited Report
ddd52c1b-9b1c-54d5-a418-1e323362c474 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
ad58cd9f-d0cb-52a1-b5b3-1ccdcca31646 | note | ○ Results to Engineer 2 wks before importing
91ff5ac3-7da9-5035-8a2f-9cc14abc1a33 | note | Verification Activity: Activity - HP
2d384711-eb35-5ede-9847-6955ef6d138e | note | Verification Activity: By - ENG
e59a4316-e6ec-4aa6-9fda-8de0905191ef | signoff | AUTHORITY HOLDPOINT
99a8be10-db02-48b1-99cb-43bf3f1355a0 | checkpoint | 1.3.2 - Weathering Resistance
f64d1617-27b7-5cb4-a38e-149a899720d2 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
e3e4bec3-4fa2-5bdd-b869-0004cd8ba26b | note | Acceptance / Conformance Criteria - AA,AB,AC,BA,BB or CA
4000eea9-1418-57ad-b165-084a5e0554c1 | note | Standard / Specification - M04/4.4.2
b0cf1d04-e218-59f7-8f8d-aded882a8c27 | note | Verifying Document - IANZ Accredited Report
a3505195-7776-536b-98dd-943626d9dc00 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
2aa4c2ff-250d-5c61-8871-338908d1e72f | note | ○ Results to Engineer 2 wks before importing
bab671ca-01f0-5c91-bceb-85ea165ef9e9 | note | Verification Activity: Activity - HP
43d7ad3f-5c4f-5737-a948-28e0800a3ae3 | note | Verification Activity: By - ENG
9573775f-ab25-4de2-a9da-1bee3ff830ad | signoff | AUTHORITY HOLDPOINT
06575a79-6a38-4152-b368-5b2294b1e19c | checkpoint | 1.3.3 - Particle Size Distribution
12f9c7b4-6bf7-5221-88eb-9bc01938b4e1 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
7f683f35-2b9f-502a-ab06-62f5fc8eabe6 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
7e761d6c-e4b1-551f-8964-24b2d9968736 | note | 19.0mm ¦¦ 98-100% passing
c75b0143-3d40-5130-b994-40c9bec3b958 | note | 9.5mm ¦¦ 50-80% passing
cb720889-d174-5d31-8a0b-af777e7f2616 | note | 4.75mm ¦¦ 29-61% passing
4b795faf-7156-5af7-bf76-1d61425f69ec | note | 2.36mm ¦¦ 19-46% passing
739af6e8-0eff-560b-ab84-1e3c6aced18f | note | 1.18mm ¦¦ 11-35% passing
461a87ed-0e17-549f-92ab-125c267ed881 | note | 0.600mm ¦¦ 5-26% Passing
9a86f6f7-f243-5907-b470-e5eb0413d0bc | note | 0.300mm ¦¦ 3-19%Passing
cee00f32-149d-5a78-aa38-23e93d1913a3 | note | 0.150mm ¦¦ 0-15% passing
5c43ebdf-6e43-529e-89e0-5fccee45234c | note | 0.075mm ¦¦ 0-1% passing
ea0641f2-4e7e-58ec-8f54-3b7764aa3926 | note | Standard / Specification - M04/Table 14
1de9bb70-0b0f-5571-bbe4-f696a3d4ca55 | note | Verifying Document - IANZ Accredited Report
200d315c-b611-5cb9-a481-18402206431f | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
202e05ba-aef9-5e3a-9cd3-3a02aa360ba4 | note | ○ 0-400 - 2 tests
123f5a52-4a97-562a-ac89-194b202505af | note | ○ 400-1,500 - 3 tests
9dd1e692-7650-5c6c-a54b-3e627e374f18 | note | ○ 1,500-4,000 - 4 tests
04da28dc-08a0-5b68-ba1f-a1163fce3123 | note | ○ >4,000 - 1 test for each additional 1,000m3
592227a5-cc84-590d-86e7-2a5a8c2d6881 | note | — Results to Engineer 2 wks before importing
10747f65-c598-5520-85a4-ee6500b9f72c | note | Verification Activity: Activity - HP
7490379f-3b4e-5cf1-9e59-40f20f90bbd0 | note | Verification Activity: By - ENG
6a810166-2be3-49bf-8f95-322088147ecb | signoff | AUTHORITY HOLDPOINT
cba917cf-698d-4361-a8ea-9d2e36f3202d | checkpoint | 1.3.4 - Maximum Dry Density and Optimum Water Content
05865d93-6a71-57a1-8e49-244ffb53040c | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
aa24673e-21cc-51db-ae13-88528e28c758 | note | Acceptance / Conformance Criteria - Report Value Only
e1ed0f76-9af0-513a-a07e-6f29512a1468 | note | Standard / Specification - M4
e726af6c-2c87-5030-914a-e2d5beea4799 | note | Verifying Document - IANZ Accredited Report
383986fa-8f95-52f4-ae16-279552181a89 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, PerSource
36df113c-52fb-5556-ae24-9374167c90a4 | note | Verification Activity: Activity - HP
b4e50101-b9f7-5c9b-bcf5-c3d6213a4943 | note | Verification Activity: By - ENG
f41d70bc-34d4-4abc-b5b4-d62b1927230e | signoff | AUTHORITY HOLDPOINT
47335c7f-56ef-45a9-8d4a-dadcaa73b23d | checkpoint | 1.3.5 - Plasticity Index
632dde1b-fbe2-5bfb-8c3a-e8ca8ac49d7f | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
37bb6b33-434e-55a1-b376-3b00e520aaaa | note | Acceptance / Conformance Criteria - Max 15
3a1fd682-6b07-55e3-8693-1a9ddcdda398 | note | Standard / Specification - M4/5.4.2
d988764c-7d53-5d31-a71d-0aeec61f36af | note | Verifying Document - IANZ Accredited Report
b7a56b0a-2800-5ab4-95d5-2060cffa1789 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
309899e7-27fa-527b-b373-618873b0b7ee | note | ○ Results to Engineer 2 wks before importing
d779f3f6-9e87-589f-9a5d-d1e88cadf952 | note | Verification Activity: Activity - HP
2224c631-7e35-56d8-812f-4af35bc197be | note | Verification Activity: By - ENG
3f297704-a3b7-4ff4-8a16-8b59799948d7 | signoff | AUTHORITY HOLDPOINT
94343189-bcc9-4f09-901c-4660b1edb497 | section | SECTION 2 - CONSTRUCTION - PREP GENERAL
dfbdb9fd-b8c7-4372-8e7d-ff57901d1fa4 | checkpoint | 2.1.1 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
e0aa3c99-a815-5fa3-8a3a-be110301e485 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
c91b6845-cbaf-51e0-b146-e9cdbb2e10d7 | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
8b25675b-8f76-5b53-abea-376115068513 | note | Acceptance / Conformance Criteria - Minimum 4 blows per 100mm penetration
aa3f7d44-7f8e-52a1-8460-0599e9287290 | note | Standard / Specification - PS 27.4.2
6bc92a7e-3d9f-5ece-b782-d8c32304eb4d | note | Verifying Document - Scala Report
8df64799-da4a-578e-895c-dab04baedf60 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
c29d0018-65ba-584a-b14e-ac024c5bc30a | note | Verification Activity: Activity - I
e592b760-0671-51db-9238-c77f315344cc | note | Verification Activity: By - SE
a887ee4e-4df1-4306-9150-7486c67a926f | checkpoint | 2.1.2 - Proof roll
964f092b-8fa7-5946-a76b-f4cdb9f17f71 | note | Detail - Visual Inspection of Proof Roll
3818e5c2-0599-593e-9487-e10d451e3cf8 | note | Acceptance / Conformance Criteria - Visual Inspection of Proof Roll
98c35b3d-3d09-58e9-a6ab-519d2d23f322 | note | Standard / Specification - Appendix XVIII
1e16f7dc-378c-555e-9c8e-3cfea2b40671 | note | Verifying Document - Visual inspection/ Photos
dbf4c57e-c7fa-547b-82e4-8b0d9ccd45ea | note | Testing Quantity Required (based from schedule qtys) - Across Whole are
78782bab-fb36-5689-a0f9-6ee546f6af24 | note | Verification Activity: Activity - I
8f76227c-d532-56b5-bb05-6cc2f1e6f422 | note | Verification Activity: By - ENG
e0dcde94-12c0-4b6e-aa52-5f787f33f64b | section | SECTION 3 - SUBBASE LAYER - AP65-2
a96cba42-5fa3-4bf3-bab7-18f47d5d1314 | checkpoint | 3.1.1 - Stringlines or equivalent
b7b2ccfa-61e2-544b-8646-fa2d19cb51d2 | note | Detail - Stringlines or equivalent to check finished height of surface.
2521dcc9-a49b-5454-88d3-6b4b0f70038d | note | Acceptance / Conformance Criteria - (-25+5)mm
15475fcf-befa-5d2b-945f-fc5a850ca435 | note | Standard / Specification - NZTA B/02 5.1
82e3a200-84da-59a7-8f9a-059d130d6bca | note | Verifying Document - Check Sheet
fe55d4b8-115b-5c06-a5d7-097d494ab4e1 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
1d5e6f47-c9cb-5a91-bc80-329496420049 | note | ○ 1 set = 5 tests
c86ca4f7-ae88-5c6b-b0c8-6bdbe24f7757 | note | Verification Activity: Activity - I
717861aa-1782-5c5b-a07c-cfa2264cb9eb | note | Verification Activity: By - SE
67b13903-3017-4f5d-869a-f754e1a22476 | checkpoint | 3.1.2 - 3m Straight Edge
fd95aeff-564b-5712-8756-27e83ed9cfa8 | note | Detail - Formation check to ensure surface is smooth
39fb68bd-f401-58da-a0b1-be68e7919ae0 | note | Acceptance / Conformance Criteria - +/- 10mm
2e84aafd-3c11-56fe-b597-47f35de130ac | note | Standard / Specification - TNZ B/2 7.7
d39e65f3-751f-523d-b550-80515488bbb0 | note | Verifying Document - Check Sheet
4c1aad0c-12c3-511e-a502-6f4b40787ffb | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres
b0cbdac4-6b08-5199-9f98-2b04e4017e23 | note | ○ 1 each lane
78bcc748-59ab-5b9e-949d-01425678a037 | note | Verification Activity: Activity - I
d830d9d3-26fc-5e03-b3e8-8742730688b3 | note | Verification Activity: By - SE
157bf6e6-c533-4e44-8bb3-2469a11168e2 | checkpoint | 3.2.1 - Compaction - NDM
33e70aa5-dc38-5395-b360-123497797f68 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
8b63b0ba-cc5e-59d5-912e-805636d7484d | note | Acceptance / Conformance Criteria - Ave >95% of MDD
17681c50-b849-57f6-adf8-1175959778e7 | note | ○ Min >92% of MDD
57c59391-fdd0-527e-8030-e9ae1b07766f | note | Standard / Specification - NZTA B/02 7.6
b1244f80-d8b4-506a-abb2-6e18147dd3af | note | Verifying Document - IANZ Accredited Report
c86929a7-b8bc-5681-b054-7cbccb24ad07 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
ff6f822a-2dc5-5be5-ade7-f8db6dab3654 | note | Verification Activity: Activity - I
f08cd4d6-332d-5004-9a1c-acae463b8555 | note | Verification Activity: By - SE
6075b5b5-bccb-4107-b61a-16f6462b710c | checkpoint | 3.2.2 - Clegg Hammer
77bccc2f-2217-52d1-b2cc-46cdc907dbd4 | note | Detail - Clegg Hammer Testing to be Carried out
3bd18f75-4d9e-5d65-8010-32193d002781 | note | Acceptance / Conformance Criteria - Min CIV18
a03bf7b2-91e4-535d-ae2c-fb80b165d2a7 | note | ○ Ave CIV 20
a8d10700-9155-57f1-a39c-bb65d82e4a90 | note | Standard / Specification - Earthworks Spec
b30cc59b-031f-544e-8dfa-e2b1a229d067 | note | Verifying Document - IANZ Accredited Report
f97498d9-9bde-5d2d-a387-dbc43615bcec | note | Testing Quantity Required (based from schedule qtys) - 2 set (5 tests) 1000m2
7eefd061-e6a7-5899-a570-0cffde3ca054 | note | Verification Activity: Activity - I
fc83c317-9784-56b4-a480-45a5dc22590a | note | Verification Activity: By - SE
bc2285ec-ca36-41c7-9ffa-1d6bd4f4dd7d | section | SECTION 4 - BASECOURSE LAYER (AP40-2)
577facf4-0dec-43e5-ba01-9363b85a4054 | checkpoint | 4.1.1 - Stringlines or equivalent
a0e57118-f10f-5c52-90b0-0c3776db67db | note | Detail - Stringlines or equivalent to check finished height of surface.
e6724e7a-216b-5871-b983-2bcc806a188c | note | Acceptance / Conformance Criteria - (-15mm+0mm)
573f6dc3-d1b6-59e6-8334-0980b3d9e423 | note | Standard / Specification - Standard
f3f1f850-867d-599c-8ff7-bd0ea8140ad4 | note | Verifying Document - Check Sheet
1951c81e-1975-59ec-add0-590167d31744 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
a6e0a71e-0910-52f1-b7af-91e4fe1fac8c | note | ○ 1 set = 5 tests
ecc845a4-b35e-514b-8473-6d83b9241f83 | note | Verification Activity: Activity - I
3c11c680-17ac-5a9f-82de-4012c9edf265 | note | Verification Activity: By - SE
8a51601e-8628-4489-92ac-ce918360e06c | checkpoint | 4.1.2 - 3m Straight Edge
525d19ea-1ce9-5b04-afd0-ca9af59639a7 | note | Detail - Formation check to ensure surface is smooth
1e6c285f-9fcd-5640-971d-9171b054c564 | note | Acceptance / Conformance Criteria - +/- 10mm
7fe9fc9d-ce4c-5fdc-981c-9eb1221b76a1 | note | Standard / Specification - TNZ B/2 7.7
c4a2b922-18de-5b71-88f0-2750b02f1965 | note | Verifying Document - Check Sheet
3db4668f-b6ba-5261-a9c2-bcd20f845037 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres
9513b61b-a511-5bca-91c6-30173fbc037b | note | ○ 1 each lane
7da3607a-4699-55b7-bb8e-7c52663d9bd2 | note | Verification Activity: Activity - I
2416c352-f2d7-5a8f-b167-deb21cb9d1cb | note | Verification Activity: By - SE
6e8cc9c8-5b00-4adc-a6e9-47f230791416 | checkpoint | 4.2.1 - Compaction - NDM
b7f3710b-cffa-5be2-ba5f-1223f1fb15e8 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
10f3a5c0-5926-5ab0-97ec-b21dcfd639e2 | note | Acceptance / Conformance Criteria - Ave >98% of MDD
b349e0ae-7e41-50f5-af1d-7130328ea5ed | note | ○ Min >95% of MDD
22cb104f-89e6-5f9d-a3c7-1fa310989772 | note | Standard / Specification - Standard
541e9c50-a090-57a0-b647-6a1723997ec4 | note | Verifying Document - IANZ Accredited Report
950693c1-fb9f-59d2-bc37-ebc52822eceb | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
9e604db6-59fd-51db-9c85-2772775dcce6 | note | Verification Activity: Activity - I
57857c81-0568-5450-8309-1cd4e44b036e | note | Verification Activity: By - SE
d4420a5b-cd73-4346-a802-0097e2f88a90 | section | SECTION 5 - BASECOURSE LAYER ( GAP20)
10113dc6-b701-4794-8adb-c620aba4b023 | checkpoint | 5.1.1 - Stringlines or equivalent
98466c60-d5c9-55ba-8f17-a61c07001262 | note | Detail - Stringlines or equivalent to check finished height of surface.
f633914f-d4b2-516a-a71d-aeb30bff7647 | note | Acceptance / Conformance Criteria - As Per Finished Surface
bc219c31-5a27-573b-bb6b-2b3cad62f3c1 | note | Standard / Specification - Standard
75c541a1-8b1b-5c75-b45b-0908de7b1295 | note | Verifying Document - Check Sheet
99475d4b-6796-558c-b592-6a799351f68c | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
470ec279-8f3d-5246-96df-a065fd226340 | note | ○ 1 set = 5 tests
709f8855-3780-559d-8127-0a86583ae4e1 | note | Verification Activity: Activity - I
644ac416-8f94-5a7e-93d5-1dd1ce1f91be | note | Verification Activity: By - SE
7c8069fb-0484-46d5-bc22-ee25c463dee1 | checkpoint | 5.1.2 - Visual Inspection
2f7ebefe-35b1-589e-bab1-60a1de5571f1 | note | Detail - Visual Inspecction needs to done With an Engineer for Final Surface
461b4d7f-948d-580f-906f-00f4a6bc7e10 | note | Acceptance / Conformance Criteria - Site Instruction
6af6780d-eaa1-51ab-a5c3-5a8ae93e4e19 | note | Standard / Specification - Standard
8e72505d-dc97-5717-9fca-9b2e2542e102 | note | Verifying Document - Visual Inspection
ed34a62f-f847-5169-84ab-e9a5786cd6e0 | note | Testing Quantity Required (based from schedule qtys) - Across Finish Surface
0fdb84c4-e052-57df-b097-38dbbe8b35ce | note | Verification Activity: Activity - W
9bc2c6ce-2c2b-5d1e-bfbc-1ec5c9b177a8 | note | Verification Activity: By - ENG
7816dedf-4e27-4b4f-ba83-6b6602ff6edc | section | SECTION 6 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
bf94b839-8e1c-47da-949c-7d6083965770 | checkpoint | 13.1.2 - As-Builts Red Pen markup
c71d7e9e-e54a-5159-90c9-c1110e8b2f77 | note | Detail - Final inspection of All Work
6207603f-6ebd-5c88-9fea-d7dd10c89bed | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
8e8a29ab-2002-5e4f-896c-d2253ff9df57 | note | ○ Record Any Undercuts or change in Design
4fa751d3-3ba8-57a7-ab64-a800ec2d9892 | note | Standard / Specification - PS 16.7.6
40d7574b-d322-59d3-8847-0756ba62c2a2 | note | Verifying Document - Survey Records, Red Pen Mark up
5ef34e80-d503-582b-a810-3d83e9925ff4 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
dc19dd69-ed30-57a7-9775-0b8887a7be91 | note | Verification Activity: Activity - D
b4e7655a-7b06-5d8a-9761-37c2f537cef0 | note | Verification Activity: By - SV
9d852f4e-6f57-43a6-8743-5f4d4b9be3cc | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
609da9e7-32ac-5fdc-b861-5aa31ea4eaad | textbox | Contractor's Rep Name:
b76d7076-3a03-5ee3-bd03-79c8009be862 | textbox | Engineer's Rep. Name:
0a736cd5-e1f6-5068-b3c5-3355318adf2c | date | Date:
cdf2bf93-e99f-4d0c-973c-b072a751fb61 | signoff | Add Signature
124fc646-e382-486f-909a-e13588048b73 | checklist | DN1210-035 ITP Chipseal Maintenance Strip Rev 0 | itp | DN1210-035 ITP Chipseal Maintenance Strip
65b11ac9-5a1b-4eb7-983f-aa7e00a4c785 | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
3dff1712-f247-4175-975a-296405277f03 | checkpoint | 3.1.1 - Crushing Resistance
a862dd71-8bc9-50be-b589-ed02c0fde5e8 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
2661a42b-6863-5e5c-befb-63177162bb86 | note | Acceptance / Conformance Criteria - >100KN
eb23a052-224e-5e56-9699-23b4ddbaa609 | note | Standard / Specification - NZS4407:2015 Test 3.10
3c767010-3a6a-5d83-814f-9d5d391b29e9 | note | Verifying Document - IANZ Accredited Report
e1ccd43a-a381-5bb2-ab6f-58817c846c60 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
1835baf7-a5e8-58f2-aabf-9507b3875f98 | note | ○ Results to Engineer 2 wks before importing
e3738d83-7b39-54e2-b999-603508e225a6 | note | Verification Activity: Activity - HP
afef9146-367f-5d5f-bea2-c2549d5eca78 | note | Verification Activity: By - ENG
5c1d0425-e66f-492c-82d4-ae4b90fb8550 | signoff | AUTHORITY HOLDPOINT
c6a23203-1140-492f-bf0a-13e700f53966 | checkpoint | 3.1.2 - Soaked CBR
f6f57c89-8475-5f3e-82a4-a7cbffd44966 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
39fb5e53-e54b-54ac-8472-f6a5e9411136 | note | Acceptance / Conformance Criteria - >60%
01ed3192-c731-5c4a-a78d-5b05cc5d233d | note | Standard / Specification - NZS4407:2015 Test 3.15
b4583fbb-c784-5882-8bc5-d06cbbe27fca | note | Verifying Document - IANZ Accredited Report
72c4ff66-84a5-5ef7-ac50-173b444dc8b3 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e125f2a9-9c82-55a8-937d-80a850106ce6 | note | ○ Results to Engineer 2 wks before importing
f8fd44b3-822e-5a49-b538-137ce23eaa6f | note | Verification Activity: Activity - HP
f2b7b5cb-fc01-50a3-8656-2f1d3040195b | note | Verification Activity: By - ENG
fdf239d0-3948-417e-9f94-4e55a14090ee | signoff | AUTHORITY HOLDPOINT
d0b8a1ec-37ae-4b48-9e92-31bc73a8bfc5 | checkpoint | 3.1.3 - Weathering Resistance
9fc0aec3-e9c4-57fe-8bf0-0cb17cd72b51 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
98ace584-b29f-5a9c-89a9-9e3bd315ae83 | note | Acceptance / Conformance Criteria - AA,AB,AC,BA,BB,CB or CA
6f89b397-abad-5e38-b953-b6a9a59cacb0 | note | Standard / Specification - NZS4407:2015 Test 3.11
548d6add-eb52-5ab8-b155-819a6db03ff1 | note | Verifying Document - IANZ Accredited Report
ea13a599-c2e6-5060-b5db-a19ab36bfeae | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
c179b3f2-7db1-5dc3-81f5-02bce28a2586 | note | ○ Results to Engineer 2 wks before importing
1d93c98f-e3bb-511c-a977-b4235fbd3f78 | note | Verification Activity: Activity - HP
c53236f1-cfc5-56c7-9d22-7bd8c24a8fb8 | note | Verification Activity: By - ENG
47a9af5d-1e8d-4b1f-82a5-576d33b6595b | signoff | AUTHORITY HOLDPOINT
7ba3620c-4fe2-4980-b776-d93f07ffe1ea | checkpoint | 3.1.4 - Particle Size Distribution
4921beef-3f32-5dc3-853a-809d6bb32864 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
b90c693e-bc59-5a7e-b424-ee3156bc9ac3 | note | Acceptance / Conformance Criteria - Sieve ¦¦ Percentage Passing
cb59df38-de05-5802-b787-5f94a5501323 | note | 63.0 ¦¦ 100%
62bbb8ea-742e-509b-bab4-71f8d3d3b25d | note | 37.5 ¦¦ 68-90%
3ae1bede-6734-5d0d-a8c5-af6ccf7b01a5 | note | 19 ¦¦ 42-76%
75ae6e60-4ef5-5e27-8021-1d68547be331 | note | 9.5 ¦¦ 26-58%
ae8fb700-5411-5f86-a6a4-14b152ac12f3 | note | 4.75 ¦¦ 16-44%
0f53b4d6-461a-5f29-a4e3-ccb66e68f01e | note | 2.36 ¦¦ 10-33%
7dc4765e-0ed1-52a7-a8e3-0a4831371254 | note | 1.18 ¦¦ 6-24%
25a8ea4f-3fbf-5465-9c2d-7b70cd25f037 | note | 0.425 ¦¦ 3-14%
e228abba-1074-56db-b1de-2f671747dd6a | note | 0.075 ¦¦ 1-6%
ce2d94df-3463-5368-b274-4b676f233b89 | note | Standard / Specification - NZS4407:2015 Test 3.8.1
4ba2169a-68a8-5b0c-9c14-c6273e76eb2e | note | Verifying Document - IANZ Accredited Report
7e2b880a-9c92-5cc5-9f59-573d83aa8740 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
b6557379-64df-5977-a8c3-9093af3db0a1 | note | ○ 0-400 - 2 tests
9d7a56b0-5c68-5f62-99db-0e46910f0beb | note | ○ 400-1,500 - 3 tests
315b97ff-c74e-5d0e-8ed6-07122961e5c5 | note | ○ 1,500-4,000 - 4 tests
2f3b0ba8-d283-5faf-bbd1-8c037cf630c8 | note | ○ >4,000 - 1 test for each additional 1,000m3
c013f400-9705-5b73-8a5d-81cfd0b3f39e | note | — Results to Engineer 2 wks before importing
51567d08-8083-5925-9f3d-988691c7c89e | note | Verification Activity: Activity - HP
a80aae0e-dbfd-5890-a157-b92a95478de9 | note | Verification Activity: By - ENG
3c598d47-6812-43bb-a3dd-78a968f78408 | signoff | AUTHORITY HOLDPOINT
01169230-aa00-4948-903a-bb6b2abc8d3a | checkpoint | 3.1.5 - Maximum Dry Density and Optimum Water Content
2cc63d4a-f908-5df1-ae89-90d7852c05db | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
58a539f4-e2c5-5473-9914-f104e3919e68 | note | Acceptance / Conformance Criteria - Report Value Only
75bd5b06-aa4c-5639-a700-b670b23cac5e | note | Standard / Specification - NZS4402:1986 Test 4.1.2
5d996ad1-14b5-5a1f-b777-ed0b72398e32 | note | Verifying Document - IANZ Accredited Report
00666406-0655-5238-8ebd-77e4f01f7e88 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, PerSource
4a923744-7195-5b66-98c0-5128ac72ac58 | note | Verification Activity: Activity - HP
20d85d74-edb8-5bca-bf06-83d5cf7675d6 | note | Verification Activity: By - ENG
6ee76c85-6970-4416-959d-25ccdd011f23 | signoff | AUTHORITY HOLDPOINT
85be88e7-a81d-4bcc-b676-2c11404f6317 | checkpoint | on - Plasticity Index
f6a6fb2a-3944-577f-b496-bc782e819bec | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
431fd072-3447-5fd6-91b7-3c9d95148679 | note | Acceptance / Conformance Criteria - <8
ec627743-7be7-57d6-ba66-c65fd3829c97 | note | Standard / Specification - NZS4407:2015 Test 3.4
1c96e873-4bb5-50ab-aa0b-87c2423848da | note | Verifying Document - IANZ Accredited Report
4fb0d4c6-3f97-56bc-aa0c-ca64f1f716b1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
7e24eb0e-c5a4-5dad-8942-5c425ce63254 | note | ○ Results to Engineer 2 wks before importing
89654d60-b40c-57fa-ab41-c662ab7574aa | note | Verification Activity: Activity - HP
8a78fdd2-0b64-5856-91a9-09d6bf9c81c4 | note | Verification Activity: By - ENG
903d482d-6c38-4a26-9eec-f510684266c3 | signoff | AUTHORITY HOLDPOINT
c93a65f6-72e8-4377-aafd-9a60ef027ac9 | checkpoint | 3.1.7 - Sand Equivalent
9842f7a5-6da9-59d3-96c1-6a2b0f91e117 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
3fd198d5-2b71-5f12-91c1-3ac2829fcdbf | note | Acceptance / Conformance Criteria - >25
4fa3f497-2c1f-5431-9261-f3799fb77238 | note | Standard / Specification - NZS4407:2015 Test 3.6
43f32e2f-4019-5de2-bcab-e98ce0209bbc | note | Verifying Document - IANZ Accredited Report
030e168f-3da3-549c-a424-68db5c76903d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
c720c0bb-6560-5ebe-b99e-0644dabbeecd | note | ○ Results to Engineer 2 wks before importing
dba8eda5-98e0-523e-b924-b8ae006e75ac | note | Verification Activity: Activity - HP
b06a1bd0-407d-57df-99f9-2afeca4df244 | note | Verification Activity: By - ENG
22b0819f-baea-4856-810b-ba1428aa4394 | signoff | AUTHORITY HOLDPOINT
6544f0ad-6bc7-41a9-a02e-6d7771bc82d6 | checkpoint | 3.2.1 - Chipseal Design
4d1c9ab8-225e-514e-b991-1d424f1c9080 | note | Detail - Peer review by WSP
9748632b-f00c-58ae-ba48-105ba1a9fad9 | note | Acceptance / Conformance Criteria - Approval From WSP
bd42c85c-7ca7-5ae5-940f-8f63c792bf42 | note | Standard / Specification - Design meets requirements of P17
43824c69-f519-55dd-a591-93f69c1ea7af | note | Verifying Document - Seal Design Report
d69e9ebf-e5bf-54d9-b8b6-e5f730e02e9a | note | Testing Quantity Required (based from schedule qtys) - Once
622e4faa-d1cb-529f-9687-e1463f481021 | note | Verification Activity: Activity - HP
e718a66e-f0a6-5393-b4f6-ddc571d71f49 | note | Verification Activity: By - ENG
d990ef57-f41b-43f2-8ad5-f4e398f7d713 | signoff | AUTHORITY HOLDPOINT
21c69dda-6558-4615-a550-dbcf448cde63 | checkpoint | 3.2.2 - Cleanliness (Grades 2-6)
562874f1-76fb-5caf-992b-5092e4cf1b76 | note | Detail - Lab Test
07616b5f-f09c-5631-b61f-2b9e5b96ff61 | note | Acceptance / Conformance Criteria - Cleanness value
c92ab297-e749-556e-b982-d7cef6cc75d2 | note | ○ G2 = 89
ca4a5b8e-02ae-57a5-b6a0-fed0e7735303 | note | ○ G3 = 87
9ae8e9a6-9166-5b4d-997a-66c98fb15a88 | note | ○ G4 = 85
be567912-4ef3-5d34-8433-55e3ecd7ae17 | note | ○ G5 & G6 Report only
726ad1ac-28ae-5407-a4c9-5232c44f3d77 | note | Standard / Specification - NZTA M/6
da10412d-1967-5f00-ae14-6e14e6ca866f | note | Verifying Document - IANZ Accredited Report
d5791e78-d7b6-5a89-bf28-18ab8ad94d66 | note | Testing Quantity Required (based from schedule qtys) - 1/500m3
8bac5b0f-fd15-5c71-ba79-ed6d45f668b7 | note | Verification Activity: Activity - HP
1aacedc7-38c6-5b92-beeb-91d7878be491 | note | Verification Activity: By - ENG
638e0a81-6c83-4e9d-a908-2e3630230faf | signoff | AUTHORITY HOLDPOINT
242369bd-a9a3-4a39-8524-5061018eb008 | checkpoint | 3.2.3 - Compatibility (Multi Layered seals)
cae367ac-62e8-56f6-9f4a-5ad0ea5a44b2 | note | Detail - Comparison Of Chip ALD 6.84, 3.62
ab5ebde4-5d45-51bd-a0a9-00bc006c7945 | note | Acceptance / Conformance Criteria - Two Coat Seal Aggregate Compatibility graph
8c34dc2c-b0fd-5bb9-be3f-2cca05bff3f6 | note | Standard / Specification - Chipsealing in New Zealand NZTA (NZTA 2005)
b20c23d5-caec-5a63-8059-45350c15f335 | note | Verifying Document - IANZ Accredited Report
0205c92b-e647-540b-83f7-a1e733744d59 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
42f06dfb-42cf-5554-a05e-ced2058a6cec | note | Verification Activity: Activity - HP
71b9b18f-1edc-53fc-a2cc-234bf7ae9dd0 | note | Verification Activity: By - ENG
dd3556d0-266f-46e3-a72c-f7b10a3ad55e | signoff | AUTHORITY HOLDPOINT
e3d0c4fc-425d-4f56-aca1-f5115e5a1248 | checkpoint | 3.2.4 - Bitumen Distributor
9ef1a582-03c0-5764-bb9e-aa7ef2d5b431 | note | Detail - Code of Compliance, IANZ Lab E/2 Results
8d13f41c-3e4b-5bd3-9229-083104f7a611 | note | Acceptance / Conformance Criteria - Speed Test(+-3% over 100m), Dipstick Test (+-50L over 2000L), Matt Test (app rate within 0.10L/m2, longitudinal within 10%, thirds within 5%, transverse within 20%)
cf03413f-47af-577f-9fd6-9aa0747e1197 | note | Standard / Specification - Code of Compliance
d162c6e0-f10a-5303-89c0-354633f78fe0 | note | Verifying Document - RNZ E2 Certificate
35550db4-ef3b-5ce4-927e-24db08a4455e | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
66691670-debe-5d18-a07c-ace6f85dd391 | note | Verification Activity: Activity - HP
c7f0315e-3195-5678-9914-5e4f8e4be67a | note | Verification Activity: By - ENG
98a257e8-df4e-4ab1-ad19-7629d3076a0f | signoff | AUTHORITY HOLDPOINT
f59c3657-1e50-478d-a033-dbbcaea0388f | checkpoint | 3.2.5 - Emulsion / BitumenTesting
e1af66bc-5ae7-5d09-a1bc-4eefbb97b672 | note | Detail - Manufacture Specification
b413e25a-3738-5ce0-af82-5630d426e8bf | note | Acceptance / Conformance Criteria - Bitumen Content, ITM 11-01, Viscosity, ITM 10-02, PH ITM-08-02
33105115-90d6-5d55-9cf7-09c07b7a1327 | note | Standard / Specification - P/3
f27f1537-0414-5a11-9c2e-90ea8b3f9087 | note | Verifying Document - Lab Testing
0da2997c-fa82-56b4-89de-d5c27c0a1b73 | note | Testing Quantity Required (based from schedule qtys) - Per Emulsion/Bitumen Production Batch
733a4fc4-6cf2-57bf-afdc-7d9334578909 | note | Verification Activity: Activity - HP
32348c54-0a8e-581a-a53b-3b486c381823 | note | Verification Activity: By - ENG
aa8eb496-d8c4-4589-a034-13cb5f95be90 | signoff | AUTHORITY HOLDPOINT
9a6ef4d3-7a4e-45da-af38-10b486e621f7 | section | SECTION 4 - CONSTRUCTION - SUBBASE CONSTRUCTION - PREP GENERAL
76cbb3b7-45c7-4faf-8869-60e5cf22d714 | checkpoint | 4.1 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
baf37d65-529d-5caa-b124-4afb112fe3c3 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
583cf331-c7db-5d2c-97ce-70c2d12558db | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
0fceb1cb-33e1-5094-85e8-b985dbaf41ff | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
fd7a6c6d-7b57-59ae-9507-e3a484e9a874 | note | Standard / Specification - PS 27.4.2
26a3c472-ae04-5224-95e4-be40c5d89d05 | note | Verifying Document - Scala Report
c82ab715-2118-58fe-be5c-6d665d0602b5 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
f91277d8-eba6-56a3-ba17-5bce7b1f1f14 | note | Verification Activity: Activity - I
dbe28377-5316-53af-b2e5-9383db9e9fad | note | Verification Activity: By - SE
825b0133-aaed-4060-9930-1283906dec93 | checkpoint | 4.2 - Proof roll
eafbee92-4abe-531c-b0fd-6b817828ee37 | note | Detail - Visual Inspection of Proof Roll
e1c82d63-31e1-5ecf-b8cb-7d1162f0420e | note | Acceptance / Conformance Criteria - Visual Inspection of Proof Roll
9f75430c-88de-5c63-b0f6-6166a2c1ac7c | note | Standard / Specification - Appendix XVIII
b33b1865-be9b-5628-abf3-d84fdbbc62fa | note | Verifying Document - Visual inspection/ Photos
aa8faf81-d620-555c-af1b-528c11ebb7ea | note | Testing Quantity Required (based from schedule qtys) - Across Whole are
2ae7c0bc-8977-5ac7-bb2a-be32551a5263 | note | Verification Activity: Activity - I
4148c30a-5363-5dc8-ae4c-9f014c6a8009 | note | Verification Activity: By - ENG
67de7f7e-3bca-4845-8cb2-02e87362f594 | checkpoint | 4.3 - Compaction structural fill - NDM
b5714e25-fa15-58ea-89d0-668def0f0d90 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
a7f63d59-aeae-5c73-ad83-186d1f3a7ffc | note | Acceptance / Conformance Criteria - Ave >98% of MDD
4339c9f6-bc6b-501a-a20a-8cfeca80d056 | note | ○ Min >95% of MDD
103a9c94-2aac-5fca-9aa2-68c27f891c96 | note | Standard / Specification - NZTA B/02 7.6
cc145703-b7db-5c93-9d3f-c91516022ff1 | note | Verifying Document - IANZ Accredited Report
73956004-b9e6-5bb9-8c32-97e057307dd9 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
23a12bc5-a82a-5be5-8a2f-f186df55c20e | note | Verification Activity: Activity - I
6f3e6b26-96d1-5328-8436-78bf78fbed9f | note | Verification Activity: By - SE
8a8e8c35-5f7b-45e2-b932-6ab33873b7b8 | section | SECTION 5 - CONSTRUCTION - CHIPSEAL CONSTRUCTION
e788e0b4-0065-4af7-a5ea-1c28c828500a | checkpoint | 5.1 - Pre Seal Survey
b1a996bb-51f7-5c9f-b70d-80d6ee90a5de | note | Detail - Survey to mark out setout
7e6b0850-6dbe-5574-af36-ba8645c6fca2 | note | Acceptance / Conformance Criteria - As per Design
19655ecd-aa99-5171-877e-e0fd87a21d7b | note | Standard / Specification - Standard
3e22b1d8-0cc4-5b78-80a5-9e13fd2120cd | note | Verifying Document - Survey Records
4e1816d9-6a00-5ed9-8889-f4f369a2ce08 | note | Testing Quantity Required (based from schedule qtys) - Once - across Whole Zone
ac97b1ce-a27e-517f-89a2-7b7d2de28f81 | note | Verification Activity: Activity - I
47f1aaeb-565c-5060-9b68-59b11a70354f | note | Verification Activity: By - SE
a8af9c73-5f5d-42ec-bb24-224b0fc435a0 | checkpoint | 5.2 - Pre seal Inspection
c77de437-d5d4-5791-bc27-bca5cbc75814 | note | Detail - Pre Seal Inspection needs to be done by WSP.
d6f47da3-2c1b-5f04-a452-1b3ae2a5861c | note | Acceptance / Conformance Criteria - Visual Inspection
bc605a34-6901-5529-9733-556c08b59e1c | note | Standard / Specification - Standard
664b3bbc-0ef2-5778-b81f-42b2fd75ceaf | note | Verifying Document - Visual inspection/ Photos
39cb4642-e4cc-5c6c-b27e-6908c8a58460 | note | Testing Quantity Required (based from schedule qtys) - Once - across Whole Zone
004ae4f4-9429-5401-8529-4a1bb71e5e10 | note | Verification Activity: Activity - I
077839ae-0e46-56c5-9418-3afe078dac57 | note | Verification Activity: By - SE
797b95f7-c808-4d35-862b-979cfc38858e | checkpoint | 5.3 - Road Furniture
710a2bcf-3dfd-533e-a53b-80a8ec4eb5a0 | note | Detail - Protect all road furniture in accordance with Crew Breifing Plan (Signs sockets Etc)
d9bbd2f2-dc3d-5e51-adab-7b0585b2f4fe | note | Acceptance / Conformance Criteria - General
bd46b832-1c84-501e-b624-1633475453f3 | note | Standard / Specification - Standard
5255342a-2587-5372-80b5-bf6c5f07b7cf | note | Verifying Document - Crew Briefing Plan
e686805b-5a8d-5438-ac5b-a5e2239448fb | note | Testing Quantity Required (based from schedule qtys) - continous - across whole Zone
54247f91-7dce-5352-8ed0-4a95c7b985a8 | note | Verification Activity: Activity - I
44eb812a-fff6-5dc2-a5f0-cf287cf41f7d | note | Verification Activity: By - SE
80decffc-5152-472b-a545-bb34171e89d0 | checkpoint | 5.4 - Kerbs protected
5abe1a6c-9401-578a-a4d6-b18560bd7c65 | note | Detail - Fabric & protect all kerb ande chanel where required
87cef03b-ec14-5cdc-bf53-7ce7ed194918 | note | Acceptance / Conformance Criteria - Visual Inspection
ae98fd3a-675c-5f07-acc5-81ba2976abe4 | note | Standard / Specification - TNZ P/3
7330d894-c555-5187-9dec-7584e9a05278 | note | Verifying Document - Visual inspection/ Photos
9a79f84c-a7ac-53f2-ac7a-80e5cbd0f10c | note | Testing Quantity Required (based from schedule qtys) - continous - across Whole Zone
dc17907e-5106-5198-8225-25be98ef25df | note | Verification Activity: Activity - I
4a42e4d0-21f7-528c-99ad-ed918a49284a | note | Verification Activity: By - SE
280d313f-d630-4596-8464-f26c9f58cb3e | checkpoint | 5.5 - Spraying
4f995ee1-c5f8-5861-b172-f15d1eaaa05c | note | Detail - Mark out start / Finish
9a4bdd16-d88f-5098-b1b1-429834ef3965 | note | Acceptance / Conformance Criteria - Paper Start and Finish all runs
4141f0de-642f-59d9-86a4-18561a69502d | note | Standard / Specification - TNZ P/3
fb983a1b-fa12-53af-9628-699eb063192a | note | Verifying Document - Spray Sheet
b4f1474f-bad1-5782-b58c-71d23848b190 | note | Testing Quantity Required (based from schedule qtys) - continous - across Whole Zone
76af2d27-6da3-53ab-b69f-6a6a8f75fd65 | note | Verification Activity: Activity - I
7902ada5-373f-5489-8cef-3c5ed51d7dab | note | Verification Activity: By - SE
e81710a1-49d8-46e3-b299-5884b13163f0 | checkpoint | 5.6 - Removal of Surplus Chip
35a7a2c2-0dfd-5a6d-ba16-c8e6122a0ebb | note | Detail - All sump and road furniture protection removed.
e7fb9517-ff08-5671-9a03-533c5763b543 | note | Acceptance / Conformance Criteria - Visual Inspection
4997c9d6-4148-5424-a6e1-152d85fa6ab6 | note | Standard / Specification - Standard
e506ef88-fc2f-5e97-8f21-b81a646a3a89 | note | Verifying Document - Visual inspection/ Photos
a431171f-5b69-514c-9e12-6c9e8f6fa6e2 | note | Testing Quantity Required (based from schedule qtys) - continous - across Whole Zone
cd0a9c88-42ab-5442-9a3d-9515917ef0d3 | note | Verification Activity: Activity - I
e728cbc7-f25b-50c5-b1f3-132752086f38 | note | Verification Activity: By - SE
c253cca1-c41b-4df7-bb7a-58aa2858e84e | section | SECTION 6 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
7e42faf3-1b4b-4b4d-99af-c5d07bb1d2e6 | checkpoint | 6.1 - As-Builts Red Pen markup
9608d276-ce32-544c-9877-4d6f0ae7bbfd | note | Detail - Final inspection of All Work
80d4d01d-2122-57cb-8553-0fc30276ecdb | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
79bfcd3c-e3b5-5f71-b550-6a976b310c15 | note | ○ Record Any Undercuts or change in Design
4920c710-b88e-58a3-b0fa-5222f0316b84 | note | Standard / Specification - PS 16.7.6
df10681e-57e1-5822-943b-83f5e88180ab | note | Verifying Document - Survey Records, Red Pen Mark up
a24e3d8d-5549-5547-bb94-67067a68b18c | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
e0b90e06-a91f-5eda-947d-fa57ba6fa860 | note | Verification Activity: Activity - D
370d10a4-b429-5513-9039-475f15c41748 | note | Verification Activity: By - SV
dc514287-4167-40d5-ba8f-ec674627cf47 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
d744573d-6eca-5887-850b-4ae18cc91bb6 | textbox | Contractor's Rep Name:
690b8cea-7fff-5d23-a952-514f93a12c73 | textbox | Engineer's Rep. Name:
8ce6c2a9-8f76-5926-b89e-d53ee5848e76 | date | Date:
3d5910c9-d40c-4a91-9eed-8e8393292d2d | signoff | Add Signature
665fe277-920f-40e1-b45d-74fe2ab878e6 | checklist | DN1210-037 ITP Wetland 2 Outlet Rip Rap Rev 1 | itp | DN1210-037 ITP Wetland 2 Outlet Rip Rap
5a60b481-19f5-414d-9ad4-027a5c312e59 | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
e1672e43-0d00-4847-ae7d-6fa96fd89594 | checkpoint | 3.1 - Earthworks Methodology
fdeec041-f5b3-5d9d-bba6-30a7278ac9c8 | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points for review and approval prior to works.
5113c588-3838-5d29-b70a-86b4d3f45e0c | note | Acceptance / Conformance Criteria - Engineers Approval
947a1d2f-a80c-5ef9-a461-84a05090ca9f | note | Standard / Specification - Appendix V
6a33c3c0-f558-5874-9972-e0073b03d91d | note | Verifying Document - Approved Methodology
9a254f2f-476b-53cd-a2f6-6c52fff71756 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
d426c81a-8931-558c-924c-8a45669f82f1 | note | Verification Activity: Activity - HP
6eafb165-ba17-5b56-87c2-66dff7391d3c | note | Verification Activity: By - ENG
b581e91d-09df-47d8-9787-cb464d71b200 | signoff | AUTHORITY HOLDPOINT
efe635a4-12d7-4462-a263-12b9a9070184 | checkpoint | 3.2 - Ecology Sign Off
7aa04f2c-69f0-56df-a672-7f488f28c91c | note | Detail - Confirmation from Ecology that earthworks can proceed
46303c03-81fa-5e20-b9ea-21d755d04682 | note | Acceptance / Conformance Criteria - Email
d535f23a-84c0-5de6-8ec0-c25da103e3f7 | note | Standard / Specification - Internal Hold Point
c5f07b2d-532e-5c31-ba50-f45b573c6f32 | note | Verifying Document - Email from Ecology NZ
db436119-4c7c-52f4-a5bd-9f5eafabee67 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
d9f0259d-e2f1-5250-b260-8b0dc599e190 | note | Verification Activity: Activity - H
113a647e-27ba-5c5c-9e60-078bfdd22a46 | note | Verification Activity: By - SE
59931675-c139-4c9e-8cbf-b119834e268c | checkpoint | 3.3 - Erosion & Sedimentation Controls
3a1d4974-6465-53c5-8bd0-d4b8317f4f10 | note | Detail - Confirm that Erosion and Sedimentation Controls are in place prior to earthworks proceeding
97e28c3c-43eb-542d-a930-3ed5974b9f8e | note | Acceptance / Conformance Criteria - As-built Completed
3ac51ed5-6628-59ae-8a17-1e41b32e9bcd | note | Standard / Specification - Internal Hold Point
faff2018-0b35-532c-a10c-7a5e9e4c06a4 | note | Verifying Document - ESC As-built
071e8400-3160-5b03-9422-8ea4dcf84a96 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
d7e1b7d1-34aa-5e8a-846b-5e476f4a4357 | note | Verification Activity: Activity - H
fbfe2de5-6fc2-5e89-8815-4b572fca8547 | note | Verification Activity: By - SE
d42d3cb8-e3eb-4bbd-8e1a-032ccfb62db2 | checkpoint | 3.4 - Design / Setout (1)
f81c4b04-a81e-50ad-9fba-7af96f425416 | note | Detail - Ensure that Design is approved and Drawings are of the latest revision
6cf263ea-f2e3-57d4-8ec9-0566c989c7d7 | note | Acceptance / Conformance Criteria - Visual inspection by Engineer
fb18071d-b85a-577b-b4a6-abfd8756c8e8 | note | Standard / Specification - Internal hold point
68902a22-3240-5d9f-abcf-452c34eb81ae | note | Verifying Document - Check Drawing Register
02a8f2e2-4f4c-5ddc-a48b-d2de0770869a | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
727a0981-7ec6-522d-a3e3-ea2f1f0e8471 | note | Verification Activity: Activity - C
e3ad06aa-f555-5221-bf93-e1ef7932ae20 | note | Verification Activity: By - SE
382a7046-a627-4853-8677-32938ef49975 | checkpoint | 3.4 - Design / Setout (2)
624fa637-5ff8-5aa1-86fa-2c8cfa8ea154 | note | Detail - Site check for service features, any required design amendments to be resolved on site
0405d119-04e3-5734-af68-032cbacbf5eb | note | Acceptance / Conformance Criteria - Visual inspection by Engineer
bdfe7afe-c625-5426-9598-74e7b9b3fe31 | note | Standard / Specification - Internal hold point
b58e796d-6b1c-5689-9c4c-84bca3d8e433 | note | Verifying Document - Engineer notified of design amendments to be resolved
be2f841a-15ac-5388-85d8-b7f7fb1a0de9 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
018e6c43-a716-5597-98ea-c2145805962e | note | Verification Activity: Activity - C
3bf474c0-7541-5a89-91c1-7de08d739e2a | note | Verification Activity: By - SE
f611c0d2-e7a9-404f-8282-5552143d851e | section | SECTION 4 - IMPORTED MATERIAL TESTING - ALL TESTS TO BE NO OLDER THAN 3 MONTHS
8582edd3-2a4a-4bb4-b3c1-08070a476798 | checkpoint | 4.1 - D50 = 250mm Rip Rap rock testing - Weathering Index of Coarse Aggregate
fda9a9ae-868e-5947-ad75-e063290fa03e | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
44275bba-7f2e-51ff-a52a-ac855aa8f5eb | note | Acceptance / Conformance Criteria - AA to CA
8e71b7b5-7cdc-50a0-b101-da54fc2b15bc | note | Standard / Specification - NZS4407:2015 Test 3.11 PS 21.7.4
de2c1ff8-18ac-54a2-8bb7-2d221d781548 | note | Verifying Document - IANZ Accredited Report
b2862fa3-623f-5ded-90f0-29724559d97e | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
937b2778-6812-5d9f-95c2-7903fcb0ea2f | note | Verification Activity: Activity - HP
99df8cec-9c0f-50e8-bcaf-5d5a780e485f | note | Verification Activity: By - ENG
03a2725b-2812-4e45-8cfe-52f207e1ba84 | signoff | AUTHORITY HOLDPOINT
3b0c54ca-7832-4453-b6a0-102949579cab | checkpoint | 4.2 - D50 = 250mm Rip rap rock testing - Crushing Resistance of Course Aggregate
0bc6dab0-6a3f-5ab0-a293-4314ab5bc8da | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
cdee72a0-8595-5a27-8c22-777b5d3cb9a3 | note | Acceptance / Conformance Criteria - > 150kN
3c89291f-1c96-5675-9815-a949f8bd5780 | note | Standard / Specification - NZS4407.3.10 PS 21.7.4
d7576f1e-8983-5757-a234-2c7dced049bd | note | Verifying Document - IANZ Accredited Report
2e5150c1-762b-52ab-a446-bb0048053123 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
367449e5-9db8-57aa-b184-c416ae5dc82b | note | Verification Activity: Activity - HP
8ae09398-04c6-5b08-a00b-1087688f8bc8 | note | Verification Activity: By - ENG
9f784bf5-5e7b-43a6-a6c8-ea89efe823eb | signoff | AUTHORITY HOLDPOINT
3ebc2fc2-b95d-4fc2-8089-452242139332 | checkpoint | 4.3 - D50 = 250mm Rip rap rock testing - Solid Density of Aggregate
cc3645d9-2bd2-5ae6-a8e0-446d87a45ce3 | note | Detail - NZS4407:2015, Test 3.7.1 - The Solid Density of Aggregate Particles
d58ee5a8-7b2d-5e98-852f-12bf40fd1683 | note | Acceptance / Conformance Criteria - ≥ 2.65 tonnes per m3
98a0ec30-2239-56c4-953a-7acd9d89c13d | note | Standard / Specification - NZS4407.3.7.1 PS 21.7.4
02d6440f-744f-5f51-88e3-52f9de5a7dda | note | Verifying Document - IANZ Accredited Report
deb1b633-f0ee-5f7d-870b-d5fbde00f6e5 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
f93a6984-d01c-52ab-915f-dac71e9239eb | note | Verification Activity: Activity - HP
6abe8f7a-6ac7-5cf9-b950-2dd7d9c41ef6 | note | Verification Activity: By - ENG
37ada6a3-c4b1-404b-af26-81551bd1e690 | signoff | AUTHORITY HOLDPOINT
ddc29299-ee27-42c3-88b8-f3a6228b53d4 | checkpoint | 4.4 - Rip rap rock testing - Grading
d91e3523-efe4-57d8-ab3d-72acdb599ef0 | note | Detail - NZS4407:2015, Test 3.8.2 - Grading of Aggregates by method of dry sieving.
6c3aeca5-dcab-54a2-93a5-273241d9e936 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
cc3a10de-f9d7-534f-a66a-667fb4633511 | note | 230.0mm ¦¦ 85% passing
e0156d4f-6683-5003-8bdb-17060a46eb45 | note | 150.0mm ¦¦ 50% passing
d99b0ba7-1e1e-558a-9054-af878283bd56 | note | 95.0mm ¦¦ 15% passing
9f017db6-cdcb-50fb-91d3-1a09d3859bfc | note | Standard / Specification - NZS4407.3.8.2, PS 21.5.14
0e189540-b827-580f-980a-7a1a5c18ffcb | note | Verifying Document - IANZ Accredited Report
74d88afb-fe8d-5f4e-a8bd-91778e0b44a8 | note | Testing Quantity Required (based from schedule qtys) - Percentage Passing %50
7882d9c0-0fcd-5335-8c7a-7f0eedcfa47f | note | Verification Activity: Activity - HP
2e168051-1ef2-5f50-b949-2131a4d7cc89 | note | Verification Activity: By - ENG
8014e927-91e3-4167-a974-641619090078 | signoff | AUTHORITY HOLDPOINT
81071b69-7cd4-49ad-a89e-5e1eed069dee | checkpoint | 4.5 - Rip rap rock testing - Point Load Strength
02e3a2db-e92d-5318-9346-df8fb7a834c0 | note | Detail - ASTM-D5731: 2017, Standard Test Method for Determination of the Point Load Strength Index of Rock and Application to Rock Strength Classifications
359bc570-b65a-5ddd-9b54-d84a2aefb283 | note | Acceptance / Conformance Criteria - >1.5 MPa
9421d252-62f8-5e16-9182-ebacc9800603 | note | Standard / Specification - ASTM D5731 PS 21.7.4
fa35df74-c53d-59aa-af24-ee9557c3a2bc | note | Verifying Document - IANZ Accredited Report
25bb1e5e-6bd8-542c-bb69-123e00a0c0b7 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
124a1e7a-b12b-558a-807a-dc749d47a78d | note | Verification Activity: Activity - HP
60efa886-946e-5a45-9aa4-eda99a820303 | note | Verification Activity: By - ENG
cad7c421-754e-4e01-ab58-810366dc6f2b | signoff | AUTHORITY HOLDPOINT
7e4b3496-9745-4ee1-abd4-3e64e1112fe3 | checkpoint | 4.6 - Rip rap rock testing - UCS Rock
05c0595f-b327-5d43-a6e2-b8b8876410c4 | note | Detail - AS4133.4.2.1: 2022, Method 4.2.1: Rock strength tests – Determination of uniaxial compressive strength
3046fb8b-af1d-5930-b58e-80659d8f2f21 | note | Acceptance / Conformance Criteria - >30 Mpa
88124f16-31c1-5285-9d2d-ecbfb805bda9 | note | Standard / Specification - AS4133.4.2.1 PS21.7.4
a8da1d28-7461-53c7-a1e3-ec868dc1aaa4 | note | Verifying Document - IANZ Accredited Report
b59e04e8-050d-5726-8ae0-f5b039c532d5 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
f47b16fd-ca5c-578a-8cfd-ab705af73078 | note | Verification Activity: Activity - HP
c956fc14-a39e-5b35-9063-9bffa53f347c | note | Verification Activity: By - ENG
c4c2897f-47e4-4d58-a116-e88d65fb42ab | signoff | AUTHORITY HOLDPOINT
3f04813b-f50a-4f24-87cd-d619d3f7eb35 | checkpoint | 4.5.1 - Geotextile
18a69e6b-f95d-5892-b700-fea069db8e10 | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation. Class C & Filtration Class 1
ac268961-3436-54f0-aa96-dfded4bb8d05 | note | Acceptance / Conformance Criteria - Engineers Approval
bf15757f-92e6-5d84-a124-80cbeb204696 | note | Standard / Specification - PS 16.5.7, Appendix V
45281675-b388-5308-9824-5f886823eb9f | note | Verifying Document - Delivery Docket/Material certificate
6036a060-3af7-542e-b195-c29b2c2d5882 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
2248b780-3b2d-56fe-9ba1-34e4a736d885 | note | Verification Activity: Activity - HP
9bd72fed-f2ff-5de6-9bde-4540b0a712e0 | note | Verification Activity: By - ENG
936709dd-fe6d-4f3a-a4e0-3b65e643bd2e | signoff | AUTHORITY HOLDPOINT
ae7f10cc-3cff-418f-abd0-1e2e243f480b | section | SECTION 5 - Imported/Site Won Material Testing - ALL TESTS TO BE NO OLDER THAN 3 MONTHS
4181d250-ad5a-4963-98ef-5b569535bad7 | checkpoint | 5.1.1 - Site topsoil - Laboratory Testing for Soil Suitability
5dfcc90d-564a-50bf-b3ad-bca7a6298f18 | note | Detail - Soil Test Results from Hill Laboratories to confirm that topsoil suitable to for reuse
6a6e9a6b-742b-59cb-ba2f-a470686ab1a2 | note | ○ Soil Reaction
929cb53d-0982-51c5-a522-32ddf6ae0ef9 | note | ○ Electrical Conductivity
9541df08-5616-5fe5-a59e-50ac14c9b4bf | note | ○ Mechanical Analysis (texture)
36ce0c4d-228d-5874-b24d-95d94fd88da9 | note | ○ Stone Content
9f5853e7-eced-5c58-abff-0fe1086fae90 | note | ○ Nutrient Levels of nitrogen, available phosphorus, available potassium and available magnesium
0ddfd454-d5f8-5096-bea1-3d99ce6a03d1 | note | ○ Organic Matter Content
c374987f-0ba9-54a9-bdc0-c0ae7367b6f1 | note | ○ Check for Toxic or Hazardous substances
5c2dbb4a-db21-5e2e-af99-b37db07990f3 | note | Acceptance / Conformance Criteria - Engineers Approval
e6b4e862-6a2c-5d33-9844-a05044abafd0 | note | Standard / Specification - NZTA P39:2013 3.1
109b7e51-eeee-506f-ab5f-e68e5ccae59d | note | Verifying Document - Laboratories Test Report
2b056f94-64ce-55ab-b1fc-8ec98522e075 | note | Testing Quantity Required (based from schedule qtys) - 10 equal samples taken from site, mixed together, then 1kg of soil sealed into a plastic bag and sent to lab for sampling
1a26b966-16d5-54c8-b30d-ded1d12dd92c | note | Verification Activity: Activity - I
912ef170-8c4c-5fdb-968a-289961588592 | note | Verification Activity: By - SE
4c75abad-9d23-4b2b-8811-ed645f3dbbbc | section | SECTION 6 - EARTHWORKS
c2d071cf-0f62-45f2-92da-1750fcb4e201 | checkpoint | 6.1.1 - Foundation / Subgrade Suitability - Free of organics / unsuitable material
7da66d98-8c5b-580e-89f7-c153c7037324 | note | Detail - Undercut all organic, soft, or unsuitable soils to below subgrade
0377230d-971a-55e7-9d28-bed6b3cfbda1 | note | Acceptance / Conformance Criteria - Visual inspection
d43135c3-ba46-50e9-9cb8-f944f53f3d47 | note | Standard / Specification - PS 16.6.4b, PS 16.7.4
ed1d11aa-5004-568d-ab68-219991230658 | note | Verifying Document - Photos
ef60471c-079d-5baf-8614-0f8d713cfb6a | note | Testing Quantity Required (based from schedule qtys) - Post contouring
00b8f306-cd6c-5efb-ab5b-1c431159a587 | note | Verification Activity: Activity - C
fa1f9c0a-131c-5c1d-b840-e6a101eeffff | note | Verification Activity: By - SE
a4955051-4cff-435a-8baa-f0e88d3ace93 | checkpoint | 6.1.2 - Foundation / Subgrade Suitability - Scala Penetrometer
64d2560a-33d5-5a33-b91f-7d25d2c847b7 | note | Detail - Scala testing to meet requirements of Project Specification for cut subgrade
491c3d35-9299-500b-9825-17998ecbd468 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
2c5dec8e-ccda-5d7d-a1a5-f280ce18826c | note | Standard / Specification - PS 16.7.4
9182edee-fec9-5c8c-94a4-d991940df521 | note | Verifying Document - Test Reports
f084ad95-07be-5c00-9acd-996a7aa6db83 | note | Testing Quantity Required (based from schedule qtys) - 4 tests per 400m2
0c4532a5-409f-5f0a-bc2f-bc95769a6a19 | note | Verification Activity: Activity - C
fcd42df6-454e-5439-b222-2b161cd00d75 | note | Verification Activity: By - SE
e08eed73-c9ba-469a-a69e-78a5269f6db6 | checkpoint | 6.1.3 - Foundation / Subgrade Suitability - Shear Vane
e8fa4011-75c9-53df-b3de-84a73461d6dc | note | Detail - Shear vane testing to meet requirements of Project Specification for cut subgrade
3bd0580d-c8d4-534a-b98c-58554bcb16ed | note | Acceptance / Conformance Criteria - Average minimum SU > 60kPA
7eb78857-bd2d-51a9-9b21-9ee2bdc84adb | note | ○ Single test mininium SU > 50kPA
9323e6b4-8a31-5e1b-a18f-5f3287f5678c | note | Standard / Specification - PS 16.7.4
97f3dca5-4461-5377-bcb2-74c1ccd0b490 | note | Verifying Document - Test Reports
53dc3fdd-a0c1-5930-b744-f5a19328ab4b | note | Testing Quantity Required (based from schedule qtys) - 4 tests per 400m2
6d813390-4242-53be-8e33-4af52e08d244 | note | Verification Activity: Activity - C
ca2241b3-4278-5033-8168-460227fb43db | note | Verification Activity: By - SE
4f811a63-7cd7-460b-b1ee-560993d9271b | checkpoint | 6.1.4 - Foundation / Subgrade Suitability - Subgrade Inspection
584cae8d-7593-5808-bc7a-67fb7da630c5 | note | Detail - Engineer to complete visual inspection of subgrade and review scala testing. Where directed by the Engineer, the unsuitable subgrade soils shall be undercut and/or improved.
ecfee509-cbf7-54c7-bf51-b61d99f79e07 | note | Acceptance / Conformance Criteria - Visual inspection
b7b60ff8-8a48-560a-95ed-a8e9581c0a41 | note | Standard / Specification - PS 16.6.4b
516fe4e0-a9c4-5050-9939-58f0ccfcaa51 | note | Verifying Document - Site Instruction
eaab0b48-7a82-599f-92b0-5c63f6733ed0 | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage on all major contours
745917f4-5346-5957-bf27-9a3794160816 | note | Verification Activity: Activity - HP
47c58d54-abd6-5c6b-aa3f-a7dc86b6ba32 | note | Verification Activity: By - ENG
04c33de6-d0a8-412c-8b2a-97b87c110406 | signoff | AUTHORITY HOLDPOINT
7bcb50b5-86cc-4f9d-b2ed-60fdb504e109 | checkpoint | 6.2.1 - Rip Rap Lined Gully - Placement of Geotextile Fabric
7da9aa98-4c28-5457-9827-0bf30cff238d | note | Detail - Place Geotextile Fabric Strength Class C (AS440) & Flitration Class 1 across pavement area, with 500mm overlaps
be5215ef-9bb2-5620-94ed-38bda19636d1 | note | Acceptance / Conformance Criteria - Visual inspection
217546c9-bdf2-5717-aadb-fdd7dc0fb916 | note | Standard / Specification - PS: 21.5.15
2360ca66-d56d-551f-bc39-702333bdf71c | note | Verifying Document - Visual Inspection and photos
e01ba062-e4ec-50db-a9fd-5705f2c8bceb | note | Testing Quantity Required (based from schedule qtys) - Before Rip Rap Placement
fca828e4-f215-5d24-ba88-3d986a4c70ae | note | Verification Activity: Activity - W
2be9148b-ccb8-517a-9ebb-a90c00cbbdb3 | note | Verification Activity: By - SE
9940f94d-9f18-4cbd-924c-91f1e68304ae | checkpoint | 6.2.2 - Rip Rap Lined Gully - Check Levels
51e5dde3-964b-521b-83cd-4b7ee2e95bb4 | note | Detail - Confirm that the rip rap is an average thickness of 600mm
9b4048ab-99ba-593c-8d63-4887aab5e524 | note | Acceptance / Conformance Criteria - String lines - or equivalent
0dbec082-ed3f-513b-af11-97abb4587ac0 | note | ○ Tolerances width -20mm +100mm
8c879598-d927-55f6-b6ba-a93bcc53469c | note | Standard / Specification - TNZ B/02:2005
d988c592-f165-5eca-b9d6-0454111e29d3 | note | Verifying Document - Survey as-builts
09706050-a0e9-5e0a-ba45-d9e8cef7d90d | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage on all major contours
5d2cfa1a-1a5d-58b8-b80e-8dbaea92d575 | note | Verification Activity: Activity - I
09460e0b-4473-5035-b0fa-f62bb03d8b41 | note | Verification Activity: By - SV
de8e37af-011e-4d4c-a015-7cfea0148a48 | checkpoint | 6.2.3 - Rip Rap Lined Gully - Shape/Placement of Rip Rap Rcok and Contoured Adjacent Land
ed95e0c3-0b38-50d1-baaa-594565611dbb | note | Detail - Shape/placement of the rip rap and in relation to the existing ground level and the contoured land adjacent to the rip rap footprint
2986de2f-8e86-521f-9fdb-8643e2ae3af8 | note | Acceptance / Conformance Criteria - Visual inspection
6097c845-3d3c-5fa7-b436-a021aaa3f2e3 | note | Standard / Specification - TNZ B/02:2005
f42fcc26-0dbc-5543-a798-388ddc28bf75 | note | Verifying Document - Photos
bb93f941-6641-56b4-9726-73970865d890 | note | Testing Quantity Required (based from schedule qtys) - Post Rip Rap Placement
1375d944-028a-5026-ad17-af222d68cca3 | note | Verification Activity: Activity - HP
14c0a639-433a-547c-9f0f-db6d7f33197a | note | Verification Activity: By - ENG
8f17379c-c5a8-4ac3-8825-ef04a2fd403f | signoff | AUTHORITY HOLDPOINT
7b5e5d4a-ea9b-4e48-a349-14f15b536b18 | checkpoint | 6.3.1 - Reinstate Existing Topsoil Layer
1751ae3f-3ef6-5950-ac5d-2a0c71654f33 | note | Detail - Reinstate topsoil to existing ground levels pre construction in areas where contouring has not occurred. In areas where contouring has occurred topsoil should be 300mm in thickness
da9dc1be-c14d-5207-862d-5cf9e190c1e5 | note | Acceptance / Conformance Criteria - String lines - or equivalent
b427e1c6-9ac5-55b5-9f77-5e3f7e441c5e | note | ○ Tolerances width -20mm +100mm
29619c4c-ca21-5351-85dd-3d8f8766a6bc | note | Standard / Specification - TNZ B/02:2005 5.1
33e84b16-86da-528f-ac07-dce9f120c352 | note | Verifying Document - Survey as-builts
9275e049-3999-523d-83c6-2ec1c26933a5 | note | Testing Quantity Required (based from schedule qtys) - Post topsoil placmenet
dac00b25-b783-5ac1-8cd3-3d9f191a34d3 | note | Verification Activity: Activity - I
e5da6670-7ef2-5741-8aa4-df4719681094 | note | Verification Activity: By - SV
58be8afa-f40b-4568-ba25-8af74273120d | section | SECTION 7 – AS-BUILTS
82770843-dcfe-4e25-a65c-12c3fb021cf7 | checkpoint | 7.1 - As-Builts
8d7b97c0-48af-54b3-b71f-fffa052bb561 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
1e42d97b-c875-5ae2-ba69-bb25e5d63986 | note | Standard / Specification - PS 16.7.6
106cb073-7ab5-5cb8-a222-8a25a6f8d1e6 | note | Verifying Document - Survey Records/ Redpen markups
addec82b-3d00-50a9-9e08-a5c069c1a5f3 | note | Testing Quantity Required (based from schedule qtys) - Post Earthworks
524a07a1-9153-5f4d-a1fc-ee7f2cd313be | note | Verification Activity: Activity - D
2d3c162b-31b7-525a-9e15-21a532910751 | note | Verification Activity: By - SV
9a9ae8b7-2069-4890-981c-cde99652ff37 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
4d0d4b2a-448f-5404-96d3-3dd28adf2af9 | textbox | Contractor's Rep Name:
846841de-ebf2-5c22-a76d-dc2fdf8dcc0f | textbox | Engineer's Rep. Name:
91d841d1-b661-52dd-bd34-3565abb89e8b | date | Date:
45907337-b16d-4a36-937d-9b121164825c | signoff | Add Signature
210b55bc-f636-4814-a77b-4be5049b8e8c | checklist | DN1210-041 ITP Underpass Stage 2 Rev 2 | itp | DN1210-041 ITP Underpass Stage 2
60a27b51-12e8-4468-8dcc-e2afb4e47b2f | section | SECTION 3 – EARTHWORKS SUBGRADE
80b42f44-3ad6-4ef8-b577-486b2b7b4b6d | checkpoint | 3.1.1 - Cut Subgrade Inspection
9603b7d1-d4d9-5970-8bc7-ecfc39ac0c37 | note | Detail - Engineer to inspect all foundation surface inspections
a830bb79-f434-5042-b00d-c437744116e8 | note | Acceptance / Conformance Criteria - Engineers Approval
110352a2-5604-5bc9-bac5-8361db6b4296 | note | Standard / Specification - Appendix V
58d58c84-f4d2-5dd2-9da2-5fa4b0d74b80 | note | Verifying Document - Visual Observation
9edf51ca-7ad6-527a-8c5d-abd70184f0e0 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
1aa08e97-2966-5804-8caf-38f8270a9aff | note | Verification Activity: Activity - HP
6ebe893d-cc89-5721-95a6-c5086dfb95d5 | note | Verification Activity: By - ENG
5a92e61b-c279-4787-98fa-ba8426144e7b | signoff | AUTHORITY HOLDPOINT
3a47bb9c-b941-4013-ad7a-c59cbfdbb590 | checkpoint | 3.2.1 - Cut Subgrade Testing - Cohesive Soil - Shear Vane
90ab269f-707e-5a9b-bbb0-af1cf44bfd7c | note | Detail - This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
4dc363a6-9b70-5d95-bf50-5b67208971a3 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
f3f6034c-cc3f-552f-b143-84291d3669b5 | note | ○ Single Test Min SU: >50kPa
6c1f4d33-00a9-5b4e-9388-925e2e991891 | note | Standard / Specification - Appendix XVIII
5daf010c-7c79-5306-9876-1d1a1eb2cd87 | note | Verifying Document - Shear Vane Report
7ea06449-6920-53ae-995f-be211bf30448 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
c2c3c450-738d-569e-a9bc-ddb3f0dfa4af | note | Verification Activity: Activity - I
9063403b-7df6-56c8-8874-f71dc8c26f17 | note | Verification Activity: By - SE
bd078fc3-ca85-4f34-8d60-5505d4a4d904 | checkpoint | 3.3.1 - Cut Subgrade Testing - Granular Soil - Scala Penetrometer
d1997c45-d67a-5fcb-aedd-07d8b2c6fb91 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
95adaeb3-8936-52a2-9a9e-54babfa3feca | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
cd8c1b37-b373-5c37-bcef-76adc92efd17 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
c0a3ac9c-7db4-55f5-900a-5a6a859bcbd2 | note | Standard / Specification - Appendix XVIII
16d69987-f4a9-52d4-b66f-63ae691a61bc | note | Verifying Document - Scala Report
598f6310-b920-5255-a650-356715bd465c | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
a4b5024e-6354-5c5c-9614-3f2c7d5afe20 | note | Verification Activity: Activity - I
b2a1dd3c-09b2-5a15-a1d7-c72d671bb25b | note | Verification Activity: By - SE
f235e188-f824-45a4-8de1-3585787ce1a2 | checkpoint | 3.4.1 - Undercut Surface Inspection
2758ffd2-c7b5-5643-a7b2-fcc17811f647 | note | Detail - Engineer to inspect undercut surface and determine undercut requirements.
8ee076ce-6e8b-5584-b93c-731b257937cf | note | Acceptance / Conformance Criteria - Engineers Approval
35feb27a-1301-5578-8bd6-80954a584b9c | note | Standard / Specification - Appendix V
5dba1409-695d-5917-85b8-504bb9446413 | note | Verifying Document - Engineers Approval
3d86bf83-c0b7-5c19-9aad-03f2441a0740 | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
ff6845b2-11c9-5320-a6cf-c5600c9a092a | note | Verification Activity: Activity - WP
09006557-d480-5dd9-9239-2fb6808d802c | note | Verification Activity: By - ENG
1899ac6c-4b02-4593-b34b-3679dd066574 | checkpoint | 3.4.2 - Placement of Geotextile on Undercut
70e4df17-d52c-5793-a092-2b3214eeea8b | note | Detail - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
887991b9-f982-56d3-b882-f0ee96e14e31 | note | Acceptance / Conformance Criteria - Engineers Approval
faa51cf7-8686-5e92-846d-276fa05e54cb | note | Standard / Specification - PS 16.6.4 TNZ F/7: 2003 8.3
33d4d4b2-6bd9-5fc6-85e7-24d850bd9979 | note | Verifying Document - Visual Inspection
e6284094-1f40-5946-b742-6555c1df1a72 | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
11f5dee2-caa9-5e90-9a5b-2bee67cc635d | note | Verification Activity: Activity - WP
aea04915-abf3-573a-8698-93d5ac7990cb | note | Verification Activity: By - ENG
d85cb5f8-1a86-42d6-b1f0-ec45528ce3b5 | checkpoint | 3.4.3 - Backfill undercut
aa8beaf5-5e3a-54b6-b509-6235dfdaf5dc | note | Detail - Backfill undercut with AP100 and lightly compact.
7d281b47-24b2-554c-ba2f-5258effbea5c | note | Acceptance / Conformance Criteria - Engineers Approval
4e4bcda5-94df-5249-91f1-d5032b50f64f | note | Standard / Specification - In Eight ref: DN1210-WSP-NTC-0207
cbb7d312-15a5-51e3-8fb9-e24fe90e1034 | note | Verifying Document - Visual Inspection
f9119c03-8c03-5bfa-9331-9a8e891c4f15 | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
5d5b8264-7951-50c9-a5d0-6a8b4f4b2379 | note | Verification Activity: Activity - I
c1ed22c7-1516-5981-b64f-efe2f7c56226 | note | Verification Activity: By - SE
159cebd4-1d07-4e85-9c89-dcffbaf95d25 | checkpoint | 3.5.1 - Foundation Compliance
74d0e4c9-a9e2-5db7-84aa-ab47a2e55ab1 | note | Detail - On Granular or Cohesive Material
c30413b3-cad6-5c2b-9063-e7eddce1e45f | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
789bb05e-f183-5d20-967f-1e12a30a4c61 | note | ○ Cohesive Material: Shear vane Strength 70kPa
175d1fbb-8904-547e-85be-910b4ea88050 | note | Standard / Specification - PS- 21.7.2 Appendix V
ad4b633e-2e71-525c-b8d5-a6c28f5c5ddc | note | Verifying Document - Scala test result or Shear vane result
9b94a865-c006-51c8-9471-6a39d39a2009 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
3dfb5da4-47d4-516f-b597-e521e35e4016 | note | ○ 0-5m: 1 Tests
6afca8d3-f4d7-5dbb-9eb2-67349a2a5784 | note | ○ 0m-10m: 1 Tests
97022502-e7d4-5ab5-b0fd-0c8ed4e8135b | note | ○ 0m-20m: 2 Tests
41290a87-188a-5a99-b159-49a20840adda | note | ○ 0m-50m: 4 Tests
bbba9151-0522-572a-bbc4-714d0d95884f | note | ○ 0m-100m: 6 Test
4b243abd-5c3a-5a29-9fb7-46ff805710a3 | note | Verification Activity: Activity - W
4d6a49e3-9d39-5e08-802a-a5869335544f | note | Verification Activity: By - SE
c99ffc6e-11e7-47a9-aceb-34da9db2be56 | checkpoint | 3.5.2 - Undercut approval
8d7c0258-774a-500d-98b9-b6ce00848811 | note | Detail - On Subgrade
37f85145-22ce-5b9f-ae0a-2214049a9c1c | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
a63156db-80d6-52e0-a6c5-398085c7fbbb | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
a55e648a-2558-5bcb-93a1-0d1ed3a6dad9 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
5a7cfb53-5cdf-5195-8809-2b0dbd519b7d | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
48f081f5-0f96-546d-a7a6-06ea156face6 | note | Verifying Document - Lab Test Report
36145c28-5f1d-5702-84c3-8ade215efef5 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
bb2bf759-823b-5c08-ae26-5a68536563b8 | note | Verification Activity: Activity - H
3f595762-adf5-5224-9154-5109bb577bb5 | note | Verification Activity: By - SE
3c559e6c-561e-4f2f-bcb6-36b92e508411 | checkpoint | 3.5.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
cc16c3c2-f637-5802-807a-7285d01dffeb | note | Detail - On Granular Material
0d88d314-1c6a-56b9-8373-8f110faefd02 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
03f0f4fd-7423-523a-9e41-bf632c8be8f8 | note | Standard / Specification - PS- 16.5.12
cfa71306-de46-5206-918d-403090b4bd9c | note | Verifying Document - Lab Test Report
67537871-8fad-550b-8f6d-225dedd2d940 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
e7e5df9c-e77a-560a-b535-00b1e75f2cc0 | note | ○ 0-5m: 1 Tests
a7f4abed-21ee-5b71-9ec8-a1579a360c86 | note | ○ 0m-10m: 1 Tests
cd2b57f1-2232-5362-91bc-09a29231297b | note | ○ 0m-20m: 2 Tests
e0ef57f3-a714-5856-8a1b-86116a83038d | note | ○ 0m-50m: 4 Tests
93eae87d-c74d-5134-a968-3b3efe97e027 | note | ○ 0m-100m: 6 Test
3625fa5a-5eda-57bc-afba-785249a2c142 | note | Verification Activity: Activity - H
caa6a2f6-14ac-57aa-9efc-1ddedd8c8595 | note | Verification Activity: By - SE
66b053e8-0a0b-4dc0-a8f1-f411c3fd4f6d | checkpoint | 3.5.4 - Bedding and Embedment Zone Compaction Testing (Polypropylene(civil boss)/Polyethylene Pipe).
5ab05a02-90c6-5b21-83cb-6c832d9deff6 | note | Detail - On Granular Material
5ecee750-811c-5b7c-9b6f-88c477da14be | note | Acceptance / Conformance Criteria - Bedding Zone:
23cccef4-5ac6-5fe9-b730-40aac7a934be | note | — 100mm(for DN300 & DN375)
29bc6af7-a52a-5239-a203-e7fce61cbafc | note | — 150mm (for pipes greater than DN375)
cafd65c5-6424-5402-9510-eb80ddc0fd92 | note | ○ Embedment Zone:
0f1a189b-917a-51ad-9d59-c0b7a99a7c87 | note | — Pipe Dia ≤450 - 150mm GAP20/AP20 - Overlay
dc66fcfb-bcb8-59fd-8786-ba0cb1701e2f | note | — Pipe Dia 450< D ≤900 - 150mm GAP20/AP20 - Overlay
a4b33b56-2cc4-5e4e-bda2-da535ee9d3e4 | note | — Pipe Dia 900< D ≤4000 - 150mm GAP20/AP20 - Overlay
7d443299-b77d-5831-a47b-ca300cddfee5 | note | ○ Minimum Compaction - Trafficable and Non-Trafficable 95% MDD on metal.
f43fe518-1fcf-57e2-a677-03abbd0d413b | note | Standard / Specification - PS- Table 21.7, PS- Table 21.12 AS/NZS 2566.2/2002
2f1aa719-10da-585f-997c-02d332c9a519 | note | Verifying Document - Lab Test Report
2832d318-b244-5b47-8a78-5cfc8313cde5 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole.
ff804675-c786-51cd-aaa1-1439fc0c00b2 | note | ○ 0-5m: 1 Tests
03954a7d-0a5a-5618-81a4-03ec8528aa42 | note | ○ 0m-10m: 1 Tests
8d4fb148-466d-572a-aac4-63b68aca58e2 | note | ○ 0m-20m: 2 Tests
9d1533a7-7056-526f-9c41-83be71f1b908 | note | ○ 0m-50m: 4 Tests
980139b1-d12b-57bf-9e74-5bddf506a693 | note | ○ 0m-100m: 6 Test
d058f529-9118-5c8b-b3bd-dd5a3ce8f92a | note | Verification Activity: Activity - H
ce4a9363-1a7d-53ef-96e5-143811949fc1 | note | Verification Activity: By - SE
5ac16f69-74e9-468c-bc3f-8ee318882f40 | checkpoint | 3.5.5 - Survey
06c7769f-3e6b-536c-9e8b-3895ad11a09f | note | Detail - Surveyor to Setout
bc9ba821-27f6-5de9-bd79-47e771fee101 | note | Acceptance / Conformance Criteria - Vertical design Setout:
b415a2c5-488e-5f9b-bafd-6ef07845a1aa | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
6f044dda-777a-501b-bcdd-f9af3ed02f73 | note | ○ Pipes > 1% grade: +/- 20mm variance
5fa32ed8-7e22-596f-8844-a33ebec0035b | note | ○ Horizontal design Setout: +/-30mm variance
e98b6150-c81f-51b6-adec-d0bea0d6a6b9 | note | Standard / Specification - PS- 21.7.6 Table 21.15
b1b1bb16-023f-5ecc-b55a-ed447f0b95fc | note | Verifying Document - Survey Data
e22071e8-301b-5165-8a65-1c5d3cf33875 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
3472613d-24f3-5dd1-a706-725746b05e37 | note | Verification Activity: Activity - H
b19bd150-f897-5b38-985d-5771866f9453 | note | Verification Activity: By - SV
7b5c67eb-a5ac-470a-b92b-d6c59fe8c0d8 | checkpoint | 3.5.6 - Backfill Compaction Testing
d6a4d10b-6c64-53c8-b2af-aaa7f5c1f889 | note | Detail - On Granular or Cohesive Material
463425b7-3eca-5938-abfd-6f5cf436eef9 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65
7f904467-2f09-5dab-af19-ee81b4ac00e8 | note | ○ Backfill Compacted in 200mm layers.
e472ff47-6f7d-5b68-96d1-4f24b659569d | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
4c9b9f68-fa31-5686-8ca5-978ad8e0626c | note | Standard / Specification - PS- 21.6.12 Appendix V
f59c2f60-6820-5390-84e1-62be741cabca | note | Verifying Document - Lab Test Report
c91e6390-9320-57b5-829e-53906d9e2787 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole.
049415e0-4347-57bc-a339-3c2cf3476456 | note | ○ 0-5m: 1 Tests
84602b74-6d9f-5b72-bcea-f71f091bf2c5 | note | ○ 0m-10m: 1 Tests
d1199da3-ae63-5336-aea7-fff7bc0943d3 | note | ○ 0m-20m: 2 Tests
d5de9fc8-3147-53b7-8b42-6fc6a07170bc | note | ○ 0m-50m: 4 Tests
b3493f26-40dd-51db-9a7b-8bdc7f106b2e | note | ○ 0m-100m: 6 Test
03471a9b-e769-5a4b-a205-397db77f1c47 | note | Verification Activity: Activity - H
bf223545-29f6-55e2-a6a1-a377a9133c15 | note | Verification Activity: By - SE
73644131-04e4-4308-8333-78df258b0f9d | checkpoint | 3.5.7 - Pipe Inspection
66d342c6-e511-5760-82b3-bf5fdf0c5585 | note | Detail - Inspection of Drainage line
2175ee33-f278-577c-9844-5cdcd0b3f08d | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place.
afd737bf-1e49-5ebf-bb5b-0e5f603c9a92 | note | ○ Check for gaps and/or defects and check pipe alignment for straightness
d9bb5444-521e-5f23-ad56-09f96093d47b | note | Standard / Specification - PS- 21.7.6
a765c1ff-de5d-57f7-8315-e67270efbe2d | note | Verifying Document - Drainage line record
add06016-b268-59d9-8f66-828ac640ee14 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
fec56a08-5776-5032-8ef0-61ad941863dd | note | Verification Activity: Activity - I
4a1f8225-ea9c-5966-887a-877b6a4be9a4 | note | Verification Activity: By - SE
636d6c86-4951-436e-8122-6e2d2fe92daf | checkpoint | 3.6.1 - Settlement Monitoring
7486bacd-a5de-5c86-a0a3-9196696c335f | note | Detail - Settlement monitoring with installing the settlement plate at underpass foundation level and as described in PS 18.5.4 during the construction at various levels.
6a37fd7c-e1bc-5217-9ab1-f6f497e51be4 | note | Acceptance / Conformance Criteria - Settlement monitoring done regularly after completion of foundation, on completion of precast installation, on completion of cover fill, on completion of finish structure.
269b398d-59c5-5071-9dce-7e5d9fc25676 | note | Standard / Specification - PS 18.5.4
803afcb3-715b-5799-bbca-5e8c7c8be92f | note | Verifying Document - Installation of Settlement plates/Visual Inspection
32cd4d5c-f568-549a-a770-3db77b06077e | note | Testing Quantity Required (based from schedule qtys) - as per construction sequence per PS 18.5.4
a366c0a1-99da-5e3a-bd7a-45a82ff780a4 | note | Verification Activity: Activity - I
71a4464b-c50d-5d06-8ea9-bacaa74f98cf | note | Verification Activity: By - SE
e73dbc5d-b1da-4dbc-87f2-d266eda621b3 | checkpoint | 3.6.2 - Placement of Geotextile
8a72dbcc-ea3f-55a9-a58b-52d6ef8bb2c1 | note | Detail - A layer of Class C Geotextile Fabric to be placed between cut surface and imported A1 Structural Fill with 500mm overlaps
08b62600-9c00-5a2f-9319-49919a178997 | note | Acceptance / Conformance Criteria - Visual Inspection
bacf06c9-4741-5d86-94a9-2b12e4289926 | note | Standard / Specification - NTC084
2dee542c-963c-5a3f-a350-133b5d64cfa0 | note | Verifying Document - Visual Observation
509b85ab-c300-5e36-9713-67a62a036a6d | note | Testing Quantity Required (based from schedule qtys) - As Required
f03c61ac-60e6-5b27-8991-7b3f8e25b406 | note | Verification Activity: Activity - I
377d9803-868d-542d-b691-5f62b0095f09 | note | Verification Activity: By - SE
38be6cb4-8c8b-4314-9358-faeaafa294fb | checkpoint | 3.6.3 - Compaction - Clegg Hammer for GAP65 & AP40
43b71f9e-1070-56cf-aee3-05837cdb2488 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
e353f986-9c29-54bf-90c2-0bccdd5a7f90 | note | Acceptance / Conformance Criteria - Structural Fill
3aaf9324-c6ea-593f-9e8f-5af37c544133 | note | ○ Min CIV 18
2d8ef7c2-32c0-5050-bfe1-336a32d5f243 | note | ○ Ave CIV 20
0d64d406-223a-50bf-9c65-5e85c724009b | note | Standard / Specification - Appendix XVIII
ac384794-5246-545f-b521-a8812c6adeb0 | note | Verifying Document - Clegg Hammer Report
346f9d91-bcb4-59e3-a1b4-ad1ed4c83269 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
e346edd5-53e5-56eb-bd8d-b391425f67aa | note | Verification Activity: Activity - I
f7d24a5c-1950-533d-9fea-b56b948febde | note | Verification Activity: By - SE
a6e47f29-9c61-4ab7-8f6e-1d616541f0cb | checkpoint | 3.6.4 - Placement of Geogrid
6e2093ce-643c-5041-aa44-cc26ac6dc3cb | note | Detail - The Durargid X 40/40 Geogrid shall be placed on top of the GAP65 layer and the first AP40 layer.
d4a020d0-e0c8-55cb-95bf-763b9cb0e2fd | note | Acceptance / Conformance Criteria - Visual inspection
af87818f-3f6e-56e8-bfb8-33e6d0ee79ff | note | Standard / Specification - STR Drawings Sheet 203
13907e4a-0708-5cc9-9467-a6a1e7ee4918 | note | Verifying Document - Visual Inspection
b4219d0a-6ffa-5fcf-a9dd-b543d77120b4 | note | Testing Quantity Required (based from schedule qtys) - Across gravel raft
071187d7-1e0f-5163-a072-879442f062c3 | note | Verification Activity: Activity - WP
0e483e8f-01c6-558f-a06b-96d63090c84f | note | Verification Activity: By - ENG
55ab33b3-730a-4db4-ab03-40e79cb177bc | checkpoint | 3.6.5 - Compaction - NDM on top AP40 layer
f29d2839-a78e-5669-9df3-01294e5fca1a | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
fd0853ce-8186-57a8-8477-78129752720a | note | Acceptance / Conformance Criteria - Ave >95% of MDD
fb5b0f6b-8b2a-58f7-88e3-82a4feabafa2 | note | ○ Min >92% of MDD
64cbf2f4-8528-5659-9984-4f37564ceb5d | note | ○ Non Granular Material
fb6a8b7c-e407-52b7-ad1a-57cf20b25b99 | note | ○ Max Air Voids 8%
5564c904-3400-55b2-ab01-d54d00d50946 | note | Standard / Specification - Appendix XVIII
eeadc31e-1fa0-562f-983e-c34ce32825c2 | note | Verifying Document - IANZ Accredited Report
126d5c00-8943-5c8f-b83f-75a90f53335e | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) on last lift of AP40
5dc80cfc-fe09-52d0-bbcc-28fe046c6f66 | note | Verification Activity: Activity - I
980a07ac-17f2-59ae-b78c-d87a559ba6a9 | note | Verification Activity: By - SE
54b6fa96-f6de-4f80-8452-b33e5b1049d7 | section | SECTION 4 – PRE-CONSTRUCTION - MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
4c52d777-f9d4-44b9-9a83-003f6b5c34c0 | checkpoint | 4.1.1 - Reinforcing steel and Strands
077b94b3-66b3-5904-ab65-77a795ad0573 | note | Detail - All Reinforcement bars and strands used in structural concrete to be approved by the engineer prior to construction.
b0bb3428-ee96-5eb1-90d3-212d1b709fef | note | ○ Post tensioning strand to be high tension ASTM galvanized and complying with AS/NZ standard
35796a38-69d2-5148-9f23-c938f15343fb | note | Acceptance / Conformance Criteria - Test certificates shall be obtained from the manufacturer for all strand, cable and bar to be used in the work and copies shall be forwarded to the Engineer at least one week before the programmed commencement of any work incorporating these materials. Test certificates shall be traceable to the batch of material supplied to the work.
9e587635-5104-5793-b6ca-bcc50dfd8074 | note | ○ High yield steel, Grade 500E, Seismic MA.
4b572cd9-cfb1-562e-bce4-2a74eb7a40c6 | note | ○ Post tensioning strand to be high tension ASTM galvanized and complying with AS/NZ standard
e1f8eb0f-e613-54d5-a421-797c9c60439c | note | Standard / Specification - PS 18.3.3, 18.5.7 and 19.13.1
12017556-1aee-5381-8b2d-dab50ab6335a | note | Verifying Document - Supplier data sheet/ Mill certs
ea010e0a-7751-5602-ba7f-832b596fbbc9 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
7690dd07-845e-5411-a733-3f4e907e4a7a | note | Verification Activity: Activity - HP
e7fd086e-4465-5d75-9286-41a22d9cf3cb | note | Verification Activity: By - ENG
d2145560-faf5-4391-8e7c-1a62f3a9a08f | signoff | AUTHORITY HOLDPOINT
45ae2667-60ce-4718-8b99-224d9c502288 | checkpoint | 4.1.2 - Concrete Spacer Blocks
b45f516d-e41f-5aa6-8ae5-26b8c5436a11 | note | Detail - Reinforcement cover spacer blocks shall be either made from concrete with a specified strength at least 10mPa stronger than the surrounding concrete; or Plastic spacer blocks.
764a8514-af0a-5153-a03f-50552707f56f | note | Acceptance / Conformance Criteria - Concrete cover spacing blocks = at least 10mPa stronger than surrounding concrete.
4fa209c9-8632-5e81-ae1a-88e868e3571c | note | Standard / Specification - PS 19.3.2
7c922377-ad48-52a4-905e-3a99c2058138 | note | Verifying Document - Supplier data sheet
ccc7c145-6d75-5889-8401-867b3c2e07d5 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
5e90bd4d-4c7f-51f0-87e5-5a318ffb852f | note | Verification Activity: Activity - I
8070174a-61ae-53e6-aa4a-facf10feb07f | note | Verification Activity: By - SE
dbb61201-4e24-4581-abed-3c36dfa82de6 | checkpoint | 4.1.3 - Concrete mix design
b9aef70f-c189-54d9-9f0e-2135b058e4da | note | Detail - Approved mix design - Concrete shall be of the class as defined by NZS 3104 have a minimum 28 days compression strength as specified for various members: for underpass apron pour: 40mpa
f1d025da-64ce-5a11-a7c6-3d7c9eb45247 | note | Acceptance / Conformance Criteria - 28 Day concrete requirements: UNDERPASS APRON POUR: 40MPA
82720ea4-cca6-549c-8387-37fd3cb1423a | note | Standard / Specification - PS 19.3.3
dcb44560-8577-58a6-8934-2db4eaac6880 | note | Verifying Document - Approved Mix design
c2dbd036-9129-5cac-9b21-dd6c8929e553 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
3d5cea89-8a78-564a-8607-16ef263b00bc | note | Verification Activity: Activity - HP
30905321-b2cf-5c66-a03f-d0e183c328a9 | note | Verification Activity: By - ENG
95c21835-a2a1-4c34-88a0-a144d4351e87 | signoff | AUTHORITY HOLDPOINT
683143c2-16ab-4cc6-be73-9e7a9fb7e32c | checkpoint | 4.1.4 - Shop Drawing Approval
82fc1032-994f-5f60-9f1e-f4fc25144f22 | note | Detail - Shop drawing review and approval from Engineer and Production QA Records to be submitted
1aa11db9-411a-586a-935f-ea5f83a736c0 | note | Acceptance / Conformance Criteria - Send shop drawings to the Engineer for review, at least 14 days prior to manufacture. Any variations between the Drawings and shop drawings shall be clearly identified and brought to the attention of the Engineer.
191bd3b0-06fe-5b80-942a-4aa15a5ae3fd | note | Standard / Specification - PS 19.12.6
056cc8fd-4761-5f9c-a8ac-1bda208c1f60 | note | Verifying Document - Shop Drawing Approval, QA records
ac44bd02-3ff7-5c15-9f07-57b489b8ebb3 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
1fc1574e-8f6b-54f4-89f3-25b5332efeec | note | Verification Activity: Activity - HP
0f25d62a-76b2-596b-8696-c2d736c94722 | note | Verification Activity: By - ENG
7d6b9666-b6e9-4c21-831d-8410f92b9f23 | signoff | AUTHORITY HOLDPOINT
186ab8bd-c797-4dc5-b0ba-b404074c342b | checkpoint | 4.1.5 - Anti-graffiti products
b25f66d6-fe40-5cb8-a535-ad8f83179846 | note | Detail - Permanent (not sacrificial) anti-graffiti coatings shall be applied to the exposed faces of all concrete surfaces including wingwalls. The coatings shall have a design life of not less than 10 years. The Contractor shall submit the proposed extent of application for authorisation by the Engineer.
d45cff7c-39b6-5916-a232-ea6b18391e16 | note | Acceptance / Conformance Criteria - Permanent (not sacrificial) anti-graffiti coatings shall be applied to the exposed faces of all concrete surfaces including wingwalls. The coatings shall have a design life of not less than 10 years. The Contractor shall submit the proposed extent of application for authorisation by the Engineer.
466dde6e-cd52-5bbb-8c85-2fda52ee8fa6 | note | Standard / Specification - PS 14.7.1
eee43911-1d9e-576d-8b77-d5a0099c4526 | note | Verifying Document - Details of pre qualified product
573d11f7-037b-54b8-ba09-31eae601e663 | note | Testing Quantity Required (based from schedule qtys) - Prior to Application - Engineers Approval
ee5988ee-6875-5f3b-ac56-1103514e85e9 | note | Verification Activity: Activity - HP
da11f217-2b5e-508c-9cb6-53aae7be356b | note | Verification Activity: By - ENG
acf34792-38c8-46cf-ae65-50c5280b8ce1 | signoff | AUTHORITY HOLDPOINT
7415f927-fc2f-4662-bc20-cc12d159d469 | checkpoint | 4.1.6 - Joint Sealing and Waterproofing Sealant
fca9ca89-b547-5351-867f-85750eda10d3 | note | Detail - Pre approved joint sealant meeting the specification requirements
51bffdc1-1126-56d3-8a1f-4ab065d21236 | note | Acceptance / Conformance Criteria - Joints are to be sealed using a fuel resistant, multi-component polysulphide sealant designed for horizontal and vertical joints in concrete and is joint sealant pourable or gunning grade as appropriate.
28278279-fcea-5d8c-988d-893d655a4e82 | note | Standard / Specification - PS 19.12.6
8c60ca2f-57fa-54cb-a0c8-4fdb49ab08e8 | note | Verifying Document - Delivery dockets and supplier data sheet
077af5cb-be65-5289-9913-1a0eeaa44786 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - Engineers approval
b9f6c41c-1d71-528b-a00c-56905493b5f3 | note | Verification Activity: Activity - HP
15b4892f-53dd-56e2-964e-22b13e07ae57 | note | Verification Activity: By - ENG
5df67dc9-4421-49d3-b0a8-c729d1fdf9dd | signoff | AUTHORITY HOLDPOINT
c261a4de-3bde-41c0-8cf5-e73c9ac081e6 | checkpoint | 4.1.7 - Compressible filler board
6d6c8bcd-b8c4-5ee9-89e7-0c1f778e9a9b | note | Detail - Compressible filler board specification to meet the project requirements.
693ebb55-57d7-5355-9b3c-3b35e7daa98d | note | Acceptance / Conformance Criteria - Details of the compressible filler board proposed to be used as a construction joint shall meet specification requirements.
68696257-2114-52c1-8d58-6ae50820e7c5 | note | Standard / Specification - PS 19.12.6
15863668-57d5-5cdb-b1d7-62b004017e21 | note | Verifying Document - Delivery dockets and supplier data sheet
54b14d31-4121-535c-8d37-2a1d54387296 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
1c220594-3ec1-5a33-8bc2-30138fa75289 | note | Verification Activity: Activity - I
89a27ab9-401c-5b8a-a6c6-c0b2890f00f5 | note | Verification Activity: By - SE
32b2b605-c87d-4577-b390-184273bb9c8a | checkpoint | 4.1.8 - Application of Non-Slip Coating - Sikafloor 91 or Sikafloor150
5f36593d-3c42-5f78-a624-a3593b2fd381 | note | Detail - Proposed product to be approved by Engineer
f802279b-30c8-502a-a2ef-e0bb9de69102 | note | Acceptance / Conformance Criteria - The top of the underpass floor slab and bottom chamfers will have Sikafloor 91 or Sikafloor 150 applied after the installation of the box culvert segments. The thickness of this is to be between 3 and 5mm. The application of the product must be done in accordance with the manufacturer’s specifications.
d54c7ef6-ea10-55c0-9c5a-b1786db62e34 | note | Standard / Specification - PS 19.2.4
c5e4a5d6-9361-5c85-8276-481645533b1c | note | Verifying Document - Product data sheet
a47c06b4-a9d0-5f06-932c-ce5c38b3644a | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
945535ed-426f-552d-adcd-4d013105fafc | note | Verification Activity: Activity - HP
c0da3904-90a6-56dd-aef7-56868e7591c2 | note | Verification Activity: By - ENG
22d98d96-a18c-4514-8781-9105b3218c04 | signoff | AUTHORITY HOLDPOINT
454e2c7f-d380-4b71-9227-ce9b8e6c57d8 | section | SECTION 5 – CONSTRUCTION ACTIVITIES - BLINDING AND PRE-CAST POUR
32032d4e-a5fb-40e7-9e93-42d253277a66 | checkpoint | 5.1.1 - Setting out of Underpass Blinding level with 1% fall towards Northern end
f6b093ea-1c91-5459-9905-1196bf9c64a7 | note | Detail - Setting out boxing and complete site checks as concrete is poured to ensure flat surface for placing precast units
9153d4d5-8d0d-5b5e-8dd6-1aac7e0e680c | note | Acceptance / Conformance Criteria - Site supervisor verification
7ffe3e34-30fa-561d-be8d-6dad10f6b6e5 | note | Standard / Specification - PS 18.5.3
42c86ced-50a2-5272-a635-5a39d5e6cc58 | note | Verifying Document - Visual inspection
c9708177-0a86-52de-9a07-d5a699886635 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
5a2ab5d7-a386-5482-9578-ab47888ed571 | note | Verification Activity: Activity - I
e8800569-02fd-552f-8a00-62ba6de89e91 | note | Verification Activity: By - ENG
c610f5a9-aafe-41ea-a3c6-bb7db1268f0e | checkpoint | 5.1.2 - Blinding Concrete
d6808455-0190-5ee7-bd3d-8b5610629a79 | note | Detail - Concrete Compressive Strength on 28 days to gain min of 10MPa
4b8e6512-ca2a-5645-b28a-e222c5c3588f | note | Acceptance / Conformance Criteria - Blinding concrete shall have a minimum 28 days compressive strength of 10 Mpa and comply with the requirements for prescribed mix concrete specified by NZS 3104
1dd0104f-631e-53c5-92cc-af404a21f956 | note | Standard / Specification - PS 19.3.3
90b92352-f893-5951-9e0d-b7f7561f5e43 | note | Verifying Document - Concrete Delivery Docket
1638a1c1-2447-545a-b14d-5633ca3be3a2 | note | Testing Quantity Required (based from schedule qtys) - During construction
f93e5505-3ce0-53e6-8955-04ad12f0a237 | note | Verification Activity: Activity - I
928b3948-cda9-5df7-b3d4-ce6f5c385744 | note | Verification Activity: By - SE
7bbde659-444c-4031-8e1c-006d1d26d4e3 | checkpoint | 5.1.3 - Setting out of positions of the Underpass units
0b165b5c-6fce-5f1e-aea8-68738d4a1236 | note | Detail - Setting out to follow design coordinates and levels within tolerance as specified in PS 18.5.3 by approved licensed surveyor to certify the Set-Out positions.
db71a4a2-0d0f-5de3-a83c-075670ff0ec4 | note | Acceptance / Conformance Criteria - Engineers Approval
550db0d2-b3ea-5d1c-b706-c407511f7627 | note | Standard / Specification - PS 18.5.3
a125a281-f6b8-5829-92c6-dff1cf0dbd9c | note | Verifying Document - Visual inspection
149c601c-e4db-57e3-8d64-6f564fcf7b33 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
c3b7be1f-dfa8-5f96-a61d-bb5a64f70dac | note | Verification Activity: Activity - I
1b93668a-8330-53e6-9ccc-ada6684d2b3e | note | Verification Activity: By - ENG
a9d43607-8f47-47ec-86a7-b6591b66bfb7 | checkpoint | 3.2.1 - Forms and Moulds
11cce2b8-1dfb-56ac-8cc8-6cbda9357eac | note | Detail - Tolerance on the placement of internal forms and moulds shall be +-5mm
821cefb9-1065-5952-b81f-2db06685754e | note | Acceptance / Conformance Criteria - Moulds shall be rigid accurately formed and of sufficient strength and stiffness to prevent distortion under vibration.
850bed47-8313-5330-a830-0486f94a7a83 | note | Standard / Specification - PS 19.12.5
57b76873-b830-5b69-a065-f28a2541f781 | note | Verifying Document - Manufacturer QA records
4779cc43-098a-52f3-986b-8d5e3b88fc1e | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
5566deb0-b036-52e5-bc51-7cae21650438 | note | Verification Activity: Activity - I
6d249115-d644-55a5-90f5-229a948add69 | note | Verification Activity: By - SE
1a4ec2e8-2bec-457d-b846-3dc0265adf26 | checkpoint | 5.2.1 - Pre Pour Inspection
b69a919e-c177-508f-8a32-626dfae6ade1 | note | Detail - Pre Pour inspection to check:
47778912-ae58-5190-9103-81bab2e287e4 | note | — Reinforcing
895fa0ff-075b-5240-acfe-5d7d5b8b33fc | note | — Moulds
576227e8-7797-531a-90e3-3851d9549b5c | note | — Cover Spacer Blocks
6e0ae3d6-745a-5fb3-a079-37d947e0792e | note | Acceptance / Conformance Criteria - The Engineer shall be informed 8 hours prior to the casting of any unit, to allow the Engineer to attend the pre-casting plant to inspect before and during production of the units.
fcc12917-b4a7-59f5-a462-d756d63be0f4 | note | ○ Reinforcing shall be pre assembled wherever possible into rigid cages using a template or jig. Reinforcing shall be tied together with wire unless otherwise accepted by the Engineer
c0b46711-1040-5556-8680-243c4016499f | note | ○ Confirm correct type and location of cover block is used.
27f3340f-06ff-5389-95e9-64f3594304c5 | note | Standard / Specification - PS 19.3.2, 19.4.3 & 19.12.3
3b652614-4180-5da5-9972-10e8b526daca | note | Verifying Document - Pre pour inspection checklist, Manufacturer QA records
2fec3be7-2628-51fa-ae4f-38a979886637 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
3704d5ec-cf06-55ac-b06f-c36580f62442 | note | Verification Activity: Activity - HP
5e3a60b2-7dee-51b3-babd-eebc991d1f0e | note | Verification Activity: By - ENG
ed247e82-4b1d-4aa3-8ecf-3a8987d166cc | signoff | AUTHORITY HOLDPOINT
ebcd2f44-cc99-424e-a376-6836471b8e3a | checkpoint | 5.2.2 - Concrete sampling and testing
b54826ea-08d3-5497-8240-11b380ac2fbc | note | Detail - Pre cast Methodology from Pre co to submit to Engineer and Compression Test Report
03c1f8cd-985f-5a56-9f19-e2064c06d38a | note | Acceptance / Conformance Criteria - For pours under 150m³: three standard cylinders shall be made for each 50m³ of concrete placed, or part thereof, for testing of 28 days compressive strength in an approved laboratory.
51538c53-9b6a-563c-8dcd-3a7a000bb709 | note | ○ For repetitive precast underpass units with 6.42m3 each pours undertaken on a regular basis, three standard cylinders shall be made for each of the first five pours of any one type, and thereafter three standard cylinders shall be made for every fifth pour of that type for testing of 28 days compressive strength in an approved laboratory.
fa2a4a21-ab8c-55b0-b567-9046cec6038c | note | Standard / Specification - PS 19.4.3
227bce6d-678b-547a-8bb1-f44269b8509a | note | Verifying Document - Slump Test/ Compressive strength test Report at 28 days/Pre pour inspection checklist
ad5a5652-e93a-5ca7-98a4-0e2ab69804e0 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
8c94317e-213c-5db1-95ea-44bfef7d076c | note | Verification Activity: Activity - HP
a9793219-c1db-5045-9bd5-1e5f07a17f01 | note | Verification Activity: By - ENG
df4a72fb-439e-4031-a5d6-5d5f9e5ba592 | signoff | AUTHORITY HOLDPOINT
761bf53e-9b26-4902-9760-d314fffb854d | checkpoint | 5.2.3 - Surface Finish of pre cast concrete Units
460f38ef-ca9c-57b4-9b81-6a5e67e22bbc | note | Detail - Surface finish to comply the requirements for pre cast concrete units.
9da07248-d7a6-5442-aae5-11ad2cac088d | note | Acceptance / Conformance Criteria - For all precast concrete units all surfaces except those against which concrete will be subsequently placed, shall have a concrete surface finish complying with the requirements of NZS 3114, F4 finish for formed surfaces and U3 finish for unformed surfaces.
8850e8f7-3657-5cd3-a02d-b91755a5d545 | note | Standard / Specification - PS 19.7.1
bb79eac9-9b70-5cce-8dcf-b28e7f732e98 | note | Verifying Document - Visual Inspection
589d3ae9-7dcd-5777-a84d-f422ea614477 | note | Testing Quantity Required (based from schedule qtys) - Each Item
6f78d299-bbd2-591d-b8c9-a21d4c3f7e51 | note | Verification Activity: Activity - I
962f734e-8d11-5000-8034-ef0ab6484983 | note | Verification Activity: By - SE
0cbe21b8-b954-4527-89ae-58735de25d6c | checkpoint | 5.3.1 - Post Pour inspections
af6c7717-dff5-5efe-9269-e60d282f9928 | note | Detail - Post Pour inspection
53d40198-698b-57c7-9763-451f95f6b104 | note | Acceptance / Conformance Criteria - Following the concrete pour and stripping out form works: the concrete shall be inspected for Size, Shape, Features, inserts, reliefs, and Finish against the drawings.
3df8a796-7e23-546c-8a96-d7e1f0ad9cfc | note | Standard / Specification - PS 19.3.1
4053aee5-a6c6-5618-8643-5fcdcf2f6bbb | note | Verifying Document - Visual Inspection/ Post pour checklist
a5c9b572-f2fd-50f2-849c-b84c32bbc12d | note | Testing Quantity Required (based from schedule qtys) - Each Pour
008928da-fb5b-57ad-8d7f-5faedbfae0df | note | Verification Activity: Activity - HP
0cdf855d-b681-5b63-aa5a-dc0cdd0d3dbc | note | Verification Activity: By - ENG
e4e07f78-3630-4e51-a2fb-c17faffe910c | signoff | AUTHORITY HOLDPOINT
ddc00347-2fb1-42b1-adad-4f1823bc977d | checkpoint | 5.3.2 - Defective Concrete Finishes
7b85b129-d8cc-565e-b2e5-9c06e6c50397 | note | Detail - Repair of defective concrete finish other than that due to minor porosity of the surface shall be carried out only when approved by the Engineer.
f6060b57-299c-5893-b2b2-7aaffcb6488f | note | Acceptance / Conformance Criteria - Repair of defective concrete finish other than that due to minor porosity of the surface shall be carried out only when approved by the Engineer.
74e5beb0-42f5-5375-be2a-a8a8f7358677 | note | Standard / Specification - PS 19.3.1
6cd0c216-e776-59dd-a039-0fa81ab28cf2 | note | Verifying Document - Visual Inspection/ Post pour checklist
dbe1a6fd-0684-5849-b3f5-b99549778f59 | note | Testing Quantity Required (based from schedule qtys) - All Concrete Elements
2d73adac-fd07-5cfc-b663-8ae36d572f04 | note | Verification Activity: Activity - HP
21e78df9-2cd3-52ac-b651-b0321b535547 | note | Verification Activity: By - ENG
76f419d2-1b0c-4ac0-9059-0193dbb7875c | signoff | AUTHORITY HOLDPOINT
79f9c2e7-4858-4e47-972e-1ffc96b5ddd1 | checkpoint | 5.3.3 - Joint Sealing of Pre cast members
fb486bf7-ff85-5a17-8fc9-f0715d5a6478 | note | Detail - Joint sealing of pre cast members
4616447c-e323-54a0-9e46-6b3efb89ec38 | note | Acceptance / Conformance Criteria - Joints are to be sealed using a fuel resistant, multi-component polysulphide sealant designed for horizontal and vertical joints in concrete and is joint sealant pourable or gunning grade as appropriate.
5a6004d6-c50c-5e40-a7ca-f4e9158c7729 | note | Standard / Specification - PS 19.12.6
2b64be70-1623-571e-8e25-7b0c3e0bccd3 | note | Verifying Document - Post installation inspection check list
910939d0-9b53-5153-8519-a23accb50334 | note | Testing Quantity Required (based from schedule qtys) - After placing pre-cast units
6e3b913a-95ab-5b7c-b970-ee845cf7e15a | note | Verification Activity: Activity - I
639d3e78-4e29-508e-8719-8ffcb21dfe04 | note | Verification Activity: By - SE
ca46a072-2d61-42ca-9c17-85c1291d328b | section | SECTION 6 – CONSTRUCTION ACTIVITY- POST TENSIONING OF UNDERPASS UNITS
2bccc64c-9bc6-4b8f-9898-03a688713d86 | checkpoint | 6.1.1 - Detail methodology for Post Tensioning of Stage 1 of underpass units to develop and send to designer for approval
3e857736-983b-5b3d-8a86-598ff03387e0 | note | Detail - Detail method of stressing
2b11752a-ccac-5309-90ff-6bf656e5a7a6 | note | Acceptance / Conformance Criteria - 1*15.2 Galvanized, greased and sheathed strand per corner (Ungrouted) to be inserted in each corner for stage 1, 16 units of underpass.
9928d889-e391-5283-babd-c26789965969 | note | ○ Both ends will have a 40mm rebate for grouting.
9ba87426-e565-504a-aef3-61af4530ca4f | note | ○ And those strands will be tensioned to meet the project specification.
1e9ac2c8-35dd-50c3-be60-215f1396a62c | note | Standard / Specification - PS 19.14.1
10a8ea28-451c-5870-aa1a-9a30bb82d6e0 | note | Verifying Document - Method Statement
7e35a1ae-d62d-5ffc-8a46-236269af6b3b | note | Testing Quantity Required (based from schedule qtys) - Before installing units
bcaa7a46-f4dd-5b95-8d7e-b3f1e363e996 | note | Verification Activity: Activity - HP
84d865a8-93a3-563e-83d9-f10b7ad29dcb | note | Verification Activity: By - SE
15234106-9075-425f-a6a5-4ba5b3cf5cf5 | signoff | AUTHORITY HOLDPOINT
478d08cb-5c85-4920-b199-c7dd34fec7b9 | checkpoint | 6.1.2 - Detensioning of stage1 underpass units for Stage 2 construction
be0021cf-3a2a-5ac0-8f56-5917d7cb00af | note | Detail - Detail method of stressing
10c8a95b-4635-5ffd-9df9-0b2837088de4 | note | Acceptance / Conformance Criteria - Detensioning will be done on one corner at a time, remove wedges via special pocket pull new strand and tension.
ed13d550-087a-55f6-8b5c-db50fd4a8501 | note | ○ This will ensure at least 3 corners remain under tension at any given time.
7e3e61a7-3615-5bcb-ab56-85f27360bcad | note | Standard / Specification - PS 19.14.1
3e876cae-a9ad-52f0-8463-6d768c30c278 | note | Verifying Document - Method Statement
7bd750df-4b0f-5d7b-89d9-2263b0dfa14c | note | Testing Quantity Required (based from schedule qtys) - Before landing stage 2 units
76692347-a092-5d8c-8768-6f95b4dd2cc1 | note | Verification Activity: Activity - HP
bd4a3e7e-c89d-58b6-ad12-dee4948f44d7 | note | Verification Activity: By - SE
22b5dc81-051d-43c2-9dc3-8c9417589d77 | signoff | AUTHORITY HOLDPOINT
46877e3f-21f3-4add-9895-a324bd25e56e | checkpoint | 6.1.3 - Stressing Operation
8e0602b5-0d6c-54f9-8453-49898dcebfce | note | Detail - Post tensioning of strand to be done not to exceed 80% of maximum ultimate breaking strength. Post tensioning strands to be stressed simultaneously or following the sequence of stressing as noted on shop drawings.
921cacf5-c8c2-5fe1-9b43-f760ae2b193d | note | Acceptance / Conformance Criteria - Stressing forces shall be as per NZS 3101 section 19 for maximum permissible levels of force within a strand during and after stressing.
dc993559-2d7d-54c5-a116-171bcc88cc87 | note | ○ In no case shall a strand be stressed to greater than 80% of its ultimate breaking strength.
88631885-c8a9-54a1-adf9-4ecaf0a28100 | note | Standard / Specification - NZS3101 Section 19 PS 19.14.1
044cb879-8659-539e-bb1c-c1942b2ac767 | note | Verifying Document - Method Statement
471a4697-4d38-5471-ba94-aa6c3692c4e7 | note | Testing Quantity Required (based from schedule qtys) - All units for tensioning
0be1579b-577f-56ec-a427-5dd27c8a5f78 | note | Verification Activity: Activity - HP
a8b0b89f-59f8-5885-a59b-ce235bdc74d2 | note | Verification Activity: By - SE
eda6a3f9-b82e-42c0-a612-93f07649607b | signoff | AUTHORITY HOLDPOINT
5f30448e-46ad-4f4b-b1d8-1045388a177c | checkpoint | 6.1.4 - Concrete Strength at time of stressing
20fc376f-0768-5dbc-b3fa-6224bf5b0682 | note | Detail - Samples taken during construction of concrete member to be tested for compressive strength and the results shall be used to determine the acceptability of the structural member for stressing.
647a5361-bc25-5fe6-8e44-c9be37ea80aa | note | Acceptance / Conformance Criteria - The minimum compressive strength required before stressing shall be 30MPa unless noted otherwise on the drawings.
d284da7f-e6f9-52dc-9083-0c2c5fa9926c | note | Standard / Specification - PS 19.14.1
ad998cab-b046-5857-8bdb-3e98167b3b3c | note | Verifying Document - Concrete Test Reports
e26101d4-037e-586a-97a6-ec0882a9530f | note | Testing Quantity Required (based from schedule qtys) - as per test report in section 2.2.2
095e5b55-9418-5dee-b39f-801651f9960a | note | Verification Activity: Activity - HP
12c07606-869f-505b-ab6b-7f5c068ed76f | note | Verification Activity: By - SE
1e0c346e-6041-4d2d-898e-c012de93bc9a | signoff | AUTHORITY HOLDPOINT
1700ecbd-0730-45d9-a5bc-eab78d53b4e0 | checkpoint | 6.1.5 - Stressing Calculations
3672a157-8ea4-58d0-bb35-48d969dc1d3e | note | Detail - Calculation done will form the basis of comparison to the actual stressing results recorded as an indication that the appropriate levels of stressing are being achieved in each strand.
103dfd26-1ae3-5f64-ba38-cdd616585f39 | note | Acceptance / Conformance Criteria - Theoretical calculations for each strand size and profile to determine theoretical jacking forces and corresponding theoretical elongations. These calculations shall be based on the assumed property of strand and forwarded to the Engineer for review and approval at least 7 working days prior to the stressing operations commencing.
79ac9996-eb20-5f34-9c62-6c7c895b7078 | note | Standard / Specification - PS 19.14.1
9aa9c161-cd6e-5a85-95f5-6049d1913fb1 | note | Verifying Document - Calculation data sheet
8de566f5-6a5c-58ac-b43c-789a84a37e47 | note | Testing Quantity Required (based from schedule qtys) - All units for tensioning
a98f9ff0-a96f-5ddc-9b4d-a7b13785ec3e | note | Verification Activity: Activity - HP
0df08010-dba1-5ff3-a205-22c177807ba2 | note | Verification Activity: By - SE
6e929a49-f4d5-48f1-bc75-47ff5e3b99b1 | signoff | AUTHORITY HOLDPOINT
685b2ec5-11e2-4269-8759-377f4edbda3c | checkpoint | 6.1.6 - Protection of Strands
9b1d8696-b9e5-5620-bf20-29d6a12a47b6 | note | Detail - Post tensioning strands shall be cut flush with the end faces of the pre cast unit (including any recess) unless noted otherwise on the drawings. Gas cutting of Strand is not permitted.
a4157b5e-79d1-56bd-9245-9ecef9ba3522 | note | Acceptance / Conformance Criteria - Cut ends of the strand sealed and protected with minimum of 5mm of epoxy mortar or a coat of high build epoxy paint.
90fff0ea-e597-5e54-bc9b-fd43c1185d80 | note | Standard / Specification - PS 19.14.1
c685df8f-2f09-5a44-a828-e0110e4e325f | note | Verifying Document - Visual Inspection
ed185715-c6ce-5bb5-adbb-322febdd7126 | note | Testing Quantity Required (based from schedule qtys) - All units with Strands
62a575eb-699f-5330-a5a0-c58eb4f09265 | note | Verification Activity: Activity - I
afbf1ad6-d1c6-508b-b601-f37d9a306f88 | note | Verification Activity: By - SE
f1cba25f-1c43-43df-82da-9248d89ba547 | checkpoint | 6.1.7 - Stressing Records
d154e311-0738-542d-a10b-9d65648fbc08 | note | Detail - Record of stressing shall be taken and reported to designer.
f9858a19-aaba-5d64-8a90-26b977bcaa39 | note | Acceptance / Conformance Criteria - Stressing record as per PS 19.14.1 section IV, subsection I
0eed16e9-dc1b-571d-b901-cf0268c18d58 | note | Standard / Specification - PS 19.14.1
cc320b13-4cee-55b8-802b-d359904b5dd5 | note | Verifying Document - Stressing records
9fc5a5a5-2ec0-58e8-acdc-a50c407fa3d1 | note | Testing Quantity Required (based from schedule qtys) - All units with Strands
c359521f-e641-57c3-9ee8-bceb20eb92ee | note | Verification Activity: Activity - I
835049ef-54b0-5547-8ef3-dbfe1905aee5 | note | Verification Activity: By - SE
a0498951-6f60-45ea-928c-e079304da6d6 | section | SECTION 7 – CONSTRUCTION ACTIVITY- UNDERPASS WINGWALL, DUCTING AND BACKFILL
03c9e912-1495-41d3-84f1-6c29f9683028 | checkpoint | 7.1.1 - Position Monitoring
c2bec360-8d4b-5e43-815e-69e62488ad9a | note | Detail - Surveying to be done on the primary structural elements as their construction is completed, location of base slab, strip footing, roof of slab, top of wing walls
47e66fd5-48f2-5bac-83cb-d4958e320fda | note | Acceptance / Conformance Criteria - Surveying done as per PS 18.5.4 on various stages of the construction of underpass. Position of underpass as built and recorded
9a0e609e-a109-5cca-be69-5e4633ffc575 | note | Standard / Specification - PS 18.5.4
04580153-2420-547b-9fd7-2801a695c9d9 | note | Verifying Document - Survey recording of position to the required tolerances
554f623c-75dd-5d15-87ff-b987b31ad96d | note | Testing Quantity Required (based from schedule qtys) - When each construction step finishes
9102d18f-cd0d-547b-9916-f8d839272768 | note | Verification Activity: Activity - I
78966a64-f61e-5781-8093-37dd71182b52 | note | Verification Activity: By - SE
02b45d53-60cd-4586-89c8-7880898f5cb6 | checkpoint | 7.1.2 - Placement of Geotextile on Cut Surface
7d49badb-e43a-5696-bf94-3a818114ddb1 | note | Detail - Geotextile to be placed up the sides of the cut surface, with joints overlapped by 500mm minimum
9a944883-dbee-5451-aeb6-cdf9d56121b2 | note | Acceptance / Conformance Criteria - Engineers Approval
2951f852-aaf3-558d-af34-7c39c6bba3bd | note | Standard / Specification - PS 16.6.4 TNZ F/7: 2003 8.3
2c2d260b-431e-5266-a137-867f7d6d5b45 | note | Verifying Document - Visual Inspection
87359eb9-2b3b-5f59-8e2a-d37b94c5ccae | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
4bae1d2c-8c77-5bcb-85e5-1747788d7e76 | note | Verification Activity: Activity - WP
00275bdc-65fa-581e-b10e-57717831be9a | note | Verification Activity: By - ENG
b2f04cce-69ae-441f-9aa0-55619b56a115 | checkpoint | 7.1.3 - Place Cirtex Armourflow at the face of underpass for backfilling with pavement millings
2f3ced79-0c39-56ef-a80f-51883183d2a5 | note | Detail - Armourflow to be placed up the sides of the underpass precast units with lapping as indeicated in the data sheet
0ca9f937-5881-5d8c-8584-9dbcb3cd7773 | note | Acceptance / Conformance Criteria - as per DN1210-WSP-GCO-300
545fbc5f-c53a-53ab-8a6a-34c134f83b80 | note | Standard / Specification - correspondence
aa51ebc3-ee2c-552b-8305-5739a1f0b6a8 | note | Verifying Document - Visual Inspection
391ae33e-a4db-5517-b790-6bd74b68c720 | note | Testing Quantity Required (based from schedule qtys) - side of the underpass pre cast units
8ba5598f-828d-53c4-9c82-3e8fe002c501 | note | Verification Activity: Activity - I
fc275d6c-8060-5eb4-836b-c50dcd970ce4 | note | Verification Activity: By - SE
5284f91f-d364-4aa1-85fe-92c247916c55 | checkpoint | 7.1.4 - Compaction - Clegg Hammer for underpass side backfill with pavement millings
d72e73b4-5168-56cb-b29d-4b8388565ebe | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
a700665a-e2c1-50c5-9e8f-0c255914782d | note | Acceptance / Conformance Criteria - Structural Fill Min CIV 28
c260b25a-b966-58d0-9d1d-6e58adfa5935 | note | Standard / Specification - DN1210--WSP -GCO-360
7e4b16d5-8d3f-55b8-9951-9f42112f8c38 | note | Verifying Document - Clegg Hammer Report
6a7c9171-fdc8-53ae-9777-c813b9dc9e76 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
5c7ad6d6-f7f0-5364-8d82-5cf0b8bd9098 | note | Verification Activity: Activity - I
5d76ddca-9a15-52cf-a23c-affb4fba0efb | note | Verification Activity: By - SE
abbc0072-d9f7-4261-85e6-c6fbb32d7cea | checkpoint | 7.2.1 - Trench Excavation
aed5e31d-30af-5064-81b5-1cf95477d1fa | note | Detail - To be excavated to within a tolerance.
3d95cb6b-2c73-55d7-bf24-eca054ab2a56 | note | ○ Not more than 100 metres of trench associated with each site shall remain open at one time.
c8a38272-c3eb-5f15-a75c-11706b95faf4 | note | Acceptance / Conformance Criteria - +/- 100 mm of the planned horizontal.
2e1339cf-e470-5215-beef-9a62a9d0761f | note | ○ The maximum deviation shall be 1 in 20 in both the horizontal and vertical planes.
025fefd3-24fd-597a-9fb8-3a2fc6ebe3a7 | note | ○ Less than 100m
68070254-e376-579a-826d-78e7ae369982 | note | Standard / Specification - PS 25.13.2 (Ai)
173bc361-428c-56d1-8d74-293bcc7c2f45 | note | Verifying Document - Survey
65d4dab8-27ff-519b-b274-15d233f37c33 | note | Testing Quantity Required (based from schedule qtys) - Every time
b26c4775-2ba5-5b68-96d5-69ca724ebb4a | note | Verification Activity: Activity - M
aa7120f1-5b54-5467-af03-ddcfaf3469ba | note | Verification Activity: By - SE
3be027dd-2823-4937-8d92-9da703b081bb | checkpoint | 7.2.2 - Unsuitable Materials
1854dec0-b9fd-5b25-8e7f-1165c05b72bb | note | Detail - All confirmed unsuitable material shall be excavated down to suitable materials.
acd769f5-5a06-57f1-8dc5-1dbb60dc303f | note | Acceptance / Conformance Criteria - Dig Down to Get Suitable Materials or get Engineers Approval.
add6296c-e722-5622-b5bc-495b00595560 | note | Standard / Specification - PS 25.13.2 (Bii)
1619c016-b2f0-5b3f-8713-52a9e1b0269d | note | Verifying Document - Visual
5c9e6cdf-4a19-52a7-943b-5265d67950c2 | note | Testing Quantity Required (based from schedule qtys) - Every time
48c306c3-596d-592e-bc6f-aa2a0bd2b61b | note | Verification Activity: Activity - M
d8487b4c-2914-5fdf-b430-5fdccbd4ab5a | note | Verification Activity: By - SE
605ffcf0-baec-4568-b1c9-336419dcc754 | checkpoint | 7.2.3 - Foundation Compliance
32cd3322-47aa-5b2e-bb8e-89267658d0df | note | Detail - It shall be de-watered prior to installation of bedding material.
7f016aef-fddb-51c1-9ed8-acb46be72c99 | note | ○ If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
df520078-0088-52c7-bc68-234ee64cabe1 | note | Acceptance / Conformance Criteria - Witness.
c7c3a09c-1aa2-54d4-a111-252ef8bb5741 | note | ○ 50mm granular layer shall be laid and compacted before the bedding layer is laid.
92b206bf-9da2-51bb-a6bd-0d7688f0cf8e | note | Standard / Specification - PS 25.13.2 (G)
ee5f8a28-9e12-5a0a-bba8-b9c9a63cbb8c | note | Verifying Document - Visual Inspection
1c167518-3028-51ad-b01e-76c03ef5dbf2 | note | Testing Quantity Required (based from schedule qtys) - Every time
d1355feb-fc12-5905-ae21-b1d0bf79f5c9 | note | Verification Activity: Activity - M
1bf08143-3130-5e25-aa0e-3554d2a70af7 | note | Verification Activity: By - SE
b6a3a08a-6ad1-43ef-b4a9-85c2d1f9ab21 | checkpoint | 7.2.4 - Bedding
11498b49-e9cf-55a9-a627-5b547c90dddc | note | Detail - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
15db7ba8-cafe-5adf-b171-e5cac0e3b6c9 | note | Acceptance / Conformance Criteria - Mixed Dust to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
87f179d0-8d8f-5931-8954-bb76e331925f | note | Standard / Specification - PS 25.13.2 (g) Modified by Engineer WSP
a8387b66-763d-5c11-b110-377bfcc4e75c | note | Verifying Document - Visual Inspection
0acab11b-88ea-55bd-8cef-1ed5d3854e64 | note | Testing Quantity Required (based from schedule qtys) - Every time
238aea09-7699-5c44-b4c4-832f656e8495 | note | Verification Activity: Activity - M
710a5d03-1304-5f61-bc47-990cb2759648 | note | Verification Activity: By - SE
d048bdf3-aaac-4c49-a924-f1e74db3a5d0 | checkpoint | 7.2.5 - Bedding (Enchased in concrete)
743664c8-e8de-5509-809c-b329bc5ef88e | note | Detail - Concrete Bedding to be placed. Compressive strength of concrete used no less than 20MPa
f143db1c-79f5-5fce-a3bf-18182cfdcb0e | note | Acceptance / Conformance Criteria - 50mm
421e1191-5a97-56e6-a76e-8348e9f451cf | note | Standard / Specification - PS 25.13.7 c)
8d3cfa42-70fe-5000-8e3b-60f244a69964 | note | Verifying Document - Visual Inspection
e0006f53-b3b9-5f00-87f9-f131d2efb561 | note | Testing Quantity Required (based from schedule qtys) - Every time
1adfb2e0-53ea-5b40-9297-bd79a957322c | note | Verification Activity: Activity - M
13a72a3e-47cf-5d52-befe-4f1c11218d71 | note | Verification Activity: By - SE
90126658-823b-4bdf-b6a5-2db6a5aa1a73 | checkpoint | 7.2.6 - Installation of Ducts
fcedefad-6754-5827-a3ef-ba2da0466d3b | note | Detail - If more than 2 ducts are being placed.
a993c048-99be-545e-8a4a-713c31866d9f | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
a626dffc-f2a6-5582-a957-09317e6f0be3 | note | Standard / Specification - PS 25.13.7 (B3)
d7f5fd88-2718-5a16-931f-c19c32fc0ae2 | note | Verifying Document - Visual Inspection
7ecdf6a2-2bde-58c2-9623-57f4cbd8c62a | note | Testing Quantity Required (based from schedule qtys) - Every time
5fe2b3c0-201d-5d2c-b3a4-10c352a925b7 | note | Verification Activity: Activity - M
d58bd3cf-258a-5ada-8678-9cff287b9c0c | note | Verification Activity: By - SE
db7ca616-3da1-4b43-9875-0fa9f3e73209 | checkpoint | 7.2.7 - Warning Tape
4c457609-6a25-5d58-b8f5-2cfed0d02612 | note | Detail - Warning tape to be placed above services.
0cb0a8b0-e6ca-5363-b6db-b6e13b44daa3 | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the duct
e5077114-01d7-550c-a8db-9d430d363f83 | note | Standard / Specification - PS 25.13.7 b) iii & f)
89ab5b37-6dbb-5b4a-8ac2-217b0d5b7731 | note | Verifying Document - Visual Inspection
02b79ebc-8cf1-54bd-a495-79254cda34c9 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
91a5f9b9-b538-5ad7-b4e2-dd5ced22bdd5 | note | Verification Activity: Activity - M
3893d40c-f472-5143-a3f8-82aac1262dad | note | Verification Activity: By - SE
5026c7a6-ddff-4dd3-8290-2a55f7b7dd7b | checkpoint | 7.2.8 - Overlay
91a4bf9d-addb-59e2-a9d7-df6770d1a62a | note | Detail - Mixed Dust to be placed and compacted
9a6786ce-73a2-58fc-85aa-f9b6a2754713 | note | Acceptance / Conformance Criteria - 100mm thick mixed dust
0e996c6d-11c2-5b4f-952e-abb2142ad083 | note | Standard / Specification - PS 25.13.7 b) ii
eb5cb356-dc6a-5315-a60f-ea93666751f6 | note | Verifying Document - Visual Inspection
ba32f1ae-cf8c-5302-84b0-e2fbc8f0b0b6 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
5a9230d5-2d75-50e2-90c3-eb127a375bb5 | note | Verification Activity: Activity - M
11733a77-c0f2-56e2-94a6-610795ce8714 | note | Verification Activity: By - SE
d39da391-a951-40d9-84c3-b7f3090de0ef | checkpoint | 7.2.9 - Overlay (Concrete Enchased Ducts)
6c55dfec-9936-516c-bd7a-33665e1af823 | note | Detail - Overlay and surroundings to be placed with concrete.
96a2561e-5e05-5b5a-8181-04f6d79fd9d4 | note | Acceptance / Conformance Criteria - 100mm thick on top of Ducts
26fd0b33-3e1d-5c10-8735-53f992f3abf7 | note | ○ 50mm thick side of the Ducts
865a95ca-a404-5c3d-ba43-a35a6b8be3ea | note | Standard / Specification - PS 25.13.7 c)
ba83a1d4-2c91-592b-9d71-232785edb1bb | note | Verifying Document - Visual Inspection
1695b02e-56ec-5837-9ab1-5a1d2e26d716 | note | Testing Quantity Required (based from schedule qtys) - Every time
ac4d0b38-b37d-58b4-a990-319e9560aaa8 | note | Verification Activity: Activity - M
e7a0a5ee-0954-5ce3-bcaf-12871478528d | note | Verification Activity: By - SE
2264fe26-3ac4-4112-a00c-c031cb714c76 | checkpoint | 7.2.10 - Overlay Testing (Concrete Enchased)
d72562e3-056b-5e87-99e1-0576fd0b6672 | note | Detail - Placed Concrete needs to meet the strength Criteria
71f4e266-7a39-575d-b43b-1625182ad732 | note | Acceptance / Conformance Criteria - >20 MPA
c55a786a-e3d3-5e77-a8bb-affe7fd82780 | note | Standard / Specification - PS 25.13.7 c)
45e17801-1c23-536b-8774-1db1730ea00f | note | Verifying Document - Concrete Dockets
9f53d1c3-4899-5be1-862b-3d35f33e5af3 | note | Testing Quantity Required (based from schedule qtys) - Every time
076774f8-4d21-52af-af5b-10b94058f0c8 | note | Verification Activity: Activity - H
2cebf41a-4f43-5691-b896-f1603be76094 | note | Verification Activity: By - SE
3f3fc4fd-e8de-4d26-baf7-2cd51d474df9 | checkpoint | 7.2.11 - Backfill
0bc87c4e-26db-54af-8244-36caddaf8e4b | note | Detail - GAP20 to be used if site material is not approved.
5b21019e-22d8-58bd-b97a-bff45295e3c2 | note | ○ NDM Testing to be carried out.
55834dd7-736c-5e76-9217-28868fcef4d7 | note | Acceptance / Conformance Criteria - 100 to 250mm thick compacted material.
9f113a4f-a465-50b0-b8bb-24c8b114270b | note | ○ Min 92% compaction and Average of 95%.
3e83c12b-44f4-504a-bcd4-4b012e30028a | note | Standard / Specification -
e37e3664-c800-5469-923b-21476e9a486a | note | Verifying Document - Lab report.
8bb842a9-ea80-52f5-8695-3e9d956129ea | note | Testing Quantity Required (based from schedule qtys) - Every Lift
b6b8a3fe-25e1-51d0-8202-e9a6995ad512 | note | Verification Activity: Activity - H
301a893c-6d1a-5e0a-8cef-358eff41e796 | note | Verification Activity: By - SE
6d66ba33-fd78-4d2b-ad5a-0bfa42f206ae | checkpoint | 7.2.12 - After Completion of Ducts
6711c2d1-e087-5b54-bb07-a9c9635a7540 | note | Detail - The Contractor shall pull the pig through the ducts to ensure there are no blockages between access points and no foreign material remains in the duct.
2eaeb49f-37a1-52eb-a2e4-28ae186d1063 | note | Acceptance / Conformance Criteria - The diameter of the pig used for proving the duct or pipe shall be at least 90% of the actual internal diameter of the pipe or duct being proofed.
37f479cd-918d-5151-9de8-01243e281af3 | note | ○ No blockage inside the pipe
76806918-277f-5180-8e7f-6b160589f980 | note | Standard / Specification - SP 25.13.7 E(1)
d3ba0b89-cc56-552c-8685-d409e5edd965 | note | Verifying Document - Visual Inspection
b5c13f17-c5f5-5e32-8e28-d2709fe16454 | note | Testing Quantity Required (based from schedule qtys) - Every time
82b477f0-5f95-57ee-9acb-e00c8835f30d | note | Verification Activity: Activity - M
85442ce4-70b8-572b-8aaa-0b901a930354 | note | Verification Activity: By - SE
bc9dd3c6-9dc3-450d-b7be-8fe0366a0fb2 | checkpoint | 7.2.13 - Caps
3219537b-6045-5ac2-a18e-746eb59633d0 | note | Detail - All duct ends shall be capped
0ffe8299-3a74-58a0-97b4-2c3292490917 | note | Acceptance / Conformance Criteria - Capped ducts
856393d4-0d31-525c-8540-23c3ffba0a99 | note | Standard / Specification - PS 25.13.7 (EV)
aa4d4622-9b47-53ab-86ab-93d1952b42f3 | note | Verifying Document - Visual Inspection
49a600d2-2e14-585d-9770-623d1579084a | note | Testing Quantity Required (based from schedule qtys) - Every time
83f489f6-c501-5886-8d0f-59d42bf3da53 | note | Verification Activity: Activity - M
540f9153-5d6b-5aa1-af8e-9643903d35be | note | Verification Activity: By - SE
f6130397-08e8-4ce0-a540-3cc47db0f948 | checkpoint | 7.2.14 - Survey As Built
c917d21f-5f5c-5488-8761-7090792f90c7 | note | Detail - As Built every ducts joint before backfill
15599aa8-b55b-58ff-9136-e116c106abc7 | note | Acceptance / Conformance Criteria - Completed as per drawings
082d1b26-77ce-55d7-af63-09824fc7dd12 | note | Standard / Specification - Standard Practise
9844df7d-89aa-51d7-8e7b-afe0f708d80f | note | Verifying Document - Survey
59208d4a-d11a-5136-b1bf-c5cce50dbcca | note | Testing Quantity Required (based from schedule qtys) - on going
2d7d2abc-c750-55df-ba48-255dc9dfc286 | note | Verification Activity: Activity - H
64863210-9945-5222-895f-0c411288bba6 | note | Verification Activity: By - PE
3d5a4b31-aec8-4477-89f4-f5d78b84cee4 | checkpoint | 7.2.15 - Compaction - Clegg Hammer
3c639ba4-40e4-53e2-a084-36f65ce0cf7a | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
26a1c758-8288-572f-a9b1-8291585c430b | note | Acceptance / Conformance Criteria - Structural Fill
5a07f515-1b43-5e5f-baa2-1962280ce479 | note | — Min CIV 18
6d1eb0f9-d589-5b61-b955-94868a7c3403 | note | — Ave CIV 20
5e4d7245-a59a-5c38-9674-849ae9bb265c | note | ○ Non-Structural Fill
6aecd11e-9019-572d-a756-9d6416bc720e | note | — Min CIV 10
84d3f092-c8d8-5885-84a6-32dcc3d5b8eb | note | — Max CIV 12
3eec275d-f7cd-57f0-a57b-000f0a585a23 | note | Standard / Specification - Appendix XVIII
fd8b8614-d12c-597c-a8fc-5fd6a8f61623 | note | Verifying Document - Clegg Hammer Report
fe860df6-1752-556a-8728-83a4b7f94d7d | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
699f21ee-9fa8-57c2-9689-d925b1fd0160 | note | Verification Activity: Activity - I
f0f6aa1f-d41e-5f40-9992-7285ae6912d6 | note | Verification Activity: By - SE
bb77894d-96a6-47a1-bae6-3ee4d8e6706a | checkpoint | 7.2.16 - Compaction - NDM
b1b12c28-3bf4-57a2-b24f-6cd2fc949bfa | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
48ad8357-dbd1-51db-afa1-f5df66f5d7ee | note | Acceptance / Conformance Criteria - Ave >95% of MDD
cead46a8-3c1f-5736-ac94-37a712e9ea55 | note | ○ Min >92% of MDD
8241fb33-e645-5f42-bbee-b866a8e8367d | note | ○ Non Granular Material
6d0e8e87-d6e6-5cdb-8b89-5ca8afee9d77 | note | ○ Max Air Voids 8%
f15da55d-efb2-5f1c-9841-dbcb8e09b5a2 | note | Standard / Specification - Appendix XVIII
58db5ace-7eb1-5c2e-8e4d-adeb9dacace4 | note | Verifying Document - IANZ Accredited Report
425b6e33-0b20-58ec-93e3-de61924db965 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
bef9ab69-2807-5b4f-8ed1-cc67e72a853f | note | Verification Activity: Activity - I
13c058ad-f00a-51f0-b4c5-9fbef5454e70 | note | Verification Activity: By - SE
2bef293b-af23-47b5-bdab-947bd7c88021 | checkpoint | 7.3.1 - Subsoil Drain inspection
53874d2b-6167-5fb7-9501-9155c65d2edb | note | Detail - Subsoils to be placed adjacent to the underpass and inspected by Engineer
f927d032-3268-559b-9695-22591f0a85a8 | note | Acceptance / Conformance Criteria - Engineers Approval
5b96c700-928e-5ab0-8946-cba869eef8bd | note | Standard / Specification - PS 17.6.3
e911f0ba-56dc-5a50-93eb-6408e9621b79 | note | Verifying Document - Visual Inspection
60a6e3ba-5630-5852-be7c-53d4934507d6 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
39bbde72-2a94-50c3-a6b3-41ed72821aec | note | Verification Activity: Activity - I
7d3414c6-e6d3-59c4-adba-18ffa27058d5 | note | Verification Activity: By - ENG
30d27084-1af9-420e-a498-8913e732463f | checkpoint | 7.3.2 - Excavation
4fd35dcd-bcde-5f84-b7bb-632b32d40b9e | note | Detail - Excavation of Trench should be within tolerances.
8cbfed79-b15c-5644-89c5-405cfa227981 | note | Acceptance / Conformance Criteria - 335mm deep x 300mm wide
6fd1f8f8-461d-58c3-a327-e12cca592e09 | note | Standard / Specification - Drawings
03a6b2c9-04bd-5844-a21f-86fe368f39a9 | note | Verifying Document - Checksheet
edca8fe7-9e67-510c-a97a-66577612d5aa | note | Testing Quantity Required (based from schedule qtys) - During Construction
077478fd-84c1-567f-baa0-4ff9052ab04f | note | Verification Activity: Activity - M
72d057d6-1535-5262-b53d-ee457a1545a9 | note | Verification Activity: By - SE
274799d6-e763-4c65-94f4-f23b96b007d3 | checkpoint | 7.3.3 - Placement of Bidim
33d82f4d-2f6c-566f-97f5-06e60835ba9a | note | Detail - A29 Bidim to be placed and wrapped around Trench.
33cbb629-8826-58e1-84ec-17c30ce85ffe | note | Acceptance / Conformance Criteria - Minimum Width 300mm.
275fc9fe-cbcb-5bac-b2d1-b7f5b1e282c3 | note | Standard / Specification - Drawings
f53dde7c-25b6-5d2e-9828-9d455f834406 | note | Verifying Document - Checksheet
58030cfd-6338-5630-8715-722920b7d546 | note | Testing Quantity Required (based from schedule qtys) - During Construction
6c1d7673-0196-5e73-a3d5-c8a579fa2f76 | note | Verification Activity: Activity - M
64f6f18f-a0ca-5e53-8b1f-1a15cf6496aa | note | Verification Activity: By - SE
2cf98304-dc5b-4159-b4db-b23f883f4ff4 | checkpoint | 7.3.4 - Cushion (Bedding)
c6838d0f-f2b0-5bc7-886a-5eeafa13b9f2 | note | Detail - Pipe must have 75mm of Cushion. Drainage 60:40 Material to be used.
ae6f8016-0e7f-54c7-a3b9-86083e6f58a3 | note | Acceptance / Conformance Criteria - Minimum 75mm
67d2307e-5566-56ba-ad61-ef93f482d1b8 | note | Standard / Specification - Drawings
d80d2229-f177-59e4-859f-1a625cc45e1b | note | Verifying Document - Checksheet
06047cfb-4abd-5ed9-b671-f3caa5dba030 | note | Testing Quantity Required (based from schedule qtys) - During Construction
90eb5e1a-b493-5c4b-bf09-0deb0136aaa8 | note | Verification Activity: Activity - M
3066241c-50a0-58a9-b1ce-ba4c5d8f125c | note | Verification Activity: By - SE
3afbd52a-e569-4a3f-b8c6-23be3882993c | checkpoint | 7.3.5 - Placement of Pipe
5cbfa824-9f4c-5120-b401-9934dfd8e21d | note | Detail - 110mm Perforated Pipe to be laid Down
f868f61b-5641-5b20-a2db-89869af00759 | note | Acceptance / Conformance Criteria - As Per Drawings
2af135c0-6e27-58d6-9e4c-629c569b77c5 | note | Standard / Specification - Drawings
480b4e66-e040-5983-9bdb-de41d851dacc | note | Verifying Document - Checksheet
fde20892-54ab-5359-bb60-1dd5c014898a | note | Testing Quantity Required (based from schedule qtys) - During Construction
0237cf55-c23f-5835-ba56-e8a4e2b93f5c | note | Verification Activity: Activity - M
56e5c482-a9cb-59f3-834e-e839c27eb852 | note | Verification Activity: By - SE
9007e882-468c-4dab-8f80-b469d79df367 | checkpoint | 7.3.6 - Backfill
486ced27-349e-5ea0-90d7-ac472cdbf8b8 | note | Detail - Pipe Must have a 150mm cover from Bottom of Pavement.
d7d28cb3-0619-5ceb-acae-8c24b229f867 | note | ○ Drainage 20:40 Material to be used.
2dbbb1b1-f6f1-50a1-8afc-b100fa41d3a1 | note | Acceptance / Conformance Criteria - >150mm Cover
ef3b8cc1-f060-58b9-aab3-927521815bea | note | Standard / Specification - Drawings
3e5114f4-a7c2-528b-8ff5-c33c5e2a9b57 | note | Verifying Document - Checksheet
60c7880f-d490-5304-bc6d-59c22f42b5f4 | note | Testing Quantity Required (based from schedule qtys) - During Construction
ed11fe8b-76a8-5de4-8fce-01ce20bd7758 | note | Verification Activity: Activity - M
3ac0994a-983a-5b30-a901-ec6f8e080a3f | note | Verification Activity: By - SE
06e785a8-2bc2-4c28-9e1c-6557d16a3e74 | section | SECTION 8 - UNDERPASS GRATED TRENCH DRAIN
7ea89661-76d9-471c-98b5-35fe95cb9097 | checkpoint | 8.1 - Installation of Channel Drain
6d70d952-8dfa-55c3-978e-219ba0e5881a | note | Detail - 300mm wide grated trench drain with WAVE HEELSAFE grate to be located at end of underpass apron. Trench drain to connect to SWMH2.1.5 via dn150 pvc-u sn16 pipe. Grated trench drain to have min. loading class C.
71194f36-a250-5e52-a32d-d1001faed2b6 | note | Acceptance / Conformance Criteria - Installed as per manufactures instructions
46228688-06bd-5d0e-bdad-652a3e0e7189 | note | Standard / Specification - 21.5.8
22b6ad59-d5a4-5604-91f5-20a87e0fa30d | note | Verifying Document - Inspection and record
26479267-eaef-5358-b87d-27d60a76afd1 | note | Testing Quantity Required (based from schedule qtys) - During Construction
e5dd5f2d-c4da-5a98-b19c-86e7954cff2e | note | Verification Activity: Activity - WP
81c0c4f1-3a39-5eea-a4e5-f7bb7e43775d | note | Verification Activity: By - ENG
eac79c25-3944-47e8-8c5c-3a2c5cf3a25d | section | SECTION 9 - AS-BUILTS/ REDPEN MARKUPS (Wave Heelsafe grate and minimum internal fall of 0.5%.)
76b38cff-561e-4a0b-90aa-8928b15e8b87 | checkpoint | 9.1 - As-Builts/ Red pen markup
7c01667f-35d2-5b5d-9937-c5af1283c34c | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
e0f0411a-dd8d-5f8d-87a7-c5b49cd2241b | note | Acceptance / Conformance Criteria - As built drawing red pen markups
b2dede63-43f7-5ddc-937e-22820e716c3e | note | Standard / Specification - PS 16.7.6
2f4e4548-487a-5de3-99ce-8604816c033d | note | Verifying Document - Red pen markups
3d7a0db1-6e32-50a0-8899-86c15422229d | note | Testing Quantity Required (based from schedule qtys) - During construction
e60b0e2b-4f56-51cd-b2ec-d037e258455f | note | Verification Activity: Activity - D
24052928-16d8-5911-809f-43f3188ad450 | note | Verification Activity: By - SE
895397a8-2585-42aa-b610-601aba07d608 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
4d3df032-c5b5-5939-a038-2d5f20b0b517 | textbox | Contractor's Rep Name:
5f770dd6-a56f-5a7a-b5f0-91ed374c2ae7 | textbox | Engineer's Rep. Name:
997b729d-b529-5961-8b1d-ef5d4a30db35 | date | Date:
0913e469-4c69-475e-adce-5b7b7878f2b2 | signoff | Add Signature
c38c2dfe-ecac-47aa-81ac-df9a3147b4a8 | checklist | DN1210-042 ITP SMA surfacing Rev 0 | itp | DN1210-042 ITP SMA surfacing
93f84c73-0c17-48b1-9b97-a2928e3aaaa0 | section | 1.0. Pre-Commencement Activities
40b8392d-f3d1-4496-9c7e-73b908e0adc5 | checkpoint | 1.1 - Approved JMF for Asphalt Base or Wearing Course
b009f629-928f-59a1-abbe-74501f4c326c | note | Detail of Activity / Test - As Per DN1210-WSP-NTC0606 for whitehall.
c8c9638f-a8e9-5587-846f-485fb3eca316 | note | Action (Hold, Monitor, Witness) - H
e74917cc-a823-507e-87c5-3dab37bad7e8 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
3c262d51-8e46-5d81-b6a4-909fc4d80417 | note | Inspection / Test method - Confirm requirements are followed
836faac9-1ef9-503d-b931-53437b86436b | note | Acceptance Criteria - JMF Validated in accordance with NZTA M/27:2020
a3a3000d-2bf0-581c-b61c-e5fca21438d3 | note | Record documents (QCP - Quality Control Portal) - Mix Design Report
ec085948-51d6-58c1-8c2c-8910fbb891f0 | note | Responsibility - Paving Contractor
d8442541-3901-56c5-8e17-2d9b6d182cfd | note | Project Specific Notes / Instructions - JMF expiry date and validation details in here
562a9d6d-a261-5a72-9905-0c2d9f3a907a | note | Designer - A
74db58e8-a9b9-556a-8429-a2dcceceb828 | note | Eng. Rep / NZTA - I
31195b1e-0b7e-563c-8900-3b42fda5168e | note | Contractor - R
09110bbb-0a9e-477a-91c1-b3484fe538d7 | signoff | AUTHORITY HOLDPOINT
1d1381d7-8691-485c-a0a8-36e53efb01e2 | checkpoint | 1.2 - Site Conditions
116740d2-79e5-596b-910e-aec15176b979 | note | Detail of Activity / Test - Weather suitable, Site extents marked, surface suitable for paving (Depths/milling/cleanup complete etc), Environmental Controls in place
cc2bd413-842d-5af3-9223-89da00f11e80 | note | Action (Hold, Monitor, Witness) - H
dab61d3c-5acf-5f12-876b-4e922f26f947 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
2edc1b0d-9e94-56aa-9c66-b880d21a6408 | note | Inspection / Test method - Confirm requirements are followed
3c714298-40d8-52bf-b6d0-bf535c117fc2 | note | Acceptance Criteria - Weather conditions and Site is suitable for paving
a02bfdfb-e6f6-5109-8966-d9dcf53e0677 | note | Record documents (QCP - Quality Control Portal) - Site Diary
a51c471c-d7d8-57f1-a27d-241357c04aca | note | Responsibility - Paving Contractor
5cf59c8d-c255-535e-80f5-699a97d92db8 | note | Eng. Rep / NZTA - I
829a47f3-1775-5d32-b660-be70e77c1264 | note | Contractor - R
0ce18a22-6a2d-4244-a673-02fbb3e8fb37 | signoff | AUTHORITY HOLDPOINT
830e5905-e535-4116-a273-92dd50c536f2 | checkpoint | 1.3 - Traffic Loops
d26b3968-74f3-571c-8485-184f3b95be2d | note | Detail of Activity / Test - Communication with affected parties
0d8e60ae-dfeb-54b5-a252-c0f907fb7a28 | note | Action (Hold, Monitor, Witness) - H
d1b15046-89d5-5ba0-8cb2-09ba82f62a44 | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 7 days Before Works commence
4e17fcc7-9cbd-539c-90af-793283f533f8 | note | Inspection / Test method - Visual
0b848f42-b72d-5661-a01e-0f8a2210b2b8 | note | Acceptance Criteria - Notify RC at least 7 days before surfacing is programmed
35232349-a64f-5b6c-b714-4eb6ef918223 | note | Record documents (QCP - Quality Control Portal) - Communication
22160b9c-d22f-5866-ace8-37b48dc1ce3d | note | Responsibility - Paving Contractor
689cf066-46d2-52dd-8553-d8ccfd53765a | note | Project Specific Notes / Instructions - only required where existing traffic loops are present
c7132b48-6132-50f7-b594-3bf9aef197ae | note | Eng. Rep / NZTA - A
708d1b91-1ded-5174-abaa-b2360e5282a5 | note | Contractor - R
df0a9f3d-7f72-4572-bb9e-ff9086558031 | signoff | AUTHORITY HOLDPOINT
5ea5cd51-5d13-489b-89cb-3ab03355d8ce | checkpoint | 1.4 - Paving Plan
47cee0eb-5eee-5a58-bd3a-0b042918e793 | note | Detail of Activity / Test - Paving Plan to be completed
0b57c434-2319-5828-80dd-6212a310ec51 | note | Action (Hold, Monitor, Witness) - H
7cf71f76-775f-5df9-af0c-69729a0db3d3 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
3df2c26c-57ba-5efa-99b8-13b1896e7cbb | note | Inspection / Test method - NZTA M27: 2020
b6826d2d-ab71-5303-ba8c-48232269f5db | note | Acceptance Criteria - Paving Plan to be completed for each shift with dimensions, location and type of (hot/cold) joints, areas and tonneages
b615be40-c3c9-59c4-978d-2aa50b53e561 | note | Record documents (QCP - Quality Control Portal) - String Sheet
0722f406-9df5-51cb-98fd-a8791c13cb4c | note | Responsibility - Paving Contractor
36296e4c-7b4e-5bb1-aa7b-c9df1b3cbb81 | note | Eng. Rep / NZTA - I
05d15b45-f380-537d-be9a-badbab446047 | note | Contractor - R
c6ebf674-2b6f-4b29-b9a3-ec57352d2fca | signoff | AUTHORITY HOLDPOINT
f67f57a6-4986-47e2-a7e6-e6b7c2f81e42 | section | 2.0. MANUFACTURE OF ASPHALT
c6efa70e-5e4c-443d-9ae0-1054be367e23 | checkpoint | 2.1 - Temperatures
22139f0d-e85a-5ab4-ab43-2ebb9a21ba7e | note | Detail of Activity / Test - Mixing of aggregates and bitumen
90dcceae-9403-5603-91fe-4a11cee98117 | note | Action (Hold, Monitor, Witness) - M
a835eed0-789b-5d7f-948e-289d7c2d7caf | note | Minimum Test Frequency (Lot = 1 day’s production) - Constant monitoring of temperature by calibrated equipment
de9a0772-e6be-5492-92e3-059f36e19785 | note | Inspection / Test method - Plant temperature probes
c7dd6b39-e7b4-58bc-aec3-aebb8985df8e | note | Acceptance Criteria - NZTA M27 2020 (4.3) states max. 185 deg.C
ae1af63f-6542-55bf-9795-2126512d4804 | note | Record documents (QCP - Quality Control Portal) - Plant site diary
02b2f173-a805-58e9-bc33-ee897bf68939 | note | Responsibility - Asphalt Manufacturer
708b571b-7362-5f6c-b711-30ed4f987165 | note | Designer - I
e6fc2955-0943-5f87-862c-9e6aa21ea4d0 | note | Eng. Rep / NZTA - I
c10f7199-6d38-5151-ae0d-a8554bd2d47b | note | Contractor - R
c41d6e49-41aa-41df-b5a1-0b07813e5789 | checkpoint | 2.2 - Production Asphalt
1aca2d36-077d-56da-8034-06f62dafdf10 | note | Detail of Activity / Test - Particle Size Distribution
3d245d40-53c1-5608-8d0e-cc7f27905a8d | note | Action (Hold, Monitor, Witness) - M
7c3f9722-cc19-59ee-a5b6-1d790db46877 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 300t at asphalt plant
4dede341-bdca-582c-827a-3381f5ecf6e6 | note | Inspection / Test method - NZS 4407 Test 3.8.1
5ca8b0c4-a667-5d7f-900e-2390fc033ce3 | note | Acceptance Criteria - NZTA M27: 2020 Refer to Table 5.2 (Refer to CWP for image)
8586bc7d-c0c8-5e6d-8720-1cf737bc69e8 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
6d72479e-95a2-5c6b-87b7-bc73fc255a16 | note | Responsibility - Asphalt Manufacturer
5089efe5-0e52-58b3-ab0e-cff41f2a4dbd | note | Designer - I
9011a956-7ff4-521e-95bc-b78a775df2af | note | Eng. Rep / NZTA - I
23f0734d-4cb7-5c4f-870a-8307f146d896 | note | Contractor - R
066af28e-589a-4154-9abf-2be7e168204a | checkpoint | 2.3 - Production Asphalt
8446de57-50af-562a-8ffb-d3bcdf00afeb | note | Detail of Activity / Test - Binder Content
c4540af9-8fb5-549a-8ca6-6aae3c3835db | note | Action (Hold, Monitor, Witness) - M
cdf9a2d2-267e-5cec-b289-15c5f7656646 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 300t at asphalt plant
acc59c34-9339-5add-93e9-7415b3641a06 | note | Acceptance Criteria - NZTA M27: 2020
852a9f71-c26b-5094-93bc-118edc975a3f | note | ○ Individual Test Result: ± 0.5
81cfb8a2-0a12-5be5-9c51-36166b26f138 | note | ○ Mean of Three Test Results: ± 0.3
67257155-5879-5350-9c50-48dff9996afd | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
1ea141da-fdf6-50a1-a076-6032500d6a30 | note | Responsibility - Asphalt Manufacturer
4915ed27-ac63-5759-9018-ec42c8f31fb0 | note | Designer - I
10473289-ebff-5c77-9a21-a01c9f1caf56 | note | Eng. Rep / NZTA - I
ad1db74a-1fd1-52f4-8f7a-6cefdee5a5e2 | note | Contractor - R
026423ab-a8f0-491c-bea0-8acd0c3433d0 | checkpoint | 2.4 - Production Asphalt
b965899c-6a14-5739-9e60-8a057b91301f | note | Detail of Activity / Test - Max. Specific Gravity (MSG) of mix
48700722-a660-5860-8cd3-6ec34f753993 | note | Action (Hold, Monitor, Witness) - M
f4c59aa1-8106-5b5a-bfd2-91616b92ef11 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 900t at asphalt plant
11db835a-585d-5456-989b-fbc59e621c9e | note | Acceptance Criteria - Report
da910189-e349-5050-a750-8296927c024c | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
c4fdd448-5448-510f-b173-88bb81684c26 | note | Responsibility - Asphalt Manufacturer
676dbeb9-6c43-55f5-b90a-9faa57c25332 | note | Designer - I
5709849c-5ef6-533f-b9d1-2fa573aac328 | note | Eng. Rep / NZTA - I
23c76725-1fdd-5ba6-97a8-f3ed75e2c085 | note | Contractor - R
382d76c5-4eaa-4640-bc9b-964eebf9f813 | checkpoint | 2.5 - Production Asphalt
4466c2c7-3ac1-556e-93f3-5d9ba6482ecc | note | Detail of Activity / Test - Air Voids at lab design compaction
6f689509-47e7-569e-980d-e15a42acf181 | note | Action (Hold, Monitor, Witness) - M
cf939f8c-187e-511c-91dd-b18ad02eef1d | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 900t at asphalt plant
650f9aa0-99e4-5d53-a7af-0bda663470f4 | note | Acceptance Criteria - NZTA M27: 2020:
0bd95e0e-6ff7-5439-a553-8223ab1a67ac | note | ○ Individual Test Results: +2.0, -1.0
fbdf5ed5-57a6-55af-96a7-e7ff53aebbde | note | ○ Mean of Three Test Results: +1.2, -0.6
8eee6b1b-838a-5003-bdb6-b10b837ea88c | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
56ed48fb-7283-589d-8e09-930b409c7c04 | note | Responsibility - Asphalt Manufacturer
e6c95d26-761c-583d-954c-ae82c76bc002 | note | Designer - I
4ea4fc06-74e1-5087-b1a2-a07f1d063bf1 | note | Eng. Rep / NZTA - I
73be4e63-0daa-519b-87ae-39469aed612b | note | Contractor - R
35f8494a-4d5d-4859-b39f-0d5d876f6a2e | section | 3.0. PLACING AND FINISHING
1c67eee1-5921-4dfb-b3db-ff3cc0cde864 | checkpoint | 3.1 - Tack Coat
0cc7f63f-ab9c-57f7-b3b4-f9b842946f35 | note | Detail of Activity / Test - Application of tack coat Seal M/27 section 9.3.1
dd8479c2-15f5-55ee-9a4d-c32c68b64875 | note | Action (Hold, Monitor, Witness) - M
ae9c4959-9da3-5b24-a48a-5e9283b6899e | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
8a5adddf-6d7c-580a-b5cb-32d91885c81c | note | Inspection / Test method - NZTA M27: 2020
f2a19dde-1e07-52bb-9c25-ee16a5666575 | note | Acceptance Criteria - Application rate, binder as per seal design
4e859eb8-a068-5747-a6a3-3671083e0369 | note | Record documents (QCP - Quality Control Portal) - Sealing Records
c59591df-1a57-501a-943d-4ab659aa104a | note | Responsibility - Paving Contractor
63842be6-ff5e-53fa-ab22-7e0d5b45f967 | note | Designer - I
3f109af1-af75-55f1-9a1c-f970b79f7676 | note | Eng. Rep / NZTA - I
9e5061bf-8402-5d06-884b-c7bfc6c0d68c | note | Contractor - R
1ba55010-ea45-4f25-ac69-faa8d98592fd | checkpoint | 3.2 - Temperature
02cf51a7-976f-50dc-91cc-2e9ef437eabc | note | Designer - I
53ceb854-ecf2-5dcd-855d-cdae77431dd7 | note | Eng. Rep / NZTA - I
73b570fc-d48c-566d-a977-614b1f5d4b60 | note | Contractor - R
dc6975a7-9e40-4b1f-8474-ef1beebf6bcb | checkpoint | 3.3 - Temperature
1d69d130-376a-5fd3-85bf-b792af37a305 | note | Detail of Activity / Test - Asphalt Delivery temperature
d6823b14-3aaf-55b0-ab3e-6e3c434a4f95 | note | Action (Hold, Monitor, Witness) - M
a2c52658-aec3-511d-9cb7-ee0adbcbc859 | note | Minimum Test Frequency (Lot = 1 day’s production) - Every Load on delivery to the Paver Hopper
6f613c69-24df-5834-8650-7e1bf7beed34 | note | Inspection / Test method - Temperature Probe
bc8cd468-fabd-5638-8b69-8ffc6366ec8e | note | Acceptance Criteria - Target ≥ 150 deg.C. in the Paver
ff91edf9-0557-5f6c-b494-ff9a80c6bd36 | note | ○ Min. ≥ 125 deg.C in the Paver
7e4295d3-ca6e-57fe-b0aa-8d049d90b7e0 | note | ○ <125°C to be Rejected
cac41cda-b478-57f9-b691-1e4a050f7744 | note | Record documents (QCP - Quality Control Portal) - Site Diary
6c86bcb9-15d6-5803-9837-0dafc16f069b | note | Responsibility - Paving Contractor
da0eee88-b821-5d0c-a032-c0c5ae6dbd99 | note | Designer - I
24135171-67b5-51db-85c4-42dff1755eb8 | note | Eng. Rep / NZTA - I
be3e17d8-a8c0-5f00-8138-10528e4c0d0f | note | Contractor - R
9fc65b81-ab04-4815-8b6a-4a7d76ba5988 | checkpoint | 3.4 - Temperature
e77db8f4-c729-57c7-b1db-5c6ba9b7ab2a | note | Detail of Activity / Test - Compaction Temperature
3a3d78fd-a713-57af-9ad5-8a05111b3c03 | note | Action (Hold, Monitor, Witness) - M
8ca325d3-8735-5562-a308-c9d4e4515a1e | note | Minimum Test Frequency (Lot = 1 day’s production) - During compaction
4ee85df0-5578-5075-a9bd-67cb1a18a82c | note | Inspection / Test method - Temperature Probe/Infrared gauge
a0d63bd1-7666-599f-86fe-0c4973baaa1b | note | Acceptance Criteria - ≥ 125°C at commencement of compaction. < 80°C - Stop Rolling
581c2528-23d5-508c-9a65-e329d47c0924 | note | Record documents (QCP - Quality Control Portal) - Site diary
7c7f4b2a-5046-5dc9-9eb9-f6db30a12b5e | note | Responsibility - Paving Contractor
fc7eda48-1e36-54df-abf6-1cd6a5a6c1ac | note | Designer - I
1ec0ccac-1782-5228-968e-d36265576d60 | note | Eng. Rep / NZTA - I
4f5c7cce-7d5f-5471-9559-049b606bf4ce | note | Contractor - R
6dcad607-644e-41d6-aa90-a1095aefdc27 | checkpoint | 3.5 - Mat
7de7feb4-0c71-5527-8d04-0757bbf3abd7 | note | Detail of Activity / Test - Load Locate
3bb38dcb-e266-5efa-b815-b4c6cf5c8a5c | note | Action (Hold, Monitor, Witness) - M
b7cfb52d-cb91-53dc-976c-444ba407a024 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each load
54204ef7-2dda-53d6-a7a4-6bbbdf727141 | note | Inspection / Test method - M27:2020
6f654738-1e7c-5a27-ad47-f914b9dcb581 | note | Acceptance Criteria - Each load can be indentified to a location using a diagram. Record includes:
3a8d5edf-9e7e-512a-bd0b-303887b27e6f | note | — Truck ID/Rego/Driver
750916a9-9707-5a67-89f2-84a0a3dab52b | note | — Depart Plant Time
28c5119f-b8fc-593c-a908-a4f27ff9b667 | note | — Arrive Site Time
3077474e-b2f3-59e6-9430-884557dad5f3 | note | — AC Temp on Arrival
d1f85238-2a3f-5efc-ad8a-cec39c1c878c | note | — Tonnage
ddf552ac-0aff-5995-a7ab-b3c0d6533498 | note | — Run Width
1e8ade00-324c-5c25-8354-4e93e3973d28 | note | — Estimated Run Length
109f2ca2-137c-5238-af59-2b8560f4ad09 | note | — Calculated Area
dacfa6a0-50d6-5696-ae52-0ba434834ea8 | note | — Calculated Average Depth
e449063f-7664-5e63-995c-e68d7b775038 | note | Record documents (QCP - Quality Control Portal) - Paving Run Sheet
92d1707a-a457-5ebc-b6ac-868b23fa219c | note | Responsibility - Paving Contractor
d1957fc8-f2ea-580d-b77c-e9340863f08c | note | Designer - I
51b1800d-f743-5ce8-a989-95c19ac58117 | note | Eng. Rep / NZTA - I
1bfc6142-50d1-51ab-a425-6b5d66a30327 | note | Contractor - R
54ec0fef-5a73-493d-9739-cbda765b4836 | checkpoint | 3.6 - Mat
7fea047f-f52e-5051-bd3d-238131e3cf47 | note | Detail of Activity / Test - Thickness Monitoring
3d292065-5b9e-56d2-946d-85c7bb450120 | note | Action (Hold, Monitor, Witness) - M
c921cda9-9206-523e-8f90-ddf845cb364e | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
25d8c0bf-9756-5152-8f1d-a58770a05e76 | note | Inspection / Test method - Dipping
1844deee-93d8-568c-bde8-f7682bc7c915 | note | Acceptance Criteria - Target Loose Thickness -0mm / +10mm
f89ab3e3-b520-5d50-911d-cf69b0e2a209 | note | Responsibility - Paving Contractor
73a9a5e2-3d88-5fe3-b746-2a21b8663d6c | note | Designer - I
2af146b7-7ea3-5a16-8793-ff85156feed9 | note | Eng. Rep / NZTA - I
f6499d1d-6728-5651-ac93-cb99b3702bba | note | Contractor - R
640d4519-25a8-4dd8-b13b-d348c7463b27 | checkpoint | 3.7 - Mat
5a89dbe1-d9d0-581b-ba98-cc5c815602c9 | note | Detail of Activity / Test - Compaction - NDM
1132c486-61f4-5f2c-b3c6-a345ef2497b0 | note | Action (Hold, Monitor, Witness) - M
2381073d-2bf6-54fc-a241-493c5adfa727 | note | Minimum Test Frequency (Lot = 1 day’s production) - Plateau to be completed on 1st run, thereafter monitor compaction/roller passes to achieve target density.
c6cd4414-4b6b-56a2-9a6f-f8bbf835988e | note | Inspection / Test method - Insitu density and air voids
5bf74152-e03d-5523-a64a-1d9f089d2f16 | note | Acceptance Criteria - NZTA M/27: 2020
aae98ee5-bedb-534e-ab33-69f7fbcb732f | note | Responsibility - Paving Contractor
dd1c3984-d777-5899-b5a4-367af2cdbd75 | note | Project Specific Notes / Instructions - Use a calibrated NDM with established core correlation. Locate and mark cores, record NDM Bulk density by core location (including any offset used).
69ea04a6-3e88-5dcb-a99a-fe2852e5a1f5 | note | Designer - I
607755d2-a91f-5c5c-8686-639214f26811 | note | Eng. Rep / NZTA - I
8f732725-9eb3-5eb6-b833-c67010faa708 | note | Contractor - R
99401708-36c7-4b38-9078-bdf0247669be | checkpoint | 3.8 - Mat
eb54dab8-dd84-56c9-bc6a-2e432e53c59c | note | Detail of Activity / Test - Compaction
ba31f980-698e-5152-beeb-4ddaaf5088de | note | Action (Hold, Monitor, Witness) - H
f7074be8-0453-595c-978a-25f03d059370 | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 2 mats and 1 joint per lot
9f4458a7-601d-57fe-a83e-da17ba87d4b9 | note | Inspection / Test method - Insitu density and air voids
7dcad680-d438-5ee7-a261-8ba9009f689f | note | Acceptance Criteria - NZTA M27: 2020 - section 9.9, GCO373 and GCO371
28d0abe1-564d-557a-8fc5-bee3076cc4b8 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
090737d5-8067-58fe-9546-e0b31472a76b | note | Responsibility - Paving Contractor
f1a1aad1-54fc-51ea-aff6-b494c4924664 | note | Project Specific Notes / Instructions - A pavement lot shall be an essentially homogeneous section of work completed within a shift of production.
d350e1c4-f2c6-58dd-a4be-55c7ac11ab90 | note | ○ The lot shall be divided into an appropriate number of approximately equal sub-lots and a core shall be taken randomly within each sub-lot.
9ab6da57-7f73-5d43-a01a-a48fa8dcbaee | note | ○ The Engineer or their delegate shall use a random method for locating each core position, such as ASTM D5361 or a similar process.
21af96b0-40c8-5838-8ac5-8b06efb0cc7a | note | Designer - A
d4ec122a-9149-5913-9196-9eeb60599002 | note | Eng. Rep / NZTA - I
00de1d6f-ac8e-5bc4-8856-374885a17186 | note | Contractor - R
5f017203-05ae-4163-b8da-5613cb70f149 | signoff | AUTHORITY HOLDPOINT
36c22244-4d26-4b14-b7ef-2c6364db1516 | checkpoint | 3.9 - Mat
522e37e3-85a3-5e65-81d6-14a50f7b31eb | note | Detail of Activity / Test - Thickness
02bf6e75-4ba8-519b-a92f-fd32e9a070e9 | note | Action (Hold, Monitor, Witness) - H
1a9bdd56-b2d6-5cb1-affc-458d65c1e760 | note | Minimum Test Frequency (Lot = 1 day’s production) - Average of 3 measurements per core
4b8132c3-0516-5762-8a57-09983b33de16 | note | Inspection / Test method - Measure Cores
635381d2-91b7-5055-8520-567e177bf561 | note | Acceptance Criteria - Average Thickness > Specified Depth (Nominal), NZTA M27 2020 - section 9.7
97c7d11b-dd91-5dd9-a2cb-ab5543d3123f | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
df461eb8-e7c8-5130-9171-90448616b210 | note | Responsibility - Paving Contractor
bc754158-82e7-519b-8042-89e7dab9c8aa | note | Designer - A
6dfa51f8-1e98-5f02-ad4a-1d56d0dddb05 | note | Eng. Rep / NZTA - I
a4fa2e2f-c2e4-5599-baf8-104e9a25e3e7 | note | Contractor - R
702e9a0a-5e7c-4e34-af53-500a731cf095 | signoff | AUTHORITY HOLDPOINT
10bb20e1-6cad-45a7-adf2-92f81de504aa | checkpoint | 3.11 - Mat
9a9146ba-8067-5d0c-bdd5-7f0cd0a097c6 | note | Detail of Activity / Test - Shape
7a99cace-0d7a-5608-afa2-36144df10ec8 | note | Action (Hold, Monitor, Witness) - M
2b41cabe-6987-5e0f-866e-6ceb61c3319b | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
6173f21d-4625-5475-8553-19430158986d | note | Inspection / Test method - 3m Straight edge
1442eb6d-543b-5c63-ad38-336e9cb4b328 | note | Acceptance Criteria - Where the length of the site or the geometry is such that a road roughness-measuring vehicle cannot be used then the straight edge can be used for checking the surface shape. Refer NZTA M/27: 2020 - section 9.8.
0d0617e1-bb54-5b31-81ff-43c647653954 | note | ○ Not more than 5mm under a 3m Straight Edge.
c8bc8cc6-060c-50e7-ba37-3a979411cb4f | note | Record documents (QCP - Quality Control Portal) - Straight Edge Record
e5c0d013-c5be-5173-99ea-b6a2f1e0749c | note | Responsibility - Paving Contractor
e3a2e179-cc74-5b28-a934-fa60a99a05bf | note | Designer - I
b01cfbd4-64a8-5917-850a-09d6e5f3c315 | note | Eng. Rep / NZTA - I
c4c76684-b157-51f4-89f8-a7d701106f92 | note | Contractor - R
20dcc8d5-29be-4872-afe7-cabc540f8bd0 | checkpoint | 3.13 - Paving Quality
1253fe09-3b39-5d24-83c0-65d1eb2108cf | note | Detail of Activity / Test - Level
61ca1e82-8787-5ad1-abe3-3e85409e71f2 | note | Action (Hold, Monitor, Witness) - M
4a96b875-5927-58c0-b528-0656c9c8242e | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site
9efac57f-ff39-5f72-84af-be9c81efcdf9 | note | Inspection / Test method - As Built Survey
72142a56-79d9-55d4-b854-7719fb13dc83 | note | Acceptance Criteria - -0 < +5mm from Specified Level
a350ed1e-2415-5c13-8038-5cdfc9f4ccfe | note | ○ Where there is Kerb and Channel shall be flush with or no more than 5mm above the LOC.
6a5f99fa-e392-5cd4-819e-fa71fcba816a | note | ○ Note: Minumum 55mm not nominal 55mm.
83fb0ab6-358f-5941-8549-03e2761eec73 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
458080fd-95f2-5586-8efe-6fade12bc994 | note | Responsibility - Paving Contractor
3fac5c3c-fcdc-5927-b5e8-275927cabc6f | note | Designer - I
df3668c7-dc3f-5a9a-883e-8c9a90e65f30 | note | Eng. Rep / NZTA - I
4e48bc92-a6b1-5946-9512-a80100a9b275 | note | Contractor - R
ce3e6af8-c218-4437-9609-5520a7135c68 | checkpoint | 3.14 - Paving Quality
b9d71ad9-73b0-5b26-a856-22a97e0d40bd | note | Detail of Activity / Test - Alignment
43e2c80c-3edd-5bb6-9767-e3575e0ca1e4 | note | Action (Hold, Monitor, Witness) - M
b2127be1-3e59-5f2a-b0ec-562732d2d8ef | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site
2452d998-52d1-56ed-a13f-6727857c365f | note | Inspection / Test method - As Built Survey
13c617f9-ddcf-5afd-a6fb-3d98dc9d80f0 | note | Acceptance Criteria - Kerb to kerb
6fe94527-884f-5ff8-849b-0ab8b683bcd5 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
3f4bd312-cd9c-5583-9589-0d59697ac546 | note | Responsibility - Paving Contractor
fea7c4ea-1c23-5f4a-901d-4e36e0524e4b | note | Designer - I
740ebe75-008d-504a-9426-2e67555e60e7 | note | Eng. Rep / NZTA - I
e29f86ea-d695-5d8b-8d70-58050bb3625a | note | Contractor - R
683d7aa8-9689-479c-92e1-c1a05054e2c7 | checkpoint | 3.15 - Post Paving Completion Checks
d44f3b12-c9ce-5022-85ac-44d4810b0fbf | note | Detail of Activity / Test - Site clear and cleanup
ee9c1dc1-47fa-5865-acb6-684afd651cc1 | note | Action (Hold, Monitor, Witness) - W
78122648-ed02-5a09-8008-268cf6df8a4f | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
97ee2bd6-97d6-57a2-9fc6-309de3dcf40f | note | Inspection / Test method - Visual
30d80e58-e44d-56ba-8157-79f6f0243e5a | note | Acceptance Criteria - Site is cleared of plant (or parked in safe location) cleanup of all waste mix, paper and detritus is complete
67443bc2-e479-5620-8afa-f66d2520f8f9 | note | Record documents (QCP - Quality Control Portal) - Site Diary
be76505d-1ea8-50cd-b71e-76a6ed94719f | note | Responsibility - Paving Contractor
45fa8cc2-c443-562f-babc-ab62bf58cccb | note | Eng. Rep / NZTA - I
5df5e717-e1f7-52c3-8124-e452d2c7894e | note | Contractor - R
466bc9a9-b1e5-42c4-918c-85ceb3a7a94b | section | 4.0. As Built Records
490f6081-4db7-41dc-ac75-ad7f2ce4acf5 | checkpoint | 4.1 - Assessment of all test results for conformity
0496b996-7edf-5011-8073-1ad5868deecf | note | Detail of Activity / Test - Review against ITP Requirements
a032829b-cc3c-5adb-a837-7e3464029fce | note | Action (Hold, Monitor, Witness) - H
13df84b3-4150-5b6e-b34d-e6cc4d96a2ad | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
8fe786ef-6807-560d-856a-696a4b4c6018 | note | Inspection / Test method - Review
d11cdc55-82ea-53cc-be6a-5a6469c9f676 | note | Acceptance Criteria - Reporting of any non-conforming results to Engineer via NCR
b1ad0495-c7d6-58e6-ab89-fdbd52dba6a3 | note | Record documents (QCP - Quality Control Portal) - NCR
e6c4b44b-9a53-5f1b-8594-f166af48206a | note | Responsibility - Paving Contractor
e1ea552f-6132-51d1-8627-c9c6686c56c0 | note | Designer - I
9945c453-6e5a-5e00-8943-b5841b749525 | note | Eng. Rep / NZTA - A
08b3cadb-835e-54a8-90c3-7afd99c25494 | note | Contractor - R
09827c23-3489-4bc3-b5d6-1bdb2f17bd0a | signoff | AUTHORITY HOLDPOINT
2a7f50bd-1f82-4895-890a-b1528e3c0478 | checkpoint | 4.2 - RAMM pavement and surface records
f33f9c19-240f-5abc-bbf4-b77fb7de93d2 | note | Detail of Activity / Test - RAMM surfacing pavement data spreadsheet updated
a5dbf860-94bc-515e-9f59-aba2c996fa9c | note | Action (Hold, Monitor, Witness) - W
f8bd4043-2c8b-5f66-afd1-4e19b8959d47 | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
be09d245-7d69-5918-9be2-3dfbddd93881 | note | Inspection / Test method - Prepare Data
e3171a31-0cb9-55b7-a471-c591c70b2c13 | note | Acceptance Criteria - Over milled and Deep lift extents recorded and verified by Contract Engineer / QA
9b7a44ac-1cb5-58a9-8f20-13725cd90820 | note | ○ Spray sheets for membrane area received by Contract Engineer from Sealing Team.
91b0e8e5-4f1a-5677-b639-ad0323a6adeb | note | ○ Surfacing layer extents recorded and verified by Contract Engineer.
85f33540-2fee-5aa0-a46d-cfb32c2c388c | note | Record documents (QCP - Quality Control Portal) - RAMM Spreadsheet
60b02b05-caae-5525-83d5-aa7e4c4916c2 | note | Responsibility - Paving Contractor
b7aa1ac2-6581-5575-b461-d1083ec5f023 | note | Designer - I
2ef16315-44f1-5407-aa75-3ec934aa5537 | note | Eng. Rep / NZTA - A
1e674a46-9219-5bc6-942e-de4fe1a224c9 | note | Contractor - R
e9be2642-962a-469a-964b-3d3b4d6af01d | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
d0e00144-55c6-59ba-81af-7c80de01620e | textbox | Contractor's Rep Name:
bffd572c-890c-551a-a6c4-28ce71a2ef80 | textbox | Engineer's Rep. Name:
ba82023e-6db1-5b6d-b038-5a941aa24d4a | date | Date:
14b2f86e-ddeb-4718-8a3f-04dad8190788 | signoff | Add Signature
7ae85e6d-e36b-474b-9708-3aa234363a58 | checklist | DN1210-SP2-003 ITP Northern Access & Carpark Earthworks Rev 2 | itp | DN1210-SP2-003 ITP Northern Access & Carpark Earthworks Rev 2
63a52af8-1190-4aa1-aa8a-3e2aac889874 | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS
c99d133e-a9d8-4077-8b7c-ab05ed2243e9 | checkpoint | 3.1.1 - Earthworks Construction Pack
10167ebf-16d3-5965-a2a7-a9efdb8611e4 | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points on Ineight for review and approval prior to works.
200adc43-adea-5a43-b827-5e6b62b4f172 | note | Acceptance / Conformance Criteria - Engineers Approval
0658ea2d-5070-58b1-b576-b23f140df0db | note | Standard / Specification - Appendix V
7cdb9548-1353-588c-a295-a0c02a5c71eb | note | Verifying Document - Approved Methodology
5aa44755-771d-5682-8997-5495a129dfd9 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
a4c78a33-c13f-5b55-a94a-09b95164990d | note | Verification Activity: Activity - HP
8dcb9355-345c-5dcc-ab62-c4c3a03c3d61 | note | Verification Activity: By - ENG
99b40231-0dff-4397-94bc-a4acf99978c5 | signoff | AUTHORITY HOLDPOINT
d8878d0b-2b26-4ab7-8850-f3be976859fd | checkpoint | 3.1.2 - Ecology Sign Off
913f5562-3c13-5b0c-9628-8014969cb2ea | note | Detail - Confirmation from Ecology that earthworks can proceed
3c301350-739a-5b41-bec1-2c868cc3765d | note | Acceptance / Conformance Criteria - Email
c215de2b-e4a6-5ffc-b565-14a1ae8df301 | note | Standard / Specification - Internal Hold Point
082cd810-4b83-5ffb-917d-2cd1fb764d72 | note | Verifying Document - Email from Ecology NZ
1bdf8d5c-9ae7-5db5-8d82-2bbf2e05a1c5 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
ec630dd6-6b4a-5fdf-b256-32e74bc0739d | note | Verification Activity: Activity - H
077477e0-1e7a-55f1-aa16-cf058c9d80b1 | note | Verification Activity: By - SE
1038659f-f4d5-4d45-9cb8-05e6cd4f28e2 | checkpoint | 3.1.3 - Erosion & Sedimentation Controls
c4ca9a21-81d1-5891-945f-dc303805393c | note | Detail - Confirm that Erosion and Sedimentation Controls are in place prior to earthworks proceeding
be8591e6-572a-5608-ad25-1c1bcb578f58 | note | Acceptance / Conformance Criteria - As-built Completed
83980992-ea22-54da-ab28-6427baef82d1 | note | Standard / Specification - Internal Hold Point
a6ce45af-19db-5de2-9da9-bd6e3859bbbd | note | Verifying Document - ESC As-built
be2b67ed-1f4c-5930-bda8-99c463df4ae7 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
2fad6462-4077-546b-bb09-acf3a329b3f9 | note | Verification Activity: Activity - H
52f429d8-ce41-5f83-9e9c-7572ed5a48da | note | Verification Activity: By - SE
d1caa6b3-2cd9-4f0a-aa38-f485771f9026 | section | SECTION 4 – MATERIAL, PERSONNEL, TESTING & THIRD PARTY APPROVAL
cf78bce4-1633-4c87-a313-89cbe60a7332 | checkpoint | 4.1.1 - Weathering Resistance
3a920aec-b935-5fc6-8bd8-5f41282c49c0 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
627d90c5-613a-552b-ade2-7b442624d8b3 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
f3391f72-c68b-5e01-b381-a9f51ad6081e | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
39c28b24-7d46-53d4-b84a-a4132fa7209c | note | Verifying Document - IANZ Accredited Report
d118443c-ee4f-5756-8aca-aa297378b25e | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
0e4b5027-674d-595b-9da2-ef3394e9a89e | note | Verification Activity: Activity - HP
49b04c1d-aca3-5324-a3c3-cfb09161aaed | note | Verification Activity: By - ENG
0145895a-37e4-4da5-8850-d292cf76dc8e | signoff | AUTHORITY HOLDPOINT
4fd16fda-09de-4762-a4d9-9815568f3d46 | checkpoint | 4.1.2 - Los Angeles Abrasion Test
e22fc0b0-1fe4-5858-bc47-5b3ff217f4a8 | note | Detail - NZS4407:2015, Test 3.12 - The Abrasion Resistance of Aggregate by use of the Los Angeles Machine
50c342e7-22bb-569b-822b-feddde72af4a | note | Acceptance / Conformance Criteria - 0.5
cfbf9a98-62eb-5a4e-9d0a-45bdd783dc5d | note | Standard / Specification - PS 16.5.5, Appendix V
e5cc0792-c4e7-58d3-b3fd-41a55a5c14f5 | note | Verifying Document - IANZ Accredited Report
20729fbb-b14d-51a4-8878-d870e39c4f93 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Required, Results to Engineer 2 wks before importing
f580c960-8790-57da-8a62-f2c3420dd472 | note | Verification Activity: Activity - HP
570710bd-1770-5ff6-872d-8908f0ef1242 | note | Verification Activity: By - ENG
2437aa78-a47c-4a38-8286-76b7e7dce074 | signoff | AUTHORITY HOLDPOINT
33b89a7b-955c-4638-9a39-8c4820593104 | checkpoint | 4.1.3 - Particle Size Distribution
faa1f97f-664c-56bc-94a4-6e9f06a60d13 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
aaaea570-aad9-5c94-8b24-eff6e7e571ff | note | Acceptance / Conformance Criteria - No Particles >200mm, Maximum fines 10% passing 75micron sieve
a929653b-5434-544e-93a4-2b9754dbb0bb | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
7d36b436-36de-5dd8-b926-3166d46e6028 | note | Verifying Document - IANZ Accredited Report
8bbf289f-876c-572d-8b87-50dbc570c688 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
0283661b-6c56-5c5e-9792-3b218459dd81 | note | ○ 0-400 - 2 tests
cf939ca3-0b76-581c-9d20-a8795c9d143b | note | ○ 400-1,500 - 3 tests
9ae37699-97c1-5df8-b4b4-056e497e79c9 | note | ○ 1,500-4,000 - 4 tests
2aed5e33-1540-52d2-8e8a-80f74dac988b | note | ○ >4,000 - 1 test for each additional 1,000m3
d4c771ce-6e90-5721-8a76-391a504ee647 | note | – Results to Engineer 2 wks before importing
8e56868f-f5a4-54f1-9853-e073298224d2 | note | Verification Activity: Activity - HP
259475d6-1cfc-5b02-b135-bc4836cbe2f6 | note | Verification Activity: By - ENG
883b7dd6-99fe-4244-927e-0ce085e8feb6 | signoff | AUTHORITY HOLDPOINT
c34accc8-8fc6-4860-a9c1-faa4c7169acf | checkpoint | 4.1.4 - Maximum Dry Density and Optimum Water Content
d15fbba4-bb1b-5b28-a702-c8bd03fe4171 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
ac5af58a-8bee-5a08-b540-ede06f1557e6 | note | Acceptance / Conformance Criteria - Report Value Only
5edeb382-bf16-562e-b8ab-e9af8d6ab527 | note | Standard / Specification - Appendix XVIII, Appendix V
977abc37-1c4e-506d-a7f4-3f41d5fc0a59 | note | Verifying Document - IANZ Accredited Report
075372c8-4abf-55e7-886a-4e4d3689fa0f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
a8bf1862-dc96-56a8-9211-4ec7715a433c | note | Verification Activity: Activity - HP
af8d7bc5-3165-5994-b7df-db161a39cb20 | note | Verification Activity: By - ENG
104656f9-73d3-4dfd-a1f4-1b0d3b55cf2a | signoff | AUTHORITY HOLDPOINT
84f16312-2375-4212-b3c7-0dcabc83c774 | checkpoint | 4.1.5 - Soaked CBR
3c415a71-daac-5975-9e6e-c73480ebdffe | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
9dfbc3ea-9b61-5fe4-81f7-3c94444858eb | note | Acceptance / Conformance Criteria - >25%
6cea0c44-3ace-59ce-84da-1314d6aee017 | note | Standard / Specification - PS 16.5.5, Appendix V
bf6cfeae-8d62-57ef-8722-c2d031491f52 | note | Verifying Document - IANZ Accredited Report
b4243790-51c3-598a-9cda-441a5e5af11d | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
a42c6419-12a5-507a-b618-49b14ae305d5 | note | Verification Activity: Activity - HP
587e0594-37c3-5e04-9d2c-aaf9282de255 | note | Verification Activity: By - ENG
4eac297b-c7f0-4d88-a3b6-1668845f81ac | signoff | AUTHORITY HOLDPOINT
920a3a52-130e-446a-9b64-457339e355f9 | checkpoint | 4.1.6 - Solid Density
dc9fa64b-1a9e-515e-bca0-1b809ce455d2 | note | Detail - NZS4407:2015, Test 3.7.1 - The Solid Density of Aggregate Particles
78856b6a-cd0e-52fb-b629-39a706b68276 | note | Acceptance / Conformance Criteria - Report Value Only
43f7b384-7963-5002-bd48-638c752db4d5 | note | Standard / Specification - Appendix XVIII, Appendix V
aba97eca-50bf-5de5-82be-86fee321e4c1 | note | Verifying Document - IANZ Accredited Report
594a4307-2a90-555e-b686-0a2959d4f3fb | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
1561d058-0399-5b8c-a919-4a87ac4ef96e | note | Verification Activity: Activity - HP
befe9656-72cb-5f45-8c15-780e4c11d84f | note | Verification Activity: By - ENG
1ef74505-c3b2-452c-97e1-0bab2365544e | signoff | AUTHORITY HOLDPOINT
882c9caf-ed08-44e4-8abe-de8e2d035ff1 | checkpoint | 4.1.7 - Crushing Resistance
8c884f04-30e7-5549-a730-b98b6b752bd1 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
9e43aec0-7f60-5ab6-9907-ecc3f7d45795 | note | Acceptance / Conformance Criteria - >100KN
1643e209-1fff-5b05-93a3-febf9ec2a53e | note | Standard / Specification - Appendix XVIII, Appendix V
d7960ff3-df73-52d3-bfe8-641a9dc9a487 | note | Verifying Document - IANZ Accredited Report
57a8d27b-1f64-5cea-9fa8-c09500b9d1f9 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
d910ed61-95ee-56d3-aedc-289f6efed97b | note | Verification Activity: Activity - HP
e69588bf-90dc-51f3-bfcc-635ece6ad6a5 | note | Verification Activity: By - ENG
64770687-0665-4822-8819-9d9e92ebbd3d | signoff | AUTHORITY HOLDPOINT
1ddda134-484e-4247-810c-cc1119235bf9 | checkpoint | 4.2.1 - Particle Size Distribution
9fc9fc49-fd65-50a4-9ceb-a8a174fe08be | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
ee8ff0d1-0700-5d3f-8f63-2c46c1c8d16b | note | Acceptance / Conformance Criteria - Report Value Only
504358a7-a60e-52b2-a706-c0ef575f3259 | note | Standard / Specification - PS 16.5.12
408c47c2-e85d-51e6-bda4-cd9aa94e6db3 | note | Verifying Document - IANZ Accredited Report
754ede11-d472-5541-bb71-5fb036f3bb97 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required?
971d1fbd-8e5c-534f-a32e-9d3b86d4d66e | note | Stockpile size:
f2436c38-9fb7-5574-8320-7b3c4053c0e8 | note | ○ 0 to 400m3 – 2 tests
7c9d7a85-7f91-5889-b0a2-516b73940b45 | note | ○ 400 to 1500m3 – 3 tests
fff24328-ddf9-598c-bdc0-c8624cf47269 | note | ○ 1500 to 4000m3 – 4 tests
238ddab0-6a0b-5cc6-938c-754eaa1cd482 | note | ○ >4000m3 – 1 test for each additional 1,000m3
d5a186fe-6df0-5a60-9ad3-11656d0b8ad6 | note | – Results to Engineer 2wks before importing
872f81fc-22a0-5053-8a6a-f7cc28cfa732 | note | Verification Activity: Activity - HP
c4b82f3a-84fd-5050-946b-2737c424ad3c | note | Verification Activity: By - ENG
ab4b0173-461d-47d4-a957-46202cd78726 | signoff | AUTHORITY HOLDPOINT
43cc80bc-ece2-449a-a479-3ec1ee22cf5f | checkpoint | 4.2.2 - Maximum Dry Density and Optimum Water Content
21481602-b958-51b7-b1e6-f09d9db142f4 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
6bbca740-a859-521b-9816-faa9d4656ad4 | note | Acceptance / Conformance Criteria - Report Value Only
fd93416f-22ed-50fd-b07c-9e2e431491c1 | note | Standard / Specification - PS 16.5.12
ef7d2497-3a0e-5368-9991-bb51ae96b815 | note | Verifying Document - IANZ Accredited Report
0879c2df-d090-566a-a994-8adf3f57b775 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
53caa342-4777-54cf-bd25-d2543d38d462 | note | Verification Activity: Activity - HP
9d2dc668-53da-55b6-9ba8-d87bf4acb6f1 | note | Verification Activity: By - ENG
e7cc0a21-52ed-4ca0-9c2d-00452bf0e59c | signoff | AUTHORITY HOLDPOINT
2ea9ad43-096d-4006-8088-157471bfdd56 | checkpoint | 4.3.1 - Crushing Resistance
74bcea60-b38d-534b-b9b1-4cd481b19751 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
bcaadb54-e756-598d-b848-fd18a815e53c | note | Acceptance / Conformance Criteria - >100KN
051bad98-0e58-56a8-9976-22cbd0afe837 | note | Standard / Specification - Appendix XVIII
416e8571-ce24-55be-9672-10667c8b993d | note | Verifying Document - IANZ Accredited Report
f1c8e9d8-a4d6-531f-985f-c2d1c5a1afb6 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
3ece5057-1a32-5c4e-b2cd-211ecb421171 | note | Verification Activity: Activity - HP
dc9563ad-9efe-5be4-aae4-f4233dde90bf | note | Verification Activity: By - ENG
91b0bdcd-ca84-4eb6-8543-0abdcedeeef4 | signoff | AUTHORITY HOLDPOINT
6501b0f3-6305-451e-833d-e2c704fa3e16 | checkpoint | 4.3.2 - Particle Size Distribution
a0c4eac5-8d73-5191-8d92-ecdc11fd6abc | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
be3a2de6-8804-50a9-976c-306a61943087 | note | Acceptance / Conformance Criteria - Max Particle Size 53mm
5e50098f-5357-5711-bd05-c175b7d20344 | note | ○ Max 10% passing 13.2mm sieve
f57b3101-33ac-5b87-9d97-f5ef90832701 | note | Standard / Specification - Appendix XVIII
d77b25c3-26a7-539c-9b74-e5e99d4e892d | note | Verifying Document - IANZ Accredited Report
8493d7ca-321b-5a00-a624-603e80481e67 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3, Results to Engineer 2wks before importing
f47399f0-6185-5a5a-b510-87549ef986c5 | note | Verification Activity: Activity - HP
39f36664-0921-53e8-b3b5-cb2dcbd4dbaa | note | Verification Activity: By - ENG
f4b31f1d-c419-4a7b-ab46-cfdbbcd01bab | signoff | AUTHORITY HOLDPOINT
18d98917-5913-4e05-ae6d-6e3ddcfd731e | checkpoint | 4.3.3 - Weathering Resistance
b6bd5b3a-31d9-56cc-bc07-b82824279d4c | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
3a25ff9a-0f2b-5d41-836c-9b277c52cd5c | note | Acceptance / Conformance Criteria - CA or better
bec8936b-0cf3-57e9-8375-89779aa4ca3f | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
b3df6dd6-59d2-5588-b69c-0ee1a0b8da76 | note | Verifying Document - IANZ Accredited Report
e544816c-5b44-521a-97ed-4b02e63f729c | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
c65a06a2-b3fd-511c-8f40-1c1215c307ed | note | Verification Activity: Activity - HP
b320dc08-a1b0-5f70-a477-236d2d6c3a8b | note | Verification Activity: By - ENG
2b883239-2884-4602-a1e0-48020171cbc7 | signoff | AUTHORITY HOLDPOINT
d79df45f-9160-4f0a-a1be-1ae1f2906bc0 | checkpoint | 4.4.1 - Geotextile
28283dee-4865-551f-a430-691a0144acb4 | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation.
e8d090a2-f35a-5e74-b8fb-cead6aa100ce | note | Acceptance / Conformance Criteria - Engineers Approval
786ca4e1-67da-584d-8bac-04368df96589 | note | Standard / Specification - PS 16.5.7, Appendix V
7d0e5257-179b-5774-b372-1fdd03c14d01 | note | Verifying Document - Delivery Docket/Material certificate
4f96f9e0-1281-5701-a0ec-7aa48b55b52b | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
aae3c485-94e4-5688-8f44-32a7e9380398 | note | Verification Activity: Activity - HP
7959b4c9-e3c1-5002-b5a0-498ee47290b8 | note | Verification Activity: By - ENG
bb082231-2fb1-41ac-997c-2b319b671b9c | signoff | AUTHORITY HOLDPOINT
ff5c68c7-efe3-4689-a40c-0abf9d43c3b9 | checkpoint | 4.4.2 - Geogrid
aa440346-d8aa-52f2-ae5d-9c32c8176590 | note | Detail - All uniaxial, biaxial and triaxial geogrid shall be manufactured in accordance with a management system that complies with BS EN ISO 9001 and BS 14001 and shall submit to the Engineer for approval.
f157f831-aff3-5b3c-81dd-e591d74e730f | note | Acceptance / Conformance Criteria - Engineers Approval
54297783-3595-5f7e-b03b-f7063d2340e8 | note | Standard / Specification - PS 16.6.5, BS EN ISO 9001:2000, Appendix V
74201647-bc89-5064-96d7-dc3f531333f5 | note | Verifying Document - Delivery Docket/Material certificate
ce76eafa-eb0b-5e90-979e-8be7e17d58b3 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
faef31c0-88eb-5cd3-97e3-28c7c24fac3e | note | Verification Activity: Activity - HP
19ed23e7-3836-511f-9788-52ea5598bb77 | note | Verification Activity: By - ENG
8c8c90b3-36fe-4353-93b4-b03191ca5b2a | signoff | AUTHORITY HOLDPOINT
cff04487-cf30-4917-af0e-0d37456176b1 | checkpoint | 4.5.1 - Laboratory Testing for Soil Suitability
11d2c865-cb90-5ea6-8aab-4b314e348841 | note | Detail - Soil Test Results from Hill Laboratories to confirm that topsoil suitable to for reuse Soil Reaction
a58df18d-48e2-5a2d-b065-774c85d88442 | note | ○ Electrical Conductivity
d94e7b64-5b58-582c-b37b-39f9e428437a | note | ○ Mechanical Analysis (texture)
5a1ec5ad-e143-51cc-b26e-2514a84b2555 | note | ○ Stone Content
bd32f399-9eb6-5802-9457-e19381c7ce8a | note | ○ Nutrient Levels of nitrogen, available phosphorus, available potassium and available magnesium
f57884db-8128-5ebb-b0a6-10fad5247479 | note | ○ Organic Matter Content
81eb07e9-17d9-50e4-a40c-e19005edaf7f | note | ○ Check for Toxic or Hazardous substances
768cc8f0-ed50-5d8a-a8cb-caf006ff1203 | note | Acceptance / Conformance Criteria - Engineers Approval
64c33bf3-a63f-5229-a9b3-f4588d846ce1 | note | Standard / Specification - NZTA P39:2013 3.1
ebe8106c-b706-57ac-bc2e-9502b2a10c0f | note | Verifying Document - Hill Laboratories Test Report
9f220b6b-699e-5885-bf8e-045064a6e63d | note | Testing Quantity Required (based from schedule qtys) - 10 equal samples taken from site, mixed together, then 1kg of soil sealed into a plastic bag and sent to lab for sampling
af757549-701f-5ec5-a456-bc30ebc3218c | note | Verification Activity: Activity - I
67708aaa-3e79-5031-9765-2505462e11a7 | note | Verification Activity: By - SE
8d2f7f28-9383-45d1-9f1f-677283936a57 | checkpoint | 4.6.1 - Crushing Resistance
7127ac6d-1699-5657-a806-6e38ad36e445 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
24c8e50b-948e-5cda-b092-5085d93bd653 | note | Acceptance / Conformance Criteria - >100KN
2fe45093-e78b-5f0a-9e96-a7f2e1d535fd | note | Standard / Specification - PS 16.5.15
db647343-6a32-50d8-97ad-b1089b670f39 | note | Verifying Document - IANZ Accredited Report
46b98987-6231-5143-810b-b004ae4e5feb | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
89a77fa7-c55c-5f83-964f-7b3d040eef2f | note | Verification Activity: Activity - HP
394ff6ac-5235-5006-8e46-cdd9b0b67a27 | note | Verification Activity: By - ENG
0a7472d2-7c0b-4dd4-86e7-886605947e29 | signoff | AUTHORITY HOLDPOINT
25ceaf3e-a8d9-44fd-8fae-a8428feaa7d1 | checkpoint | 4.6.2 - Particle Size Distribution
50798836-e42d-5cba-ac5a-2988bce9fb41 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
f89e8adc-3caa-5502-96a2-101286521281 | note | Acceptance / Conformance Criteria - Max Particle Size 130mm, Max 5% passing 19mm sieve
ac62921d-59dd-5d5a-b065-c0d2e5f14baa | note | Grading:
c6ad294a-e4ac-5152-b9e3-99adc546ee05 | note | Sieve Size ¦¦ % Passing
2ece2c6a-d34c-5168-b51e-00ac91207e9b | note | 130mm ¦¦ 100
a7b74c18-be2f-5192-9e1c-408f2e98fbd3 | note | 100mm ¦¦ 70-80
b806526a-4b19-58ed-a0e6-1f4ff51bffe4 | note | 63mm ¦¦ 40-50
8fd6533d-e7af-5ad8-bad4-033e6502359d | note | 37.5mm ¦¦ 20-25
06fa4641-87ae-5f5f-a7f1-ad8e7610d8aa | note | 19mm ¦¦ 0-5
ef91176a-8e03-5385-aec6-83f168b95c84 | note | Standard / Specification - PS16.5.15
097d27fc-3e2a-5413-8d77-e20f65e74381 | note | Verifying Document - IANZ Accredited Report
ba5af504-3836-5f5e-88d0-eeeeb2672e5d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
cac7277c-5672-5681-8032-fdb2d169a4f9 | note | Verification Activity: Activity - HP
ba90e3ba-c441-5f93-ae91-28d1aefdd5bd | note | Verification Activity: By - ENG
5244dfca-6304-4859-8657-cf713071285b | signoff | AUTHORITY HOLDPOINT
be483645-c21f-4675-b4e6-62b8696f1903 | section | SECTION 5 – CUT SUBGRADE TESTING
dfc0978b-38b8-4b8d-81d1-44e40f83afca | checkpoint | 5.1.1 - Proof Roll
098a4dfc-dfb0-5a2c-8ec4-ad9db56d9f66 | note | Detail - Visual Inspection of Proof Roll
d08e3ab3-5d57-5f3d-8246-8eeccd5ec8a7 | note | Acceptance / Conformance Criteria - Displacement <15mm
d136410d-c24c-58de-ace6-5363edcb13e9 | note | Standard / Specification - Appendix XVIII
5d797d84-3e15-54af-bc88-20a78fbc1d21 | note | Verifying Document - Visual Observation
0b78dac1-fb93-5477-9295-79682b2adc77 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
ffc402ce-0c33-5438-a154-610b3dc23646 | note | Verification Activity: Activity - HP
497b7d19-aa07-5e67-bbba-77bad0f89c45 | note | Verification Activity: By - ENG
89ac51aa-9619-4d63-bde0-f03f672a4173 | signoff | AUTHORITY HOLDPOINT
b51917db-1f28-470a-9806-d857f775ba73 | checkpoint | 5.1.2 - Cut Subgrade Inspection
51bb84cb-b6e8-5a69-95e5-626ab7e46970 | note | Detail - Engineer to inspect all foundation surface inspections
d79755e6-34af-5e2b-8d1e-93ba2ca86e10 | note | Acceptance / Conformance Criteria - Engineers Approval
ebaa6c50-d055-5444-b433-ea6c9bc37de7 | note | Standard / Specification - Appendix V
791e8dc0-2308-5ea4-84c0-08a1fa129e5e | note | Verifying Document - Visual Observation
b10d2496-eb16-5d58-8761-afb4f804a97c | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
e739f339-3f77-5620-bc1d-151267ce68c8 | note | Verification Activity: Activity - HP
0ffc3abf-f81b-5aae-9387-983c2772393a | note | Verification Activity: By - ENG
fe71315d-d86c-4ac2-8d13-90a2a270ed75 | signoff | AUTHORITY HOLDPOINT
f568b83a-74a1-43ba-b0f6-1fe2131c604e | checkpoint | 5.2.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
d1bdfe48-979b-5de1-9ff1-3a84a7e9f657 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
9e2ad0be-5bd3-5940-84cc-4d36d58abef0 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
2ef57dfb-4d5d-56b0-9b37-45b2be16f941 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
eb3c9ee2-7ba1-52dd-b0ec-bfce8092b595 | note | ○ Single Test Min SU: >50kPa, 2-3m deep
e3a57475-597c-5c47-ac56-f484936f8739 | note | Standard / Specification - Appendix XVIII
9bece1b8-e49b-5d52-844c-582d31917804 | note | Verifying Document - Shear Vane Report
e3952059-d267-59f4-a947-ff1ae1904035 | note | Testing Quantity Required (based from schedule qtys) - 0.5m interval, 4 test per 400M2
ab7e2dec-9301-5f14-895f-0b9107098bb6 | note | Verification Activity: Activity - I
eb223c11-ede7-5c2f-96d5-c9140d94dd9a | note | Verification Activity: By - SE
8b04bba0-3e53-4c7a-a6ce-8e6b89b7ede8 | checkpoint | 5.2.2 - Cut Subgrade Testing - Cohesive Soil Scala Penetrometer
0acf793e-d137-570c-9925-f4026b1e4930 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
efbd34b5-d40f-56b2-a973-96f4000ebf5a | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
d361eed9-c00a-50fa-976e-d1e8d1ec793c | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
89476ac3-6e9e-5a24-bbec-bd97a011393f | note | Standard / Specification - Appendix XVIII
9c1be8ba-1563-5d74-917d-b5e07ce6cb43 | note | Verifying Document - Scala Report
28b14fde-5db8-5d0f-9ade-614649931d75 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
e4ae1aa2-af42-51ff-9c1f-1e965de3a3b9 | note | Verification Activity: Activity - I
61c1477a-0d84-56f9-a0f7-5f93faf95339 | note | Verification Activity: By - SE
dbf6344d-29bd-4591-8fa4-d0420808f0ed | checkpoint | 5.3.1 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
b8446bc3-e5ef-5ae7-8d1c-8e6c62a77849 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
c5af1f06-7744-554a-bcc0-305fcf3b6fcc | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
40aaeb85-2db9-59ea-bc62-0eb01c3f5294 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration, 2m deep
57c24a30-6044-5bdd-96e9-8811abdbbcd3 | note | Standard / Specification - Appendix XVIII, PS - 16.6.5
ca971eb5-06c9-57b2-a591-bc6d9f953eb0 | note | Verifying Document - Scala Report
3ff8e003-8f9e-5f9d-8ad5-37ce3eb92753 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
6a4b7cc2-dd21-547a-9e0a-0f2eb6170540 | note | Verification Activity: Activity - I
00fc9fdb-4279-54e7-aff0-7928e3bd3dc3 | note | Verification Activity: By - SE
35c58996-e979-4edd-ab81-95cf3292a042 | checkpoint | 5.4.1 - Release of Hold Point
ae80a22f-bb21-5913-808d-eb2b3c8bb618 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
f0454278-57b3-57b8-99e7-c5fe6815bf1d | note | Acceptance / Conformance Criteria - Engineers Approval
07df8add-1601-5ef6-a8d3-3e5b35efa1d4 | note | Standard / Specification - PS 16.9.3
a10fd2c9-cce7-5992-b11f-86216c277950 | note | Verifying Document - CONQA Approval
0888c961-40ae-5682-ba6a-a1b791ec9e0f | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
8d437422-039f-5b46-a41f-bc524882f7e2 | note | Verification Activity: Activity - HP
9140f5a1-dfc8-55f1-8ab7-93bf60b9194f | note | Verification Activity: By - ENG
08a66dd7-101a-4de4-804e-2d1241183392 | signoff | AUTHORITY HOLDPOINT
84b73365-bef8-46ab-b379-0e77985630cb | checkpoint | 5.5.1 - Subgrade Level Confirmation
978866de-77f6-5342-823e-f636fe33fc19 | note | Detail - Confirm subgrade is 735mm from finished height
8a22d0d9-2c5e-5265-bf43-1953dcf354c1 | note | Acceptance / Conformance Criteria - String lines - or equivalent are 735mm +0mm/-30mm
b2872315-e3e0-52c8-a93c-8045c42622c0 | note | Standard / Specification - PS 20.14.5
4f173124-a627-5ac7-bef5-408cd8953a98 | note | Verifying Document - Survey as-builts
e17bb15e-0e57-56f5-be02-9172dbc289ec | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage
237ed36d-3b50-5a5f-bbb9-540dbe738241 | note | Verification Activity: Activity - I
7dbced6f-5bcc-5e48-ac45-7ec869714a02 | note | Verification Activity: By - SE
6efa6117-2285-4e55-9090-577bdf42996b | checkpoint | 5.5.2 - Subgrade CBR Testing
7e0b6f12-df06-5a43-b1b4-fbfb4c1e3548 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
84d5b86a-4d52-51b8-88e0-720b103ff87f | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
cb3e2e99-7599-5da0-a276-d4f07e6dc83f | note | Acceptance / Conformance Criteria - Pavement Type 1
5b72eb2d-08fb-5a92-8114-8a2e7d8f7cb4 | note | ○ CBR >6
5a517362-2140-500a-a281-7375a68e64f9 | note | ○ Min 3 blows / 100mm
3db91f7d-6715-5c6e-ba40-b8193970f36a | note | – Pavement Type 2, 6, 7
6fde8757-b4d9-5d5d-8352-0d957d8e4d8a | note | ○ CBR >2.5
9801f996-a34b-5ce4-a61d-5be1a0d3d1db | note | ○ Min 2 blows / 100mm
41238e87-7765-591d-9585-aa1ca0080c40 | note | – Pavement Type 3, 4, 5, 8
2cbc3cbf-97b8-5269-a8f2-4169cfdac5a9 | note | ○ CBR >3
2bc56818-f4c2-595f-bcd3-2aecf29d09a9 | note | ○ Min 2 blows / 100mm
9e07dfdb-c580-5ad5-8776-21223f830f3f | note | Standard / Specification - PS 20.4.1
4265bbf5-dc54-58cd-a99f-46ed1fc9ab16 | note | Verifying Document - Scala Report
caf15e9d-4393-54f7-b32d-e5cc60ffcf09 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100M2
1d0e3c60-79f8-5539-9489-3f7ad1db14f4 | note | Verification Activity: Activity - I
2b1a036d-1b4e-53c0-94cc-65b87411f4a3 | note | Verification Activity: By - SE
914c6b79-0ff0-4745-b2d9-1c3edc76d5af | checkpoint | 5.5.3 - Release of Hold Point
66fad841-4980-55e6-a7e4-30a79e0cb2a1 | note | Detail - To release the subgrade hold point and be able to start placing pavement layers, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
111e6026-9a21-5c35-8fae-082cfd42a485 | note | Acceptance / Conformance Criteria - Engineers Approval
705e553b-66c8-56bb-89f1-5507a9686269 | note | Standard / Specification - PS 16.9.3
2b62974a-60e7-5a0e-b744-aaddd091076d | note | Verifying Document - CONQA Approval
72bcf30e-1a4f-5b63-a5ca-21bb3c66df1f | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
e44537c4-93a7-5159-9110-a0502f5e6e5b | note | Verification Activity: Activity - HP
492dd4d6-8c56-5755-9aae-2b8dcc41bb04 | note | Verification Activity: By - ENG
65d37d78-1c8e-400b-81ef-ea4e1062c492 | signoff | AUTHORITY HOLDPOINT
8117beef-b5fd-4fb2-8198-6009aa3fa232 | section | SECTION 6 – CUT SLOPE INSPECTIONS
c414198a-45f6-49bd-94cd-b22c6710e237 | checkpoint | 6.1.1 - Cut Side Slope Inspection
023cc0a1-3b0c-5773-bcf5-90033e4e93ac | note | Detail - Inspection records to include photographs, logged soils (to NZ Geotechnical Guidelines) and shear vane testing
c878c9fc-3ce4-5272-8b0e-5d24c6ebf88a | note | Acceptance / Conformance Criteria - Engineers Approval
1f32848a-b8b7-5bf9-9cc9-5ce588adf0f5 | note | Standard / Specification - PS 16.6.4
bf760bd5-ea12-56c1-88e5-233d940b0a25 | note | Verifying Document - Site Records
e706dd8c-74b9-528e-86c6-8a3604c3734f | note | Testing Quantity Required (based from schedule qtys) - As per Engineer
d77c3907-969d-5f0a-9089-1439ce1373b8 | note | Verification Activity: Activity - W
c5b7aa59-06be-51e8-87d0-0966e3444976 | note | Verification Activity: By - ENG
cde568f3-5661-4e69-b3b2-5697e1054ed7 | checkpoint | 6.1.2 - Cut Slope - Soil Log
27870974-295c-5425-94b3-1e9f3c4578d1 | note | Detail - Soils to be logged to NZ Geotechnical Guidelines
939bf334-b6de-5aba-a943-ac2857810fd5 | note | Acceptance / Conformance Criteria -
b66e0e22-abc0-5f22-811d-560908c79b9c | note | Standard / Specification - PS 16.6.4
199098c1-f77b-501b-9b27-b666aed7a876 | note | Verifying Document - Soil Log
18f8a3cd-3cd6-5fd9-b232-34b1261c334d | note | Testing Quantity Required (based from schedule qtys) -
412d41e7-d6b6-57e0-baad-9d9ed27ae4e4 | note | Verification Activity: Activity - I
c8f9430d-3bc2-523b-951a-f31dbcb0e896 | note | Verification Activity: By - SE
ed167d0e-9ff7-411b-9248-10134dbf89a7 | checkpoint | 6.1.3 - Cut Slope - Shear Vane Test
33c23fc1-7919-507d-9d3a-64e60770f4e4 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
60b7245d-6b54-5b28-992c-55dc80367291 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
95b22c56-8cff-5776-a05e-e25af27e646d | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
4a2e678a-9ccf-56e7-a030-404b0935b5da | note | ○ Single Test Min SU: >50kPa
8f3177b2-94d4-5007-99d0-e56e2b73c7ca | note | Standard / Specification - PS 16.6.4
5926a7d4-5d92-5d2b-b9b3-c57b34a666ff | note | Verifying Document - Shear Vane Report
9d8d8541-aabc-521e-8eaa-c5e2f1dd6e72 | note | Testing Quantity Required (based from schedule qtys) -
485a8a00-fb49-5fa2-a596-34315ed34954 | note | Verification Activity: Activity - I
b782b88e-0f32-5920-a9ce-fba1ddcf3ad7 | note | Verification Activity: By - SE
6a091508-c937-4d61-987b-c573fa12ab2a | checkpoint | 6.1.4 - Drainage Measures if Seepage Encountered
8e495619-13ca-5471-8aea-e65ac29b08af | note | Detail - Borehole Drains or ballasting may be required, to be directed by Engineer
bdc330da-377a-5006-ade2-cad242dc30f9 | note | Acceptance / Conformance Criteria - Engineers Approval
7af9ad0a-e2cc-5781-bf17-ccecd0231a94 | note | Standard / Specification - PS 16.6.4
1cc6b52f-8473-56c2-9fb1-fbeca9963383 | note | Verifying Document - Engineer approval
f7f18a75-5005-5d13-837c-2d6ff84f15ab | note | Testing Quantity Required (based from schedule qtys) - As per Engineer
e1b9f004-2d9f-5b58-a4ca-ce0a1c933e05 | note | Verification Activity: Activity - I
ae95c875-6383-556e-9761-5937be172749 | note | Verification Activity: By - ENG
86433569-6812-4fdb-ad45-2c7c43b6f31d | checkpoint | 6.1.5 - Design and Grade Check
8a966e6d-9dc1-5a7d-8c1c-9ba75da3373c | note | Detail - Confirm cut slopes have been correctly excavated to design and grade
44227bbf-1a2b-5c38-a3b5-4eaf0d88768a | note | Acceptance / Conformance Criteria -
1f58862d-9c02-57e2-a51b-aded16165714 | note | Standard / Specification - PS 16.7.1
f5e54251-aa95-5f00-aa2d-6094deb42a3b | note | Verifying Document - Survey Records
2003e1ee-aacc-53db-b029-3fc43a786722 | note | Testing Quantity Required (based from schedule qtys) -
a44e031c-385a-5c34-a5f2-5120eb53211d | note | Verification Activity: Activity - D
80d39d8f-4d94-58ab-b4ca-034de57fdba8 | note | Verification Activity: By - SV
4f51f1df-4238-4069-a0c0-73ce67212fea | checkpoint | 6.1.6 - Stabilisation of Cut Slope Surface
3066f967-fd59-5182-a02f-dfdee1c59a33 | note | Detail - Cut slope surfaces to be topsoiled and grass seeded or planted as soon as possible
3ec0573f-ec3c-5e34-b9c0-d25ed2421dc7 | note | Acceptance / Conformance Criteria -
be41bfc5-3cc9-5d2f-bb32-af47a5695fba | note | Standard / Specification - PS 16.6.4
826e8dab-e9c0-5729-ade5-1df922b33f6b | note | Verifying Document - Site Records
7256d485-d934-51c8-80f5-42992b56d72e | note | Testing Quantity Required (based from schedule qtys) -
05ec052b-80d3-51ac-8f29-a26119629df2 | note | Verification Activity: Activity - C
1ad7b84e-6f78-578c-b4b3-1cc724c3cfb4 | note | Verification Activity: By - SE
fb81c9be-f31b-432c-8b2b-81bf42c9ea3b | checkpoint | 6.2.1 - Release of Hold Point
bda6d2a7-7005-53e3-ab65-25237f8d05a7 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
a5ab3bf3-f328-5c77-863f-0e789d098000 | note | Acceptance / Conformance Criteria - Engineers Approval
914afdce-e4c9-5221-91a9-be0a3ca2684d | note | Standard / Specification - PS 16.9.3
59ce497a-dafa-598d-abfe-5e42b0a2ddd9 | note | Verifying Document - CONQA Approval
da195f72-c14d-58c0-9445-5e2c9864e65b | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
559fd59f-c709-5190-ad72-55a7ecb5b61b | note | Verification Activity: Activity - HP
56ed7567-e0b1-566f-aa82-f37a4a15a5eb | note | Verification Activity: By - ENG
3fcaf40a-91bf-4d8f-a9a7-b2f41cb0c4ee | signoff | AUTHORITY HOLDPOINT
8ea0e304-a00d-43c6-8739-d448383c1db0 | section | SECTION 7 – UNDERCUT TO WASTE & BACKFILL
0781a768-0a32-4344-8e4e-20c171df31e1 | checkpoint | 7.1.1 - Undercut Surface Inspection
a29bab05-38fb-5558-af6a-320ec1d90314 | note | Detail - Engineer to inspect undercut surface
31ec49b8-ff03-5920-9239-0e445d371c3d | note | Acceptance / Conformance Criteria - Engineers Approval
5bbcaeba-fa6f-51ca-9abc-027243b05d91 | note | Standard / Specification - Appendix V
01f13bac-9a3d-5b4e-baec-255c566e54f4 | note | Verifying Document - Engineers Approval
f4c2bcd0-0b9f-5974-9ad7-185755be0c28 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
5ba65619-c883-5591-96d0-48e121cefa4f | note | Verification Activity: Activity - W
b329a92e-8214-5377-8fd9-c08226f5829a | note | Verification Activity: By - ENG
23e7b460-cfb3-4485-ad1a-0a68d0d5b989 | checkpoint | 7.1.2 - Placement of Geotextile on Undercut
fd838f5b-ced6-52c6-b28e-645755a28c92 | note | Detail - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
d23ba909-7c66-5a8e-ad1e-9be452db6058 | note | Acceptance / Conformance Criteria - Engineers Approval
8800b7a7-68d2-5e71-bd48-d23fde36dcdf | note | Standard / Specification - PS 16.6.4, TNZ F/7: 2003 8.3
8c75fcad-8bc6-5cb7-a3b4-c321045191cb | note | Verifying Document -
3c9c5b77-635e-59fe-9289-2c82645ec2cb | note | Testing Quantity Required (based from schedule qtys) -
38cb6bb1-2f25-56de-82f4-df646133cdd4 | note | Verification Activity: Activity - W
2656f423-4985-5fc1-9a38-93b111921f1e | note | Verification Activity: By - ENG
16dd6fb6-dfda-408a-9922-3e1b9fbdfcac | checkpoint | 7.1.3 - Subsoil Drain inspection
806c2bc9-4497-5c04-9ef8-d1c46328db37 | note | Detail - Subsoils to be placed at base of cuts where directed by the Engineer
101697f6-9e6f-515d-b23b-6d1bc0c4105b | note | Acceptance / Conformance Criteria - Engineers Approval
d47f5355-1c23-52f1-b54f-5abae6f1f70d | note | Standard / Specification - PS 16.6.4
28a21e02-b605-5d32-bc48-1e8f3ec93013 | note | Verifying Document -
6cf509b3-9276-5bd1-acc4-611b323e79b8 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
0986ac29-45f8-58b6-9098-35917f9e9ba6 | note | Verification Activity: Activity - W
5d6095bb-f45a-5d54-bad7-7f72c1b46cee | note | Verification Activity: By - ENG
ab30b7bd-91f4-4d6a-80fa-f096d21b2fed | checkpoint | 7.2.1 - Release of Hold Point
37a22d96-95db-5957-8792-2bb00c74ef9c | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
01a90689-ca23-5e5f-9844-496754f6af8f | note | Acceptance / Conformance Criteria - Engineers Approval
d9fe0936-444d-56ca-82ed-6c81a0c2fddc | note | Standard / Specification - PS 16.9.3
3ab7afd8-28ce-5784-bec9-96f70c27a185 | note | Verifying Document - CONQA Approval
917560fa-3f1d-5b37-8d02-dba9751bad27 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
e08b9c95-b2d9-5e8c-b580-7190856fbb2a | note | Verification Activity: Activity - HP
63fa45f9-6267-5731-83c4-e346e2689f6f | note | Verification Activity: By - ENG
194c22bd-619b-45e4-a92a-52e5707fc0d3 | signoff | AUTHORITY HOLDPOINT
ce8741bd-d7a3-4497-b02f-5e353e91fdec | section | SECTION 8 – COMPACTION OF IMPORTED FILL
28314c46-79c9-459a-8246-5826afaf703b | checkpoint | 8.1.1 - Placement of Geotextile
f572abba-0bf1-5184-8f3c-ec292bc02c5a | note | Detail - A layer of Class B Geotextile Fabric to be placed between cut surface and imported A1 Structural Fill with 500mm overlaps
dd350f9e-1e85-5afe-8b76-35f68c0aa1fd | note | Acceptance / Conformance Criteria - Visual Inspection
532419ca-3317-5872-b054-de36a2c504bf | note | Standard / Specification - NTC084
76aa943f-4bfc-574b-b681-9f9037f9a2d0 | note | Verifying Document - Visual Observation
70992602-9c24-5c69-83d1-bb86c2a7acc7 | note | Testing Quantity Required (based from schedule qtys) - As Required
53bf64e8-36df-5932-8a42-585016361800 | note | Verification Activity: Activity - I
7e60f3df-0351-5b13-872a-0888d788253c | note | Verification Activity: By - SE
0563f76a-bf92-4fdd-a6c3-32429085a8cc | checkpoint | 8.2.1 - Compaction - Clegg Hammer
964a5260-a265-5db2-b07b-5935f95e33c1 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
3b781eaf-7c37-5d2f-a76d-6853b5a22201 | note | Acceptance / Conformance Criteria - Structural Fill: Min CIV 18, Ave CIV 20
089305e5-5cce-57f1-b13f-add1522a51d5 | note | ○ Non-Structural Fill: Min CIV 10, Max CIV 12
d7025ec6-0ca3-54b2-805e-19701f9db974 | note | Standard / Specification - Appendix XVIII
e406e0ea-13e6-5acb-96b7-ad46018bf8ef | note | Verifying Document - Clegg Hammer Report
a9846bae-f7cc-50ac-84f0-2d125ab61b20 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
fba95479-95a0-5506-af9b-fd4e5b43eed3 | note | Verification Activity: Activity - I
9c506d3d-94c0-5769-8b8b-0e85bcf87640 | note | Verification Activity: By - SE
d85da4d3-cc2e-4bf2-bcb5-a8a388b0df3f | checkpoint | 8.2.2 - Compaction - NDM
0ecfc4fa-96bb-5cc7-80fa-3ac7ca394bb9 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
7bfe2a6f-c917-59ca-9244-7a547cd11d39 | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
e4d59f85-ba3a-5845-af20-553e9aa70653 | note | ○ Non Granular Material: Max Air Voids 8%
0dea1e1d-773b-584a-818b-634b7d024e69 | note | Standard / Specification - Appendix XVIII
eace9fa6-2137-51cd-8e22-aff30120f6aa | note | Verifying Document - IANZ Accredited Report
c1081b72-650c-54ae-abd7-e14a3addcff0 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
759cfe41-9c2f-5d6e-87e1-22e49b6c9e2b | note | Verification Activity: Activity - I
c7f20b94-4b29-5d58-8874-df31453b7b98 | note | Verification Activity: By - SE
71a294cb-c8ed-4981-8a3a-600d0c351ec0 | checkpoint | 8.2.3 - Compaction Trials
e2ff21cd-6177-596d-8472-9da03051c4c1 | note | Detail - The Contractor shall carry out compaction trials of the various soil types and combinations on site, and any imported fill materials, using different layer thicknesses, types of rollers and conditioning plant (ie construction discs and scarifiers). The trials shall be conducted over the duration of the earthworks operation with the objective of determining the most suitable and efficient techniques to meet the compaction requirements. The trial details, test data and conclusions shall be reported and copied to the Engineer within five days of completion of each trial.
2dbd85d6-5e84-55a3-8bb8-9861623f39e5 | note | Acceptance / Conformance Criteria - Engineers Approval
549db573-c8bb-5d4c-83d5-83a09597dddb | note | Standard / Specification - PS 16.6.5
bb764a26-c943-5f74-a858-36c596278bf3 | note | Verifying Document - Trial Results
3fcb3cdf-7687-57d4-8b14-bc6646de5626 | note | Testing Quantity Required (based from schedule qtys) -
9cd21e41-3310-5562-b124-22d0cddc035b | note | Verification Activity: Activity - R
445d8a25-6b11-5b5a-a2b3-2b9905e44f32 | note | Verification Activity: By - ENG
da386258-58d2-4b0c-8c0b-9b672d953b10 | checkpoint | 8.3.1 - Compaction - Structural Fill Scala Penetrometer
f1624108-4588-5aec-ad30-a69b3bbf61b1 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
5b0905fd-fd35-598d-8f68-37e402e98936 | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
efaa4208-2fed-5e97-b627-89f6588ff9c4 | note | Acceptance / Conformance Criteria - Minimum 5 blows per 100mm penetration
c694dd7b-e74c-50da-b871-b2e7f1f99311 | note | Standard / Specification - PS 16.5.12
abb91d08-aaaa-5819-a29c-8f7d61c8ab86 | note | Verifying Document - Scala Report
4776851e-1e4c-584d-a0ed-cee58cdeb60c | note | Testing Quantity Required (based from schedule qtys) - Minimum 1 test per 500m3 of filling evenly distributed over the extent and depth of the filling. A minimum of 1 test per 500mm lift or part thereof to be completed through the full lift thickness.
a5bdcbee-0715-5dd2-bd76-007b8663fbe1 | note | Verification Activity: Activity - I
9b7e8b3e-ce0a-50f7-ad87-71cddf2309ab | note | Verification Activity: By - SE
fcdff1e5-23bd-4954-9140-ed5e2efcd1d5 | checkpoint | 8.3.2 - Compaction - Structural Fill NDM
ddf0fbc4-6a80-5be6-907a-d823a94353b2 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
70348de7-3521-52db-a5e7-1cae1275b84c | note | Acceptance / Conformance Criteria - Ave >95% of MDD
a8828faf-8762-5d94-8516-88640ab1f1a7 | note | ○ Min >92% of MDD
369edca3-8e60-5ad8-871a-f061e53adbaa | note | Standard / Specification - PS 16.5.12
94190a09-43b0-5e25-91ee-a00d385b5c3f | note | Verifying Document - IANZ Accredited Report
c4bfc1cf-4b82-5e78-adbf-3168c0c4aa6f | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
0d381acc-e496-5978-84e9-fb46f4932e28 | note | Verification Activity: Activity - I
7cba9401-43ff-5df8-bd1e-3823f63a620e | note | Verification Activity: By - SE
f8a243ea-a509-416b-96ae-0969f339194c | checkpoint | 8.3.3 - Pumice Sand Fill
61a882eb-aab5-5648-b726-162fbe9a3c65 | note | Detail - Pumice Sand Material shall be contained with an outer layer of fill with a minimum thickness of 600mm. Must be Hardfill and/or imported Type A1 material and/or Type A2 material and/or Type A3 material
b0bc56b6-67b3-557f-b878-b249cf94f47e | note | Acceptance / Conformance Criteria -
f8fba99b-3f3d-5e0c-84c3-eb06fadce78d | note | Standard / Specification - PS 16.5.12
05af8a9f-73ae-5967-9b16-3ba158babe42 | note | Verifying Document - Site Records
ce0119a9-b26c-5a43-841a-2d5c2c3df3bd | note | Testing Quantity Required (based from schedule qtys) -
f3599b30-cf72-5e38-9bc8-b9846f61529f | note | Verification Activity: Activity - H
ca72cada-0754-5ea7-920b-252fc980ebc1 | note | Verification Activity: By - SE
5967f1b6-16f5-4bfa-8818-f55adf617aaf | checkpoint | 8.4.1 - Cut to fill
1e7d98f0-cc16-57f7-9cd5-8beae0bcf00e | note | Detail - Cut from classic building and use as a fill material
febc238d-8b89-5f1b-bfc2-1d3cd0f6494c | note | Acceptance / Conformance Criteria - Engineers Approval
f94dff61-0699-5791-b5b9-572d607f988b | note | Standard / Specification - PS 16.5.5 (b)
59575344-cc13-5019-854a-20b0f3475bfe | note | Verifying Document - Visual Observation
32fbfd2b-3b6c-5158-bb2e-02726787190e | note | Testing Quantity Required (based from schedule qtys) - If there is change in colour or after every 1000m2 of placed
371bcc6c-47c7-5fc8-a3c3-729d493d9c2a | note | Verification Activity: Activity - HP
2fe6dd9a-2f22-5d4d-8994-3b2916a95d0f | note | Verification Activity: By - ENG
6aa1a7a9-90be-4fc0-b37a-3e4110ace36b | signoff | AUTHORITY HOLDPOINT
a494e477-6f88-484e-a333-319228ca6545 | checkpoint | 8.4.2 - Compaction - Structural Fill Scala Penetrometer
e88b20ca-ec46-538b-b2a4-f01e414bb2fb | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
98d74863-26bb-514d-afb5-15b6c16e506e | note | ○ Scala penetrometer testing to be undertaken
3b68cdbb-3b67-5f98-b618-9dfb6664da05 | note | Acceptance / Conformance Criteria - Minimum 4 blows per 100mm penetration
9b2269b5-84d9-50ad-a3fe-55b6fc2cdfcc | note | Standard / Specification - PS: XVIII
73b312da-bd43-5275-9541-79c313a2a954 | note | Verifying Document - Scala Report
b0ecff54-ebb8-5a2d-91ba-ad1a38e33f86 | note | Testing Quantity Required (based from schedule qtys) - Minimum 1 set(5test) per 100m3 of filling evenly distributed over the extent and depth of the filling. A minimum of 400mm lift required.
acae5698-471a-55e7-b659-f30299858969 | note | Verification Activity: Activity - I
ac60b448-47d2-5db0-843a-eef7d4f69cf9 | note | Verification Activity: By - SE
e509cf73-7398-4005-b9bc-be775e63b128 | section | SECTION 9 – TOPSOIL PLACEMENT
c2cab1aa-65e6-4d2f-bc65-320687eca21f | checkpoint | 9.1.1 - Topsoil Placement on cut and fill embankments
d09b8fb8-2aa6-5ed4-9d38-5d2826813abf | note | Detail - Confirmation of thickness and material suitability
1022d2c7-74c0-5aca-a140-27cd1dfc2072 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
51f6394d-e159-5603-a284-e6f13e2e9a9a | note | Standard / Specification - PS 16.6.3 b)
11aa633a-1880-5351-9bf9-78df7b6e151f | note | Verifying Document - Visual Observation
e129084a-77a5-59af-a735-67e8f15e6404 | note | Testing Quantity Required (based from schedule qtys) - Once per lot after topsoil re-spread
622ccf0c-850a-52a4-9c54-07c8253dafab | note | Verification Activity: Activity - H
88cb1a66-2b9c-579c-a89a-98f16d4a6097 | note | Verification Activity: By - SE
e8229b09-d6fd-4e54-92d9-c62459ab74f3 | section | SECTION 10 – SETTLEMENT INSTALLATION & MONITORING
58be23bf-4688-4e30-b0b2-b6b63a7357ba | checkpoint | 10.1.1 - Instrument Reading Notice
9013008a-1bbc-5afe-93f2-5815006cfddd | note | Detail - The Contractor shall inform the Engineer two days in advance of planned instrument readings so that the Engineer may observe the work.
4cf9f484-599a-5a1a-92d1-f842aa9700a2 | note | Acceptance / Conformance Criteria - 2 days notice to Eng
14972fff-789f-5eb5-b768-2716392c64c4 | note | Standard / Specification - PS 16.8.2
927cfcce-64ed-5e0d-a6a1-767df4a2d19a | note | Verifying Document - Site Records
e3bf3ff9-7446-52e1-9691-e7db9dcc158b | note | Testing Quantity Required (based from schedule qtys) - Every Time
f4b5baa9-c32e-5c53-bfbc-80ac2316d794 | note | Verification Activity: Activity - H
9896fdbb-83c1-5d98-b01b-d15b55ce2d2e | note | Verification Activity: By - SE
26a94fa6-6bbf-416f-90cf-5e9e95d5e04c | checkpoint | 10.1.2 - Results Submitted to Engineer
d8525a80-1b19-517b-baf8-3d266e0a3134 | note | Detail - Results will be submitted to the Engineer within 1 day of reading the instruments
2bf5e40a-5d2c-5192-9709-12ece7fb2881 | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
0fb8386d-01a2-5f56-941e-4e5fa6c80c68 | note | Standard / Specification - PS 16.8.2
155a4973-cd4d-50c2-b8b5-7868a8c43d61 | note | Verifying Document - Site Records
05813563-805b-568b-9eb3-57a9539b17fd | note | Testing Quantity Required (based from schedule qtys) - Every Time
f01c0039-3b93-5c60-b9f7-e45061a296cc | note | Verification Activity: Activity - H
417f66b3-6342-53ec-b170-fed1a106cdfc | note | Verification Activity: By - SE
90b8ebf5-99a2-4fbd-9102-f172d3a0400b | checkpoint | 10.1.3 - Baseline Readings
0c152c63-7513-5a8b-9783-b06dfa808be7 | note | Detail - The Contractor shall take 3 sets of baselines readings from all instruments at 2 day intervals
bb96dc01-ab8e-57c7-91e2-1d1ec46ea28a | note | Acceptance / Conformance Criteria - Engineers Approval
da720b12-9a72-5ce7-8d72-8ff6c6aa3de0 | note | Standard / Specification - PS 16.8.2
71e0cdc8-3eb9-5a32-b833-55f8298a29d0 | note | Verifying Document - Site Records
2755e0f4-0dca-504e-a4d5-f19ee3b05343 | note | Testing Quantity Required (based from schedule qtys) - Every 2 days
6eeae8a2-6193-52aa-a3a6-c23e064de208 | note | Verification Activity: Activity - H
18c7965d-4bd9-5aec-a48c-f2adc455a2ff | note | Verification Activity: By - SE
0cbbce5b-3444-47d8-a57e-e12e058129cc | checkpoint | 10.1.4 - Readings During Active Fill Placement
4197cef7-d738-5556-b253-1545b28c8a62 | note | Detail - During active fill placement, the Contractor shall read all monitoring plates twice a week or every 1 metre of fill whichever is more frequent
db84ea5a-e268-5946-998b-18850c51d04c | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
9eca1f22-45d5-531e-bf9e-61ccfa5b84e4 | note | Standard / Specification - PS 16.8.2
5e7f206d-a75b-57c0-b499-2aef9f3d5e35 | note | Verifying Document - Site Records
4e3a2db6-9a55-5c97-8358-88b1435c7b92 | note | Testing Quantity Required (based from schedule qtys) - Twice a week
75f44174-7e1d-5cba-8660-8066fa3819f1 | note | Verification Activity: Activity - R
a045c7ac-9280-59f4-940d-46b5fe77607b | note | Verification Activity: By - SV
c934e3a6-8d4e-427a-84ae-4023bcecf911 | checkpoint | 10.1.5 - Readings During No Active Earthworks in Area
6fb21a42-c624-5660-9916-402a978f7cd0 | note | Detail - The Contractor shall read all monitoring plates weekly if there is no active earthworks taking place in the area
5c2145e6-39c3-5d7d-bb58-7b442a6c8e3a | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
ec69199c-8728-5949-ac73-99a35badc6f8 | note | Standard / Specification - PS 16.8.2
3d410bcc-215a-5931-aa23-a54a79e11990 | note | Verifying Document - Site Records
2795fa80-cd50-5ea7-9fb6-8b6bb8a60bce | note | Testing Quantity Required (based from schedule qtys) - Weekly
ffd719cc-d7c3-5e6e-b572-29f82aa3fe16 | note | Verification Activity: Activity - R
77dbba5c-7689-5482-b9c0-957ec7e8dce3 | note | Verification Activity: By - SV
e110b10a-f3f4-408f-ae33-65c4c1d3d958 | checkpoint | 10.1.6 - Settlement Monitoring Termination
780a6751-c986-51fa-9550-2ade040b1d3e | note | Detail - The criteria for terminating the embankment preload are either: Three consecutive measurements indicating the t90 settlement value has been achieved, A rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed. The settlement readings shall be evaluated by the Engineer to assess the need to extend the monitoring.
d6d8be6e-969e-581e-ba89-3965fcfe93e5 | note | Acceptance / Conformance Criteria - Either:
f8aed0bf-4a71-5d16-a811-6409ccddc2c8 | note | ○ 3 Consecutive Measurements showing T90 settlement value achieved
1c278dbe-dd7a-5b3b-89ef-28ff3eb72ecf | note | Or
3cb40c75-75cf-5cb1-a7ba-cee3b2811e31 | note | ○ Rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed
55b1f356-5628-5166-8bc3-0ec5b75bc340 | note | Standard / Specification - PS 16.8.5
edcc3231-271c-570d-8511-110efa0f5000 | note | Verifying Document - Site Records
cf103fa0-97ac-55af-9741-8daa9dd3a34b | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
c518c396-d5a1-5d3b-a3f1-867ed7d60d3b | note | Verification Activity: Activity - HP
06f0858c-8c5c-5623-b7c7-7ee08b1dd8c3 | note | Verification Activity: By - ENG
69dd92b3-df53-4990-a6f7-7426016b08eb | signoff | AUTHORITY HOLDPOINT
cf645024-fa01-4361-8fcc-6ffc48edeae4 | section | SECTION 11 – AS-BUILTS
6b6ee8e5-bffc-4685-b200-07529d88117c | checkpoint | 11.1 - As-Builts
cb5ddbd4-8b3f-5603-94d9-82f17700d657 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
d25443ea-366e-5df3-a9d7-57ca49b1eeab | note | Acceptance / Conformance Criteria - As-build record
aecac2b9-9f9d-5ed6-babc-e8e89e1ad75a | note | Standard / Specification - PS 16.7.6
8b7fb3b1-5706-58e9-92e9-76b26f384385 | note | Verifying Document - Survey Records/redpen markups
1722e594-0f26-544b-841f-646f99f95d1d | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
883f666e-15ca-55c3-9490-1089d15cad50 | note | Verification Activity: Activity - D
047410e9-1559-5ea5-b9eb-bfa9072acf4b | note | Verification Activity: By - SV
92f5b9bc-fb99-4286-8260-5508499e3c20 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
0a533e5f-f9ae-5ae3-9fce-85af0750349d | textbox | Contractor's Rep Name:
5ee7cbe6-5df5-5a26-b69e-cfb72eda4898 | textbox | Engineer's Rep. Name:
38028213-2a86-5e72-b9b1-c50b3c2fbd2e | date | Date:
f555597d-3e8e-4492-ace5-f06d34450f5f | signoff | Add Signature
fcfd5d08-3f3b-4b4b-8470-ccc187cfacbc | checklist | DN1210-SP2-003 ITP Temp works - Removal of Traffic islands and swale backfill Rev 0 | itp | DN1210-SP2-003 ITP Temp works - Removal of Traffic islands and swale backfill
53d1e63d-ba83-46fd-a672-8c7a20436e3e | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS
183650fc-395a-4c82-97ee-e0d68a3ce422 | checkpoint | 1.1.1 - Methodology
871daec1-bf5c-506c-b1e8-9e229b5190bb | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points for review and approval prior to works.
b343a29e-8e8e-506b-979e-4429875e2ae1 | note | Acceptance / Conformance Criteria - Engineers Approval
87791dda-ff77-50e0-b4bb-bdbc840226da | note | Standard / Specification - Appendix V
a0dad9c5-c910-53d4-ba98-9f3643ef4b6d | note | Verifying Document - Approved Methodology
5ca5e53b-c4c8-5915-ae9f-2b75d2065a89 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
4694ee63-248a-5a26-b77c-b8137dbdbd2b | note | Verification Activity: Activity - HP
74882bde-0f42-526d-a2e3-040e1f1e0d07 | note | Verification Activity: By - ENG
34b52e0e-9679-4939-8d9c-4179600f59b0 | signoff | AUTHORITY HOLDPOINT
6aea78be-4f3c-4685-b1f7-b0bbae58a3df | checkpoint | 1.1.3 - Erosion & Sedimentation Controls
d42d5416-01fb-5eb4-9668-fb10c6770c1d | note | Detail - Confirm that the weather and environment will be suitable for works with the Environmental advisor.
84e42fe2-c5a4-5ff5-bbda-d8c9b4a29ab5 | note | Acceptance / Conformance Criteria - As-built Completed
be2e3663-9bcf-5259-8e11-f3d6cc4ea52f | note | Standard / Specification - Internal Hold Point
9dd8ca8d-72c3-5d3e-94bf-a974e82d1e90 | note | Verifying Document - ESC As-built
e6a9909c-6653-5f8a-85b4-6dcb949e037c | note | Testing Quantity Required (based from schedule qtys) - Prior to works commence
b07e535d-a8a4-557b-ac3a-6cd4347858fd | note | Verification Activity: Activity - H
59490025-55a8-5a29-a58b-6ee7949071d3 | note | Verification Activity: By - QM
434dfae4-9534-4a15-a03d-001c01f62846 | checkpoint | 1.2.1 - Geotextile
909ed18d-2112-5bf2-a926-d2f3f21ba29a | note | Detail - The Contractor shall submit the full details of the geotextile they propose to use to the Engineer for approval prior to installation.
a1d4b849-6698-5e3a-8f70-35b8b7a3e8d0 | note | Acceptance / Conformance Criteria - Engineers Approval
d638d01b-264e-56a0-b17e-81452b9149eb | note | Standard / Specification - PS 16.5.7, Appendix V
3b6e995c-05a2-52df-86a0-1e6450752aa4 | note | Verifying Document - Data Sheets
15bdd476-2b14-5f53-9416-5f900a79f401 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
e0ef2bba-e4fc-5dde-b918-abf444a50101 | note | Verification Activity: Activity - HP
ea21f3bf-4b6d-5dcc-930f-4bb42f1584c1 | note | Verification Activity: By - ENG
8a23fa3f-033b-48b9-a79e-a4a856fc2acd | signoff | AUTHORITY HOLDPOINT
59922969-035d-4da2-9ef2-e08497f3de7e | checkpoint | 1.3.1 - Source data
06ba33e7-df67-56d6-a236-dcc44de120f9 | note | Detail - NZS4407:2015, Test 3.11 - Weathering Quality Index
530cdcee-59c0-57d1-84bd-580163c7eaaf | note | ○ NZS4402:1988, Test 4.2.1 - Standard Compaction Result
0e8757bd-07c4-5f6f-b2aa-1379e073be84 | note | ○ NZS4407:1991, Test 3.12 - Los Angeles Abrasion Test Result
b6d9e160-5e98-5292-814d-aaf708682beb | note | Acceptance / Conformance Criteria - As per specified criteria
9704fc8b-3485-548f-b1f1-56d4bc07772a | note | Standard / Specification - PS 16.5.5
69b2eb06-2689-5b8a-93be-2b4e1edf5fc6 | note | Verifying Document - IANZ Accredited Report
4cd83dea-24c6-5ff6-81bb-992a5b734edc | note | Testing Quantity Required (based from schedule qtys) - 2 Test per Source
3dc2c8eb-3f81-5dcc-8573-bd773e4b35b2 | note | Verification Activity: Activity - HP
96a5d8eb-d8d5-5f63-a182-a0498418a690 | note | Verification Activity: By - ENG
70bb1424-38b7-48f6-b6a2-26fc3a5b8156 | signoff | AUTHORITY HOLDPOINT
541c128a-50ce-49c0-86ae-fd445fd66bb2 | checkpoint | 1.4.1 - Dense Graded Asphalt
04d330f5-2eb6-5fa9-8fa1-452e4ca8f0de | note | Detail - Conforming sieve size and Mix designation refer to clause 3.3.1 and Table 3.5
6044fdb8-ce10-56bf-97f3-9436a672b392 | note | Acceptance / Conformance Criteria -
50b9af76-1d2d-54b2-bcd3-ab29fd0b190c | note | – – – – – – – – – – – – –
8afffc12-cbb0-5be3-affd-11495a17c3a1 | note | Sieve Size (mm) ¦¦ Mix Designation: DG7 ¦¦ Mix Designation: DG ¦¦ Mix Designation: DG14
2ba3db7a-bc64-5d24-9103-a761b810d949 | note | Percentage Passing Sieve Size (By Mass)
e4e621ca-27a0-5900-8a53-6a4ea2c7e7e9 | note | – – – – – – – – – – – – –
d6e2067c-cb76-59bc-b448-98d27ff95057 | note | 19.0 ¦¦ – ¦¦ – ¦¦ 100
b6b87316-637a-5cc9-992c-ad8245b4e9dc | note | 13.2 ¦¦ – ¦¦ 100 ¦¦ 83 – 100
d08557d4-42a6-5fbd-b476-cd4de0a2a9f5 | note | 9.5 ¦¦ 100 ¦¦ 79 – 100 ¦¦ 68 – 90
fb66f1e4-ebdb-5567-bb43-c5dd33d2293a | note | 6.7 ¦¦ 80 – 100 ¦¦ 63 – 90 ¦¦ 54 – 79
ef4c790d-f63f-5f6a-b7bd-b27fd6d0695b | note | 4.75 ¦¦ 66 – 90 ¦¦ 50 – 79 ¦¦ 43 – 70
3bd9394f-1619-557c-b6ca-c243c9c562ba | note | 2.36 ¦¦ 44- 75 ¦¦ 32 – 61 ¦¦ 28 – 55
e4bb4ce4-4990-50a4-840a-4da3b06ceabf | note | 1.18 ¦¦ 29 – 60 ¦¦ 22 – 48 ¦¦ 19 – 43
d4f2c482-11b0-5b4d-a262-a5150303a52d | note | 0.600 ¦¦ 19 – 47 ¦¦ 15 – 36 ¦¦ 13 – 32
6afdd9cf-afdf-532e-9a13-e03a001327f7 | note | 0.300 ¦¦ 12 – 33 ¦¦ 10 – 26 ¦¦ 9 – 23
66cbc57b-b145-54b7-80ba-05bd90d12329 | note | 0.150 ¦¦ 8- 22 ¦¦ 6 – 17 ¦¦ 6 – 16
9ead9df4-e8e9-5a11-9b32-5444783b3bc8 | note | 0.075 ¦¦ 5 – 12 ¦¦ 4 – 11 ¦¦ 4 – 10
0e18938e-49cf-5ea8-b725-0fe681779027 | note | – – – – – – – – – – – – –
2d940bbb-0f63-59a7-b205-f219826d89fd | note | Minimum Layer Thickness (mm) ¦¦ 25 ¦¦ 35 ¦¦ 50
92121793-6597-56af-9591-45b5ec02b163 | note | Binder Content ¦¦ 5.0 – 7.0 ¦¦ 4.5 – 6.5 ¦¦ 4.3 – 6.3
35ca611c-ae38-522a-8e25-24cd09a164bc | note | – – – – – – – – – – – – –
a6d9598d-21cd-5981-86f8-15ff49ed02b7 | note | Standard / Specification - NZTA M10: 2020 / PS 20.12
c5a562db-4153-581b-b1dc-118727172676 | note | Verifying Document - IANZ Accredited Report
8d79dfe9-871d-5736-bdde-02a194455e10 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction and during construction
e949c1e1-fba7-5129-b267-05b94672af5b | note | Verification Activity: Activity - H
49a0a5de-3b89-5f47-9af5-40d2dd03cc90 | note | Verification Activity: By - SUP
ea6220da-4c98-4bf0-a2a6-66f72f4a434d | checkpoint | 1.5.1 - Subsoil Pipes
274529b2-fff2-5b79-afca-87bf1f241eba | note | Detail - Drainage pipes used in subsoil drainage shall be smooth bore perforated Landflow 100mm diameter complying with NZTA F5 unless otherwise stated on the drawings. Pipes shall not have a geofabric filter sock unless requested by the Engineer.
70f779f2-1281-5509-aa93-746212566faa | note | Acceptance / Conformance Criteria - NZTA F5
e4ce6dc7-93b8-5a66-8850-28a98ff8581a | note | Verifying Document - Verifying document to be copy of delivery dockets, photos of pipes onsite with tag showing class
38a3131f-81d9-547a-bb7f-53e1a7544a54 | note | Testing Quantity Required (based from schedule qtys) - During Installation
723bc1e9-d4c0-561d-8260-bb39260dc6d7 | note | Verification Activity: Activity - I
2b0211d6-6d18-575f-be8a-7e75f048d9c1 | note | Verification Activity: By - SE
2178114d-9de7-4294-9fc9-e58f479ba78e | checkpoint | 1.5.2 - Catchpit
de14068c-2a46-5e41-939e-2ca8bfb3f022 | note | Detail - Catchpits are proposed to be precast concrete chambers with grate and frames shall be cycle-friendly Hynds Hydro Stormwater Grate and Frame or approved equivalent for all local roads and the state highway
1e985340-c406-562a-a217-a6827b2527ba | note | Standard / Specification - PS 21.5.4, PS 21.6.12
ed79978f-1b0a-5a2a-94ee-d02f1f4721cc | note | Verifying Document - Site Photo / Checksheet
a8b74203-ae81-53ab-a4fa-f5d1cd0b51fb | note | Testing Quantity Required (based from schedule qtys) - During Installation
090aa7c6-b9e8-5601-b21e-9e9d82c7c927 | note | Verification Activity: Activity - I
9a3f1b34-fda6-58ab-a227-02ec023ea8dc | note | Verification Activity: By - SE
e7f10a24-7f58-4c17-9c55-358659d949f1 | section | SECTION 2 – TEMPORARY CONSTRUCTION - EARTHWORKS
4ceb2292-4e9c-476c-81d6-5cc8de855785 | checkpoint | 2.1.1 - Cut Subgrade Testing - Cohesive Soil Scala Penetrometer
de086e42-0d54-5b7a-8da2-d393e47f5cf9 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
b0a13e6d-ac70-5612-a267-92a442116454 | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
4d8e20d7-5c7d-5fc2-a9ee-5a1e26de2315 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
729aa5e4-60d6-53bf-99e2-4cdd873a7bfd | note | Standard / Specification - Appendix XVIII
ce08cad8-13c2-5549-be60-ce5598350eac | note | Verifying Document - Scala Report
3f087b76-8a50-599f-8b9c-7612255a7cb9 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
3a4220cb-9d39-5b71-8be6-8a0be3bbbd5a | note | Verification Activity: Activity - I
f34ab335-ab1d-5764-ae67-0780172b9e23 | note | Verification Activity: By - SE
065e6f73-ac5b-45c4-b0b1-2fcd47b9c343 | checkpoint | 2.1.2 - Proof Roll
94fd5a28-9d58-52c0-9b91-e93b474ece94 | note | Detail - Visual Inspection of Proof Roll an d undercut surface
e037022e-2515-5a26-886d-137ae2396c00 | note | Acceptance / Conformance Criteria - Visual Inspection
93ea7a20-8df7-532c-ae33-e49db0b86f41 | note | Standard / Specification - Appendix XVIII
0aa4b4ba-4ea5-5984-92f4-3b4d958aa56b | note | Verifying Document - Visual Site Record
4fcae931-91e8-58c0-8054-803e9bf384e2 | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
10035b01-d93c-56e1-866b-2af53df54c86 | note | Verification Activity: Activity - I
fe735711-1de5-54a5-a10e-2881c1cf95ed | note | Verification Activity: By - SE
b404eef9-ea3d-4386-8c39-8dbec1300748 | section | SECTION 3 – COMPACTION OF IMPORTED FILL
054753db-cca2-4bbd-ac76-d6ad0d696f7b | checkpoint | 3.1.1 - Placement of Geotextile
2bc709f3-e2de-5063-9748-f970e0608557 | note | Detail - A layer of Class B Geotextile Fabric is to be placed between the cut surface and imported GAP65 Fill with minimum overlap 400mm between adjacent geotextile strips.
00b4ed1c-65de-5a06-b6ab-8a9072a01a57 | note | Acceptance / Conformance Criteria - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
3bf1f8c1-e5d3-5668-9a60-524709998556 | note | Standard / Specification - Engineers Approval
0607936b-5794-5c25-a57b-9b3044c54ab9 | note | Verifying Document - PS 16.6.4, TNZ F/7: 2003 8.3
760871b2-de5d-576f-a99b-7f801276e992 | note | Testing Quantity Required (based from schedule qtys) - As Required
ad1ac9a4-d6de-5f16-9043-3b36669d8d82 | note | Verification Activity: Activity - I
d0ffa18c-dfa5-56bd-b722-d06d585442a0 | note | Verification Activity: By - SE
2ca6c86f-5d41-4a86-8c9a-40a268cccd51 | checkpoint | 3.1.2 - Subsoil Drain inspection
ebc8eb7d-2085-582e-b64c-23d034db425b | note | Detail - Subsoils to be placed at base of cleaned-out swale to falls required to drain to existing road crossing drainage
134a64d0-8cd5-5c64-94c3-4d1f4d335424 | note | Acceptance / Conformance Criteria - Visual inspection
11c437e3-1960-5a2d-81f7-ba05bbf1a222 | note | Verification Activity: Activity - I
787ded38-8143-5b32-90b9-679becd4b77c | note | Verification Activity: By - SE
e535c3db-e835-4f06-abfe-9605a50c1984 | checkpoint | 3.3.1 - Backfill Installation
0dab4155-9287-5e68-86ff-4f9fcf420d68 | note | Detail - All backfill is to be installed in 250mm lifts and compacted to the following standards.
94cbf07b-7e89-51af-8ff1-70cac812c5e2 | note | Acceptance / Conformance Criteria - Visual Inspection
18d0b3d6-9ccc-53cf-92fa-878e99c7d01e | note | Standard / Specification - Appendix XVIII
ad99ce20-52d5-5d48-b062-6f3c5e4ce303 | note | Verifying Document - Photo
fd639c1c-51dc-54d3-af8e-2ac09a49f782 | note | Testing Quantity Required (based from schedule qtys) - Each Layer
876f27ef-d962-5c30-8b2c-493fef588687 | note | Verification Activity: Activity - I
752e2378-a643-5636-8857-836647115373 | note | Verification Activity: By - SE
8f2c1d1d-230e-48f3-9dda-afa9ef584bb4 | checkpoint | 3.3.2 - Compaction - Clegg Hammer
0d575b74-7a86-500f-a99f-ee1fb300d03b | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
f72c9dff-1d42-5e18-8d32-f6473b9f92e8 | note | Acceptance / Conformance Criteria - Structural Fill
884f1458-45a0-501b-a08c-c0d003b57912 | note | – Min CIV 18
d4d9a7ab-e2b2-53dd-a65a-b522cab76baf | note | – Ave CIV 20
1ee97c69-3a61-5262-af92-ebfc03c198ec | note | ○ Non-Structural Fill
cb1aca23-5a38-5c4d-af95-d41b8ab16215 | note | – Min CIV 10
685b1d7c-55fc-5447-9806-0a30de0d78bc | note | – Max CIV 12
b8ecc57e-0750-525d-a74d-5c80ee14b730 | note | Standard / Specification - Appendix XVIII
bf92fd5a-2b8c-5b40-8cca-37b9126d573b | note | Verifying Document - Clegg Hammer Report
43ce03af-0531-5bb0-a217-996a67d50099 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
7c21f5ed-66b7-5579-99a0-8d8361f5d62b | note | Verification Activity: Activity - I
674ca043-7c15-5d0b-a073-a5e3628bdd7f | note | Verification Activity: By - SE
e19829af-d77f-41fa-8f0d-a7cab600b594 | section | SECTION 4 – SURFACING
83f1f40c-2c87-42ff-9f3b-3dbb1878c39e | checkpoint | 4.1.1 - DG10 Asphalt
996b6b68-5904-5e5e-af77-ffd9bfe7ff52 | note | Detail - Layer thickness to be min. 40mm or approved by Engineer
4e7f6814-f05f-5362-b3b2-37d5f27c217c | note | Acceptance / Conformance Criteria - Visual Inspection
b918bb4e-ca80-554c-b704-a137e9e4adc5 | note | Standard / Specification - NZTA M10: 2020 / PS 20.12
80a44eed-3023-54cd-b83f-21f2825a8eae | note | Verifying Document - Prior to Paving
f746a21b-fad5-5e98-a6b3-69c4c6ff19d7 | note | Testing Quantity Required (based from schedule qtys) - During construction
dddfb60b-8707-56c8-9fad-a6aa725c8eea | note | Verification Activity: Activity - I
e233fc4d-76e5-5b69-ba51-4e7b2c6937f7 | note | Verification Activity: By - SE
eacf6503-0788-475a-a241-99a991259e8c | section | SECTION 5 – AS-BUILTS
535991ae-488e-4945-80d7-2c5e51fa8f21 | checkpoint | 5.1.1 - As-Builts
80072cf2-4d98-528e-b971-defb3b1a2eb6 | note | Detail - As-Built records and drawings shall accurately record the layout and extent of all the work and locations of subsurface drainage systems and their outlets.
e00ea4d4-cf7a-5dc3-9888-e305600d3710 | note | Standard / Specification - PS 16.7.6
738a6ffa-73be-5a98-ad1a-190736096ccd | note | Verifying Document - Survey Records
83154674-a7a1-564c-bf82-18d03e3b9439 | note | Testing Quantity Required (based from schedule qtys) - Post Construction
874cc4b8-9414-5123-a60d-748a610fe08a | note | Verification Activity: Activity - D
b3937cc1-4fce-55dc-b9f8-77ae2281a726 | note | Verification Activity: By - SV
36dc5489-9969-404c-bf55-0431d994ef94 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
ad404e68-0b2a-5337-b0f6-a2dae4118ac0 | textbox | Contractor's Rep Name:
65fe3d6b-1341-5134-8da0-99624d67bdc3 | textbox | Engineer's Rep. Name:
e0658281-fc66-5a34-bd92-5a4dff3f6047 | date | Date:
6e18cc9f-808b-4961-87bb-11354f7fe25d | signoff | Add Signature
7ca02e9a-1bf6-4899-b82e-560ffb5fb8ed | checklist | DN1210-SP2-006-001 - ITP Northern Access Road Carpark Pavement 4 Rev 1 | itp | DN1210-SP2-006-001 - ITP Northern Access Road Carpark Pavement 4
39ff8a79-3f95-4fb0-953a-5deb4512eac0 | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
21fba1a6-0a0f-45d2-a30b-8d9765086ddb | checkpoint | 1.1.1 - Crushing Resistance
4bcc4794-aa93-571f-b94b-8b9c75f1a80c | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
4bda5bd8-0640-58ff-a01b-7fda798bf168 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
4f3baefe-1bb2-54fc-ad16-e91cf161914d | note | Standard / Specification - TCC-IDC IT-4.7.1 table 4.4
222e6f92-9b0b-50a8-a930-6bdd2056ea8d | note | Verifying Document - IANZ Accredited Report
39f063e7-5193-528f-a309-7c7141c9ab5a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
3072d13c-1469-544d-9db3-4efef98b9b57 | note | ○ Results to Engineer 2 wks before importing
8daf1a8c-feb0-5447-8d87-8ffbee11dc61 | note | Verification Activity: Activity - HP
b6798273-b791-521f-ba91-ae0597a5a178 | note | Verification Activity: By - ENG
f5aff5c3-5665-4b79-b233-49b24ae52db3 | signoff | AUTHORITY HOLDPOINT
48fb2617-baa9-48db-aa5a-57197500e198 | checkpoint | 1.1.2 - Soaked CBR
66bfa783-b920-53f6-8299-b8c03e527220 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
08acfacc-9b43-5f09-83ee-5921c74d4064 | note | Acceptance / Conformance Criteria - ≥ 60%
3f4e1be2-02f5-5cb2-8b55-4fdd41c3d0d5 | note | Standard / Specification - TCC-IDC IT-4.7.1 table 4.4
a494e579-a6c6-5a81-ac1f-3fdcf4498a52 | note | Verifying Document - IANZ Accredited Report
87bc8f74-439b-5ffc-9ee8-59e746bfa134 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
ddf46b3f-3296-55d4-8231-2408bb7f7d31 | note | ○ Results to Engineer 2 wks before importing
2bd47548-56f9-50c8-8a74-95921bdc2eef | note | Verification Activity: Activity - HP
d4a7a1b2-2c07-577d-81a6-6042b0990a3c | note | Verification Activity: By - ENG
c60b319b-4d5b-4d59-b505-8e6f73bbc5be | signoff | AUTHORITY HOLDPOINT
d93d42b6-1359-4c5e-8928-e13ef2de715f | checkpoint | 1.1.3 - Weathering Resistance
9aebbb65-5da1-5b1b-b8b8-de3ffee968bc | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
b3238194-862e-5f81-a779-4cc2abd39d71 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
080ebdd9-3eb7-529b-ab6b-24afc8a4a1ea | note | Standard / Specification - TCC-IDC IT-4.7.1 table 4.4
abb3b4a5-f01b-5acd-ad9f-34ee17c682f9 | note | Verifying Document - IANZ Accredited Report
c855812a-da9b-5672-8620-678782a72833 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
acda6c21-20ab-52d1-b0c1-5fc94755bffc | note | ○ Results to Engineer 2 wks before importing
1f5ef382-1c0a-5f9a-82f1-f3f3109d923f | note | Verification Activity: Activity - HP
e1c2002d-9e71-5fc9-8610-ed0a03fd47c0 | note | Verification Activity: By - ENG
68756017-5903-4a70-a38b-be87ec941a31 | signoff | AUTHORITY HOLDPOINT
bead6618-78cd-490f-97b0-c7b1cae148db | checkpoint | 1.2.1 - Particle Size Distribution
186f7ae6-0d4a-5285-8478-122740f81881 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
f2defd5c-41d5-5309-977a-5e1c9fc709d1 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
77a448e0-6f71-5bf5-8acb-7512f8411045 | note | 63.0mm ¦¦ 100% passing
d131a7b9-7c26-5477-9815-b10c65ce426c | note | 37.5mm ¦¦ 55-85% passing
43832fa8-b8cc-52c7-8266-b17c0dca8f49 | note | 19.0mm ¦¦ 33-65% passing
d321e55c-a45b-5214-b8b7-459b2fbcffdd | note | 9.5mm ¦¦ 20-50% passing
1179987a-b153-59b7-80ee-a3e049b6c1cb | note | 4.75mm ¦¦ 10-36% passing
5ca847bf-043e-5129-97de-b01ff16c6e4a | note | 2.36mm ¦¦ 5-27% passing
c74374c8-3c80-50ce-87ef-01940262f7de | note | 1.18mm ¦¦ 2-20% passing
71f1b53b-bb31-5b65-9943-8e6a097aff73 | note | 0.425mm ¦¦ 1-13% passing
b3f9b339-ffb3-59d3-91f1-945ecf3f2310 | note | 0.075mm ¦¦ 6% max passing
6ca50919-4cce-5556-9c8d-4c8c0c2497c2 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
7e12c909-9a65-57fa-9fb3-89145360a822 | note | Verifying Document - IANZ Accredited Report
25843796-395c-57b1-8c16-a8820cc348ad | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
e5ab4459-d41f-523a-8aec-6492e3f57fa8 | note | ○ 0-400 - 2 tests
731c3954-0ff5-5c6c-9c53-0208ffb93233 | note | ○ 400-1,500 - 3 tests
705f0bbe-8bd0-5c5e-b65f-5e388c34768e | note | ○ 1,500-4,000 - 4 tests
681cfb75-d779-52ed-9f25-29ef9a652d7f | note | ○ >4,000 - 1 test for each additional 1,000m3
2eab5c1f-ffd8-5ede-8145-4a6e789bf8e9 | note | – Results to Engineer 2 wks before importing
a1722413-3b72-50c9-98a7-67c50d8162a1 | note | Verification Activity: Activity - HP
d7b7353c-351b-5ba6-8af8-dbaea277efb9 | note | Verification Activity: By - ENG
4b6b56cc-7880-461c-a1d3-9d1be632f96f | signoff | AUTHORITY HOLDPOINT
0a29909b-7df2-4b63-9c2f-ae7f3eeee40a | checkpoint | 1.2.2 - Shape Control
12aaae88-5f49-548b-a68e-776a49375fd5 | note | Detail - Tolerance allowed from approved grading curve (%)
d6144050-fee3-5899-89ee-c713498528bd | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
da592349-70a1-5f0f-8ca7-d27af0a72ccf | note | 37.5 – 9.5 ¦¦ 34-50%
2723ed4d-e51a-5e17-a664-6fa56404f36d | note | 19.0 – 4.75 ¦¦ 18-40%
4fec7e3b-9bb2-53dd-bb7b-ad9b1471e5ad | note | 9.5 – 2.36 ¦¦ 12-32%
c9979751-ca31-55f1-a6c1-232ce4916d39 | note | 4.75 – 1.18 ¦¦ 6-24%
c63770e8-94b7-5e89-a419-077cca3ab696 | note | 2.36 – 0.6 ¦¦ 2-20%
145cb119-63f3-5d6b-be2d-5c1a00011837 | note | 1.18 – 0.3 ¦¦ 0-15%
ed69bc74-82fc-57d6-8fcf-e619fb97373e | note | 0.6 – 0.15 ¦¦ 0-12%
7c9ed9f0-3195-5f3c-bdc0-b35e8d065389 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
0b8b134d-f8f3-555f-a334-9bf4d053cf2e | note | Verifying Document - IANZ Accredited Report
92cdfc26-6cdf-5b6d-9ef0-44994adb7314 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
90243c27-d070-50f9-be8f-261791c2816e | note | ○ 0-400 - 2 tests
d58abe77-452b-5f10-a9cc-f5e4447dd63e | note | ○ 400-1,500 - 3 tests
b5addd33-3ca9-5e5c-90d5-9e1766222be5 | note | ○ 1,500-4,000 - 4 tests
d699f384-afdc-5bbf-881e-b01cb0cc17c9 | note | ○ >4,000 - 1 test for each additional 1,000m3
6807170c-bc9d-563f-a7f2-f20779fe7ab5 | note | – Results to Engineer 2 wks before importing
47da934d-94c8-52f0-90dc-b154c035ee4b | note | Verification Activity: Activity - HP
0f9e4c8f-618f-5a5a-83e4-bcbea5326bce | note | Verification Activity: By - ENG
0f4bf4a0-4d2d-41f9-a042-46915820ab2b | signoff | AUTHORITY HOLDPOINT
bcdc031f-b107-44e4-8646-cd04b92ca167 | checkpoint | 1.2.3 - Sand Equivalent
5b0eddb0-44b4-5aa9-8239-b370ad3798df | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
144697f5-d658-5a7a-8ac0-e29eb94d7da1 | note | Acceptance / Conformance Criteria - ≥ 30
3b467afb-c496-5771-a538-4945770784d9 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
2164aee3-fc16-527f-a440-204c5df6b8a1 | note | Verifying Document - IANZ Accredited Report
d7ca59db-590c-5115-8fb0-246b8e647104 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
a5c6035e-0af7-562f-a2eb-672954f8b38a | note | ○ 0-400 - 2 tests
ef007893-e49a-5eb7-97b8-ae6e9558c7cd | note | ○ 400-1,500 - 3 tests
8465c284-5179-5756-9833-80de3892642e | note | ○ 1,500-4,000 - 4 tests
8c05216c-a006-530e-98a6-e3fdfdd00c5a | note | ○ >4,000 - 1 test for each additional 1,000m3
f82f6226-68b1-5122-83c5-29d8bc02fd5e | note | – Results to Engineer 2 wks before importing
5c2579ba-494d-5d4e-a74c-32f7136c4715 | note | Verification Activity: Activity - HP
4342892c-6806-5795-b6cb-3bb43d75d071 | note | Verification Activity: By - ENG
9307f8c2-9eec-4a41-b048-de67a2cda9a3 | signoff | AUTHORITY HOLDPOINT
d1810625-c98c-4142-9911-713642cad8a6 | checkpoint | 1.2.4 - Cone Penetrometer Limit
6f35f3b3-8179-5080-88fb-40a37605bbb3 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
6198a42d-bd88-5594-aaca-bc596e45c0d3 | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 25
0a6cdf02-7854-5939-b2c5-944c72f3a5fa | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
49c3a4f1-9cb1-51de-ac25-36652c29d0e8 | note | Verifying Document - IANZ Accredited Report
e8113f1d-bcf2-5565-90e8-bdbd6273d146 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
300cd2c3-0eb6-56f4-9144-649ca13ae4cd | note | ○ 0-400 - 2 tests
08273d7e-fa70-502e-9f9c-e6fc8cbacfc0 | note | ○ 400-1,500 - 3 tests
25a952b3-4f98-5b0d-9cb2-4e0b89bdd1a4 | note | ○ 1,500-4,000 - 4 tests
0ac30ce4-8886-5837-9411-f4b1a80c649e | note | ○ >4,000 - 1 test for each additional 1,000m3
f96eeccc-94e8-5ad7-a34b-3b97aea705ba | note | – Results to Engineer 2 wks before importing
04f2d9bc-8b31-5ae0-acb6-6f0cd8409239 | note | Verification Activity: Activity - HP
d6d69ab2-34f0-5a47-a02a-e29e690e66c7 | note | Verification Activity: By - ENG
ffce4b38-6bd6-4ee6-a27f-8c90698b5e67 | signoff | AUTHORITY HOLDPOINT
95b01fe1-fa7d-40a3-a12c-ab13648ac97f | checkpoint | 1.2.5 - Plasticity Index
f8be753c-423d-549a-9a2d-d86ca7544ba4 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
0da8e495-3f7a-5f65-be7f-b2a43dab4944 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
36bfb54b-f73b-5fdf-b7c8-41532e77c7b5 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
dd9aefbd-f319-54f0-aa80-8557392d7819 | note | Verifying Document - IANZ Accredited Report
e550091e-9e33-5f6a-8a15-da1d83fbecc1 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
f4b94eaf-28a2-5a10-a334-e5f6ad6c8c72 | note | ○ 0-400 - 2 tests
b92a34ec-0839-5399-9669-372337a17b2e | note | ○ 400-1,500 - 3 tests
2126a739-a5a5-5b77-9c5a-db0fd0d4d923 | note | ○ 1,500-4,000 - 4 tests
6a4ce228-6142-5426-a9c3-6e94795a54ae | note | ○ >4,000 - 1 test for each additional 1,000m3
88e30764-ecea-5a3b-a84f-d66b9fd3e809 | note | – Results to Engineer 2 wks before importing
7368bd10-f529-5399-8a02-38658ea2f230 | note | Verification Activity: Activity - HP
26b84afc-5ccc-521a-9995-59fcee8fdeda | note | Verification Activity: By - ENG
5ccd4a8b-ec65-4dbd-a110-e46d5f7bb261 | signoff | AUTHORITY HOLDPOINT
ebc4036d-f6ec-4af9-975e-dc04c7f7b51e | checkpoint | 1.2.6 - Accelerated Weathering
4770b6e5-e0a0-540c-b070-9b0dc085d8d1 | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
cc5250d4-714c-55a7-a1c3-9e9ce300a6ba | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
25bf4c2f-1aea-5cbf-a2c1-b77792e832a2 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
5b52a233-60cc-52bc-8af0-afaba690c1f4 | note | Verifying Document - IANZ Accredited Report
a85088ac-39f1-5cb0-a5e3-7d12976737d3 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
6a175314-0108-5d97-a93f-fb47f0ad09e4 | note | ○ 0-400 - 2 tests
59f0b802-c46b-56e0-b08c-9c492a726263 | note | ○ 400-1,500 - 3 tests
88b95da6-5af5-5da2-97c5-cd28c1a4357c | note | ○ 1,500-4,000 - 4 tests
4dc1f709-5aaf-5a15-b141-d2b0e4199e13 | note | ○ >4,000 - 1 test for each additional 1,000m3
9e755834-9b3c-581d-8f39-b0130c5322f0 | note | – Results to Engineer 2 wks before importing
bae86160-1c9a-5ef6-88df-f9358a4264b7 | note | Verification Activity: Activity - HP
56aabfd3-b5b3-533e-9b44-5fdd5a049e04 | note | Verification Activity: By - ENG
d20d675e-c2a8-46d3-9e07-f5afab28ef05 | signoff | AUTHORITY HOLDPOINT
50aefd72-c22d-40a3-8b46-b6bc936a9947 | checkpoint | 1.2.7 - Maximum Dry Density and Optimum Water Content
55e9a352-d9e4-5464-aa43-8f57c96b2a34 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
3f80db51-3fa5-5f20-89b5-b75a2695d46b | note | Acceptance / Conformance Criteria - Report Value Only
d5abc860-c6fd-5863-8b02-0a9d80a3b909 | note | Standard / Specification - TCC-IDC IT-4.7.1
9fb27b85-c0fa-55c5-b306-72bb95205636 | note | Verifying Document - IANZ Accredited Report
1d7ab5cd-4d2e-5c57-9c27-921be94f88f8 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
5bcc37a9-2536-5b2d-affd-b6096a56af89 | note | ○ Results to Engineer 2 wks before importing
1d987b14-18cd-5126-94b7-12aab4b82e49 | note | Verification Activity: Activity - HP
444be81b-158c-5d0d-be16-7d960a35ff63 | note | Verification Activity: By - ENG
6d8a7f61-761d-4610-bcd2-9cba2c0824dc | signoff | AUTHORITY HOLDPOINT
ab877bed-1551-44ad-9e03-9703ffb5e094 | checkpoint | 1.3.1 - Geogrid
bfc8294f-0e1b-5b5e-a26e-65f0cbde3f0d | note | Detail - The Contractor shall submit the full details of the geogrid they propose to use to the Engineer for approval prior to installation.
f86ab8ee-4734-5995-9fb9-67db013c65ee | note | Acceptance / Conformance Criteria - Engineers Approval
e6580752-4baa-5cc3-a30a-d27b9bede20b | note | Standard / Specification - PS 20.5.2, PS 16.5.13
d162a642-fb94-5d21-bdaf-109de957ef5b | note | Verifying Document - Data Sheets and Approval
f1d67de8-200b-579b-87b0-a8a91d4bb568 | note | Testing Quantity Required (based from schedule qtys) - Once prior to works commencting
7cc85a70-4d6d-5c12-aa13-957cb9609a08 | note | Verification Activity: Activity - HP
e5fc97bd-1fb5-5e11-944c-881e27a23b17 | note | Verification Activity: By - ENG
51558b85-27a9-40cc-aa74-2bb2828b7dc8 | signoff | AUTHORITY HOLDPOINT
580dbb47-77c3-4acd-9a94-f58db5193cc7 | checkpoint | 1.3.2 - Geotextile Fabric
8de5d0bd-dd37-57af-859e-1b05729bd3b6 | note | Detail - The Contractor shall submit the full details of the geotextile fabric they propose to use to the Engineer for approval prior to installation.
40dbd616-1530-56ad-a409-2169bf769928 | note | Acceptance / Conformance Criteria - Engineers Approval
cec1ebb6-2781-5374-b0e3-e720647b1573 | note | Standard / Specification - PS 20.5.2, PS 16.5.14
3ce5b17a-3ce5-51b0-a098-5cabe675b32d | note | Verifying Document - Data Sheets and Approval
10260c42-b6a9-558e-a176-b491d517d50e | note | Testing Quantity Required (based from schedule qtys) - Once prior to works commencting
70daade6-e540-508c-9057-bf41c693601c | note | Verification Activity: Activity - HP
0e98a1f9-c5e4-56a9-915f-1781f7c54c25 | note | Verification Activity: By - ENG
3cabdb07-25dd-4e77-b844-24ae462defed | signoff | AUTHORITY HOLDPOINT
c36da2fa-c60e-4e95-afe2-682f90cc801f | checkpoint | 1.4.1 - Crushing Resistance
9712525e-30a0-586e-9330-fd29d0f5b6ea | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
61531903-0fd1-5d0e-86da-5916a9c1240b | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 100kN
7efbf267-0234-522a-b5b7-1de5866610f9 | note | Standard / Specification - NZS4407:2015, Test 3.10, TCC-IDC-IT-4.3.1-4.7.1
ec170364-4840-5bca-b2f8-5e8ce5363d31 | note | Verifying Document - IANZ Accredited Report
6f548086-eac2-59b7-bd3e-187f43c1cd4c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
a73ecbb2-b655-500a-807c-b03786d04793 | note | ○ Results to Engineer 2 wks before importing
f6a5af8c-78e5-5ce5-a019-f5df7d5c0fbd | note | Verification Activity: Activity - HP
96731405-5223-5fdf-996f-d5c5d24c4b0e | note | Verification Activity: By - ENG
57bd8146-9a49-4aca-b534-b3674617611f | signoff | AUTHORITY HOLDPOINT
5b92e045-080b-4dd5-adea-affa2e731788 | checkpoint | 1.4.2 - Soaked CBR
f0784c99-d565-51b5-8fd1-a65b9d661ae6 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
412aad67-556a-56e1-a03e-230a9e9f86f7 | note | Acceptance / Conformance Criteria - ≥60%
c57b416d-14f7-51f6-b349-7847a16e2a25 | note | Standard / Specification - NZS4402, Test 6.1.1, TCC-IDC-IT-4.3.1-4.7.1
d90c8018-3522-5fd7-81b0-6aef97901090 | note | Verifying Document - IANZ Accredited Report
40445e28-f0cd-5487-8225-8b1e1db35dd2 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
011c24dc-e814-55d6-869f-30b73357bbb4 | note | ○ Results to Engineer 2 wks before importing
fe5e4045-0182-5d56-a73c-28bf62826f82 | note | Verification Activity: Activity - HP
a13cead1-ddc9-5312-ab22-417405e5bf72 | note | Verification Activity: By - ENG
0981b494-759b-4b45-a625-1404e9901f00 | signoff | AUTHORITY HOLDPOINT
2cc24730-437d-4610-b9b5-7007dd4b67cd | checkpoint | 1.4.3 - Weathering Resistance
7963aa7f-a2d0-5f04-a30e-e5d8300a2172 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
5553837d-fa01-5a2c-a407-cd0e63779f7d | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, CA or CB
cf9f04a0-2234-541c-9f74-20aa95d8a8a8 | note | Standard / Specification - NZS4407, Test 3.11, TCC-IDC-IT-4.7.1
7676fee1-ad89-5404-812e-b791ada849da | note | Verifying Document - IANZ Accredited Report
bfd050a7-4aeb-546b-9105-db3ec72c82f4 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
feaea986-7515-5f5c-ab65-e53411c00ecb | note | ○ Results to Engineer 2 wks before importing
c3475f99-7b2c-5ceb-b50f-1c647996354e | note | Verification Activity: Activity - HP
8847b600-33b0-5531-8cbe-dd03eff96959 | note | Verification Activity: By - ENG
7df6267e-a2fb-4d12-ba56-cabbadd6c310 | signoff | AUTHORITY HOLDPOINT
cdc4b49c-2599-46e0-97fa-8cfab2d6bd39 | checkpoint | 1.5.1 - Particle Size Distribution
a7a6e8cd-51b3-5d21-b411-3c878f6771f8 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
2f460500-eb2d-5a23-af7d-19d63ef0518f | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
8f9a6c3a-701a-5a6c-948a-f28fc30ddd31 | note | 63.0mm ¦¦ 100% passing
17ed7b4c-33f1-5c04-812d-d221c753a42c | note | 37.5mm ¦¦ 68-90% passing
8be897ec-95db-58fb-ae9c-aaaf1789484e | note | 19.0mm ¦¦ 42-76% passing
d49a3e6f-b807-58a0-a13b-4b8214a2587f | note | 9.5mm ¦¦ 26-58% passing
7de4f75a-74d2-57b3-b92a-8d19f675eceb | note | 4.75mm ¦¦ 16-44% passing
c19491a5-60b4-54a2-bc2b-f725d3dff5f8 | note | 2.36mm ¦¦ 10-33% passing
84e79dc1-4191-5b8e-bcab-97fdb6d1e4b7 | note | 1.18mm ¦¦ 6-24% passing
2d15d775-4a43-516a-b0b6-4784fdf3378c | note | 0.425mm ¦¦ 3-14% passing
d7f2339b-e738-572c-a6f7-5dbe44b4b935 | note | 0.075mm ¦¦ 1-6% passing
5f7623b3-a91b-52cf-9309-c16f373a7877 | note | Standard / Specification - NZS4407, Test 3.8.1, TCC-IDC-IT-4.7.2
1dac607c-c0bc-5007-a694-8813e4ed586f | note | Verifying Document - IANZ Accredited Report
b45c0ab6-1a5a-5a52-8e46-c80e33ba9173 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
a2f4caaa-dd91-5e6a-86f1-7f0418c70ab7 | note | ○ 0-400 - 2 tests
5f2d7577-ad1d-59ec-8907-8bac4a5d2869 | note | ○ 400-1,500 - 3 tests
3436602f-eee6-54fd-b079-59fb58eec085 | note | ○ 1,500-4,000 - 4 tests
079eeb04-ae05-5214-8b39-a3ea8108db0f | note | ○ >4,000 - 1 test for each additional 1,000m3
585f9655-b754-52da-8a7c-e71b61185c6e | note | – Results to Engineer 2 wks before importing
bb067c82-a16a-5cbd-b3fa-f47738a8a4c3 | note | Verification Activity: Activity - HP
35fd776f-7ea9-510d-b7be-7755419e8cbc | note | Verification Activity: By - ENG
5012df9b-7677-4bc4-b736-710d93ba3672 | signoff | AUTHORITY HOLDPOINT
825e4eeb-111c-4477-b26e-4be22027c63d | checkpoint | 1.5.2 - Shape Control
2d9788c0-af61-5451-8f3d-ec21fa8a9e1c | note | Detail - Tolerance allowed from approved grading curve (%)
de23e13f-c4fa-5b36-b269-aa74c655ee87 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
0ffcf7bc-6c1c-5cb1-96b2-837158f0ef4d | note | 37.5 – 9.5 ¦¦ 34-50%
bb7ad080-92a4-5288-a95b-4237de55dced | note | 19.0 – 4.75 ¦¦ 18-40%
831b2b1f-a096-56fb-8570-81c27d6f8172 | note | 9.5 – 2.36 ¦¦ 12-32%
5913e682-e57c-5d15-a8d4-b3cc928dac18 | note | 4.75 – 1.18 ¦¦ 6-24%
63f81280-e1c2-5dca-8af2-2bd03bbd3e40 | note | 2.36 – 0.6 ¦¦ 2-20%
7581f39a-3f7b-5b64-9ee2-3244cbc23377 | note | 1.18 – 0.3 ¦¦ 0-15%
53d6b4f1-b4b4-52a8-b133-51bd53c5f82f | note | 0.6 – 0.15 ¦¦ 0-12%
ae01406f-7786-57f4-b445-a7bb9182bbf4 | note | Standard / Specification - TCC-IDC IT-4.7.2
ffcf5a6f-cc10-55b8-a60c-9a64d5e5b126 | note | Verifying Document - IANZ Accredited Report
373a33b1-bf50-541a-a8b7-abdd9a93d3de | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
afc1d4ef-fc53-551c-ad69-a7d41a0fe8fc | note | ○ 0-400 - 2 tests
56650446-3317-583b-b0be-422bf179ca79 | note | ○ 400-1,500 - 3 tests
1f2e3370-588d-5633-859a-8b59fccb8dca | note | ○ 1,500-4,000 - 4 tests
590661ab-bf8c-5592-8d8d-9a307ebd8c2d | note | ○ >4,000 - 1 test for each additional 1,000m3
f511905e-e91b-5510-bd09-04fbcfc2785d | note | – Results to Engineer 2 wks before importing
49e13647-768d-59c8-88ba-8d614f967616 | note | Verification Activity: Activity - HP
e5726cde-808e-59d7-904a-69b777cde02d | note | Verification Activity: By - ENG
5f922ce6-26c2-4a83-aad3-59d0ed2caa73 | signoff | AUTHORITY HOLDPOINT
4f912624-b94c-4157-b64a-27e3830d264b | checkpoint | 1.5.3 - Maximum Dry Density and Optimum Water Content
e8941148-2393-5221-b289-9a85e3f83658 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
c95147ea-1f72-508c-96cb-554cce2e89e1 | note | Acceptance / Conformance Criteria - Report Value Only
90175757-ef46-58e1-b5d4-c2c5800a5099 | note | Standard / Specification - NZS4407, Clause 4.3, TCC-IDC-IT-4.7.1
84246308-0d81-5a7f-aa03-7cc863a756d0 | note | Verifying Document - IANZ Accredited Report
47a61983-bfdf-526e-8ce9-37f2d722719b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
5dd42bc6-d95d-5f6a-a8cb-d70c58c1ce3b | note | ○ Results to Engineer 2 wks before importing
8ecb247c-4607-534a-9c35-073784218b1f | note | Verification Activity: Activity - HP
710cd3de-15b2-59fa-955d-1f77152febc4 | note | Verification Activity: By - ENG
67a4cdb7-3a20-46c2-a72c-eb64878819fa | signoff | AUTHORITY HOLDPOINT
14406d46-9edc-4d5f-a730-4844029fa470 | checkpoint | 1.5.4 - Plasticity Index
1d411290-10b0-5647-9919-087ec0de2b62 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
29855e1c-b102-5c37-ae52-d774d556e1e6 | note | Acceptance / Conformance Criteria - ≤ 8
24f46ae3-ef5f-5b1d-bd59-d4c7251b33bf | note | Standard / Specification - NZS4407:2015, Test 3.4, TCC-IDC-IT-4.7.2
e9012e8a-d899-5d64-b468-6b11a9c7f479 | note | Verifying Document - IANZ Accredited Report
231d5aaa-7c42-5cc9-ad21-0560d27c2ff6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
50e34684-c9bd-5143-8a6d-8192b29fb25e | note | ○ Results to Engineer 2 wks before importing
8b3f9956-02da-5a90-b902-eca726224ed1 | note | Verification Activity: Activity - HP
0c82923a-4106-5dcb-9ea6-fed8831f2e27 | note | Verification Activity: By - ENG
a45a4e20-c1ab-4e6f-89e9-acf876eeaf13 | signoff | AUTHORITY HOLDPOINT
dd60881e-5766-404d-ba64-52151480b0cb | checkpoint | 1.5.4 - Sand Equivalent
392fd4e8-4455-5411-8554-35d31e4a8a22 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent Washing method
73c345db-3eef-517d-9afe-e7ea51d0dcf4 | note | Acceptance / Conformance Criteria - ≥25
5b796f44-5b00-574c-b229-df24ef8f0117 | note | Standard / Specification - NZS4407, Test 3.6, TCC-IDC-IT-4.7.2
a9a4612d-1ef1-56c6-9197-a4966ca73ca2 | note | Verifying Document - IANZ Accredited Report
93715ee2-ce3e-5cc7-a697-b945c5f87831 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
adfcdf4d-bbf6-5be3-ae9c-297603e550b0 | note | ○ Results to Engineer 2 wks before importing
46f19b79-29b3-5d36-a3bf-421d1254d1cd | note | Verification Activity: Activity - HP
6075ea10-0a42-5095-b60d-9008ed70fbf9 | note | Verification Activity: By - ENG
68c39e19-ea06-4bbc-a87d-720d4799d07b | signoff | AUTHORITY HOLDPOINT
47686f5c-fb44-4002-aaab-5ec3948214b4 | checkpoint | 1.5.5 - Accelerated Weathering
9b86e9d0-94ae-502e-946d-1016710e93b0 | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
32d486a5-a8b3-52b5-8bed-1dca56228bb7 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
e1e2b7a0-13c5-5e9a-8790-fecf66f94c16 | note | Standard / Specification - TCC-IDC IT-4.7.2
0c7098ce-491f-5e64-809b-55ad1c874941 | note | Verifying Document - IANZ Accredited Report
c7dcfb59-b688-50a5-8c3f-1e60561a734f | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
3b0385e0-f570-58bb-af1f-93e9f6c0f252 | note | ○ 0-400 - 2 tests
69b2bf43-1109-561f-84d4-1a378cce1703 | note | ○ 400-1,500 - 3 tests
9031a666-9ff0-505e-ba0c-5b058af15d44 | note | ○ 1,500-4,000 - 4 tests
2a3062f8-4594-5510-8075-38bfc8c626cd | note | ○ >4,000 - 1 test for each additional 1,000m3
0d68beb5-b28a-5d36-985a-8cebdfe81351 | note | – Results to Engineer 2 wks before importing
bc13ca84-a2fe-5c0d-85c4-7e3b045d97f4 | note | Verification Activity: Activity - HP
4a17a5ec-4501-5e2f-945e-e906a923d575 | note | Verification Activity: By - ENG
28c621ad-8814-412c-960d-96c43846dfc9 | signoff | AUTHORITY HOLDPOINT
433b1c56-e862-48b9-89ab-fed70a96fd9e | section | SECTION 2 – Subgrade Handover from Earthworks
04c777fb-1ae1-415e-ba83-4e039e29ba8d | checkpoint | 2.1 - QA Submission
89607dc6-7ecf-56bf-b5c3-44efd2fe951d | note | Detail - Submit all Subgrade QA before proceeding with next pavement layer
5d73d17b-1fee-5ca7-9fe1-4f6e0e2a377e | note | Acceptance / Conformance Criteria - Engineers Approval
7bf01af2-149b-55b6-8b87-62afb7eeea56 | note | Standard / Specification - Appendix V
af364ab9-2366-5390-a1c0-48f9fb0d698c | note | Verifying Document - Conqa Siggnoff
d7fa44a2-57e8-5494-b2b5-2135197605b5 | note | Testing Quantity Required (based from schedule qtys) - Once
00d0c2d7-a9fa-58e2-a346-52e137d6c83f | note | Verification Activity: Activity - HP
07838230-e235-53a0-ae72-4313d5cbb575 | note | Verification Activity: By - ENG
1bce2fd0-39a2-4268-a3e8-032ee43402b8 | signoff | AUTHORITY HOLDPOINT
496f7a5c-52b4-4ceb-9828-d3522dd69f8b | section | SECTION 3 – PLACEMENT OF GEOGRID AND GEOTEXTILE FABRIC
fb0a2d77-9650-4a31-a409-6cc4f243688b | checkpoint | 3.1.1 - Placement of Geotextile Fabric
6fc7deac-bb07-531f-abe2-fc6b9f4d5a4e | note | Detail - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
d9749664-8e1d-5e1e-aac1-0991b565c289 | note | Acceptance / Conformance Criteria - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
84dfbeca-0563-5e89-a2e4-3ad5a82cfde3 | note | Standard / Specification - NTC0097, 232735.02-WSP-DR-PVS-0401-REV4
b424eef6-67bb-5577-935c-4dd5acf6f63e | note | Verifying Document - Visual Inspection and photos
e2c5735b-bbf7-55df-8e83-4f67bfc2375d | note | Testing Quantity Required (based from schedule qtys) - During construction
6286cf63-7854-56ea-9bd6-3fa548fafe3b | note | Verification Activity: Activity - W
c4945cd1-20ec-5403-a2d7-bf774abc281c | note | Verification Activity: By - ENG
ac85a80a-21c1-4033-a43d-6d1d9971dc38 | checkpoint | 3.1.2 - Onsite Check by Engineer on Geogrid
123472c8-aaf7-557a-a498-c42fa6d27316 | note | Detail - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
59079e6d-0473-50c9-84ae-3b2a6e026fcc | note | Acceptance / Conformance Criteria - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
7e492011-d8f0-573f-bbf8-3f9000a92b70 | note | Standard / Specification - NTC0100, 232735.02-WSP-DR-PVS-0401-REV4
43e847e2-5cae-5a3f-906c-fa6800b4809e | note | Verifying Document - Visual Inspection and photos
6373ea9b-a0db-585f-8daf-8a7151879f7c | note | Testing Quantity Required (based from schedule qtys) - During construction
ad8693a5-6b53-5eba-a5d8-07ca563c6435 | note | Verification Activity: Activity - HP
adcecb92-4b4e-563f-959b-e416bd1b561c | note | Verification Activity: By - ENG
2a0b78a7-a928-4c3a-ad6e-cdcf8f0b2a29 | signoff | AUTHORITY HOLDPOINT
8ee08b69-926e-47ce-a03b-8c9261ed9674 | checkpoint | 3.1.3 - Placement of Geogrid
8745f8cb-9903-5fe4-b6ea-7438982f27bc | note | Detail - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
ee58a103-0a6f-5277-98c7-297b9ec75fc4 | note | Acceptance / Conformance Criteria - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
2d2e3c76-f6f2-59c2-a75b-654adcec1b31 | note | Standard / Specification - NTC0100, 232735.02-WSP-DR-PVS-0401-REV4
2dffa7d7-e32c-5ac1-a80b-f39f05470c40 | note | Verifying Document - Visual Inspection and photos
ab83141b-804f-5a9f-bbae-71b12cc7bfbf | note | Testing Quantity Required (based from schedule qtys) - During construction
9f4b1f04-14ba-533f-8a3c-3805cb932f4a | note | Verification Activity: Activity - W
61d70b14-32d6-5f9c-8ec5-5f2064ba385b | note | Verification Activity: By - ENG
70fd561c-fd70-4b42-a7b4-a285e7001d6d | section | SECTION 4 - PAVEMENT TYPE 4
71588cfd-70d7-4f8f-9c4e-e7b564f515d3 | checkpoint | 4.1.1 - Plateau Density Test
975a2552-a795-5a74-8fad-e4b803758c62 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
c81573c5-a722-5b2c-a1a8-407df84d8438 | note | Acceptance / Conformance Criteria - Plateau Density Report
4e9fd173-9d52-59b0-aee3-ae54fa32c943 | note | Standard / Specification - TNZM/03, TCC IDC IT-4.7, AS per NTC 349
218a02cf-0091-5dd2-b401-f7dbd1cf4c26 | note | Verifying Document - IANZ Accredited Report
9581c7cd-7caf-5e70-9dd7-e07589083d52 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
0e859cf2-e93d-5a1c-b0b8-e1d76e17503c | note | Verification Activity: Activity - I
378f0562-714c-5ede-b58e-7840758f70b5 | note | Verification Activity: By - SE
d165e6ab-3fbb-4426-b8e2-915c4757261e | checkpoint | 4.1.2 - 3m Straight Edge
8a380894-2653-5372-9964-6d8804ed59f1 | note | Detail - Formation check to ensure surface is smooth
072b4b27-6bdf-5f60-97e6-866be595dce1 | note | Acceptance / Conformance Criteria - +/- 10mm
b4897be6-4aa0-507d-9942-61665b4a51f1 | note | Standard / Specification - TNZM/03, TCC IDC IT-4.7, AS per NTC 350
ccbff6ec-9a5d-5afc-bbe1-28ee90375d34 | note | Verifying Document - Check Sheet
a43332c8-f175-5eb2-852b-5da3efc71496 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
1bb2ea7a-330f-53b7-a879-b15a66413e4b | note | Verification Activity: Activity - I
3801fd97-86cd-54b3-be5d-c123f6e504b9 | note | Verification Activity: By - SE
942bc342-75cf-44f2-8b90-5af8023ba9af | checkpoint | 4.1.3 - Stringlines or equivalent
0ae03fe7-2c16-5c87-9192-9439294ea940 | note | Detail - Stringlines or equivalent to check finished height of surface
21c21486-fb09-556f-8924-71b42d72fe87 | note | Acceptance / Conformance Criteria - -15mm + 0mm
4f292b2a-80d0-50e2-9dbe-e14c0718fa81 | note | Standard / Specification - TNZM/03, TCC IDC IT-4.7, AS per NTC 351
d49b4207-a464-52ab-97d9-82f04b1d36f2 | note | Verifying Document - Check Sheet
5d69bf4b-194f-5e4a-bf2b-d0f459bd4e00 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
49020674-eb20-57ea-ba10-36fe1ae66c23 | note | ○ 1 set = 5 tests
fd011753-47ee-556e-9398-e9cf5065730e | note | Verification Activity: Activity - I
c2d79b48-185d-54af-ae1a-a62e1b1f792f | note | Verification Activity: By - SE
0ebf5a1e-b802-44e0-b2b9-6e2b0c25e411 | checkpoint | 4.1.4 - Compaction - NDM
32e3d4dc-2b02-5247-9b22-3ba44dd95fe9 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
fe53b468-81c2-5355-b260-26dc55e6bc99 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
a0eaf3d3-11f8-5179-b30d-767bc36dadff | note | ○ Min >92% of MDD
05dd824e-067b-5afa-ad91-7027b0a3be47 | note | Standard / Specification - TNZM/03, TCC IDC IT-4.7, AS per NTC 352
febc497c-ab30-5231-9fc5-c6b6ad3e3791 | note | Verifying Document - IANZ Accredited Report
eef39295-dfd5-5fb2-b71a-760d6cdba7cd | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
a86a0f83-d9c8-57b7-8af0-b68ce39cdab1 | note | Verification Activity: Activity - I
3f9347e2-c057-597f-9662-79d8f32d86ca | note | Verification Activity: By - SE
45ab02e2-8fda-48c3-ac15-6573220429c0 | checkpoint | 4.1.5 - Benkelmen Beam
7fa4e28f-96b3-5a10-bee0-dadb4efe5100 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
e626116d-8228-5730-93bd-cf274cae513c | note | Acceptance / Conformance Criteria - 90th Percentile: 2.1mm
8c8d6cc7-97d6-5483-b3c5-e508ada714dd | note | ○ Maximum: 2.62mm
222c4140-6952-5396-9898-1985d4411fe8 | note | Standard / Specification - PS 20.14.5, NTC0160
a22a7301-75ee-52ab-9f01-df20851f8841 | note | Verifying Document - Test Report
23085760-848d-5a3e-9598-694ed2cfe686 | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
8324726d-3d13-54e5-9481-3033789a0dfc | note | Verification Activity: Activity - HP
9d40cc8e-2693-579d-b408-2f68dfb6d708 | note | Verification Activity: By - ENG
b82837bd-6e6a-44fb-8788-f49d7cdf6e9a | signoff | AUTHORITY HOLDPOINT
8e67cf0c-047d-42de-a4ca-15bb561a79e1 | checkpoint | 4.2.1 - QA Submission
6e9e8acb-3f17-5e23-928a-8cd42e48c6d8 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
78dffad9-da9e-5d06-bf5d-2f0916d37696 | note | Acceptance / Conformance Criteria - Engineers Approval
7e93e8f7-6739-5d4e-bfd5-550c2e23b4da | note | Standard / Specification - Appendix V
c05abeac-2a31-52d2-b944-e7eac2d21f5b | note | Verifying Document - All test reports
2b8cb33f-2494-5552-b663-8d7cc9e359c8 | note | ○ Material Test Results
2e53223d-63e8-5560-b477-650bc21692ae | note | ○ Laboratory MDD
5e7c1d64-ca72-52e2-a3dd-480ab64f5359 | note | ○ NDM results
22922abd-1696-548f-bcd4-0ea4c850f44c | note | ○ Proof Roll
37a31f19-b86f-5550-90c9-ed70922f6ae3 | note | Testing Quantity Required (based from schedule qtys) - Once
523313ce-354d-5ea4-9c77-267f3866a4c9 | note | Verification Activity: Activity - HP
8cc70def-54f9-5f0d-ac66-d411b24b1060 | note | Verification Activity: By - ENG
200d504d-e300-4d32-8a72-fd36cf70e865 | signoff | AUTHORITY HOLDPOINT
dcad0c62-48db-481d-abd1-d38c2bc58b7c | checkpoint | 4.3.1 - Plateau Density Test
efe3343b-24c6-516f-8bfc-852af0ca0932 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
bd397227-2ce1-52c1-ab96-1ad168c620bc | note | Acceptance / Conformance Criteria - Plateau Density Report
279a235c-6178-5185-bd8e-bc889ee0f00a | note | Standard / Specification - NZTA B/02 7.5 (a)
493a16a9-c49f-590d-9570-318f2a8b08f2 | note | Verifying Document - IANZ Accredited Report
383f27b5-89f1-5f64-ade5-b8c2acf9510d | note | Testing Quantity Required (based from schedule qtys) - 1 Test
ed209643-0eeb-55ca-95a8-e3d5c92346b6 | note | Verification Activity: Activity - I
320c6f1e-d38e-57c6-9e49-f124a82ae666 | note | Verification Activity: By - SE
b4dbfe1b-5ac7-4b57-b87d-a0901e048c22 | checkpoint | 4.3.2 - 3m Straight Edge
981e4234-552f-5783-a606-bb19d57f30c8 | note | Detail - Formation check to ensure surface is smooth
dfa4d8cd-3cce-5caf-9fe4-3ecd3497f87a | note | Acceptance / Conformance Criteria - +/- 10mm
12ce862c-cb33-5bdd-b889-3dca815da01f | note | Standard / Specification - TNZ B/2 7.7
c854423f-c04c-5cf9-af1e-96547485b377 | note | Verifying Document - Check Sheet
d1e153ca-62f5-5e3d-8d41-7d0825fdf114 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
42e5467c-301f-5643-940f-63632ddb83d3 | note | Verification Activity: Activity - I
f2517107-a5b9-53cf-9ad3-04141c6a301d | note | Verification Activity: By - SE
b81fb5c5-89e2-4e51-8467-5c1c896afd64 | checkpoint | 4.3.3 - Stringlines or equivalent
134b0267-766f-5510-a61e-2f4f24caaa4c | note | Detail - Stringlines or equivalent to check finished height of surface
6f6b390a-e985-50d9-b0f1-59f3208cb93d | note | Acceptance / Conformance Criteria - -15mm + 0mm
83ba290c-db9a-5e29-8b20-e0c4f0eafc8e | note | Standard / Specification - NZTA B/02 5.1
edf01194-baeb-5be4-b114-86f2de6b480e | note | Verifying Document - Check Sheet
be66e2f6-a5d8-5601-88a6-9eb2f7c66eb0 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
f43b55f5-2b65-53ee-8513-ee32a7907441 | note | ○ 1 set = 5 tests
8e358138-68ba-55cd-831f-64bd189ef105 | note | Verification Activity: Activity - I
0f46cdea-370e-5ad4-8991-603ad863de82 | note | Verification Activity: By - SE
1e94f6d2-4255-495e-9720-ab3183e73cbd | checkpoint | 4.3.4 - Compaction - NDM
48d5157d-1a6f-56c6-998f-4e31b3b4222e | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
be32f6b4-3951-5f6b-a316-8b4f9ed0e741 | note | Acceptance / Conformance Criteria - Ave >98% of MDD
5ad60028-33b6-5f2f-849a-b252230c5a95 | note | ○ Min >95% of MDD
32ccf7c0-a537-5efd-a924-ea856101afad | note | Standard / Specification - NZTA B/02 7.6
4ca70113-9f6f-524b-a1e5-faee1c1ebccc | note | Verifying Document - IANZ Accredited Report
54d66dd5-952f-5210-a2da-3412af92700c | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
d1160886-cc10-5c44-9f41-b8044c0a91fe | note | Verification Activity: Activity - I
2fae0654-1cf1-5917-a3d6-5e58d241b907 | note | Verification Activity: By - SE
7cb1b6ac-489a-4f5d-9e09-292eab7a60c6 | checkpoint | 4.3.5 - Benkelmen Beam
7e8ead5e-e267-51bf-b131-081a4e2b12a2 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
5ce1afbc-283e-56bc-87e0-b54d58da6eae | note | Acceptance / Conformance Criteria - 90th Percentile: 1.44mm
f094ca57-c6bb-5b85-85c8-41d69af092eb | note | ○ Maximum: 1.78mm
25596709-cdc4-5511-9f97-87682ec92d25 | note | Standard / Specification - PS 20.14.5, NTC0160
a641f2c0-b346-5dec-bea4-ebf0ec6061b6 | note | Verifying Document - Test Report
2425281a-c314-5647-8331-c5855ba6244e | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
9800854c-1079-5e53-8f7c-4970a0e8e0c0 | note | Verification Activity: Activity - HP
e3cfc268-5926-541f-ad80-57a3b5491b1d | note | Verification Activity: By - ENG
cb45900f-ccb8-4964-bbac-eefc02b8bcd0 | signoff | AUTHORITY HOLDPOINT
4688b906-c4d5-4622-9758-4274b14604b9 | section | SECTION 5 – AS-BUILTS / REDPEN MARKUPS
46e1b36c-f6e3-4318-88cd-601db178fa09 | checkpoint | 5.1 - As-Builts/ Red pen markup
82788c85-1868-564c-90da-faff08c9554b | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work
e88f7592-94b2-5a42-9358-e7717429d2ed | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
469c040c-82ce-5ba6-85f3-73925bca6219 | note | Standard / Specification - PS 16.7.6
82851569-aaf4-5df2-a1fe-655bc353bd34 | note | Verifying Document - Red pen markups
95433199-52c3-5df7-a32e-2f1764075369 | note | Testing Quantity Required (based from schedule qtys) - During construction
b96ca1b7-9d61-5981-b433-007b45d1a356 | note | Verification Activity: Activity - D
8f150bc3-317f-52ae-ba4e-2018e48b81cd | note | Verification Activity: By - SV/SE
ca5c775a-e52d-4504-be17-9edd0ba7d660 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
7dc4a7f6-5cd8-5514-96c5-80f795813b60 | textbox | Contractor's Rep Name:
edb80d48-034d-5bed-863a-93cec7ec4781 | textbox | Engineer's Rep. Name:
9812344b-94b4-57b6-8ac0-5ffc394f2fc2 | date | Date:
4ff01815-d338-4c9c-994c-3070dcfdb0ec | signoff | Add Signature
a51b89be-344b-46eb-99dd-51cc5ad4aa7a | checklist | DN1210-SP2-006-002 - ITP Northern Access Road Carpark Pavement 5 Rev 0 | itp | DN1210-SP2-006-002 - ITP Northern Access Road Carpark Pavement 5
cad3efe5-ac1d-483b-b32f-0cbd6332e3eb | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
8393e1e8-b44a-4063-8b8a-773e0a28e7f3 | checkpoint | 1.1.1 - Crushing Resistance
326fa685-842f-5a57-90dc-a88cbcad82de | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
83003bd7-82ed-549b-afce-11a272f4a684 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
2e4a7b2d-7278-5135-bc25-c54f9f79766c | note | Standard / Specification - TCC-IDC IT-4.7.1 table 4.4
870a5289-7da3-52d4-8cac-b7c75a63378c | note | Verifying Document - IANZ Accredited Report
aabfa245-e351-5aba-b399-7f2fc1079807 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
177ad0a0-cdaf-5ada-a2a0-5a2d0dce71ba | note | ○ Results to Engineer 2 wks before importing
384fd764-5a1a-5706-8345-e82f664e8fda | note | Verification Activity: Activity - HP
27d1af91-17c5-5117-a85f-c15568e9e1df | note | Verification Activity: By - ENG
b170a773-fbb2-494d-9854-0d4bbdc87520 | signoff | AUTHORITY HOLDPOINT
69f765f0-0eec-47e7-80e9-8359fc98d751 | checkpoint | 1.1.2 - Soaked CBR
d0ebd9ac-5937-5277-bf88-b8585e1d0e90 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
6a7bdc46-d6a7-54dd-b096-3bfc56e8bfc7 | note | Acceptance / Conformance Criteria - ≥ 60%
3098a1d1-8866-5515-8c00-90ca9ed86643 | note | Standard / Specification - TCC-IDC IT-4.7.1 table 4.4
e46dd737-ef21-5044-9ea6-fc746e3e8855 | note | Verifying Document - IANZ Accredited Report
c03321a1-b1d7-521b-ac13-877c6773bc5c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
89c31558-7371-5991-b69f-eba67620b1a3 | note | ○ Results to Engineer 2 wks before importing
229a5abc-92ac-5668-b315-4d6d1348f368 | note | Verification Activity: Activity - HP
e0498dea-9aa5-5968-b554-147884ff75af | note | Verification Activity: By - ENG
a00ee74e-932e-4a87-bb40-2380aa5bedbd | signoff | AUTHORITY HOLDPOINT
da98dc48-4e53-46ac-afdb-52b06a845091 | checkpoint | 1.1.3 - Weathering Resistance
ea46f1ef-e2de-5c73-a68f-5e2445e2c05a | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
a960deba-0f53-5076-8489-192d235e2359 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
e0bfd164-bf05-5f52-98d5-2a362589f9da | note | Standard / Specification - TCC-IDC IT-4.7.1 table 4.4
4f6511f4-1b0d-5819-98ea-61865c73fec3 | note | Verifying Document - IANZ Accredited Report
d7ac745b-c072-527d-a401-5314b4038ef8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
ebcdc8a4-9238-5f18-95a7-3e0077b351d9 | note | ○ Results to Engineer 2 wks before importing
808acf8a-79dc-5be3-8998-d1e09f288251 | note | Verification Activity: Activity - HP
838f1058-1c38-5eb4-807c-8aa83f6c3c1d | note | Verification Activity: By - ENG
e567df0c-1f98-4a4f-9824-6de74bada8fa | signoff | AUTHORITY HOLDPOINT
7757e49d-efa2-43b8-847c-c4f8437e3eed | checkpoint | 1.2.1 - Particle Size Distribution
68846155-34b2-501c-a3e4-4478cf84c3a2 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
1725e0f5-f1e6-5e61-ac31-79e19373526c | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
78f1d0e0-6218-59f7-a566-e561d8adc778 | note | 63.0mm ¦¦ 100% passing
8155382c-1c8c-5f48-a3c1-b2c2e6c4315e | note | 37.5mm ¦¦ 55-85% passing
b53393b8-8815-57b2-8abc-0c3ed6cae30b | note | 19.0mm ¦¦ 33-65% passing
a7fbc912-eb99-592e-9b9b-38523ac7cf7a | note | 9.5mm ¦¦ 20-50% passing
762b9f37-2d31-5713-b3c6-710bceff40d3 | note | 4.75mm ¦¦ 10-36% passing
bca38538-e687-5354-8f30-52e4215cd8c0 | note | 2.36mm ¦¦ 5-27% passing
431d8d56-35e4-5a1b-aae7-11eac119c101 | note | 1.18mm ¦¦ 2-20% passing
4db21689-0110-5494-b079-3546d1f96577 | note | 0.425mm ¦¦ 1-13% passing
83428b02-556c-5255-bfee-7264254f9606 | note | 0.075mm ¦¦ 6% max passing
b881cfbb-4672-57d5-b490-11f88e138779 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
34c9c5d6-f5ff-5e09-9bf6-f537dacc63ee | note | Verifying Document - IANZ Accredited Report
34b9d5bf-6c68-570a-85fa-de6c37003177 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
b577d16d-f03e-5556-971a-8c53c2a72669 | note | ○ 0-400 - 2 tests
9edb3410-bcc5-5f5a-b65b-98b00ddd2e3a | note | ○ 400-1,500 - 3 tests
a0a5f456-79b5-5ebf-85b3-b9dcd6b89349 | note | ○ 1,500-4,000 - 4 tests
3a4aaca7-72d0-54be-b13b-e0a076d189f9 | note | ○ >4,000 - 1 test for each additional 1,000m3
b129cf33-456a-5c69-8e9f-1b348f1c2379 | note | – Results to Engineer 2 wks before importing
2d546961-4e0f-59e2-8a1e-b541756b3e55 | note | Verification Activity: Activity - HP
43ca5d10-537a-5ad7-8201-8be3cd4e8646 | note | Verification Activity: By - ENG
f34c4a46-31b7-40f5-8b39-a9a95035574e | signoff | AUTHORITY HOLDPOINT
14a9738f-4b6b-4f03-b4cc-b696ed0521ae | checkpoint | 1.2.2 - Shape Control
1c751f90-81f0-5d16-a46c-afdf73fdd81d | note | Detail - Tolerance allowed from approved grading curve (%)
ab78043a-6ac1-5edc-a1e7-05f1f69f8211 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
7325135f-94f7-52be-addb-000a21ce8651 | note | 37.5 – 9.5 ¦¦ 34-50%
dcfbf57a-5e7b-53e8-bc65-1889bc7e07a7 | note | 19.0 – 4.75 ¦¦ 18-40%
82273e55-8fd3-5d66-b865-9e42b10f9429 | note | 9.5 – 2.36 ¦¦ 12-32%
ee1de1ce-182d-53f2-89af-d542ab85019a | note | 4.75 – 1.18 ¦¦ 6-24%
c1c89bf1-f840-5f4f-a092-fb7040e33ed7 | note | 2.36 – 0.6 ¦¦ 2-20%
fb7771dc-2674-5e5e-b60f-addb9f8ec1c7 | note | 1.18 – 0.3 ¦¦ 0-15%
e27521e0-c0dd-5f98-a723-a0b985f372f7 | note | 0.6 – 0.15 ¦¦ 0-12%
7b8fcf6f-3577-5da5-ade7-7d7d6eecc1a3 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
887951e3-5cd7-5952-836a-2d5f48a924bf | note | Verifying Document - IANZ Accredited Report
de35a502-c687-58d2-a657-00a291b71c60 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
c8d10c66-f358-5600-a4d2-03286851673a | note | ○ 0-400 - 2 tests
6dac0784-55f6-5762-9ecf-aa4fe8dedf7c | note | ○ 400-1,500 - 3 tests
f32e9df0-8665-540a-9612-7a9c353a06be | note | ○ 1,500-4,000 - 4 tests
fd5df300-8bb2-5ba4-8ea2-16dc202f4ddf | note | ○ >4,000 - 1 test for each additional 1,000m3
3c115ccd-2eed-5ef9-9809-8066c6a6e284 | note | – Results to Engineer 2 wks before importing
0a67ea35-8b54-5f2d-af63-e20ded241868 | note | Verification Activity: Activity - HP
422308fb-ca40-52fb-a2af-30d66ac8c89a | note | Verification Activity: By - ENG
dab34e02-0cea-4318-8396-006e452bfa30 | signoff | AUTHORITY HOLDPOINT
ec5de953-6955-4849-ba99-f075fc3cf8a6 | checkpoint | 1.2.3 - Sand Equivalent
ac68a699-b2eb-5768-bf2e-4ef14d28b069 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
3e8f06b0-bd10-535e-a686-e3cadff99142 | note | Acceptance / Conformance Criteria - ≥ 30
8481bd9e-c4b5-5073-9618-015429d140d3 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
37c9e93b-7157-54dc-9b19-0a3c6a03cec5 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
6032a8ea-a81c-5e08-9a8f-17a2c73a992c | note | ○ 0-400 - 2 tests
73ed2569-b19e-599c-af63-d5939e0aa9a9 | note | ○ 400-1,500 - 3 tests
8f089d8f-8e57-56c7-ac9e-9ee2d9daf6b0 | note | ○ 1,500-4,000 - 4 tests
589fd94d-6ce4-55a6-8b89-0c4e5ee91f61 | note | ○ >4,000 - 1 test for each additional 1,000m3
02b3a721-bca6-5e59-8d9f-ae9bcf6f538e | note | – Results to Engineer 2 wks before importing
804cfcc4-f957-593c-b70c-381b2d5c9c0f | note | Verification Activity: Activity - HP
67faece6-5076-5dfd-9275-5e518a87d144 | note | Verification Activity: By - ENG
728d1693-9bad-4432-8345-e262968db724 | signoff | AUTHORITY HOLDPOINT
4b749037-01b2-491a-98dc-33d3b776cc49 | checkpoint | 1.2.4 - Cone Penetrometer Limit
fcd1cdad-bcd4-554e-85fd-58ef4e7b2e4d | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
50dc572d-0651-558c-bb78-a8144af0424d | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 25
7ac7a21d-2a2d-5d4d-8ed4-6f35601f3a0b | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
0e6650c2-62ca-583f-bd35-27ec437e7ba6 | note | Verifying Document - IANZ Accredited Report
96b1acca-7b56-5d82-b6a3-598694172195 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
2aa9bc26-0af6-566f-a119-570d9b1780c9 | note | ○ 0-400 - 2 tests
b1142e18-82c3-5ab0-83c9-730d1f694c38 | note | ○ 400-1,500 - 3 tests
b51de564-0df1-5381-9b90-f3b487700627 | note | ○ 1,500-4,000 - 4 tests
6092d41f-00db-55bf-8864-d6364332e159 | note | ○ >4,000 - 1 test for each additional 1,000m3
1d697680-d785-5c8c-b1f7-1854901d764f | note | – Results to Engineer 2 wks before importing
8cc5f221-bb1d-57ec-a9ed-0e45931eb57b | note | Verification Activity: Activity - HP
80b67c02-153f-51f9-b41b-436a8615384b | note | Verification Activity: By - ENG
39596708-094c-48cf-9466-7c8ca358e1ea | signoff | AUTHORITY HOLDPOINT
ac860713-b265-493d-81b5-9383440a4c6f | checkpoint | 1.2.5 - Plasticity Index
edcc9828-326e-5b62-b84d-d39df3420fed | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
2a11dffa-9ab4-54d5-b143-9e9480077ad7 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
5f9fcd62-788c-59ae-993d-995ffa98dfeb | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
47f19ab5-196a-5739-a550-90a6f4499d48 | note | Verifying Document - IANZ Accredited Report
489ae581-2d70-5b5a-8382-dca5c7f54444 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
d28a3520-4483-55f3-b7af-32111793a6b4 | note | ○ 0-400 - 2 tests
3b23b1a2-a770-5315-8ae8-07020dcf40ec | note | ○ 400-1,500 - 3 tests
ca80f06d-2fef-537c-b114-93e5a44b906c | note | ○ 1,500-4,000 - 4 tests
02496d85-d22d-54a5-a12e-5ede9c0bc3bb | note | ○ >4,000 - 1 test for each additional 1,000m3
88fb2d44-e4da-505d-9fa5-ad94ef4a8c5a | note | – Results to Engineer 2 wks before importing
d9d79278-b051-543e-a20b-5138804db59f | note | Verification Activity: Activity - HP
8f84259c-68cc-5538-8b04-bbde0cf970c6 | note | Verification Activity: By - ENG
7f7c11be-6208-4b3a-b50f-df84a8ed1a85 | signoff | AUTHORITY HOLDPOINT
05784ba9-5982-43ab-899a-516179ce8366 | checkpoint | 1.2.6 - Accelerated Weathering
1ea2a9af-e26d-550b-90fa-358b1dac2d95 | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
752658e1-10cf-52f8-962e-432b48d9d4f4 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
83ff4b09-552d-5fbf-bcb2-aac8115e0708 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
00684053-9080-526e-b310-d73298e059c5 | note | Verifying Document - IANZ Accredited Report
856bb5c3-bcdb-5848-b005-f0a74ceacb4d | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
a2d7d7de-e8c8-5059-bdce-0d7b3508d95a | note | ○ 0-400 - 2 tests
3fe02db4-55fa-51a6-bfe0-662d74f423df | note | ○ 400-1,500 - 3 tests
cee6fe7f-97b6-5d0f-bef2-fb1e56befccb | note | ○ 1,500-4,000 - 4 tests
91af8616-050b-5f16-84e0-781fd00db5a1 | note | ○ >4,000 - 1 test for each additional 1,000m3
923149a8-aa66-5f5b-b526-1350fcb4628e | note | – Results to Engineer 2 wks before importing
a57661d5-f30a-54e7-9288-d41c9174cde4 | note | Verification Activity: Activity - HP
00ff73ee-6cb4-57f4-91b8-5966a08eca36 | note | Verification Activity: By - ENG
9a52b777-49ec-46e1-b982-b7f9af680c6c | signoff | AUTHORITY HOLDPOINT
c2a92050-e573-4870-a8bc-488f09f89c1d | checkpoint | 1.2.7 - Maximum Dry Density and Optimum Water Content
d6725dc2-9624-55f2-a5c5-913db810079f | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
7861930c-fb1b-53e4-bba9-7c4c866c729f | note | Acceptance / Conformance Criteria - Report Value Only
9f9fd2cb-657a-5e31-946e-de4b05bcb18b | note | Standard / Specification - TCC-IDC IT-4.7.1
97c79612-0243-5aef-b8b0-9bde714602a5 | note | Verifying Document - IANZ Accredited Report
f0886751-ac3e-51bd-90be-d6776a1d7741 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
b6415f87-b4fb-5d10-b885-8ac75506373a | note | ○ Results to Engineer 2 wks before importing
d486da15-dae3-51af-9cab-1e3d6f177216 | note | Verification Activity: Activity - HP
8e9f976f-2597-5906-8541-1f9a4fa594aa | note | Verification Activity: By - ENG
a98ffd38-14b4-4553-86f9-54987e54fc70 | signoff | AUTHORITY HOLDPOINT
d6d77908-3660-4237-99e6-1832056b8c3e | checkpoint | 1.3.1 - Geogrid
acc4d657-1bc7-5fc0-9b15-c11a9c342093 | note | Detail - The Contractor shall submit the full details of the geogrid they propose to use to the Engineer for approval prior to installation.
cb73baef-3658-5bcb-91fb-e04642f00510 | note | Acceptance / Conformance Criteria - Engineers Approval
e6eb6349-ec2c-5574-8abe-efff6b9a489b | note | Standard / Specification - PS 20.5.2, PS 16.5.13
3e6cae1f-a421-55a1-966c-a34c0034c53e | note | Verifying Document - Data Sheets and Approval
55ed5b14-29e2-5195-b5c8-099c7f374c26 | note | Testing Quantity Required (based from schedule qtys) - Once prior to works commencing
35d6f438-60c9-5b06-9d83-b8bf939fbd06 | note | Verification Activity: Activity - HP
5b40582e-af51-52b6-b3f2-60dc1c4e6c1c | note | Verification Activity: By - ENG
d393bb52-b7ce-4d51-b85e-2183dbd1de44 | signoff | AUTHORITY HOLDPOINT
0b72440a-ddd3-4bb5-ad06-ac324135ec69 | checkpoint | 1.3.2 - Geotextile Fabric
dbf4116e-bec5-5d4a-876e-b747871be115 | note | Detail - The Contractor shall submit the full details of the geotextile fabric they propose to use to the Engineer for approval prior to installation.
e2eaf243-e54c-521e-833a-1948aa358673 | note | Acceptance / Conformance Criteria - Engineers Approval
16d041a5-52d1-5451-95a1-8ad15242a00c | note | Standard / Specification - PS 20.5.2, PS 16.5.14
1ce6c546-a092-59b8-b297-935b54292782 | note | Verifying Document - Data Sheets and Approval
a1cb8933-515f-5f69-b803-6469f0077d7c | note | Testing Quantity Required (based from schedule qtys) - Once prior to works commencing
ab54cec3-b7f4-5e0c-8728-8b023543b0a4 | note | Verification Activity: Activity - HP
4c3e3016-09fa-5977-9667-5092d0b40f6a | note | Verification Activity: By - ENG
b20229af-8b7c-4877-8988-7b1b00b96075 | signoff | AUTHORITY HOLDPOINT
595259e8-63d4-44c1-9cee-6f58f7a8bafc | checkpoint | 1.4.1 - Crushing Resistance
4005c560-da95-524c-9a9f-6f9c9b182aa0 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
7a14c588-ad4e-5cda-8241-0136bf505910 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 100kN
1a0e44f4-e3cc-5e66-b08e-711ac320f099 | note | Standard / Specification - NZS4407:2015, Test 3.10, TCC-IDC-IT-4.3.1-4.7.1
b8a878a5-ebfd-5ea7-9b39-f4b540b8faaa | note | Verifying Document - IANZ Accredited Report
20800785-3a16-5aa8-809d-b52d4d220b72 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
a71886e4-4eee-5442-8768-e1b0c57cd411 | note | ○ Results to Engineer 2 wks before importing
24c3adaa-e107-5c68-b052-7cb662c4270b | note | Verification Activity: Activity - HP
f4f19c63-05ee-58ab-8f54-62d908586bd1 | note | Verification Activity: By - ENG
85e785d1-d2ed-4c77-8607-6efef4a89096 | signoff | AUTHORITY HOLDPOINT
3f0b0092-6f2e-4700-8c44-dee477cde64b | checkpoint | 1.4.2 - Soaked CBR
1093c273-7769-5d98-8787-c954423890c1 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
241dd3cc-0baa-509e-bbfb-f97393db66e6 | note | Acceptance / Conformance Criteria - ≥60%
111fde34-3612-5dca-96f0-66e9a5639143 | note | Standard / Specification - NZS4402, Test 6.1.1, TCC-IDC-IT-4.3.1-4.7.1
76f6be1b-9f32-5cf1-a3ac-1bf02ca51fd5 | note | Verifying Document - IANZ Accredited Report
633250ae-fb34-56db-b9f0-e4b3bb806891 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
51f14b3e-55c5-5e33-beac-b3ff79dc2ee7 | note | ○ Results to Engineer 2 wks before importing
e2d482b5-7661-5484-8ab3-a2401fe1e38e | note | Verification Activity: Activity - HP
9a0c131e-f2c5-5163-8952-6f4dcfe1f230 | note | Verification Activity: By - ENG
6a91bb4c-aad0-4163-b66a-b34c3b2efd22 | signoff | AUTHORITY HOLDPOINT
cf3fcb71-6575-49cc-8f63-b2678c65d01f | checkpoint | 1.4.3 - Weathering Resistance
372027a2-929b-5471-a7e5-aebcf5ec2904 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
3ed768df-bb55-58a4-ae7b-5e1d15ccf713 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, CA or CB
a6018029-6be9-5d56-b50b-df7d99eca850 | note | Standard / Specification - NZS4407, Test 3.11, TCC-IDC-IT-4.7.1
134d678a-4312-5483-90e9-a0cee074a6f1 | note | Verifying Document - IANZ Accredited Report
8d77cd72-ee08-5c92-8412-c9b0bea75c93 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
91aaf19f-16f9-5456-9ac8-288df9ed1e91 | note | ○ Results to Engineer 2 wks before importing
960875d9-bede-59c0-ac75-a08e264c25cd | note | Verification Activity: Activity - HP
bd8cae47-8d7f-57e8-a5ac-e4ddc3270bff | note | Verification Activity: By - ENG
b0d12d6d-0c37-42d4-a745-b1ff76565913 | signoff | AUTHORITY HOLDPOINT
6e8411c9-096b-4983-ad89-5418e3537943 | checkpoint | 1.5.1 - Particle Size Distribution
55b50ef3-e6bb-51eb-b6d9-525d71c99c24 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
e57053c0-7a65-5770-b525-01a5ad47e913 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
b6a08fd0-09af-594e-8421-99cf9f46f09f | note | 63.0mm ¦¦ 100% passing
0b4b055e-1548-553f-a882-5fa43728838d | note | 37.5mm ¦¦ 68-90% passing
e110ea53-7f0d-5aaa-890c-c4266c485f68 | note | 19.0mm ¦¦ 42-76% passing
a467093a-2def-59b8-9141-d9b858764606 | note | 9.5mm ¦¦ 26-58% passing
0d90d3fd-9305-58d1-8b10-3e2caf5fc01f | note | 4.75mm ¦¦ 16-44% passing
2c3c4d95-fb87-581f-b440-cd7294376c42 | note | 2.36mm ¦¦ 10-33% passing
aef7319a-722b-5a04-974d-b6b9c37840a9 | note | 1.18mm ¦¦ 6-24% passing
a26e7a31-a717-5d64-b999-fe4046eaf84e | note | 0.425mm ¦¦ 3-14% passing
7395b06c-0c01-52d7-985b-af5bd1d91a32 | note | 0.075mm ¦¦ 1-6% passing
0600b651-e3fc-520f-9c45-ae9c02cd7a69 | note | Standard / Specification - NZS4407, Test 3.8.1, TCC-IDC-IT-4.7.2
83572ee3-b1c3-5d56-b013-d110def6fcab | note | Verifying Document - IANZ Accredited Report
09fb8358-f33b-549c-90bd-8dd339562729 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
d9b27b26-4869-5bd3-b49c-5baf8cdd81c6 | note | ○ 0-400 - 2 tests
ec9c6e37-624f-5eb6-a5f6-718bdce6e76a | note | ○ 400-1,500 - 3 tests
46900bc9-75be-573c-b179-10684445162b | note | ○ 1,500-4,000 - 4 tests
fafd7b54-afe0-5bfa-a558-bcb7b880d31f | note | ○ >4,000 - 1 test for each additional 1,000m3
c1732627-0f7a-57ac-a3fc-46611471d941 | note | – Results to Engineer 2 wks before importing
7d55c212-73ec-5971-83d2-f6814a2704d9 | note | Verification Activity: Activity - HP
b00c14e3-dfca-5518-bb58-e8caf89e9280 | note | Verification Activity: By - ENG
ee3f084a-d421-4ecd-8685-62b38f22c31d | signoff | AUTHORITY HOLDPOINT
679f1dab-c053-4997-83af-c39b06dbf248 | checkpoint | 1.5.2 - Shape Control
8233a4f7-219d-52cf-abf6-51d40496571c | note | Detail - Tolerance allowed from approved grading curve (%)
1ac40a57-a598-579a-a2ac-ac680ced5c4e | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
78c43f47-bd33-5f02-bd6d-7754cf203ef1 | note | 37.5 – 9.5 ¦¦ 34-50%
69b35460-1a51-5c19-8543-a11085e5fe32 | note | 19.0 – 4.75 ¦¦ 18-40%
b4fbfd8b-b4fa-5186-9adf-f0b8e85fc4cc | note | 9.5 – 2.36 ¦¦ 12-32%
00668c32-fb82-5a7a-9f73-14a656052fa1 | note | 4.75 – 1.18 ¦¦ 6-24%
a64772ea-49d0-51f6-a190-d7ed313e026d | note | 2.36 – 0.6 ¦¦ 2-20%
c213d8c3-b3a2-5b1f-ab10-bf8e97c49c21 | note | 1.18 – 0.3 ¦¦ 0-15%
3ef501a4-9383-5d98-a12e-6e98cadb60ad | note | 0.6 – 0.15 ¦¦ 0-12%
fc81b1c7-376c-58aa-9a78-23211c58b139 | note | Standard / Specification - TCC-IDC IT-4.7.2
333d2820-6efa-5ccf-9b52-34f33e3ba04c | note | Verifying Document - IANZ Accredited Report
9bb80fbe-7c17-5126-bb98-e3b751275336 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
deacb8be-7d47-5850-9728-530ca7205395 | note | ○ 0-400 - 2 tests
e5a80065-c901-50ed-bb14-043bbd0ece88 | note | ○ 400-1,500 - 3 tests
dd594f50-097f-5533-a109-02c4466be502 | note | ○ 1,500-4,000 - 4 tests
a444df45-a1c1-54c0-ad47-cb5426b4d1f8 | note | ○ >4,000 - 1 test for each additional 1,000m3
16a5106d-d038-5812-b847-b2723fdfebe8 | note | – Results to Engineer 2 wks before importing
b8beeb6a-8967-5ff0-8cb5-c41322570e7e | note | Verification Activity: Activity - HP
b6a019d2-46fb-50d8-9f76-25e83339a529 | note | Verification Activity: By - ENG
a5c6bb0b-e464-4e25-9be1-8a8e424954de | signoff | AUTHORITY HOLDPOINT
e2e51ef4-5fe9-4106-a2de-c5947d1b2da0 | checkpoint | 1.5.3 - Maximum Dry Density and Optimum Water Content
361149a5-6718-576e-b6eb-db2d501e118d | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
bc5aa756-2516-5c06-b625-3e3250542c46 | note | Acceptance / Conformance Criteria - Report Value Only
4ce97dbb-98b2-5f9b-bf5f-c4b4f0f6fa25 | note | Standard / Specification - NZS4407, Clause 4.3, TCC-IDC-IT-4.7.1
89d3bcab-96af-59ca-9a6e-9b01a0dc8d61 | note | Verifying Document - IANZ Accredited Report
e1bc9d65-a5ec-55ad-8adc-dfde89010dea | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
7d3e2d84-cd72-5a0f-bf7c-b04b558ed2b1 | note | ○ Results to Engineer 2 wks before importing
47f4e4a7-d1d2-584b-9acc-dc55d57c0662 | note | Verification Activity: Activity - HP
5f0d670a-7434-5534-b951-2c865679899e | note | Verification Activity: By - ENG
2d2139c9-419b-420e-869f-6886c467f049 | signoff | AUTHORITY HOLDPOINT
83ab0aa1-0a7d-47f6-a605-2e28a4e43ebf | checkpoint | 1.5.4 - Plasticity Index
4949b199-b28d-52d6-81bf-aa0d27aaa7a1 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
effa338e-5935-5ac2-be67-0aa8fc9d4ba6 | note | Acceptance / Conformance Criteria - ≤ 8
5ee359a4-70db-528f-8496-795bc5ccf432 | note | Standard / Specification - NZS4407:2015, Test 3.4, TCC-IDC-IT-4.7.2
4729c07d-7dbf-52a5-9bf0-a85608de776d | note | Verifying Document - IANZ Accredited Report
4531abb2-d443-5bcc-b02e-e764272bb5e4 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
46776de0-8c11-5755-98c6-02be2cfab524 | note | ○ Results to Engineer 2 wks before importing
964300d8-813b-58e2-899a-77c51399a287 | note | Verification Activity: Activity - HP
62e826b4-15a1-542b-b377-5a64dc7fc6ad | note | Verification Activity: By - ENG
4ebad269-9b9c-40ce-9d40-0e23a79754a3 | signoff | AUTHORITY HOLDPOINT
e71f95ea-928a-4d2a-8a39-c3d9bb5d3421 | checkpoint | 1.5.4 - Sand Equivalent
c102e29a-8690-5ac5-8056-ea6ff14ac112 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent Washing method
0aebf9ad-424c-5995-973c-f2a474eaf773 | note | Acceptance / Conformance Criteria - ≥25
92e3932f-9862-5b07-8082-8417d7514a34 | note | Standard / Specification - NZS4407, Test 3.6, TCC-IDC-IT-4.7.2
22729800-4b79-5039-b483-bcebca5ad57c | note | Verifying Document - IANZ Accredited Report
5d8be517-7cdf-5b1f-bd6e-a25694fedf61 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
f321ba85-54f1-523a-9bc8-0cb59c7e633f | note | ○ Results to Engineer 2 wks before importing
c94debe9-9753-552e-b77d-1f88715fa100 | note | Verification Activity: Activity - HP
4806a3e9-d934-536e-a429-fce1ccb5b981 | note | Verification Activity: By - ENG
8da3737d-cb63-46ef-9a35-ccebf0abb37b | signoff | AUTHORITY HOLDPOINT
6a931bb1-1cbe-40a5-badc-32a8cce30291 | checkpoint | 1.5.5 - Accelerated Weathering
02d09067-8ec6-5a46-8da9-d911fecf2bd0 | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
dd4bc42d-5a05-5038-a4aa-fd881c97b898 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
3063fa3f-bbcc-5abe-ac21-cba89d72367f | note | Standard / Specification - TCC-IDC IT-4.7.2
02d005d1-f909-5db7-87f7-134e328bd80e | note | Verifying Document - IANZ Accredited Report
82bc3eb8-1b83-5b90-87cc-3817ca952b3a | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
a9ba312b-9734-56ad-8812-881ab84a3ab0 | note | ○ 0-400 - 2 tests
26a29b69-fd06-5925-b5db-ff654fc65cff | note | ○ 400-1,500 - 3 tests
b4f95e1f-b598-548b-b1dc-3d0a9b7f14ec | note | ○ 1,500-4,000 - 4 tests
a355efbc-dd38-535d-972d-a0028e2196bb | note | ○ >4,000 - 1 test for each additional 1,000m3
64a36fa2-3b47-5b68-b0e1-87b8ab6e5c9c | note | – Results to Engineer 2 wks before importing
ad5b0818-de61-56d4-83c7-c55f6b80a142 | note | Verification Activity: Activity - HP
0b66e470-d3d8-533a-94ff-01a39fd16673 | note | Verification Activity: By - ENG
11db9d0e-508c-4e73-9411-6bb441ec1f19 | signoff | AUTHORITY HOLDPOINT
c974c020-b08e-41fc-aa24-92e4d70bd732 | checkpoint | 1.6.1 - Crushing Resistance
39e857b6-86a8-5b7b-b005-fd9811e5373b | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
c84f60ad-bf58-5f03-88ea-560fd38ee8e2 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
5118d1f9-6b21-5878-bc4a-fe8a0faae2d9 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.6
8bbe9860-be60-5a6f-adf3-1a0ab3e90e6c | note | Verifying Document - IANZ Accredited Report
eea61c44-1d9d-5875-812b-498f255b659a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
50904faa-5d47-5e5a-991e-4259c4f1e795 | note | ○ Results to Engineer 2 wks before importing
ffd87d48-1f24-50e3-8b0e-0d9f6857d542 | note | Verification Activity: Activity - HP
29e2435f-617f-5940-aa3e-aa1af7eea371 | note | Verification Activity: By - ENG
7dd52a69-8a22-4c79-a6da-c8aa0e861084 | signoff | AUTHORITY HOLDPOINT
5cf2990f-eb4a-49a1-a88a-af28d9252d68 | checkpoint | 1.6.2 - Soaked CBR
7c77ade7-d964-5c40-99cc-d8c33280cbc1 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
f91093bb-1494-528c-aae8-9844ff77769d | note | Acceptance / Conformance Criteria - ≥ 80%
f1e07b53-f0af-5de2-9146-2af761ddb73a | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.6
528b0886-2168-5715-87e3-99cd7b04778a | note | Verifying Document - IANZ Accredited Report
699db6b4-315b-59ef-b6d2-6d9886132589 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
860825fa-6ecf-558e-ab8c-3c229f62c0ad | note | ○ Results to Engineer 2 wks before importing
68b75ed7-207b-545a-a195-5c8c188d89bb | note | Verification Activity: Activity - HP
532cdfb0-a35e-50aa-8b2f-a7b29494be0a | note | Verification Activity: By - ENG
39588dd7-1476-421a-8215-03c4dd529858 | signoff | AUTHORITY HOLDPOINT
f07a77ba-6151-4a6e-9ddf-64e0164d4aa2 | checkpoint | 1.6.3 - Accelerated Weathering
0e4963a3-c14d-587c-8eda-bf13715ca966 | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
bd5165f0-0796-5296-9ce1-0d0d7dff976e | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
d20ecee1-f3bf-5a41-a06d-ad589366790e | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.6
b01270d5-9f4b-5934-90b7-64d9f1cc3904 | note | Verifying Document - IANZ Accredited Report
fc403976-bb32-513f-8981-c8d9bd621ce8 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
c358cd8a-438b-5c13-8390-007ecd22d69a | note | ○ 0-400 - 2 tests
a1250551-6a30-58de-8a71-8e841780f9e8 | note | ○ 400-1,500 - 3 tests
3dcb4b0b-aceb-5859-88a3-2bebbcfabb52 | note | ○ 1,500-4,000 - 4 tests
5e125fd6-d6d7-5c09-b1a5-79c6d0bc20a1 | note | ○ >4,000 - 1 test for each additional 1,000m3
789aad3e-9df0-5611-aacd-bb0acaa8e3aa | note | – Results to Engineer 2 wks before importing
5a32e75d-a142-5ce1-b0b6-c0b162c77970 | note | Verification Activity: Activity - HP
34bc6a12-6111-51a0-83a7-41593cc4326a | note | Verification Activity: By - ENG
aafae794-8b80-437b-84db-cda3b3b93997 | signoff | AUTHORITY HOLDPOINT
3e56a21b-57d6-448c-bf4c-98c6f8a54d12 | checkpoint | 1.6.4 - Weathering Resistance
84419380-14dd-576e-9c55-91bdb9ef4611 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
0fc2612d-8c8c-5a1a-b953-ca33dd34a078 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
74622e3d-97a4-5d43-b87b-73cc9f0232df | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.6
ec6161a3-605f-501d-b6f5-e88a670697b5 | note | Verifying Document - IANZ Accredited Report
788db097-ce9c-5ca2-993a-8ff89da49a5a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
edb52a85-23e0-5121-9acb-40278230d686 | note | ○ Results to Engineer 2 wks before importing
b679e04d-7d14-5c1f-b2f6-796aa399edc9 | note | Verification Activity: Activity - HP
13a36268-cc11-5c3c-87ba-73dbdea357c0 | note | Verification Activity: By - ENG
7c0f7ee8-2c25-4815-9d1f-2457ec51db1d | signoff | AUTHORITY HOLDPOINT
951ea490-ec20-4e98-a727-21ddb84ce033 | checkpoint | 1.7.1 - Particle Size Distribution
f0e0e004-e229-52e3-9246-19e7af6cfda9 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
ab03f313-799d-5814-894f-c33fd2e09006 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
62895d2d-5364-5a8e-b77b-6124fd96e638 | note | 37.5mm ¦¦ 100% passing
5f02c6d8-06a4-5d66-aeaa-8c6032b1de42 | note | 19.0mm ¦¦ 60-75% passing
c5969520-1227-5548-a008-9685d3303b85 | note | 9.5mm ¦¦ 37-50% passing
17da57b6-0eab-507e-9cb7-57433b4cd4fc | note | 4.75mm ¦¦ 20-35% passing
0f1a0ee6-d01f-5848-963c-16022c4a0301 | note | 2.36mm ¦¦ 12-28% passing
b36bb56d-ffb1-5961-8725-fdc73b07e732 | note | 1.18mm ¦¦ 9-20% passing
e5d5c3c6-3a2b-52ba-9b8f-b96aacb7a16e | note | 0.600mm ¦¦ 7-12% passing
ca0d2f54-8ce3-5b38-999f-5f745b488b16 | note | 0.300mm ¦¦ 3-10% passing
955c691b-9e1f-5861-b50d-fa68d54b4f4a | note | 0.150mm ¦¦ 0-5% passing
3b9e98af-6064-5711-b6b1-4604d81777a7 | note | 0.075mm ¦¦ 0-5% passing
03b76761-ef67-594a-b642-b68aaea2dfae | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
f1d13be1-9feb-512b-97bd-0db24eaa5cac | note | Verifying Document - IANZ Accredited Report
6191b963-bbca-5d80-bb21-eb0ba9a7cf7a | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
758bc89a-d168-51aa-8bfb-fc1369ef015c | note | ○ 0-400 - 2 tests
f6f8bed6-9dbf-5f0f-b600-de6d757ff575 | note | ○ 400-1,500 - 3 tests
d3525668-e32a-513d-9a05-8714ed2400fd | note | ○ 1,500-4,000 - 4 tests
687973bd-6bbf-5131-b28f-e4f67912f1b5 | note | ○ >4,000 - 1 test for each additional 1,000m3
dc1799f7-7b88-530c-b4cb-cfafa4a8fadf | note | – Results to Engineer 2 wks before importing
fd12cd78-1a4d-5ad3-9fd9-7608cb69177e | note | Verification Activity: Activity - HP
866ad867-c3bf-5282-b7ee-c20612ffc026 | note | Verification Activity: By - ENG
66ad3fc4-b1c2-4b14-82b9-ca8f17dce3a4 | signoff | AUTHORITY HOLDPOINT
71f2fbda-88e5-456b-bee9-e186e1ec81ad | checkpoint | 1.7.2 - Shape Control
df99a2f3-4e37-5b64-a6a6-6aadd346d86e | note | Detail - Tolerance allowed from approved grading curve (%)
2cb2b955-9193-5b03-b74c-f24bbb599388 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
5cbf19d8-47d5-5b18-8554-00392017776e | note | 37.5 – 9.5 ¦¦ 28-48%
7dd58f74-de14-5875-9069-00596d02f62c | note | 19.0 – 4.75 ¦¦ 14-34%
c282b860-ce87-52d7-a62b-73bbf7cd978c | note | 9.5 – 2.36 ¦¦ 7-27%
e7ea62a1-c112-5900-98b9-302b2f7c47e0 | note | 4.75 – 1.18 ¦¦ 6-22%
de54713f-3015-5974-9482-b8b49523bd7f | note | 2.36 – 0.6 ¦¦ 2-20%
75fd8887-5954-58fd-a9ea-b44e46dc2718 | note | 1.18 – 0.3 ¦¦ 5-19%
93235b83-694f-531d-8803-28fd153c3378 | note | 0.6 – 0.15 ¦¦ 2-14%
14272d11-bb4f-5705-a0ac-c04a8e032096 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4..8 table 4.7
18bdcc5a-145d-55e2-b3be-7db6938f5904 | note | Verifying Document - IANZ Accredited Report
81b90470-f640-527a-b879-8e461a41a99b | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
c207df4d-0db0-5b46-9861-3497cceaab1b | note | ○ 0-400 - 2 tests
b45cc1c7-64f2-54cc-8a0c-3540d0809a79 | note | ○ 400-1,500 - 3 tests
4b9923a2-27de-520d-8027-7bee599ac3a5 | note | ○ 1,500-4,000 - 4 tests
874d0eaa-97b9-5262-b789-02e857457114 | note | ○ >4,000 - 1 test for each additional 1,000m3
8c5100cc-117d-534f-8461-e9e6f8bcf3e2 | note | – Results to Engineer 2 wks before importing
4000a5c7-3a9b-5a6f-8706-a577e5cc5a7b | note | Verification Activity: Activity - HP
1ddc69a4-4131-5d1f-81e1-24bd0b8f4f4b | note | Verification Activity: By - ENG
a1bdae09-5f69-4d4a-ba66-906aba24f3c8 | signoff | AUTHORITY HOLDPOINT
4c805b65-1a7c-4ff4-88f5-0c55435ac768 | checkpoint | 1.7.3 - Sand Equivalent
8fd21c80-e45d-51b9-89fc-27be2502613a | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
6d0279a2-2793-5d2c-a8dd-0ce77242011e | note | Acceptance / Conformance Criteria - ≥ 40
5914f817-e979-5772-9fd2-5d5fa6c12fc2 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
a1e9c4d1-259a-5848-94d1-193ead21b8c7 | note | Verifying Document - IANZ Accredited Report
4b8c7332-777d-5fb2-96ca-05ba9d3c52df | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
943333f1-2963-5bc7-a979-4d9012e40322 | note | ○ 0-400 - 2 tests
8d7d523c-d746-585e-9cfc-e07b344c345a | note | ○ 400-1,500 - 3 tests
98a831c4-29c9-5c59-b0b4-351a8189106b | note | ○ 1,500-4,000 - 4 tests
eba10df7-021d-5db7-9e23-bcf2f5ec74d4 | note | ○ >4,000 - 1 test for each additional 1,000m3
1ba03e69-06bd-597d-9b30-7435a14e80a2 | note | – Results to Engineer 2 wks before importing
de7e7f70-3c89-5f1c-b82d-236f84c23783 | note | Verification Activity: Activity - HP
a70fe2af-0c3b-5615-a2a1-bf9147be8615 | note | Verification Activity: By - ENG
d7dc6364-b2c1-4f14-b25c-441b935c6feb | signoff | AUTHORITY HOLDPOINT
a8e945a5-2bf4-4783-b27a-3665548a4238 | checkpoint | 1.7.4 - Cone Penetrometer Limit
967d3c97-3bde-59ad-a50c-3f0582ab9a50 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
46898f67-681c-5250-9df7-89e97e62e2d5 | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 30
470ed578-c8b5-5782-8e5b-c5a0dea5423a | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
3a27db4e-4cc5-5654-9ced-71a22d59a30c | note | Verifying Document - IANZ Accredited Report
cc5298ac-6ef4-5176-89d8-0cbd511bb8a6 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
03e7b20f-7a7a-515d-bdc2-ec1064532c89 | note | ○ 0-400 - 2 tests
85b1540a-f036-5973-875d-9dd896d60059 | note | ○ 400-1,500 - 3 tests
322efb3e-e85f-583d-a1f3-708703964f7c | note | ○ 1,500-4,000 - 4 tests
5d0499d9-3793-5a3b-a736-15e4eef5c055 | note | ○ >4,000 - 1 test for each additional 1,000m3
2467421a-68cb-5ad4-a20a-f8f52bbb396c | note | – Results to Engineer 2 wks before importing
acc65d2c-b3f6-56bb-aa3d-35bf7a3757d7 | note | Verification Activity: Activity - HP
26b92bad-75f6-506d-8f27-ae59f5b63b20 | note | Verification Activity: By - ENG
c69ce8a6-4f79-4ec6-ae5a-ef33fcfea8f1 | signoff | AUTHORITY HOLDPOINT
9d9fa6d4-4832-4803-b266-7550307a1ca4 | checkpoint | 1.7.5 - Plasticity Index
10f9c5f6-a078-564e-943f-9c82c4c66e7e | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
844ca8d7-cb59-54ab-ad9d-ea07851a2844 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
58066432-9636-5a0f-9405-74ee5a7e6dd8 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
0a6ca716-6acc-5312-b8a4-cb76cf2107e0 | note | Verifying Document - IANZ Accredited Report
2383705c-349e-5d9b-8104-2e79928c09e2 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
087d0b26-7380-5efb-b93a-5972004834f7 | note | ○ 0-400 - 2 tests
0d36937c-7952-590a-8553-deda828e3162 | note | ○ 400-1,500 - 3 tests
46ea6e87-4051-585f-8608-f127e163a7db | note | ○ 1,500-4,000 - 4 tests
a77a0853-1f25-556b-a787-c86d6952771b | note | ○ >4,000 - 1 test for each additional 1,000m3
594477f4-9499-5ced-b4c0-9534982ac809 | note | – Results to Engineer 2 wks before importing
9e052c36-9840-5b32-8166-b4c50b3b7908 | note | Verification Activity: Activity - HP
39034ca7-d759-554b-a625-4a8572755bc1 | note | Verification Activity: By - ENG
b85bfc96-d6a2-48cf-8c9e-477a857c09f2 | signoff | AUTHORITY HOLDPOINT
23cdaa9c-a946-4b51-8fd0-e004cf6fd67e | checkpoint | 1.7.6 - Clay Index NZS 4407 Test 3.5
3af095c5-980f-54f8-b3c8-fd3f3a771e90 | note | Detail - Clay Index NZS 4407 Test 3.5
56d0b1b5-63d8-506e-9419-e0e2756733d2 | note | Acceptance / Conformance Criteria - ≤ 5
f893bed8-20b0-5b8d-8732-e4a341b591cd | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
292ea6c6-0664-53e2-8369-492975baaa22 | note | Verifying Document - IANZ Accredited Report
b9286b71-30b7-5d4b-ab2c-dacc0ec76a74 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
ba700f7e-6a59-5bb2-8152-5e27b9eed1f2 | note | ○ 0-400 - 2 tests
ba7ca286-0c66-5d43-abf2-70dc536c43c7 | note | ○ 400-1,500 - 3 tests
af758d46-f333-5c31-ae1f-95fc854837f4 | note | ○ 1,500-4,000 - 4 tests
8ad3fd80-b89c-5754-ba36-a3227dbf9f7e | note | ○ >4,000 - 1 test for each additional 1,000m3
3d2e665c-4ccb-5b2b-9a58-647a1d72b2d6 | note | – Results to Engineer 2 wks before importing
83693f55-b035-5147-998b-7cd3aef8ca5e | note | Verification Activity: Activity - HP
4bc1ffdf-67f5-5981-88dc-32d89d23a42d | note | Verification Activity: By - ENG
dd9acf9e-a51c-4d54-a2e8-e54ba640c205 | signoff | AUTHORITY HOLDPOINT
4aced24c-0071-4236-837d-cb8ac209e4cc | section | SECTION 2 – Subgrade Handover from Earthworks
6f22d992-1d54-4339-b4be-9f61036636b7 | checkpoint | 2.1 - QA Submission
7c59f070-433c-5edf-a42c-0782e38765a0 | note | Detail - Submit all Subgrade QA before proceeding with next pavement layer
5c222e35-2f5a-5a2a-9993-e542e7be1d7a | note | Acceptance / Conformance Criteria - Engineers Approval
10e13edb-6b15-5a88-9cf5-4866065402c9 | note | Standard / Specification - Appendix V
49893f44-8024-55ce-958d-31e7b32499d3 | note | Verifying Document - Conqa Siggnoff
ddd94afc-3d9b-56d9-a99b-a86edcb8f7a9 | note | Testing Quantity Required (based from schedule qtys) - Once
80a6e501-99c3-56cc-bbcc-68c840ce15f2 | note | Verification Activity: Activity - HP
760a5751-bee2-55d3-9daa-a05e5f7beca7 | note | Verification Activity: By - ENG
eaab1a0a-297f-444c-bd05-b12aed9451f9 | signoff | AUTHORITY HOLDPOINT
7721652c-10a5-4d6d-9b72-aacb4cc9e86b | section | SECTION 3 – PLACEMENT OF GEOGRID AND GEOTEXTILE FABRIC
0c8ee800-eaa6-4763-832c-7b2b62448f50 | checkpoint | 3.1.1 - Placement of Geotextile Fabric
af501f8e-28ed-5a3c-b5bd-4bd15dcccb03 | note | Detail - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
9918e0b5-f878-5981-94da-567527c011cc | note | Acceptance / Conformance Criteria - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
1ce74cba-7b59-56d5-9a61-6b8e92c382da | note | Standard / Specification - NTC0097, 232735.02-WSP-DR-PVS-0401-REV4
9ba8f2bf-8491-5501-b72f-9a5a0ca8260d | note | Verifying Document - Visual Inspection and photos
e2cb6dfe-1274-5d59-9261-a66f22b7af85 | note | Testing Quantity Required (based from schedule qtys) - During construction
3566b06a-3f0a-58fe-9ea8-727a6a8d22e1 | note | Verification Activity: Activity - W
8c6f6825-8335-5abf-8444-1b35ac7b71af | note | Verification Activity: By - ENG
81ed5225-ac49-44b6-8c18-52bee71c124d | checkpoint | 3.1.2 - Onsite Check by Engineer on Geogrid
4315f965-1c27-5163-94da-2bca18c3a922 | note | Detail - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
6929cd40-93f1-51e1-a094-9a30b1c33098 | note | Acceptance / Conformance Criteria - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
cdb65f52-f9e9-5f47-ab2a-84c5df88a636 | note | Standard / Specification - NTC0100, 232735.02-WSP-DR-PVS-0401-REV4
3aa6df74-4d51-5635-97f7-1e92e532c8d1 | note | Verifying Document - Visual Inspection and photos
18feec7d-8d65-52e1-8510-d5a1bc0d7443 | note | Testing Quantity Required (based from schedule qtys) - During construction
c62e2f62-06a0-5267-9a8e-5f6a4163ded6 | note | Verification Activity: Activity - HP
7e68e453-1a75-5cae-b3c8-4d25eee4332f | note | Verification Activity: By - ENG
23b93cbe-0aff-4697-80fd-a7737a5eb91e | signoff | AUTHORITY HOLDPOINT
be1fd1b3-2610-4ca9-93ad-35e25374f092 | checkpoint | 3.1.3 - Placement of Geogrid
666cb7c9-7125-5298-a21f-f2beed51df66 | note | Detail - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
53a89742-c9cf-5142-8076-bc4778cad67a | note | Acceptance / Conformance Criteria - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
94cbbdb1-5985-5802-9f0a-2ea2633f7caf | note | Standard / Specification - NTC0100, 232735.02-WSP-DR-PVS-0401-REV4
e204774a-13e4-5b59-904f-9b3e7a805415 | note | Verifying Document - Visual Inspection and photos
b677dc86-71a1-5e4a-9ab1-26c06ad3dcca | note | Testing Quantity Required (based from schedule qtys) - During construction
7eae9770-d87e-5ec8-a253-6fb695787dbd | note | Verification Activity: Activity - W
20365f1f-3eae-5dc5-8e49-585a20768dba | note | Verification Activity: By - ENG
1fc1087e-8156-4377-85fd-6f3b18d98d84 | section | SECTION 4 –PAVEMENT TYPE 5
a3c59949-b771-44c9-832c-e18f19b6f8b6 | checkpoint | 4.1.1 - Plateau Density Test
905cac7b-27e9-59ee-879d-8882be54981d | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
02ddd4be-f217-5cd9-9294-d23f804eb13e | note | Acceptance / Conformance Criteria - Plateau Density Report
7f3ca640-603a-5b8f-aee2-271d5def6040 | note | Standard / Specification - NZTA B/02 7.5
b11320ce-1c8e-54b4-8308-1b7577d40cb0 | note | Verifying Document - IANZ Accredited Report
8e8f9eac-9e79-57f1-bfb7-112a71dc0c1b | note | Testing Quantity Required (based from schedule qtys) - 1 Test
3c86843b-b5b7-531d-9ed0-490d4b2a583c | note | Verification Activity: Activity - I
3a350568-f3fd-57c1-a2ce-0909328e6a50 | note | Verification Activity: By - SE
3054114f-2c79-4802-85d7-c352b8afcb45 | checkpoint | 4.1.2 - 3m Straight Edge
f94b7d01-d246-51d4-96d0-478085be98fc | note | Detail - Formation check to ensure surface is smooth
365c1ff0-ffd8-5c36-a189-b26562c0be9c | note | Acceptance / Conformance Criteria - +/- 10mm
837aaaf6-6927-5b9b-899f-3a0167f0a3da | note | Standard / Specification - TNZ B/2 7.7
d0b2d5f4-7463-5d0a-8b7a-2439124ad794 | note | Verifying Document - Check Sheet
acfe97b4-16e6-5656-93ef-6fa3aa529051 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
49266e15-c700-5698-9726-31f31092f9d8 | note | Verification Activity: Activity - I
fdae1316-0d79-505a-bb90-8c7a2ce02428 | note | Verification Activity: By - SE
4b487d9f-474c-4848-bfde-22319a90cadd | checkpoint | 4.1.3 - Stringlines or equivalent
6d4ab656-6f68-56fe-9212-01c2e49eeb23 | note | Detail - Stringlines or equivalent to check finished height of surface
844c9906-8edc-5d9b-8d9b-bec23dfd2d66 | note | Acceptance / Conformance Criteria - -25mm + 5mm
d9ea4714-09d0-5a45-8fe8-fe55361e04d6 | note | Standard / Specification - NZTA B/02 5.1
1a21e62c-4a81-5daf-80b6-728d5025d14c | note | Verifying Document - Check Sheet
cad578bc-d61b-5df6-8af2-04b30daf3d65 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
89f8df76-35d3-56a7-abab-00b32c45bbcf | note | ○ 1 set = 5 tests
abf9d0aa-9261-5dc1-9024-64c0d337508e | note | Verification Activity: Activity - I
8cd82f69-d073-58dd-b425-ee0a7d0d9fe1 | note | Verification Activity: By - SE
16165eb7-6949-4502-8fce-675dafeff5b0 | checkpoint | 4.1.4 - Compaction - NDM
2d2cebe2-79f5-5718-9b80-52b2560b469e | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
1e83b6cf-c1e8-55e3-beed-b8409811fd6a | note | Acceptance / Conformance Criteria - Ave >95% of MDD
f1f4ee23-b024-5c5b-97de-2d7d6c95629b | note | ○ Min >92% of MDD
0bc33da6-71e1-5a4d-8e7e-39fd8ab432fe | note | Standard / Specification - NZTA B/02 7.6
288d97bc-e780-5575-a21d-612d1de46f48 | note | Verifying Document - IANZ Accredited Report
19939f0e-43ee-5a2c-b8d3-c4772c7b91f3 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
947bbc9c-0da4-55ab-9550-7967bebde3ea | note | Verification Activity: Activity - I
92da9812-3bb4-58bc-9ca6-b57431f730d7 | note | Verification Activity: By - SE
6fc9fd5f-1233-4d7a-af7e-e4cb57a3417c | checkpoint | 4.1.5 - Benkelmen Beam
0952a270-68b1-5dd8-b09c-c1ae08207001 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane. Unbound layer.
f5bdc584-322a-5c60-9115-150e6bd6e137 | note | Acceptance / Conformance Criteria - 90th Percetile: 1.90mm
2ee1819a-8883-51e5-b122-9f10761563cc | note | ○ Maximum: 2.34mm
58d6cfaa-49c3-54da-8ca9-4e10f3be9ed8 | note | Standard / Specification - PS 20.14.5, NTC0160
200348b5-0f35-59f0-bc6d-50264ae81921 | note | Verifying Document - IANZ Accredited Report
ddc041cb-d62a-5dd8-9e21-b128d06ed3ef | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
cb23c259-08b7-5219-8000-5e1d62e00d2a | note | Verification Activity: Activity - HP
e9db3400-cbe4-5477-b2fa-48f286f9e6f8 | note | Verification Activity: By - ENG
d1dbbe9e-2549-4ea9-816d-63e34566545c | signoff | AUTHORITY HOLDPOINT
48ee3be3-df63-4a52-8094-313da8cb9dfe | checkpoint | 4.2.1 - Plateau Density Test
ed142478-1861-575b-a1f5-52e2fade9e60 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
91c1c809-5837-5ebd-8371-928068fd8a91 | note | Acceptance / Conformance Criteria - Plateau Density Report
e8b3948e-35ba-5ee6-a418-5b67b434dc9c | note | Standard / Specification - NZTA B/02 7.5 (a)
7bc3364c-86cd-5489-83da-d5a26d7265ee | note | Verifying Document - IANZ Accredited Report
bb690496-1ea6-5784-8cf2-9756b1f5d8bc | note | Testing Quantity Required (based from schedule qtys) - 1 Test
a1670179-3b81-5612-a81f-2fabf3104f97 | note | Verification Activity: Activity - I
06acd1b5-6b67-5e54-8c04-3283790ebc13 | note | Verification Activity: By - SE
5c60e7f6-a882-4add-8ea0-65e07cf075e6 | checkpoint | 4.2.2 - 3m Straight Edge
e8457b36-9208-53ed-b70c-ab20a66f279a | note | Detail - Formation check to ensure surface is smooth
d1ec1124-8945-5389-a162-c14897c8a911 | note | Acceptance / Conformance Criteria - +/- 10mm
85084b24-1928-53fe-8f60-a75512794b59 | note | Standard / Specification - TNZ B/2 7.7
8fe644d2-b495-5b4b-97ef-798cceba931f | note | Verifying Document - Check Sheet
42d7b536-2df9-58c4-9162-b3f51b89b7eb | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
6b3b7730-5254-50fe-8b45-cf7d6f12c113 | note | Verification Activity: Activity - I
bb590413-0cea-5891-b347-87996c330a5c | note | Verification Activity: By - SE
2fcad387-effd-4a7f-b10a-c4f5e7ca3a99 | checkpoint | 4.2.3 - Stringlines or equivalent
27dc7f46-be67-5a86-a623-d16266fdc721 | note | Detail - Stringlines or equivalent to check finished height of surface
3dbe7596-7703-50b0-98e4-624912568716 | note | Acceptance / Conformance Criteria - -15mm + 0mm
6b3edf29-81df-50cd-ad7a-6a3d95cfb087 | note | Standard / Specification - NZTA B/02 5.1
7b851834-e8d1-5fb0-ab76-40e1da803e2a | note | Verifying Document - Check Sheet
fc8ce9a7-5a46-537e-aab9-8ec23103f35d | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
7e3281bf-a961-5325-8615-96053cfcbaaf | note | ○ 1 set = 5 tests
cac98223-1694-5c29-940d-58b9963786d6 | note | Verification Activity: Activity - I
52456862-080d-54ef-be6f-9da06cc2c592 | note | Verification Activity: By - SE
11c240f8-a752-45a1-b693-07c28ac5837d | checkpoint | 4.2.4 - Compaction - NDM
0856ee1d-b41c-596c-871e-d10b6c25159c | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
c1e5786c-d7f8-5f18-b146-9dabf6a548c6 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
5e95fc1a-6645-5e65-b678-f2cd59e5c134 | note | ○ Min >92% of MDD
25909411-4fdb-5b95-920e-9a0eea1ef01f | note | Standard / Specification - NZTA B/02 7.6
4f5afa7b-87ab-58dd-908c-6fc3a6c44017 | note | Verifying Document - IANZ Accredited Report
5757027f-f44f-52b0-8b1e-fe486bf165c8 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
b9fb2710-80c1-5fdb-b3e8-c73470e1a76e | note | Verification Activity: Activity - I
77bdf73e-8f9e-55d8-9f78-4f3db9d81b31 | note | Verification Activity: By - SE
1f9fb6f4-f501-463f-8340-843208696556 | checkpoint | 4.2.5 - Benkelmen Beam
cef39921-4afd-5442-bc65-5e747f715086 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
ecef339d-6728-525d-8754-aa0d7dd7bcf7 | note | Acceptance / Conformance Criteria - 90th Percentile: 1.39mm
ea3febda-32bc-56cb-81c0-8d4a2e7606c2 | note | ○ Maximum: 1.70mm
0c36811f-c350-5b17-9d32-6d33cd24802c | note | Standard / Specification - PS 20.14.5, NTC0160
687494c0-2c0f-5337-8aeb-27fe1aba7c9c | note | Verifying Document - Test Report
73def429-b7f2-594f-b488-828cb76a9672 | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
3c9d5c9f-4eb2-585e-894b-a426140cea7c | note | Verification Activity: Activity - HP
833b2f79-5828-518e-b47a-f7a04a8147fd | note | Verification Activity: By - ENG
5ec40a30-1748-4ac2-8480-76ca608e5a04 | signoff | AUTHORITY HOLDPOINT
86071949-d5ec-4f86-a7f6-00312bac3cc5 | checkpoint | 4.3.1 - QA Submission
f0f776e5-93f5-5ba2-9741-dbf4a1b34d96 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
dc0ab803-e512-57a6-a9c8-bad6c3f82460 | note | Acceptance / Conformance Criteria - Engineers Approval
b622582b-2d6e-5394-948f-d782027e00f9 | note | Standard / Specification - Appendix V
dffd1700-7e16-55fd-8b71-b261b6252614 | note | Verifying Document - All test reports
c290a7af-196c-5698-8c56-4dae49d5b1cd | note | ○ Material Test Results
3b2e992a-4538-51fd-b37b-fec6986bc56b | note | ○ Laboratory MDD
b553d776-653a-5f8f-920a-ac28c3d2d163 | note | ○ NDM results
48e2586e-d973-5f19-b98b-2be4df3e89ec | note | ○ Proof Roll
5037ba3b-47b8-52b4-a3c9-b6120e20fef3 | note | Testing Quantity Required (based from schedule qtys) - Once
ac1b3bc2-615b-57d0-983a-a80dca54bdd7 | note | Verification Activity: Activity - HP
7526f2bd-3041-5392-b8f6-2d2461c46842 | note | Verification Activity: By - ENG
6b6110c3-aa91-448e-8d35-84b2b1211dfd | signoff | AUTHORITY HOLDPOINT
be5ee976-afc6-4868-8556-55e0cdf95416 | checkpoint | 4.4.1 - Plateau Density Test
bf9211ea-c110-5da8-a7e1-91ae68f79973 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
c506108e-4611-5dc4-9d45-5f3490b9a8e5 | note | Acceptance / Conformance Criteria - Plateau Density Report
3294bb6b-2c32-5502-8840-9741a38358d3 | note | Standard / Specification - NZTA B/02 7.5 (a)
ef2a48aa-7879-558b-94b1-ec2fbe8841ac | note | Verifying Document - IANZ Accredited Report
047a0afc-9dc6-5b6b-825d-87be568759ff | note | Testing Quantity Required (based from schedule qtys) - 1 Test
667742fa-efa0-5389-8c94-4d88a1f65520 | note | Verification Activity: Activity - I
d8fe97da-0d0e-597c-a1e7-37a5a4982756 | note | Verification Activity: By - SE
0e3ba9e2-a35b-409e-9e7b-4a926086b021 | checkpoint | 4.4.2 - 3m Straight Edge
84b88ae7-a0bd-5777-a533-9c8c43d51935 | note | Detail - Formation check to ensure surface is smooth
750acbf6-10ee-53cf-ae57-eeeda0ca6e71 | note | Acceptance / Conformance Criteria - +/- 10mm
2a9cf170-2948-5a26-ac8c-5d45d10e76af | note | Standard / Specification - TNZ B/2 7.7
40554a4e-5c3a-517e-854f-337227929d38 | note | Verifying Document - Check Sheet
30736979-7418-5833-aecd-86a0a70fb980 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
693f0fab-aedc-518c-b168-0596c357ce2e | note | Verification Activity: Activity - I
cb8adc90-2603-5c0f-8fa5-4ca1afd00e90 | note | Verification Activity: By - SE
946c2718-6d8d-4b09-a163-9e0e20169021 | checkpoint | 4.4.3 - Stringlines or equivalent
9f7f3efb-e4f6-5c69-bcfa-0091eecdbfb3 | note | Detail - Stringlines or equivalent to check finished height of surface
959a58eb-c5fd-59d7-8605-d4a4149a4ace | note | Acceptance / Conformance Criteria - -15mm + 0mm
8b214020-8f44-5a41-8a67-0e4b0997a986 | note | Standard / Specification - NZTA B/02 5.1
943554b4-d0f2-5677-84e6-5641cb401bf7 | note | Verifying Document - Check Sheet
38525cb4-c461-5d8b-a7fa-2cbaaa612938 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres, 1 set = 5 tests
166da2f2-e6de-5217-9bc3-7de425906032 | note | Verification Activity: Activity - I
2eaad194-926b-59c9-a908-cd5ed275bce7 | note | Verification Activity: By - SE
693b71a9-3671-45c6-8200-949ca0bee8c5 | checkpoint | 4.4.4 - Compaction - NDM
f624039d-b215-5626-8958-fa6cdb505f44 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
8d7a8efe-1308-55b2-984f-b03f6c7dba4f | note | Acceptance / Conformance Criteria - Ave >98% of MDD
a0ec8a69-38a2-5079-ab53-f5876c1dfc03 | note | ○ Min >95% of MDD
2902046a-db4c-5577-abb8-70b05e7be6b1 | note | Standard / Specification - NZTA B/02 7.6
5f602535-d8bc-5fee-9104-bce19623682f | note | Verifying Document - IANZ Accredited Report
6fae0f99-e11a-5be3-b3cb-20b9500d8d08 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
3b4f14a1-b281-5d18-8aea-d87d4d857c7b | note | Verification Activity: Activity - I
4d7ed9aa-89c7-5914-a97e-f64acc1b41a9 | note | Verification Activity: By - SE
49074dd4-f012-4abf-853e-31161c5e29f6 | section | SECTION 5 – AS-BUILTS / REDPEN MARKUPS
86d1ea60-47c2-4e94-92fd-4cf23b6953ef | checkpoint | 5.1 - As-Builts/ Red pen markup
43216430-b950-5031-a9f2-fd9047c8c60b | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work
85faae57-3408-50b9-99f9-4593d6117079 | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
138d7f7e-72b6-5df3-adc9-3cf662c2315b | note | Standard / Specification - PS 16.7.6
5070ec53-15d4-517d-be74-9589e3cbff82 | note | Verifying Document - Red pen markups
4efcdc02-39ac-5df9-a094-214e1602a1e4 | note | Testing Quantity Required (based from schedule qtys) - During construction
ccd9ec72-0f8f-5d7b-a3ef-89a0d92b256e | note | Verification Activity: Activity - D
c69a3fb4-4936-515b-b07f-d45f46e61c92 | note | Verification Activity: By - SV/SE
63469784-629d-4b89-bd5d-71caf5c302ee | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
5f4cfdd5-2817-5efe-970f-8a099b8fce61 | textbox | Contractor's Rep Name:
0f8e8e67-6420-500c-b026-eb20e533dcda | textbox | Engineer's Rep. Name:
2af81043-ac6f-56d4-8692-3e2ff6407037 | date | Date:
2e6b8b66-7e88-4284-be09-b22686bc4226 | signoff | Add Signature
92786a9e-a391-4aad-ba13-5d37cbe522d0 | checklist | DN1210-SP2-006-003 - ITP Northern Access Road Carpark Pavement 6 Rev 1 | itp | DN1210-SP2-006-003 - ITP Northern Access Road Carpark Pavement 6
c95a50dd-d20d-4e8e-ba4c-0e35f6aff3dc | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
8bdb124d-fc1d-4cee-b5ba-97bd3a5846c2 | checkpoint | 1.1.1 - Crushing Resistance
df475bae-66e5-555c-af4c-921e84f147f8 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
1bc9cf70-2ed9-5e45-93d4-e42b9cca1a8d | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
4ccef736-7f16-5cfe-aa30-59abae3f9043 | note | Standard / Specification - TCC-IDC IT-4.7.1 table 4.4
6f99a4f9-fad1-545d-bc70-3160325c2160 | note | Verifying Document - IANZ Accredited Report
c66b36a8-54b1-58b6-80f5-f69e27a06a46 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
f94589b6-7f5f-52f7-a0d0-552db495f0a4 | note | ○ Results to Engineer 2 wks before importing
8b47f992-4a3d-56f8-a7f2-883029f51704 | note | Verification Activity: Activity - HP
e16b5c6c-a02f-5d53-b6cb-870fc9856550 | note | Verification Activity: By - ENG
e6bf5700-31a6-4ffd-90db-4446b198fd5d | signoff | AUTHORITY HOLDPOINT
9bcf17f8-3397-475d-8d25-653ee03d73c4 | checkpoint | 1.1.2 - Soaked CBR
a193f047-f46d-58b3-bb6a-79b0c6e79c08 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
db857916-a7a0-568f-bafa-e5eb83301414 | note | Acceptance / Conformance Criteria - ≥ 60%
1571a5e4-a43c-5442-871e-f82ece50fba9 | note | Standard / Specification - TCC-IDC IT-4.7.1 table 4.4
5c3e6d6a-ed11-52f1-9c15-f868c0817362 | note | Verifying Document - IANZ Accredited Report
fc18ecdf-5952-5be1-b469-39630183d390 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
266f42f7-e0bf-579d-a15e-16ee8e64abc0 | note | ○ Results to Engineer 2 wks before importing
8be47139-66f8-5b0b-a6d1-6d659c2107e5 | note | Verification Activity: Activity - HP
e523e93e-f9a1-518d-b69a-54ec59b526e1 | note | Verification Activity: By - ENG
e105277f-fea8-4f36-a83e-540f87584906 | signoff | AUTHORITY HOLDPOINT
43f8090e-efa8-4ad3-8133-8de9b9a8563c | checkpoint | 1.1.3 - Weathering Resistance
3e08d3ec-aaa7-555d-8e33-243706c8cbdb | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
03a27b90-855c-51f8-885b-8682ed037f82 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
c8131a9b-1a6d-5921-a228-adbe471324e0 | note | Standard / Specification - TCC-IDC IT-4.7.1 table 4.4
481b6e17-e405-52f3-bc17-ab88b88edc16 | note | Verifying Document - IANZ Accredited Report
a5c6c37f-27ea-5fbc-917b-2c97987cd7a9 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
93c412d1-a4d6-577b-8dec-37273aaf90a6 | note | ○ Results to Engineer 2 wks before importing
c365735e-fc39-5f8e-926d-24e21138fbf3 | note | Verification Activity: Activity - HP
4ceaf26e-227b-59df-b7da-dce5e37cdf6b | note | Verification Activity: By - ENG
eb71a08a-08f8-4ccc-85b4-b6ac87ef8694 | signoff | AUTHORITY HOLDPOINT
d2051eeb-5372-4d3a-bc58-332f77d30b2d | checkpoint | 1.2.1 - Particle Size Distribution
f46f978a-6bab-5710-9e8c-07a2ecfeba51 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
62e01050-b2a0-5837-b995-53f67cabef6e | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
7502f332-d7da-5beb-8ba6-28fc73aef0ca | note | 63.0mm ¦¦ 100% passing
a9f70044-92ec-5be3-a8d7-427c3c570043 | note | 37.5mm ¦¦ 55-85% passing
697d34b2-cde0-5516-86f9-6fb135364118 | note | 19.0mm ¦¦ 33-65% passing
130cb4a2-84d9-59ed-aaaf-7e3f49e1d154 | note | 9.5mm ¦¦ 20-50% passing
c274bec9-e3d5-5650-851e-cfa737ee98eb | note | 4.75mm ¦¦ 10-36% passing
a78d26d6-3798-5a6f-ad10-a33590837a3c | note | 2.36mm ¦¦ 5-27% passing
c1071c4d-c687-5ca9-a970-b40f3370852b | note | 1.18mm ¦¦ 2-20% passing
631d02be-7795-57bf-bfcb-ffd8caa871e4 | note | 0.425mm ¦¦ 1-13% passing
c33eb804-6e02-5748-8613-05b0626c81cf | note | 0.075mm ¦¦ 6% max passing
1999fbf2-47a4-50f6-97ab-455abc99a017 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
4476e6c1-4596-5d67-8ddc-b12ee3cc0ce8 | note | Verifying Document - IANZ Accredited Report
e89979f3-e916-57ed-a0c0-25e38e9263c0 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
f439fdde-030a-5a39-9a21-2932a945c46e | note | ○ 0-400 - 2 tests
cf2545b1-120c-5322-953a-9768bf0187b5 | note | ○ 400-1,500 - 3 tests
1611b1c2-e7af-58fe-a5fe-6e7c0a1fdf9f | note | ○ 1,500-4,000 - 4 tests
846fb5cc-bae4-53b5-ae9c-2f98551c0382 | note | ○ >4,000 - 1 test for each additional 1,000m3
0eadb459-ac3e-595c-8dc0-bb39e4432eff | note | – Results to Engineer 2 wks before importing
f063c734-886c-572b-9465-946bebae91b1 | note | Verification Activity: Activity - HP
20ebfa45-3d8d-5deb-925d-08d67aa2d5e3 | note | Verification Activity: By - ENG
17a6b326-86ea-4300-ab2d-836783369bfd | signoff | AUTHORITY HOLDPOINT
8d8bc211-571b-43c6-881e-aab2e64e80d2 | checkpoint | 1.2.2 - Shape Control
d23db4e3-7ca0-5c3a-8bce-6287a2d7a059 | note | Detail - Tolerance allowed from approved grading curve (%)
491221fd-c820-5117-9f21-c6af66abd6b8 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
c1b63599-f585-5265-8c7c-9c669386930a | note | 37.5 – 9.5 ¦¦ 34-50%
c72702d6-38f5-5e04-88d3-c50ccbf4b852 | note | 19.0 – 4.75 ¦¦ 18-40%
94404136-c659-5d62-84d7-87d452bd2dd8 | note | 9.5 – 2.36 ¦¦ 12-32%
9398253d-d873-5145-83ec-94f0055ee307 | note | 4.75 – 1.18 ¦¦ 6-24%
6111bf4b-803b-56b1-a6d7-1c6410f1c2f6 | note | 2.36 – 0.6 ¦¦ 2-20%
08c2229d-f266-58dd-8d81-5d27b3e6616e | note | 1.18 – 0.3 ¦¦ 0-15%
e88ff4c2-e388-5156-b695-94fa9e82213d | note | 0.6 – 0.15 ¦¦ 0-12%
a348dfeb-45e0-5ecc-8b48-2c0e1fe39aa2 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
df5f2010-bff3-5ad9-9fd5-4379b19edda1 | note | Verifying Document - IANZ Accredited Report
de1c5b2c-65a3-5dfc-930d-73a5f7588970 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
158f864f-03a4-534d-a397-cff39f231e3a | note | ○ 0-400 - 2 tests
5a6ad6c6-e6bf-598d-821e-49abbf042a4f | note | ○ 400-1,500 - 3 tests
09b55de8-fa57-54ab-869e-c3a79e47cb1d | note | ○ 1,500-4,000 - 4 tests
06200277-bbe1-534b-9d09-dca38d120df9 | note | ○ >4,000 - 1 test for each additional 1,000m3
a778ef5f-dc21-5eaa-8987-87f8a4562e62 | note | – Results to Engineer 2 wks before importing
33cb51b1-235f-567f-97f9-bbc73e2a7ce4 | note | Verification Activity: Activity - HP
d12d70b4-6555-5174-b21d-5adf8c3738c8 | note | Verification Activity: By - ENG
52be5cb7-0798-4c01-8d4b-4ea3cd9c63e3 | signoff | AUTHORITY HOLDPOINT
cd2aa339-ff94-4730-8bb6-69b6e8d416ea | checkpoint | 1.2.3 - Sand Equivalent
c0e114a9-beb6-5e59-924c-969f7fed2102 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
540fe0ab-b2c9-5132-9c3e-81fc19e0fb53 | note | Acceptance / Conformance Criteria - ≥ 30
20962945-c7df-5964-8f5a-2e389c4f1025 | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
80c91347-2e84-551c-82bc-08fca03a1da1 | note | Verifying Document - IANZ Accredited Report
166eb906-4615-51cb-a2cb-7ba651557a60 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
bd27e21b-3e26-5ee8-9aa4-575ef6ad5714 | note | ○ 0-400 - 2 tests
c99f00d5-73cb-5d6a-8de0-9e00344859e1 | note | ○ 400-1,500 - 3 tests
15f697bf-e55a-5dea-a4b4-2dc203e63ab1 | note | ○ 1,500-4,000 - 4 tests
5c4864f5-8975-5e8b-b5b2-d5e2651d3e75 | note | ○ >4,000 - 1 test for each additional 1,000m3
d9fd35ca-6b13-5426-8306-a37e4ac4012a | note | – Results to Engineer 2 wks before importing
6d0d5308-89c7-56ba-9d2f-bb46ff40dbb9 | note | Verification Activity: Activity - HP
20526c94-33db-57a3-85db-e63a016faab0 | note | Verification Activity: By - ENG
95ef6d90-e26b-41d5-82e9-b0965184a138 | signoff | AUTHORITY HOLDPOINT
5bbd39ea-2b19-4ee5-8d44-fe44c7bd09a9 | checkpoint | 1.2.4 - Cone Penetrometer Limit
a1bb43cd-311d-52db-8663-48d44d3042ed | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
e07f1185-02d7-558a-a2a2-fb73049997d5 | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 25
9d8ed6f0-ca0d-5e6d-b8d3-b4ba027c145d | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
68ac8815-f38c-5c8f-9af0-603db5a0eef3 | note | Verifying Document - IANZ Accredited Report
7a8d31b3-3c53-5821-88c3-7f1b4486de0b | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
daa89719-5ea8-55a1-ad99-196a047a4ad6 | note | ○ 0-400 - 2 tests
5badba8d-9358-59d8-9da1-6a7ec5beb121 | note | ○ 400-1,500 - 3 tests
2d5fd725-96d7-56f0-9dd2-f69f82c0cb99 | note | ○ 1,500-4,000 - 4 tests
24add82a-5479-503d-85fa-0b7bf970a014 | note | ○ >4,000 - 1 test for each additional 1,000m3
b4dfe2bd-ea1a-57a5-ab26-f7e7abb45743 | note | – Results to Engineer 2 wks before importing
49cdf3dc-6bcf-5fa0-bd78-c121feb60335 | note | Verification Activity: Activity - HP
5e9c1325-cf07-57f1-9328-24d061084ed3 | note | Verification Activity: By - ENG
92b2fdb5-5c53-4902-b92f-3fa53ca5250d | signoff | AUTHORITY HOLDPOINT
8ac9caf4-2268-4ccf-9af9-0d3739b6415b | checkpoint | 1.2.5 - Plasticity Index
292dda6e-1008-585e-8ea4-d65f87eeb840 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
571d23e9-f645-5913-b74a-c4076f17fdd1 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
7450522a-3efa-584b-8d10-a3b37ea1a15c | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
0c539b93-d87a-53fb-8397-9a51c3e41062 | note | Verifying Document - IANZ Accredited Report
beee9e98-db84-5268-8743-a36cf0430171 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
fb8bc5de-47e4-57d3-b22c-47e0d442529e | note | ○ 0-400 - 2 tests
dbd360f4-d206-5880-b387-88e3ca081fcd | note | ○ 400-1,500 - 3 tests
5cbcd897-013b-5a6c-a59a-ae0807a6e67a | note | ○ 1,500-4,000 - 4 tests
a6128717-e48f-59aa-8763-78defee8615a | note | ○ >4,000 - 1 test for each additional 1,000m3
9842773f-9e36-5de7-80ea-3b4e5aa1aeae | note | – Results to Engineer 2 wks before importing
04cd855a-5a31-59ba-be31-525a435bfdf2 | note | Verification Activity: Activity - HP
13261f3b-e097-56e9-addf-05187d7a3c0c | note | Verification Activity: By - ENG
7a741e82-e911-43a2-8540-bf52bb5b15e8 | signoff | AUTHORITY HOLDPOINT
a5b91b09-f0ed-4a6b-8c6c-b2083fc58a2e | checkpoint | 1.2.6 - Accelerated Weathering
a54312fd-910c-5b9b-8b11-d51ecb58d4eb | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
913b7700-263f-552d-80aa-87d6a50251e2 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
402e788f-fe0b-5ac4-97e3-03186d3a712c | note | Standard / Specification - TCC-IDC IT-4.7.2 table 4.5
b92721d1-db1f-5fbc-ab02-b058c2d4b73a | note | Verifying Document - IANZ Accredited Report
d39ffd4a-be45-5cf8-991b-c21d21b8a9bc | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
c61a6940-5781-5f2f-8a0f-9788c90930f7 | note | ○ 0-400 - 2 tests
e30c15c9-82aa-5b7d-980a-541aade7ee10 | note | ○ 400-1,500 - 3 tests
7623ef95-f86a-5dbc-8ac2-071b359c74db | note | ○ 1,500-4,000 - 4 tests
1f9a0ab2-bdc8-570f-ae6a-f206d8581876 | note | ○ >4,000 - 1 test for each additional 1,000m3
0090cc62-3f4c-51a6-8670-99de19e3ab6d | note | – Results to Engineer 2 wks before importing
688d6218-9a18-530b-aca9-315ef33a36fb | note | Verification Activity: Activity - HP
79f41811-b147-5b89-8bcf-712e107954fb | note | Verification Activity: By - ENG
c35b98b2-5c3f-4546-94db-bd653158ea1c | signoff | AUTHORITY HOLDPOINT
675561b8-4c23-4949-9e30-d865f53592c8 | checkpoint | 1.2.7 - Maximum Dry Density and Optimum Water Content
d99ef3ae-878b-5a1c-a363-855613454f8f | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
f0379e36-baa3-539b-936c-58c034355371 | note | Acceptance / Conformance Criteria - Report Value Only
66f508af-fdbe-548e-91a9-e4752df6ca13 | note | Standard / Specification - TCC-IDC IT-4.7.1
195252ba-fd37-5c26-ba18-06e2a35cc8d5 | note | Verifying Document - IANZ Accredited Report
2d069f57-ce5c-5cac-acab-68673e3dff92 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
3d12868e-ca9f-5f56-b808-672a27e2b79f | note | ○ Results to Engineer 2 wks before importing
a881e161-6728-5087-bcc1-f153822e6c96 | note | Verification Activity: Activity - HP
332a456f-a73f-5b00-845c-c2e1a56c552a | note | Verification Activity: By - ENG
554dda65-a230-4add-b27c-dfb0614a7e18 | signoff | AUTHORITY HOLDPOINT
110c1435-91d7-4112-b823-3644585c5f1d | checkpoint | 1.3.1 - Geogrid
2f9a9ac6-d82a-503d-ae18-625b6d72097b | note | Detail - The Contractor shall submit the full details of the geogrid they propose to use to the Engineer for approval prior to installation.
0f9b6f9c-72be-5d40-a49c-552521dbbb26 | note | Acceptance / Conformance Criteria - Engineers Approval
565685a8-32f4-59c1-bd32-31c86e3509bd | note | Standard / Specification - PS 20.5.2, PS 16.5.13
2da941d1-efba-5563-b6ea-465ade1a23c9 | note | Verifying Document - Data Sheets and Approval
6ad39f3a-0895-577a-abea-ecb49f584d17 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
65f7813b-8007-57a7-bd8b-d8dd70ce3289 | note | Verification Activity: Activity - HP
6979e065-5388-5455-91f3-e422d0533963 | note | Verification Activity: By - ENG
c29a2110-5096-402f-a6aa-ac45ed1164d5 | signoff | AUTHORITY HOLDPOINT
45a20e1b-124a-4a40-834e-31963c4fe766 | checkpoint | 1.3.2 - Geotextile Fabric
b9f92a36-5964-5f80-a70d-297fa2e53c40 | note | Detail - The Contractor shall submit the full details of the geotextile fabric they propose to use to the Engineer for approval prior to installation.
247b30ea-5d15-5fd1-b438-68d9d11f2418 | note | Acceptance / Conformance Criteria - Engineers Approval
2dcfc34a-2396-5529-a32a-0a2f6d5aa3a5 | note | Standard / Specification - PS 20.5.2, PS 16.5.14
68ccab0e-b388-5390-a995-1be840bd7a4f | note | Verifying Document - Data Sheets and Approval
1820bbe5-3753-5c9c-b233-eb045b5270a9 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
9f52433f-276b-5fa6-a28f-a1242a46ad00 | note | Verification Activity: Activity - HP
d53f2752-3c41-5f81-9306-54301ebec36b | note | Verification Activity: By - ENG
1b760c9f-d98c-4cab-b5e6-f6f423ecbb60 | signoff | AUTHORITY HOLDPOINT
13a3a566-6aac-4b77-92c3-f0655cd7e12c | checkpoint | 1.4.1 - Crushing Resistance
81640d17-5800-5808-8736-9632cfda6b33 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
8aaaeb38-b00d-5e56-b122-707af8df425f | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
40168aa9-3ad1-5465-88b8-2035c78f9786 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.6
38ecd5b8-9f27-55b2-8c12-ea1507980f0e | note | Verifying Document - IANZ Accredited Report
804dc38d-e80e-57b2-84f4-925d970d8fdb | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
a0cf04c1-0ada-58d1-8e36-0600f798c7bf | note | ○ Results to Engineer 2 wks before importing
03fa239c-3897-5012-80ac-14241b62e04f | note | Verification Activity: Activity - HP
185c2389-cf63-5b96-803e-9c76c7bd1720 | note | Verification Activity: By - ENG
6d23f32a-16f9-41ab-b7d4-ea3ed7e1cf28 | signoff | AUTHORITY HOLDPOINT
af0311b1-abe4-4b18-943d-99ea69f4a099 | checkpoint | 1.4.2 - Soaked CBR
f0068e49-af82-5086-bfe9-bc890bae5afd | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
dfd137b8-e6b9-5660-b91e-fe9f0f11e567 | note | Acceptance / Conformance Criteria - ≥ 80%
51af7939-acb7-52a7-80c1-cd9b974d7dd0 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.6
e7f27238-6f7a-5ccd-84cb-019844bb71c8 | note | Verifying Document - IANZ Accredited Report
2e52e1cf-8fae-5812-8b67-3a088c4566e3 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
11e0d572-ab55-5723-82e4-2dd0695ded06 | note | ○ Results to Engineer 2 wks before importing
03bfc6cd-a8d8-5421-a0ba-b219581fcb46 | note | Verification Activity: Activity - HP
4fce205d-4b0a-5025-bffb-4a4091f99058 | note | Verification Activity: By - ENG
d35bb480-dede-49ce-a27a-88a75991ca7a | signoff | AUTHORITY HOLDPOINT
4fe27d10-b7d7-4fa5-985e-fc9c5f5160c7 | checkpoint | 1.4.3 - Accelerated Weathering
a048d20b-0c66-511f-8ecd-1d88973a0a35 | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
a4a6ab55-2598-513b-9d37-cad702859ad9 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
0eff7c8d-2dea-54e2-83da-548fce1e186e | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.6
391447c1-ae64-561e-b8a6-45b2b26d0bfa | note | Verifying Document - IANZ Accredited Report
4479d983-d896-5675-8204-1fe62b861bef | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
a0312ac0-8abf-5118-b976-2e45557403f9 | note | ○ 0-400 - 2 tests
7d5af9bd-2413-5505-bd03-2c7ef21a55dc | note | ○ 400-1,500 - 3 tests
46e49765-a1b6-5601-a594-e4089dcc13a5 | note | ○ 1,500-4,000 - 4 tests
6f75d7a0-7407-551f-a931-eb407354a728 | note | ○ >4,000 - 1 test for each additional 1,000m3
8cff7491-36e1-52da-971f-e756ddcbd978 | note | – Results to Engineer 2 wks before importing
c820141d-5c34-5833-ac74-c3c8a2d63455 | note | Verification Activity: Activity - HP
3c5dc38e-c169-5a05-8f01-d7ede8bc2d9e | note | Verification Activity: By - ENG
b79ebcc1-1e11-4c7e-b73c-314a17b7b9fd | signoff | AUTHORITY HOLDPOINT
82510c16-c254-4d90-bb86-c5dc63ac4504 | checkpoint | 1.4.4 - Weathering Resistance
ebf782fc-f6f2-5a1e-bcf6-a702a3ca6f37 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
01742934-b4d9-5922-9f17-b37166f29cdd | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
ab07a7a9-a3d5-5eeb-9048-6afbea3b6955 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.6
83e180db-9555-5483-86b9-8f386f347b6d | note | Verifying Document - IANZ Accredited Report
b69a5ff1-2977-55c0-a21f-fa113f3cf7e5 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
0d278b00-1a7c-5a31-8302-393def200683 | note | ○ Results to Engineer 2 wks before importing
2535cd29-eb6c-5ae3-b897-524419669405 | note | Verification Activity: Activity - HP
67583ec1-e188-528a-973b-fd471616df36 | note | Verification Activity: By - ENG
a140c7d0-cd80-426d-9947-12332cc765a8 | signoff | AUTHORITY HOLDPOINT
b531b905-edc0-45f8-b639-6a066c55f3f0 | checkpoint | 1.5.1 - Particle Size Distribution
359bcad3-da56-5074-a093-2e119873b2f1 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
847ffddf-ddd7-55e9-9334-c61c890fa26b | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
e6297637-e8fc-5b2e-9c39-7858414595da | note | 37.5mm ¦¦ 100% passing
dad6a806-b20f-51dd-b9a1-07fed1250fd3 | note | 19.0mm ¦¦ 60-75% passing
fcbca889-f1b0-57ca-ae47-4a3692e950c3 | note | 9.5mm ¦¦ 37-50% passing
e2bb01be-4579-5414-a385-d770f9b82f52 | note | 4.75mm ¦¦ 20-35% passing
05eabc25-84bc-55a1-8b7e-7e9b9750450b | note | 2.36mm ¦¦ 12-28% passing
fa3b63ee-3262-5ae6-ad12-b64e66611295 | note | 1.18mm ¦¦ 9-20% passing
77ea6a93-5084-5560-96bf-9cdf98a3cbab | note | 0.600mm ¦¦ 7-12% passing
b7b18663-cd2f-5f6c-a9d0-aa4e17e26164 | note | 0.300mm ¦¦ 3-10% passing
02c680e0-c4b7-5001-9fe1-50c421456057 | note | 0.150mm ¦¦ 0-5% passing
11d98c99-ef9b-5293-be3e-16ad8994472e | note | 0.075mm ¦¦ 0-5% passing
4edfc40f-e0df-5147-b95a-84294012d7c1 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
a19046b0-fcf8-5247-b91c-e5a69d386662 | note | Verifying Document - IANZ Accredited Report
69f6be5b-0995-5bb1-8127-6ff2277d7f4b | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
1531907d-280e-5453-b624-da05e6ccccdc | note | ○ 0-400 - 2 tests
f74c235d-fcf8-5224-8e34-d8fa4ae06099 | note | ○ 400-1,500 - 3 tests
6c4ccd61-dc79-5e46-845f-fa760e21729c | note | ○ 1,500-4,000 - 4 tests
c7ac36bd-fe2e-5cb0-a88e-dc0f024238ca | note | ○ >4,000 - 1 test for each additional 1,000m3
c81f1b6e-37bd-5711-b9a6-98354c0cfda4 | note | – Results to Engineer 2 wks before importing
83bffa52-e2bc-59e5-b882-bdd6cd1015ba | note | Verification Activity: Activity - HP
e9655016-0666-5aa9-946f-ce8bdc5396e1 | note | Verification Activity: By - ENG
c09bef73-c727-4050-9dd5-15d6abb831bb | signoff | AUTHORITY HOLDPOINT
a4085223-4615-477f-83bf-75b3da2a18b8 | checkpoint | 1.5.2 - Shape Control
447441fe-c328-5c85-966c-c36a84195cba | note | Detail - Tolerance allowed from approved grading curve (%)
767ead2f-cbe0-5a7c-ae89-59119fa6ea6c | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
f7a95140-4d2c-5fdc-a17e-a664b4e6a76b | note | 37.5 – 9.5 ¦¦ 28-48%
24491fc0-f335-5c08-a880-e9ab9b212441 | note | 19.0 – 4.75 ¦¦ 14-34%
a555d957-12cb-5721-921a-c0283842544f | note | 9.5 – 2.36 ¦¦ 7-27%
6d1b6253-0e18-52b6-ae55-03eeef155ae8 | note | 4.75 – 1.18 ¦¦ 6-22%
1400ec0b-bee0-55c2-9c45-406b5c54cfc9 | note | 2.36 – 0.6 ¦¦ 2-20%
3fe99781-6ff9-5184-b91d-e84a870137b3 | note | 1.18 – 0.3 ¦¦ 5-19%
24e31cd3-69e9-5e96-adc8-3e706c7bf9c0 | note | 0.6 – 0.15 ¦¦ 2-14%
7aa16eea-ada8-5cd3-99c2-a4d4aae776e5 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4..8 table 4.7
66639bcd-e8fe-5582-8c7e-9d59c34fb7a9 | note | Verifying Document - IANZ Accredited Report
7c0e94c9-3465-5012-b20c-1e28d5ed13b0 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
309c85c9-b7e9-5a74-9418-de783d2fc986 | note | ○ 0-400 - 2 tests
50679f23-0288-5cd7-ae43-3536fdb9b875 | note | ○ 400-1,500 - 3 tests
2bca8721-29ca-5ece-9824-8dfbd4497a87 | note | ○ 1,500-4,000 - 4 tests
bfba9c0b-8628-549f-ac7d-5cb725bced1c | note | ○ >4,000 - 1 test for each additional 1,000m3
1419aa4a-991e-52fe-9b82-10a2cfdb51c2 | note | – Results to Engineer 2 wks before importing
6f7c9116-e81b-5586-97cf-940fcc5a6425 | note | Verification Activity: Activity - HP
df0b6faa-761a-5e1c-81ad-a28444a3094e | note | Verification Activity: By - ENG
d42c904c-8777-4c99-a68c-c5ed0f8295db | signoff | AUTHORITY HOLDPOINT
1fca014c-2da4-4716-a61a-9023d01406a3 | checkpoint | 1.5.3 - Sand Equivalent
9757d139-e2b7-5e34-86dd-2c78785c10cf | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
df6c67e0-541e-5c36-8e44-e9c8c610b361 | note | Acceptance / Conformance Criteria - ≥ 40
b5947d74-1f31-5fa7-9864-f78f49cd7dd6 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
fe1738b3-2c91-5b39-9e96-95c2e82d4da2 | note | Verifying Document - IANZ Accredited Report
7eaf99f8-90ff-53fd-bede-13532e175aca | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
a421dede-8c85-5680-8370-720337134a5c | note | ○ 0-400 - 2 tests
dcac68e2-ff79-5111-beb0-0267b5cf8da3 | note | ○ 400-1,500 - 3 tests
e4c5406e-a2a8-5598-9a97-6ab035d01d7b | note | ○ 1,500-4,000 - 4 tests
4146f9f4-a036-562e-addd-63639494378d | note | ○ >4,000 - 1 test for each additional 1,000m3
f82963d9-d69a-5fd2-9910-724e83d9d46c | note | – Results to Engineer 2 wks before importing
84ca94b8-e4f4-5290-b2b7-69f71f30497e | note | Verification Activity: Activity - HP
f2a0855e-44d5-5e1e-99b1-d5817c76fb09 | note | Verification Activity: By - ENG
0d235711-e96f-40f3-a576-196085441cd8 | signoff | AUTHORITY HOLDPOINT
6643fca3-fa00-47cd-b2c5-5574ca61c7c5 | checkpoint | 1.5.4 - Cone Penetrometer Limit
ab1ffced-ce7c-5bee-b7a1-6c257a9fa946 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
e790ad0b-584f-5b82-9f6f-c4774e370a7f | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 30
0aa44b01-ae3a-57c1-b2b9-2b055a74eecf | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
acd1e1c8-fcaf-50ba-94d1-43034c4ea236 | note | Verifying Document - IANZ Accredited Report
88421d08-cd2c-5fe4-842a-b5cc810218ad | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
b30440a4-1b8c-571a-bc1e-4ea1a94382d4 | note | ○ 0-400 - 2 tests
7a17a204-541b-5450-ad18-da82020251b4 | note | ○ 400-1,500 - 3 tests
defb6efd-4779-5b17-b9c7-5703933419cd | note | ○ 1,500-4,000 - 4 tests
ae8c825d-90f2-532f-b235-6c014ae23444 | note | ○ >4,000 - 1 test for each additional 1,000m3
26ab345f-cd14-510e-9048-2217397e1096 | note | – Results to Engineer 2 wks before importing
948a3e06-829a-59e0-ba37-fd7b0a339475 | note | Verification Activity: Activity - HP
bdb43b93-8f1c-556d-ae9f-702e022bafe6 | note | Verification Activity: By - ENG
304d6cba-9124-49bb-8dca-c130d0b40590 | signoff | AUTHORITY HOLDPOINT
39ff164e-0309-47b8-b0b1-13adcf643d70 | checkpoint | 1.5.5 - Plasticity Index
74c582ec-dbdc-5a85-b71b-3237a8a4faa2 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
753d2dc7-6281-5d6f-a02c-008943254878 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
36962953-84e4-59cf-8fe2-663b8e84c3f8 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
93359e71-78e5-5d79-bcca-182aac1560b1 | note | Verifying Document - IANZ Accredited Report
c70e3583-9472-57fd-bf03-620a03b489d2 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
71a7d073-7240-564e-a92b-9a22c9c29c87 | note | ○ 0-400 - 2 tests
a3681a7a-635b-57a2-b2c7-96f09e114b1d | note | ○ 400-1,500 - 3 tests
17279039-3450-5947-861f-f2453e727ee4 | note | ○ 1,500-4,000 - 4 tests
5c6352ea-856c-5454-9331-fe816daa8759 | note | ○ >4,000 - 1 test for each additional 1,000m3
64833d1f-341a-5324-b087-ce0bb20bcf16 | note | – Results to Engineer 2 wks before importing
cc48da61-62f4-5e0c-b583-1fe5d591b4c9 | note | Verification Activity: Activity - HP
7ad2be29-a0ac-57d8-97d2-7e7cf6f9c207 | note | Verification Activity: By - ENG
e1ec425a-b77f-495e-8bde-031b2f691c5f | signoff | AUTHORITY HOLDPOINT
39a761e7-36ae-4e6e-a76f-a2ed10f659d0 | checkpoint | 1.5.6 - Clay Index NZS 4407 Test 3.5
0d9df8d2-6358-58c8-bb49-600aeb1c10fe | note | Detail - Clay Index NZS 4407 Test 3.5
34483ae6-a27d-5551-ba98-f72471fda0c5 | note | Acceptance / Conformance Criteria - ≤ 5
d51a97ac-025e-5965-bdc0-d490d964d7a3 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
d2ab9a89-0cf2-5eb2-9677-9139f7b2c034 | note | Verifying Document - IANZ Accredited Report
c6e33c92-c01c-5103-bf59-bf7e16309245 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
3606e3ea-3eba-5c8d-8e0b-b05df133611e | note | ○ 0-400 - 2 tests
0d2ccca1-e10f-52f7-adfc-7f483ac3cdd6 | note | ○ 400-1,500 - 3 tests
2b00c0ec-e82e-5042-b376-d8a9c8190c9a | note | ○ 1,500-4,000 - 4 tests
3f6b1f52-0b9f-58b0-8911-2a6e4c8ae24c | note | ○ >4,000 - 1 test for each additional 1,000m3
8b4d4d14-adef-5ff5-8746-3204a7fddfae | note | – Results to Engineer 2 wks before importing
bfe23057-aecf-58ba-a96d-e498298587a7 | note | Verification Activity: Activity - HP
e7cf2c39-40fe-5167-876a-690de37e2022 | note | Verification Activity: By - ENG
8bd25786-f21e-4071-843c-3bb76f7c421d | signoff | AUTHORITY HOLDPOINT
e8a9e598-21fb-4de0-9abb-0cf4a660ae80 | section | SECTION 2 – Subgrade Handover from Earthworks
7308ccb7-7838-45e8-938b-5583841c5db4 | checkpoint | 2.1 - QA Submission
e4bbc964-bc8e-5f6a-8b10-bffeda2d3496 | note | Detail - Submit all Subgrade QA before proceeding with next pavement layer
24a57df4-95cf-53c0-bdfb-9e0ad8531308 | note | Acceptance / Conformance Criteria - Engineers Approval
9deff2dd-fc98-5a21-bcbd-610a544e11e2 | note | Standard / Specification - Appendix V
4962789d-2558-5b45-b7be-38d4278092ba | note | Verifying Document - Conqa Siggnoff
2ac3c733-de56-5b5f-a0c1-4cf2daaddd5d | note | Testing Quantity Required (based from schedule qtys) - Once
cd0acd5a-8e03-5329-80e4-12beea20b358 | note | Verification Activity: Activity - HP
6fd688b4-f4ea-5bf4-916e-734284c9f5e4 | note | Verification Activity: By - ENG
2c932a69-9e8e-4854-ab55-082d2353f26a | signoff | AUTHORITY HOLDPOINT
eccf0508-18cc-4501-814c-d701a0d82a4e | section | SECTION 3 – PLACEMENT OF GEOGRID AND GEOTEXTILE FABRIC
a8bd5d15-04fc-4238-bd51-0911118f93ad | checkpoint | 3.1.1 - Placement of Geotextile Fabric
38781f9e-7617-5ab4-af0b-a4d3923056cb | note | Detail - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
171ff38f-51db-5b76-8eef-ee3653751dcd | note | Acceptance / Conformance Criteria - Visual inspection
d401b023-b0b7-5447-b7ca-45c58b976f1b | note | Standard / Specification - NTC0097, 232735.02-WSP-DR-PVS-0401-REV4
74fcff11-97c0-57ab-bcb6-cf8a3fd9011e | note | Verifying Document - Visual Inspection and photos
ce5552e8-ac36-563a-85b1-77cab9dc1d8b | note | Testing Quantity Required (based from schedule qtys) - During construction
f1b820a9-7c1e-51fc-8fc7-ac6d8a6200b5 | note | Verification Activity: Activity - WP
a05e26f9-c0bc-5577-81c0-573963395ccf | note | Verification Activity: By - ENG
2958297b-f911-4e80-935a-a1be5e477ff8 | checkpoint | 3.1.2 - Onsite Check by Engineer on Geogrid
15498564-2c00-59b6-83f3-02201f8c973c | note | Detail - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
861a376b-db19-5b9f-bfd4-ea84984e6280 | note | Acceptance / Conformance Criteria - Visual inspection
3dacdabb-5751-5499-980d-acd638b00293 | note | Standard / Specification - NTC0100, 232735.02-WSP-DR-PVS-0401-REV4
130c4b77-cd01-5ac2-9277-f81a4df964d9 | note | Verifying Document - Visual Inspection and photos
9b38d308-ba49-5ee4-87c3-7322dfaf9b7b | note | Testing Quantity Required (based from schedule qtys) - During construction
05db732c-1423-53f3-ba5d-35946c3b1979 | note | Verification Activity: Activity - HP
8578ca04-93f2-5289-8fbf-b41e5ecfe716 | note | Verification Activity: By - ENG
2ee7f588-e5a0-46a8-987c-e14a4787e7a7 | signoff | AUTHORITY HOLDPOINT
6f1747c6-52bc-469b-80ad-e392202462d6 | checkpoint | 3.1.3 - Placement of Geogrid
f1372f44-c6fe-5364-9a73-523422f9ca85 | note | Detail - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
ee1d1215-0ccb-574f-95a4-fb5e6c97404a | note | Acceptance / Conformance Criteria - Visual inspection
2253898b-ba8c-59bc-8f7b-c19a9bd75db6 | note | Standard / Specification - NTC0100, 232735.02-WSP-DR-PVS-0401-REV4
e418a17c-bb15-526c-bf9e-20e6a0666aca | note | Verifying Document - Visual Inspection and photos
6c8bb0d0-6344-5bd9-9bf0-9000ff115581 | note | Testing Quantity Required (based from schedule qtys) - During construction
b2a0329b-0001-559d-9951-e4d421cd67b8 | note | Verification Activity: Activity - WP
ccf5cad0-8e6d-5e71-a3b5-aac869adadfd | note | Verification Activity: By - ENG
00234583-8c8b-47b6-9bd0-0ac9ce4a2e24 | section | SECTION 4 – PAVEMENT TYPE 6
19544f52-6234-4385-b052-992039c71124 | checkpoint | 4.1.1 - Plateau Density Test
63e37d59-6cf6-53b6-bcc7-ae6c7473e795 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
6908151c-daa1-506a-8346-40090ba39d7f | note | Acceptance / Conformance Criteria - Plateau Density Report
ce1a0036-bb65-5c02-a77a-bd27031bf23e | note | Standard / Specification - NZTA B/02 7.5 (a)
09d1b63f-d28e-56be-9f9b-297b113fc11a | note | Verifying Document - IANZ Accredited Report
724007b4-b369-59a9-bf46-be02b658179c | note | Testing Quantity Required (based from schedule qtys) - 1 Test
ba78a9b7-6e52-514b-9e6e-0f492e0922d3 | note | Verification Activity: Activity - I
7ee45772-cc2a-5f42-bae9-94345a101421 | note | Verification Activity: By - SE
00f7c6e7-a882-4e68-b27f-a421ec29ee1b | checkpoint | 4.1.2 - 3m Straight Edge
e8113d6f-5067-5205-bbd9-b2e83be95f80 | note | Detail - Formation check to ensure surface is smooth
5eba09d8-16e9-572e-9095-656de2d14ab3 | note | Acceptance / Conformance Criteria - +/- 10mm
76188b07-cfa2-565c-a781-63863e0ff48c | note | Standard / Specification - TNZ B/2 7.7
4a60f8d5-3e9e-5880-a12d-c0dfe5a50952 | note | Verifying Document - Check Sheet
f428fcd6-1b2f-58ae-90b6-99997f2757a5 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
13c5b729-5bfb-57b2-8dfc-0299b04a0c10 | note | Verification Activity: Activity - I
ad849b28-52a1-5a2a-bcfe-9efe9fdcfcd1 | note | Verification Activity: By - SE
f39a64c1-f0fa-45eb-a149-2d059616b545 | checkpoint | 4.1.3 - Stringlines or equivalent
a6fb08b4-9c59-5c43-903d-d95a01ef6a65 | note | Detail - Stringlines or equivalent to check finished height of surface
f86d5c37-dc34-5d04-93a8-36e4733a4c55 | note | Acceptance / Conformance Criteria - -25mm +5mm
8af64284-24e5-5b72-acfa-10fc222fa029 | note | Standard / Specification - NZTA B/02 5.1, NTC 349
e207d7fe-043b-5d33-8c9c-a5f5485a7a00 | note | Verifying Document - Check Sheet
425d4fcc-1dc5-503a-93c9-a257b04189e3 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
5b642e90-86b9-5b89-8365-7e436383d225 | note | ○ 1 set = 5 tests
1796476f-7799-5180-a742-fddb3c7312cf | note | Verification Activity: Activity - I
714c4ad5-c61b-5b0d-abff-5ed4da2aa48e | note | Verification Activity: By - SE
fb8de6d9-d276-4c3a-8cf3-fd25dc8bdd9b | checkpoint | 4.1.4 - Compaction - NDM
65af9b82-5d34-5c49-91ee-23e58e7a931b | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
2b25a7d0-6081-5bc7-90a5-88fef3023a82 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
2c3f2ef4-f27a-57b1-a74d-3b225d994ecb | note | ○ Min >92% of MDD
de1e3935-3e76-56bb-a955-57ad06d666bf | note | Standard / Specification - NZTA B/02 7.6
176d2e52-aebf-56d5-afc4-8bc796d4999a | note | Verifying Document - IANZ Accredited Report
51a98758-d0cf-5113-a3d7-1df03eab0bcd | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
d95d8afc-8d49-548e-bced-fa81fc7b1837 | note | Verification Activity: Activity - I
73b58e5b-16a4-582a-b0e1-945342443e7f | note | Verification Activity: By - SE
76966da1-685d-4e9f-a7c4-52a9d5d4dae2 | checkpoint | 4.1.5 - Benkelmen Beam
4dfb6cd2-91ec-50e9-a084-4aa152e417df | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
6927b982-5fac-5a50-8e24-b061a9743d0a | note | Acceptance / Conformance Criteria - 90th Percentile: 2.47mm
edece0e2-14ff-5847-8731-6c74f3834196 | note | ○ Maximum: 2.92mm
2e478966-8ff6-5d70-883a-875b1b822c21 | note | Standard / Specification - PS 20.14.5, NTC0160
b146da68-1087-5b11-92a1-b22dec75ed70 | note | Verifying Document - Test Report
5db6c89a-06d6-5da8-8d23-a3839d20e2eb | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
94bac16a-968b-55a5-9df7-b259fe8271a5 | note | Verification Activity: Activity - HP
2d7a6327-fa19-5572-a313-322573f93624 | note | Verification Activity: By - ENG
f860194e-7532-4ccb-a509-0b95c42c0fdb | signoff | AUTHORITY HOLDPOINT
76895536-21ca-4dd8-8e5c-3e9809169071 | checkpoint | 4.2.1 - QA Submission
d7e737d0-4a2a-5601-a4d4-a08ccdfcf037 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
1adb0985-89e8-5b67-971f-eacd4484e33f | note | Acceptance / Conformance Criteria - Engineers Approval
cfe70835-7640-563e-93bd-89f6e183a36d | note | Standard / Specification - Appendix V
ab56d4f6-dba3-5032-9409-93bb7cc348b0 | note | Verifying Document - All test reports
12bd8487-7916-552b-9599-88e6cb34053b | note | ○ Material Test Results
e98fa0d6-7a8a-58b2-b976-e2168a545c99 | note | ○ Laboratory MDD
cd1e2fea-ec7c-5e64-80c3-63195fcebcd5 | note | ○ NDM results
bf794397-e207-5457-8e2a-e412359acf2f | note | ○ Proof Roll
ae1a3e05-9ff0-5ef5-8aff-6e47967b34a0 | note | Testing Quantity Required (based from schedule qtys) - Once
c92c873a-8ba8-5a0a-9717-037d24e74cbd | note | Verification Activity: Activity - HP
cb26b090-9ff2-5f07-832b-e7bb4afa3332 | note | Verification Activity: By - ENG
74b2e171-29df-4d45-9600-5aa3798920b1 | signoff | AUTHORITY HOLDPOINT
b5be1057-bc41-49c9-826d-634cd8ddf44c | checkpoint | 4.3.1 - Plateau Density Test
f491052d-827d-5bfc-8fb7-ec0fe0fae8ec | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
651baeeb-edd7-56b0-afbf-1efe30a70042 | note | Acceptance / Conformance Criteria - Plateau Density Report
c78cc68e-f57c-5ed3-a79e-9db0f7977e03 | note | Standard / Specification - NZTA B/02 7.5 (a)
857722ab-84fa-58a0-a72e-754d72a762af | note | Verifying Document - IANZ Accredited Report
f9da290b-5024-5c24-803f-27fce8c175da | note | Testing Quantity Required (based from schedule qtys) - 1 Test
143748bf-4731-5e0c-b052-a5892f6415ce | note | Verification Activity: Activity - I
146bdfc6-b41f-51db-8805-b9a017cfcbd8 | note | Verification Activity: By - SE
cb51c35b-f19b-4544-8878-393478912ee6 | checkpoint | 4.3.2 - 3m Straight Edge
6bdd683c-0468-51c6-8160-0c70146e3386 | note | Detail - Formation check to ensure surface is smooth
161cb117-5125-5029-a7ca-c75a73c09227 | note | Acceptance / Conformance Criteria - +/- 10mm
61794eef-7293-52fb-8af9-b3cc90c9ae88 | note | Standard / Specification - TNZ B/2 7.7
3e324855-352e-5c94-ad2b-409453e9d868 | note | Verifying Document - Check Sheet
d51271e4-4d08-58cd-9159-b3d88c1bbdf7 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
d6ad1bd7-cef5-5762-afbd-905ff77349e8 | note | Verification Activity: Activity - I
26ce4d8d-9426-5c80-9a0c-0fde7804a6f6 | note | Verification Activity: By - SE
bbc180ea-be40-468b-b07b-d3307fdbcfbf | checkpoint | 4.3.3 - Stringlines or equivalent
9b6723fc-39bd-5b29-a363-e9a45fdffdd9 | note | Detail - Stringlines or equivalent to check finished height of surface
ff548532-6666-5cbc-9544-7714368bb6dc | note | Acceptance / Conformance Criteria - -15mm + 0mm
e3a7fa60-1d31-5bac-9a95-a91f918804ed | note | Standard / Specification - NZTA B/02 5.1
5f8d538a-39be-57fd-a348-f7881d55ce41 | note | Verifying Document - Check Sheet
25fd93b7-aafb-5ea4-9fbe-02c77060d2b0 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
83147431-55a0-5498-8247-59cc667d0dff | note | ○ 1 set = 5 tests
bf77e08c-3ebb-52d2-9573-f5aee8dba462 | note | Verification Activity: Activity - I
2ff20482-401b-5248-bf2d-24deb83f3c8d | note | Verification Activity: By - SE
7c33de7b-be25-47b2-8969-805631a77076 | checkpoint | 4.3.4 - Compaction - NDM
0cc9607f-711d-5190-9195-e1028dd45cbe | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
794e5e62-7641-5e83-bc8e-69a7d9874f0f | note | Acceptance / Conformance Criteria - Ave >98% of MDD
1e438cdf-d306-5f33-b12a-0bf8ca7ca9db | note | ○ Min >95% of MDD
29c1fc03-06af-5bc5-a332-3ffe3bccdd2e | note | Standard / Specification - NZTA B/02 7.6
233d1a1b-2816-5c12-b143-d5b01559f5bc | note | Verifying Document - IANZ Accredited Report
47218d03-6a75-5dc0-9da7-f2567b79f216 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
d5d47bd4-1b41-57f3-8b00-5d38f5405be0 | note | Verification Activity: Activity - I
2250fb9a-e004-5fb1-a367-ee996c12098c | note | Verification Activity: By - SE
2d967084-d89a-41f0-9b8c-9de3c2cce0c6 | checkpoint | 4.3.5 - Benkelmen Beam
5af1861f-ee53-54bc-a95a-917666be2cb1 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
87ba95bf-a592-52c7-ba39-ca7ce06c9df6 | note | Acceptance / Conformance Criteria - 90th Percentile: 1.85mm
99720cd4-bcd1-50d1-9dda-20dd4430c98b | note | ○ Maximum: 2.24mm
2171bb6b-afc7-530f-9d56-473d2c8a200d | note | Standard / Specification - PS 20.14.5, NTC0160
803449d1-0466-576f-94cc-4801b73cb399 | note | Verifying Document - Test Report
025ba246-e1b5-55e1-b5ba-28810b39b9ad | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
0f6703bc-6e77-5e6f-a0eb-248a1ad55d75 | note | Verification Activity: Activity - HP
bdbf9aff-6244-5659-8a21-d6d0a8b8f2fc | note | Verification Activity: By - ENG
1c2a0acf-8144-4fa4-bcec-5effafbeeec4 | signoff | AUTHORITY HOLDPOINT
ebe5fa09-3eda-4ab9-ade0-24d4f9955d04 | section | SECTION 5 – AS-BUILTS / REDPEN MARKUPS
40a0156b-4915-48f0-ba41-a90e63ecd29c | checkpoint | 5.1 - As-Builts/ Red pen markup
564a767e-467c-5c45-8e30-6808e147e91c | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work
d71e0af9-f707-5ad3-8bc4-cd7d557256bc | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
0b5feb5f-1e51-5943-a865-0fddd0c5f643 | note | Standard / Specification - PS 16.7.6
e9d97572-cbb3-53c0-943b-6739ccfe6308 | note | Verifying Document - Red pen markups
e01b3b93-d153-5f31-8ff0-978b3fcc05b1 | note | Testing Quantity Required (based from schedule qtys) - During construction
01131634-9271-5495-aa73-f103241cfd44 | note | Verification Activity: Activity - D
aaf5e9c6-2b08-5bc0-80e5-ec1210ca374e | note | Verification Activity: By - SV/SE
1c140017-f508-4bd2-9502-b2735a5fcf59 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
0f545c01-0374-57e0-ae48-343d5577895b | textbox | Contractor's Rep Name:
95b56981-e007-5241-91fb-656908f88417 | textbox | Engineer's Rep. Name:
5f694e0a-52f0-5e1c-a75a-3659f06e80a5 | date | Date:
cd9d6bf9-6196-4b57-9ca9-4ce4aa13e0ed | signoff | Add Signature
209aff14-6963-4363-935b-bf765cf6a735 | checklist | DN1210-SP2-006-004 ITP Northern Access Road & Car Park Footpath/Shared path Rev 1 | itp | DN1210-SP2-006-004 ITP Northern Access Road & Car Park Footpath/Shared path
41213aa3-44d4-46cd-8bb7-8a36689c8d30 | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
683dc913-b4c3-4c10-8990-24da3a0a991a | checkpoint | 3.1.1 - Crushing Resistance
061799f5-aa8d-5882-932e-f196601612f0 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
5ecd604b-5783-5992-bbf4-91a61c72f669 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 100kN
1ed4f794-042f-504e-af4e-fc6b7ea57b59 | note | Standard / Specification - NZS4407:2015 Test 3.10 TCC-IDC-IT-4.3.1-4.7.1
048a5ff2-3faf-559a-b197-96dfbc26288e | note | Verifying Document - IANZ Accredited Report
ada07a43-c5e6-5b87-a0dd-7e628e11e8f7 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
f972ff30-d984-5612-8c9d-cab467d70786 | note | ○ Results to Engineer 2 wks before importing
a74af11b-cb99-5458-82b9-58fefefa4761 | note | Verification Activity: Activity - HP
bb815868-b4a5-5909-aa65-9c10c8cde22e | note | Verification Activity: By - ENG
dc644b36-36db-40a3-93f7-a7b5e67bc07d | signoff | AUTHORITY HOLDPOINT
68337365-38c2-46ed-83c7-7c2038ad2d5e | checkpoint | 3.1.2 - Soaked CBR
ca4bcb25-2148-58cd-a762-632ec0e39caf | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
2ada370a-54b8-5d6c-92f0-37749fc7f256 | note | Acceptance / Conformance Criteria - ≥60%
7fe44bc2-8425-5c91-b0ef-6c18e1725395 | note | Standard / Specification - NZS4402 Test 6.1.1 TCC-IDC-IT-4.3.1-4.7.1
7245c85b-4f38-5e8a-9789-4b3f056b266a | note | Verifying Document - IANZ Accredited Report
42813c8d-215f-5fb1-8e92-de3d091f368f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
93e3f520-d0b0-5e55-8585-0495b5906cbe | note | ○ Results to Engineer 2 wks before importing
aa4c2ee9-380e-5558-bee1-63857d1c100c | note | Verification Activity: Activity - HP
772ba502-794d-5be0-9c1c-60cabf807173 | note | Verification Activity: By - ENG
6ba16b4f-ec21-42a1-8553-c1ef5569576f | signoff | AUTHORITY HOLDPOINT
af7a2c2d-19bb-49e5-8b92-9d343433fe07 | checkpoint | 3.1.3 - Weathering Resistance
166a117a-5535-517d-967f-d16ffb4a574b | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
ce212bbf-2173-5079-b6e0-2dc09a2805ef | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, CA or CB
8e162e7b-fb0e-580f-a871-72a2c7488d92 | note | Standard / Specification - NZS4407 Test 3.11 TCC-IDC-IT-4.7.1
3b045e4e-3d7a-5040-82dd-9adbeb228287 | note | Verifying Document - IANZ Accredited Report
9cbc1911-ec36-5032-b87f-9d6e81449fd8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
35033af1-2fef-57e6-bb92-456f257080fa | note | ○ Results to Engineer 2 wks before importing
ae9c12c8-54cf-5828-8394-f4fbeae7e73b | note | Verification Activity: Activity - HP
2e69a515-71d7-58a6-8d74-1debd9e30fe9 | note | Verification Activity: By - ENG
79aabcf7-38d4-4d59-b57f-f2a7ca8e4eab | signoff | AUTHORITY HOLDPOINT
a3e3495e-452a-41d0-a6db-f8a80a5f1569 | checkpoint | 3.2.1 - Particle Size Distribution
0b1e0731-230f-57c1-8cd9-0d75e31532df | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
edcbec09-bdfb-5c85-ac20-74137e33f24c | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
41b067ac-8d5f-59ab-b0cb-3abd4a135d0b | note | 63.0mm ¦¦ 100% passing
4fba2904-a2ed-597c-afcf-307ed87f8220 | note | 37.5mm ¦¦ 68-90% passing
a20a01a1-c09c-5f9a-a186-7f2ae53a4ef7 | note | 19.0mm ¦¦ 42-76% passing
77040784-9a7f-502b-affa-9c6f08349863 | note | 9.5mm ¦¦ 26-58% passing
15fd7c5c-040d-53ad-a581-e1636d3b4049 | note | 4.75mm ¦¦ 16-44% passing
893c096e-f9ea-52d1-8ab7-7ee9533d5906 | note | 2.36mm ¦¦ 10-33% passing
4d4b11ee-6a70-56a9-938e-dfb1d3644d73 | note | 1.18mm ¦¦ 6-24% passing
2557872e-aa7c-5982-bdd0-9f8a9e9473f0 | note | 0.425mm ¦¦ 3-14% passing
bcd206e6-64fe-514f-877d-b7ced6c244bd | note | 0.075mm ¦¦ 1-6% passing
e2dd7a24-48d4-5e91-8e0f-3f3c778ed4b7 | note | Standard / Specification - NZS4407 Test 3.8.1 TCC-IDC-IT-4.7.2
eb78bc90-5777-5e02-9c4e-aa289a9d02a5 | note | Verifying Document - IANZ Accredited Report
a94e0951-f9e6-5183-8699-66d7c7971cf9 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
0119565a-a61e-5fa7-9d24-6add5fbc983e | note | ○ 0-400 - 2 tests
12a16104-9bb4-5902-8f3e-b01e6e673572 | note | ○ 400-1,500 - 3 tests
2bf31ce2-0d09-584b-b149-2f8699ecb949 | note | ○ 1,500-4,000 - 4 tests
99442a3e-681b-57c5-9aff-48a2717b6122 | note | ○ >4,000 - 1 test for each additional 1,000m3
7b202885-bfee-59a2-9d37-b82f5ced120e | note | – Results to Engineer 2 wks before importing
128e5eed-ffa9-509d-8478-73dfaa9c8a11 | note | Verification Activity: Activity - HP
2b602f1b-5630-5ba8-8841-edce5c49c010 | note | Verification Activity: By - ENG
8907a6ad-aa7a-49aa-836e-71876513d39b | signoff | AUTHORITY HOLDPOINT
55a065da-0f7d-4d2a-9655-369934e6c506 | checkpoint | 3.2.2 - Shape Control
c8af4010-802f-5449-804f-880b72029326 | note | Detail - Tolerance allowed from approved grading curve (%)
56fb523a-d8dc-5e80-9c92-17ed2dd2e5f7 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
6626bccd-b6ff-5dbc-966d-a3b22d71d52b | note | 37.5 – 9.5 ¦¦ 34-50%
ed7cc228-b5ca-5f6d-98bb-81b1fb7d5ea9 | note | 19.0 – 4.75 ¦¦ 18-40%
5093e3d2-7d4f-588a-8322-d94d29eec5e3 | note | 9.5 – 2.36 ¦¦ 12-32%
53b3df5b-3b46-5895-9c39-b2041600d6e1 | note | 4.75 – 1.18 ¦¦ 6-24%
15ec4eac-d238-5297-a6ef-e5543489116a | note | 2.36 – 0.6 ¦¦ 2-20%
2f534734-2ee0-5a65-9396-4952c22ebae3 | note | 1.18 – 0.3 ¦¦ 0-15%
aa3fa8ae-7814-500b-9374-55eaea2afbdf | note | 0.6 – 0.15 ¦¦ 0-12%
4b6e4490-7cde-5b82-b2dc-eb0fc842c39b | note | Standard / Specification - TCC-IDC IT-4.7.2
de53c3fa-e2f3-5d70-8630-c1815924aa17 | note | Verifying Document - IANZ Accredited Report
60ce50ed-ae48-5c34-935c-82ceb69b7437 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
b0e1d7f4-0238-544b-b4d6-d63b4f2cebfe | note | ○ 0-400 - 2 tests
c18a30fc-ee2a-5d9e-85cb-ade4ea9af0f0 | note | ○ 400-1,500 - 3 tests
5d9e0154-2e6e-5ea7-91d3-28f1505bfdf2 | note | ○ 1,500-4,000 - 4 tests
c44cba7f-b9e1-5abc-a396-2a6157e5d395 | note | ○ >4,000 - 1 test for each additional 1,000m3
7cbc5995-4236-5b6d-b639-02ca3ea5619f | note | – Results to Engineer 2 wks before importing
d9dadd56-08cb-5828-b785-83f4497b89ba | note | Verification Activity: Activity - HP
ce87e654-b265-50d9-812d-002f1770018e | note | Verification Activity: By - ENG
6a37aff0-690d-4100-88d3-b5db901b5471 | signoff | AUTHORITY HOLDPOINT
134bacd3-e41f-4289-a236-251233469874 | checkpoint | 3.2.3 - Maximum Dry Density and Optimum Water Content
644a2ce2-9692-5184-b6d5-4bb52818fe11 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
1da41076-9a84-5580-a1c0-9186957072f2 | note | Acceptance / Conformance Criteria - Report Value Only
10506244-afd0-527c-8c61-cbcec95e658c | note | Standard / Specification - NZS4407 Clause 4.3 TCC-IDC-IT-4.7.1
9578e376-6a5c-5613-8b07-9b55e8e92563 | note | Verifying Document - IANZ Accredited Report
f5fa2dbf-7934-5564-9db7-9946fc214440 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
15fbb72a-723e-5ee7-bcb3-105a758d4783 | note | ○ Results to Engineer 2 wks before importing
1eb206d3-4db3-5ae1-afdf-a6c138bedb81 | note | Verification Activity: Activity - HP
6ea354bf-4022-52c7-925b-5b926673452b | note | Verification Activity: By - ENG
7962b5be-e7e5-4884-aca7-5e2549fc2d1c | signoff | AUTHORITY HOLDPOINT
91e5a789-7e46-43dc-8b24-92c79c232ab6 | checkpoint | 3.2.4 - Plasticity Index
a7efffdf-547c-51f3-b71f-de255d096449 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
930179df-33eb-5158-8311-76d5ca06fb5d | note | Acceptance / Conformance Criteria - ≤ 8
2b469464-711b-5157-a6db-21a2bac983db | note | Standard / Specification - NZS4407:2015 Test 3.4 TCC-IDC-IT-4.7.2
6097e977-4cc3-56dd-9915-e4e0e7fa54d0 | note | Verifying Document - IANZ Accredited Report
c7a53348-9476-5f2e-b770-6b1f2a9e9ef0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
97a95803-ff43-515b-af21-59b1cdc6a34f | note | ○ Results to Engineer 2 wks before importing
f20974be-232c-5617-855e-f16ae5d45aec | note | Verification Activity: Activity - HP
76950d41-5f32-5d51-a119-79e8fb43553d | note | Verification Activity: By - ENG
7626c5e0-8155-4e7b-b89e-d7b649848759 | signoff | AUTHORITY HOLDPOINT
75adb2cf-ba51-4e0f-8311-541cf0d56b3b | checkpoint | 3.2.5 - Sand Equivalent
99260651-e578-5170-b4c5-ae965caf6ef7 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent Washing method
6d523520-0cd6-5410-9071-2f200518056a | note | Acceptance / Conformance Criteria - ≥25
e1c0970c-48ac-57b8-850d-eff27457c0ac | note | Standard / Specification - NZS4407 Test 3.6 TCC-IDC-IT-4.7.2
e57c74a9-1f71-504f-8050-e7a596c65b25 | note | Verifying Document - IANZ Accredited Report
f6b13295-f635-5b97-b9c0-13d43a41739a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
2fdf565a-faf1-5128-9945-3d26e858c9bf | note | ○ Results to Engineer 2 wks before importing
4a2ea93c-53e9-51a0-bea9-01d2079dafa7 | note | Verification Activity: Activity - HP
326f0670-6c02-53bc-a2e0-cab654ea3a32 | note | Verification Activity: By - ENG
623f96ee-4430-473a-adc3-2f511bf064ea | signoff | AUTHORITY HOLDPOINT
a5223fc2-e16c-4129-b5ed-8fd71eaed529 | checkpoint | 3.2.6 - Accelerated Weathering
1e64722b-770b-5080-9b87-85699aa1d60d | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
7b244472-ed4e-5179-818a-bc35762cdd85 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
3186a1bd-1c83-506f-97c5-bdaca70f8074 | note | Standard / Specification - TCC-IDC IT-4.7.2
0fc62be8-4563-55ee-8f1b-baa3e71e45f7 | note | Verifying Document - IANZ Accredited Report
c8dee97c-ae47-5661-a7e7-d6ffffaf9153 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
f072e3e9-e53e-5479-b1ed-95c9e2b971b8 | note | ○ 0-400 - 2 tests
1663837c-f9cc-51ee-9383-c0aab2247697 | note | ○ 400-1,500 - 3 tests
0a993364-4444-5949-ba4f-b7f547e7cc5e | note | ○ 1,500-4,000 - 4 tests
65ba79ed-c25e-524c-81a1-f7f512f62920 | note | ○ >4,000 - 1 test for each additional 1,000m3
aed7eb97-cbc2-54a9-99af-31b525dad9a9 | note | – Results to Engineer 2 wks before importing
91edfa23-8295-5703-a3bd-de63af7e13b0 | note | Verification Activity: Activity - HP
736acdf3-5915-5145-b5de-8ec75bad029e | note | Verification Activity: By - ENG
b13b8dbf-3ffb-4d90-bcda-127a49975891 | signoff | AUTHORITY HOLDPOINT
8e7bc8c4-c8fe-4c58-8606-92bd9b45c8d0 | checkpoint | 3.3.1 - Crushing Resistance
8f0ac916-1d00-5989-b807-773e21101ff2 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
a7ca51e0-076f-50e5-a1e2-a361a2c481f0 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
93ee17b3-49aa-5f09-a8c9-26689c224e89 | note | Standard / Specification - PS 20.9 TCC-IDC IT-4.8 table 4.6
3d732799-277b-5d1d-a450-61ccc454fb78 | note | Verifying Document - IANZ Accredited Report
f68196f6-62e7-5caf-b614-bf64cf64fdcd | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
c1a70227-10bd-5525-b3c7-1b77cba396a5 | note | ○ Results to Engineer 2 wks before importing
05c112c5-c91f-5bb6-8232-a244e9ae5341 | note | Verification Activity: Activity - HP
933557b0-e6c1-56de-a942-469fb7b212cc | note | Verification Activity: By - ENG
17bf537a-5a7b-452b-a9ba-0a94c2d8789b | signoff | AUTHORITY HOLDPOINT
04fed827-5d90-40af-a04f-8a22d2513b60 | checkpoint | 3.3.2 - Soaked CBR
3281f929-a14b-5184-944d-55b8c7dc8799 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
b082f930-9a02-55cf-a279-373548934094 | note | Acceptance / Conformance Criteria - ≥ 80%
83abad04-3e6e-5350-816d-832f82a48d98 | note | Standard / Specification - PS 20.9 TCC-IDC IT-4.8 table 4.6
a228de49-e7c0-5fc8-b31b-eb8f00eb7474 | note | Verifying Document - IANZ Accredited Report
fc33d47a-b44e-5590-9857-b7c29ab0af9e | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
1587de4a-f4da-543d-af0a-05510ef13c6a | note | ○ Results to Engineer 2 wks before importing
a0b16d98-a52e-54e5-80eb-d99cf355e137 | note | Verification Activity: Activity - HP
1146dbf9-ec11-5008-a025-565f0f6637d7 | note | Verification Activity: By - ENG
2d82200d-eaac-4ea7-8b15-d8980b71131f | signoff | AUTHORITY HOLDPOINT
341bc8ed-78ec-422b-9323-1492cd140010 | checkpoint | 3.3.3 - Accelerated Weathering
5d97ada0-9f58-5760-a50e-5ec6b477b514 | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
2e30d6fd-27dd-5c75-af4b-29dffbb9a964 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
58372268-e042-5007-b281-cbea061bc120 | note | Standard / Specification - PS 20.9 TCC-IDC IT-4.8 table 4.6
48d1f6c3-19ff-5646-b1d1-42378a0fb43c | note | Verifying Document - IANZ Accredited Report
1ca6d4dc-15c9-5b45-8db2-3c752e998559 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
5b9c5102-91c5-5a42-bd54-2791922ea3d2 | note | ○ 0-400 - 2 tests
5027d91d-e5d8-5d16-9dcc-c07acc43e164 | note | ○ 400-1,500 - 3 tests
b8b82c91-2f54-5f35-800b-016f7406d6ae | note | ○ 1,500-4,000 - 4 tests
539e06d9-025a-5107-a459-3940467d4e07 | note | ○ >4,000 - 1 test for each additional 1,000m3
33daa6e4-73a2-5f55-aedb-ce213cfcca35 | note | – Results to Engineer 2 wks before importing
608ce464-7586-52cb-af47-cab02c599daf | note | Verification Activity: Activity - HP
79611eab-f4ee-5bf9-844c-a0d49193ae75 | note | Verification Activity: By - ENG
378a4497-2d01-4f37-bcd4-526e3685cd0b | signoff | AUTHORITY HOLDPOINT
c171529b-464d-49ae-b376-e60fc635bc9e | checkpoint | 3.3.4 - Weathering Resistance
2a3f1af3-985c-52fe-b8d9-a9e0da4ca2da | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
71354341-c7e8-5ea4-9b3c-da6f6181ed93 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
94fe3f5e-0801-5727-a827-c4fe7b212ac3 | note | Standard / Specification - PS 20.9 TCC-IDC IT-4.8 table 4.6
e36bc98a-ea6d-58a7-93b8-3378d94fe92b | note | Verifying Document - IANZ Accredited Report
31d16c94-f3de-5780-963c-e87105787218 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
2b9151f7-f4f7-5b5f-a16d-52c8e45b0133 | note | ○ Results to Engineer 2 wks before importing
81f07c46-30e0-5e98-89f2-eff34e345cda | note | Verification Activity: Activity - HP
ada56846-2d8f-5e56-8a75-b956f683fe71 | note | Verification Activity: By - ENG
fdcf3077-bafd-44f3-9fee-f307d61c0716 | signoff | AUTHORITY HOLDPOINT
befbe407-14df-438f-91a2-57245c7da648 | checkpoint | 3.4.1 - Particle Size Distribution
b2adb7dd-1cee-5d97-a978-b43eb47aed55 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
be3e64c9-451a-5f7e-ab52-650e2f458143 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
8e42d8b3-cd48-506d-ad35-615581985b4e | note | 37.5mm ¦¦ 100% passing
85b1e584-5673-53b0-856f-cfb8e7fc8cca | note | 19.0mm ¦¦ 60-75% passing
0dad3deb-b2bf-5d2c-ad3f-a015f0b838b4 | note | 9.5mm ¦¦ 37-50% passing
d314608c-7fa9-5485-937b-913c7ef8dc89 | note | 4.75mm ¦¦ 20-35% passing
7dcfae0d-5c24-54e4-8320-f531642909d2 | note | 2.36mm ¦¦ 12-28% passing
7d7e5f3d-81ed-55de-8de6-2fa0a320f4d7 | note | 1.18mm ¦¦ 9-20% passing
1fa97c0e-6d10-5a5b-afa4-9f90237664a2 | note | 0.600mm ¦¦ 7-12% passing
9fa2d486-409c-595f-8e2e-26a22ea61b30 | note | 0.300mm ¦¦ 3-10% passing
425e3285-d0d1-51e3-996e-8bb756b0a9b9 | note | 0.150mm ¦¦ 0-5% passing
ec95c9d0-26d1-5161-899f-935cd2ce44a0 | note | 0.075mm ¦¦ 0-5% passing
264c5f53-36dc-5822-a1b6-13d5b0a617f1 | note | Standard / Specification - PS 20.9 TCC-IDC IT-4.8 table 4.7
218acf70-4597-55e6-9c5d-28cd30327ba0 | note | Verifying Document - IANZ Accredited Report
f7ce4af3-6f99-572e-88a9-6baed54736ec | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
3097330f-f990-5cd3-8207-7b65367dd076 | note | ○ 0-400 - 2 tests
7103d953-9e4f-5e62-bb60-c077ca1caaa8 | note | ○ 400-1,500 - 3 tests
381251e4-87f3-51bc-bf77-0223af69e741 | note | ○ 1,500-4,000 - 4 tests
6c6a1cd4-a350-5aaf-9fee-6077595ca0ce | note | ○ >4,000 - 1 test for each additional 1,000m3
f67a66ca-d71e-5eda-891b-5e3b6c9cfad6 | note | – Results to Engineer 2 wks before importing
1b72a0f3-009c-5740-a521-7b2b3fb17e0b | note | Verification Activity: Activity - HP
22ad7a83-86e7-5815-9d48-552d861d8a2d | note | Verification Activity: By - ENG
7ae9dbc8-0d10-4bad-80a3-786cefb2482a | signoff | AUTHORITY HOLDPOINT
017a87b7-f6e6-4973-8705-d193d5ad3fce | checkpoint | 3.4.2 - Shape Control
85d08952-86e5-5df9-ae05-ad73d4f3ea7d | note | Detail - Tolerance allowed from approved grading curve (%)
8e5fb0a3-d65f-52db-89de-a79718e13b00 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
72580833-e158-57ec-812c-37b4c3709b54 | note | 37.5 – 9.5 ¦¦ 28-48%
38e89587-c82d-5a20-9caf-eddb29bb0301 | note | 19.0 – 4.75 ¦¦ 14-34%
c03f3e48-f9d2-5b46-847b-c1201b51e8c5 | note | 9.5 – 2.36 ¦¦ 7-27%
c9c2180f-db55-5398-90bc-25bf656eedc4 | note | 4.75 – 1.18 ¦¦ 6-22%
2f138844-9acc-532c-8e30-1f572a20d642 | note | 2.36 – 0.6 ¦¦ 2-20%
d54deb47-539b-5510-9c25-f1ef5793fce5 | note | 1.18 – 0.3 ¦¦ 5-19%
15a90b42-fdbb-5212-891c-e47a74cbaac4 | note | 0.6 – 0.15 ¦¦ 2-14%
2c884dec-f712-5d9e-935b-c26d40d2afd1 | note | Standard / Specification - PS 20.9 TCC-IDC IT-4..8 table 4.7
378ab2d4-b367-5410-b2b4-193c613c5bba | note | Verifying Document - IANZ Accredited Report
2cbd0191-edba-5c79-8011-afaa31c14ab5 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
3758238d-78e7-5eb7-9352-cbb09283add0 | note | ○ 0-400 - 2 tests
7b3896a3-6896-5d4d-8526-46b026e76017 | note | ○ 400-1,500 - 3 tests
9ecacdce-afe4-583e-a338-30ac1f27aaed | note | ○ 1,500-4,000 - 4 tests
9864b282-ad4d-5e6a-a7d3-bf5bff09b89d | note | ○ >4,000 - 1 test for each additional 1,000m3
1871dccd-b3cc-5421-bfbe-a0aa3a47904d | note | – Results to Engineer 2 wks before importing
c2efe528-5db8-5b25-b5e1-21988bd69128 | note | Verification Activity: Activity - HP
be0e1cdd-d35b-5b08-b240-998ea2e2ed5a | note | Verification Activity: By - ENG
d23b3668-b1b4-43ed-b1ce-69d4a41cc8c8 | signoff | AUTHORITY HOLDPOINT
10d6f38f-54fe-4df6-9914-f913beea77a6 | checkpoint | 3.4.3 - Sand Equivalent
a168cd62-f68c-583f-bbc4-1b54f52ff00a | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
1d047ea0-68a9-5641-9d58-cd2f71f52650 | note | Acceptance / Conformance Criteria - ≥ 40
f11901ea-c34e-5baa-8243-940f9cd2da4e | note | Standard / Specification - PS 20.9 TCC-IDC IT-4.8 table 4.7
ecab70b6-aaad-5330-900d-d5cd48f17cd4 | note | Verifying Document - IANZ Accredited Report
2e46e178-8d2a-5822-854d-59f4e4a0fd11 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
e6ee07c8-ae57-5658-b3f8-082dd6e6086c | note | ○ 0-400 - 2 tests
aade8906-210a-5963-97f0-80ed23ddcd69 | note | ○ 400-1,500 - 3 tests
76df69f0-130e-5403-9e4c-9076035df761 | note | ○ 1,500-4,000 - 4 tests
e5facaf0-5e67-5ec1-906d-ada3d2e4f46d | note | ○ >4,000 - 1 test for each additional 1,000m3
54f62961-4c17-51d3-8c93-fe4b02f04970 | note | – Results to Engineer 2 wks before importing
d55083ee-2421-5472-a886-eb22396eac77 | note | Verification Activity: Activity - HP
f1830a8d-17ee-5ee2-ace5-ad816f90ab1f | note | Verification Activity: By - ENG
c5b09494-3c7d-4d8d-9957-3b84c9ab17df | signoff | AUTHORITY HOLDPOINT
3962f358-3261-442f-923f-3d8a6d746fb0 | checkpoint | 3.4.4 - Cone Penetrometer Limit
ab60dfff-63c9-5c09-9c0f-93e732ca8f15 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
84adb2fb-29ca-52c9-81ab-0a850f889318 | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 30
6fceaaa8-e2c8-571f-bbb8-35c9ba506f67 | note | Standard / Specification - PS 20.9 TCC-IDC IT-4.8 table 4.7
0a72db03-f91e-5fd8-868d-ae513da45535 | note | Verifying Document - IANZ Accredited Report
16d0c77a-5559-58a1-8287-ffb749499017 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
cbcf7599-4c8e-5c67-b4df-d534635a6311 | note | ○ 0-400 - 2 tests
ede3f44d-7708-5f52-a40d-aabd839b88bd | note | ○ 400-1,500 - 3 tests
66680017-f0fd-5d58-a473-1c5d6d98afd7 | note | ○ 1,500-4,000 - 4 tests
21d3740b-a0fd-5b8e-9b07-80d8353df437 | note | ○ >4,000 - 1 test for each additional 1,000m3
00850523-60ba-5f21-90c2-3e02993ace31 | note | – Results to Engineer 2 wks before importing
aa9bb2f2-9b49-53ec-a90e-e1bceeb96734 | note | Verification Activity: Activity - HP
6198a299-a2c6-5148-b149-895722d2371a | note | Verification Activity: By - ENG
3540d536-9446-4638-8959-b66068f33440 | signoff | AUTHORITY HOLDPOINT
9b535de8-22df-4ffd-9885-d60dc7d9f5b2 | checkpoint | 3.4.5 - Plasticity Index
a1159dff-9c70-5aa5-9395-8f2661ff7f8d | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
a2e8df55-80a5-5c63-9684-b30663542788 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
793cc5cc-eb9a-5ada-bcc0-c4d84691e9c3 | note | Standard / Specification - PS 20.9 TCC-IDC IT-4.8 table 4.7
30d1e08f-4f14-5de5-95ca-4b37a1d098d1 | note | Verifying Document - IANZ Accredited Report
4039c687-9c25-5725-9d3e-86f3a063c870 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
9cad3718-5346-58b7-8340-7d0b88500362 | note | ○ 0-400 - 2 tests
5e19954a-d3bc-59d7-9233-49a417d67336 | note | ○ 400-1,500 - 3 tests
e006e1ef-27c6-5dd0-a357-911976178d7a | note | ○ 1,500-4,000 - 4 tests
10032dcf-b865-5d76-b469-b5c18c02df3a | note | ○ >4,000 - 1 test for each additional 1,000m3
d8cffee0-edfd-580f-9e87-c8df5eeaa086 | note | – Results to Engineer 2 wks before importing
425560c4-6c24-5186-8bd3-dcbeddea903d | note | Verification Activity: Activity - HP
aaf8f6f1-b132-5354-b8bd-e875edbbf0d5 | note | Verification Activity: By - ENG
f23a53a0-dbf2-4665-9be6-09169ece540a | signoff | AUTHORITY HOLDPOINT
04f796ee-6028-449f-b7da-1eff79291e7e | checkpoint | 3.4.6 - Clay Index NZS 4407 Test 3.5
c34cbebc-61da-5889-b5cf-08bc6f792bf9 | note | Detail - Clay Index NZS 4407 Test 3.5
12b01be6-a2e6-5437-b717-00a76a0a7990 | note | Acceptance / Conformance Criteria - ≤ 5
828dcb9e-7430-596a-9e62-aff9ff0b9eda | note | Standard / Specification - PS 20.9 TCC-IDC IT-4.8 table 4.7
07e12738-cd76-5cbe-8d6c-845ea0b7de76 | note | Verifying Document - IANZ Accredited Report
e72bc67c-fb13-52dc-b490-9ab8e21765e0 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
1535a518-b5d4-5d4d-9d8c-d8896382126f | note | ○ 0-400 - 2 tests
e90b5c5c-93f3-57ea-81b3-40c92ebfae7e | note | ○ 400-1,500 - 3 tests
7b9cf0c4-fd63-584c-a4f9-5faff046653e | note | ○ 1,500-4,000 - 4 tests
aea303da-490f-55b0-9a11-906ec0e88ce2 | note | ○ >4,000 - 1 test for each additional 1,000m3
e639cfcd-4315-5bde-828b-5141b828ca8a | note | – Results to Engineer 2 wks before importing
2514f2b5-b087-5823-8245-0cde2b481986 | note | Verification Activity: Activity - HP
10f82dca-12d7-5806-b391-0cfea700523f | note | Verification Activity: By - ENG
6c71a21b-b1e6-47c4-bdab-75dee2a3adab | signoff | AUTHORITY HOLDPOINT
38c4925a-942d-496c-ad4c-d42a7c5c1b49 | section | SECTION 4 - CONSTRUCTION - PREP FOOTPATH
7513e780-0137-4341-9837-8de384f797f8 | checkpoint | 4.1.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
bbbec647-dc8a-5a73-9df0-0c6a7ea28b75 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
ea65ba42-a7b2-500c-8db0-5b4d452a6a29 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
f34ac56b-a2e1-5a7b-a09e-1509c8e65599 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
01c9d5d1-477e-521c-8b5c-427717110c43 | note | ○ CBR: <3
60d4b635-978a-5415-a42e-70d63a77bfcc | note | ○ Single Test Min SU: >50kPa
d1559613-56f8-5ba2-925a-7fc5cbffc0c5 | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405 PS:27.4.2
53ee11ea-8369-5160-a521-928bc37592d7 | note | Verifying Document - Shear Vane Report
fca559af-74f0-530e-b8ff-8463e268bd54 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100M2
52052f51-81bf-51fa-83e6-9d63b23b5f74 | note | Verification Activity: Activity - H
bda43d12-e9e6-5b9b-ad58-f1d2f08590d5 | note | Verification Activity: By - SE
5628d71b-f0c7-42f4-8fce-e35b9e3b9f5c | checkpoint | 4.1.2 - Cut Subgrade Testing - Granular Scala Penetrometer
8edabdde-949a-50fc-b811-159371c5b84d | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
b1a9b4ea-cdba-5212-8021-4e5e1e728fc6 | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
3763ec3d-e549-5861-a776-5f80794350fc | note | Acceptance / Conformance Criteria - Minimum 2 blows per 100mm penetration or <3 CBR
df65e4fb-94d7-5faf-a800-5fd073aa36e3 | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405 PS:27.4.2
914fbb42-3d79-5099-91e7-449fb2bceb06 | note | Verifying Document - Scala Report
39d78db2-6c26-54ca-8b4a-38e54b8671e2 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
308067a9-7dec-5451-b041-0b77ef5bb62f | note | Verification Activity: Activity - H
232d057f-7b7c-5f6c-ba05-a3a4a48c05e9 | note | Verification Activity: By - SE
877c12fb-ddc9-4970-9457-af9fd2060b95 | checkpoint | 4.1.3 - Proof Roll Subgrade
1a83c531-d133-56e2-8728-73907ca21cf9 | note | Detail - Visual Inspection of Proof Roll
b030e17d-62df-5576-8fd8-20c101fceb82 | note | Acceptance / Conformance Criteria - Visual Inspection
6fbbb1c2-6b09-504b-8eab-06306399939e | note | Standard / Specification - Appendix XVIII
a23a241f-11f9-5f6e-984f-947598abeffb | note | Verifying Document - Visual Site Record
f02cb1cd-68ea-55fe-bea0-78a9cf4d89ef | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
5a6dd822-cc7f-57e0-80af-a1bddc609926 | note | Verification Activity: Activity - H
76745e3c-9cfd-5197-84a6-0097b52b4263 | note | Verification Activity: By - SE
c98977f2-4e92-4d9b-a955-0ec85e382713 | checkpoint | 4.2.1 - Stringlines or equivalent
fcb44751-f247-569a-8c2a-7e2e4617b753 | note | Detail - Stringlines or equivalent to check finished height of surface 225mm Below From Finish Height
1b2e2938-6950-501f-9c48-2722b62915eb | note | Acceptance / Conformance Criteria - +0mm/ -30mm
2db3081a-4716-5332-9fad-e6e77917a07e | note | Standard / Specification - TNZ B/02: 2005 5.1
e69b4cc4-b07e-5b62-a5eb-1024e75be6f5 | note | Verifying Document - Check Sheet
cc3bfc71-a927-571c-a5b8-2e7625f2e4c2 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
0fd5ae74-1d81-529f-8637-3e371f07690f | note | ○ 1 set = 5 tests
977c76d1-4b7d-5a28-b357-5e6c7f7b3eea | note | Verification Activity: Activity - H
32a6f22a-5f15-557c-a564-77c5673f56c0 | note | Verification Activity: By - SE
bcb67a3d-7fba-4c28-83a0-bdd906e9e521 | checkpoint | 4.2.2 - Compaction - Clegg Hammer
3c55ecfe-abbf-5528-a43f-6b9dcad61011 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
823f96f3-e4b8-57cc-8183-2cfdad5ca7ef | note | Acceptance / Conformance Criteria - Min CIV 18
5808c9cb-a83e-5e07-977d-f32ce228fdbb | note | ○ Ave CIV 20
ef535ade-3d24-58fd-89c8-98454eb29dbe | note | Standard / Specification - Appendix XVIII
0e02052e-51f3-5dce-b71b-e8a507c5ad9a | note | Verifying Document - Clegg Hammer Report
2ea0c37b-44ec-509a-b355-834936447a85 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
0785b7f4-9a91-5d44-bb37-693ef2ebf665 | note | Verification Activity: Activity - H
f8685b67-f9fe-5bab-a726-a689104723c8 | note | Verification Activity: By - SE
41f0e4b0-6b7e-4820-aec9-731d509fa18b | checkpoint | 4.2.3 - Compaction - NDM
36701f35-e184-5caf-9eb3-75cf364ea90b | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
97508192-3172-54b3-90a2-21bfafd4fbf4 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
9de02dc4-626f-5c5e-aa7b-eb7d8e697664 | note | ○ Min >92% of MDD
718a5b4c-968a-5c6a-a84c-ecfa54fc3a81 | note | Standard / Specification - Appendix XVIII
82f15606-5a87-5699-99d2-89e7f28a9647 | note | Verifying Document - IANZ Accredited Report
e07a2091-56e8-52e5-9cb7-9ecdfe83a503 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
3b2f69a3-4e0a-598f-b1e2-815c18ca645a | note | Verification Activity: Activity - H
74cb388d-93a8-5c17-b3e7-6a53814798a5 | note | Verification Activity: By - SE
31c7f058-7e08-4668-9a8f-4011ac174ba8 | checkpoint | 4.2.4 - Hold point
becefe13-7eaa-5f5f-94aa-a62671ecd69d | note | Detail - Subbase signoff
6ec3d351-0566-5ef0-8fc3-6b6b23280bfb | note | Acceptance / Conformance Criteria - Conqa signoff
80051a6c-b836-581f-865a-253b41e84b1f | note | Verifying Document - Conqa signoff
5d9bfa03-ae71-5811-b796-ee361618284d | note | Testing Quantity Required (based from schedule qtys) - Each area
875aa57a-7b00-5dcb-ba1c-27f5bfae5ed7 | note | Verification Activity: Activity - HP
23a2cdc7-7e1d-5bcc-bb8f-73aa1c3b2d5f | note | Verification Activity: By - ENG
07b36cd3-db50-4cd4-b6ef-6a9c4eebb6d7 | signoff | AUTHORITY HOLDPOINT
71821503-3fdd-4c2e-8913-bbd5286976df | checkpoint | 4.3.1 - Stringlines or equivalent
fbf39789-f745-5c5f-aa0c-011c47f17e9a | note | Detail - Stringlines or equivalent to check finished height of surface 125mm Below From Finish Height
67ab8fea-7aba-5f56-9410-93dfb573d752 | note | Acceptance / Conformance Criteria - +15mm/ -5
c91c39f1-99b4-5817-abcc-d1e7e9ca2291 | note | Standard / Specification - TNZ B/02: 2005 5.1
0644e6cd-0c6e-59c6-b3f2-49590b603737 | note | Verifying Document - Check Sheet
6f524334-c184-54ca-ba21-e1c930eee3cf | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
af4351f0-3d13-5fa2-8ad0-a29816752dd0 | note | ○ 1 set = 5 tests
8e174397-57db-5f6b-9f38-d77a8ccc8feb | note | Verification Activity: Activity - I
39c893e1-430c-5bca-9ab6-f5230a731e5b | note | Verification Activity: By - SE
8efaa154-6ec3-4497-a8aa-dc4c7a69f328 | checkpoint | 4.3.2 - Compaction - Clegg Hammer
81f130de-065a-5877-b121-c101a1de8e41 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
99d4f560-2a9d-531a-8b38-3caf0ba05cdb | note | Acceptance / Conformance Criteria - Min CIV 18
c171c4f4-996c-59c5-8d07-cdbc01617620 | note | ○ Ave CIV 20
abe34bda-e750-57c4-b13b-71178f3dc7da | note | Standard / Specification - Appendix XVIII
2b389ae1-32a6-5779-bb0c-ad9157062f01 | note | Verifying Document - Clegg Hammer Report
6fd3dff1-ce7c-5a4d-9e0c-0c6fcd3950bc | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
9476be6f-d57b-567c-9608-ed8c88d12f4a | note | Verification Activity: Activity - I
e911b977-cdc0-5b9c-9536-3c3594dafeaa | note | Verification Activity: By - SE
a5b45ded-e75c-48a7-96d1-6898da0bdf06 | checkpoint | 4.3.3 - Compaction - NDM
7a3b7761-b9e5-5273-987b-24de156848a9 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
423555bc-f6e3-5d82-acca-85c2a2f08305 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
0b9ede9a-e2bf-50e7-a535-7bc764a3c53a | note | ○ Min >92% of MDD
b286e07c-2d33-5f6d-ac16-72333c2f31da | note | Standard / Specification - Appendix XVIII
7b48145a-4c60-5287-91a8-7dc3811a6471 | note | Verifying Document - IANZ Accredited Report
0a8226b3-4517-5793-bdcb-8f818a6771c8 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
b0ec946d-f516-5414-95e6-256ae84f3d93 | note | Verification Activity: Activity - I
c7976f38-1672-517b-8568-42d8317dc679 | note | Verification Activity: By - SE
3f41dac4-ad9d-4d97-84f1-8588af0b1482 | checkpoint | 4.3.4 - Hold point
71656193-6dbe-5dd3-b052-57ff97e4046c | note | Detail - Basecourse signoff
6a1575af-4c96-5394-862a-9a01ee5463f6 | note | Acceptance / Conformance Criteria - Conqa signoff
93f12067-1c9f-5ae3-93bb-eafa166c7f6c | note | Verifying Document - Conqa signoff
c437354c-924c-5a4e-9fa4-f18cfeced8f1 | note | Testing Quantity Required (based from schedule qtys) - Each area
94ae545b-2ccc-50c9-87d8-ce78db32b969 | note | Verification Activity: Activity - HP
8aeb9f1a-e3b8-5dd8-8214-61e45cd2ec27 | note | Verification Activity: By - ENG
998e8b35-499a-4653-b11a-1f39137bff2f | signoff | AUTHORITY HOLDPOINT
d60dcb69-8fe8-450e-b28a-d80e5586f586 | checkpoint | 4.4.1 - Surveyor check
b701b3e3-e125-5fdf-986d-6aae47c4bcda | note | Detail - Equivalent to check the position of the formwork
ee821c24-d19c-5bb0-8a8b-196c6823fc6f | note | Acceptance / Conformance Criteria - +100mm/ -20mm of design
6879d593-86a7-5de7-a636-0c1efb2537e5 | note | Standard / Specification - TNZ B/02: 2005 5.1 PS:27.4.5 viii
44a3194c-1ecf-5815-915c-783c2ebbeeda | note | Verifying Document - Check Sheet
8b926bc2-ffc0-5636-b84c-9d75ed5c363c | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
37cae08f-1e69-5363-8e68-58f85094415f | note | ○ 1 set = 5 tests
c9b0d6b5-416c-561b-be7c-c72562f2fb02 | note | Verification Activity: Activity - HP
259d08d5-4e4a-54fb-8fbd-0288e9ea05a3 | note | Verification Activity: By - ENG
9b015801-a67b-4ebd-8832-8119fd3ccfd3 | signoff | AUTHORITY HOLDPOINT
1d547f54-a2c7-493a-aab4-85b01d53ed65 | checkpoint | 4.4.2 - Surveyor check
7979cfa2-1b36-59ee-9ad7-cde05b92cebe | note | Detail - Equivalent to check finished height of framework
d3920885-e31a-5e6c-90fc-2ebdc4cf998a | note | Acceptance / Conformance Criteria - +\- 10mm of design
ec4e844e-cb89-5561-9f4a-25280cf0f50f | note | Standard / Specification - NZS 3109:1997 PS:27.4.5 viii
580142ef-eadc-5887-871b-d80e19733aaa | note | Verifying Document - Check Sheet
7513da25-bc11-588e-99bb-5abcfdcea602 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
e5ffae27-a831-580e-b479-5fe794cb5116 | note | ○ 1 set = 5 tests
5248f6c9-6690-5f77-a16e-87a2030ad008 | note | Verification Activity: Activity - H
74c6ca71-3b67-5396-9ab5-4b5716d7f4eb | note | Verification Activity: By - SE
a891e089-346a-45ed-b201-a42ec2483edd | checkpoint | 4.5.1 - Reinforcing Mesh Check
3eb0137d-9f87-5683-ba61-d8cf2d198595 | note | Detail - Ensure the right mesh
6597a543-a649-5943-852a-f61ceb40ef96 | note | Acceptance / Conformance Criteria - 665 Reinforcing mesh
885ccd27-cff0-533c-9ae8-55954386575f | note | Standard / Specification - Project Specifications 27.4.2
19d0a242-884f-5468-a756-cf411f667a48 | note | Verifying Document - Dockets
5a758a75-09ca-5278-bae6-b9933f726abe | note | Testing Quantity Required (based from schedule qtys) - Measurements
53a7d340-ab6e-5300-9002-3e21fafca82b | note | Verification Activity: Activity - C
eed709d2-3d6e-59d8-8211-d936f15345e9 | note | Verification Activity: By - SE
96b56c88-1c64-446b-a55a-e70b215b6b23 | checkpoint | 4.5.2 - Reinforcing Mesh Check
925d6c3d-c934-535b-b9bb-b33f8481edcc | note | Detail - Ensure that overlap and clearince from edges
4e2f9cb7-fa82-5c1d-90f7-3f82a3edcd14 | note | Acceptance / Conformance Criteria - 50mm top cover, 300mm overlap
fa878e3c-8212-52ea-af4b-9f50ba7089f0 | note | Standard / Specification - NZS 3109:1997 5.3.2
e487bd71-c369-5e46-8ba1-be0dc54e0c5b | note | Verifying Document - photos
bc0363dc-6eb3-57da-b357-79f9ef591d83 | note | Testing Quantity Required (based from schedule qtys) - Measurements
202fd8b8-081a-5990-b634-daab22e8502b | note | Verification Activity: Activity - H
8a46fc71-0494-571b-8b25-cbaf1bbaa123 | note | Verification Activity: By - SE
e31c2f2d-209d-4f5e-bc96-a01de85b9789 | checkpoint | 4.6.1 - Concrete
ed6d0f3b-dcf2-5254-be61-6329298761dc | note | Detail - 20.0 MPA concrete. 4kg/m3 black oxide (2.5%)
3fd46eda-429f-5549-aed5-ed070e3a0ac5 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 20MPA
43d3d606-d24c-52ed-9485-8262b3120fba | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405 PS:27.4.5
b5eefb53-ad1f-55c1-965f-8f90610b49ee | note | Verifying Document - Concrete Delivery dockets
1b591733-52b0-5f70-94e9-b41e42fb4e90 | note | Testing Quantity Required (based from schedule qtys) - During construction
c4d7e5c7-4de7-5907-bde2-64b395a78d85 | note | Verification Activity: Activity - H
069cc3cb-7bc6-5858-8573-22f3e6ca2bb3 | note | Verification Activity: By - SE
d126f24a-7566-476b-86b0-27d4ded60bb8 | checkpoint | 4.6.2 - Control Joint
287ef83c-e3b3-5615-828f-f011a50b7634 | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
fd0fd6a4-7e8a-5930-83f9-6a9ecee558bc | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
7c24977e-b661-58c1-ae06-83eae81cf125 | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405
5d917e31-92b7-5c56-9f73-1dd675b0996e | note | Verifying Document - Post Pour Checksheet
0d9aaaa0-4246-5b83-9ed1-1de85d7c2df4 | note | Testing Quantity Required (based from schedule qtys) - After pour
78cf0e8f-a50c-53c5-999c-fc8b7e1c1576 | note | Verification Activity: Activity - H
50c1ad65-7706-5071-9a1c-3c48d1589cea | note | Verification Activity: By - SE
17bcc3c7-c411-4323-ae9a-67c1508bf7cd | checkpoint | 4.6.3 - Final Finish
e3a7548a-d1bb-5110-bcf3-6bf9e24b15da | note | Detail - Finish to be either:
492cc6e9-f58c-52ff-a77c-1659c2a2496c | note | – Brushed finish
79277a2d-1c91-5409-9a62-54972d2bfa47 | note | Acceptance / Conformance Criteria - U5 Finish
93add4e3-6a58-5c2b-ae53-be023dd20473 | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405 PS:27.4.5
13664300-e9f3-55b3-a9ef-3b5ab5708c9e | note | Verifying Document - Post Pour Checksheet
2ac2a762-e348-57aa-9bc7-75bbdaad14e9 | note | Testing Quantity Required (based from schedule qtys) - After pour
549a9eeb-7070-5a0a-bd46-4069f235bbe9 | note | Verification Activity: Activity - H
1b807574-2759-5d54-9af3-7128d80980c6 | note | Verification Activity: By - SE
48ad1f58-b0e9-4e28-8d35-a6d7160e7f51 | section | SECTION 5 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
d4fdb88c-f9d5-4724-a752-76427ea8ad0e | checkpoint | 5.1 - Final Inspection
6628a4e4-5a2a-5e7f-982b-bd964c09950e | note | Detail - Final inspection of all concrete work.
f34b36fc-b1a7-5123-826c-3b8f0d0b155a | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
dfa21e82-5642-577f-a5af-b6fe6316c65e | note | Standard / Specification - NZTA P39: 2013
8000fde3-c244-5df9-8bf0-c11bc5579298 | note | Verifying Document - Final inspection report
9446033b-c4cc-544b-8fa9-59ca4f919521 | note | Testing Quantity Required (based from schedule qtys) - 100% of works
ed193698-80b0-5d40-850b-ba1e31aca069 | note | Verification Activity: Activity - HP
e474d3ea-288d-5ee7-8a56-f74f13978f49 | note | Verification Activity: By - ENG
f21f26e8-2d45-41c6-b685-8d9aca4f51ec | signoff | AUTHORITY HOLDPOINT
4bb3e534-e8e8-45ff-a029-b18807e07559 | checkpoint | 5.2 - As-Builts
13dafbed-8535-5624-aa93-2c473c13edf8 | note | Detail - Final inspection of all concrete work.
079eb987-7b1f-5190-a409-04b8fc224f7b | note | ○ Red Pen Mark up
2e93cb4d-ccc1-5841-8b33-de40c26938dc | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
1d7576e8-47aa-5eaf-9059-54c8709c45cc | note | Standard / Specification - PS 16.7.6
b6df67a5-2979-5ce0-8514-b1a4a846e36c | note | Verifying Document - Red Pen Markup
a568a42f-c6af-5ada-adbe-e7e1453421e7 | note | Testing Quantity Required (based from schedule qtys) - All completed works
a62cf1a2-a73f-56ec-8a08-4b2f3da8154f | note | Verification Activity: Activity - D
95f322de-b99a-5b08-b10f-46d037177c1d | note | Verification Activity: By - SV
600d6d27-853e-424f-baab-da0d26bdc742 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
3033e8fe-df20-5f01-b07a-6920ebf4e391 | textbox | Contractor's Rep Name:
22176b0b-a31d-5d67-8e1b-07ff4d5dbe8a | textbox | Engineer's Rep. Name:
80647da0-fc2e-51c4-b3bd-7760bdae5943 | date | Date:
24c8e4cc-dd7a-411a-afc9-ed9a639e5278 | signoff | Add Signature
a6bfd44e-da11-4d77-ae90-9445c205bf7a | checklist | DN1210-SP2-006-005 ITP Kerb & Channel Rev 1 | itp | DN1210-SP2-006-005 ITP Kerb & Channel
7ed78c71-57cd-420a-a7c5-3eceec5a770e | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONNEL & THIRD PARTY APPROVALS
01759048-b3c9-422c-8235-f4404bf812d4 | checkpoint | 3.1.1 - Crushing Resistance
b79a6137-e360-5a62-b4cc-57bde4fd6c6f | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
6ef74e6c-539b-5fa0-882e-05a5cf448672 | note | Acceptance / Conformance Criteria - >100KN
c5be6825-a12e-576e-bb80-876d0547def5 | note | Standard / Specification - Project Specifications Appendix XVIII
9746fe6c-7f50-56a2-bb27-ad214d8c08c4 | note | Verifying Document - IANZ Accredited Report
7a9b2b23-a913-5ee7-a19e-c3c2d3f5734a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
b3d9de5f-d713-5c80-8593-25fbdb735c8f | note | ○ Results to Engineer 2 wks before importing
ea6c2924-86dd-5167-9531-959c522bdd6f | note | Verification Activity: Activity - HP
b734368b-a6a8-5fcc-8d5e-0d76cf4b7205 | note | Verification Activity: By - ENG
1e0493b0-e4f9-4102-a5b1-e66231d386cd | signoff | AUTHORITY HOLDPOINT
a5095729-dbd2-4403-af85-ea0f52de9677 | checkpoint | 3.1.2 - Weathering Resistance
a5998c20-c06a-5207-bd2a-21f9a9639830 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
86409cfa-a364-5a5e-87fc-6e21700dac77 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
be097504-07d8-57ad-95b1-9490bea4d252 | note | Standard / Specification - Project Specifications Appendix XVIII
deac198e-3c0c-5872-a449-f5e596da1983 | note | Verifying Document - IANZ Accredited Report
a95803c8-af0c-5d1f-88df-99c0f9616f57 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
6e2315c5-1452-5350-af6c-9ea53ae4c286 | note | ○ Results to Engineer 2 wks before importing
1bf8d467-a8f1-5652-9e46-b1436147b5db | note | Verification Activity: Activity - HP
61c8a2d0-99e2-51ac-9cc8-f66848bc86a0 | note | Verification Activity: By - ENG
04836c42-ff87-4a77-b08e-99d3929b7329 | signoff | AUTHORITY HOLDPOINT
5c558f90-49cc-4f83-aefe-156bd7f62c6f | checkpoint | 3.1.3 - Particle Size Distribution
5e99cf17-19da-5e45-9982-bfd375289bfe | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
6fc24bf1-c18c-583a-99b1-515943aa3f83 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
9c5cb939-498b-574d-8729-b017ec4bc1bf | note | 37.5mm ¦¦ 100% passing
29bbf16f-c7b9-5d0c-a920-0c590968b702 | note | 19.0mm ¦¦ 60-75% passing
39208a14-4134-5ecb-aa7c-4d6086cdeefb | note | 9.5mm ¦¦ 37-50% passing
608dc3dc-077f-5518-8dd1-8d07d456a11e | note | 4.75mm ¦¦ 20-35% passing
1c3c188e-1cb4-57b0-a74c-69e3675a938f | note | 2.36mm ¦¦ 12-28% passing
3c4ae4f6-21d6-5aaa-888e-6e59f5b89b46 | note | 1.18mm ¦¦ 9-20% passing
70831a77-21c2-5ad7-9f75-0d07183e5ce0 | note | 0.600mm ¦¦ 7-12% Passing
26a5de41-c419-52fa-bdd2-3cc873c5e275 | note | 0.300mm ¦¦ 3-10% Passing
745339b3-b87a-5509-88d0-b4f8024cfb13 | note | 0.150mm ¦¦ 0-5% passing
f80357db-f6b6-5482-a567-7378d103301b | note | 0.075mm ¦¦ 0-5% passing
49d80839-05b5-57da-a537-0c09f9487f22 | note | Standard / Specification - Project Specifications Appendix XVIII, Tauranga Council IDC - Table IT-4.7
e4df5418-4b44-55a7-aabd-8bb577714ce6 | note | Verifying Document - IANZ Accredited Report
a8b7e117-61f8-5dc6-9ab1-03dd87e6bcaf | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
f0ba1e92-2130-5409-afbb-146aba8d16eb | note | ○ 0-400 - 2 tests
e71470e9-723b-5a16-a306-f69d1c4aef8b | note | ○ 400-1,500 - 3 tests
bf26cecf-f5e5-556a-8310-105eddb79aca | note | ○ 1,500-4,000 - 4 tests
f1f03a2e-5e24-5f9b-8d01-fbc2fc4a5f08 | note | ○ >4,000 - 1 test for each additional 1,000m3
17915ef7-83d9-54f7-acd1-bdd78c1ab150 | note | — Results to Engineer 2 wks before importing
bf0fcb4b-494c-5872-b65b-c2784c2f1938 | note | Verification Activity: Activity - HP
71b7ac4c-7bd7-5c6c-8956-e2bbb6d8fa41 | note | Verification Activity: By - ENG
7a2798e9-ddf1-4fc4-aac6-a43cbccebade | signoff | AUTHORITY HOLDPOINT
5812356e-5d61-4f29-a0f5-c1e84a2fa0a7 | section | SECTION 4 – CONSTRUCTION - KERB & CHANNEL PREPARATION
62a6e4d6-215f-4728-8539-a699962fbe65 | checkpoint | 4.1.1 - Stringlines or equivalent
2f03edd1-8a7b-566a-964f-09f3bbebc9df | note | Detail - Stringlines or equivalent to check finished height of surface
33417950-2c39-5250-9f46-23cfda9546af | note | Acceptance / Conformance Criteria - -0mm + 20mm
5a43f7d2-f1bb-52de-ad34-68f45679630f | note | Standard / Specification - NZTA B/06 8.2.2 - Table 3
9909b4c3-5868-5df0-867b-55d56654f7de | note | Verifying Document - Check Sheet
36661fe7-67da-5a76-a952-34b370ca756c | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
9df0ba29-063a-5ed3-9d24-9a6c30f5d5fc | note | ○ 1 set = 5 tests
50f902b3-fa9f-5564-970a-1f4116de3837 | note | Verification Activity: Activity - I
728ba783-645e-5b52-b8a6-7c29c736b5d9 | note | Verification Activity: By - SE
1165779c-d76f-4ee5-9fd3-90f5fd9b7657 | checkpoint | 4.1.2 - Compaction - Clegg
65b29fa9-d8f4-5909-8adc-01f229376584 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
afc69710-58a0-5fd1-8339-a134a39c613a | note | Acceptance / Conformance Criteria - Min CIV 18
d66e5acb-bb3b-5fb6-91b6-297b027b9022 | note | ○ Ave CIV 20
247fb76d-1de0-5d05-9365-f5b6a71584c7 | note | Standard / Specification - PS Appendix XVIII
538c1ff1-3ebf-5fa6-8ac5-8456d81c954a | note | Verifying Document - Clegg Hammer Report
cec0af81-f11f-54d3-a7e8-8edf1767e327 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
bce05e61-1b7b-50e8-b0ac-0f337c1d1412 | note | Verification Activity: Activity - I
c42918c7-215f-51cc-9a60-b840bb37655e | note | Verification Activity: By - SE
9f2c4ea1-35ed-4d69-b8b0-4e725fee2f28 | section | SECTION 5 – CONSTRUCTION - KERB & CHANNEL PREPARATION
a551c635-6afc-4fee-b399-6935079e524d | checkpoint | 5.1.1 - Pre-pour inspection
79801c32-8d44-5c54-81cb-c8ca08aec09f | note | Detail - Subcontractor string line to be checked by Site Engineer to ensure horizontal and vertical smooth transition and to ensure the channels flow towards the catchpits
58fed178-b5d1-5fb0-b579-fe66af3953c9 | note | Acceptance / Conformance Criteria - Tolerances are
d5e3f4f9-0740-5f2d-8eb9-ba3806e62909 | note | ○ +/-5 mm variance to vertical design setout
a04aaf1f-c26c-574e-ab83-36969e10dfd6 | note | ○ +/- 10mm variance to horizontal design setout
91072c2b-d74d-5d4e-959b-0eceea673601 | note | ○ The deviation from a 4.0m straight edge shall not exceed 3.0mm.
fbed39de-3842-5f4a-ad7a-5676e76ceda6 | note | Standard / Specification - Project Specifications 21.7.6
f890b131-dadd-5e8e-bdf8-87659d6e292f | note | Verifying Document - Kerb construction record
f848c6ef-e5f8-5a2f-bd91-fec44bf2f543 | note | Testing Quantity Required (based from schedule qtys) - During construction - Before every pour
f4826af9-9471-5023-b80b-a9c1227a4097 | note | Verification Activity: Activity - I
1fc658ec-7367-5008-b515-cf7a01c1201d | note | Verification Activity: By - SE
1f9ee57d-4305-4289-ac9c-50ae70d915f0 | checkpoint | 5.1.2 - Concrete
f11e3a4c-7f4f-5d46-92b5-a87b0ece447d | note | Detail - 17.5 Mpa Concrete
3e51589a-675b-5669-9024-e1120b93ee38 | note | Acceptance / Conformance Criteria - Delivery Dockets
15381127-d5cb-58e9-a243-5e89ef4a1f74 | note | Standard / Specification - Project Specifications 26.7.3
c9e17437-954e-5ab3-9e27-c826d9dddfe4 | note | Verifying Document - Concrete Delivery dockets, Concrete Test Results
575c1f8d-2cb8-5c60-85dc-7251187a3b5d | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
3cbae387-94de-5750-ae2a-3a9b08ee62c2 | note | Verification Activity: Activity - I
7d65fcda-1c0f-5d57-acf1-d77a125e2ac1 | note | Verification Activity: By - SE
1027a3a2-9a59-4603-b50d-cb62bdef3e50 | checkpoint | 5.1.3 - Control Joint
3d30fc6d-fa42-507c-b3b3-a76a83b6d442 | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
529cb75b-5199-57ac-b68e-7a3b4acf4383 | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
32fa293d-5ae8-58aa-bcb1-692cb0126f56 | note | Standard / Specification - Project Specifications 27.4.5 (c)
af83df3b-6973-5485-81a6-7cfa21ea84e6 | note | Verifying Document - Post-Pour Checksheet
7ca56671-9e00-579b-94fa-6fd0e5de1070 | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
62ba601a-2525-5155-a44d-8dac7c1580ce | note | Verification Activity: Activity - I
c4dfff4d-10c0-56bc-a046-32742a4f4087 | note | Verification Activity: By - SE
af783698-88b0-411a-bca2-08133968821d | checkpoint | 5.1.4 - Final Finish
30b18729-46b7-512a-872d-25dae40670c5 | note | Detail - Slip form kerb and channel
cf2f6e94-6a59-5aed-be1e-a3e3f0f31a42 | note | Acceptance / Conformance Criteria - Slip form kerb and channel
534f94dd-369a-5273-acb5-1a57a6ef7883 | note | Standard / Specification - Project Specifications 26.7.3
ce213d48-3b04-59ac-a0dd-ca7120c88146 | note | Verifying Document - Post-Pour Checksheet
af8205c1-6c43-59e5-8f97-11e1990494e7 | note | Testing Quantity Required (based from schedule qtys) - After every pour
9eebbdfd-9cf2-5ce0-ab93-bdfeba1a6b22 | note | Verification Activity: Activity - I
9f779432-9b5e-55a7-8573-be0a05682772 | note | Verification Activity: By - SE
6bc52b67-8ea1-4f0e-8c0c-59ea7a60a136 | checkpoint | 5.2.1 - Pre-pour inspection
c6b38088-f0d4-5f85-ad19-654aa9bc9ebd | note | Detail - Subcontractor string line to be checked by Site Engineer to ensure horizontal and vertical smooth transition and to ensure the channels flow towards the catchpits
3d9ae161-ad61-586d-bfc8-518f8ada306e | note | Acceptance / Conformance Criteria - Tolerances are
ba1f037e-284e-5354-93bf-6fa9ece32b0a | note | ○ +/-5 mm variance to vertical design setout
64d0ab24-edbf-58fd-a7af-9d831e3e5837 | note | ○ +/- 10mm variance to horizontal design setout
bacbe1dc-b8b2-5486-9923-3dc242aeac0a | note | ○ The deviation from a 4.0m straight edge shall not exceed 3.0mm.
3bda6de7-fb89-5269-9f8c-7d04b0ad06b2 | note | Standard / Specification - Project Specifications 21.7.6
40caa7fe-2cd4-52c4-833c-5b7e7d919983 | note | Verifying Document - Kerb construction record
36ba07b7-f499-54a7-a01d-1986856cc672 | note | Testing Quantity Required (based from schedule qtys) - During construction - Before every pour
c0b6c4a5-6928-5f6d-b01e-f08dabb01b84 | note | Verification Activity: Activity - I
3528170f-3b8f-55a8-a310-f90105541ec2 | note | Verification Activity: By - SE
da7c3edb-50da-48d9-b89c-e1b30b7da40c | checkpoint | 5.2.2 - Concrete
96316e76-52b8-5a04-a8d3-6d1d4a463e1d | note | Detail - 17.5 Mpa Concrete
e89ff0ef-7808-58d3-a47b-53b7ed8040c6 | note | Acceptance / Conformance Criteria - Delivery Dockets
7b4ab449-703d-564d-a736-890366c0b60d | note | Standard / Specification - Project Specifications 26.7.3
9847400d-6df6-5fb3-80f2-71e42746166b | note | Verifying Document - Concrete Delivery dockets, Concrete Test Results
90b2f45b-1b0c-56ec-af30-7de1332b1a7a | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
ad2d08b6-7b3d-51dc-ab69-0d32f6005a06 | note | Verification Activity: Activity - I
b026045d-6efb-5a1d-bf6c-158a8969f8fa | note | Verification Activity: By - SE
41915970-6c7d-4cca-9e16-d2c7afcf1b8b | checkpoint | 5.2.3 - Control Joint
af3cbef0-6866-5752-af04-aa8bdaad2af1 | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
2f217aae-b7fb-53ae-bb8e-896336e93d10 | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
1f978e40-690f-5d4f-bf3e-cfe0fb1bfe68 | note | Standard / Specification - Project Specifications 27.4.5 (c)
8c6c6b56-c96c-5f1f-9527-58936a30dbea | note | Verifying Document - Post-Pour Checksheet
d35df0cb-1b85-5f89-8452-6a4b3d685911 | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
07f6fe4f-60e0-59b0-b6f9-62fb9567e7e9 | note | Verification Activity: Activity - I
b86528b1-8b51-5b47-af65-428ae0bfb399 | note | Verification Activity: By - SE
a4c489be-8a7d-4a80-bf08-a1e7ec47855e | checkpoint | 5.2.4 - Final Finish
6517a0ab-7a63-5588-8bff-91b4463a2563 | note | Detail - Slip form kerb and channel
a9ccfd40-144e-5e3b-a139-58abec3eeb54 | note | Acceptance / Conformance Criteria - Slip form kerb and channel
14a37edc-8fe0-57f5-be65-ed850554e136 | note | Standard / Specification - Project Specifications 26.7.3
a27a5e43-972f-5212-b1a6-11e78c608603 | note | Verifying Document - Post-Pour Checksheet
931e36b6-ff42-58fe-934f-a02729888ff6 | note | Testing Quantity Required (based from schedule qtys) - After every pour
1697fdbf-062e-5184-bf09-0771a8a1a35b | note | Verification Activity: Activity - I
6eb967d5-e413-56c2-961d-66e8a3aaf471 | note | Verification Activity: By - SE
c0b08d28-bee0-4366-938b-87371e3e5ecd | checkpoint | 5.3.1 - Pre-pour inspection
4bd3b591-0654-5060-978a-4c903b00ef5d | note | Detail - Subcontractor string line to be checked by Site Engineer to ensure horizontal and vertical smooth transition and to ensure the channels flow towards the catchpits
a77f94a1-b4eb-58af-9909-acd9b333e1b6 | note | Acceptance / Conformance Criteria - Tolerances are
f6172b53-619f-5060-a70d-b572dab7b227 | note | ○ +/-5 mm variance to vertical design setout
27fd5467-0eab-51ed-9818-95fb80b3eeec | note | ○ +/- 10mm variance to horizontal design setout
3ba8b6e3-c1be-58fe-8286-af71317f427e | note | ○ The deviation from a 4.0m straight edge shall not exceed 3.0mm.
4627d380-78cd-591b-af1c-154d6e88c850 | note | Standard / Specification - Project Specifications21.7.6
84320fef-5a68-59f7-b01e-ba9d9fa58362 | note | Verifying Document - Kerb construction record
28eb6567-4c14-57cf-a050-fa13f4b687c2 | note | Testing Quantity Required (based from schedule qtys) - During construction - Before every pour
912fb653-933f-5e18-93ea-df2e97a6bfa5 | note | Verification Activity: Activity - I
a97f7d82-2566-5e60-b5cb-334bd140a1f4 | note | Verification Activity: By - SE
92389ea9-c1fa-4fd5-8086-153cae88418f | checkpoint | 5.3.2 - Concrete
8966acb5-6d22-5dae-b203-0777647812e3 | note | Detail - 17.5 Mpa Concrete
23e7547e-1cb9-5d0a-b2b6-ceda5fc6641b | note | Acceptance / Conformance Criteria - Delivery Dockets
434f0f97-5d5f-565b-8bc4-b58876259374 | note | Standard / Specification - Project Specifications 26.7.3
a7dcd160-b8d3-59c2-9452-6c692085795b | note | Verifying Document - Concrete Delivery dockets, Concrete Test Results
6e61ff84-a92a-5920-a670-4d40407bce8e | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
37bf2afc-358f-57f7-9dfe-24b5ea15c705 | note | Verification Activity: Activity - I
17443d6d-06cb-5c32-bbdf-b5a3ce4f3c85 | note | Verification Activity: By - SE
d2ab6bcb-fd1e-4241-939e-cddce07db2f2 | checkpoint | 5.3.3 - Control Joint
8e70596e-281e-5241-af1a-1a82d7d41255 | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
257efcc9-b4cb-52a5-80e7-0ea182f01cdc | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
7bcf670c-50f9-5ace-97c0-55c5141603df | note | Standard / Specification - Project Specifications 27.4.5 (c)
4a6b20fb-4e8c-5cea-a7e5-b78c73b01e41 | note | Verifying Document - Post-Pour Checksheet
8c5642a3-5e10-5601-9b3a-c3fdc38366cd | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
3885adbc-4c39-5074-8953-bfdfd4ae274d | note | Verification Activity: Activity - I
64b08dbd-efeb-52f1-b1a3-572130e6670f | note | Verification Activity: By - SE
ca6e7502-6ef2-4a31-8aea-9d5c786b2315 | checkpoint | 5.3.4 - Final Finish
5b261a99-fde8-50ee-a70a-6a73e69c093f | note | Detail - Slip form kerb and channel
957bf372-ba55-5161-b7e5-35f82d9d587f | note | Acceptance / Conformance Criteria - Slip form kerb and channel
5aee4092-0fb5-56d6-aafe-b8454091e9ea | note | Standard / Specification - Project Specifications 26.7.3
b14d72ed-a02b-5539-9eac-97a6dfdb52e3 | note | Verifying Document - Post-Pour Checksheet
41ce040c-a88c-56b5-9979-b229bc5fa82b | note | Testing Quantity Required (based from schedule qtys) - After every pour
0a754ae0-ae7d-599a-a187-4810523dcb24 | note | Verification Activity: Activity - I
503ca39f-fcbf-54c2-88f0-f2617915c810 | note | Verification Activity: By - SE
cdeb8e82-4b60-461d-9f92-3ed674d32dbe | checkpoint | 5.4.1 - Pre-pour inspection
c0ae0731-316a-5772-8a95-b4ad551089db | note | Detail - Subcontractor string line to be checked by Site Engineer to ensure horizontal and vertical smooth transition and to ensure the channels flow towards the catchpits
8b8582b4-1537-5e08-9454-3f722ab0beef | note | Acceptance / Conformance Criteria - Tolerances are
9bf1fb98-abb5-5f7f-9e3c-b1290ebdeb4d | note | ○ +/-5 mm variance to vertical design setout
e32d7e7b-4dba-5753-b2ef-f6a2395be535 | note | ○ +/- 10mm variance to horizontal design setout
efed9c1a-1da0-5b97-96d5-5a6208258eb2 | note | ○ The deviation from a 4.0m straight edge shall not exceed 3.0mm.
143c3f7e-36c7-530b-92b8-c74d14583262 | note | Standard / Specification - Project Specifications21.7.6
d12ae126-1234-5194-b1cd-868585298bb5 | note | Verifying Document - Kerb construction record
8ba6c72c-434b-5d65-813e-b1dc4f57cd5b | note | Testing Quantity Required (based from schedule qtys) - During construction - Before every pour
213e0075-a22b-5f17-b82d-67d3af48df5e | note | Verification Activity: Activity - I
f1c8d402-78ce-5d80-b552-37e2ceb69c28 | note | Verification Activity: By - SE
7b9a760c-b1b8-4816-bacb-e6351918ce98 | checkpoint | 5.4.2 - Concrete
1e57b630-753d-5418-8bcc-6e447fd55da3 | note | Detail - 17.5 Mpa Concrete
ef289ece-9cbc-5f87-9a32-af2c35c5f35a | note | Acceptance / Conformance Criteria - Delivery Dockets
4c93357b-97c7-5e67-918e-3e802caededd | note | Standard / Specification - Project Specifications 26.7.3
e1746f56-ea62-5557-8413-ac75b0fcd425 | note | Verifying Document - Concrete Delivery dockets, Concrete Test Results
b0a0abd1-69cc-50a0-8d19-17b28812ab3a | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
c3d0ec35-e49a-5f48-81c7-b4f63d754b9b | note | Verification Activity: Activity - I
9f4ab137-8f09-59d2-89f4-74210fa709bb | note | Verification Activity: By - SE
96e957e0-09e1-44e6-bfef-07329e288aa7 | checkpoint | 5.4.3 - Control Joint
ff48dec9-4480-5d88-8bdb-a15e8cc41098 | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
b6b9d55a-6287-5ef1-9922-480d59f970f5 | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
a7d09f92-74c5-55a1-bd30-c46b7e52725a | note | Standard / Specification - Project Specifications 27.4.5 (c)
b0050ef1-5bd4-5f12-9260-11c63b7099d2 | note | Verifying Document - Post-Pour Checksheet
7cd886a9-141c-5087-830e-70ecc0e45ec7 | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
a4833f8b-bcd2-54ca-8ef5-fd339259bbc4 | note | Verification Activity: Activity - I
1fbcd001-5848-5c1d-9119-6e0fca997aa0 | note | Verification Activity: By - SE
0e9d60f8-7b75-479d-9036-e4bb1671de52 | checkpoint | 5.4.4 - Final Finish
d4dd1c00-6ea7-5bc7-8d25-849db6b817d4 | note | Detail - Slip form kerb and channel
e7bd678a-063d-5957-87cb-4df626c153a4 | note | Acceptance / Conformance Criteria - Slip form kerb and channel
3af4f0c8-fc76-5eed-bf1e-6ac8cecc5cfb | note | Standard / Specification - Project Specifications 26.7.3
dab9cdd8-d458-50e4-bb5b-b4801e812720 | note | Verifying Document - Post-Pour Checksheet
f4e2069e-c9f9-53d6-8bd0-082735a7bea0 | note | Testing Quantity Required (based from schedule qtys) - After every pour
644b545e-7575-5aaa-af86-1d699a943b73 | note | Verification Activity: Activity - I
021d99cd-7338-5cab-9d5a-eab838d3608f | note | Verification Activity: By - SE
c2230a80-5728-4c68-8284-189bbd8217af | checkpoint | 5.5.1 - Pre-pour inspection
de5a88eb-333d-5a90-bce9-68c94d9281e0 | note | Detail - Subcontractor string line to be checked by Site Engineer to ensure horizontal and vertical smooth transition and to ensure the channels flow towards the catchpits
77d88f52-c674-5533-a66b-407a78d29f2c | note | Acceptance / Conformance Criteria - Tolerances are
33ffee56-4f7d-5059-8c34-45e7fb27d9d9 | note | ○ +/-5 mm variance to vertical design setout
0ad904b7-e1bf-5570-8cc0-654f55291fc8 | note | ○ +/- 10mm variance to horizontal design setout
451fd335-cd75-5f1b-9bca-0a4c838e7b04 | note | ○ The deviation from a 4.0m straight edge shall not exceed 3.0mm.
34ddf6e9-9233-56a6-81a9-6e30ea29e01a | note | Standard / Specification - Project Specifications21.7.6
db29ca4f-10c3-5090-9c67-6ee989de94f8 | note | Verifying Document - Kerb construction record
d91a4f1c-1945-5037-832a-fec97a1db657 | note | Testing Quantity Required (based from schedule qtys) - During construction - Before every pour
efe6c96f-4ce6-5b2a-ac0b-90c262fb1a22 | note | Verification Activity: Activity - I
d0ff901b-cc22-5c3e-a0f1-c54fe386f018 | note | Verification Activity: By - SE
736b8679-0294-44fd-9d69-aa78b18a4431 | checkpoint | 5.5.2 - Concrete
9a6d9521-6254-5d92-8226-7faaaae1abec | note | Detail - 17.5 Mpa Concrete
04cd81b2-a229-5466-9d79-a86ff060031b | note | Acceptance / Conformance Criteria - Delivery Dockets
a1b9e171-8513-5fee-84fc-a987de161bd9 | note | Standard / Specification - Project Specifications 26.7.3
3fcaf4c9-314b-5cb2-bcc6-7ba64a483c85 | note | Verifying Document - Concrete Delivery dockets, Concrete Test Results
46edf379-405c-54d8-9e5d-d66c370ed3d5 | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
b310f06f-fe05-5c13-bbc9-94da08319b1c | note | Verification Activity: Activity - I
f1916771-8a11-520e-a411-476934af8c42 | note | Verification Activity: By - SE
db0483b2-8967-4919-b10b-34c93f8f00aa | checkpoint | 5.5.3 - Control Joint
fe5ebe0e-6a1a-56a5-b8f2-15f113ea6895 | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
a320c267-2fb4-52dc-8fe9-cf51d2e2d8b4 | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
8899ffbc-9c13-568e-904c-b62c0556ab53 | note | Standard / Specification - Project Specifications 27.4.5 (c)
ba51239c-9988-525d-9a9f-241557a2eb26 | note | Verifying Document - Post-Pour Checksheet
57325910-0a94-53c3-94d3-bdcdd87e3bfe | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
0147d3ff-33a6-502c-a333-a9239d1d7919 | note | Verification Activity: Activity - I
2fcac062-ff18-5b87-b491-00ab570a70e0 | note | Verification Activity: By - SE
638e7ec2-bbd3-4505-8c1a-4bc6cb028e8d | checkpoint | 5.5.4 - Final Finish
3c625ce9-4d3e-5289-a319-78903e3db077 | note | Detail - Slip form kerb and channel
86a7c417-65e5-5569-963b-db053b729745 | note | Acceptance / Conformance Criteria - Slip form kerb and channel
2e8db52b-b39a-5b97-9c27-d7a44f9236f8 | note | Standard / Specification - Project Specifications 26.7.3
78dbc264-558a-5b32-8d4d-779b6f29fb23 | note | Verifying Document - Post-Pour Checksheet
b64cb268-f270-50d9-a436-47530b554a08 | note | Testing Quantity Required (based from schedule qtys) - After every pour
748c2cf1-f92b-52c1-956f-c1321c26cafa | note | Verification Activity: Activity - I
4dac6537-2d80-5ba8-9438-122be2924faa | note | Verification Activity: By - SE
b14d0521-1801-4608-975f-def4ca4966e7 | checkpoint | 5.6.1 - Pre-pour inspection
d3953672-36a1-5a9d-a8d5-42455bf3784e | note | Detail - Subcontractor string line to be checked by Site Engineer to ensure horizontal and vertical smooth transition and to ensure the channels flow towards the catchpits
453d83ac-2779-5aad-a6ba-fbfcaeb1072d | note | Acceptance / Conformance Criteria - Tolerances are
640ac00e-f44d-54df-a819-35b2c0615816 | note | ○ +/-5 mm variance to vertical design setout
7d00cf75-5a6b-5c5f-aff4-aa92dde6ccbd | note | ○ +/- 10mm variance to horizontal design setout
5c3b1e2f-2c0b-502d-a7bb-c5e594cecaf5 | note | ○ The deviation from a 4.0m straight edge shall not exceed 3.0mm.
314919d0-7e12-5874-8f23-4b0940ae6def | note | Standard / Specification - Project Specifications21.7.6
735c4e7d-9a45-5b3c-9a8a-85ae4137197f | note | Verifying Document - Kerb construction record
c1a6fdc3-24ab-5c3d-b7f0-e742d6d31a7f | note | Testing Quantity Required (based from schedule qtys) - During construction - Before every pour
d55c7a90-36bc-5016-809a-46f511d3725c | note | Verification Activity: Activity - I
48fe042a-650f-5213-af1d-de5fe78ee4cf | note | Verification Activity: By - SE
78d9be11-ec41-441f-88bc-be745ab60f74 | checkpoint | 5.6.2 - Concrete
c3c6cc44-0efd-569e-8c4b-979e5236038d | note | Detail - 17.5 Mpa Concrete
496a0f80-df83-525a-89bf-4eae726e0816 | note | Acceptance / Conformance Criteria - Delivery Dockets
11e59b0a-5a40-5a63-8e00-01198f4db5d0 | note | Standard / Specification - Project Specifications 26.7.3
87ad8357-34b1-5d3a-9cd9-6a9a1cb4b11c | note | Verifying Document - Concrete Delivery dockets, Concrete Test Results
2fa6a62a-2d96-5048-bfd6-87a5e8790cb7 | note | Testing Quantity Required (based from schedule qtys) - During construction - Before every pour
f5af61bb-2e27-5f0b-a047-7a368ae790f8 | note | Verification Activity: Activity - I
a5296bb1-4e4e-5722-b32f-acb88e2061da | note | Verification Activity: By - SE
bd549a56-19f4-44d1-84a4-f0688b21eb3a | checkpoint | 5.6.3 - Control Joint
3951878a-c2f3-5f53-94fc-8e07fe126611 | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
095e319c-075b-57aa-a9e4-8a7c60590a3d | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
a3f98822-6f02-5ec7-a0bc-e2bbe7570be9 | note | Standard / Specification - Project Specifications 27.4.5 (c)
b6f7d232-03d8-5efd-986d-788915f2dd01 | note | Verifying Document - Post-Pour Checksheet
ba95b42e-379b-56f9-ab0c-ce2cfdb18836 | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
fbba15ed-5dd4-5c34-aa36-fb34336684c3 | note | Verification Activity: Activity - I
30cde8b8-fdbf-5f4a-a798-ec46d4a2bb23 | note | Verification Activity: By - SE
bf66190b-fa73-46bb-ac5a-3312d3758119 | checkpoint | 5.6.4 - Final Finish
e31c0593-33b7-5529-b799-7604faa46f56 | note | Detail - Hand poured and formed concrete kerbs
cac21241-1833-5447-a3f5-4684afc72421 | note | Acceptance / Conformance Criteria - F3 Surface Finish / Slip form kerb and channel
5272dd06-8478-5e81-b2d4-5fe0ab5f89fe | note | Standard / Specification - Project Specifications 22.10.2
8a4a5e20-dd67-541a-906b-2e076a0fa434 | note | Verifying Document - Post-Pour Checksheet
241a8e15-72ba-5f94-b73b-206c974083cd | note | Testing Quantity Required (based from schedule qtys) - After every pour
772606b1-2b35-53c4-9022-57e6a429d7d6 | note | Verification Activity: Activity - I
0ada01d2-2f2a-5cfc-941b-b682154334e7 | note | Verification Activity: By - SE
5b734875-2d1e-4a69-a64d-54da68c61697 | section | SECTION 6 – CONCRETE ISLAND
e6f646ab-785e-4d53-9efa-d291ce4e2e37 | checkpoint | 6.1.1 - Stringlines or equivalent
62666604-fe55-595e-b4a3-4f25052ca729 | note | Detail - Stringlines or equivalent to check finished height of surface 75mm from finish concrete level
3b7ad799-d503-5c7d-93d8-32e92c1e9a14 | note | Acceptance / Conformance Criteria - -0mm + 20mm
2dd295d4-e6c1-5e9a-bb22-90d1ab69e922 | note | Standard / Specification - NZTA B/06 8.2.2 - Table 3
5ac2ef22-e45d-5d28-8f4a-9916373adedc | note | Verifying Document - Check Sheet
bd73cc49-8b65-596c-a13a-babceac0f09f | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
8bc75df0-efd7-5746-a3c1-32dbc8ffc9b6 | note | ○ 1 set = 5 tests
bc7a905c-9742-5580-bd9e-32d02e7f0afd | note | Verification Activity: Activity - I
adab9e40-35ce-5d94-9302-84cf50ec0746 | note | Verification Activity: By - SE
c53f34b9-4ded-4490-ad14-d82f725c4e38 | checkpoint | 6.1.2 - Compaction - Clegg
ace8aec7-af2d-5cf0-862b-8727bff23cbf | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
2c86c95a-a55f-5463-9d8f-fe5855cd93b7 | note | Acceptance / Conformance Criteria - Min CIV 18
d0f8d56c-cbda-5690-8b9b-2a65deaf1757 | note | ○ Ave CIV 20
9ceb40c7-e057-5ae7-b3c6-7ed754674ed6 | note | Standard / Specification - PS Appendix XVIII
ac68e4b7-d8cb-515e-b368-7596a8f859fc | note | Verifying Document - Clegg Hammer Report
0cc952a0-f16d-5db2-adf9-280c5d50546b | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
0a241895-e755-564d-bb48-0f9a29e95564 | note | Verification Activity: Activity - I
0e18d737-0440-5284-bf6d-11f7fefdf064 | note | Verification Activity: By - SE
f7213c56-ea5c-44ad-abcc-925fc3ab7f26 | checkpoint | 6.3.1 - Concrete
c9d3c92c-6887-5fda-bcd2-1360e37d6e9c | note | Detail - 20 MPa coloured with 2.5% black oxide
f1b09faa-ea38-5d63-895c-89bf302c65d8 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 20MPa
4bf8ac8d-8541-56a2-aeb2-8826a535c255 | note | Standard / Specification - 232735.02-WSP-DR-UDL-0405
64d10457-e4ea-5bf8-b943-d817b0318958 | note | Verifying Document - Concrete Delivery dockets and test reports
e6cde333-a4ab-5fc1-9e5a-309041c88718 | note | Testing Quantity Required (based from schedule qtys) - During construction
7965cefd-69a5-5f9e-9f99-2440f6a0da8b | note | Verification Activity: Activity - I
6cd7a164-1e44-502b-ba33-7d32e53de2e6 | note | Verification Activity: By - SE
96b42978-fa74-4377-99c4-6439fed21a74 | checkpoint | 6.3.2 - Control Joint
ac57a32f-ba0b-5414-bfaa-9cdabe5df651 | note | Detail - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m.
b9f6fad2-fe28-5101-9cf6-7b0fdd5f0b71 | note | Acceptance / Conformance Criteria - Control joints must be formed while concrete is still wet using trowel with maximum spacing of 3.0m
c7ef304d-edc7-5c0a-ad21-345ae380e998 | note | Standard / Specification - PS 27.4.5
aa227fca-3b6f-5fbb-bd62-28b72b365c90 | note | Verifying Document - Post Pour Checksheet
3e8459b6-687a-56a1-8136-38877520801b | note | Testing Quantity Required (based from schedule qtys) - During construction - Every pour
589c83c9-126d-5107-a3c5-77a4a7c945d0 | note | Verification Activity: Activity - I
4ea01cc0-7a5c-5615-aedf-632db1c4a43d | note | Verification Activity: By - SE
a1aa1617-085c-4a8d-83ca-8284c253eed1 | checkpoint | 6.3.3 - Final Finish
6f58458f-3501-5a9f-a365-5c7d8c9702f8 | note | Detail - Trowelled
759aa101-3753-5747-b62e-e9dd9ff75bcc | note | Acceptance / Conformance Criteria - U3 Finish
dacd2ea1-4e6b-57c2-a64f-a4e89030cc2f | note | Standard / Specification - 232735.02-WSP-DR-UDL-0405
8d8a34e2-2dc7-5db6-a59f-bf689b6660c6 | note | Verifying Document - Post-Pour Checksheet
e44fd4f4-dfdd-5b05-b08e-be1930296e6a | note | Testing Quantity Required (based from schedule qtys) - After pour
54dbfe04-84ab-524b-9160-5ffc00ce60a0 | note | Verification Activity: Activity - I
6e83c33f-359a-569b-a56b-4af1cb886f02 | note | Verification Activity: By - SE
23b0a098-2e38-4f47-968f-d8382dc0920a | section | SECTION 7 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
e00063a9-daae-4067-a3ef-fb404e11d985 | checkpoint | 7.1 - Final Inspection
dc58f424-9822-5282-a6b1-b548a9cfceac | note | Detail - Final inspection of all concrete work.
400f2d54-7bfe-59cd-9cbf-c14ed75a5231 | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
d7d10526-f40e-5043-a202-ee1f26f7b751 | note | Standard / Specification - NZTA P39: 2013
0e9d0b0c-fccf-502f-901c-598e4a29f440 | note | Verifying Document - Final inspection report
246a3a93-50a7-59ca-b356-62f1d30cf6f8 | note | Testing Quantity Required (based from schedule qtys) - 100% Completion of works
60557840-cb24-5c60-beb6-99afd6f2f212 | note | Verification Activity: Activity - HP
dd2a062f-e41f-5506-95c4-00b27cce87c3 | note | Verification Activity: By - ENG
e5dfd431-e681-44be-95c8-7bae71b0a2f4 | signoff | AUTHORITY HOLDPOINT
7d9da674-ba53-438f-b12b-13281de2ea78 | checkpoint | 7.1 - As-Builts
6fe9c4a6-1d5a-50ba-873a-156190f70d94 | note | Detail - Final inspection of all concrete work.
c80838b8-6333-502d-871b-5d78ee846347 | note | Acceptance / Conformance Criteria - All works meet project specifications and standards. - any changes to be added to redpen markuProject Specifications
1ef32b72-f9ca-5585-a78c-2bbc3521ca5c | note | Standard / Specification - Project Specifications 16.7.6
da8167de-7886-5dbf-8edf-61cd7296a4c7 | note | Verifying Document - Redpen markuProject Specifications
5ff310c1-cb5a-5283-8d2c-96956775f860 | note | Testing Quantity Required (based from schedule qtys) - 100% Completion of works
01b8e5c8-4e4f-5cd9-94b5-591ec4e26d13 | note | Verification Activity: Activity - D
a1b1c4c2-133f-5ad2-86cc-88308988cb87 | note | Verification Activity: By - SV
4f841283-42bc-40fb-88b1-1efa6ea93381 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
ff7064a5-e8f8-5789-888b-78e2b88ffcec | textbox | Contractor's Rep Name:
dffc4694-fbc1-5962-b95b-1ae22056c4c6 | textbox | Engineer's Rep. Name:
bcee3d2a-c3ab-5394-be80-0b8e8f0b12af | date | Date:
0ef2892d-a1c0-4b41-b85d-b761564ef8a7 | signoff | Add Signature
92409d18-91cf-46f5-8d22-88f5a61f7c68 | checklist | DN1210-SP2-006-006 ITP Vehicle, Pedestrian, Pram & Cycle drop kerb crossing Rev 2 | itp | DN1210-SP2-006-006 ITP Vehicle, Pedestrian, Pram & Cycle drop kerb crossing
dff5d352-6fa2-43a9-9270-524f1efe95fe | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
55119ea6-9212-470c-b14a-7c0a7d1677ac | checkpoint | 3.1 - Crushing Resistance AP40-1
6f1a7a4a-60f3-5a07-9063-18ad1e030aa5 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
f12450ac-aa49-57c9-81e3-e39167347f57 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
aeadcdda-d0ba-54c3-9ea8-ebae272d0046 | note | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4.8 table 4.6
d7235f02-30dc-5897-81cb-34cc9fdad1eb | note | Verifying Document - IANZ Accredited Report
5ea7428f-29e0-5ced-bc3f-a5972986f0a1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
9ed48d90-f674-56fd-8a7d-11f33d92dd27 | note | ○ Results to Engineer 2 wks before importing
9cf8a394-25b0-5d2e-bdaa-bb64c58c339d | note | Verification Activity: Activity - HP
1dd22604-05ac-50ca-b84c-ebbc94ee0528 | note | Verification Activity: By - ENG
d273635b-15e9-434b-b857-c0340074fc55 | signoff | AUTHORITY HOLDPOINT
4ee3b01b-eecf-403a-801d-1a33cab9c82d | checkpoint | 3.2 - Soaked CBR AP40-1
988a9b15-708d-5517-8837-7b7962ae050b | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
728f1878-4ffc-5a53-b2b4-16a1b9da7545 | note | Acceptance / Conformance Criteria - >80%
d4c33829-bef7-5a79-a9e5-6618fdcfff1b | note | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4.8 table 4.6
29b39abd-0ac6-5a7b-93cf-32d9b02fdf22 | note | Verifying Document - IANZ Accredited Report
61f04fee-7be3-51b5-897e-af94daf397a8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
6b1c728a-47d8-512e-94d5-9d51d64255ef | note | ○ Results to Engineer 2 wks before importing
10481de2-4744-5293-bb75-4c92d2e9e59b | note | Verification Activity: Activity - HP
b1d20a36-e4a1-56e6-8280-781c8acf65fd | note | Verification Activity: By - ENG
81d00c01-b17a-42fc-a42b-1fb9d7c3a777 | signoff | AUTHORITY HOLDPOINT
9b49930d-0474-4c84-b43f-70272fe3977c | checkpoint | 3.3 - Accelerated Weathering AP40-1
7be8b0c8-6ad8-5734-85d3-88ec7d638091 | note | Detail - NZTAT/20 Ethylene Glycol Accelerated Weathering Test
25e1e997-f3b9-5ce4-9a6c-fc2fdca77bc2 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
e7883e57-5632-581d-809c-163fcf17074a | note | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4.8 table 4.6
4d39f290-b936-53bf-a9e5-003d313e544b | note | Verifying Document - IANZ Accredited Report
b4d041b5-777e-56de-88a3-d2764b4dd30f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
71ebdd6b-61c7-572a-9bb8-6bec3abe367d | note | ○ Results to Engineer 2 wks before importing
00afc856-aab4-58af-a2ce-d5896d491771 | note | Verification Activity: Activity - HP
262ab5d4-4ccb-5a35-9431-b7bdd45a91da | note | Verification Activity: By - ENG
68f8db7f-87b7-4b6d-849f-f3ffa5211e8d | signoff | AUTHORITY HOLDPOINT
91d43e78-df7a-4496-a1c8-9c7ffe1f65c5 | checkpoint | 3.4 - Weathering Resistance AP40-1
35873832-0dce-5358-b5b8-80df977ddb79 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
38c58eae-fe6f-5ca1-b75e-09cf3ca0789a | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
f7138c26-0946-59da-a7ae-521f2c24c231 | note | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4.8 table 4.6
ee1ef0e8-e36e-5a43-8022-ff8018a7609b | note | Verifying Document - IANZ Accredited Report
b073a260-f2e0-58ef-a31d-a830a9671ee5 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
1ed59a8a-883c-5894-b5d1-d84908d28ca8 | note | ○ Results to Engineer 2 wks before importing
94292049-3894-5944-9ee1-20f8e46a4d42 | note | Verification Activity: Activity - HP
ba0fb1f6-4f06-588b-9995-285eb2ac2fb8 | note | Verification Activity: By - ENG
798361a2-8985-4b30-be2c-6b6159e5b162 | signoff | AUTHORITY HOLDPOINT
44ca489b-a331-43f0-a65f-61de634b196f | checkpoint | 3.5 - Particle Size Distribution AP40-1
7185d299-00b9-5bd6-a08d-6852d87515ef | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
4fbc84e4-47cf-5ad2-ae90-e2f297f96b05 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
f8b66273-99fa-59c1-b30b-052fe8c97554 | note | 37.5mm ¦¦ 100% passing
5af99f39-5a57-5245-945b-6bfb408cbfe2 | note | 19.0mm ¦¦ 60-75% passing
9e35fb86-8bbd-53f0-9956-15880952aba8 | note | 9.5mm ¦¦ 37-50% passing
76baca25-37da-50cb-ab5d-5e2f905a22dc | note | 4.75mm ¦¦ 20-35% passing
43af3f64-790f-542d-bec3-26fe701fc840 | note | 2.36mm ¦¦ 12-28% passing
4851c5fc-9ef3-5a1d-9d59-6105b8bcf907 | note | 1.18mm ¦¦ 9-20% passing
5054e4dc-5b1e-55ed-86e1-4ee9cec5ee7c | note | 0.600mm ¦¦ 7-12% Passing
bed5a96b-39d4-504e-9182-f52a63321b3f | note | 0.300mm ¦¦ 3-10% Passing
ca81538f-9884-5108-9b00-9a29df5bef6e | note | 0.150mm ¦¦ 0-5% passing
ceb34991-378e-5b31-a80f-9b1cb55adf31 | note | 0.075mm ¦¦ 0-5% passing
cd3f9aeb-70a1-519d-bd1e-1fd5a5d1801e | note | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4.8 table 4.7
510e3f8f-120b-5800-b68e-87e8af452247 | note | Verifying Document - IANZ Accredited Report
b60a839f-1954-5dd3-bb02-b9204822a531 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
03a6ef6a-7de0-5e66-9749-7a9b6fe451ce | note | 0-400 - 2 tests
8b502acb-524f-567d-9791-f2122462ea41 | note | 400-1,500 - 3 tests
fd43e87a-5c0f-53fc-b383-d749c775592b | note | 1,500-4,000 - 4 tests
80830d2e-fe2a-55b6-8015-b0564650d2bd | note | >4,000 - 1 test for each additional 1,000m3
a07715a2-6666-54ca-abbe-aff9cc26cad3 | note | ○ Results to Engineer 2 wks before importing
39b348b2-8549-5971-93c0-d8bd44f0f809 | note | Verification Activity: Activity - HP
197a99c7-88ba-5e42-8628-5e41196c9db7 | note | Verification Activity: By - ENG
f9cb295a-6435-4168-b8a5-bb7366a6d9c8 | signoff | AUTHORITY HOLDPOINT
ef51dba4-403f-47c2-9142-bf0045bdf56e | checkpoint | 3.6 - Shape Control AP40-1
d95d36e8-3bd1-5dac-9174-325041e17319 | note | Detail - Tolerance allowed from approved grading curve (%)
12e9c736-746c-5b1a-9696-dda14cbb12f6 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
72baf9ba-3d19-5e49-bf3b-9e2516686966 | note | 37.5 – 9.5 ¦¦ 28-48%
8ccb1bfe-9d09-5288-b9ee-e24f810036e9 | note | 19.0 – 4.75 ¦¦ 14-34%
a7d25c9a-277e-59f2-a92c-d2d70bb6e676 | note | 9.5 – 2.36 ¦¦ 7-27%
4d55a631-b42b-54f2-964a-52d7765a9b02 | note | 4.75 – 1.18 ¦¦ 6-22%
89d4761e-aadc-533b-a438-3a0406a1bc17 | note | 2.36 – 0.6 ¦¦ 2-20%
5ddc10b1-ce92-5ffe-b990-2a12326bf995 | note | 1.18 – 0.3 ¦¦ 5-19%
05473226-fd19-5938-babf-15e4bc0eec2f | note | 0.6 – 0.15 ¦¦ 2-14%
c761319a-2d7d-5c9e-8b60-7629f5e1c4b2 | note | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4..8 table 4.7
b53113e5-f579-5cbd-9a5a-6f952a2596b2 | note | Verifying Document - IANZ Accredited Report
39649912-65ed-541c-89b1-835552d7deb2 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
1030c74b-3b98-5efe-a9fe-3f801770c5eb | note | 0-400 - 2 tests
eaae7533-cda1-595d-8566-abffbfb9a7a0 | note | 400-1,500 - 3 tests
24d33a10-f793-5db0-be0f-6ec95b3cd761 | note | 1,500-4,000 - 4 tests
b21b9385-01ba-57a2-af11-20666e2336ed | note | >4,000 - 1 test for each additional 1,000m3
4e33ae93-460a-5caa-b344-023eee74286d | note | ○ Results to Engineer 2 wks before importing
42b277e5-4fa3-5f86-85d7-33c9956c69ac | note | Verification Activity: Activity - HP
5ee781aa-a401-5bcf-a4fe-97ad8c31ffa9 | note | Verification Activity: By - ENG
bb77ffd1-901f-4cdd-8847-236579c76a56 | signoff | AUTHORITY HOLDPOINT
3c1bfc84-bc75-4cd5-8e58-d5328d6e5aa2 | checkpoint | 3.7 - Sand Equivalent AP40-1
20490099-c474-54b5-9f91-5dfb72a6f7f1 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
6ef70d06-ae6d-53e5-abc5-bc846ec29e51 | note | Acceptance / Conformance Criteria - ≥ 40
62d06608-e27f-569b-a7b9-79b14c22d1b9 | note | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4.8 table 4.7
5edfdb93-0ef3-58ca-a02a-5fe93c8521f9 | note | Verifying Document - IANZ Accredited Report
08d76c7f-7ddb-50b7-b035-ab5e53b38d7d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
dad679a2-95f4-5572-b071-2a9d744cf5de | note | ○ Results to Engineer 2 wks before importing
95557adf-ef23-5f70-80be-de55ae1d5762 | note | Verification Activity: Activity - HP
d70fdfbe-b166-5c82-bcb1-9455725ad818 | note | Verification Activity: By - ENG
b9ab9143-0e12-4ebf-aa6e-da2b30fe75fa | signoff | AUTHORITY HOLDPOINT
bd9ec764-ed98-48f2-853f-e5c8cb911c7c | checkpoint | 3.8 - Plasticity Index AP40-1
311a73b1-9c32-5017-b5c2-61cbb4c2e924 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
0ffc9a1a-833e-5c0d-9203-006b150f1ae1 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
0ee4669a-77f0-5020-b117-c5902b27a085 | note | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4.8 table 4.7
836d2375-f19e-5944-ad83-8dcccf0be7a3 | note | Verifying Document - IANZ Accredited Report
5abcb87f-3bc3-5bbf-a680-6c321234dfa2 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
692d6bc3-ded2-5e68-be73-481550c15b1f | note | ○ Results to Engineer 2 wks before importing
48c39bf9-df77-51e2-b94e-8e5f88073e75 | note | Verification Activity: Activity - HP
28273671-b7eb-566a-a25a-9bb459b87a4a | note | Verification Activity: By - ENG
b13d1c4c-46f2-445e-ba86-322c31162eff | signoff | AUTHORITY HOLDPOINT
a3e4c26b-fb8b-4d37-8907-4811296581ad | checkpoint | 3.9 - Cone Penetrometer Limit AP40-1
a11a03fd-8180-557e-8a37-15d48309d627 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
263cfe2a-55df-5212-aaba-e1f65cf4ffc0 | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 30
516b5720-b922-5d1b-b00f-cbb5f6cd3021 | note | Standard / Specification - PS 20.9 TCC-IDC IT-4.8 table 4.7
f32d9074-9915-5d19-9343-fefe8bd14188 | note | Verifying Document - IANZ Accredited Report
a8a8a844-e236-55f5-b464-261b23f15ebb | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
332f754f-80ef-53ea-ba6e-c231c450202f | note | ○ Results to Engineer 2 wks before importing
24d2d1f9-fe4e-5339-8841-f8ebfe60d468 | note | Verification Activity: Activity - HP
4e04f391-2630-5c0b-ad53-22a88b8d2764 | note | Verification Activity: By - ENG
2aa79dc1-dde3-4c31-bfca-24f0cbc6fb0f | signoff | AUTHORITY HOLDPOINT
9d907072-07ec-456c-8031-72142a38f3f8 | checkpoint | 3.10 - Clay Index AP40-1
153cee03-2f75-538b-ad55-6ae9b2d122a7 | note | Detail - NZS4407:2015, Test 3.5 - Clay Index Test Report
67a1f8a0-3c47-5be9-8ee8-9269faab26cf | note | Acceptance / Conformance Criteria - ≤ 5
8f7a28ab-eeef-5ac8-8dcc-ea054524999f | note | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4.8 table 4.7
e4082c3b-24b9-5417-aefc-360e52756a36 | note | Verifying Document - IANZ Accredited Report
9b2041b0-589a-525e-bab5-488b739b3b3a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
6c7b8be0-9617-534f-9950-5590389a54bb | note | ○ Results to Engineer 2 wks before importing
8825c4a2-cdca-5315-b68e-5bdcee3059d7 | note | Verification Activity: Activity - HP
9f7709e0-947b-5f4b-ab84-57a0ea001e5a | note | Verification Activity: By - ENG
40452a89-3b19-4c70-ae70-18a8a2acc2b3 | signoff | AUTHORITY HOLDPOINT
fbf9d29a-c12f-4fc5-a745-3dd4fc8f774a | checkpoint | 3.11 - Maximum Dry Density and Optimum Water Content AP40-1
22e3f3a0-0cd1-5922-ba6f-d4a8fb90e906 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
b5e14e62-2273-5274-8dd0-c3505a954d39 | note | Acceptance / Conformance Criteria - Report Value Only
17a34cd5-7839-5873-a04f-014d4263d00c | note | Standard / Specification - NZS4402:1986 Test 4.1.2
4d0a9968-45c3-54de-9c92-bd86414748e6 | note | Verifying Document - IANZ Accredited Report
ead4acc3-5a66-55f2-b01c-2b4dbf270866 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
ea8214f1-4aef-5a51-bfa3-b6003f49d783 | note | Verification Activity: Activity - HP
1df3400b-44c0-54c4-803a-48968df32bf1 | note | Verification Activity: By - ENG
d6985e0f-a419-4b36-b927-1582d6eac580 | signoff | AUTHORITY HOLDPOINT
870e4232-d4e0-49ed-aea4-0f5e6ab7a189 | checkpoint | 3.12 - Reinforcing Mesh
67b4d9db-33a4-54f2-851a-f759b0bc4b2e | note | Detail - 661 Reinforcing mesh (Commerical Vehicle Crossing)
2123372d-8112-58bd-afb5-59af53a2415c | note | Acceptance / Conformance Criteria - 661 Reinforcing mesh (Commerical Vehicle Crossing)
5d0de0b1-80a4-5796-8c27-e0cf26855417 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
792f5c28-0ea8-56ba-a86d-8a8cf8202e28 | note | Verifying Document - Material Data Sheet Engineer's Approval
16e5279a-af21-56ba-9cb3-108ff71bd25a | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
e41e91a3-b672-59b0-a34a-6e40290226fb | note | Verification Activity: Activity - W
34723dd9-b4cb-544b-87e8-3bd38c8b911b | note | Verification Activity: By - SE
8554a41c-c9fc-49af-b76d-5716e2d86026 | checkpoint | 3.13 - Reinforcing Ties
82c89975-afa5-5308-afb1-01052ca2521e | note | Detail - R6 Ties (For commercial crossing only)
21ee6caa-60e1-5cba-b26b-b919b499d0e8 | note | Acceptance / Conformance Criteria - R6 Ties at 600 centres with 60 mm (For commercial crossing only)
04e86c72-631b-5b6f-9a13-7063dc6efd57 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
fc2e7ae1-5090-5131-95ae-9e19fe0d2bf9 | note | Verifying Document - Material Data Sheet Engineer's Approval
b5086ffc-ac53-58cb-a723-d5a2412a1a60 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
b91fcf85-9695-57b9-9499-a83b0cf91692 | note | Verification Activity: Activity - W
108f155a-ed90-508d-9deb-255a298bfce7 | note | Verification Activity: By - SE
74466020-4d2d-4849-b19f-b574786dd452 | checkpoint | 3.14 - Reinforcing Bars
a3eb3387-5966-5b53-aa9b-d16c0e42a87d | note | Detail - 4-D12 Bars (For commerical crossing only)
2a05ba1c-c6ff-5e0a-9883-4f8855a53efa | note | Acceptance / Conformance Criteria - 4-D12 Bars with 50 mm Cover (For commerical crossing only)
b99bd81c-203b-5b69-9725-d7c5a3ee19b8 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
d7f43b15-cf59-5d8a-9c82-fa6d7b68ac9f | note | Verifying Document - Material Data Sheet Engineer's Approval
2d68f874-c84d-5224-acf8-68c19f0c7c13 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
a9e70408-3f79-5e92-a5bb-9b4957c43821 | note | Verification Activity: Activity - W
a9543611-6886-55bd-b30a-a0554bac6b8b | note | Verification Activity: By - SE
8a7298ff-84c6-4931-8ff6-ef6da61aab5a | checkpoint | 3.15 - Concrete Mix Design
5ee5a56c-241e-51cf-b1a6-e965ae2377ac | note | Detail - 20.0 MPA concrete. 4kg/m3 black oxide (2.5%)
ad4fdddb-d035-5c9a-a9d1-30b328526c79 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 20MPA
bddbd9a0-cebf-587a-86b4-9f4c6418590d | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405
2451e509-ec8a-5f01-9f5c-26e9d6349a43 | note | Verifying Document - Material Data Sheet Engineer's Approval
b6b0ec4c-2cd7-5600-9863-70bd7ffed300 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
a9976407-a2a9-5c2f-81e6-81a004848ff7 | note | Verification Activity: Activity - HP
f7a80757-7755-5511-abb3-f4922bc6e7d4 | note | Verification Activity: By - ENG
a78d8094-7699-4834-b5df-d3a4cb6210a2 | signoff | AUTHORITY HOLDPOINT
fad519b6-ea76-45ba-ad0e-51e8555b2744 | checkpoint | 4.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
a2fb88f4-6a82-5304-9b15-56627e370fde | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
d1c8d191-23f5-52fe-9919-1fd0c0bfe512 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
394074f0-2136-5e50-91e1-f422b7239311 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
f2989927-409b-5546-a61b-868d0aebec62 | note | ○ CBR: >3
51de5b30-fd13-5f1e-ac6b-ca62ef608750 | note | ○ Single Test Minimum SU: >50kPa
7fd8ed8f-a4cb-5488-80e0-bbbd2f6a68d4 | note | Standard / Specification - Project Specifications Appendix XVIII
0b3f5ca7-2e0a-5600-92dd-4413ca8c8f42 | note | Verifying Document - Shear Vane Report
f7178e20-37a5-5072-8ab9-5a550391ad72 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100m2
562bd974-0c17-5f1b-a757-ba5ba4a88e7c | note | Verification Activity: Activity - I
5a8b80a7-6120-558b-a1cd-af2cb4d5476f | note | Verification Activity: By - SE
d3f3d83b-4a00-40c2-a300-ab0d665e206b | checkpoint | 4.2 - Cut Subgrade Testing - Granular Scala Penetrometer
9cdd536c-cb32-5003-97c3-25aeb9cb8360 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
466aa08a-4f4a-5c20-a8fe-3ed323e8b71b | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
038287bd-97a0-5c30-81ae-95906d866fb2 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
107b84ff-948f-5eb7-aa8c-80955cfe7a11 | note | Standard / Specification - Project Specifications Appendix XVIII
8effd770-f368-5ca0-b895-e95c48d7680d | note | Verifying Document - Scala Report
076c2a31-ffbd-5b4d-895a-dd9702411e8a | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400m2
5d213efa-4d60-5311-bf15-829213346419 | note | Verification Activity: Activity - I
fe5b2b2b-b8ce-5f17-ba75-29bdb9f84359 | note | Verification Activity: By - SE
b6019b2b-479a-4901-83b9-2e4489a9c681 | checkpoint | 4.3 - Proof Roll Subgrade
d130298d-8cc7-54a7-9d36-05f0dcb55c2e | note | Detail - Visual Inspection of Proof Roll
d335d3e9-cbb7-5f27-a4ab-f9fd89ad76ac | note | Acceptance / Conformance Criteria - Visual Inspection
5c2a4f3e-58a4-5577-b64b-693c7e7951a8 | note | Standard / Specification - Project Specifications Appendix XVIII
0a9930a4-09a2-5ffc-b56b-1dda6a652aa0 | note | Verifying Document - Visual Inspection/Photos
8f2ca425-14a9-56b7-81e2-88f92e8bce07 | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
b29715cf-1535-5f26-9123-3e549a22fcc5 | note | Verification Activity: Activity - I
464ccc26-e6fa-5062-ac23-efffbd3f945d | note | Verification Activity: By - SE
e1d95dc3-af51-45a2-bbc4-12a56713c353 | checkpoint | 4.4 - Hold point
e69d59d3-4f40-579b-ac05-642bdbccdb9e | note | Detail - Subgrade signoff
c2b8d676-8a55-5806-8e75-034c829e371b | note | Acceptance / Conformance Criteria - Conqa signoff
4f58d071-9ecb-5528-aea6-8879980eb697 | note | Standard / Specification -
39a55e13-7a9c-5dc0-b09b-c3f38d5a1961 | note | Verifying Document - Conqa signoff
246c7d9a-f8f2-5d80-bb0a-8f7fda777a0e | note | Testing Quantity Required (based from schedule qtys) - Each area
02d9fc61-3256-5e94-ac7d-545b877f8abc | note | Verification Activity: Activity - HP
7d2b1b49-e424-5ff7-b7fd-13095da615ce | note | Verification Activity: By - ENG
5fe2da02-430d-41de-b1c3-f786d3c95179 | signoff | AUTHORITY HOLDPOINT
4945cef2-867a-45cc-9bb7-d26187e983e4 | checkpoint | 5.1 - Stringlines or equivalent Basecourse (AP40)
1284211a-6b50-556d-8eca-73cf2b6cff49 | note | Detail - Stringlines or equivalent to check finished height of surface
ffefcf21-f7fd-5200-bc39-1ed11c13b302 | note | Acceptance / Conformance Criteria - Height +15mm/0mm
e59685be-cd17-5099-9a05-23cb9f07186f | note | ○ Width –20 mm +100 mm
3775e975-b2ee-5d56-815f-460b17a276fb | note | Standard / Specification - NZTA B/06 8.2.2 - Table 3
ec36e44e-91e7-56bf-b856-700cfb2fee5d | note | Verifying Document - Surveyor Records
450c2516-ee4f-5ede-872f-31a0e5f34030 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres 1 set = 5 tests
27140b61-2825-5158-b7c6-9e9297d6fdc9 | note | Verification Activity: Activity - I
626a6d84-083f-5566-8cea-38c4b10dbd67 | note | Verification Activity: By - SE
719f9058-0b22-4afd-b334-7965d68099f2 | checkpoint | 5.2 - Compaction - Clegg Hammer Basecourse (AP40)
54682ad5-f002-56ae-b3b2-9e9fec3ac222 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
cb1451d8-859c-5ac9-86c3-c547c318a5d6 | note | Acceptance / Conformance Criteria - Min CIV 18
8eafbe36-f6f3-5f48-94eb-a13300f00758 | note | ○ Ave CIV 20
76b8104b-0a42-5105-9ef4-488bf8b9b33d | note | Standard / Specification - Appendix XVIII
76ec4b88-c467-5ee6-be83-3331241eccd0 | note | Verifying Document - Clegg Hammer Report
283788dc-bbe5-5860-8237-430fd22ad0c6 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
394e496c-e9f1-5b74-a877-ad4e61659da7 | note | Verification Activity: Activity - H
b46ff47b-6f07-5a5d-a5ab-1b4512441512 | note | Verification Activity: By - SE
f305598e-6f60-4335-a667-0593c44e5f1b | checkpoint | 5.3 - Compaction - NDM Basecourse (AP40)
45902692-4466-5393-81ed-2354776ce578 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
5a8f9b16-a47f-5fb1-ad59-2aec43e5c866 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
fc9fc492-0fdf-5208-a962-fbb98e322c15 | note | ○ Min >92% of MDD
9dc8a9bf-bc0a-5129-9d14-ad7d5a28b841 | note | Standard / Specification - NZTA B/02 7.6
33dbe885-1316-5c2a-89b1-39c3bd36f923 | note | Verifying Document - IANZ Accredited Report
39d49d5f-1dfd-5bdf-a96d-cdf251de8d37 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
e824baa7-d19d-5076-91c3-1b3d67825355 | note | Verification Activity: Activity - I
a8f7ff9f-5717-518d-afeb-a9d1228ff9d8 | note | Verification Activity: By - SE
b8fbcd0f-2fd0-42ff-9f93-7c79e4e7951a | checkpoint | 5.4 - Hold point Basecourse (AP40)
75fc2d71-c2b0-58f2-bcda-3f324180e328 | note | Detail - Basecourse signoff
aba6f9d2-252c-54c9-b53e-f6d26d172a7f | note | Acceptance / Conformance Criteria - Conqa signoff
cd788c71-2ea6-59b2-8e6a-dc6ba9a8d872 | note | Standard / Specification -
d64f50c3-747e-5c84-ad90-18c7c0ef5967 | note | Verifying Document - Conqa signoff
83a8c666-8512-5459-923d-ac33a54587e1 | note | Testing Quantity Required (based from schedule qtys) - Each area
31a8f88b-63fa-5b47-b46a-eb38c0da5344 | note | Verification Activity: Activity - HP
77ed4cfa-55f9-51d8-b135-fe596eb25e06 | note | Verification Activity: By - ENG
61991fc2-1b62-488d-936a-bad4ab13c5a2 | signoff | AUTHORITY HOLDPOINT
0f8d8485-5b37-4e66-a3fc-a2ba26f4864a | checkpoint | 5.5 - Surveyor check FORMWORK
d410731d-c37c-55e5-b141-9f2ad6e11c98 | note | Detail - Equivalent to check the position of the formwork
6d9c1510-55a7-56a8-a8f3-8ee89b2345b1 | note | Acceptance / Conformance Criteria - +\- 100mm of design
4c7f1649-1a0f-5fe5-bd7f-bb99c9d6c966 | note | Standard / Specification - Project Specifications 27.4.5 (b)
4036d351-d428-5501-9beb-0ea585d4b716 | note | Verifying Document - Surveyor Records
06ae842a-b0e8-5680-9f54-35f3150ee8d0 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres 1 set = 5 tests
d2db4247-3089-5cd3-ba8b-4b387b8b564f | note | Verification Activity: Activity - HP
5bbfdf06-1748-56cd-a456-b7ddf4036b62 | note | Verification Activity: By - ENG
569a1f27-4e91-4c40-8466-6d9c77d56759 | signoff | AUTHORITY HOLDPOINT
2ca0904a-9fd8-4371-af3c-3de25cf095ce | checkpoint | 5.6 - Surveyor check FORMWORK
d2887b78-65d8-5df5-ada8-377e5403c8a9 | note | Detail - Equivalent to check finished height of framework
90edbc58-226c-524b-a77f-247bf05f1228 | note | Acceptance / Conformance Criteria - +\- 10mm of design
62cf691f-be5f-5f64-b1e7-32f674687942 | note | Standard / Specification - Project Specifications 27.4.5 (b)
7f75245d-9230-548b-bc37-dc0a8c104c5c | note | Verifying Document - Surveyor Records
9749cc13-8006-530d-8fa4-7e4d1ab3fe95 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres 1 set = 5 tests
c028b8c1-f935-53a5-8bc5-f3b06c38dc43 | note | Verification Activity: Activity - H
2e0806f8-7d9a-538f-b7fd-0411f57f3f91 | note | Verification Activity: By - SE
81c88f14-fb2e-41fe-a62a-785d97a752f6 | checkpoint | 5.7 - Reinforcing Mesh Check
761b7ed6-1afb-5efc-80a9-17a69bdbf30c | note | Detail - 661 Reinforcing mesh (Commerical Vehicle Crossing)
336607f8-e7c4-544c-9513-6271a2eaffc9 | note | Acceptance / Conformance Criteria - 661 Reinforcing mesh (Commerical Vehicle Crossing)
966fa8ba-ed1e-5f61-b52c-993d53c7dd28 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
10953c70-03c4-5b0a-b30d-89e32fdba47f | note | Verifying Document - Delivery Dockets
a953ae86-bf13-5e0d-aa0e-f7ef90ebc829 | note | ○ Visual Inspection/Photos
9ddc9bf9-2546-5ef2-a530-24a3a171e7be | note | Testing Quantity Required (based from schedule qtys) - Before Pour, During Construction
39438422-6a7b-5e7e-9569-506baf02cd44 | note | Verification Activity: Activity - H
1288554a-6ece-5d11-bdd0-5c0263bccd9d | note | Verification Activity: By - SE
001af409-2f61-435a-9d06-ac882ac51478 | checkpoint | 5.8 - Reinforcing Mesh
4855189f-1e06-5e39-a158-d100e521e37a | note | Detail - Ensure that overlap and cover above and beneath mesh
0ce7b539-2dcb-5ad7-8f09-1d986363e1f0 | note | Acceptance / Conformance Criteria - Reinforcing mesh to be placed centrally in the concrete layer
216321a6-837f-5012-8b73-9da2ed8ca6cc | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
f89aa209-8f62-599a-83d3-5a6c42bc3e14 | note | Verifying Document - Visual Inspection/Photos
13af5fec-c308-5e74-b581-d0bbd0e06641 | note | Testing Quantity Required (based from schedule qtys) - Before Pour, During Construction
0443d682-6e33-5c7b-92ea-701b2f1314e1 | note | Verification Activity: Activity - H
7845e3cf-1369-5000-abc8-61186255ec37 | note | Verification Activity: By - SE
ff151522-8570-4603-8c59-5c10c555c246 | checkpoint | 5.9 - Reinforcing Ties -REINFORCING STEEL (COMMERICAL VEHICLE CROSSING ONLY)
57e7d8de-0f9c-59f1-9a71-a2a93186dc19 | note | Detail - R6 Ties at 600 centres with 60 mm (For commercial crossing only)
dc5d605d-ad84-5f0d-976a-369f9ffd11c8 | note | Acceptance / Conformance Criteria - R6 Ties at 600 centres with 60 mm (For commercial crossing only)
5df02f89-e3b6-546a-8c35-f863f2c454f8 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
9d4c5d49-1406-5021-82b2-ca3b233f2bb5 | note | Verifying Document - Delivery Dockets, Visual Inspection/Photos
2b516b30-e107-506d-a12f-46fde32926a0 | note | Testing Quantity Required (based from schedule qtys) - Before Pour, During Construction
8fca45ee-4af7-577a-a691-58db6ff786fb | note | Verification Activity: Activity - H
5177608d-d700-5aa4-a96c-b9c31b8d7c25 | note | Verification Activity: By - SE
224350a2-65f0-441a-9d2c-881152f81af3 | checkpoint | 5.10 - Reinforcing Bars - REINFORCING STEEL (COMMERICAL VEHICLE CROSSING ONLY)
7bc97e17-1072-508b-9ed5-44570e71ce8b | note | Detail - 4-D12 Bars with 50 mm Cover (For commerical crossing only)
a645f6cf-1540-53da-9bd2-6f2581a16cfc | note | Acceptance / Conformance Criteria - 4-D12 Bars with 50 mm Cover (For commerical crossing only)
68250e01-32a9-5aa1-8820-b9dc1e910894 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
ca5db0b0-364b-51b3-9214-8501a22fd773 | note | Verifying Document - Delivery Dockets, Visual Inspection/Photos
b678cb5e-9e63-57fe-b123-0bfcf01d2af0 | note | Testing Quantity Required (based from schedule qtys) - Before Pour, During Construction
5a8d839d-8193-5136-809c-39d2727ca658 | note | Verification Activity: Activity - H
03a90494-8cfb-5cb7-95d1-d88c5e95fce7 | note | Verification Activity: By - SE
052c69ad-28e9-4e4a-a12e-c90fc47e1124 | checkpoint | 5.11 - Concrete
c8535f81-6bc3-5c81-b0f4-2f2e4e061765 | note | Detail - 20.0 MPA concrete. 4kg/m3 black oxide (2.5%)
6ab740f0-95f3-5386-ac4c-c4bd46029b4f | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 20MPA
cc7d1faf-8b97-52bf-bcb7-5e1d184e1f9f | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405
4b564f4c-b21f-56e6-996e-d7e14842ce4f | note | Verifying Document - Concrete Delivery Dockets, Test Results
cf2fe36e-2a8f-5e08-ac68-9476fdaac243 | note | Testing Quantity Required (based from schedule qtys) - Before Pour, During Construction
2fdf0a11-8232-515d-b131-3fe9b10da53b | note | Verification Activity: Activity - H
9ae2f4a5-b3d8-5c59-803d-3777ea9e66ca | note | Verification Activity: By - SE
0ef0189f-1909-4413-9642-d359accbca19 | checkpoint | 5.12 - Concrete Layer Thickness
df878378-d557-5a77-8104-20c0873857da | note | Detail - Concrete layer thickness to be 150 mm for Residential Vehicle Crossings
fe7c4ea0-7cb2-5b90-93b8-e5ff8a95131b | note | ○ Concrete layer thickness to be 200 mm for Commerical Vehicle Crossings
8ea00c13-fb4c-5838-8a22-fbf0f40d8f2e | note | Acceptance / Conformance Criteria - Concrete layer thickness to be 150 mm for Residential Vehicle Crossings
33cfb4d1-e8fa-527e-aa20-2a3fc0a6a26d | note | ○ Concrete layer thickness to be 200 mm for Commerical Vehicle Crossings
c6531446-04e6-54f7-bb26-ffd7667d4ca0 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
3ab2d220-59c0-5f5a-8d31-46c0e36dd07b | note | Verifying Document - Pre-Pour CheckSheet
de897fbe-4837-5c5d-b144-f5205519adec | note | Testing Quantity Required (based from schedule qtys) - Before Pour
02f736df-36cd-52e6-bc9d-dfbe1c8c1a53 | note | Verification Activity: Activity - H
a29d224e-1d97-55fd-928d-c3b03a65f2ee | note | Verification Activity: By - SE
ebfaa95a-ded6-4ffc-b45d-3179ff844396 | checkpoint | 5.13 - Final Finish
0e7d5a89-c5ae-5a58-9253-6b023441bbd8 | note | Detail - Rough broom finish
d39d2fc4-1cc9-575f-a374-8694852e07e3 | note | Acceptance / Conformance Criteria - U5
f7324e74-890b-5975-baf2-9c2c4a064b9a | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405
8a972112-991d-50ee-834e-8767e4edefc9 | note | Verifying Document - Post-Pour CheckSheet
1c13b019-2ba6-5ca4-a541-78a06f6814d4 | note | Testing Quantity Required (based from schedule qtys) - After Pour
f735f7a9-3955-5050-b626-a301b44029e6 | note | Verification Activity: Activity - H
c94224ce-b6f9-58ed-9996-d46964b6a817 | note | Verification Activity: By - SE
0ee2b0e8-9952-409a-8b18-1c5cf4d9c509 | checkpoint | 5.14 - Saw Cuts
eb3392d2-ab5c-579d-b963-e471a2eefbfe | note | Detail - Saw cut expansion joints at 4m centres maximum each way
947b8a05-d199-55bf-accd-4f407d4abeed | note | Acceptance / Conformance Criteria - Saw cut expansion joints at 4m centres maximum each way
2479c242-f0ba-5dfa-bb5d-b94bc27c2ecc | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
e7945b4e-8526-5c68-a7f0-8746e64610ac | note | Verifying Document - Post-Pour CheckSheet
4a85f4ad-781a-5c8c-a24d-ddbf364ee6a6 | note | Testing Quantity Required (based from schedule qtys) - After Pour
d4e473b2-3fd8-52ae-8752-28d223229567 | note | Verification Activity: Activity - D
3ed4b38c-35f9-5f3a-ac0f-07e1693ddae7 | note | Verification Activity: By - SE
05e44245-66ee-4b80-a54a-a564ff65c616 | checkpoint | 6.1 - Stringlines or equivalent Basecourse (AP40)
e8310ad2-fde4-5be6-876f-9ac8da0c8e60 | note | Detail - Stringlines or equivalent to check finished height of surface
99d02a4f-6771-58eb-bce1-f56ae7c61888 | note | Acceptance / Conformance Criteria - Height +15mm/0mm
e4cfb46a-e754-5fb5-a204-cb7c4502a654 | note | ○ Width –20 mm +100 mm
fb812dae-2f22-5456-a05f-90eb2d6d70cf | note | Standard / Specification - NZTA B/06 8.2.2 - Table 3
e548a37f-ad1c-57e6-b1bc-6ff2f7c90976 | note | Verifying Document - Surveyor Records
068576c6-a139-533d-b02d-288532e729bb | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres 1 set = 5 tests
f634c309-08cb-5856-88bd-58c6378bc2cc | note | Verification Activity: Activity - I
d08a79d5-5700-5adb-9e2d-394b8d68967c | note | Verification Activity: By - SE
e11d3ca6-7bad-4c10-902a-7de94671f38d | checkpoint | 6.2 - Compaction - Clegg Hammer Basecourse (AP40)
08d5da89-9ba5-5238-827b-048ba131f6b6 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
05bb2ae6-220d-5f7e-baa8-694f39c41be5 | note | Acceptance / Conformance Criteria - Min CIV 18
1b85d791-f229-50c3-9fff-1e978d352d0a | note | ○ Ave CIV 20
55e68498-f597-569d-bcde-c4566086508c | note | Standard / Specification - Appendix XVIII
53abf339-4022-52a7-a51d-ac5b3e42a723 | note | Verifying Document - Clegg Hammer Report
9faf1ca1-bfb1-5bda-a27b-6fc4adf40e6d | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
6eab055d-15bb-5381-a0bd-d6f6aebe0f96 | note | Verification Activity: Activity - H
d45af9d8-b58a-5b44-8a84-129a4dd13b0a | note | Verification Activity: By - SE
da1578a3-be50-4532-b3f0-a787bbe61191 | checkpoint | 6.3 - Hold point Basecourse (AP40)
8c14d710-07d5-536e-84f8-27ae061b7845 | note | Detail - Basecourse signoff
3c673987-e3cd-5fc2-9a73-c55185d1e5b8 | note | Acceptance / Conformance Criteria - Conqa signoff
df773ee9-5b80-5f03-9804-b553027e40a0 | note | Standard / Specification -
454cd192-ec9d-5ec3-b1dc-23eb9f31aa91 | note | Verifying Document - Conqa signoff
323d3d58-ea0c-5eb1-b4f6-6485ce300c06 | note | Testing Quantity Required (based from schedule qtys) - Each area
eaab690c-8a7c-567d-a90e-6eaf4165f25c | note | Verification Activity: Activity - HP
2c0e8c8c-a9c0-5a3e-9464-26bcfcdfba16 | note | Verification Activity: By - ENG
a26e1a11-79c2-4c80-af0f-49a7db4e0f0f | signoff | AUTHORITY HOLDPOINT
e836e53e-cf3c-4f1f-8e73-ca78a92e1e09 | checkpoint | 6.4 - Concrete Layer Thickness
4bdde025-275c-529a-826d-0e77ff870fab | note | Detail - 100 mm thick concrete
7c0a6751-b182-523b-9e42-d16c93f72a84 | note | Acceptance / Conformance Criteria - 100 mm thick concrete
2735ab55-51b8-5246-b45e-792dc14935bd | note | Standard / Specification - 232735.02-WSP-DR-RSA-0304
413305e0-833c-508f-9894-28baa117cafd | note | Verifying Document - Pre-Pour checksheet
f95bae3e-8ed4-5368-a0e7-fc3e6f10e2a1 | note | Testing Quantity Required (based from schedule qtys) - After pour
a45d49a4-4a6d-5068-ab0b-084c84b8b481 | note | Verification Activity: Activity - I
3b938fe8-36e3-521e-aec7-930ec5538fa8 | note | Verification Activity: By - SE
94a14f37-d16c-4c0f-83f3-1569b3be9a0e | checkpoint | 6.5 - Final Finish
379d3f70-e056-536b-842c-6b7da0812561 | note | Detail - Rough broom finish
0ffb873e-aeb2-56bd-8519-ed729f3a9c20 | note | Acceptance / Conformance Criteria - U5
a7a55b52-cfc0-5a7a-b2ee-d6b0ba75b260 | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405
255ea64b-4500-513d-9093-ab40312ab81e | note | Verifying Document - Post-Pour Checksheet
99a9383e-9a6f-5779-aa2e-96760f597969 | note | Testing Quantity Required (based from schedule qtys) - After pour
4fe7a6a2-151f-547a-93eb-0aa858f5c1b4 | note | Verification Activity: Activity - I
c31c91cc-31d1-58b1-8678-06c3033b35e2 | note | Verification Activity: By - SE
c5cbe8e8-f6ff-4d3d-872c-ec28d9974fd2 | checkpoint | 6.6 - Cycle Entry Ramp Detail
8b9e23ca-c8df-5bf9-81a0-8d0e0a31dcf1 | note | Detail -
666632cf-6fcf-569f-9325-ba60e11c605c | note | Acceptance / Conformance Criteria - Maximum 1 in 10 Grade
e4d130d3-19a1-5ed1-b31a-6d313dd1c37c | note | ○ 1200 mm wide cycle entry ramp detail
06d33fdf-4802-5beb-ab77-f785341193ad | note | ○ 45 degree angle from the travel lane in the horizontal plane
91372278-a85c-5a12-b1c0-ee8b240fef44 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0304
4e449817-50b3-5dad-b7d5-387407eceedf | note | Verifying Document - Photos, Measurements
e011165d-0686-50f6-bf87-87de1cf37da1 | note | Testing Quantity Required (based from schedule qtys) - During construction
f03334fe-e21e-56fd-9e13-d4b5b1b5e386 | note | Verification Activity: Activity - C
88914c27-b24e-5410-bc8f-1b40c1323619 | note | Verification Activity: By - SE
1869ab82-b1a8-4f11-9498-bd4b7ae1b310 | checkpoint | 6.7 - Cycle Exit Ramp Detail
4491f8d3-d65b-53be-89f8-47f6422966e5 | note | Detail -
cbd7bc80-8ffb-517c-949e-df669433efa8 | note | Acceptance / Conformance Criteria - Maximum 1 in 10 Grade
534b36bc-9089-59ce-b9d3-2f6cb8c1ed04 | note | ○ 1200 mm wide cycle entry ramp detail
34b991b4-d4ad-52a3-8cc2-4003c16c4038 | note | ○ 20 degree angle from the travel lane in the horizontal plane
5f1ae0c2-baa0-5c74-ab7e-9b5f1c3266f4 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0304
c9ba477c-2cd5-5f75-8a76-0cececcaa7fb | note | Verifying Document - Photos, Measurements
cf91dffb-e0a4-5cf9-82d2-a158795cbe65 | note | Testing Quantity Required (based from schedule qtys) - During construction
ffcc5594-c4ef-593c-9f2f-052f7b5c8252 | note | Verification Activity: Activity - C
505a9114-d123-5300-b663-3f8be0ddedd8 | note | Verification Activity: By - SE
418701c4-6f9d-47dc-bc63-d9a846bc3846 | checkpoint | 6.8 - Bedding TACTILE PAVERS (PEDESTRIAN CROSSINGS)
e1166e57-2b46-5713-bc5d-f3a459fafe9c | note | Detail - 40 mm thick 2:1 sand/cement bed
209f05a0-b18b-53f1-a8fd-58dfbd4091f5 | note | Acceptance / Conformance Criteria - 40 mm thick 2:1 sand/cement bed
e7c2e6bc-9537-5d6e-b1f8-4cc158a3b22e | note | Standard / Specification - 232735.02-WSP-DR-RSA-0304
ddb08eee-4171-58e9-ab23-041be19944d5 | note | Verifying Document - Delivery Dockets, Check sheet
479f98a9-fdf2-5fdf-a3cf-bb8f17d18f41 | note | Testing Quantity Required (based from schedule qtys) - During construction
0feebb80-6c31-50f7-aae0-09a954ee293c | note | Verification Activity: Activity - C
0bae0d36-592e-561a-8bc6-36f91a1281a4 | note | Verification Activity: By - SE
39caebab-de2d-4d84-9289-c0e1e8fb2526 | checkpoint | 6.9 - Warning Indicators TACTILE PAVERS (PEDESTRIAN CROSSINGS)
6f8c09e6-ef1c-5c99-be7d-7d3d5aec3b57 | note | Detail - 300 mm square
214dff7e-283e-53e2-ad1e-d83266b501e1 | note | ○ 60mm thick
b9ba677a-28a8-52c1-a178-5a0177af8fe3 | note | ○ Shall be aligned with the intended direction of travel of the pedestrian
e269e241-b075-5912-8369-97f868e558f0 | note | Acceptance / Conformance Criteria - LTNZ RTS14 STANDARD
73128456-60ea-53d4-9b78-73e6fbf0b3c4 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0304
f1a3d8b8-5b85-59db-84a2-ef360f37a0d9 | note | Verifying Document - Delivery Dockets, Check sheet
4d2f2c0b-843b-52d2-a3b0-163ebb7edf65 | note | Testing Quantity Required (based from schedule qtys) - During construction
ad6e349c-a519-59ab-93f2-baeb2549cba0 | note | Verification Activity: Activity - C
232df158-f4f3-5098-a5a4-58a8bef99723 | note | Verification Activity: By - SE
581ceed2-d97d-4315-9af8-deaf2bfd2769 | checkpoint | 6.10 - Directional Indicators TACTILE PAVERS (PEDESTRIAN CROSSINGS)
53e24a82-a5b5-529b-b887-802e932452b6 | note | Detail - 300 mm square
827eb56a-c97e-58da-8b4c-9130e1bd96a0 | note | ○ Shall be aligned with the intended direction of travel of the pedestrian
e6620123-b1cf-50e0-916e-91d2e532cbb1 | note | Acceptance / Conformance Criteria - LTNZ RTS14 STANDARD
0d2c318f-3302-5aa3-b083-8064bbd937f2 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0304
01ab398f-ca6d-5e17-a972-00373f9f3dce | note | Verifying Document - Delivery Dockets, Check sheet
7fe9c4f2-e2cc-5789-b75b-c076c8e1e0f1 | note | Testing Quantity Required (based from schedule qtys) - During construction
8ef3f483-5d07-538f-91ab-1c7793017794 | note | Verification Activity: Activity - C
dc56b608-ab5f-5e2e-85fb-dcc0ef2ab425 | note | Verification Activity: By - SE
433822d7-44eb-404d-9d50-3b0e52e73587 | section | SECTION 7 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
75077ba7-71c9-4f3a-9c91-856fdefb3ad7 | checkpoint | 7.1 - Final Inspection
4f94bd7f-b060-575b-9353-89ca3dbd7514 | note | Detail - Final inspection of all concrete work.
5a27e39b-cca8-5b04-8f4c-c0d9c69a1f10 | note | Acceptance / Conformance Criteria - All works meet project specifications and standards.
5ed53aa4-8288-51ae-ac1c-11e2d24ca267 | note | Standard / Specification - NZTA P39: 2013
bb2843c1-f4cf-58bd-a62a-71ced83c42c8 | note | Verifying Document - Final inspection report
45f490ca-37ed-5723-a34a-c8eeb430531d | note | Testing Quantity Required (based from schedule qtys) - 100% Completion of works
dba4fc47-9bc5-5088-8ee0-a9570c83217d | note | Verification Activity: Activity - HP
be7f6c4c-c44c-5266-85fb-d60c3926248f | note | Verification Activity: By - ENG
ae0f2727-687e-497f-9e97-c0d511809cd8 | signoff | AUTHORITY HOLDPOINT
48173a91-933a-4e90-bde2-7c40c79704b2 | checkpoint | 7.2 - As-Builts
f3014eac-dc75-5325-a955-a646ce80557e | note | Detail - Final inspection of all concrete work.
317cb403-7bad-5071-b581-a1b507662292 | note | ○ Red Pen Mark up
59318bfe-ce07-5f4b-a65e-43f84b5a1ca5 | note | Acceptance / Conformance Criteria - All works meet project specifications and standards. any changes to be noted on redpen markuProject Specifications
d613d325-03d3-55ca-8256-49fb8f9bfd91 | note | Standard / Specification - Project Specifications 16.7.6
6ba00932-e916-5390-a92a-e14caa94b799 | note | Verifying Document - Red Pen Markup
1973436c-0f60-586e-8287-574ca9c44505 | note | Testing Quantity Required (based from schedule qtys) - 100% Completion of works
8ff63bc2-6f53-5f39-aa2a-f03bd96ba845 | note | Verification Activity: Activity - D
19434bbc-fda2-50cf-b592-1a0526066273 | note | Verification Activity: By - SV
4c331c31-e2b0-492c-a619-cdd5221d5d35 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
ec3ab1cf-257b-5a9f-be01-c3dcf6a08700 | textbox | Contractor's Rep Name:
cfb675bb-ea30-5988-a0f5-db94f4e30ded | textbox | Engineer's Rep. Name:
0f9dbd9b-9fee-538d-8d6f-ecb8d8170d13 | date | Date:
765cb286-804a-4e6c-9319-806e521673c0 | signoff | Add Signature
a3ec19ea-fb3a-415e-ac47-612b76a92e36 | checklist | DN1210-SP2-008 ITP Noisewall 2-7 Rev 0 | itp | DN1210-SP2-008 ITP Noisewall 2-7
9e8119d8-8d2d-4ad3-91eb-edbc51f3bb0f | section | SECTION 3 – PRE-Construction - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
34acb1bd-6583-4d72-928e-31b1a77e49aa | checkpoint | 3.1.1 - All metalwork to be approved by the engineer after fabrication
6f40c8b1-010a-58e6-a5d4-a145312f5fe1 | note | Detail - Hot dip galvanised to standard hdg 900
fba28635-fbaa-5aad-966f-a7c84c1d8374 | note | Acceptance / Conformance Criteria - Hot dip galvanised to standard hdg 900
c9bf6de2-6326-5093-933b-cddc5e6aa21f | note | Standard / Specification - PS 18.6.3 (a) ii
218cc756-cf9f-5182-8130-ac9e28d9b121 | note | Verifying Document - Supplier data sheet, Engineers approval
8ed89573-61e7-5b93-bcd6-747b616a072d | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
a4966bcd-24b9-5f4f-9f57-4078947a09ee | note | Verification Activity: Activity - HP
f31a60fe-69c1-5c1f-a9c7-718a1b73d68d | note | Verification Activity: By - ENG
69093c9b-2817-4483-9764-992f35f729bf | signoff | AUTHORITY HOLDPOINT
aeefb3b0-7999-49b2-b3e1-8dc2d572f40d | checkpoint | 3.1.2 - Hot rolled steel plates
206cf21d-2867-5c07-bd23-4feef957d07f | note | Detail - All hot rolled steel sections shall be grade 300 complying with AS/NZS 3679: part 1
7e8ba921-8145-5b9c-95d1-a71525398bb6 | note | Acceptance / Conformance Criteria - Grade 300 - AS/NZS 3679 Part 1
5ee74d86-5686-5f18-b9a1-34ddbfeb410d | note | Standard / Specification - PS 18.6.3 (a) iv
b891024a-675a-5b8c-bc7d-a3aaa11528b3 | note | Verifying Document - Supplier data sheet/ Mill certs
a6c412be-88c9-5ee4-b6ae-79bc13e2476f | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
e71d4a27-6fe0-56b7-ba7b-696ef14ed512 | note | Verification Activity: Activity - W
a42b8fac-e60a-5c1f-b596-c8e1769db4f0 | note | Verification Activity: By - SE
de457bfd-5578-4b02-b8c4-d0941afff4a9 | checkpoint | 3.1.3 - Cold formed steel plates
04c451fa-4f21-5922-aa79-272d63dba929 | note | Detail - All cold formed steel sections shall be grade 350lo complying with AS/NZS 1163
42801bf5-bf45-5742-8acb-43dbcc6016a8 | note | Acceptance / Conformance Criteria - Grade 350 lo - AS/NZS 1163
e036e252-185b-5586-8600-15224ab205d8 | note | Standard / Specification - PS 18.6.3 (a) v
24de84a5-2a6e-523b-b3f6-a459924d78ab | note | Verifying Document - Supplier data sheet / Mill certs
edf16b43-6adb-590b-8183-1962682d6051 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
d5ded677-4b02-5e0a-9d91-85d60f3b0770 | note | Verification Activity: Activity - W
84e2a5e5-9043-5280-8da5-945e93789a34 | note | Verification Activity: By - SE
f7781b0a-b59a-47b1-a578-9d3adca5dabe | checkpoint | 3.1.4 - Mild Steel plates
e0f34842-0e31-5eee-b6b2-f18ccc0526e7 | note | Detail - All mild steel plate shall be hot rolled grade 350 complying with AS/NZS3678 (AS/NZS 3678-350)
90a5bfec-cb92-51bc-b618-c24f7c84661b | note | Acceptance / Conformance Criteria - Grade 350 - AS/NZS 3678 (AS/NZS 3678-350)
438b4241-be92-5c45-a353-9ab2e0f216ee | note | Standard / Specification - PS 18.6.3 (a) vi
2dd300ac-be74-5d5e-89a8-49c65bbf23b3 | note | Verifying Document - Supplier data sheet / Mill certs
97343aa3-5331-5c7d-b370-93d4b5d1f47b | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
c943a071-28b0-5eb3-a0ee-b538c60858c3 | note | Verification Activity: Activity - W
7408c952-7b71-57f9-b986-4fdbaf792d8a | note | Verification Activity: By - SE
b451e18a-2730-4919-9457-9dbdc93c647c | checkpoint | 3.1.5 - Round bar/rod
53a09e66-20bb-5881-8168-0563a78ac332 | note | Detail - To be grade 300 to AS/NZS 4671
5b91baf6-5cbb-515c-9e88-6895fd388775 | note | Acceptance / Conformance Criteria - Grade 300 - AS/NZS 4671
8d104787-4867-539b-930d-ffc1f14741b4 | note | Standard / Specification - PS 18.6.3 (a) vii
88a89188-8480-5cc1-bcf5-ad5edfa71111 | note | Verifying Document - Supplier data sheet / Mill certs
348e007e-b912-5a76-a8c7-5a0b436fe690 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
24bb8c6f-39d8-515d-a7d7-e87219cd64fc | note | Verification Activity: Activity - W
3d114b97-b0d1-5c6c-99ef-443014ad5181 | note | Verification Activity: By - SE
807a5e96-ab78-4c19-bda1-068311391440 | checkpoint | 3.1.6 - Bolts and treaded rods
463fc6b1-c1ee-58d5-84c8-64d258b9d5d5 | note | Detail - All bolts and threaded rods shall be category 4.6/s to AS 1252
04de57e1-25a8-5881-bf2f-4aad338aadfb | note | Acceptance / Conformance Criteria - Category 4.6/s to AS 1252
57746664-0fc4-57b5-8007-89537ca9b03e | note | Standard / Specification - PS 18.6.3 (a)viii
45de62ce-0058-58fa-be94-736b74f52250 | note | Verifying Document - Supplier data sheet / Mill certs
5560faa5-bd31-5f0a-a441-a626f8afe1fc | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
382fc319-94a2-5b30-8981-95f8cff25869 | note | Verification Activity: Activity - W
dec06419-d79f-5c45-95b7-287b8b07f734 | note | Verification Activity: By - SE
6a23f570-1f3e-46c2-b32f-dfbb2c67c65d | checkpoint | 3.1.7 - Rough or sharp edges
304c2ace-9368-58cf-8fb9-759a5aa1686c | note | Detail - All rough or sharp edges or protrusions to be buffed smooth
b2600f41-f9aa-5e64-af34-64fdaf2fd8fc | note | Acceptance / Conformance Criteria - All rough or sharp edges or protrusions to be buffed smooth
70649c90-f3ff-5292-939c-d5e763bb0e98 | note | Standard / Specification - PS 18.6.3 (a) x
1bcff286-e874-5e60-8c8e-9b8c91c2cd0c | note | Verifying Document - Visual inspection
14567ca1-a225-5df4-9779-ae6613a50efe | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
a5eab302-6847-52a6-a0b7-39dac69bda17 | note | Verification Activity: Activity - W
8b7d1bf2-fd53-5332-9a5a-7a872cd1fd56 | note | Verification Activity: By - SE
2df55bd0-c1d8-41a1-b611-9162e7702c3f | checkpoint | 3.1.8 - Epoxy Coating to the Steel column
18dc5a75-14eb-5983-a162-59782e97e248 | note | Detail - 250 mm high build epoxy paint all round the UC column concrete interface
52178578-9a77-59b7-ac49-2634f1e2fd67 | note | Acceptance / Conformance Criteria - all columns must be coted with epoxy at steel and concrete interface
d94f0821-ce9f-5f6b-a420-1d1cb1c8afab | note | Standard / Specification - WSP-DR-STR-0306
b7f04ba3-da99-5208-ad19-f21d6f249999 | note | Verifying Document - Visual inspection
cc7b9328-aee2-57c6-86c1-68c24aa596a2 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
318c99b6-9ea4-5722-9b38-80ce70435d1d | note | Verification Activity: Activity - I
eff90e94-9668-5b1a-90ac-095369a52950 | note | Verification Activity: By - SE
e1cb7638-3fac-4df4-a709-f6acae567a33 | checkpoint | 3.1.9 - Butynol sheeting - membrane
c4341796-624e-5291-a14e-45087f01832b | note | Detail - Butynol or any similar approved shall be used between timber and steel
32a50aea-7503-5450-bf05-f02a0a86ce7f | note | Acceptance / Conformance Criteria - Membrane seal
a503594f-90fc-535e-a153-9638b049d38a | note | Standard / Specification - PS18.6.3 (c)viii
7e141d4d-4162-5c82-a3a7-1970f02c7cb0 | note | Verifying Document - Supplier data sheet, Engineers approval
5b0deaea-dee7-5e6c-b6fa-2fc09114aa2b | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
fab02a30-b374-5a16-a594-f86c8e49d752 | note | Verification Activity: Activity - W
9f58bd19-9e95-5579-bbe8-4c2e546b2d97 | note | Verification Activity: By - SE
b578cb56-16f8-42eb-9434-25faaaf09826 | checkpoint | 3.2.1 - Timber
bdd53f89-9f3c-5e42-b02c-426386310ac6 | note | Detail - Timber shall be VSG8 grade radiate pine complyng with NZS 3603 and graded to NZS 3631
1845798f-7811-5071-8bb7-b12d6116f024 | note | Acceptance / Conformance Criteria - VS8 Grade radiate pine with a Timber strength - 11.7MPa
54f6e5e1-8cfd-5f4b-ae38-60e878e2cf85 | note | Standard / Specification - PS 18.6.3 (c) i
cad1a497-6f24-5a87-a01b-3b891ef0ea31 | note | Verifying Document - Delivery dockets and supplier data sheet
431a2847-68f3-5412-a5ac-0c3f2e472574 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
b8c0af06-19a6-5499-add8-d93a25fc03cd | note | Verification Activity: Activity - W
4e50c507-7218-5e1a-b7a4-202c3785253b | note | Verification Activity: By - SE
b3a77905-9fd4-4722-858e-9e0330dbabd8 | checkpoint | 3.2.2 - Timber - in contact with the ground
e4d7deca-a7f3-55df-947d-2c0d5c692720 | note | Detail - Round or rough sawn piles in contact with the ground to be H5
4e00b3cd-9eb5-5df9-81b6-f838d8f21b64 | note | Acceptance / Conformance Criteria - H5
858fe13d-dc37-5ada-9930-119bea94d02e | note | Standard / Specification - PS 18.6.3 (c) ii
97e8aef7-1506-53ac-ad87-4ba5b2cf39d8 | note | Verifying Document - Delivery dockets and supplier data sheet
78619f17-c04a-59e9-bd9f-221e83a5162a | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
e6c3ff42-450d-5f7c-b22a-d861a17b9479 | note | Verification Activity: Activity - W
43a729ea-f952-5619-8e7d-79606a7f0d59 | note | Verification Activity: By - SE
19e96e9e-bb8a-4a9a-a2c8-5849ca14c362 | checkpoint | 3.2.3 - Timber - not in contact wth the ground
cbcb9439-79db-5a29-abd6-d3c4583691ae | note | Detail - Rough sawn timber not in contact with the ground to be H3.2
e6cb1fd2-7534-5341-b8e4-6e5fd2ef9e7d | note | Acceptance / Conformance Criteria - H3.2
60ab5116-4577-50aa-a336-029166b9255e | note | Standard / Specification - PS 18.6.3 (c) iii
feca7eaf-a26f-59f1-aa7e-8dcd3b6939a2 | note | Verifying Document - Delivery dockets and supplier data sheet
9778e2d8-7cd6-5f83-a2aa-d2b56dfd4b25 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
ed67ff92-fe43-5e4b-ac50-28487bc420a8 | note | Verification Activity: Activity - W
5562bb4b-3e8c-5f00-8671-b140b9e70d88 | note | Verification Activity: By - SE
1964fe77-e14b-4372-babc-158e4c925818 | checkpoint | 3.2.4 - All timber components of noise wall
1f8a2f32-4de0-5a5e-bf22-c860fe34336d | note | Detail - Timber treatment shall comply with requirements of the NZ Timber Preservation Council incorporating - MP 3640.
0997d6aa-eab8-5482-85ea-bb5e76373b12 | note | ○ All timber shall be branded to NZS3640:2003 and must be treated not less than 2 months prior to use.
c5c17f2d-cf9c-52d1-9d41-6d88ca2ed51c | note | Acceptance / Conformance Criteria - MP 3640 NZS3640:2003
3251af99-2845-5bac-9707-3429346ff9cd | note | Standard / Specification - PS 18.6.3 (c) iv & v
404cb3fa-cb6e-58c8-8c99-8f678fe98479 | note | Verifying Document - Delivery dockets and supplier data sheet
cfd5978d-e9ef-5115-a121-d89aab987b7a | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
aed68953-ef49-5dc9-a6c8-a3f0581cd315 | note | Verification Activity: Activity - W
248e9f23-b0ec-5230-a7c1-ef204f5bc598 | note | Verification Activity: By - SE
3156536d-569e-437c-8a4f-84f79a5d7ac7 | checkpoint | 3.2.5 - All timber components of noise wall
693027df-3ab9-536d-9a17-54ad02777d82 | note | Detail - Timber shall have a moisture content less than 18% at time of installation to avoid excessive shrinkage effects.
b597cdf4-a5be-5ef1-961d-279408bbe2ff | note | Acceptance / Conformance Criteria - Timber shall have a moisture content less than 18% at time of installation to avoid excessive shrinkage effects.
854d267a-2364-5787-9c9c-df7e58251787 | note | Standard / Specification - PS 18.6.3 (c)vi
8cd5a344-19c6-576e-b409-a11beab04073 | note | Verifying Document - Delivery dockets and supplier data sheet
3fb776e3-a02e-5e35-a2b2-5deb0adcb4c1 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
a9b80a5d-ff38-5c6b-9c29-de27a20e2abf | note | Verification Activity: Activity - W
d8b441f5-69f6-5f8b-9520-a548a7c6ac6a | note | Verification Activity: By - SE
9d8a47ca-e37a-4e4b-b83c-88e72fe3ea19 | checkpoint | 3.2.6 - All timber components of noise wall
2ace340a-4e52-58af-95e8-b9bb0148ca5d | note | Detail - Treat all cut surfaces with clear zinc naphthenate preservative and in accordance with NZ 3602.
cff91989-97e3-50ad-a7f3-6d0b05d08a97 | note | Acceptance / Conformance Criteria - Treat all cut surfaces with clear zinc naphthenate preservative and in accordance with NZ 3602.
99a826f5-d66d-5ec7-b3d5-825e19e5cfa7 | note | Standard / Specification - PS 18.6.3 (c)vii
2df3cedf-0b46-52fe-80af-4e1cd74731a5 | note | Verifying Document - Delivery dockets and supplier data sheet
01a50cd3-fd5c-5cc1-89c7-8d96a4c2d0e8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
b43e391f-ae2c-5331-9bf4-1b99e77d2267 | note | Verification Activity: Activity - W
6cf2d1fd-fc87-5ec9-9e4d-34b1d6e4fc9d | note | Verification Activity: By - SE
bb313164-e312-485b-bab7-f4a5aab7bce8 | checkpoint | 3.2.7 - Galvanised bolts
a2c3564a-451d-5977-b46e-c02bf5e91f98 | note | Detail - All galvanised bolts in contact with H5 treated timber shall be protected using CP grease in pre-greased holes
0d72f1d5-bee4-543c-940f-182fe55b02b0 | note | Acceptance / Conformance Criteria - All galvanised bolts in contact with H5 treated timber shall be protected using CP grease in pre-greased holes
18f422be-1663-5fe1-bf3c-1fe918fe7174 | note | Standard / Specification - PS 18.6.3 (c) ix
864e444e-9bef-5340-9aad-31718a13265b | note | Verifying Document - Delivery dockets and supplier data sheet
8326cf66-1333-5bf2-b612-304b1d6fd98d | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
cdb89f4a-445d-5b6c-ad6a-780235c8444f | note | Verification Activity: Activity - W
e16c3fbc-546f-5eeb-ab56-8657238389f5 | note | Verification Activity: By - SE
27dbbde2-c50b-42e8-9d53-4e51d2c6cf5d | checkpoint | 3.3.1 - Concrete Grades
e12c7afe-0474-50e9-ac55-249263c4ea6d | note | Detail - CONCRETE (cont.)
c1a85fb6-459d-5f10-a238-61b8c79380ac | note | – – – – – – – – – – – – –
73059c58-425e-5f3f-b15e-a0af82bf9282 | note | C9 CONCRETE GRADES SHALL BE: (UNLESS NOTED ON DRAWINGS)
c818110f-6773-5f52-bf68-c664da02e912 | note | ELEMENT ¦¦ CONCRETE GRADE (MPa) ¦¦ EXPOSURE CLASSIFICATION ¦¦ MIN. CONCRETE COVER
6a1a1890-ca20-5488-bcda-ce4158fc4e31 | note | – – – – – – – – – – – – –
6f6f70a5-564e-5838-9b72-5dfe8bc5d1b3 | note | ○ PRECAST METALS ¦¦ 40 MPa ¦¦ B1 ¦¦ 40
e8518eff-2b69-5f0a-a051-5e9e146df215 | note | – – – – – – – – – – – – –
1cd93a72-30db-59fb-89b1-719483381b4b | note | Acceptance / Conformance Criteria - Concrete grade to be >40 Mpa
0a10fa1a-f45e-5def-9755-2c78cc49ce00 | note | ○ Exposure classification to be B1
f718dcf4-01a7-53a9-8335-ab312be985a0 | note | ○ Min.Concrete cover 40 mm
660c5051-ea8e-59e5-8887-0f42751233f0 | note | Standard / Specification - NZS 3109:1997
05e4bc5d-0c00-520f-8ef3-7cfa82297283 | note | Verifying Document - Supplier data sheet, Delivery dockets
1f7ada98-67d4-5687-9b9a-121359ea2e9c | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
6535feea-0eaf-5c9a-aa22-89e5a7207661 | note | Verification Activity: Activity - W
6160ae43-439e-5ebd-95f2-b3d0963cb050 | note | Verification Activity: By - SE
ae6a0e29-a0d3-41e0-8a32-7b70a78a2fe1 | checkpoint | 3.3.2 - Concrete Materials and Worksmanship
fa15f7de-8166-50f6-a70e-5cb449b410c8 | note | Detail - All worksmanship and materials shall be in accordance with NZS 3109:1997 concrete Construction.
c3e225bd-db90-5caf-b6ed-2939b384611a | note | Acceptance / Conformance Criteria - NZS 3109:1997
8b81a1a4-52f0-58ef-96ea-58b52a3f2dff | note | Standard / Specification - NZS 3109:1997
0ba24437-96e3-57eb-87d6-7574f4dd1f89 | note | Verifying Document - Supplier data sheet
1138f96b-a2dd-55ea-b429-6c0f14861f02 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
52cb29b7-07d1-5b09-a9da-8e3cd99e3b05 | note | Verification Activity: Activity - W
d2338ef0-7982-525c-92c2-dff9014bbcb3 | note | Verification Activity: By - SE
547e6e54-1279-47bb-8534-d71da1cbc9f3 | checkpoint | 3.3.3 - Aggregate & Concrete Mix Design
8de604ab-ef41-5977-9ed9-3d12f237e230 | note | Detail - Aggregate and overall mix design to meet the provisions of 'TR3 Alkali Silica Reaction 2003 (CCANZ)'.
feec80ef-7552-5abd-95c0-68cd3c728b13 | note | Acceptance / Conformance Criteria - Aggregate used and overall mix design (including additives) shall meet the provisions of 'TR3 Alkali Silica Reaction 2003 (CCANZ)'.
ef8c774a-07e7-517d-9996-6d95928d66b0 | note | Standard / Specification - TR3 Alkali Silica Reaction 2003 (CCANZ)
98fdf24f-b3f8-52ad-bc4d-97aa74f6abce | note | Verifying Document - Supplier data sheet concrete mix design approval, Delivery dockets
70d3e1b0-e871-5ed0-9560-9538fa0ad697 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
c75648b5-0fe5-5b2b-97bc-0fdcab423b29 | note | Verification Activity: Activity - W
c6a7990b-ee66-5229-8a65-8efb7bb486fc | note | Verification Activity: By - SE
e0f6e659-1790-4e34-a4bd-66980687668e | checkpoint | 3.3.4 - Concrete
6384d33e-c5ec-520e-8828-07cb0852eed9 | note | Detail - Concrete shall not be spread by vibrating.
a9799cd5-79db-5951-95cf-c8e9f3518bfb | note | Acceptance / Conformance Criteria - Concrete shall not be spread by vibrating.
58e97f68-2a2c-5c11-9f43-ef507a7f575c | note | Standard / Specification - WSP-DR-STR-0306
185419c2-618c-5142-9ded-ff18cc7abcb1 | note | Verifying Document - Supplier data sheet
1f0d8128-5c51-55cb-81d9-8493d1d16238 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
ecc18b36-b75c-5620-9aab-51cac32b4618 | note | Verification Activity: Activity - W
58f148f6-50d5-560d-a0fc-dc794557385b | note | Verification Activity: By - SE
3f535275-80c4-411d-bb78-06c0dd3cfb65 | checkpoint | 3.3.5 - Corners and Edges
2794251b-f9cc-5fcd-8e0e-db2480eef79c | note | Detail - 20x20 chamfer or fillets
2b17750c-b810-5125-bc69-417ee6da9a8e | note | Acceptance / Conformance Criteria - All corners and edges to concrete surfaces shall have a 20x20 chamfer or fillets.
dbb4a099-3c8b-5b90-a215-0d136b49ea4f | note | Standard / Specification - WSP-DR-STR-0306
9186210e-9af3-5216-9029-3d5b9727b2b1 | note | Verifying Document - Supplier data sheet, Visual inpection
4b906102-cf37-51f1-85a8-654cf7b8c908 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
c3e8bbfd-bfd1-5684-ae66-f2934f07448b | note | Verification Activity: Activity - W
8bd4bdb2-5619-5e04-88b9-f492fc6bde58 | note | Verification Activity: By - SE
012cc681-9fad-49f1-953c-1ba5a79d4ca5 | checkpoint | 3.4.1 - Concrete Mix Design
db435ab3-1a36-500a-9200-3cc9046ee1df | note | Detail - 17.5 MPA Concrete
9cc91a38-0d2a-5a1d-9ffe-f7474c4a49a4 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 17.5MPA
6d253da8-c9cc-598e-824e-2f4580906b71 | note | Standard / Specification - WSP-DR-STR-0006
bc69f77f-042c-57d0-a907-51ed70eb5c52 | note | Verifying Document - Delivery dockets and supplier data sheet
b4144b06-a121-54d8-a25a-3bf211204830 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
a1743cf8-b26b-50c0-8285-e4602be4e03b | note | Verification Activity: Activity - HP
e6d3e4c2-74b0-5fca-a363-decdef707e74 | note | Verification Activity: By - ENG
cbc75664-efc4-441b-b98e-90fa4850299b | signoff | AUTHORITY HOLDPOINT
a0bbfb5f-f3d9-43d1-af83-2a67eca5b111 | checkpoint | 3.5.1 - FH Nails
0205cf51-9a26-583a-9bba-402d98f6cdba | note | Detail - General structural use 75mm x 3.15mm FH nails . All nails shall be flat headed, unless otherwise shown, hot dip galvanised and fully driven
9de9ba5b-ad22-5091-b4fd-34702e52b80f | note | Acceptance / Conformance Criteria - 75mm x 3.15mm FH Nails
8cf052c6-0856-5a41-83ae-1621f84bf1e8 | note | Standard / Specification - PS 18.6.3 (d) i
da8560f6-172c-50dd-abf7-22b6c5b4ad07 | note | Verifying Document - Delivery dockets and supplier data sheet
166777ff-0407-5868-ae47-fc8d27208332 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
e05cf486-d1be-5ff4-a47f-1c459f9ef1a0 | note | Verification Activity: Activity - W
a661775e-cf55-5665-8fa7-c6d8f1ee29b8 | note | Verification Activity: By - SE
bfc8d9fb-1b6e-41ac-8ea4-74819f301001 | checkpoint | 3.5.2 - Bolts
e9b7a763-29d0-5b66-b65f-a3da4ddc89e0 | note | Detail - Bolts shall be M12 hot dip galvanised engineers bolts fitted with 50x50x5 galvanised square washers both ends. Washers for coach screws shall be provided in accordance with NZS 3604
7715dee4-0f1d-5307-aed0-32cb65afe6f4 | note | Acceptance / Conformance Criteria - M12 hot dipped, 50x50x5 galvanised square washers
88b61790-e651-51e0-bc0a-84d165e8a411 | note | Standard / Specification - PS 18.6.3 (d) iii
05d2b9de-6ae6-5031-8a88-a9281c28052f | note | Verifying Document - Delivery dockets and supplier data sheet
0488bbd7-bcdc-54b8-a3ab-1a1dc7eb7b44 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
bd45e861-9ed6-5daa-8e7b-622d8bb50dc5 | note | Verification Activity: Activity - W
0c50c021-86e9-5d82-836e-5d3b09657afe | note | Verification Activity: By - SE
ebdfb3ef-b90c-467e-bb36-3effef433822 | checkpoint | 3.5.3 - Bolts within 100mm of ground
2aace6e3-140e-5ce0-ae21-01451c986fa8 | note | Detail - Bolts within 100mm of ground to be stainless steel.
3c8d5359-17df-5377-ae38-b56da07f3443 | note | Acceptance / Conformance Criteria - Stainless steel bolts
937bc58b-80a2-531f-817c-df9a1e2ce6be | note | Standard / Specification - PS 18.6.3 (d) v
c840a0b9-5af3-5f39-b295-811e50ddf33e | note | Verifying Document - Delivery dockets and supplier data sheet
d592613d-eb05-54b0-a38b-ca313b89683c | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
f7fe5e7d-dbed-5347-a23a-c0cc77d9b57c | note | Verification Activity: Activity - W
3e858371-94f9-537d-a526-e754f1f93d0b | note | Verification Activity: By - SE
899ca642-06f8-46bd-87e2-019b3a2af040 | checkpoint | 3.5.4 - Coach screws
b57ccd0a-cf20-5a09-bc0b-7755763d656d | note | Detail - All screws shall be hot dip galvanised and screw fixings shall be pre-bored.
aee7e2b8-a94d-5ce2-bfcf-69f4e63f4a62 | note | Acceptance / Conformance Criteria - Hot dip galvanised
307763eb-49da-5354-8f97-a364643ad0bd | note | Standard / Specification - PS 18.6.3 (d) vi
f2e7e2cb-0341-55ed-bc99-29e76aa90dc6 | note | Verifying Document - Delivery dockets and supplier data sheet
d2f44108-f364-5b1f-9f1b-2d7044ad981e | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
87df8ee5-cedc-5bae-a86e-218803d00687 | note | Verification Activity: Activity - W
a57676c1-8123-556a-a868-d56cb0a39999 | note | Verification Activity: By - SE
54b4d6c0-6731-4860-b831-0984df344189 | section | SECTION 4 – Construction ACTIVITY
47bb9bf9-fca9-49a6-aee8-02fd7cb28366 | checkpoint | 4.1.1 - Removal of existing timber fences & chainlink fences
bb52213e-3de8-540c-8ff4-f75adece7437 | note | Detail - Removal of existing timber fences & chainlink fences
40bfb92b-f9e0-573e-ade1-dfcad8673b34 | note | Acceptance / Conformance Criteria - Removal of existing timber fences & chainlink fences
0dc8c5e7-9552-514a-85c0-2a599651cccc | note | Standard / Specification -
3e543e96-0af8-5dd6-8c33-b4656723b9ff | note | Verifying Document - Visual inspection/photos
e7b0a30d-ad32-5752-961d-07c1126eff68 | note | Testing Quantity Required (based from schedule qtys) - After Construction of each Area
f81441c3-515a-5d44-ab0d-78a76b972a63 | note | Verification Activity: Activity - I
42c283ad-a048-5024-b320-ccf687fd9d33 | note | Verification Activity: By - SE
7edad62c-901e-4ad7-a600-ff73376f91e1 | checkpoint | 4.1.2 - Ecology and Environmental Manager Approval
2931d585-1609-5cec-8453-239d56a98f40 | note | Detail - Ecology and Environmental Manager to approve the removal of existing vegetation prior to site clearance.
a490e484-9e2d-547a-b694-893f2bdbebda | note | Acceptance / Conformance Criteria - Ecology & Environmental Manager's Approval
b6e4f32b-2e97-51d1-b035-5f0feaf2aa0d | note | Standard / Specification - PS 27.3.5
0e5ba300-f411-5a9a-a930-c72aacf9fd48 | note | Verifying Document - Visual inspection/photos
a69f3914-9d97-5b41-82b8-37e0970c4a55 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
7a19853f-34b1-5f09-92ce-68c092046d6e | note | Verification Activity: Activity - W
ce56c775-c0fc-5f81-925f-7967121a554f | note | Verification Activity: By - ENG
c2f15ace-2712-4a78-92f3-08dae9119515 | checkpoint | 4.1.3 - Clearing and Disposal of Existing Vegetation
6603c803-ce52-5dd2-ac5c-ec78cdbeea0f | note | Detail - The clearing and disposal of existing vegetation, removal and disposal of existing hardstand surfaces, inorganic debris, site preparation spraying, pruning and minor landscape earthworks, and topsoil re-spreading shall fully comply with Section C of NZTA P39:2013.
213f6146-0e7d-5675-a478-f553c65d7c47 | note | Acceptance / Conformance Criteria - NZTA P39:2013
67f31278-c71b-5c3c-a390-184132729795 | note | Standard / Specification - PS 27.3.5 (a)
0dc6407a-5040-5c56-939c-9d7aa31c500d | note | Verifying Document - Visual inspection/photos
fc786797-a6d8-5dc0-a844-0a0bc7b47ba9 | note | Testing Quantity Required (based from schedule qtys) - After Construction
c685a21e-c648-5420-9651-a854a57d3069 | note | Verification Activity: Activity - I
6055fe0c-6337-5d15-9f71-09a969fda3d0 | note | Verification Activity: By - SE
a166d665-7a97-4eee-a2f6-41c087db9a58 | checkpoint | 4.1.4 - Existing Vegetation Mulch
fcffecd2-6956-5692-b5e4-7387a661a169 | note | Detail - Where possible, existing vegetation, excluding pest plant material, that is removed via site clearance shall be converted to mulch and, if required, stockpiled in an appropriate location.
83596a0e-6d2e-56d8-913d-6ccbbe60430b | note | Acceptance / Conformance Criteria - Existing vegetation converted to mulch and stockpiled if required.
64257802-104c-5265-b431-8d7f03aef9ff | note | Standard / Specification - PS 27.3.5 (b)
fdc6cf8e-eeb6-5d7d-91fb-519ca642a5c7 | note | Verifying Document - Visual inspection/photos
1d0cddf8-6433-51e2-bb48-76652cdf6b61 | note | Testing Quantity Required (based from schedule qtys) - After Construction
40ee05c3-1145-528f-be59-8dec3df141d2 | note | Verification Activity: Activity - I
d8e19cce-bfa7-5243-8c30-0d1ea2e87ba1 | note | Verification Activity: By - SE
a88bab40-57c3-427d-bf56-8ed737cd6248 | checkpoint | 4.2.1 - Setting out of Noise wall Posts
fb927d3a-0a1f-53be-afc5-414578decb28 | note | Detail - Setting out to follow design coordinates and levels within tolerance as specified in PS 18.5.7 section (e).
6d1a5d14-0904-5043-bc55-970b69499b68 | note | Acceptance / Conformance Criteria - Engineers Approval
018bb785-6246-58ee-bc35-286201e96873 | note | Standard / Specification - PS 18.6.1
1c0185cb-5a99-54b2-a246-e40ee3cfb430 | note | Verifying Document - Survey records
fc03cd6a-6f77-58d5-8586-29a03aea5886 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
7798b364-44d5-5ba1-b329-674e8c3ac816 | note | Verification Activity: Activity - W
b2b018c9-92e3-5b63-912f-d7076695874f | note | Verification Activity: By - ENG
4e09de53-6685-47f6-aad8-a52176c863c5 | checkpoint | 4.2.2 - Geo Technical investigation on each post holes
37f74bf4-5639-5eed-a032-3a2dd156064b | note | Detail - Holes are to be 400mm dia and 2.8m deep
b4c346a3-2daa-5813-8508-3e56114ece7e | note | ○ Shear vane testing at the base of holes to be completed to a strength of 60kp
bde5f4d4-041d-512d-9e9b-32afae797088 | note | Acceptance / Conformance Criteria - Shear vane strength of 60kpa
0ccecb7e-7baf-521f-960c-feb8208a6c5e | note | Standard / Specification - PS 18.6.2, WSP-DR-STR-(0212-0219)
dd83c48d-61b8-5312-a5ac-9c5a66cb9164 | note | Verifying Document - Shear vane test report
a91a15c4-95dd-5028-a702-7e33d23cc75d | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
e69fc9b6-1276-5532-b7ed-5aa69cb0d59e | note | Verification Activity: Activity - HP
c41e4760-0e20-5ae7-8e3a-fd57f719f9fb | note | Verification Activity: By - ENG
48ddd762-c8cc-4dec-b7a2-9a070aa16867 | signoff | AUTHORITY HOLDPOINT
b4106595-673a-4506-9da9-d8168d461980 | checkpoint | 4.2.3 - Noise wall footing concrete
dca7db32-773e-56fa-8425-ba3db1f5bbb6 | note | Detail - 17.5 MPA Concrete
215cb9a5-ac7f-5f7a-a274-68bb844baaf0 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 17.5MPA
a257366a-e3c4-58ad-82e1-0d899bc29df8 | note | Standard / Specification - WSP-DR-STR-0006
3b85fa93-fd1f-5a79-882a-114711449b55 | note | Verifying Document - Concrete Delivery Docket, Concrete inspection checklist
4a8f0ef8-06eb-521d-be5f-9438948c0a8a | note | Testing Quantity Required (based from schedule qtys) - After Construction
9c400b11-fd8d-5b7b-9f39-7952f7140ec0 | note | Verification Activity: Activity - I
2ae33883-0062-586d-bb26-e2ba38ab7b04 | note | Verification Activity: By - SE
4af6b83e-445f-49e4-907d-8f90e7306c55 | checkpoint | 4.2.4 - Installing Wooden Railings
b54390e4-26e4-5233-a184-29a934efb0b2 | note | Detail - with sufficient embeddment of nails and connecting details as per drawings - WSP-DR-STR-0006
a34b38c9-a95c-5934-9c75-df3cf6a9e963 | note | Acceptance / Conformance Criteria - Skew nails shall be installed as shown.
ab4ea8f1-0164-56fd-af94-34f87a32bdf1 | note | Standard / Specification - WSP-DR-STR-0006
613459f2-9980-51a7-b3ca-9b11fdc2eb99 | note | Verifying Document - Noise wall Checksheet
ba1e19c2-36c5-5ecd-bed1-347467948cc2 | note | Testing Quantity Required (based from schedule qtys) - After Construction
7ba2a32c-a125-5c76-a52e-92db0cff4a43 | note | Verification Activity: Activity - I
a83db245-9f11-5463-8f4b-a1cd56e17d89 | note | Verification Activity: By - SE
01308910-c8ad-4f3d-91cb-dea29d333bef | section | SECTION 5 – POST Construction ( HANDOVER)
c37d9763-93e6-4bea-9ba7-595422971148 | checkpoint | 5.1 - As-builts
5b3aa14b-b5ad-5451-868a-b37cd20686f6 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
dc9c940b-46ed-5ae0-9b2f-6ab45e67ee28 | note | Acceptance / Conformance Criteria - All changes to design need to be captured on the noise wall drawing set
a2a521cf-c9ce-5f86-9d12-ca05f12dc46b | note | Standard / Specification - PS 12.2.2
3c71e236-87ce-58a1-875e-f6556fe93f31 | note | Verifying Document - Redpen Markup
11fdcec9-ac64-5f08-a10d-26311ef5bd2c | note | Testing Quantity Required (based from schedule qtys) - During Construction and After finishing
da0623ea-e959-532e-aa8a-240b2a7740aa | note | Verification Activity: Activity - H
ce290dae-7337-5c98-a2dd-8cfeb5ba07c4 | note | Verification Activity: By - SE
039f1735-c4ea-4cd1-9874-40f294b3ffb2 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
7db72920-6837-555b-9726-ca0bb69c316b | textbox | Contractor's Rep Name:
bb3e4149-3d0d-5407-badd-accaf0f8e773 | textbox | Engineer's Rep. Name:
2d462ac8-37a9-568d-b368-e3fa53b22635 | date | Date:
683aa53b-cd47-40ac-8843-cb2da339148a | signoff | Add Signature
7731ea66-0c68-4e94-8c5c-330156920396 | checklist | DN1210-SP2-010-002-001 ITP Retaining wall 04 Base slab + Toe + Kicker Rev 1 | itp | DN1210-SP2-010-002-001 ITP Retaining wall 04 Base slab + Toe + Kicker
bee04adb-250f-4136-9859-69c8d06c7536 | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL , PERSONNEL & THIRD PARTY APPROVALS (P&G / ESTABLISHMENT)
5786c555-ee92-48e2-9e4b-7fb470f274b7 | checkpoint | 3.1 - Methodology
6313d874-390b-54cb-89e4-b622c366a2b0 | note | Detail / Activity - Method statement
0a2880fc-55a9-5cda-8925-305383644948 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
35e09c4a-cd9a-5ff4-aa87-80e6a026a8d2 | note | Standard / Specification - PS- 22.3 Appendix V
ebf16885-bae6-5e16-85bb-7f45b0b43e4b | note | Verifying Document - RW-04 Permanentworks Construction Work Pack Sign off
610c8dd6-2ff7-5c6f-b1ef-def374d668c9 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
eb611a08-cf1f-5527-9a58-6a459e8bd9dc | note | Verification Activity: Activity - HP
8c2a7740-6992-514c-8c79-435d06d72b1c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6016f3b5-9980-5560-b18d-8809388063ad | note | Verification Activity: By - ENG
01351ab4-cbea-46b6-9749-8f3ea890159f | signoff | AUTHORITY HOLDPOINT
7427754c-0a71-43b1-a05c-8fb11e932859 | checkpoint | 3.2 - Reinforcement Modelling
59e03152-4705-5dd4-afc9-af0278100c7e | note | Detail / Activity - 3D modelling completed, bar bending schedule checked against latest construction drawings and submitted to the Engineeer for review
e36eb4f7-c72d-5f6f-950c-6dcc89d3e26d | note | Acceptance / Conformance Criteria - Downer
dbe53a43-928d-5be8-bde9-274bd97cb99b | note | Standard / Specification - Reinforcment shop drawings
88d6a5fa-a835-5bff-8d74-90d3025cf1be | note | Verifying Document - Each batch of reinforcement
d99b2168-cbf0-5ec1-be8b-5b47a06f172d | note | Testing Quantity Required (based from schedule qtys) -
5c547da0-da0a-50d6-a85d-c53d44ca7524 | note | Verification Activity: Activity - HP
5e4a5a12-0d5f-52fb-a9ba-12c3195d7c81 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
9f710d5f-6238-53c2-bd19-fa77a4911426 | note | Verification Activity: By - ENG
8158b081-25cf-40e4-928b-b237d5755261 | signoff | AUTHORITY HOLDPOINT
696ff3e7-b250-4c68-84ea-b36f5a2595a5 | checkpoint | 3.3 - Steel Supply, Delivery and Storage
9829e2fd-8abb-53b4-a67a-b3f26348bcf0 | note | Detail / Activity - Mill & test certificates for each batch of reinforcement used to be provided to the Engineer.
1bf8bd32-d34b-5105-9720-729b4b3040dc | note | Acceptance / Conformance Criteria - Design Drawings
e1e7a764-bf6a-52a3-8da4-554472470c5d | note | Standard / Specification - AS/NZS 4671, PS 19.13
0ef5eff4-bde0-50f2-811e-9fff24a1b643 | note | Verifying Document - Delivery Dockets / Mill Certs
0269273e-2ce7-5245-b0b0-9bb339732182 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d1dfdfcc-72c0-55fc-a59b-ccd457385e55 | note | Verification Activity: Activity - H
944ce55f-e93e-5140-8383-a4ee13e42f3a | note | Hold Point (Internal)
d62d4c50-2915-55c8-91de-66da0fb61b67 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
f5e2f709-666a-50a2-bef8-9de00c6da1c9 | note | Verification Activity: By - PE/SE
964b49e8-ae3c-4e02-8670-18e1f4bdf10c | checkpoint | 3.4 - Concrete Mix Design
0618af34-5925-5f01-a6a8-3c8c4a875136 | note | Detail / Activity - Concrete mix design to be completed and reviewed by the contractor prior to use on site. The following criteria are to be satisfied:
f46e426b-4e34-52c8-9c2f-4fbfe8584387 | note | ○ Strength: 50MPa
b0fcef64-c2bc-5d90-906e-c3906b41fb69 | note | ○ Normal maximum aggregate size: 19mm
aaf2de51-511c-5217-b2a7-36be1942afbf | note | ○ Concrete materials and manufacturing are to comply with NZS3109
1d080d6e-fc81-559d-aefa-329eca9edc6e | note | ○ Aggregate Used And Overall Mix Design (Including Additives) Shall
db03471f-15df-51ac-af01-2ac1c80a7ee2 | note | — Meet The Provisions Of 'Tr3 Alkali Silica Reaction 2003 (Ccatnz)'.
7affd04b-a2fb-53b1-83ce-f218b53c29f3 | note | Acceptance / Conformance Criteria - NZS 3104 Design Drawings
4779e655-ae48-5992-ad97-63fd09a7a233 | note | Standard / Specification - PS 19.3.3
3c2df8e4-cb6d-5723-9242-42b83af504ec | note | Verifying Document - Concrete Mix Design
d43846c9-bcf4-56d2-a73b-c573053ad8b9 | note | Testing Quantity Required (based from schedule qtys) - All Mix Designs
c619343d-4e1e-5fab-aafc-c4f168a309cd | note | Verification Activity: Activity - HP
e0156d90-eb9f-5127-b810-8f1c47b6bac5 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
acec63cc-d955-5563-af86-91cfa3920a3f | note | Verification Activity: By - ENG
0c61ba82-6cca-49b8-acc8-931b883bf62c | signoff | AUTHORITY HOLDPOINT
6d318401-5020-403f-b1c2-a7f4878da4b8 | checkpoint | 3.5 - Subsoil Drainage
bf3a428c-deb5-5361-bf05-05dd001de5d5 | note | Detail / Activity - Shall be 110mm diameter NZTA F/2 compliant smooth bore perforated pipe with filter sock
10f5d51c-d6c0-5365-bc89-dbff40a16879 | note | Acceptance / Conformance Criteria - Engineers Approval
19f108d8-0eb1-5641-9165-523b8b22ac9c | note | Standard / Specification - PS 21.5.17
d32ac2a7-d26a-5041-b153-1bb8987e57b8 | note | Verifying Document - Material certificate/NTC
57007a5d-1dca-5c6c-8f8d-75299325b8ef | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
4aefe6cd-c6eb-5444-b10a-585370635c42 | note | Verification Activity: Activity - HP
063b0281-332f-5c2b-b5c1-0b447491d180 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ca7b1bc5-6f32-5d61-a555-e9648bb82e51 | note | Verification Activity: By - ENG
3272f22a-f9bb-45ab-a04d-088d9e01274e | signoff | AUTHORITY HOLDPOINT
3420ee60-276b-4e25-b188-7ccfd72a6035 | checkpoint | 3.6 - Granular Material (Imported Pumice Sand, GAP65/AP65)
64815ed5-530d-5cc0-9515-c9590f69b98f | note | Detail / Activity - Confirm Specification and material in good condition.
908e4689-e302-5fcb-a909-f4b761ab283a | note | ○ NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
7b651ef2-01c9-558b-b7bb-0b3d8af6ea6c | note | ○ NZS4407:2015, Test 3.8.1 - Particle Size Distribution
e84c984d-0fb2-55ea-bf19-7f13c29d91a9 | note | ○ NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
67cb47df-0eda-5485-8b51-cc5914171b10 | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
a27fabb4-ecd1-5afc-befc-86b729936068 | note | Standard / Specification - PS 22.4.1
c6393749-0d51-5468-ba9e-a389609fa9c8 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
7a3eea93-3670-5047-9b92-c819c71bb6cf | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
9a6d663d-274e-5f25-80be-ee6b8894deb2 | note | Verification Activity: Activity - HP
e544e5f5-146e-5571-909d-510539d26fd0 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7e6421ec-e016-58db-b6cb-7c40205fd51d | note | Verification Activity: By - ENG
980a43b4-b75c-4ddc-b5e9-cd1f3c029185 | signoff | AUTHORITY HOLDPOINT
ae0c0cfd-f116-4f66-93c3-59f55d974c33 | section | SECTION 4 – CONSTRUCTION ACTIVITY - CONCRETE BASE- Excavation and Subgrade Preparation
567caea6-0e2a-4526-a721-97854287a872 | checkpoint | 4.1 - Cut Subgrade - Inspection
f803b38f-a5fc-5b91-b0c6-c2919acfd93d | note | Detail / Activity - Engineer to inspect all foundation surface inspections
1d10e074-ee5f-5c17-a99f-02671c47820e | note | Acceptance / Conformance Criteria - Engineers Approval
906dff23-6d1d-596b-925d-db8d88cb3b88 | note | Standard / Specification - Appendix V
1a7b191a-6855-58f8-a4a0-a51ba09f55eb | note | Verifying Document - Visual Observation
83c1e30c-8e2a-5ef0-85d1-7e5aa8ace7b7 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
f25c8c7c-fc3d-58e4-a602-42525dba941e | note | Verification Activity: Activity - HP
1560969e-1dca-5a28-b2af-16ae748b18d2 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a3860406-f67b-5f13-b6b1-4b114ee8979e | note | Verification Activity: By - ENG
72020980-9594-4b96-b14c-bcec2857135e | signoff | AUTHORITY HOLDPOINT
77c2f167-06ad-4d43-a6e2-9c82aad5a411 | checkpoint | 4.2 - Cut Subgrade Testing - Cohesive Soil - Shear Vane
82d07795-5a83-5f1e-a798-8a4d9773a973 | note | Detail / Activity - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
f252c709-7e95-5cf2-870f-bccde5c3b6c6 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
8594f9f4-e1fe-5bb1-9f99-a569793ecd0b | note | Acceptance / Conformance Criteria - Average Minimum SU:
71c80ad6-2921-578f-8174-7a2a3c039917 | note | ○ > 60kPa
99bf04a5-d6d1-52da-a0f9-df8249bb2d44 | note | Single Test Min SU:
d7a46ab6-adff-5803-afb6-42d117315522 | note | ○ >50kPa
f9d29e28-9cd8-5244-97b3-1b490d44c40f | note | ○ 2-3m deep
3c310abb-b9cf-5230-a3b6-f67feb3f51c6 | note | Standard / Specification - Appendix XVIII
b0da6c49-20f5-5932-952a-ebe6c608118c | note | Verifying Document - Shear Vane Report
a2cce4a1-7748-56fd-af52-19e94664ec49 | note | Testing Quantity Required (based from schedule qtys) - 0.5m interval, 4 test per 400M2
3ce5eb47-6506-5a1d-86ef-9f7ea3a288a4 | note | Verification Activity: Activity - M
2333916e-8865-53b1-a8fb-d3a8d0d35305 | note | Verification Activity: By - SE
55b21578-3f67-418d-8378-de981d5d4468 | checkpoint | 4.3 - Cut Subgrade Testing - Non-Cohesive Soil - Scala Penetrometer
4ea72902-50c6-58d3-91a8-d55cabad2c24 | note | Detail / Activity - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
219ce936-53d4-5e22-afa9-c1eba43fa582 | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
4efbb684-e803-527c-9ebe-72bb4dc0aff8 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
7c1418a5-9476-512d-a7a8-e303c7614d26 | note | Standard / Specification - Appendix XVIII
f6be0e38-2adb-5182-adc8-8d51a2fccd7a | note | Verifying Document - Scala Report
6d5308dc-df3c-5dd3-b338-f2ae871804a1 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
800bbe95-52e6-5f1a-908d-4f5d4bb282be | note | Verification Activity: Activity - M
0068c550-b7fa-5b3d-9755-edd6720aacd8 | note | Verification Activity: By - SE
f79b9e86-7513-47b0-81ad-08843f06ab31 | checkpoint | 4.4 - Cut Subgrade - Import Structural fill - Release of Hold Point
802dc3c2-14cc-5391-955c-c5e460228c76 | note | Detail / Activity - To release the subgrade hold point in-order to start placing the Blinding Contractor shall provide written certification that all inspected and tested subgrade complies with the requirements in PS 16.6
60c015eb-7afd-501a-af52-74bf74714022 | note | Acceptance / Conformance Criteria - Engineers Approval
c81ceac5-38d2-56d5-ac3a-684f2c7e85d1 | note | Standard / Specification - PS 16.9.3
9894ae39-0d5f-54e0-84f0-8568735e2a14 | note | Verifying Document - CONQA Approval
17dc423e-6c70-5fc9-ac8b-530859de3ddf | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
22ce154e-9636-526b-a010-d5cb40fc2887 | note | Verification Activity: Activity - HP
2c0ad7eb-46ab-5f3f-aef6-e6531bac8892 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b9fc6e0d-4076-5602-af38-2a2cf897e2e2 | note | Verification Activity: By - ENG
c4d0362a-07d1-4499-8d25-402a0c3a4039 | signoff | AUTHORITY HOLDPOINT
1310215e-2434-4438-8ea4-2fa82d69a36f | section | SECTION 5 – CONSTRUCTION ACTIVITY - CONCRETE BASE + TOE + KICKER-CHAMFER - Steelworks
ce8813a5-a80e-470c-a21d-7ca0a1f39a68 | checkpoint | 5.1 - STEEL - Reinforcing Ties
60b0bb2a-cab3-5870-9900-1dd8b473f553 | note | Detail / Activity - Tie bar diameter, grade, and length match shop drawings and bending schedule
275a191d-a46b-57e9-9036-d10593af1a0e | note | ○ Spaced correctly as per design (e.g., 200mm c/c), full enclosure of longitudinal bars
7f9e24da-20dd-56ce-8e0a-ff3750397a9c | note | Acceptance / Conformance Criteria - As per Drawing
f56c4e9e-2e5b-599e-8b66-b9aaa569b307 | note | Standard / Specification - NZS 3109, PS 19.13
c8fb00fe-bb78-51ae-bc9d-01ba938e9ecd | note | Verifying Document - Delivery Dockets, Checksheet
fd38da35-13df-52cd-8ef3-d7fa66501373 | note | Testing Quantity Required (based from schedule qtys) - During constuction
7d505b03-6cc3-57a7-a078-cb4d692e8ac8 | note | Verification Activity: Activity - H
3f09f5fc-79b3-5341-a21b-847e6bf74981 | note | Hold Point (Internal)
9e2e1058-63dc-5244-8499-4eb9ee6d1226 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
c51094a0-2085-56c1-80f5-69236eac63fb | note | Verification Activity: By - PE/SE
0844fc27-ef1f-4bcf-a37f-d7fe7860953f | checkpoint | 5.2 - STEEL - Onsite Cutting & bending
3af117d3-ee46-5075-997b-5134724a5238 | note | Detail / Activity - Complies with bending schedule & radius limits
bf9ad1cf-6535-57d5-bc5b-8b43d50583b4 | note | Acceptance / Conformance Criteria - As per Drawing
1034c993-695a-5005-a877-25a46bb4e5bf | note | Standard / Specification - NZS 3109, PS 19.14
0342950b-7f9c-5236-ba54-8f6a33bf5842 | note | Verifying Document - Visual Inspection
0dcaac62-d4db-590b-beb7-a2400998043d | note | Testing Quantity Required (based from schedule qtys) - During constuction
13ca86e0-20df-5ba4-ae5e-820aeb3b1cbd | note | Verification Activity: Activity - H
e9828c3f-d514-559e-9a32-955485b4ad9e | note | Hold Point (Internal)
9d2db94c-da1f-5574-adc1-fa6e9368dbb0 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
52b010b6-a380-58c3-936e-f51b6a161446 | note | Verification Activity: By - PE/SE
17d151ed-70b2-45a4-82ea-ed34f78d4371 | checkpoint | 5.3 - STEEL - Reinforcing Bars (lapping/starter bars/dowels)
25b30ce9-3f78-5993-8ae0-c0c8ed757492 | note | Detail / Activity - Correct bar size, spacing, cover, lapping as per shop drawings
166d5c2e-9198-51a2-8c6a-e8b6bb8bdffa | note | ○ Min. lap length, staggered laps as per design
9f069c7b-887a-5a07-95a0-5218aaee337c | note | ○ Location, projection & alignment must match prior pour
67232a19-9293-5b8f-89ca-2b763af26732 | note | Acceptance / Conformance Criteria - As per Drawing
d862532a-8759-53b9-aea8-9a6d81aaf68c | note | Standard / Specification - NZS 3109, NZS 3604, PS 19.13
5be6f915-3457-5327-9720-4ffe181af9ca | note | Verifying Document - Delivery Dockets, Checksheet
ba6cad5b-ba96-52cf-99f1-09afad7afde9 | note | Testing Quantity Required (based from schedule qtys) - During construction
4b220336-044f-515e-9a90-a58ef54c4dfc | note | Verification Activity: Activity - H
9cb3d782-967b-5b61-a238-72063d71b9e9 | note | Hold Point (Internal)
af9d6f1c-2f07-5514-985f-63830f02d5c7 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
6930b329-5731-5de1-9f6b-d79011de0a84 | note | Verification Activity: By - PE/SE
ae740519-b615-4d16-8e59-e04b6ba25312 | section | SECTION 6 – CONSTRUCTION ACTIVITY - CONCRETE BASE + TOE + KICKER-CHAMFER - Concreteworks
35379f9a-6a73-4e06-a9d7-3e95e431d750 | checkpoint | 6.1 - CONCRETE - Unfavourable Conditions - Cold Weather
3dcc9fb6-bb38-5999-954e-222cfd321960 | note | Detail / Activity - Concrete shall not be placed in conditions where temperature is below 5°C with temperature decreasing or below 2°C with temperature increasing.
6267750c-8f05-5e5f-aa04-f000877f167c | note | Acceptance / Conformance Criteria - Prepour Checklist
88f1e2e7-9c79-5af8-ab17-2dbe85a8f401 | note | Standard / Specification - NZS3901:1997 Cl 7.2
4efc83fd-14f6-5566-aaa5-cc50d5679936 | note | Verifying Document - Pre Pour
3d936726-11ea-5d8b-8f8e-a52b45336245 | note | Testing Quantity Required (based from schedule qtys) - During construction
22fda16a-fe75-5b81-9ae9-35b8c17b9d39 | note | Verification Activity: Activity - M
c41aac92-e585-5cbd-ba6e-717d7c0738b3 | note | Verification Activity: By - SE
4586d7f4-5733-42b1-acc6-990886154caf | checkpoint | 6.2 - CONCRETE - Unfavourable Conditions - Hot Weather
51460153-96f8-50b3-9aa1-e8c29d20ffbb | note | Detail / Activity - Concrete shall not be placed in excessively hot dry conditions. Concrete temperature should not be higher than 30°C
4fa7d6da-433e-59f9-9f29-3f7950fe8d4d | note | Acceptance / Conformance Criteria - Prepour Checklist
bb6146e2-b074-500f-91ba-d93325595949 | note | Standard / Specification - NZS3901:1997 Cl. 7.2.1 & Cl. 7.2.2
bd7f93ba-7b3d-543d-adbc-45c54afbde7c | note | Verifying Document - Pre Pour
3314e0cd-2fd7-5b88-89cd-d693c7a8fca4 | note | Testing Quantity Required (based from schedule qtys) - During construction
a180c542-9fa7-532c-8829-7364283b4020 | note | Verification Activity: Activity - M
35fe0e6b-f729-562b-aff7-8419893a78c2 | note | Verification Activity: By - SE
3a973a61-db5b-42ff-bddd-0d85ac69657d | checkpoint | 6.3 - CONCRETE - Unfavourable Conditions - Rain
1e2755b4-be16-5f4a-b478-ce09336979e0 | note | Detail / Activity - Concrete shall not be commenced when heavy rains is falling or threathening and if rain commences during a pour, the work shall be protected as directed to prevent damage to the concrete or to any newly finished surfaces until the concrete has set to such a stage as to withstand leaching of the cement.
17319838-71fc-506e-beb3-bc166ca52a79 | note | Acceptance / Conformance Criteria - Prepour Checklist
a70fc893-972c-511f-bdb7-00b317624343 | note | Standard / Specification - NZS3901:1997 Cl. 7.1
5c980805-b9a9-5b98-b74e-c08e1ac638d1 | note | Verifying Document - Pre / During Pour
b66f8dab-eb0c-5185-9b41-ddb270dc08db | note | Testing Quantity Required (based from schedule qtys) - During construction
cd0e8a2b-6e8e-57f1-abb4-c0a0b4b9309c | note | Verification Activity: Activity - M
9701e78f-fbb0-5348-a21e-1c620f3ecaeb | note | Verification Activity: By - SE
378804d4-5ff1-42ad-baf8-9e1deda673b0 | checkpoint | 6.4 - CONCRETE - Spacer Blocks
026f0693-5bcd-5202-b1d7-ef051109e817 | note | Detail / Activity - Correct type, spacing, and fixity
58f70b64-039f-58ac-b46b-b74fe97a2cd5 | note | ○ Shall be concrete spacer blocks made from concrete containing 8% Microsilica 10MPa
8b06016d-26ef-5e42-a342-13d590c8c5c0 | note | Acceptance / Conformance Criteria - Prepour Checklist
540f050f-9d8b-55d1-be6f-3a289f162e75 | note | Standard / Specification - NZS 3109
17089f37-5bef-5c4f-81d1-2720714bdfdd | note | Verifying Document - Delivery Dockets, Checksheet
02caf45d-6dc0-584b-b76a-97efea778024 | note | Testing Quantity Required (based from schedule qtys) - During construction
70dfe636-035a-5ad8-b94f-79556c699a25 | note | Verification Activity: Activity - M
f8c98eec-9a3b-51de-8db1-57fefb79f3cd | note | Verification Activity: By - SE
ac1bfc5d-972b-4cd7-b22d-314af089924f | checkpoint | 6.5 - CONCRETE - Construction Joints
348bd945-5f37-5f8b-9fa7-68124ef047ef | note | Detail / Activity - Where a concrete surface is to act as a construction joint to receive infill over or adjacent, the contact surface interface shall be prepared to the Engineer’s satisfaction to be clean, free of laitance, and with a peak to trough roughness of not less than 5mm to ensure compliance with Type B construction joints as defined by NZS3109 Section 5.6.
5a4e5041-0ecb-52c1-8629-4964c8c00a25 | note | Acceptance / Conformance Criteria - Prepour Checklist
7207c59c-44eb-5fb0-8164-22bbb88c2425 | note | ○ As per Drawing
461d63b6-118d-5636-bb8d-7c6d1d961a49 | note | Standard / Specification - NZS3109:1997 Cl 5.6, PS 19.5
81063d48-d04c-51d0-a937-a39e808279af | note | Verifying Document - Photos/Checksheet
aae7c229-f98c-5dfc-9000-28fa5aa03eed | note | Testing Quantity Required (based from schedule qtys) - During construction
dc927bbf-7b4f-5837-9114-9dc4e67bb3fd | note | Verification Activity: Activity - HP
77f0b2f0-0ff0-5b53-8d7d-88d61482df01 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0da9db42-596e-550f-97c6-f77c3b07e30c | note | Verification Activity: By - ENG
1f802938-76d3-47a6-98a4-7ffa623726df | signoff | AUTHORITY HOLDPOINT
e25c3ff1-cce3-41e1-b4c2-442039c24547 | checkpoint | 6.6 - CONCRETE - Delivery Dockets
ccc69540-d2db-514c-a525-eb9c6390076e | note | Detail / Activity - Each batch delivered shall be accompanied by a delivery docket certifying the cement type, maximum aggregate size, specified strength, slump or spread, date, time mixing completed, and time water added at the plant.
a3a96406-a7cd-5d19-9aa7-ce38024577db | note | ○ Delivery dockets and other certified records of concrete quality and quantity shall be kept on site for inspection by the Engineer.
0423c349-4f4d-5681-a9fa-031affc24551 | note | Acceptance / Conformance Criteria - Engineer Inspection
c40fc856-48b6-53c5-a31a-59e635227fcf | note | Standard / Specification - PS 19.4.1
c61d393f-34b5-5989-b53f-9fdb279f9b79 | note | Verifying Document - Dockets, Checksheet
66dd4c58-33a6-514c-bef5-fdd2a1579cd2 | note | Testing Quantity Required (based from schedule qtys) - During construction
ca485f21-f2b3-5b77-b882-8f1390589894 | note | Verification Activity: Activity - M
f93d01d6-2464-5d28-a741-918a5f2dac5f | note | Verification Activity: By - SE
89eeefe4-629b-4a14-8b99-f3b1ed0e48a3 | checkpoint | 6.7 - CONCRETE - Slump Tests
90fb7886-6b18-599f-8d97-b6d855e43038 | note | Detail / Activity - Slump tests or spread tests shall be taken for each delivery of concrete and the results recorded by the Contractor
62518390-6dda-551f-8014-2a445d15c851 | note | — — — — — — —
ecf55236-a7e4-5e7a-877d-4d4723ccc851 | note | Table 9.1 - Tolerances for nominated slump
6fc985fa-20ed-527e-bcef-70b71e1e2386 | note | — — — — — — —
2c29ba6d-e892-5edd-8c4a-26b493b5dfce | note | 60 or less ¦¦ ±20
deac1d83-dc94-5adf-864c-77bded5a4dfa | note | 70 — 110 ¦¦ ±30
ca3413ca-bc19-5cf6-9884-140169746073 | note | Greater than 110 ¦¦ ±40
e4f1e446-1472-5d63-ae1f-0072870db356 | note | — — — — — — —
55a8e323-ec9f-5732-a6c6-48e93885153c | note | Acceptance / Conformance Criteria - Prepour Checklist
30a4e1db-b8a2-52a2-8909-cb9636e68098 | note | Standard / Specification - NZS3109 Table 9.1
e2633a20-609f-5192-9427-871404c832b6 | note | Verifying Document - Photos/Visual Inspection or slumps and on-site records
643e136a-41e0-5d29-8e4d-d6225c639220 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery
108432db-5cdf-5704-9856-4e39f2fbcc42 | note | Verification Activity: Activity - H
e757edac-5335-586a-a508-80ed4442cd6b | note | Hold Point (Internal)
3ee25427-61e4-5cb1-8665-0f0612ac8107 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
0a2d5ed2-d79e-519e-8d22-ad7ffe3a7e14 | note | Verification Activity: By - PE/SE
b8bff546-af60-46dc-bc93-1a0daa5dffe5 | checkpoint | 6.8 - CONCRETE - Time Limits
66c2ef39-34ca-5a79-a564-712503c60927 | note | Detail / Activity - Any addition of water or admixtures to the concrete mix subsequent to leaving the ready mix plant shall be only be undertaken by, or with the approval of, the ready mix plant supplier. Any such addition of water shall be strictly in accordance with clause 9.4.2.1 of NZS3109. All ready-mix concrete supplied shall be poured within 90 minutes of batching.
d2184fdb-f4e6-58f9-8f54-d7ca2f9a6c33 | note | ○ For concrete mixes containing set accelerating admixtures the above times shall be halved.
8ec66dd8-c003-55c6-8e21-ef9b75907dc8 | note | Acceptance / Conformance Criteria - Prepour Checklist
739dba4b-3f50-5ac2-8cdd-2763204882aa | note | Standard / Specification - NZS 3104, NZS3109 Cl 9.4.2.1, PS 19.4.3
0c15b4d9-29c9-5454-8bc1-cf4dd85e8c34 | note | Verifying Document - Dockets, Checksheet
f4364f5a-d0d8-5f8b-933e-9731508e23b5 | note | Testing Quantity Required (based from schedule qtys) - During construction
9c03c8c8-dac7-5502-833d-654ba9307bf4 | note | Verification Activity: Activity - M
8e0a57b8-c997-56de-8ef5-5e2989b9eb03 | note | Verification Activity: By - SE
2bcd3cdd-234e-4b93-b725-db6e3c2c027b | checkpoint | 6.9 - CONCRETE - Compression Testing
e6cfcfd4-7995-5ad8-923f-90448fa30787 | note | Detail / Activity - The Contractor shall have the off-site testing carried out by an approved IANZ-accredited laboratory at his own expense and shall supply copies of IANZ-endorsed test results to the Engineer.
a8d50b8a-b9a5-525f-a12b-175597ae8d6d | note | ○ For pours under 150m³: three standard cylinders shall be made for each 50m³ of concrete placed, or part thereof, for testing of 28-day compressive strength in an approved laboratory
25afa24d-6a92-59c8-b8d9-4735fe64c9c6 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 50 Mpa
63536a3a-e1e6-5aae-80e8-f2e5ac5ede6d | note | Standard / Specification - NZS3109, PS 19.4.2
962ad461-8aaa-5777-a25b-52507b770a7e | note | Verifying Document - Compression Test Result
b0defeea-417c-5c82-9c4c-c229acff880f | note | Testing Quantity Required (based from schedule qtys) - During construction
bd94b333-8152-5611-98c2-b63d531f285a | note | Verification Activity: Activity - H
9a4b4840-5e52-5eb5-be40-708bb76226d6 | note | Hold Point (Internal)
caa455c1-c81c-5013-adb1-2dd80a3e201b | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
55fa33ea-32b7-57b2-ba34-d77c0b868939 | note | Verification Activity: By - PE/SE
180b4bdd-df1f-4289-9093-f4412404fb8c | checkpoint | 6.10 - CONCRETE - Curing
6cf4f757-fd71-58f2-9897-c1408d0ab187 | note | Detail / Activity - After concrete has set sufficiently its exposed surfaces shall be kept continuously wet for a period of at least 7 days. Special attention shall be paid to curing in the early stages.
6df0e573-77f1-5737-b050-5dfb3b42bea8 | note | Acceptance / Conformance Criteria - Acceptance / Repair Details
f9c57b80-5064-5ae7-a885-ed7d0c7fa9b2 | note | Standard / Specification - NZS 3109:1997 Cl 7.1.3, PS 19.8
3dee8843-fd18-549e-94d1-293839da6b65 | note | Verifying Document - Post Concreting/Compression Test Result
ec208516-e12b-57ad-8bb4-28733a311c63 | note | Testing Quantity Required (based from schedule qtys) - During construction
695e6e7f-cd32-5122-b2ce-1c56efaf8646 | note | Verification Activity: Activity - H
388d1d48-8b24-5a73-bab0-8ec939dd729e | note | Hold Point (Internal)
e36f7520-0e74-5b42-b6b8-b617b97411c9 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
effcc52a-88ee-51cf-b46d-b87b42c9e2fa | note | Verification Activity: By - PE/SE
5057f961-cb0b-4f18-b4f4-194a6fbe9969 | checkpoint | 6.11 - CONCRETE - Finishes
4d4a1c89-4601-512e-b6d0-ead7e0b00de5 | note | Detail / Activity - Concrete finishes are to be as specified by NZS3114 & AS/NZS 3661, scheduled as follows:
2e9e10e2-63a9-5db3-a95f-bed39cfc06bd | note | ○ Top surface of Base: U5 Brushed Finish
2d200793-a839-5174-80d2-feff5428fbb3 | note | ○ Type B construction joints to NZS3109
f1f4b9ee-b3d3-5587-b9d9-d709ff8cecf4 | note | Acceptance / Conformance Criteria - Drawings
63e2df5d-1835-5538-ae88-e8e74cfcca76 | note | Standard / Specification - NZS3114, NZS3109
df542afa-ca91-536e-99be-389850736fb0 | note | Verifying Document - Photos/Approva/Repair Details
5e083d91-e05b-5343-b870-0512eb5e9f42 | note | Testing Quantity Required (based from schedule qtys) - Post Concreting
503bee5e-57fa-5498-a580-605ac98eaf4e | note | Verification Activity: Activity - HP
bac51830-d29d-54de-a500-3d692ea132c9 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3bd21e06-f4a8-55db-a8cd-b238b2325b33 | note | Verification Activity: By - ENG
9a01d774-3697-4246-b315-70f11d498956 | signoff | AUTHORITY HOLDPOINT
52193c68-2540-4047-98bb-30977224e4c2 | checkpoint | 6.12 - CONCRETE POSTPOUR - Falsework and Formwork Installation/Removal
ae7974d7-9b0f-56ac-93cc-85d1ef9fa7f7 | note | Detail / Activity - Formwork shall not be removed until the minimum periods set down in Table 5.3 of NZS3109 have elapsed.
8f2b6e76-499b-5fe4-82bc-79e9428ed5ef | note | ○ Design details, construction drawings, and a formwork certificate (PF-T-442) shall be supplied to the Engineer prior to the formwork assembly and at least 14 days prior to concreting of the component, for review
9bfc6f3d-2af4-5a67-8b02-a1c0f58b0553 | note | Acceptance / Conformance Criteria - As per Temporary works Drawings, Engineer Approval
9a0aebdf-a3a1-55a1-bc38-14afd91474c9 | note | Standard / Specification - NZS3109 Table 5.3, PS 19.11.3 Appendix XIX Downer
0a71a563-b050-5608-9f99-20b7c45f3db2 | note | Verifying Document - Approval
ec502d48-1ed2-580d-ba5b-3ae19ca4fa05 | note | Testing Quantity Required (based from schedule qtys) - Before installation and removal of Falsework and Formwork
24bbce08-3865-5475-8fc3-3fe7e0d463e3 | note | Verification Activity: Activity - H
e6dc68cc-a7a1-5e2f-80a1-d67027a7d2a6 | note | Hold Point (Internal)
a8295f37-5d1e-5209-9092-caa30c6554e7 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
1b7f5eb1-8c84-5385-b569-4aded84f0e21 | note | Verification Activity: By - PE/SE
18a8fc61-195d-43ca-9c63-d6406c834def | checkpoint | 6.13 - CONCRETE POSTPOUR - Post Pour Inspection
de956a3e-8226-50b7-b294-d94cd1b6cd90 | note | Detail / Activity - Post pour inspection undertaken by the site engineer and captured in the ConQA web app. Engineer notified of any defects.
d07a0f82-a053-5bfc-bd90-c5bcd1735f90 | note | Acceptance / Conformance Criteria - Downer
ccf51611-dd7d-5766-9ee4-be48558291bf | note | Standard / Specification - Site Photos
46c1e189-8d92-5061-a7bd-b8ba8863afa8 | note | Verifying Document - Each pour
a7b75712-64b9-57ca-975c-d44fd6d73106 | note | Testing Quantity Required (based from schedule qtys) -
be40deb6-4c46-53bc-9ed3-3779082a4c70 | note | Verification Activity: Activity - H
da2086c7-c905-51ef-9d5e-cccb5186e7fa | note | Hold Point (Internal)
d7a8cf1a-990e-5c3f-9ff6-fda5b933cb6a | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
ab7e6138-b5a5-5e55-b6a0-5eff1dc8f7cd | note | Verification Activity: By - PE/SE
7fd0f13b-e959-4c4d-b5ad-fea171b7d813 | checkpoint | 6.14 - CONCRETE POSTPOUR - Repair
4d931868-7b3b-5dd8-8105-a19a52664e6d | note | Detail / Activity - Repair of any minor surface defect or structural defect of concrete shall only be carried out with the Engineer’s acceptance.
702c1a0e-7326-5d31-adfe-295dda345437 | note | ○ All repaired concrete shall have the same strength, durability and surface finish as the parent concrete unless otherwise accepted by the Engineer.
47fc35fe-a975-57c2-a6c9-aee1de2c75fa | note | Acceptance / Conformance Criteria -
0d0a97b4-da64-5796-9bf6-67280362373e | note | Standard / Specification -
6aaae375-0aed-5e36-be69-8d50884ecb22 | note | Verifying Document - Acceptance / Repair Details
fd6d2c8f-c306-5694-b902-3de1f71c5fa4 | note | Testing Quantity Required (based from schedule qtys) - Prior to Each Repair
b2356c3e-1466-5010-8a9f-5759c2eb2251 | note | Verification Activity: Activity - HP
be71f0ba-6a4c-53f8-9b64-ddfd1da9315a | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4e67562d-e477-5c2c-930f-29c390f43420 | note | Verification Activity: By - ENG
ad890860-d1e2-4222-b0b9-873b23323c85 | signoff | AUTHORITY HOLDPOINT
ccba63d1-fd0d-467b-9284-fa159051baea | section | SECTION 7 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
1470fa75-f504-4a96-8c02-53ed5cc4719c | checkpoint | 7.1 - Survey As-Builts
1c710f0b-9a2f-580e-ae23-39108f72d16f | note | Detail / Activity - Quality Check on Nee pipeline and structure based on the tolerances in RITS
af7a3dcb-1ec7-51b4-8e55-04c13695ea39 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
5a60f7e1-5c0f-5db1-810d-7b343889f4c2 | note | Standard / Specification - Project Specifications
a42c322c-fb37-5806-acf8-f0f1449d2faf | note | Verifying Document - Red pen markup only
9e627554-1894-5bfd-9208-c4b2338f24ba | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
32e6f97b-f96e-56af-a4de-374e1d942e76 | note | Verification Activity: Activity - H
1bdb39a4-c834-5eea-9644-90da55bb9dd4 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3c7a3d2f-65b3-59f7-9a57-37a25851a4fa | note | Verification Activity: By - SE
818b28ab-277e-4afa-896a-457e858abf50 | checkpoint | 7.2 - Redline Drawings
02dbeefd-8794-5b17-bbd0-108ee91c7f1b | note | Detail / Activity - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen.
d8ea0dad-59c6-52da-a2ea-ad5b22e36a54 | note | Acceptance / Conformance Criteria - Drawings
fbda46c2-effb-5f38-b462-59f891f45168 | note | Standard / Specification - Downer
de4705ff-1fe4-5599-88b0-7a481404a0fd | note | Verifying Document - Redlines
bfee510c-1b33-5b61-899e-b0bfe10b59f4 | note | Testing Quantity Required (based from schedule qtys) -
d835ce3c-2c89-5621-a41a-ebe473517ff9 | note | Verification Activity: Activity -
3099ab85-1ab2-5b60-bc8c-a98f6bab8a42 | note | Verification Activity: By -
87a9a4ef-7f10-48d6-a74e-fb934ea0405d | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
0654dc0a-6726-5032-9c28-973147624b44 | textbox | Contractor's Rep Name:
e9678fc4-9dfe-5a85-be3d-7d541c2f8d85 | textbox | Engineer's Rep. Name:
7ae3d52a-31f2-53e4-975e-6c7b140174d7 | date | Date:
275dee99-1ccc-4062-bd99-80442dba9c19 | signoff | Add Signature
cb7a5963-4825-4ac8-9ceb-c401fe55f233 | checklist | DN1210-SP2-010-003-001 ITP Retaining wall 4 Wastewater Rev 1 | itp | DN1210-SP2-010-003-001 ITP Retaining wall 4 Wastewater
24393055-2add-4561-ab57-b13a8bfa87ea | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL , PERSONNEL & THIRD PARTY APPROVLS (P&G / ESTABLISHMENT)
c705759f-7e4f-4039-896a-e20d1d7e0b26 | checkpoint | 3.1 - GENERAL - Pipe Laying
4925b567-a5e7-5dfe-9542-2631b28588a8 | note | Detail / Activity - Method statement
d5198a79-71f7-5905-b10a-3c7b7579f75e | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
cba2d00f-cb98-5bc5-b1b8-226ac04b6778 | note | Standard / Specification - PS- 22.3 Appendix V
6fd9972f-c17e-53f2-9746-87d464cfb192 | note | Verifying Document - Wastewater Construction Work Pack Sign off
8a100839-75c7-5be8-a33a-fcf0418aa775 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
0e54a103-296a-5700-bfad-b525ece3e4ea | note | Verification Activity: Activity - HP
ceba0c16-36f1-534f-bccc-e5c9d6531022 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
2d21a68e-b257-5bfb-a0d5-bc361c34b4df | note | Verification Activity: By - ENG
fc683106-5a02-497c-9931-e8df19e43216 | signoff | AUTHORITY HOLDPOINT
7d17f89a-e607-4da8-924b-ab7a803c25bb | checkpoint | 3.2 - GENERAL - Pipeline Pressure Testing
6cfb8c7f-6f2c-5fe8-93e3-e0c5de4b9049 | note | Detail / Activity - Method statement
dd0e5d35-3de8-5a8c-bf75-94419a3e64cd | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
1f822b4e-ab8a-51d9-b4d7-ac50d66c55e0 | note | Standard / Specification - PS- 22.3 Appendix V
aa78ee66-d143-56c5-b38b-fa2db384cb55 | note | Verifying Document - Wastewater Pipeline Pressure Testing Work Pack Sign off
0990835a-a133-5fb9-88b1-cf287e660e78 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
61a3003b-af5a-5757-a3a1-42721dfbbb07 | note | Verification Activity: Activity - HP
7751219c-0393-52f1-94f8-e0d46a23ba86 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c06ade26-f92e-5a7b-946d-a4b8053c05f8 | note | Verification Activity: By - ENG
1a2f6347-c918-404c-b5c3-98119b84a0e7 | signoff | AUTHORITY HOLDPOINT
1a90bd83-c7b6-4b36-91ac-e7a716134ef3 | checkpoint | 3.3 - GENERAL - Extent of Line Setout
eb1efef7-cf2c-5174-9a02-778237c3b4ba | note | Detail / Activity - Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings.
cc8a6fa7-8f19-590d-b54a-ee8c70fb53ec | note | ○ Identify any clashes before construction.
b854eb9f-16ab-592d-8e4d-316a9bd1ec45 | note | ○ LOT- markup
088ca249-db01-533f-aff4-917b7ec69934 | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
60ea85e5-7565-5f17-a3f2-2195ca07f189 | note | Standard / Specification - Design Drawings
663ea03f-190a-5f61-b629-d010fee51067 | note | Verifying Document - ITP Sign Off / Mark-up
9fd40531-f754-510c-8e74-0562fabad6d1 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
d58779c5-ce8e-5abb-9a2f-385e424c256b | note | Verification Activity: Activity - HP
45fb1580-c127-577c-98df-8a1d10f4a4d8 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c48d1f44-1043-5f90-b659-124d3bff0e9d | note | Verification Activity: By - ENG
1030fb84-bbaa-4c91-834f-62a96128a3aa | signoff | AUTHORITY HOLDPOINT
8d7c31b4-63b5-428e-acc1-8fd5039b8406 | checkpoint | 3.4 - MATERIAL TESTING - AP65 Material grading: Materials (Gap65/AP65)
05b42e2b-8fe5-543c-b31d-bb9e2e729b8a | note | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
33b16a08-2067-5b9d-9d3d-2761118138ed | note | Acceptance / Conformance Criteria - No Particles >200mm
c77183d9-ab96-5620-ba67-2a3e0d6f21af | note | ○ Maximum fines 10% passing 75micron sieve
bfc8e9b3-a8a0-5926-9a30-3d11f21d10d7 | note | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
d2a386f8-8030-58bc-b5af-aa7c0dcea513 | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
6bc21cb5-a16b-53b8-89cf-ea194e45b6a3 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
1c289687-8901-5ed8-9b54-bb1a06dbbe76 | note | ○ 0-400 - 2 tests
112a6f63-fa37-5b6d-b64f-31bef7e8dc2a | note | ○ 400-1,500 - 3 tests
7034bb80-f7f7-50bf-8614-06124a1a02d1 | note | ○ 1,500-4,000 - 4 tests
75f548c0-8497-5da6-b609-689de186ca2b | note | ○ >4,000 - 1 test for each additional 1,000m3
23e97bf8-2730-501f-a5cf-70292c09a58f | note | — Results to Engineer 2 wks before importing
3cfb4b3c-83f8-536d-8955-e68b417626a8 | note | Verification Activity: Activity - HP
2a266c05-71f2-558c-b627-40ca19399f33 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f583d14c-23b4-5556-8c13-5c1fe261ced9 | note | Verification Activity: By - ENG
9776dfc6-8f50-43d8-9f9b-6249727f4c31 | signoff | AUTHORITY HOLDPOINT
af6ea73c-4119-47db-8645-427e7908710b | checkpoint | 3.5 - MATERIAL TESTING - AP65 Weathering index: Materials (Gap65/AP65)
38587ac0-c49d-538b-b7b0-e1e42c9342f2 | note | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
2127e723-88a1-55de-9a81-1d4a67e0506b | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
d81245e8-a6a5-5ff6-b01c-8241fb459e69 | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
8fe95a4d-ed7f-5109-9c2b-0462ce83ec34 | note | Verifying Document - IANZ Accredited Report
e125e6e2-4c52-5ad5-a79c-6ed0a30916c8 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
642eadc0-f753-5f7e-a967-616286a72cb2 | note | ○ Results to Engineer 2 wks before importing
e3cc6e59-e75c-55cf-8d6b-0efd603bd7a5 | note | Verification Activity: Activity - HP
cec1d9bb-f8f6-5566-b1fa-f5e678501e7f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0faf632c-de55-5f9e-b7c6-f2d7f004d7db | note | Verification Activity: By - ENG
38890e23-66c6-471f-8b53-80ba5e228091 | signoff | AUTHORITY HOLDPOINT
f92ef9a7-998e-4e8c-ba0f-75790402bbfa | checkpoint | 3.6 - MATERIAL TESTING - AP65 Crushing Resistance: Materials (Gap65/AP65)
d18fc663-c323-5503-ae23-f0944b78f510 | note | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
0a594f4a-d3d7-5812-9888-67682f5b7e5c | note | Acceptance / Conformance Criteria - >100KN
66992d10-2cb1-511b-8fa4-c706b4d43a17 | note | Standard / Specification - Appendix XVIII, Appendix V
07b5ed57-fc91-598d-9ca7-023fcf3f4daa | note | Verifying Document - IANZ Accredited Report
8a9e6727-dec2-55c4-9ffe-ab61d1c337fe | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
74bebecc-1bb4-502f-9ecd-a79a3e920708 | note | ○ Results to Engineer 2 wks before importing
c11f92de-6f0a-589f-9ccf-5e971de41dc2 | note | Verification Activity: Activity - HP
d56dfb28-686c-5bec-8437-e1f62b22d0d7 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
04501bac-87ca-5757-855a-445b009a902b | note | Verification Activity: By - ENG
9d24aeeb-ec37-4870-aba3-13dde1cc3a15 | signoff | AUTHORITY HOLDPOINT
039e4b13-0069-499f-9338-a2323924cf3e | checkpoint | 3.7 - MATERIAL TESTING - AP65 Maximum Dry Density and Optimum Water Content
95276425-8623-5949-b2cd-b79104be020d | note | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
4a7f20c5-d688-540b-a0e3-3cb546a8aa89 | note | Acceptance / Conformance Criteria - Report Value Only
7402188f-051e-559c-984e-7bf64bce8262 | note | Standard / Specification - Appendix XVIII, Appendix V
3a8360d0-558d-5d37-831e-a196a660d089 | note | Verifying Document - IANZ Accredited Report
042bb852-0f84-5ab0-a9ed-b657438e1b2d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
0847e942-cbc5-5ade-b1d9-98dede921a62 | note | ○ Results to Engineer 2 wks before importing
5baeaa2c-bf96-5c64-90a9-2a375cf7e653 | note | Verification Activity: Activity - HP
da117814-4cbb-5a33-a013-7ad2c14192a1 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
32fa3120-4f33-5409-9da4-d6e37ab1051d | note | Verification Activity: By - ENG
7a3b486b-1a56-4475-9756-d3bc98c665ae | signoff | AUTHORITY HOLDPOINT
f40da1cf-d41a-4097-8152-d575ebdd3031 | checkpoint | 3.8 - MATERIAL TESTING - Pumice Sand Material grading: Materials (Sand)
a30f534e-fc36-5f45-987a-543326a8dc73 | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
2b477a9a-674d-541f-8a80-c9e97ce00c81 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
ca40ba8e-1bbb-5ae0-8c33-1585fbaea325 | note | 19.0mm ¦¦ 85-100% passing
34496bba-3612-52bd-9e9d-3ffb7daee5eb | note | 9.5mm ¦¦ 25-55% passing
89cd032c-fd89-5441-9a1b-6e9972cb43a8 | note | 4.75mm ¦¦ 0-10% passing
b47e3316-07ed-5a61-87b4-bbeb0d557f44 | note | 2.36mm ¦¦ 0-5% passing
a978fb1b-e554-5144-8b03-8626945bed24 | note | 0.075mm ¦¦ 0-2% passing
e8de9667-7c7c-5a3f-96b9-4ad7574e9118 | note | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
17464271-4305-5c37-a794-64d2ec854b9a | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
e3fd0cb4-82e8-52d4-8673-d91a7ec1b991 | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
192a7e96-1288-5d9b-a0d1-cea4c2af9eb4 | note | ○ 400-1500m3 ¦¦ 3 Test
980def78-7763-555a-a744-557e1199218d | note | ○ 1500-4000m3 ¦¦ 4 Test
169c6814-ee8b-5c87-a493-97ce4b9eb8a7 | note | ○ >4000 ¦¦ 1 Test Additional 1000m3
159d10b8-0257-520d-85b4-91a1aebd69d2 | note | Verification Activity: Activity - HP
fb4dc7e8-5949-534c-bf8d-5222ef0bb72f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b83c3f9f-8804-5486-a27b-a30284680ef1 | note | Verification Activity: By - ENG
34f3483b-327c-4e9d-9cce-b1ef7c16365d | signoff | AUTHORITY HOLDPOINT
3edc4b21-892c-4c9f-8558-43451e222fbc | checkpoint | 3.9 - MATERIAL TESTING - Pipes (PE/ PVC)
be9f1042-4073-5176-b270-d13449d06d3b | note | Detail / Activity - Manufacturer's record and location of extrusion plants.
aef28feb-ac4b-5547-9bd3-a2d8975c5c82 | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
da04fb03-3d3f-5904-a677-744c382bf897 | note | ○ Full Traceability information and certification of analysis for the resin batch.
e8db201d-30e9-5424-bae0-880fe97bc825 | note | Acceptance / Conformance Criteria - Full Traceability information and certification of Material and resin.
2edf8214-1cc8-5318-ba41-86777d60959f | note | ○ PE/PCV Pipes in accordance with the IDC Approved Material List AM-6 Wastewater AS/NZS 1477, AS/NZS 4130
788ca215-f311-5fd0-950b-4fa8e288a6a1 | note | Standard / Specification - PS-22.4.1 (d)
5cc835a3-c4b7-5159-871c-5a117577f1d2 | note | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets
1d52178b-ee2d-5dc8-9c1b-8e38897be7b1 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
0e082dd1-412d-580a-aea8-74cfb189bf3d | note | Verification Activity: Activity - HP
050f26e0-e63d-5134-a36b-3010e5545fcd | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
edbf1a03-326c-5ac2-bfd2-c7db6ca2a888 | note | Verification Activity: By - ENG
162945d0-c9fb-47b4-8c61-a3e8616fd038 | signoff | AUTHORITY HOLDPOINT
6b2244bf-548b-49dc-abe7-a38f5ec61a62 | checkpoint | 3.10 - MATERIAL TESTING - Pipes Green Dome Odour Filter
2ac8ad0c-f927-5ec1-a8d6-1b87d7b41522 | note | Detail / Activity - A Green Dome Odour Filter (Model GDOF36) complete with DN150 ducting.
c867a12c-699f-511f-b29d-d9b698e9a3ae | note | Acceptance / Conformance Criteria - IFC Drawing 0324-1
e22d49e9-4ea4-5f19-833b-05bd522a453e | note | Standard / Specification - Model GDOF30
d91dfb43-729d-59d5-b423-b1ef214809b1 | note | Verifying Document - Delivery Dockets
d53b6bdb-393b-52d8-bc16-b19b71a0197a | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
9543fa2a-7f96-5c7d-9484-4fa7f7f35b68 | note | Verification Activity: Activity - HP
c3e5b9f0-9124-5ff4-ac94-585cb8723ed7 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ae9634da-49c2-51e4-92cf-99de15dc3bf4 | note | Verification Activity: By - ENG
415f9261-1698-490e-b4df-e0fa2f6bdc3e | signoff | AUTHORITY HOLDPOINT
5712804e-aad1-4a3a-8c6f-c62dcb7c3f1a | checkpoint | 3.11 - MATERIAL TESTING - Pipes Valves, Adaptors, Flanges and Fittings
338e8c0d-cdc0-5beb-8791-e02def3412bf | note | Detail / Activity - Have a pressure rating no less than the designed pressure.
d1b60b8b-c309-5efe-b88f-7adc55d233ab | note | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
406a5800-41e4-5ffc-a8fd-58412b47573a | note | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
27bab1c7-1ed0-5875-944a-09e111eaec6e | note | Acceptance / Conformance Criteria - Engineer approval AS/NZS 4129
041ee261-9efb-519a-bc2e-f937aa95f8fa | note | Standard / Specification - PS-22.4.2
a9058e64-7f93-5371-a199-bfbea2c64688 | note | Verifying Document - Delivery Dockets
6febd3a7-9d8d-57f7-8e12-7bb877d046e1 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
bd49c048-b7be-52f4-9c9b-50a73d52b765 | note | Verification Activity: Activity - HP
d57ee983-195b-573b-a27e-c12284ea484b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
20f11ad4-7151-55b1-80d1-9827e6798b91 | note | Verification Activity: By - ENG
1e0fa076-dbad-4a1b-ad5d-8f3c131b5da7 | signoff | AUTHORITY HOLDPOINT
645104d3-ecad-4d26-9fbe-b80f2e07eb59 | checkpoint | 3.12 - MATERIAL DELIVERY - Pipe and fittings. (PE100- DN180 PN16, PE100- DN90 PN12.5 & DN150 PVCu SN16)
3376e675-7099-5ba3-9e5f-8eefcfed1f83 | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
1aee6eac-5029-5adc-bb9b-548f36460262 | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
ed01f1b0-07f4-5276-9715-23574e12776e | note | Standard / Specification - Design Drawings
41a8570f-007c-5759-9532-a6f51f2fdb51 | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
ee689af6-7a66-5075-8936-b895e3a450af | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
f644d31d-cf3c-5b7e-81ab-6053d9053039 | note | Verification Activity: Activity - H
2ee71bca-208f-5395-8c2f-f867c49fbce5 | note | ○ Hold Point (Internal)
9b9351ff-8108-5265-b26a-1210f53bcf42 | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
f649f9f6-1f52-5e76-949e-30e4c4ccaf0c | note | Verification Activity: By - PE/SE
6c1d7f15-36ce-4443-8bd5-d754b405e4de | checkpoint | 3.13 - MATERIAL DELIVERY - Valves, Adaptors, Flanges and Fittings
2787c292-f7d7-53bb-b579-2fbbd43a3a7e | note | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
79c2b834-3227-59a2-a84b-da8db07b1632 | note | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
603c3adf-2ac3-56c2-a294-716d7833db53 | note | Standard / Specification - PS-22.4.2
4731b7fb-7253-5622-a0e6-0aad61ba2bf6 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
f348578e-cf81-534a-a798-539df52e7dd6 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
e0234f63-4a6c-54db-9f20-ba9f12c59635 | note | Verification Activity: Activity - H
99e76c43-3789-5295-a426-67bd271d473d | note | ○ Hold Point (Internal)
c467571c-6a97-514b-ad7c-52b4a804482b | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
9cfe7bf8-7945-5a07-8fcb-bae7e9acb452 | note | Verification Activity: By - PE/SE
739d7500-0872-41cb-b1c6-9524b01d7187 | checkpoint | 3.14 - MATERIAL DELIVERY - Granular Material (Imported Pumice sand, GAP65/AP65)
d36effc7-9b8e-53dd-ac2d-d52b31b6b6b5 | note | Detail / Activity - Confirm Specification and material in good condition.
c7dcde44-e172-5212-a0f3-80c085e3101b | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
15468dc7-bc60-59d2-bcc0-7db456feb0d4 | note | Standard / Specification - PS-22.4.1
8627e198-a056-51c8-a359-e420b0f182f0 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
8181c5b8-6736-5e69-8639-fc0de3857be4 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
c07c984b-4891-585d-a77f-b3cd40e5bdff | note | Verification Activity: Activity - H
3915d859-6648-54b8-a104-00c00ab1e092 | note | ○ Hold Point (Internal)
fbc8bcf8-c0ea-55e8-b166-708c3fd0e0b9 | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
46ce02b1-16b6-5d76-bc87-e04b5142f884 | note | Verification Activity: By - PE/SE
e7da888d-440c-4511-857e-a97a74b6aae5 | checkpoint | 3.15 - MATERIAL DELIVERY - Bidim/Geogrid
670964bb-f50c-56b0-9438-122e33a5de33 | note | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
b66044a9-981c-5011-937c-9def1dc771d9 | note | Acceptance / Conformance Criteria - Site Engineer Approval
16c53a1f-083f-515b-83d4-f745f41d5c59 | note | Standard / Specification - PS-22.4.1
19931f0d-2b97-5cdf-b34d-e7d5c48bc623 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
3ed3d549-f200-5270-9992-5c133d3f5532 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
b71b072e-0b13-5f34-9cbd-ffb4499aee98 | note | Verification Activity: Activity - H
83d0c3f2-9959-5fc9-b512-4efe5f10a79b | note | ○ Hold Point (Internal)
e8545b33-0c1f-5d1f-ae31-69fc5e687402 | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
6d256470-e783-5983-bf34-b0edb6e5f941 | note | Verification Activity: By - PE/SE
3958d281-ef57-4c5d-9e0f-0fd18120e52d | checkpoint | 3.16 - MATERIAL DELIVERY - Manhole WWMH 24
b5c8101d-a1cd-5de5-82f2-2f4e0666269f | note | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
fca61d8c-1c2c-5d91-8ab9-8178ee086438 | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
803e69a0-3e30-5857-9975-6c273ec47af2 | note | Standard / Specification - Design Drawings
3e0b199b-370b-5be0-abad-e80194310751 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
eac14574-b63b-5fa0-a899-9475e73bdada | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
c3765b01-10a2-542f-b66f-76a0854eb190 | note | Verification Activity: Activity - H
d553fefc-d2a5-52f8-aa3e-52e69ff88748 | note | ○ Hold Point (Internal)
82561c2f-a501-5997-bc8f-579e3e38cd91 | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
88919a87-e69e-5861-933c-611f362df630 | note | Verification Activity: By - PE/SE
5f2dc326-759f-4839-b9c2-b23d61a3ef34 | checkpoint | 3.17 - MATERIAL DELIVERY - Manhole WWMH 11
fbfb6127-a62a-571d-97ec-12c286494bd6 | note | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
56505724-8171-5415-84a8-aa0898d7f9bf | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
57018b33-582f-57ee-87fb-5791b4e82650 | note | Standard / Specification - Design Drawings
216221c1-771e-52da-98cc-20e1fec69497 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
63bc3cce-2f6f-54e8-b921-a8620e80175f | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
a7d3db85-2324-51ba-aeb0-8fbc669bbfc1 | note | Verification Activity: Activity - H
2ef3c1de-61ca-5253-9726-211d0962edeb | note | ○ Hold Point (Internal)
b088ea6a-9e4d-5966-b31c-1a773ac6ca1c | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
8e328784-97f1-5c36-8dd7-74737e41c590 | note | Verification Activity: By - PE/SE
fd6108b9-9b72-44e6-afe9-a1cf9b686d86 | checkpoint | 3.18 - MATERIAL DELIVERY - Bedding material
1362fdbe-ba91-5d67-88af-405eca4e8aab | note | Detail / Activity - Free of larger sharp particles conforming sand
5490946b-a0fe-544e-a4be-7eb62d1d0ca7 | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to sand
7a368e3a-ec95-5da9-a7f2-5e5f497d7cce | note | Standard / Specification - PS 25.13.2 (g) & (h)
8832a2ab-0895-58b1-9681-733d4f305a1e | note | Verifying Document - Delivery Dockets/Material Certification
1be7303b-8f39-57d4-9e03-2d2f8ff38cd5 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5a8c6c89-9d39-5afd-ad25-611d05e93b59 | note | Verification Activity: Activity - H
12c2f928-8f30-5af4-a154-54b41e4a3fe4 | note | Verification Activity: By - SE
8ab80e27-3603-4ea6-983e-deeff409bd49 | section | SECTION 4 – CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE- Excavation and Laying
c66d9ff0-b62a-4b21-a48a-d1e38e101af6 | checkpoint | 4.1 - WASTEWATER PIPELINE - Excavation and Laying - Foundation Compliance
1ad63881-13a8-5f9b-a644-d8c6bd6c23cb | note | Detail / Activity - On Granular or Cohesive Material
8c3fdf64-e54a-59f3-8ad5-2640889e345c | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
faa571cb-99f3-553a-be0c-cfaabd71483d | note | (Or)
e0d29ebb-8da6-57a9-9456-8ec94382ddd7 | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
a198eec1-8b5e-5953-a2ff-60aae3fe3190 | note | Standard / Specification - Appendix V Table 21:11
3a8f681a-7f68-5c41-83d8-29974d1d2848 | note | Verifying Document - Scala/Shear test result
dc337122-fa4e-53fa-a5af-a7b55c123b0c | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
4fb0048a-31e1-51be-a323-e154b246d3ff | note | Verification Activity: Activity - W
287bfae7-755a-5545-9793-cc4d4ba6ee00 | note | ○ Review of text reports/records or other evidence of compliance
86c52d91-5f5a-581c-a85d-7fb59eada38f | note | Verification Activity: By - SE
9e9516b3-0572-4bb5-86ec-f4547b6bd62d | checkpoint | 4.2 - WASTEWATER PIPELINE - Excavation and Laying - Undercut approval
ca62a0bc-e2a5-5539-816a-fac7150436b8 | note | Detail / Activity - Trench Foundation
4a85b240-e700-5aa8-b39f-fb1cf7618551 | note | Acceptance / Conformance Criteria - 300mm Max cut
a3c6bfd2-6275-50c9-b50f-e705f841fbee | note | ○ IFC Drawing Sheet 320
6d389748-f781-529e-9d1d-b71e65d8911c | note | (Or)
9815b6ce-a5ae-5575-a126-4220cbc5e0f0 | note | ○ Engineers approval
c48d9a9f-1de8-5dde-b547-8a5177416339 | note | Standard / Specification - IFC Drawing WST 0320. AS/NZS 2566.2/2002
f6e217b6-a659-5354-984e-d32295d7bca8 | note | Verifying Document - Lab Test Report / Wastewater line record
5312fb1b-09bd-501b-969d-650a6d200d55 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
51170502-8ae1-51be-9410-064c49beed7e | note | Verification Activity: Activity - H
72bc13af-44c4-5133-8e6d-a97c88b0fe52 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7754a609-f9ba-553d-8549-159e6315a75a | note | Verification Activity: By - SE
c006821d-5ab3-4973-b9a0-eda19c1e7561 | checkpoint | 4.3 - WASTEWATER PIPELINE - Excavation and Laying - Undercut Backfill Compliance (GAP65)
02c0efa1-ca70-545a-acc7-92645f591098 | note | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
6276da1c-7875-5d0c-aac2-622d53ef372b | note | Acceptance / Conformance Criteria - Visiual Inspection
d75ae629-abc4-548b-9484-97c1623473ec | note | Standard / Specification - IFC Drawing WST 0320
e08284f3-8d35-5d09-817b-bac22169ec6f | note | Verifying Document - Lab Test Report / Wastewater line record
066b5b08-e28b-56f6-b26b-e1bd2b184347 | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
63f86938-c278-5b3c-99e2-491ab8414070 | note | Verification Activity: Activity - H
39e39880-641a-54d8-a740-2184abff3f30 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
051dc86a-bf42-537b-be7d-5dcc11ddf26a | note | Verification Activity: By - SE
2d01092d-bd15-4ea1-899c-0c2bdfc1a73e | checkpoint | 4.4 - WASTEWATER PIPELINE - Excavation and Laying - Bedding Zone Compaction Testing
ab0fa452-28de-5c66-a846-a377f703c668 | note | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip)
a80b0636-32cb-59c8-b488-56f794d2debd | note | Acceptance / Conformance Criteria - Bedding Zone:
7c8317ab-389a-5b65-ba79-dd5ecb7df38c | note | ○ 100mm minimum thickness (compacted) over the bottom of the trench.
7a79e40e-acf9-5c08-88e8-96504ecc656a | note | ○ Minimum Compaction- 85%MDD
c6fd79eb-11ec-5bc3-be43-bcd51e0be4b1 | note | Standard / Specification - IFC Drawing 0320-1 AS/NZS 2566.2/2002
15b80ad5-f385-5d4c-8fcb-ab93b8ea99e4 | note | Verifying Document - Lab Test Report
a49d9394-6e8b-569b-bf69-aa02844b0736 | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 10m evenly spaced intervals.
6cec4088-642d-5fb8-a6e3-567603912923 | note | Verification Activity: Activity - H
232247e3-b3ab-5a53-a9d4-146c55fb0109 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e0f01bea-fe60-52da-b94e-3ae7f6172c5c | note | Verification Activity: By - SE
f2080aae-4fbc-41c9-918f-b7940c7bbc74 | checkpoint | 4.5 - WASTEWATER PIPELINE - Excavation and Laying - Laying of Pipes
78853554-befe-5186-b761-0d232df4e38a | note | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
29b50394-aebe-57ed-8316-19b9d970f9f4 | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
487a58fa-2790-5514-8689-44e4c6b7876b | note | Acceptance / Conformance Criteria - As Per Drawings (232735.02-WSP-DR-WST 0208), AS/NZS 2566.2
3498ea4b-c9b0-5bfd-93b9-d796d6a269f1 | note | Standard / Specification - PS22.7.1 C, AS/NZS 2566.2
2e7c8f6c-4b8f-5fcd-86dc-35bf5b2277f7 | note | Verifying Document - Visual Inspection / Wastewater line record
6268011d-f725-5979-958b-fbd689f5a2a6 | note | Testing Quantity Required (based from schedule qtys) - Every Line
2cdf0bad-3e99-50c4-b591-c33eb5778e10 | note | Verification Activity: Activity - H
c4ab8b29-9b32-58bb-825e-bb3221738a11 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
131a4ef4-3771-5bb0-ae02-862b90aa765b | note | Verification Activity: By - SE
22eb1490-1520-46c3-8a1b-69cffa2f4490 | checkpoint | 4.6 - WASTEWATER PIPELINE - Excavation and Laying - Pipe Installation on Curved Alignments
aed37a57-bb36-5e9d-bfbc-626921bd77f0 | note | Detail / Activity - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
e7aa0c90-fb8f-54b4-93ce-8b88971d7b42 | note | Acceptance / Conformance Criteria - AS Per POP 202
cc1ee248-243c-5a00-b3be-27671cc6bf34 | note | Standard / Specification - PS 22.7.1 D
149e3289-386d-5c7b-ba51-811ce5c2dc14 | note | Verifying Document - Visual Inspection / Wastewater line record
8cb3b594-1ed8-5e3d-9896-d10d8c70877d | note | Testing Quantity Required (based from schedule qtys) - Every Line
e7a4d2b2-fb85-56aa-a221-b714f8f2239b | note | Verification Activity: Activity - M
69421282-db2a-5781-9eb8-c2e20191e509 | note | ○ Monitor on Random Basis
5f45c29c-15eb-5621-aa3e-505147fcc6a0 | note | Verification Activity: By - SE
d6ccb176-57fa-4544-9587-4e8444b075c7 | checkpoint | 4.7 - WASTEWATER PIPELINE - Joint and Connection: Flanges
a34c40aa-e3f7-5807-a3a8-b7f1b13e7e45 | note | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
9f273ff7-f439-5d7c-9667-41db8ac18305 | note | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
a8c493c4-df81-5a81-bf4f-c619e3bda5b7 | note | Standard / Specification - PS 22.7.5
6fc06939-8b9d-5b6e-9fa1-d38f376b60d1 | note | Verifying Document - Visual Inspection
4726a3b2-6bd0-5ec5-acdf-d1d87871794f | note | Testing Quantity Required (based from schedule qtys) - First flanged joint
78a10b58-173c-5496-b8ed-e1d70c43e685 | note | Verification Activity: Activity - HP
4878d7be-c3d2-5556-b77d-9ef3967927db | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
78e1e3c9-fae8-5e24-9eb4-856ca600e3ea | note | Verification Activity: By - ENG
6afd7dfc-2dc2-4e75-a84b-08b58bab5f77 | signoff | AUTHORITY HOLDPOINT
21913007-8ed9-4483-9a5d-496eee6cc95b | checkpoint | 4.8 - WASTEWATER PIPELINE - Joint and Connection: Bends
381a3d11-baf2-5bc6-ae83-502f4f080e2f | note | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
e7af0e1d-9497-55fc-aa2b-b41b0a100ac3 | note | ○ Fitting must meets the same PN rating as the adjacent PE 100.
4213cd17-8bfe-52a5-9bd8-00b2f363530b | note | ○ Fittings must be suitable for producing the joints shown on the Drawings.
e4de2bf3-e8f0-5f3f-8ac7-d6eb5d4e737b | note | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
deab69f9-799c-5e56-b4b9-d1f368ec1b9a | note | Standard / Specification - PS 22.4.2
e381fb8a-6a14-52cf-94b6-8168c874ac82 | note | Verifying Document - Visual Inspection
5c7851ed-7659-538a-b78a-367515d9136c | note | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
211da4bd-6bb5-5c2e-871a-33c8e771a085 | note | Verification Activity: Activity - H
010a0b6c-cd0f-513e-82b1-c41544b95643 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
74532d5d-a48f-5dd3-8e6d-15018b52f5f7 | note | Verification Activity: By - SE
b8438f42-571c-48ab-b5c2-35dbe74d893f | checkpoint | 4.9 - WASTEWATER PIPELINE - Butt-Fusion Welding - Butt-Fusion pre construction weld test
9e7a0a88-7abc-52f3-9e20-272fa355ec72 | note | Detail / Activity - One weld on the most common size of pipes used for the project.
a33c905a-0e14-5f02-9f28-a369a5357877 | note | ○ One weld on the thickest wall (highest PN) pipe
74cfd2a7-b78e-5642-a5b0-f7f8e2fa2e9e | note | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode.
f2645f14-4658-56bd-99e4-c09eca91b313 | note | ○ WMS Report DVS2207-1
4b54982b-a4be-564d-b692-3af35daf431d | note | Standard / Specification - PS 22.9.6 (a)
6eabdbc1-9de2-5ab1-b3c5-e3b970b1bc67 | note | Verifying Document - Visual Inspection
db3bfee4-8560-5a20-acfa-8e2449d1de41 | note | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
a4361fa0-334f-5d5f-90e1-696a14e911e3 | note | Verification Activity: Activity - HP
12881f1d-baeb-5581-8cb9-2d4b129aac57 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
98809b5e-4715-53ad-8b17-2dd5aca9c259 | note | Verification Activity: By - ENG
20163195-1acb-4100-b7e5-4b9e25df061e | signoff | AUTHORITY HOLDPOINT
e9e1261d-cf1b-4100-8b80-616313998e08 | checkpoint | 4.10 - WASTEWATER PIPELINE - Butt-Fusion Welding - Butt-Fusion Welding
5d019ee1-e560-568a-b892-f6532335d167 | note | Detail / Activity - Use only semi-automatic or automatic welding machines.
410aeff6-c8c1-5360-bacf-cd26343b3715 | note | ○ Maintain a site record for all butt-fusion welds.
d65e3e6a-d2b0-5063-9cd1-6478d050a59d | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
cebd592f-c8e2-53e1-9a92-853b2e521707 | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
308beecf-cadc-52b5-af5b-ddc8e0fe6851 | note | ○ WMS Report
7e05ea03-4968-537a-96d9-60bd09a74c90 | note | Standard / Specification - Appendix 22. PS 22.9.4 C
149246a1-c6cc-5c22-8fe1-88a0b06c3291 | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report
1e1e8d6a-6edc-5e53-b655-2b0b2dcbf01f | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
29a2dfd7-26d9-5866-a771-829fe2d360f0 | note | Verification Activity: Activity - HP
cae5bdb9-381d-5351-88af-971adb1b8be2 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a133bcd5-e47d-5e93-8fc5-35b6870a80a5 | note | Verification Activity: By - ENG
c4355ac1-43b6-40e4-8848-4da561dd263d | signoff | AUTHORITY HOLDPOINT
4e1afeff-7dd2-4aa4-bed0-6b1268d114cd | checkpoint | 4.11 - WASTEWATER PIPELINE - Butt-Fusion Welding - Butt-Fusion Construction weld test
77cb19c5-722b-5d12-9fea-4b60b6763b33 | note | Detail / Activity - Test at least two welds from the first 50 welds.
a23310f3-2088-5b6d-bf0f-62d056306f56 | note | ○ One of the welds to be selected by the Engineer for satisfactory result.
dd8a379f-e528-5da3-9b4d-5a3310d1d211 | note | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
da26b171-4502-5850-88ea-f2d90bf338d7 | note | Standard / Specification - PS- 22.9.6 (a) (iv)
7d77a520-7b60-5333-8270-380cc1d56eb4 | note | Verifying Document - Test report
0ef252b0-7c82-5c74-8fd7-7d4816790426 | note | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
eabe726c-42fd-5263-8253-db7cd1aff0f6 | note | Verification Activity: Activity - HP
05a9c1ab-4009-502d-8ee1-afde46aeaf42 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
81c3b94c-fa51-5909-9983-e261ae8e79e6 | note | Verification Activity: By - ENG
6ed5ef1f-e55b-4560-b09a-54af38b28ce8 | signoff | AUTHORITY HOLDPOINT
69a62969-5176-45f5-bfe1-61d5ad3425cc | checkpoint | 4.12 - WASTEWATER PIPELINE - Butt-Fusion Welding - Survey
740c53bd-c676-5566-9451-fb6b86fa490c | note | Detail / Activity - Inspection of Pipeline Inverts
4cb468b3-5938-5197-84f9-061f8187426e | note | Acceptance / Conformance Criteria - Vertical design Setout:
1d8ac440-bcc2-5dd3-9ac8-ed16bca71878 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
1dc0287a-28ca-5ef1-9265-48ac7cbef999 | note | ○ Pipes > 1% grade: +/- 20mm variance
582d37ce-a0c8-519a-8ae3-47c1b571c351 | note | Horizontal design Setout:
6258bf8c-d277-50c6-828c-a7fb8645db7d | note | ○ +/-30mm variance
506c32a3-ff1d-58ba-8553-7768817ad70a | note | Standard / Specification - PS- 21.7.6, Table 21.15
2081eb11-0212-5718-8183-d5013961d2c0 | note | Verifying Document - Survey Data / As-built record
2294e105-067d-518a-b3b9-7db923538d79 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
d3d6e2ec-4955-5c34-ab19-dd04586b268b | note | Verification Activity: Activity - H
8400f451-563d-5bfe-8544-20b99ce854af | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
deedd68e-18c4-5114-9020-a10d75edb919 | note | Verification Activity: By - SE
0a4afa1b-b44c-4045-9188-18c1baead9f8 | checkpoint | 4.13 - WASTEWATER PIPELINE - Backfill - Emebment Zone - (Side Haunch Overlay)
e0e1223d-3b39-5ca7-a42f-500d9bf0549d | note | Detail / Activity - Granular Sand backfill Compacted in 200mm Layers.
c345edf7-ccdd-5cd8-963b-67f9268d5482 | note | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays
c580e62a-2d37-5d4c-8a1b-bfbcf85d0d35 | note | ○ NDM BS to be Carried Out
c72bb9c2-8b85-5b48-88b1-d185a9fd27da | note | Acceptance / Conformance Criteria - in 200mm layers.
6a7bc615-2599-50bb-bcd0-75881168794e | note | ○ More than 85% of MDD.
64e94a94-2226-588e-a8d0-135d2497dd7d | note | Standard / Specification - IFC Drawing 0320-1
8f30b883-d6e4-52ec-bb0c-3b2909fe3f6a | note | Verifying Document - Lab Report / Wastewater line record
c0ed391a-9625-5a5d-bb3c-495214c23b0d | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals. 200mm lift
91723202-2139-5067-bd53-5df068995841 | note | Verification Activity: Activity - H
264a1a4d-11e0-5ac5-972e-71d3dd86a120 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
24845f46-6a8a-58b0-8a6b-d877662d2b6f | note | Verification Activity: By - SE
0009e818-98d6-4412-bfb9-38d9e56f7879 | checkpoint | 4.14 - WASTEWATER PIPELINE - Backfill - Pipe Markers
e557a14c-8589-5ede-b62c-21fc81d8a2aa | note | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
fbf556e3-d39e-5aeb-a052-55306118eb4c | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
d81be316-2ece-58b8-9943-de1ab99f3b79 | note | Acceptance / Conformance Criteria - AS Per Drawings.
f5c951c2-8856-5185-b727-95eef19ccc50 | note | Standard / Specification - PS 22.7.3 a
7366ac13-a12f-59f9-a5ed-76754092a730 | note | Verifying Document - Visual Inspection / Wastewater line record
14e00182-c38a-56cc-8da9-266be5562116 | note | Testing Quantity Required (based from schedule qtys) - Every Line
914307fa-53aa-5ea1-997a-5ce403fa81f8 | note | Verification Activity: Activity - H
d81e22f5-d6a8-5315-9787-87c02dc33812 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e284f1df-e6fe-5b9f-a926-290089b997bc | note | Verification Activity: By - SE
d81f416d-9a08-4a38-828c-809d4a79443e | checkpoint | 4.15 - WASTEWATER PIPELINE - Backfill - Backfill Compaction Testing
a4b79ed0-9d4a-52a5-833e-8ef25d93b535 | note | Detail / Activity - GAP65/AP65 Backfill Compacted in 200mm Layers.
e9dfffe9-36f8-5341-8b11-78af5c03e486 | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
0147cdf3-988f-5acf-a912-d52707d4fa72 | note | Acceptance / Conformance Criteria - GAP65/AP65or site won material Backfill Compacted in 200mm layers.
1cf8772b-a95e-5170-a9b1-6db1e07e060a | note | ○ Testing to be completed on maximum 200mm lifts of backfill.
5f4b405c-9f94-5b24-81d2-57c377c76543 | note | ○ 95% NDM on Shared and Carriageway.
d8a1bdc9-24eb-51e8-afa5-e3ffef4f94ae | note | OR
8ced0b6d-d4cf-5130-96e6-ac532d5759df | note | ○ 28% CIV
0c9598d9-8375-59d5-a1b9-04e1ae805fe8 | note | ○ For site won min >60kpa
a52fad53-a12b-5958-9f21-25a30c511243 | note | ○ Ave > 80kpa
d2c5f184-caa5-53ba-9729-98eb99b982ee | note | Standard / Specification - PS- 22.13.5 NDM Standerd 25832, NZS 4402 Test 4.1.3, IFC Drawing 0320-1
3af5e840-c615-54b0-9e7f-2ab2bfe07284 | note | Verifying Document - Lab Report / Wastewater line record
9f325da5-48c3-500d-90bb-c14e59bbf77e | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 10m evenly spaced intervals.
0c93cc0d-473b-5824-be78-762a1a3feb1a | note | Verification Activity: Activity - H
13fb6c1d-4007-518e-a3ba-821f84fe1432 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e1dc72c9-9809-5692-9659-53214d6efb0b | note | Verification Activity: By - SE
57599b6a-41cc-4082-85a6-5cdb42e635d5 | checkpoint | 4.16 - WASTEWATER PIPELINE - Inspection - Pipe Inspection
a1e954c3-8058-5fc8-ba63-65beb2164338 | note | Detail / Activity - Inspection of Drainage line
6d68fe40-90e3-5751-a4be-65b960d3f841 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
30a6098e-ddd7-5d86-bc46-b9fa9f258fe0 | note | Standard / Specification - Internal
0edf0ae6-0d78-51b2-9439-73db670b307b | note | Verifying Document - Wastewater line record
0ca691a7-2cfc-5d84-af38-9816bd0b4a2e | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
3d9fd078-1e92-546d-805e-50e77d6cb7d1 | note | Verification Activity: Activity - I
7ebd5b2f-96f5-5822-bf6d-33e1e0718942 | note | ○ Formal inspection activity to be undertaken and recorded.
c2953b5f-538f-5438-bb33-9a40f9aec95a | note | Verification Activity: By - SE
78663a46-7e2e-4027-b4b8-95c98353da36 | checkpoint | 4.17 - WASTEWATER PIPELINE - Testing - Pressure Acceptance Testing
35ee16c4-8db5-5a2b-b85e-abbe1009d456 | note | Detail / Activity - Backfill/cover with embedment before testing
66b807d0-b6a1-5e8d-9863-a053e0d702dd | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
2767620a-f671-54e5-8db0-5a9f20a40536 | note | Acceptance / Conformance Criteria - Wastewater Rising Main Pipelines – 800kPa
c94a704b-f6a9-5308-aebf-c2730acb5331 | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
23a90bb3-c0d5-5d3d-905a-9a3cde630a24 | note | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
b9ced20c-d96f-52dc-8013-160fbeeef0f6 | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
1ccc5e03-11aa-5d2b-910f-93d4a5c6659e | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
176465a2-b4d9-56f3-b30f-e4279a722125 | note | Verification Activity: Activity - HP
a850fddb-764f-530d-9a11-fc510bb88c91 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d5827eec-2d4a-5688-b85e-e3040fae1a15 | note | Verification Activity: By - ENG
4a8004d8-9420-4635-a0a7-6d1358e404ad | signoff | AUTHORITY HOLDPOINT
e3a9ca8c-a437-400b-bfb2-d16507b2fc86 | checkpoint | 4.18 - WASTEWATER - Manhole installation - Foundation Compliance
ac7d6623-9c3e-5a8a-8220-1ee9c27c82ed | note | Detail / Activity - On Granular or Cohesive Material
8fc8e1b4-81c5-5125-ac5c-55181eae4c8b | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
f4726ccc-6921-5720-86c7-09145124c6fc | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
753f6b28-8228-5c25-8eb5-1d1ab15eb52c | note | Standard / Specification - Appendix V Table 21:11
029dca74-45c7-5416-91f2-80f03c71d251 | note | Verifying Document - Shear vane or Scala test result
0bef6257-81e5-5612-a5f2-e41100d5547f | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
653f4802-3c80-5a34-8d34-a4adafb4e55f | note | Verification Activity: Activity - W
ec9f4ae1-5a3e-5fc6-8d14-c92562beb824 | note | Verification Activity: By - SE
a9012a64-3b84-4a1a-8146-c4b9b3b25871 | checkpoint | 4.19 - WASTEWATER - Manhole installation - Undercut approval
8055decc-0924-50f5-9e9e-e85c011a3452 | note | Detail / Activity - On Subgrade
9bded7b5-8348-5d7f-a3d7-131027c146a3 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
c18d72e7-c75f-525e-8422-bd63e6c21a6c | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
773102f4-295a-5d7d-aa9a-514f88a3f17a | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
e1d33c62-f5ed-5ca8-ba75-eb7fd237bc47 | note | Standard / Specification - Table 21.5
916ad09e-24ed-5f86-82c1-3411b222313a | note | Verifying Document - Lab Test Report
ddfe7114-354a-5b49-a2dd-80ac5b4e0bba | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
0ff9b2ca-ce3b-5d46-b416-952fb1c71a06 | note | Verification Activity: Activity - HP
0287099e-0728-5db3-b5e2-a83752558c68 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
437d7dd6-576a-5e0a-8243-da54f74b2aca | note | Verification Activity: By - ENG
c41c8f03-5a14-430c-864a-9fd6688df6f1 | signoff | AUTHORITY HOLDPOINT
6bf6ef9a-2085-4a99-aea0-238ee6684aa0 | checkpoint | 4.20 - WASTEWATER - Manhole installation - Undercut Backfill Compliance AP65
731e579f-95eb-5b1a-ad44-a3f76f6cc03b | note | Detail / Activity - On Granular Material
9455cc98-74da-515b-aa30-37511a915d20 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
47bcf044-c731-5ce1-91a6-d3bab8670ada | note | OR
65e2cd92-b1b0-5212-83ef-cf4a4a1a25ed | note | ○ Clegg 25% CIV
9d678f65-82fd-5bcd-a27b-8da59b9e40a1 | note | Standard / Specification - PS- 16.5.12
ebe54783-c7ec-5878-9313-00f6b67a9dd4 | note | Verifying Document - Lab Test Report
1fbf7243-1d3e-5cb6-b1ac-61e1c76f61b9 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
73f13a87-c2af-5bcc-b44b-46dacf6a890b | note | Verification Activity: Activity - H
f93538f4-99b1-5fea-a253-2369e3244827 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c02b4493-d231-561c-bea6-d08a05835129 | note | Verification Activity: By - SE
d8bde92b-a3ab-4ab9-a47c-51a719550870 | checkpoint | 4.21 - WASTEWATER - Manhole installation - Bedding Compaction Testing AP65
d4c43e45-1e33-5471-8fd9-caa60704faf1 | note | Detail / Activity - On Granular Material
332a068a-451c-523d-8e82-416f2df848ce | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
f15f9771-d266-5837-b760-0519c89b175d | note | OR
f10798c9-f88b-58f4-bc02-b09b96593e51 | note | ○ Clegg 25% CIV
5d5c19a4-d25b-5eb1-8702-dc1260ed37b0 | note | Standard / Specification - PS- 16.5.12, PS- 21.6.11
6f2076de-0786-5627-aa8a-c4bcd1d752e0 | note | Verifying Document - Lab Test Report
f06b93bb-6ae7-513c-bb07-68a18dbbb224 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
e6846f76-ad0f-5841-a814-0688ddb2eaf1 | note | Verification Activity: Activity - H
0cef2c32-b084-56f0-af73-52b74f7a4f0e | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b917a4e0-da8b-5b0e-b785-70ac75ae21b7 | note | Verification Activity: By - SE
8ef7f509-1752-4799-adbb-8426f4fdfbf0 | checkpoint | 4.22 - WASTEWATER - Manhole installation - Survey
0a509e17-9fd4-5f9b-9149-5bc325de6438 | note | Detail / Activity - Inspection of Structure
e08ee5af-d87a-59c1-87a0-a5df969c5971 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
3f12eedb-c50c-52fc-8618-a3a264ec8edd | note | Standard / Specification - PS- 21.7.6
89c9b458-8cc8-5306-a208-f7f425ae67bc | note | Verifying Document - Survey Data
d0e9aae9-0333-5cb0-b249-031ecd8612d8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
bafc83ad-445c-5c7b-9778-a5afc1dc426a | note | Verification Activity: Activity - H
9d531f5b-ff0e-5f31-bf08-f007ec525e91 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
542d9887-fdbe-51a2-9703-7ac96a96d137 | note | Verification Activity: By - SV
d516a9ae-dfe5-49d1-a21f-061b12d36e6d | checkpoint | 4.23 - WASTEWATER - Manhole installation - Sidefill Compaction Testing
ea0b0b3b-1281-58d2-883b-cf942890f85a | note | Detail / Activity - From the bedding layer to the overlay layer of pipe.
3a3a5b41-05a7-504f-bcac-19817dd48d13 | note | Acceptance / Conformance Criteria - AP20/GAP20
f56b990b-892d-5d52-a100-18da42ebb3d0 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
58cb01c5-9926-5e0f-b02b-8c9e1e3efad3 | note | ○ AP20/19mm chip
8e81ef1b-7ae9-5423-bbf1-8c3119bd3816 | note | Standard / Specification - PS- Table 21.12
a5ffca85-1a15-59f8-9a6d-3b4cb2b1786d | note | Verifying Document - Lab Test Report
86db83d4-e08a-5463-9b69-8ace23adc034 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
51419abf-82c8-5890-a8a1-93656af4fd68 | note | Verification Activity: Activity - H
9ddea27e-4d84-56db-9bd6-2f33a26445c2 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
16f26f2e-2f0b-5622-8e48-0985facc8d66 | note | Verification Activity: By - SE
c94d8078-6fcf-4278-90cd-12ed090d523c | checkpoint | 4.24 - WASTEWATER - Manhole installation - Backfill Compaction Testing
6fcb0325-f3eb-5b5a-ab04-885001bf2c11 | note | Detail / Activity - From Overlay layer to the subgrade layer
6bbe4527-0c13-5687-ae38-0d9b3acc3345 | note | Acceptance / Conformance Criteria - AP65
9c676a5f-6b3a-5a83-9fdb-d8595d778670 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
8fcb2854-8284-5e66-98f7-51d6773306a7 | note | ○ AP65-Clegg28%CIV
85ef7e11-2fc6-5721-a5d1-700fcf709b3d | note | Standard / Specification - PS- 16.5.12
7288ba29-9302-5474-9883-f2253fc74b10 | note | Verifying Document - Lab Test Report
c9b5f86d-b56a-5eaf-8b18-906c0ed67c6a | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
38c37c3c-9c18-5935-b8e2-a690de12b9c4 | note | Verification Activity: Activity - H
314fa061-f545-5556-ae09-d215bd0a56ff | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3bab1ed2-31cf-5834-9b8e-15863d561231 | note | Verification Activity: By - SE
fd2bf9f1-90fe-4f6e-897e-c2817763ffed | checkpoint | 4.25 - WASTEWATER - Manhole installation - MH joints inspection
53464b90-e49f-5acf-a8bf-376f59b80c1e | note | Detail / Activity - Inspection of joints
805dcecf-977b-5257-b255-7642285ab139 | note | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
685b8ed1-7500-5835-87c2-8507312faa8a | note | Standard / Specification - PS 22.7.10
ae88cc7e-8411-539d-b1f1-e609a6766de4 | note | Verifying Document - Visual inspection
8d94b262-97fb-5e32-949a-341716faae48 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
67e8dfb0-73e5-5a75-bd4a-ff635e547f99 | note | Verification Activity: Activity - HP
c4a65dc0-3987-59a7-830d-4c1f664eec5e | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
266f39d2-25cf-5070-8283-95ac4e5ef15b | note | Verification Activity: By - ENG
aae67039-ef4d-4ab5-be78-0ee2f70f17a8 | signoff | AUTHORITY HOLDPOINT
30f14060-918d-48fb-b8bf-e2a2814ca62d | checkpoint | 4.26 - WASTEWATER - Manhole installation - Inspection
43e9d7c0-f478-5a14-bf2a-ac033f2e4147 | note | Detail / Activity - Inspection of Structure
77441b44-8678-5b63-a771-93114c7ebf98 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
2dd7d8a4-062a-561a-847d-58ed652776ab | note | Standard / Specification - PS- 21.6.11
9d9d0ab3-5ad3-5d87-84ac-3b421551f072 | note | Verifying Document - Manhole/Catchpit Record
8b580cf2-56b9-538a-b0d2-0f90d447b7b5 | note | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
e0084946-3108-50bd-81d1-676e984776f8 | note | Verification Activity: Activity - I
b26e511b-2fec-5332-ac1e-f71e02e76b01 | note | Verification Activity: By - SE
36a62afc-cf07-48d2-89d7-91026b4d2233 | checkpoint | 4.27 - WASTEWATER - Manhole installation - Plumb
be7a3312-333f-5393-8bbf-5f04382fee17 | note | Detail / Activity - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
06dde24a-2333-54f8-83cd-5d00b49da47e | note | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
e751619d-f5f1-5049-a2d4-c6078805a679 | note | Standard / Specification - PS-22.7.10
c46440e1-3a4a-514b-9def-4387e9c05105 | note | Verifying Document - Survey Data
0e52a310-e375-538c-9edb-3079df0d3381 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
7a974347-6a95-51be-ac45-a7755b189814 | note | Verification Activity: Activity - H
bae7e433-4b8b-5c60-9ea0-5577d315831c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ae713555-c8ca-53b6-a3d8-8d2188794569 | note | Verification Activity: By - SV
eb8ef2d2-baf1-4766-aeed-62cf17732e5c | checkpoint | 4.28 - WASTEWATER - Manhole installation - Step Rungs
f3480232-9a03-59e8-8033-5dd6a4a306fa | note | Detail / Activity - Step rungs evenly spaced at nominal 300mm vertical intervals
ed86dd44-fd44-5621-9519-dd64f1f5c89a | note | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
67a023e4-38bc-52a2-aa31-88eaa7c9bafa | note | Standard / Specification - PS-22.7.11
53c78f33-c202-5ce0-9ee9-6bee5902d905 | note | Verifying Document - Visual inspection
d90a522b-ffcc-5ae6-99a8-b92f5eb548b6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
9d32fbf3-90e1-501d-a565-2c1a9c4ad734 | note | Verification Activity: Activity - H
ca62b883-529f-5437-abe4-3634fb93018f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
58546770-ac9b-59d3-b555-cb1b3a2e1e06 | note | Verification Activity: By - SE
d1e141bb-792b-4900-95da-b570fdac5184 | checkpoint | 4.29 - WASTEWATER - Manhole installation - Manhole frame and covers
8808c75b-36f4-5176-b9a6-978faab3cf65 | note | Detail / Activity - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
3a799603-a2c4-51f3-bfeb-81a604b86768 | note | Acceptance / Conformance Criteria - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
d75bedef-30b7-55a9-9b4e-8b02a268af76 | note | Standard / Specification - PS-22.7.12
8d85a478-afe8-5201-ac5a-41e8fbecc326 | note | Verifying Document - Visual inspection
6b6557be-11c8-5dd9-a665-7bf503f40792 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
41b10468-956f-5686-94a9-dea150f0b140 | note | Verification Activity: Activity - H
e0837433-9a7e-552a-897b-05969da8ec7c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
407a27b2-efc2-5124-a899-fa9d2db3bbb3 | note | Verification Activity: By - SE
ebde94d3-5041-4219-ba33-d522032e2fe4 | checkpoint | 4.30 - WASTEWATER - Communication Duct Installation - Foundation Compliance
2d14e79e-fe7a-59ef-8d6b-cf135062aa22 | note | Detail / Activity - It shall be de-watered prior to installation of bedding material.
38dcb317-36fb-52b1-9b54-0b6811ea959b | note | ○ If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
3cc56fef-29c9-538d-96c7-9d51443c3ea2 | note | Acceptance / Conformance Criteria - 50mm granular layer shall be laid and compacted before the bedding layer is laid.
d293a605-52e2-520c-a183-9caf0c332797 | note | Standard / Specification - PS 25.13.2 c) and g)
7c1df846-e0e1-5069-a730-ffe713d15ebd | note | Verifying Document - Checklist
37a3d2fc-cf74-5533-93fa-92065849c04d | note | Testing Quantity Required (based from schedule qtys) - Each Cable
dcae8ef8-2ed8-594e-a732-7bd48dd35642 | note | Verification Activity: Activity - M
9c331bcb-3a3b-58d6-b0d4-11d6e6589113 | note | Verification Activity: By - SE
ec283c56-ec88-4dd6-8877-c0aabaec9349 | checkpoint | 4.31 - WASTEWATER - Communication Duct Installation - Bedding
15b7ac83-6c18-5634-8090-9d80814ac2de | note | Detail / Activity - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
b10000d0-6a3c-5492-8bf5-e8489d041e7e | note | Acceptance / Conformance Criteria - Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
5f318637-095a-5f46-aa8a-2eca65100cfd | note | Standard / Specification - PS 25.13.2 g)
e03f39c1-71d8-509a-8a79-1e722f617e54 | note | Verifying Document - Checklist
3c288d70-e5d4-58c6-8d5c-1f87a2045d2c | note | Testing Quantity Required (based from schedule qtys) - Each Cable
008e50c6-9619-510c-bdf7-226b2fc762b5 | note | Verification Activity: Activity - M
c938aba7-0f1e-5e98-81b5-84dbe37736ed | note | Verification Activity: By - SE
ea8da45d-52fb-433b-8bac-f6b2e9fba6b4 | checkpoint | 4.32 - WASTEWATER - Communication Duct Installation - Installation of Ducts
e717868f-a577-595e-800b-597ebde5ba84 | note | Detail / Activity - If more than 2 ducts are being placed.
f3da569c-0094-5e8d-b470-99d3dcc394d4 | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
ddf0d546-2cab-5221-b638-38f09b84af54 | note | Standard / Specification - PS 25.13.7 b) iii
31598755-aec0-518e-9c60-e8962d38851a | note | Verifying Document - Checklist
a356c93d-bb1c-5473-99a2-031e93fdc748 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
f1c6ce0c-b9d3-576b-9b20-3f42fbbf1d31 | note | Verification Activity: Activity - M
c127fb44-b679-55de-a290-7d0167f13d64 | note | Verification Activity: By - SE
1ea0f21c-ca64-43ea-a2ea-bb98035fdb58 | checkpoint | 4.33 - WASTEWATER - Communication Duct Installation - Draw Wires
915d42c8-c803-5b4b-bd21-b302b6d60e60 | note | Detail / Activity - A draw wire shall be intalled in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting.
b000756a-e92d-5e1b-9f57-25bd1db63ff0 | note | Acceptance / Conformance Criteria - Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load.
f73497e4-ab7a-5f1f-addc-efe9d5311167 | note | ○ ≥20 years design life.
99925a6c-752d-5723-9041-4d665342f172 | note | ○ The ends of draw wires shall be made fast within the pits and be secured to the duct plugs.
3ba4b3bc-3e15-5586-ae2d-bd0430f4f200 | note | ○ Blue colour wire
62d203cb-4703-5e0f-8cbc-6f9aa4949d0c | note | Standard / Specification - PS 25.13.7 e) ii to iv
c392aa24-ae7e-534b-b480-a52acd8fe375 | note | Verifying Document - Checklist
d0e29246-423c-581a-9500-0a008fd40c43 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
be9dc107-4c59-5f90-b0a0-5fc34b1e34e9 | note | Verification Activity: Activity - M
831ec295-8397-50cb-aba3-e097dd81b3b0 | note | Verification Activity: By - SE
e178f933-f9d6-4148-91fc-e36c49f2cbd3 | checkpoint | 4.34 - WASTEWATER - Communication Duct Installation - Caps
d8830d4d-94b9-59d8-8ed7-0d7255501ed3 | note | Detail / Activity - All duct ends shall be capped
5ab8a37f-28be-5221-a6a2-8c4bd8470ac8 | note | Acceptance / Conformance Criteria - Capped ducts
ce7a2caf-5478-52dc-bff5-139119a7f88c | note | Standard / Specification - PS 25.13.7 e) v
0c0ed932-8d69-5b61-9dea-578e88ee0b2e | note | Verifying Document - Checklist
bee5db94-33eb-5f96-9994-6443fefc43db | note | Testing Quantity Required (based from schedule qtys) - Each Cable
9686ef23-42ce-5777-8b80-c979d6becbaf | note | Verification Activity: Activity - M
56ba6a9d-69bb-51d2-bcdc-341dac0faf5b | note | Verification Activity: By - SE
eb3ebd7e-b4ba-4d0b-9d71-2d5694d5adb6 | checkpoint | 4.35 - WASTEWATER - Communication Duct Installation - Warning Tape
4a1379b3-88dc-5ebf-8d73-dfa0393c6cfa | note | Detail / Activity - Warning tape to be placed above services.
43e68678-ac9b-504a-8af3-4315c6cfd4b5 | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the topmost duct
69949156-27aa-51fb-8f96-1fae4fecbf49 | note | Standard / Specification - PS 25.13.7 b) iii & f)
98821763-9cad-5e2a-8a6a-e57e6472a011 | note | Verifying Document - Checklist
1757e0e7-5334-52ed-96ac-326b1b733aaf | note | Testing Quantity Required (based from schedule qtys) - Each Cable
4e55c4f8-d701-5c38-bea3-22e8b6ef0558 | note | Verification Activity: Activity - M
cf7be2c6-6e64-57f1-a1a3-c16b471951b2 | note | Verification Activity: By - SE
c4f7f296-63e6-4f2b-85ef-baa2e8dc3610 | checkpoint | 4.36 - WASTEWATER - Communication Duct Installation - Overlay
545d457f-43be-557f-a6e9-5e169fba01ae | note | Detail / Activity - 150 mm minimum sand placed on top of duct.
776d3bf2-855e-5b67-a69e-76ac3ecb7cb6 | note | ○ No mechanical compaction will caarry out till 300mm drom top of duct.
49f5f3ff-9b16-5ac2-99d2-ed3edb0dce07 | note | Acceptance / Conformance Criteria - 100 mm minimum sand placed on top of duct.
380db2c5-0209-583f-9a62-012d8415d273 | note | Standard / Specification - PS 25.13.7 b) ii
87067a13-712e-5287-9e0f-dbf33ea1fdcf | note | Verifying Document - Checklist
da60323b-7393-59c6-8475-ab894319c9ca | note | Testing Quantity Required (based from schedule qtys) - Each Cable
70cd481b-1b8f-593a-b8c4-b3622db6b5d0 | note | Verification Activity: Activity - M
27919061-bef7-5788-b388-404292ab71c2 | note | Verification Activity: By - SE
7cd46f98-dc8f-413c-8070-40de61c06d37 | checkpoint | 4.37 - WASTEWATER - Communication Pit - Location
f27b3976-a760-5c8f-b8fe-ead0dd883e40 | note | Detail / Activity - Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid .
69dbbb42-851d-504c-aa75-dec2033fa582 | note | Acceptance / Conformance Criteria - Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas.
e699d2f3-bf85-50d5-b630-71b66c38169a | note | ○ When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side.
3334297b-e602-5a95-9fc9-bcaee4f41870 | note | ○ When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side.
a66bd258-93a6-598a-b0af-2302bc8e4c5e | note | Standard / Specification - PS 25.13.8 a) i and ii
0896eb4d-a0fa-5221-9e27-cd97192cdafd | note | Verifying Document - Checklist
45bc0374-b767-535b-bdcb-e58876f279ec | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
68dfad1b-d922-511b-8c0e-c4fe73c49392 | note | Verification Activity: Activity - H
26ebdce3-2739-5640-a3f6-7a893de13e76 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a5c4daa4-eac6-557a-85d2-74f11a0fb429 | note | Verification Activity: By - SE
9dec5b2a-ba1a-45f2-8629-b6ed59228682 | checkpoint | 4.38 - WASTEWATER - Communication Pit - Bedding
c7ac0615-2cfe-5afc-818a-fdbc64639873 | note | Detail / Activity - Bedding with 150mm compacted GAP20 hard-fill coverd with 20mm compacted sand. Pits shall be carefully lifted into place and lined up with the ducts to penetrate the chamber.
def56796-0f46-5ede-8d65-d36a94742b57 | note | Acceptance / Conformance Criteria - 150mm compacted GAP20 hard-fill covered with 20mm of compacted sand
391dcad2-6f91-51af-8918-9684631b6180 | note | Standard / Specification - PS 25.13.8 d)
a837eb44-cab6-5534-8910-c011094299b8 | note | Verifying Document - Checklist
69d21c29-db12-53d1-b303-5b70687c4a89 | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
dc75201c-7ebd-5b13-b72c-d893007312b0 | note | Verification Activity: Activity - H
2cee1b7e-b877-50e2-b77f-124aa8adef20 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
538c988c-0355-58e7-8795-571c0c0b8dba | note | Verification Activity: By - SE
8fa9410b-2819-41ec-b750-958094dc2b08 | checkpoint | 4.39 - WASTEWATER - Communication Pit - Sidefill concrete
a3f4252d-693d-552d-baa1-7eb4cba8b89e | note | Detail / Activity - Plactic pits shall be cast into the ground with 150mm concrete surround
845d4958-008a-5ad9-9111-39bf3fbe4b0a | note | Acceptance / Conformance Criteria - Plactic pits shall be cast into the ground with 150mm concrete surround
f8d14e99-0bc2-5fcb-80f1-3225157fcd20 | note | Standard / Specification - PS 25.13.8 d)
ca2870f7-f102-5755-9fb9-d0b956c754b9 | note | Verifying Document - Checklist
7b4d3e0c-af07-5d39-bf97-572f65bcfac7 | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
4a13e1a9-0d28-5f0e-92a6-816085c5bb70 | note | Verification Activity: Activity - H
d1f45170-b126-5e80-af2a-4cf0272b2958 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
86da0330-903e-5b9b-83b4-5ad3c3e6e281 | note | Verification Activity: By - SE
2427c431-5835-4b9a-93b0-a08c8be3f43a | checkpoint | 4.40 - WASTEWATER - Communication Pit - Backfilling
cc96233c-65c1-5ee5-aef5-20b0dd4903b9 | note | Detail / Activity - Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts in 200mm layers of GAP 65.
b75d8f88-f8d0-5c39-9b7b-66cf1b4b8192 | note | Acceptance / Conformance Criteria - Min 92% compaction rate and Average of 95%.
2da08e73-35c7-5e20-98a9-c2fedd7df41f | note | Standard / Specification - PS 25.13.10 a) modified
9dae6591-27df-574a-aca8-1fec4c70ffa3 | note | Verifying Document - Checklist
8b83a39a-4828-503b-b6af-b05739a5d139 | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
b7e48d73-eabe-5ffa-aae9-23e2412998b8 | note | Verification Activity: Activity - H
10b4708d-80fb-5e44-9875-bb6dcb6be001 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
99218260-535e-5a1a-8d83-d58c9b6f75be | note | Verification Activity: By - SE
75a4eff7-fd6f-40c8-ac7c-f1f3d25d6002 | checkpoint | 4.41 - WASTEWATER - Communication Pit - Concrete
1d7ce8ad-fc5a-5923-8458-9aa43d6b4b23 | note | Detail / Activity - Top 300mm of pit shall be concreted around with a width of 150mm with a 20MpA concrete.
b89012dc-7f7d-5726-a101-e1fd3f183537 | note | Acceptance / Conformance Criteria - 20 mPa
bb896833-b956-5027-8c7d-c890a09a674e | note | Standard / Specification - PS 25.13.8 d) iv.
2b5fecf3-6964-5d31-88a7-d53a74100d0f | note | Verifying Document - Concrete Dockets
e0b7f9e4-8785-5a1f-a6c7-930c92f27664 | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
2f243716-1fc7-5b14-8e2b-3f2af25cff3e | note | Verification Activity: Activity - H
654d9b94-d185-580f-814a-b9be0c69b791 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
82076aa3-9e7c-5c56-94cc-8b43992f1aaa | note | Verification Activity: By - SE
7519d742-9786-4ef7-86f7-e7ef92ea2080 | checkpoint | 4.42 - WASTEWATER - Communication Pit - Clean up
32ad42ef-4240-5f2e-a02d-e01c6c868cd6 | note | Detail / Activity - Clean out all pit after completion of the work
9e4b4ea0-e414-50a8-a997-ac5979084c96 | note | Acceptance / Conformance Criteria - Pit are free of dirty, mud,water and foreign materials
5093c74a-1b06-5c50-9075-30747b0a9df5 | note | Standard / Specification - PS 25.13.8 e)
f481770c-bb89-5e40-8f2d-e183fc2237f8 | note | Verifying Document - Checklist
90559074-3b01-56b8-9524-c725e50b4735 | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
0850ae73-df09-535b-b193-8f016299b24f | note | Verification Activity: Activity - M
43e67f3b-fdfe-5987-819d-923da2d3853b | note | Verification Activity: By - SE
f2a581c6-504f-48d1-a1bb-2f6d88cc196d | checkpoint | 4.43 - WASTEWATER - Communication Pit - Survey As Built
83bc04b9-6d34-5233-a0f9-b150da38ce81 | note | Detail / Activity - As Built every ducts joint before backfill
d2059974-ca68-5be0-ada0-4b577817e0de | note | Acceptance / Conformance Criteria - Completed as per drawings
0148908d-31ae-57a2-8589-4dd14e1fae5f | note | Standard / Specification - Standard Practise
7863cfa5-0bed-5ffa-a269-67b9de0fface | note | Verifying Document - Survey
00931ada-0b63-5b6d-8977-daf1f5bc812f | note | Testing Quantity Required (based from schedule qtys) - On going
71472064-725b-5aa5-a9fe-e050446921da | note | Verification Activity: Activity - H
cdb365d1-2a4c-54a9-b1c7-acd12bc5a298 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e6342f01-1a48-5a2b-ba45-638a6729fc4d | note | Verification Activity: By - PE
a11c40e0-97b8-4b7e-a596-195e4307418e | section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
596a2ca4-2bde-4d65-9dc8-0ce6f1d3a385 | checkpoint | 5.1 - Survey As-Builts
4f90f7bd-4bf7-571a-9141-e52311fab15a | note | Detail / Activity - Quality Check on Nee pipeline and structure based on the tolerances in RITS
5a3ce09f-a314-567d-b3f4-05801b0611f8 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
3e0791e0-d785-54d3-8d41-230b0c4ecdd1 | note | Standard / Specification - Project Specifications
ce16dd9a-1524-59a5-ae29-92c29a8fdb1e | note | Verifying Document - Red pen markup only
082f4659-c623-59cd-8048-a6922eabf7b5 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
55dfc4e5-2555-5cad-b8cd-b5ca402967ba | note | Verification Activity: Activity - H
69a8cd6d-12b9-55ba-9910-b9092768b945 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8f320082-0cbb-5886-9196-c63c7d8eb729 | note | Verification Activity: By - SE
984166d2-b485-47c6-8073-347ba6c5ee09 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
b7dba065-ad4a-56fd-9a14-cc221e3f28f3 | textbox | Contractor's Rep Name:
9df41ee8-f50e-5a8e-a810-37a08c81334e | textbox | Engineer's Rep. Name:
1209041a-c725-5fb9-8574-37c9872c9d9e | date | Date:
a59cdc3d-e2ee-475b-bef3-dad30583f4c5 | signoff | Add Signature
c47f4bcf-f1aa-49ae-ba45-902d49ca26ca | checklist | DN1210-SP2-010-003-002 ITP Retaining Wall 4 Watermain Rev 1 | itp | DN1210-SP2-010-003-002 ITP Retaining Wall 4 Watermain
8a61d9f2-ea6e-43b9-8d75-ae1d4ac79145 | section | SECTION 3.0 - PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
a42878c7-fd5f-4cac-8598-83b9fd58c363 | checkpoint | 3.1 - Pipe Laying
3de1360c-5093-5f79-9c53-e90864781e4f | note | Detail / Activity - Method statement
18d9c70c-3895-5095-826d-340d4c9ca8ea | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
99717a64-34a8-598e-8722-e69abea3650d | note | Standard / Specification - PS- 22.3 Appendix V
a27ebe1d-be0a-5b80-801f-da00e7e9da33 | note | Verifying Document - Watermain Construction Work Pack Sign off
d08adbb8-f123-5333-9ece-bf6cf3e7b896 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
6dc71f0a-e993-50d6-853a-bef27a149f81 | note | Verification Activity: Activity - HP
e375829e-0e3e-53dd-b65b-c58939b4136a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e0328d95-ca38-5fe8-ad13-0c80935cec74 | note | Verification Activity: By - ENG
05e425c5-88ce-4494-bdd1-bb40d5c0945c | signoff | AUTHORITY HOLDPOINT
2cc81c73-9f2d-445a-8fdb-f5ab13482a27 | checkpoint | 3.2 - Pipeline Pressure Testing
f9a7cb15-06a2-5512-b972-3a0b5dab87aa | note | Detail / Activity - Method statement
5da8db1b-4e03-5df8-840b-b5093141d29a | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
cf088fc3-0746-5cb6-819b-7752f33111a2 | note | Standard / Specification - PS- 22.3 Appendix V
68c496cc-3b78-533c-a9c8-c8fc62d0cd3c | note | Verifying Document - Watermain Pipeline Pressure Testing Work Pack Sign off
31d24315-0ff7-53f5-b772-97d173f09a1d | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
d99d368f-80b3-5fdd-9db4-d8cf4fb03143 | note | Verification Activity: Activity - HP
e67b204d-c940-5ce2-8382-d6638864aeed | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d9654971-d27e-5100-8326-e0b2c553da7d | note | Verification Activity: By - ENG
d4caeaa5-f818-4ed1-80e1-9652d43ac109 | signoff | AUTHORITY HOLDPOINT
bbc3acfb-5573-42b6-be10-245081daccf6 | checkpoint | 3.3 - EF Weld Tests
90458005-00f9-5c19-92c4-53c53ab48f27 | note | Detail / Activity - Passing result in accordance with ISO21751 (strip bend test) tested by an IANZ accredited laboratory)
07e9777e-1273-5454-8667-8a9e7cd66746 | note | Acceptance / Conformance Criteria - Passing result in accordance with ISO21751 (strip bend test) tested by an IANZ accredited laboratory.
46942edb-753d-51d0-8c41-103d0769c674 | note | Standard / Specification - ISO21751, TCC IDC, DS-7.6.4.b.ii, PS 22.9
159b9935-f86f-5c29-8b44-0c171305014b | note | Verifying Document - Laboratory Test Report
155efd0d-9055-5588-90b9-c80fae4111be | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
c3f6d7cf-8338-59d2-b7a5-6610802ddf73 | note | Verification Activity: Activity - HP
a5a3c02c-125f-5b41-a9a6-0fedea2553e8 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
39a16c94-afc2-5d61-b821-edbf09370797 | note | Verification Activity: By - ENG
f10b8051-5598-4c85-92af-fc2640563578 | signoff | AUTHORITY HOLDPOINT
a397497c-3eac-4acd-a5af-cc8fe2b53c34 | checkpoint | 3.4 - Butt-Fusion pre construction weld test
13af9c78-4b11-5c37-8653-17e1f58aaf89 | note | Detail / Activity - One weld on the most common size of pipes used for the project.
471ea941-cf5f-505e-b881-1e20c076220b | note | ○ One weld on the thickest wall (highest PN) pipe
a0f74e25-4e97-542a-8226-6d0db691ffde | note | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode. WMS Report
d1ed4a44-0456-59f8-ade0-fab871c1387f | note | Standard / Specification - PS 22.9.6 (a) ISO 13953 Standard
f8fcb530-a8cf-56cb-bebf-5c6b07f9e18b | note | Verifying Document - Visual Inspection
1d97c827-19e0-52e4-8a2f-24240c496995 | note | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
e6a18635-e046-5836-8bf9-c73ed5cf5d29 | note | Verification Activity: Activity - HP
adfaec18-a290-51a0-bbcc-fc7a73e5eb28 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ddbaa0ef-366f-5635-a6a9-2f31a7eea473 | note | Verification Activity: By - ENG
9d3606f1-0da1-4bc3-b3e4-a5b750be345f | signoff | AUTHORITY HOLDPOINT
278887db-ddf0-46d9-92d9-cfd4226c9aab | checkpoint | 3.5 - Extent of Line Setout
33c8dabe-95c8-557c-aeb6-2f7d243416ca | note | Detail / Activity - Ensure line and level of Watermain has been marked out and agreed with Engineer in accordance with Watermain drawings.
b1e18522-34fa-57d6-bd69-3d30ade77234 | note | ○ Identify any clashes before construction.
47558297-ddb3-5b7e-8d28-27136e6f578f | note | ○ LOT- markup
2529601e-c18d-53a9-b139-0fa7a811d0b2 | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
6da7f6b6-733a-569b-98be-03d75394646e | note | Standard / Specification - Design Drawings. 32735.02-WSP-DR-WAT
01457b5d-528d-55eb-9220-c47313593317 | note | Verifying Document - ITP Sign Off / Mark-up
c681543b-da9e-5fdb-9a47-0d354044ff74 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
afedc576-437e-5783-960e-bd54d97ee149 | note | Verification Activity: Activity - HP
a8511fe3-2732-5a8b-acc4-5b042a6e1bd6 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
dc0c8b09-6b88-5545-afff-9a59d5fa9fc8 | note | Verification Activity: By - ENG
6a7a28fd-a668-472c-8ace-1ebe3507cf3a | signoff | AUTHORITY HOLDPOINT
9df45ab2-4257-4ec0-93d7-e9ce4c7e2238 | checkpoint | 3.6 - Pipe and fittings.
3eaa422c-6dec-5a8c-80b8-e789934ebf6a | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
8837ef0f-b3b6-52b8-a430-9fe340afce45 | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
2ee6d8a8-e292-5e10-9ca5-ddbc351f92dd | note | Standard / Specification - Design Drawings. 32735.02-WSP-DR-WAT
f5d88922-8dfe-5b10-b0b5-49f4ba707fb0 | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
71a5096e-5ab0-5a2f-8ad3-9c122008c8eb | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d18a99a4-fc45-569f-a5be-67e6b4e3c93b | note | Verification Activity: Activity - H
11ea83ee-6d1d-5220-b880-313dd7edfb0a | note | ○ Hold Point (Internal)
088fd13f-3aa1-5c0a-9e17-095611564b57 | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
10415c8f-101d-51cd-8ce9-b1a4fbcab99f | note | Verification Activity: By - PE/SE
9e0b103a-ea6e-4545-b77d-51fe3b10c917 | checkpoint | 3.7 - Valves, Adaptors, Flanges, Caps and Fittings
e7c3827d-6787-5c9a-aed8-9fa3c7f1e1d9 | note | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
e717e597-91c5-588a-90e7-a89baf09cc30 | note | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
efa6b271-bfc4-5c80-8d1c-6305296ba8ff | note | Standard / Specification - PS-22.4.2
f6284707-a2fc-5d5c-b70d-bd74dbe36a40 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
9c571203-8f5d-59f7-b162-dd81436b768b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
e300c40d-aed2-5a52-b897-ff806144d383 | note | Verification Activity: Activity - H
94e5849d-1e1b-5700-8211-058788a02500 | note | ○ Hold Point (Internal)
da72c26b-dd98-50ff-aaf7-b2d4a6d32a4a | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
181488a5-9909-5efb-ae8a-55e0451ff5d6 | note | Verification Activity: By - PE/SE
0c2e1bca-cf63-4cc9-88d0-4f7f3fce51ea | checkpoint | 3.8 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65)
76aa6ff0-4586-5a5a-9889-c46015ee6006 | note | Detail / Activity - Confirm Specification and material in good condition.
f21c44e2-fb18-5239-b547-b1f4adba6d52 | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
4f323292-941f-57c5-a8ec-fe6e15257c18 | note | Standard / Specification - PS-22.4.1
be360d2b-58a9-53e8-8aa9-a55b6e9ab7ba | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
410d2564-60a2-5661-b6a3-b81594194dfa | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
fdc9a84f-32f1-5401-a730-5b5d0b40c8ef | note | Verification Activity: Activity - H
34dc29c8-483d-5904-9f56-d8ae97e65a01 | note | ○ Hold Point (Internal)
c7473011-793a-5471-aa84-a52f987fa6bc | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
213f6fe0-9278-59b1-ae6d-99c5695b7908 | note | Verification Activity: By - PE/SE
504966c2-7af8-4255-9504-757b415c3837 | checkpoint | 3.9 - Bidim/Geogrid
61a6a253-54b5-5eaa-b2c9-0c8309985eed | note | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
b93953e8-3e59-5dff-85a7-a7dc1ad2023c | note | Acceptance / Conformance Criteria - Site Engineer Approval
03875754-2980-5e9d-a743-f691e90a1df9 | note | Standard / Specification - PS-22.4.1
5b6b24de-b3b9-5960-a043-69eeb52efc90 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
7f733014-019a-5577-8c0f-1d0920ddb13d | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
329bf3da-800e-5b96-9f06-da027047fc22 | note | Verification Activity: Activity - H
d6abc494-6389-5645-8b1b-21cdc0929ee8 | note | ○ Hold Point (Internal)
ef7c12e8-c6a7-5194-a2d7-9b203e602a5a | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
e234433d-db91-5c09-8bd8-34e1892617cb | note | Verification Activity: By - PE/SE
06ada176-dd9c-4a2e-b333-cd82caf31745 | checkpoint | 3.10 - Pre-cast Manholes
16f21a67-f420-50f2-b441-1a53184d869c | note | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
f0e4943a-6cb8-5c60-81d8-f7f2c83e3b6f | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
da067811-f113-5a65-86a4-c9a1d484330e | note | Standard / Specification - 32735.02-WSP-DR-WAT
3e6c1701-aff7-5c45-a7bf-58a0fce219d5 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
16d2f6e9-7650-57d8-b622-b671c2ff388c | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
c8bf5138-7c75-5324-9a04-dbbdf3a7eac2 | note | Verification Activity: Activity - H
c456e8cc-d3ad-5c5b-b4e0-8f6f70cf5d76 | note | ○ Hold Point (Internal)
30659fc1-7c85-551a-926b-0fd7c489b67d | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
3f863d6d-6c18-556a-aa7d-40923a644483 | note | Verification Activity: By - PE/SE
d02c7b90-1eea-429d-893c-034c668f87d7 | checkpoint | 3.11 - KWIK Spacers
7c8c73c3-c9b2-5cdd-8128-6fd994088961 | note | Detail / Activity - Confirm Specification and material in good condition. Spacers for DN315 pipe and DN560 sleeve.
423afbbc-8dc8-53d8-8487-f63952a5cba5 | note | Acceptance / Conformance Criteria - Model: HDXT43
1b072d50-91ef-54b9-a725-5c18346726c2 | note | ○ Height: 43mm
99c02631-9677-5fbc-b186-bd11979dcbcf | note | ○ Spacing: 1.5m
561d4b50-d441-5b32-8cc0-ceea64901ad0 | note | ○ Installation: Centred and restrained
a7a91b55-11d0-5335-b9a5-d7ed4da7662c | note | Standard / Specification - Manufacturer’s Installation Guide. 32735.02-WSP-DR-WAT
59a85f31-06a6-5b4f-ac85-e6782d62918a | note | Verifying Document - Photographic Evidence
6242475d-db59-5d7a-b076-aac9444fd153 | note | Testing Quantity Required (based from schedule qtys) - Every spacer
0f98d2e9-04be-5dad-b6b1-56a94f7456b7 | note | Verification Activity: Activity - W
f9d7b455-259e-5564-8762-7dc7cd1cc452 | note | ○ Review of text reports/records or other evidence of compliance
90bfde5c-bc49-54be-b807-2fb234cf7380 | note | Verification Activity: By - SE
643e3343-f516-470b-b346-eba0ed33352d | checkpoint | 3.12 - DN560 Sleeve
885083e0-f0bc-5ab5-b4e1-911495f96831 | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the sleeves are correct and in good condition.
59978588-d546-55f9-b255-ba6136d23939 | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
c77836dd-fe63-5f52-bfbc-5abfdc307d18 | note | Standard / Specification - Design Drawings 232735.02-WSP-DR-WAT (Sheet #0312)
1d37154a-2bca-5ac4-89a3-e69d2b2bd565 | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
74a73818-ac58-59ca-990d-cde7809e3c9a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
ed0cc856-21c1-58c1-8e17-f4c8d2a1583c | note | Verification Activity: Activity - H
53e116e3-d37c-51bd-9dc4-b5087e6913ba | note | ○ Hold Point (Internal)
8038e508-d2b8-59e9-972b-980d20750a2f | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
42ba630c-8ca6-566c-abf1-955af85b8281 | note | Verification Activity: By - PE/SE
029dc57e-90b3-429c-b73e-6d7726ddea55 | section | SECTION 4.0 - PRE-CONSTRUCTION - MATERIAL TESTING
065f7233-ca1d-4978-a9a8-7a3e6a5b532a | checkpoint | 4.1 - Material grading: Materials (GAP65/AP65)
d014e844-c373-57dd-9580-45a2cf8bb898 | note | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
d07081d3-880c-5ed0-9e43-7abc39759c9d | note | Acceptance / Conformance Criteria - No Particles >200mm
aa24c79d-2954-5617-8f9e-7b24ed882947 | note | ○ Maximum fines 10% passing 75micron sieve
8dd48936-393c-500d-b787-a8d89481f4dc | note | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
efc8a25f-9503-5ee6-a250-78b5c5640cb6 | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
908a1d7b-6e43-506e-bddb-7394166ce037 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
e4e137c3-4d1e-54ef-87c1-c61840003a72 | note | ○ 0-400 - 2 tests
78e72885-d53e-523f-b786-0d53b81162ad | note | ○ 400-1,500 - 3 tests
8f392934-759b-5a70-8d44-a25992835e3f | note | ○ 1,500-4,000 - 4 tests
8e853f37-1a16-51ce-87a1-221b9e7bb691 | note | ○ >4,000 - 1 test for each additional 1,000m3
769ebc03-f817-5e6f-9998-a872f8083a64 | note | — Results to Engineer 2 wks before importing
cabb47e4-f907-55ab-9cbe-c4f107e0cc5d | note | Verification Activity: Activity - HP
05f835cf-2952-5898-ae7e-1331282593e9 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d17be77e-d2c8-5e6b-9bf2-79358981428b | note | Verification Activity: By - ENG
f3ccea12-92bf-4e0e-a0bb-b25178f43c58 | signoff | AUTHORITY HOLDPOINT
265439c6-2b64-477b-b85d-07f927ae5bec | checkpoint | 4.2 - Weathering index: Materials (GAP65/AP65)
ffee73b4-146a-5a8e-9ba8-6e10dbb50637 | note | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
de5a888d-a687-5e0a-8a37-2ad6c36cb83c | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
0fbb224c-6d6b-5abe-803b-1082f1f8890d | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
6fdd4451-265d-54d6-97bd-6b940d5a160c | note | Verifying Document - IANZ Accredited Report
08ce9d0e-7f3d-5cab-bc9c-8e089d13817a | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
cdcc2fd9-6fa3-5bb6-9560-c8c21c18e224 | note | ○ Results to Engineer 2 wks before importing
2039b7de-6a61-576d-a8c5-17a2487e7bb7 | note | Verification Activity: Activity - HP
a9a98989-b8d1-525e-8a83-e671daad60bc | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d0e1858d-b69e-5d8c-8be5-d680a44a1251 | note | Verification Activity: By - ENG
9a5ce424-6c32-4509-90c8-1075d426e1d8 | signoff | AUTHORITY HOLDPOINT
c991b671-dc22-43ca-a0fc-ce476b91f995 | checkpoint | 4.3 - Crushing Resistance: Materials (GAP65/AP65)
8b1ef2ab-0b5c-5ec1-96de-505db81b8fa0 | note | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
8fd34780-ba91-5c4b-93cb-19b7479280da | note | Acceptance / Conformance Criteria - >100KN
2b2bfe48-7543-57c0-9f72-c762ef797ca1 | note | Standard / Specification - Appendix XVIII, Appendix V
36b03184-fe7f-5a8c-a070-b90456147d9f | note | Verifying Document - IANZ Accredited Report
e896e25d-ef36-5f1b-b33a-1368151ae2e3 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
bdb7bdab-65d9-5806-be2f-b211a175f0d9 | note | ○ Results to Engineer 2 wks before importing
c77bf8a2-66b4-5af8-af93-88ffc7c4b23f | note | Verification Activity: Activity - HP
ab8fa1f3-e136-5343-8803-bf89452a79fa | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8eb247ec-a908-5cd5-982b-24d51d5c7098 | note | Verification Activity: By - ENG
62f23392-5be6-4bc6-b707-29bd182037e5 | signoff | AUTHORITY HOLDPOINT
f06cf671-d04c-4a80-a6f8-41e423f43346 | checkpoint | 4.4 - Maximum Dry Density and Optimum Water Content
83bb8c62-215e-59f8-8173-3802ecea526f | note | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
54695710-d4f4-54a9-9578-47c83501063b | note | Acceptance / Conformance Criteria - Report Value Only
584e3016-3562-505f-a746-691d04a250f1 | note | Standard / Specification - Appendix XVIII, Appendix V
db05d2bd-3573-5fda-996d-9a7dbd4d5e85 | note | Verifying Document - IANZ Accredited Report
b7ff9ea7-24bf-5d2f-b5e2-9ca890c8377b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
b9d2d90f-d671-5ec1-b2dc-d2c5ed5a8311 | note | ○ Results to Engineer 2 wks before importing
87ab2bc1-846d-5fd0-b540-2fbf4e81396f | note | Verification Activity: Activity - HP
062282f2-702f-501c-9b24-67657a78918b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
542e9fe1-73c8-5618-bfc4-e8fcd200760d | note | Verification Activity: By - ENG
50fba662-5611-4ddd-a6b5-d114d1da0aea | signoff | AUTHORITY HOLDPOINT
95be6002-2f5f-41b4-a7e1-969cc5449682 | checkpoint | 4.5 - Material grading: Materials (GAP20/19mm chip/Sand SAP7)
53a02d86-1824-598e-94a0-963d64af4e49 | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
af38229c-4b5d-5cd2-92ee-ad04eb354c15 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
22d8283b-00c4-543f-98db-8666cc808bd0 | note | 19.0mm ¦¦ 85-100% passing
0f4580c9-5c9e-5d12-b016-8707b31eeb33 | note | 9.5mm ¦¦ 25-55% passing
bcf88387-a60e-589a-bfe2-45a50dab929a | note | 4.75mm ¦¦ 0-10% passing
ee5d6778-bad9-5a52-baee-170b55dbdb7f | note | 2.36mm ¦¦ 0-5% passing
f13c1dca-cf93-5501-875a-4b973a9bed83 | note | 0.075mm ¦¦ 0-2% passing
0d8a83f7-9df0-566c-afd9-c32a6c85a141 | note | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
fbcbbac4-44f5-5b28-a6e8-8507f7e73747 | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
115943c0-266d-5a21-b219-712386fa5fd9 | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
fd6f4f0d-0664-5041-8ecf-36cc4664c692 | note | 400-1500m3 ¦¦ 3 Test
36568d42-e4be-5325-81bb-967f5bc1611f | note | 1500-4000m3 ¦¦ 4 Test
e7b6f01d-d66a-5b08-9a88-684366421b36 | note | >4000 ¦¦ 1 Test Additional 1000m3
6488289d-9b47-5fbd-a703-f817278822a2 | note | Verification Activity: Activity - HP
dfa4c00d-6396-5218-86ec-bbc8e23053c4 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
21a0ad14-beca-5add-9078-e43dd36fc2b9 | note | Verification Activity: By - ENG
f326be8f-fc50-463b-aa71-2d5d1759e12f | signoff | AUTHORITY HOLDPOINT
a426f176-9a2f-472d-ab1c-0107425e1835 | section | SECTION 5.0 - PRE-CONSTRUCTION - MATERIAL TESTING (Pipes)
8011aae6-9b15-4091-8922-684b174c22e5 | checkpoint | 5.1 - Pipes (PE)
093da5d9-e201-5dea-a31e-545cedbf594e | note | Detail / Activity - Manufacturer's record and location of extrusion plants.
e49fd1e6-c9c4-5d75-a9f0-ea8cfdd5c282 | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
1df41383-76bf-529b-9354-af2670bfe97e | note | ○ Full Traceability information and certification of analysis for the resin batch.
b14d400a-1b1b-5372-89dc-25fda2396ac7 | note | Acceptance / Conformance Criteria - Full Traceability information and certification of Material and resin.
008524fb-3df2-56ca-8d5c-7784380f7b4b | note | Standard / Specification - PS-22.4.1 (d)
9cb2e6a6-5353-5f20-96f6-3e216b0bc97d | note | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets
d8887bb6-33af-5c64-886a-68dbc3997858 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
4feed52e-1e68-54ca-ba24-ee6e76e2f74d | note | Verification Activity: Activity - HP
b2c6805f-9876-5fea-b678-6a58ee06ffbf | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ee7d3742-774d-52eb-a6b4-4cfdd23e3dee | note | Verification Activity: By - ENG
c84f08d9-653c-4e83-90a3-4c5fcc645134 | signoff | AUTHORITY HOLDPOINT
f78c893f-f211-4ae7-859c-f8e1616448cc | checkpoint | 5.2 - DN560 Sleeve
3aaf5295-a035-5730-961f-99e699ee7868 | note | Detail / Activity - Butt fusion Weld 13 x 17m DN560 PN16 pipes into 210m string
00923972-8d9d-582d-80cc-d91cbe6c5dde | note | Acceptance / Conformance Criteria - 95% tensile strength; welds aligned
1ad14c74-678d-535e-9a28-b0f4dfc3ff83 | note | Standard / Specification - NZS/AS 2033:1980; Appendix XXII(a)
8267cdca-05c4-54c8-a491-0bae191efe21 | note | Verifying Document - Butt Fusion Welding Record; Photos
cc90a409-a89f-53ec-bed0-278b4b8cf3b4 | note | Testing Quantity Required (based from schedule qtys) - Every Joint
103ab4b9-d195-504d-ab9e-eb13f6f8a1f3 | note | Verification Activity: Activity - HP
97e3efdc-d2c1-53de-a032-b8f1ce1b60a0 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7d5028dc-8873-5a57-92b2-70fbe6d43e13 | note | Verification Activity: By - ENG
f38724f6-cda8-463a-804d-bbdc275e9670 | signoff | AUTHORITY HOLDPOINT
b533da7d-3221-4592-9058-10eeec9c3db9 | checkpoint | 5.3 - Valves, Adaptors, Flanges and Fittings
57956dcd-d452-53b5-aefc-784fe6ee8479 | note | Detail / Activity - Have a pressure rating no less than the designed pressure.
cf43f135-261a-56bc-8137-a92a6cc9dfcd | note | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
235b400d-05e3-5eab-bd7e-1c2bdcd2bd84 | note | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
f0be7e7d-5c31-586d-a707-b3ba157b431e | note | Acceptance / Conformance Criteria - Engineer approval AS/NZS 4129
283597cb-d70d-5d5e-b2cb-c0ae821d0bb0 | note | Standard / Specification - PS-22.4.2
4e8283ae-896e-5ec6-9380-7dd5c46f2553 | note | Verifying Document - Delivery Dockets
6967c657-be37-5fc2-9731-9bbcbe31902c | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
fe84d3ed-d70a-5964-8fcc-847025e22070 | note | Verification Activity: Activity - HP
98ac70fe-30ee-551e-9118-002781a4daf9 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
52979e9c-b2b3-5105-92cd-22c52ebb3c61 | note | Verification Activity: By - ENG
8a41bb89-9b99-4473-a148-f5938a6a0a62 | signoff | AUTHORITY HOLDPOINT
81f38962-21cf-4d3b-9f87-88a8aea033a3 | checkpoint | 5.4 - Fusion Joint Compatibility
cde47c70-8a4d-51f1-b8e2-fb95cdc06c94 | note | Detail / Activity - Confirm pipe and fittings compatibility for fusion welding
57f096bf-248c-551c-ab89-c551a5080e58 | note | Acceptance / Conformance Criteria - No defects, compatible resin types per NZS/AS 2033
6659266c-a724-5742-9440-3f23cd4fd2ed | note | Standard / Specification - NZS/AS 2033:1980, Clause 4.2
c489dcc3-af79-5923-9f27-c5197cd03e19 | note | Verifying Document - Test Report
c1bec0a7-1865-565e-99c8-d89898e30310 | note | Testing Quantity Required (based from schedule qtys) - 1 per material type
4dadf331-5d68-5de0-acb0-21d16074469b | note | Verification Activity: Activity - H
1ce2bca1-f7e7-5cf6-8d67-1392263c901f | note | ○ Hold Point (Internal)
55aa8a2a-d0d1-5569-bbb1-2cc03cb4110b | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
57004c97-7fa0-583d-ab81-887df4f3d945 | note | Verification Activity: By - ENG
b5d1e079-bf93-41a3-8153-01afd5b81bd8 | section | SECTION 6.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE INSTALLATION - Excavation and Laying
d72ea243-ff61-4e12-a45d-d66e5af7a49f | checkpoint | 6.1 - Foundation Compliance
8677b390-89da-5d57-a3f3-285ce8f2aa7e | note | Detail / Activity - On Granular or Cohesive Material
8ab64cd7-8e9c-5bab-a87d-1dbd03e4f8bb | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
84f03cbd-fbde-5838-8f69-bebdc132a95a | note | (Or)
f56cadbc-ce42-5f9e-90d6-9397c1d43fd4 | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
55bc07fc-a4e9-5dd3-b961-51faf9a35773 | note | Standard / Specification - Appendix V Table 21:11
e7985170-4ff2-5bf3-a3ab-b61d48ed9de3 | note | Verifying Document - Scala/Shear test result
cbbdea8c-b1e9-53a5-b5af-8d2bee4b63f0 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
7c545703-e1d6-5916-9716-b75ad99d0fdb | note | Verification Activity: Activity - W
342f9302-e1d8-5ea1-a0c7-3a4a15cd2539 | note | ○ Review of text reports/records or other evidence of compliance
f6047151-f063-5937-92d8-0a594d8c07b6 | note | Verification Activity: By - SE
3d7ef09f-adad-4aa1-bd18-99ca9a1fc3c5 | checkpoint | 6.2 - Undercut approval
5a461622-da37-53b6-a5ad-d5bd5f31226d | note | Detail / Activity - Trench Foundation
700f2d46-0804-57bf-b713-4b263d9a401e | note | Acceptance / Conformance Criteria - 300mm Max cut
ebceba64-0d4d-5285-9f7a-369294b59b0e | note | ○ IFC Drawing Sheet 320
ec6b7f2d-685e-5605-89f0-e84d88014b19 | note | (Or)
4101dc76-df5a-5fc6-93ce-790a313d67b4 | note | ○ Engineers approval
e53ccd98-da86-5f2f-aabd-9744c307a1bc | note | Standard / Specification - IFC Drawing WST 0320. AS/NZS 2566.2/2002
b8fed546-b739-5455-899a-d3f17fa416ae | note | Verifying Document - Lab Test Report / Watermain line record
1594b11a-e6bd-5dc4-9ae9-10ae5e687fe4 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
294c3bf7-263b-539b-823f-cb87f98aee96 | note | Verification Activity: Activity - H
84f1352f-7628-5881-b67d-b971b4746e1f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
9363fe6c-712a-524a-8d0a-a80a2182bfdc | note | Verification Activity: By - SE
bc126fa0-bdae-4b9e-bc71-e1c0d89aa5d5 | checkpoint | 6.3 - Undercut Backfill Compliance
5b453df0-1ff2-5c34-8bc4-b77ab2ad405f | note | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
ac2e0f6c-2037-514c-985e-bcb675850cb0 | note | Acceptance / Conformance Criteria - Visiual Inspection
040c2d10-01b7-5ee0-8e23-2f0cb102b4d2 | note | Standard / Specification - IFC Drawing WST 0320
a17e6945-0b28-59b2-88b8-669c8e5d1376 | note | Verifying Document - Lab Test Report / Watermain line record
107219c4-4225-5e2b-9f00-09a133da4253 | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
c38681ef-1b34-5485-a83d-3a836cd39632 | note | Verification Activity: Activity - H
5d799e9a-9f0c-52bb-929f-89e0ed1d38d7 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
60323844-11c9-58e1-9fbd-b02b5197f0d5 | note | Verification Activity: By - SE
522acf17-a998-4cd4-8422-718d48dfd93c | checkpoint | 6.4 - Bedding Zone Compaction Testing
4780bae2-df41-5dc1-8002-3b43111a95be | note | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip)
5a0e6997-9c59-58bd-94e3-d4476fb05d43 | note | Acceptance / Conformance Criteria - Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench.
ded9cbc0-0ed6-56cd-9b1c-c58b772170ae | note | ○ Minimum Compaction - 85%MDD
a89e2f98-5fa7-5122-a9e8-e1a06d45850a | note | Standard / Specification - IFC Drawing 0320-1 AS/NZS 2566.2/2002
4ebe5cb8-b828-5faf-881c-17a4153aba88 | note | Verifying Document - Lab Test Report
82503a37-e488-5106-8b4b-fc5cdf0c8f4a | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 10m evenly spaced intervals.
9ee5cd20-e45b-52cd-a980-7e0810098324 | note | Verification Activity: Activity - H
34660728-09bd-5813-a7c4-cc5146fdd965 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
362ea92b-81dd-5b48-a326-2fdcfce41a59 | note | Verification Activity: By - SE
405b99f5-e1cb-4533-ab4a-9d816d503b8f | checkpoint | 6.5 - Laying of Pipes (DN560 sleeve and DN315 PE Pipe)
f37f23fd-9061-5e1c-9a5d-3d46e62cb5c1 | note | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
686da8d9-6779-53f0-a74e-852026709435 | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
d751c9a9-6784-5a5e-9ff1-d12c7ec8955b | note | Acceptance / Conformance Criteria - As Per Drawings. Facing upwards
a15f33b0-e858-5b7f-ba20-e20c78bb402b | note | Standard / Specification - PS22.7.1 C
37429ca2-382b-54c1-b751-eb8a883e8c0f | note | Verifying Document - Visual Inspection / Watermain line record
e85e564f-2a2a-5cf6-affd-ca42ff9488e6 | note | Testing Quantity Required (based from schedule qtys) - Every Line
cab58560-c863-5d30-98b3-bc0c3bd8b9a4 | note | Verification Activity: Activity - H
8653d1c2-7c33-5ba0-804f-9fd3b37e12f9 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
90b913b5-8db3-5826-b67f-697c55993bf8 | note | Verification Activity: By - SE
0b6c2d90-1367-4e97-ab11-ac0be8461969 | checkpoint | 6.6 - Pipe Installation on Curved Alignments
7574aa7b-3082-5c0b-a88d-8224a370aa80 | note | Detail / Activity - All Industry Guideline PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
555a897c-637c-5bbf-b43e-dc877ba30e80 | note | Acceptance / Conformance Criteria - AS Per POP 202
29ef9ce2-527f-59ed-ac63-bcb508c04dbf | note | Standard / Specification - PS 22.7.1 D
36d3fd72-9b66-5b82-ad01-42b62a354d88 | note | Verifying Document - Visual Inspection / Watermain line record
a3d739c6-4222-53a3-bdb1-3dbb8e1f37cb | note | Testing Quantity Required (based from schedule qtys) - Every Line
1d8ff894-7dc9-5c17-b37a-8c600fb0be9a | note | Verification Activity: Activity - M
300b9fec-5971-5080-88a7-d82b54f4d723 | note | ○ Monitor on Random Basis
6d01b540-fce7-5702-bb2f-bd27486178e4 | note | Verification Activity: By - SE
875880f0-1249-4b13-a29d-a5e37da0491b | checkpoint | 6.7 - Anchor block and to extend past edge of concrete
a2d8b4b8-b441-5c6f-9ffe-9e3a0a0e9162 | note | Detail / Activity - REFER to ANCHOR BLOCK TYPE TABLE on drawings based on pipe size
28d91e97-16ab-5c62-981a-ffd438c7c543 | note | Acceptance / Conformance Criteria - IN ACCORDANCE WITH PROJECT SPECIFICATION as per sheet 0321
4964054a-5ed7-5f58-9047-76b42f59f864 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
aeee75bd-3d8d-5a60-9447-cdf7da3cd999 | note | Verifying Document - ER APPROVAL
cfff9b7c-bdd9-515f-8b7f-6ebb1bb02ae4 | note | Testing Quantity Required (based from schedule qtys) - SH29/Camrbridge Rd
b6dd58d7-e1e3-5d4f-a3ec-3957e3e62cdf | note | Verification Activity: Activity - HP
683e1ef8-12b3-5854-b11e-95ad36014f1c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0c6c0835-d274-5a26-a47b-cee0aadf73f5 | note | Verification Activity: By - ENG
175b201e-56cc-43a9-b9b5-eea691416575 | signoff | AUTHORITY HOLDPOINT
4982db88-85df-4cbc-8f04-af7550df1726 | section | SECTION 7.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Joint and Connection
eaeb93fe-8f29-4347-b24f-5d5813df449a | checkpoint | 7.1 - Flanges
56d29cfa-3fc7-5b5e-8d6d-93f68ae8f1d5 | note | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
edefc95f-8b08-5075-81c3-c859360ead9c | note | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
4ae23fb2-5cf0-5af9-b438-b794ab37ef66 | note | Standard / Specification - PS 22.7.5 Appendix XXII
de3aec8d-9a64-5a57-bdfb-9384afc37b32 | note | Verifying Document - Visual Inspection
46ca7419-48ed-5c2b-a526-b2b7cf44dbaf | note | Testing Quantity Required (based from schedule qtys) - First flanged joint
43cfda40-fcad-5a40-86e5-42bf65504694 | note | Verification Activity: Activity - HP
eeae1975-dee0-5c9b-b650-a941567a2c99 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
03f1946f-3e58-53f9-8f80-39dbdf5e4708 | note | Verification Activity: By - ENG
da691f5b-e8f6-4352-82fc-bcb6e19e6e6c | signoff | AUTHORITY HOLDPOINT
ff77f5c1-88a5-45cc-b256-e2c17e788a00 | checkpoint | 7.2 - Bends
0afef746-e0da-50c1-9ea5-560fa33b8403 | note | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
0fc99cf3-74f1-5a81-9a0e-aba16eda3b81 | note | ○ Fitting must meets the same PN rating as the adjacent PE 100.
7e227935-a9fe-59e3-a495-d257acdaa7c5 | note | ○ Fittings must be suitable for producing the joints shown on the Drawings.
e23cfe4b-f6cc-5a93-92a5-8b7820ea02c4 | note | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
957c97ad-010b-582f-9ccc-5cd1cb059d9e | note | Standard / Specification - PS 22.4.2 Appendix XXII
82ac08c4-77c7-5a6f-acef-6e038ebda2de | note | Verifying Document - Visual Inspection
b45d4c0c-d2f6-5581-abe1-0e6bc5a90f5a | note | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
e70e7de8-a89b-5575-9cdf-6fdda51b3203 | note | Verification Activity: Activity - H
af2f5223-96f8-5b9c-ab22-651d3d7b5182 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
658b6b8a-64ec-5789-8f80-6828a9e45eff | note | Verification Activity: By - SE
a780633b-8664-4505-9378-1df627ab8211 | section | SECTION 8.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Butt-Fusion Welding
d70e5575-7db9-47ac-b517-12ad2c2ed8aa | checkpoint | 8.1 - Butt-Fusion Construction weld test
d7d12123-6ece-53e7-86f4-986bb4d06b5d | note | Detail / Activity - Test at least two welds from the first 50 welds.
54e62ba5-ec61-5767-8fef-65940b14deba | note | ○ One of the welds to be selected by the Engineer for satisfactory result.
a5da78aa-0c76-5294-9b61-2973714a93ea | note | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
1184688f-5876-54d2-92f5-c4d48dac9f83 | note | ○ 95% tensile strength; welds aligned
22bceb8a-2d52-58ff-8199-2c77c44c1d1b | note | Standard / Specification - PS- 22.9.6 (a) (iv)
b4809fce-3fc9-5b25-bc21-8aa957da7153 | note | Verifying Document - Test report
5ccba314-f078-585f-97e2-f82238d4b4c7 | note | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
8c2b695c-9292-5e31-81ab-b0985179f16f | note | Verification Activity: Activity - HP
eabd2bae-2691-5c4b-ab43-4b46cc2d24c6 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5af94b3b-ad07-5a41-a487-8e74316dc599 | note | Verification Activity: By - ENG
22257f33-c0cb-461b-b93e-eb774f0bf6ac | signoff | AUTHORITY HOLDPOINT
0bffa531-7116-4b06-bf8f-7aee138eed5a | checkpoint | 8.2 - Butt-Fusion Welding
c1ef4422-5ae5-5768-b2b5-df258c1a9d14 | note | Detail / Activity - Use only semi-automatic or automatic welding machines.
f6892e00-27b7-5e53-a8cf-d1ffedf0abe8 | note | ○ Maintain a site record for all butt-fusion welds.
23e5b1b0-a14f-55f8-afcc-b3502026d415 | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
68f6db7c-797b-50a0-8c8d-f46bb47519e0 | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP). WMS Report
be1776c7-2e97-57b5-b557-58b512fd1600 | note | Standard / Specification - Appendix XXII PS 22.9.4 C
4b700ed1-f693-50aa-b6bb-c8bc1b3fbd91 | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report
63c59913-94cc-5218-94eb-1351ab547f4c | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
1b81e536-09b5-5154-a86c-630e7a9d8ea5 | note | Verification Activity: Activity - HP
c53dcd6e-7f27-5523-963f-d2eb0a023c30 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ec819f14-71b1-5cb4-a586-dd97a2e47750 | note | Verification Activity: By - ENG
883f0caf-2265-42a4-85bd-a5aa8129c5a2 | signoff | AUTHORITY HOLDPOINT
37bcaabc-eb99-4902-aed9-0afb29bf9200 | checkpoint | 8.3 - Survey
77e9cefb-c5f0-5b3f-83a7-ef3965c7ff26 | note | Detail / Activity - Inspection of Pipeline Inverts
f852623f-3202-563a-ab84-7ff9523764aa | note | Acceptance / Conformance Criteria - Vertical design Setout:
201d44b9-25a8-513c-8cdb-c4f73692ca1b | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
2ae168bc-b084-5784-8641-af10494819db | note | ○ Pipes > 1% grade: +/- 20mm variance
7f5dd2b0-65f1-533d-bc78-763b7bfbaf13 | note | ○ Horizontal design Setout: +/-30mm variance
cb306757-bfd7-5034-8a3f-a6ec86184009 | note | Standard / Specification - PS- 21.7.6 Table 21.15
78458985-9cb2-52fb-ab4e-8806e0a20d47 | note | Verifying Document - Survey Data / As-built record
b5329ecb-630f-572e-8e63-6e7629b3d604 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
b4a5e2f7-6250-5d68-8fef-9540c9ad669a | note | Verification Activity: Activity - H
82679697-f410-58b4-87c9-c1e038f96fe8 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
759805e1-0b19-5a59-b084-0c489b226dee | note | Verification Activity: By - SE
37356498-c86e-4d6e-b3e2-5ba57f03d4b9 | checkpoint | 8.4 - Photograph of Each Weld
25434d90-cd45-55ef-a569-ed43f02c15e3 | note | Detail / Activity - Take sharply focused photo while clamped
af59830c-088f-576c-a0fc-65c59317fa66 | note | Acceptance / Conformance Criteria - Unique weld identifier visible
65d749d9-9a28-5d98-9c07-e21f657d44b8 | note | Standard / Specification - N/A
11868ae4-2684-511a-84bf-270e5bf50308 | note | Verifying Document - Weld Records; Photos
7ce06ace-b591-5c5d-8c2f-63b9d2f4cada | note | Testing Quantity Required (based from schedule qtys) - Each weld
e1d3828a-3176-5563-983b-984fc2faa318 | note | Verification Activity: Activity - I
6efa5236-ce1d-5bee-bcbe-ce2b13ffe8ae | note | ○ Formal inspection activity to be undertaken and recorded.
5f2f19f4-8109-5ae7-8882-0dd08fcb1d8d | note | Verification Activity: By - SUB
fe778ce6-1b46-4b7e-8fca-962a1f7bd0dd | checkpoint | 8.5 - Weld Treatment for Corrosion Resistance
2f2170a0-2422-5bc9-868c-76e375bec5d3 | note | Detail / Activity - Treat welded areas to restore corrosion resistance
aefbb4f7-0b72-5185-a2d5-cf12e1af73df | note | Acceptance / Conformance Criteria - Treated weld areas
6db29925-55d9-5775-824b-d6701c65b931 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
0f9a212a-3218-5802-857a-38ac3e9932a9 | note | Verifying Document - QA Documents from Welders
66276b87-16d1-57bb-b355-1b459bf85ed2 | note | Testing Quantity Required (based from schedule qtys) - Each weld
1cd74f68-8170-5959-a4bf-464de2918966 | note | Verification Activity: Activity - W
7747e5e8-ffaf-563a-878f-f41bf618d948 | note | ○ Review of text reports/records or other evidence of compliance
38ff89a7-6494-50fc-8aec-8337d2ad2952 | note | Verification Activity: By - ENG
bdab5316-7f4a-40cf-98bf-281718041939 | section | SECTION 9.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Backfill
4914cc5e-3ea0-44c2-9d79-5a0aa504ef3b | checkpoint | 9.1 - Emebment Zone - (Side Haunch Overlay)
4d8a4730-326b-581c-ba02-2a9096947547 | note | Detail / Activity - Granular Sand backfill Compacted in 200mm Layers.
8b12460c-5920-54ab-9c0b-7be687ac7231 | note | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays .
b57d8c7b-61c5-554a-9bfc-034ed89199dd | note | ○ NDM BS to be Carried Out
5d191cab-fa3c-5eca-9ca3-06ab51cd990c | note | Acceptance / Conformance Criteria - In 200mm layers.
a7805833-4871-5bb7-9574-015cb2268fd3 | note | ○ More than 85% of MDD.
2d2f8394-c574-5bb6-a728-01330dfd1e8a | note | Standard / Specification - IFC Drawing 0320-1
d7c55e1a-2b31-5f6d-9a21-29665495d1b0 | note | Verifying Document - Lab Report / Watermain line record
083aa143-79f5-5cb0-a610-d3133b16fddd | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals. 200mm lift
c38f519a-de60-5242-9781-0af84eab8ab8 | note | Verification Activity: Activity - H
e2ce7199-4f6b-524e-9fee-6843a393e219 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
aa81d011-e1c1-5728-aab3-25d3e999e72f | note | Verification Activity: By - SE
6324adf0-4045-427c-af0d-de7618bceb9b | checkpoint | 9.2 - Pipe Markers
639bb4de-823c-59b0-a6cf-3525eedfb98b | note | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
44f2c12e-fbef-51be-89f0-0bdee8bd266c | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
70ea2c77-03fa-5deb-b03d-7626987243a3 | note | Acceptance / Conformance Criteria - AS Per Drawings.
edd0b3e7-9d74-57ed-9253-9b5854a56d33 | note | Standard / Specification - PS 22.7.3 a
2f3e6fe4-bb9d-5e42-aa25-f93858d0cc73 | note | Verifying Document - Visual Inspection / Watermain line record
c9233763-40e5-536f-9368-fbf76cc349cb | note | Testing Quantity Required (based from schedule qtys) - Every Line
d07a914f-6467-5541-a2a5-4947ba659c74 | note | Verification Activity: Activity - H
fdb36d79-6a27-54b9-bc7e-d205f0eb306a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
67499e2a-5b3b-5768-a18a-a644d8a77cd5 | note | Verification Activity: By - SE
38ce8c62-e614-4f14-a51c-245403e72f1e | checkpoint | 9.3 - Backfill Compaction Testing
80a3ad99-1e71-5d80-a4d0-c8ba6d7e37a3 | note | Detail / Activity - GAP65/AP65 Backfill Compacted in 200mm Layers.
1f47a28d-a72d-589d-b0c5-6c6a3c3f897b | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
a4486c1a-bed5-57ce-a9c1-85dbe6627320 | note | Acceptance / Conformance Criteria - GAP65/AP65or site won material Backfill Compacted in 200mm layers.
a9cbfb6a-8626-5493-848c-273ae6998a9d | note | Testing to be completed on maximum 200mm lifts of backfill.
02dce6fa-4138-5d60-be67-c62244a18ec6 | note | ○ 95% NDM on Shared and Carriageway.
394910b8-3533-5966-b1fe-9305c90bf918 | note | OR
32f91748-1975-5e7a-afd0-7a9b01fa33db | note | ○ 28% CIV
aebd543e-09c9-52a6-a08d-c2068c5aa5a2 | note | For site won min >60kpa
de37c3b2-9319-5851-b0c0-5a3f4c24139d | note | ○ Ave > 80kpa
af9962f2-183f-5297-9efa-ee3e8602e099 | note | Standard / Specification - PS- 22.13.5 NDM Standerd 25832, NZS 4402 Test 4.1.3, IFC Drawing 0320-1
8e93d356-6866-5655-8ac1-fff7817755cb | note | Verifying Document - Lab Report / Watermain line record
c66e533b-61cd-59fd-a13c-335e37e1551f | note | Testing Quantity Required (based from schedule qtys) - As per Specification. One test per 10m evenly spaced intervals.
0ad460f0-31a9-55e0-856a-a47ebac61ae3 | note | Verification Activity: Activity - H
bc575406-7b32-528c-a6f9-1cb67d48ff4e | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
26dedc63-8f4d-582d-8f49-2654ebb12edd | note | Verification Activity: By - SE
e0129b07-5c1f-482e-a400-fb1189ed64b5 | section | SECTION 10.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Inspection
44bb5cb1-1078-44b0-b83c-9407cd1b753c | checkpoint | 10.1 - Pipe Inspection
4f18281d-212b-52ad-a9c8-f1b1bddbaa2b | note | Detail / Activity - Inspection of Drainage line
8d4ce086-f959-576e-a3bf-b8dc55114af3 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
20b7d407-f199-5535-aaba-58e4d4e80e22 | note | Standard / Specification - Internal
e56959a7-069f-520a-ac5b-e591883b3b40 | note | Verifying Document - Watermain line record
dce234b8-bbc5-51af-a9c9-c68a2ac70e2c | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
6cf1535d-557e-585e-8d52-440865f1d6b1 | note | Verification Activity: Activity - I
a807901d-59ad-523a-9549-03caf6818f81 | note | ○ Formal inspection activity to be undertaken and recorded.
0a06217d-ec7a-5574-9b30-1d9c5b1a92de | note | Verification Activity: By - SE
dfaec2f7-5083-4288-9bb0-5d759f2fbeed | section | SECTION 11.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE TESTING
ccf9f189-668b-4bc7-9df9-f4b159f8131c | checkpoint | 11.1 - Pressure Acceptance Testing
a4011af2-5d77-5561-94c5-f936cf18634a | note | Detail / Activity - Backfill/cover with embedment before testing
bae9afe3-d8c4-5fee-98c9-b4f34dcb15c4 | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
d2ee5dcf-54d2-52ca-9970-60d4701582fa | note | Acceptance / Conformance Criteria - Potable Watermain Pipelines – 1250kPa
594db359-ebc7-54f8-8caf-75d4ed64aec2 | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
8c8e92f9-48e2-5f50-b8c3-86cbde6fca6d | note | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
4a40165f-0bd6-5c36-a765-fc1c8cf0e289 | note | Verifying Document - Test Report. Pressure Log in.csv or .xlsx format
4166706d-f7c4-52c6-badc-2dbfade8ff58 | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
0a8ea45f-70c6-513e-9042-40cbd69d8281 | note | Verification Activity: Activity - HP
b4562028-1ce3-5656-b562-006838954f4f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b1ca5b00-6a7a-538b-8fb1-b7d93e3c91e4 | note | Verification Activity: By - ENG
6bb680ab-609f-4b99-844c-19f530e247dd | signoff | AUTHORITY HOLDPOINT
c199ac3f-daaa-4657-8040-807e5222a50d | checkpoint | 11.2 - Swab New PE Watermain
88fe84f0-a837-5430-8e24-242ae2b9dccb | note | Detail / Activity - Swab to remove debris and air
6a1ceef4-8ea2-56aa-8685-0d75a83c9d88 | note | Acceptance / Conformance Criteria - Water running clear & removed entrapped air
8e31933a-df31-5605-b7f0-b5259f200a6c | note | Standard / Specification - TCC IDC TS-7
dc439ac8-2252-56ee-aaeb-ab7de090bc61 | note | Verifying Document - Swabbing Check Sheet
db53759b-7ceb-5053-b892-5438ebbf5d32 | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed
d9b293eb-0f89-5c56-9c1e-23874d85de1f | note | Verification Activity: Activity - H
e6a9cfaf-98f0-5d56-837f-674c12022f00 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5b4c286a-ce8d-5e89-86bc-5c96e63cbf80 | note | Verification Activity: By - SUP/SE
195a876f-4bd1-4445-959f-3c608f1ec998 | checkpoint | 11.3 - Pressure Test New PE Watermain
3c6ba968-e20b-5412-a2d9-1cb7be36ea6e | note | Detail / Activity - Conduct pressure test. Due to not commissioning the pipe until later in the project, CB will complete there own pressure testing upon installation of the pipe, with the full pressure testing and chlorination to be completed once the pipe is ready to be commissioned.
75cc8e9c-631d-5c27-a4ae-fa27fea57689 | note | Acceptance / Conformance Criteria - No leaks, no failure of any pipe, fitting or other pipeline component.
34d1944a-9eae-5731-aaeb-b43c9185d15d | note | Standard / Specification - TCC IDC TS-7.1c Pressure Rebound Test Method; TS-7.1a Constant Pressure Test Method
17dfba34-e195-57fe-b939-da72722abaf9 | note | Verifying Document - TS-7.1a/c Pressure Test Method (Test Report)
6db06016-1f66-5836-8451-acd659decf88 | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed & swabbing passed
0b7eb555-7d31-5239-aede-9313622a1813 | note | Verification Activity: Activity - H
edf40fd7-2e57-5649-819c-ed8311acd7b1 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
670c4529-7fb2-5555-8066-277b337e7360 | note | Verification Activity: By - SUP/SE
86692719-401b-40ff-a28e-c5d120db6b59 | checkpoint | 11.4 - Chlorinate New PE Watermain
954f4667-3ced-5d94-950c-58bae0e9cc1c | note | Detail / Activity - Chlorinate watermain
f3f1e69b-88d4-54ac-b55d-1831d25df68c | note | Acceptance / Conformance Criteria - 5+ pH on chlorine tester
3ad4b8cc-9cba-5077-b1fb-b893b7c01a89 | note | Standard / Specification - TCC IDC IT-7.4.1 Disinfection Procedure
e23966d3-ec2d-52a5-8330-94f0d1fe1e45 | note | Verifying Document - Picture; Signed Chlorination Check Sheet
80851c5e-6f89-5d41-985e-440af836af65 | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed & pressure test passed
d142c98a-518d-59f6-9510-11da2a2a60b2 | note | Verification Activity: Activity - H
fbcd07e4-79ed-5825-a565-c2c3504b6389 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c3ce19a2-34bd-584d-94ed-b2dcce86fa97 | note | Verification Activity: By - SUP/SE
89681b2e-9899-46a0-b09a-3644dcb6f462 | checkpoint | 11.5 - E. Coli Test New PE Watermain
c05aee57-3262-5445-ab96-40b9d9d1943f | note | Detail / Activity - Test for bacterial contamination
eb093b2a-9505-5d02-b160-c85a7224718d | note | Acceptance / Conformance Criteria - <1 E. coli; <1 Coliforms
2b2de0c5-0c99-5ca7-b29e-6ebb90e9f274 | note | Standard / Specification - TCC IDC IT-7.5 E. coli Sampling
de95b9a2-c1e6-510b-89b6-7756e38a6b39 | note | Verifying Document - E. coli Test Report
a5cf0c6a-999f-5ee1-a69b-377317824a04 | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed & chlorine test passed
539fe0b3-6ed9-5ce2-a609-1bc776349fa2 | note | Verification Activity: Activity - H
9ace7ef1-5484-5efb-a04e-b4cc419a0edd | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5e6fc4c8-fd57-52bf-8e5c-caf634273d68 | note | Verification Activity: By - SUP/SE
fd8a185c-a955-4cf6-8531-9ee14eeb7bc7 | section | SECTION 12.0 - CONSTRUCTION ACTIVITY - WATERMAIN Manhole installation
b95ae567-a4a7-4fd7-a8fa-afcbc5e70102 | checkpoint | 12.1 - Foundation Compliance
b91e7241-2a69-5ffd-bad4-7f381ccb7374 | note | Detail / Activity - On Granular or Cohesive Material
2a0304ed-51ae-54b6-b0a6-08fe3ecd4d1f | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
e9edb238-2c01-5e5b-8b67-aa134c7444f1 | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
3bcf8b2e-4fa2-5aaf-af97-af75a0dbae9a | note | Standard / Specification - Appendix V Table 21:11
a08561b6-1c3a-5a89-8a15-233e03c4da8d | note | Verifying Document - Shear vane or Scala test result
295f6f7c-97ee-5534-b77b-f55eb51deb8c | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
a1057712-3eae-5502-a96f-cac0847991d0 | note | Verification Activity: Activity - W
9ab2609e-3994-5de1-a3e0-aa712546b49d | note | ○ Review of text reports/records or other evidence of compliance
b2f7f2d5-5f81-567d-a8b4-ff695a5b0271 | note | Verification Activity: By - SE
bfc6e880-f856-4f03-bd83-32c6f63c2aee | checkpoint | 12.2 - Undercut approval
56779193-6fef-5c45-88fb-6e5f54608dfd | note | Detail / Activity - On Subgrade
9ff4e71b-96e3-5078-8a75-ec7045cab767 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
3f3ffb78-6e69-5a12-a2e9-c568ecba4744 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
9a1c18a0-d54b-5528-8af0-09913c79827c | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
31a72c0b-03e0-55a0-a228-3ed65da83d47 | note | Standard / Specification - Table 21.5
7b9099b6-0cc0-574b-8e55-8ad007225365 | note | Verifying Document - Lab Test Report
0f001139-406c-5d20-aad3-2931a4077c30 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
6aba8afd-e26d-50fa-9479-5bb74e0764fb | note | Verification Activity: Activity - HP
11d9442f-0a91-5840-959b-5fd98dc4561b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7eaa4e74-e604-5922-a5a3-68117749185f | note | Verification Activity: By - ENG
e25f0fa8-065b-4a90-b9f0-0ed8166230aa | signoff | AUTHORITY HOLDPOINT
05e6a79e-89f6-4800-b25a-0406826d283e | checkpoint | 12.3 - Undercut Backfill Compliance AP65
e2aebe8b-63f3-520a-bf58-f28423091bfa | note | Detail / Activity - On Granular Material
f7038bfd-db27-5a08-90b4-a044def37147 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
6f68f920-e2cd-51c2-9420-e5c9c79481e0 | note | OR
c5eca947-7bfb-5cb4-bfb4-960ec43bbb7d | note | ○ Clegg 25% CIV
edbfb074-90b0-5c24-b955-63477251f479 | note | Standard / Specification - PS- 16.5.12
4bd3571d-ec37-5019-9a15-46c54115e5eb | note | Verifying Document - Lab Test Report
5bd94b70-bd51-5ad5-8405-7a9ef336cbc6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
b1cc29e8-6bee-5472-abb4-4c23720ec571 | note | Verification Activity: Activity - H
4886ea56-2315-58b0-8e8d-d0f4f1ec8eca | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
afffe11f-c800-57e8-b0e2-9e732c922279 | note | Verification Activity: By - SE
2185d6b6-4c23-486f-a42b-130a4d6a0d88 | checkpoint | 12.4 - Bedding Compaction Testing AP65
2ceb7ca8-3dc2-56d4-9c53-8db96dd3eded | note | Detail / Activity - On Granular Material
a910e3b5-c564-5c50-b8ab-d0a4b850979c | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
43762ae2-7acb-5000-a927-9b3ad8e2c1f5 | note | OR
ab0361fa-e8a2-50d1-bff8-ef8bf2310cee | note | ○ Clegg 25% CIV
fdb81124-2cbe-505d-9d93-9e3c4f54d9d4 | note | Standard / Specification - PS- 16.5.12, PS- 21.6.11
e9eb948d-86f3-5fae-a912-6dc95e01cea0 | note | Verifying Document - Lab Test Report
afa116fb-bcd3-56d7-8212-53394c5c3143 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
ac952aec-ecc3-57b1-8e84-e46e492715b4 | note | Verification Activity: Activity - H
a2e1d6b3-1c6d-56f0-a076-b628aae30602 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
58f0a491-0f9a-526f-994b-5e9cc62b69e0 | note | Verification Activity: By - SE
60719da6-d5cb-440e-ad6d-0c5cded2386d | checkpoint | 12.5 - Survey
ee48c4df-3d1a-55ef-8ce0-f26563f54cb8 | note | Detail / Activity - Inspection of Structure
72ba3650-d0e4-537b-8cce-03f61cfa9e4d | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
d5af1ba5-627c-5f26-a5cd-9cce82024e2b | note | Standard / Specification - PS- 21.7.6
f9b226f2-dc3c-514e-a8c9-23277a826514 | note | Verifying Document - Survey Data
1521d80f-c107-5662-aa0e-6afad9ab9db6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
7573a7a4-1990-53f9-aba2-98c881bde53a | note | Verification Activity: Activity - H
840d2649-dc5f-5fd7-9b50-ef451f8d81be | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
73805e02-0eeb-5bb9-8e2e-93bbf54abbb6 | note | Verification Activity: By - SV
add6d05d-c754-4397-b316-751bb7e0a6ab | checkpoint | 12.6 - Sidefill Compaction Testing
f11d6a6c-e4d4-5da9-98dd-b114102eb82b | note | Detail / Activity - From the bedding layer to the overlay layer of pipe.
bfcfb708-6a7c-51bf-b565-d53fe16c17d5 | note | Acceptance / Conformance Criteria - AP20/GAP20
7a3e4b74-2d9e-55f9-9c95-51888219438c | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
2e07b942-9c2f-545d-88b9-3985df1904f6 | note | ○ AP20/19mm chip
8269c4e4-c79d-5bd2-a475-f40805355897 | note | Standard / Specification - PS- Table 21.12
de7a0ff1-285b-526e-86fc-fa1298d08ac9 | note | Verifying Document - Lab Test Report
47d09ad6-f515-567e-97e3-cd71f9a4ef7d | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
d4482570-c069-5e01-95bb-15966214f3b4 | note | Verification Activity: Activity - H
c7c84204-46fe-55a2-9fbe-b7386859ff24 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0fffb9d5-0e43-5be1-a8d1-b14bbe8cb4b0 | note | Verification Activity: By - SE
491419db-d409-4648-b758-1c1269b2b341 | checkpoint | 12.7 - Backfill Compaction Testing
832e0f92-6b3f-5392-a7b8-0c38e2ae0884 | note | Detail / Activity - From Overlay layer to the subgrade layer
e8f48611-0f88-5136-b284-694bbad6e8ea | note | Acceptance / Conformance Criteria - AP65
65e81299-dbe6-53b7-9412-24cf7a433623 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
2c54455b-7b75-5de1-81d4-5a240aeea987 | note | ○ AP65-Clegg28%CIV
a3192d58-f9a6-5d59-a8a5-0dd0ee8fdf1f | note | Standard / Specification - PS- 16.5.12
cb794606-d2dd-5d8d-bb6c-0750c5a415e3 | note | Verifying Document - Lab Test Report
6fea5269-826a-5ff2-9561-5447e8ea2b6c | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
cbf5158e-2683-567a-a3a2-0b3ff7e2a775 | note | Verification Activity: Activity - H
56bf8b88-df11-58f8-83fa-a14a4938da9f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e149e991-a908-5429-85d6-5b4ad499545d | note | Verification Activity: By - SE
5881d6f3-5153-4716-93d4-a3f361ae9a92 | checkpoint | 12.8 - Manhole
3fe6ec4f-bfb6-513d-a4e5-213534892d1f | note | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
c110f734-84d9-5dac-ab92-3e6c69de0974 | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
bd24d111-84b1-5f39-ae6d-0b712c59f0fb | note | Standard / Specification - Design Drawings 232735.02-WSP-DR-WAT
2da1e192-ac2c-5657-9e0c-9fa7fd424b36 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019) Manhole checksheet
0e3bda97-427c-5fd6-8999-4a7c2a7504e5 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site/ per manhole
b1775513-c8a1-5f38-bb19-eaf7cbb2102f | note | Verification Activity: Activity - H
6c266d03-9368-5c71-99df-601eea1b5708 | note | ○ Hold Point (Internal)
0338e94d-6e98-5fce-baf9-bc880995d6e6 | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
0c290643-b59d-5426-9d98-9fbd9fb96a60 | note | Verification Activity: By - PE/SE
3c5eda43-ea74-4f82-acca-a855d28b5f26 | checkpoint | 12.9 - Installation of concrete chamber for Air Valves
8cd52d47-42c6-5fbe-ae53-33db46aedfde | note | Detail / Activity - NEW 1200mmØ PRECAST CONCRETE
e594b11a-c80a-54e1-9862-a1a2f67190b3 | note | ○ MANHOLE Concrete cut a hole in the base of the concrete chamber to a suitable size as to fit the pipelines. CONTRACTOR TO FORM HOLE IN
cd610f59-557b-5ef6-9ed9-f4dd0abe2f6e | note | ○ CONCRETE CHAMBER WALL. HOLE TO BE SIZED JUST ENOUGH FOR FITTING SIZE, REPAIRED WITH SIKADUR 42
b2668f4e-344a-5930-9596-9a668888c37c | note | ○ OR EQUIVALENT NON-SHRINK GROUTand 2 layers of Malthoid placed arouind pipe3
acb0a3fb-e1a3-5852-86fb-2bf70a0de75f | note | Acceptance / Conformance Criteria - TYPICAL IN-LINE DN50 AIR VALVE INSTALLATION as per drawings
3c6c9e35-97ed-5f71-a96b-bcadbe589308 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
344c3fcd-82d1-5225-960e-d5b6e4b8f8b0 | note | Verifying Document - MANHOLE CHECKSHEET
45e69663-6f03-5283-abe8-982298276713 | note | Testing Quantity Required (based from schedule qtys) - Per manhole
7919ea51-29f2-566f-aa96-0b7a68a5565d | note | Verification Activity: Activity - I
393b7ea3-9358-501d-9731-e3a9c139a102 | note | ○ Formal inspection activity to be undertaken and recorded.
4685dcaa-7347-5c04-9051-47753de58104 | note | Verification Activity: By - ENG
bc38df96-9554-4c20-94bb-fd244d936c22 | checkpoint | 12.10 - Installation of manhole vent offset in the berm
0915615a-d4bf-52a4-835d-57800844b29f | note | Detail / Activity - 50mmØ GALVANISED STEEL VENT - TO BE SET BACK IN BERM. LOCATION IN BERM TO BE DETERMINED ON SITE
67c40c17-3d75-54c8-890a-7d68487e0647 | note | Acceptance / Conformance Criteria - To be determined on site
aa25f77f-f9a3-523d-9912-5231ce79c90d | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
e9fa4aa1-f3b3-5220-9cfd-769746e04073 | note | Verifying Document - MANHOLE CHECKSHEET
4fc80bef-8102-5fc0-95ae-556268b15014 | note | Testing Quantity Required (based from schedule qtys) - Per manhole
95e617ce-dcff-5f8c-9036-6f10cee7c89c | note | Verification Activity: Activity - I
5802b736-2c36-5a56-ac1d-71c91aae6ead | note | ○ Formal inspection activity to be undertaken and recorded.
8786d296-a1af-59cb-bd39-fe6b735795fb | note | Verification Activity: By - SE
cbcb4af5-7879-45cc-9979-3ddce4b09264 | checkpoint | 12.11 - Deep drainage sump installation
1059d271-3903-5024-90ba-b19b59106556 | note | Detail / Activity - 150 x 150 x 100mm DEEP DRAINAGE SUMP FITTED WITH DN80 PVC PIPE PIECE, 300mm LONG AND COVER GRATE
44adaf0f-ac4e-5014-9c8b-4fb0ec771b1e | note | Acceptance / Conformance Criteria - As per drawings
5c9ef146-1f02-5b29-aae8-3e168b6eb577 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
7b20bdbb-b9e9-522e-b8b1-b69b891f02a8 | note | Verifying Document - MANHOLE CHECKSHEET
66e7cd98-aade-5ea5-9b71-f2f023431f09 | note | Testing Quantity Required (based from schedule qtys) - Per manhole
e28e35d0-27e6-5c55-b239-bedaeb5d3618 | note | Verification Activity: Activity - I
053dbda4-4144-5dcf-b55e-213b1e7267a3 | note | ○ Formal inspection activity to be undertaken and recorded.
0a0e8879-2fa6-5c57-b7e8-d6a8a0b28584 | note | Verification Activity: By - SE
9eb0656e-496c-49d0-8e23-16e474763679 | checkpoint | 12.12 - 25MPa CONCRETE THICKENING, Corbels for the pipe entries/exiits
a12ff6ad-0a38-52e4-88c1-5c60af83c02c | note | Detail / Activity - YD12 REINFORCING STARTER BARS DRILLED 50mm INTO MANHOLE WALL AND EPOXY GLUED
f00d55c5-7c64-5164-b66b-9947a5ea295e | note | Acceptance / Conformance Criteria - As per drawings
b222b3a1-d11c-5bc4-af89-4d9c8003d535 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
f77463b2-9ee3-559b-a213-6cc6e17c4f8c | note | Verifying Document - MANHOLE CHECKSHEET
7801a940-9ee9-5728-9b98-89a344631565 | note | Testing Quantity Required (based from schedule qtys) - Per manhole
b4b2d199-54d0-56db-8813-8447cf55cee6 | note | Verification Activity: Activity - I
ca8fac09-1beb-5fcf-a8c3-4a81bb76883e | note | ○ Formal inspection activity to be undertaken and recorded.
ceab1505-6602-51f7-9785-584f0fb69728 | note | Verification Activity: By - ENG
2a0f005f-cedd-44dc-a066-209809d06386 | checkpoint | 12.13 - Installation of heavy duty chamber lid and backfill of manhole
a8668897-ac9f-5417-85cd-dc69f14771cb | note | Detail / Activity - Install the chamber lid onto the concrete chamber cover and frame as per the manufacturers specifications and backfill.
eced7048-4490-5dca-9013-478d79ddb89b | note | Acceptance / Conformance Criteria - As per drawings
dc57bcf7-bee5-5971-b741-5c7c994a63ff | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
fd5bef8f-6160-503a-9341-41569dbdbb04 | note | Verifying Document - MANHOLE CHECKSHEET
45a1aad5-2ede-5ab5-bc30-2ca98b498297 | note | Testing Quantity Required (based from schedule qtys) - Per manhole
a6f7d445-d0ad-5ef7-9dc7-b9d09fc4bc0f | note | Verification Activity: Activity - I
7dc36772-6271-5881-9f21-3664fbf51510 | note | ○ Formal inspection activity to be undertaken and recorded.
549e4c72-703a-5864-81f7-f8bf11512c12 | note | Verification Activity: By - SE
9ba4ae5f-e1ee-43c3-991e-5df2039aae60 | checkpoint | 12.14 - MH joints inspection
ff8a38f2-c0ac-557e-8e97-84e286de38be | note | Detail / Activity - Inspection of joints
94eaecd2-b1ac-567f-9101-3b5206803203 | note | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
9f637638-d1af-508f-a08f-5d38ce7020b1 | note | Standard / Specification - PS 22.7.10
3fa87883-4a47-5321-81ed-5f64e0d29f79 | note | Verifying Document - Visual inspection
06d2eb5c-58d5-55b5-9a34-db155c664855 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
7e0d7101-6f70-5722-ac87-068188714e43 | note | Verification Activity: Activity - HP
e0969cde-f17a-5940-93c2-02d8e303c41f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
fed4366d-69b7-58de-9f4e-741700f91226 | note | Verification Activity: By - ENG
dd81a206-b28b-484f-b5da-9b75b09cee38 | signoff | AUTHORITY HOLDPOINT
87633412-be84-462f-a167-74c6f559a2f4 | checkpoint | 12.15 - Inspection
f249f770-87a2-5577-82e3-7a1c315005c0 | note | Detail / Activity - Inspection of Structure
3bac29d4-d9c5-5a77-8de6-05e2aec1a7e7 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
41bd8233-c584-58ad-9b2e-d3c167280f06 | note | Standard / Specification - PS- 21.6.11
3adb37dc-ae96-5499-b939-35252debad27 | note | Verifying Document - Manhole Record
16da8dd5-b5b6-55f1-8951-774fe244b51e | note | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole
3c77ae56-76bf-557d-883f-88d04cd4e8d9 | note | Verification Activity: Activity - I
c57264ff-0ecf-5c7e-88db-5f8ccff28771 | note | ○ Formal inspection activity to be undertaken and recorded.
033a9ce2-09f2-5a68-86b4-6f8b4f22130b | note | Verification Activity: By - SE
9b725fe4-c020-4bc7-bf8c-297a7dc0b3e1 | checkpoint | 12.16 - Plumb
2e6d8a22-c095-58dd-a10a-9bb1afb9ac1a | note | Detail / Activity - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
2cd2d326-4727-5a76-95d4-72a05c8fb315 | note | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
cd894951-9e3d-5b7f-991b-41c618fe55ad | note | Standard / Specification - PS-22.7.10
5bef7a9b-dd00-5251-9a81-0506bcffff01 | note | Verifying Document - Survey Data
2d055ea3-cf44-5f6e-bb82-467a40ec0c85 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
2bfed878-a4b3-55e0-85ad-d9bb66ae222c | note | Verification Activity: Activity - H
25ca764b-0670-577e-87a9-7647fa230794 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0e420226-f4b0-511d-817d-a8870be85b56 | note | Verification Activity: By - SV
02d25b75-e355-4113-af4f-f8c1c9b08b45 | checkpoint | 12.17 - Step Rungs
4998f2aa-b7cc-560a-9854-302c35190f53 | note | Detail / Activity - Step rungs evenly spaced at nominal 300mm vertical intervals
14c66418-5445-5377-9463-16a943376563 | note | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
d5514201-c776-5e86-8c93-014213a56c75 | note | Standard / Specification - PS-22.7.11
76e9b7b1-5ad4-5506-870d-4c650e518ad6 | note | Verifying Document - Visual inspection
659f125e-e14d-5bba-9abe-a49efcc40220 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
7fe2bac2-e390-53b5-a2d4-e19171fccd57 | note | Verification Activity: Activity - H
4536f083-1687-55cd-afb1-dc35633fca28 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e22041d8-46b6-5940-bc36-b26fae6b6ba6 | note | Verification Activity: By - SE
c491c5d1-15cd-4342-9be0-e249ac759faa | section | SECTION 13.0 - CONSTRUCTION ACTIVITY - AIR VALVES
74159979-097b-45a8-a148-0cbee0dcfd22 | checkpoint | 13.1 - Valves/Fittings
8022c0bc-f87a-546a-b697-c7589645eda5 | note | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
d3dd7a8c-cc40-5cf1-a6fa-cb76e634bc62 | note | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
49bc6f69-6eae-5340-9733-a24bb6ef4d58 | note | ○ Air valve 10 & 11 is DN50 size.
67c332d4-1a30-515d-805b-cbd0b9b315d4 | note | Standard / Specification - PS-22.4.2, PS 22.5.10
2574248e-574e-5d27-ab58-9259b917fc24 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
a1b92f12-acf2-559a-b343-d6d016a02a3e | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
1964775b-e9ae-52d6-bec6-5aa81fa390bd | note | Verification Activity: Activity - H
5a6a6c1a-fccc-5dfe-ae38-f291bdb83915 | note | ○ Hold Point (Internal)
5a807b2b-361e-5229-a828-a9abbdcb8b0b | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
495e03d5-fb48-52d1-aba0-72d987618b39 | note | Verification Activity: By - PE/SE
fe6cb000-a8a0-4e15-acf3-e9e905c89ea6 | checkpoint | 13.2 - Installation of Isolation Valve
7e90c39e-5720-5d38-8e16-182c1375389a | note | Detail / Activity - Verify installation per manufacturer’s instructions
58356182-ea8b-530d-96ce-65cb5c8151b4 | note | Acceptance / Conformance Criteria - Installed as per manufacturer’s instructions. Project Specifications
9dd72c92-291b-5d27-b661-19d484dab089 | note | Standard / Specification - PS-22.4.2, PS 22.5.10
603a79f0-915a-5b45-a729-e76db7ba0421 | note | Verifying Document - Air Valve & Isolation Valve Check Sheet
f7f8ed06-4b77-5115-b476-056e5f44a3cf | note | Testing Quantity Required (based from schedule qtys) - Each isolation valve
d5f690fb-56e1-5b77-9829-853cf0c21420 | note | Verification Activity: Activity - I
6ea2d7fc-b9b6-5631-8111-7ffd335756f1 | note | ○ Formal inspection activity to be undertaken and recorded.
d0e3c733-f6aa-5f11-97db-dbafb6e4bcb7 | note | Verification Activity: By - ENG
e27d6cfa-07de-4e48-95cc-5e5c4b3a1c79 | checkpoint | 13.3 - Installation of Air Valve
6e11f9cd-4cb4-591e-9ae6-11a9aba7925c | note | Detail / Activity - Verify installation per manufacturer’s instructions
3e1120bd-82f5-5a8b-adca-75f3d6f8dca5 | note | Acceptance / Conformance Criteria - Installed as per manufacturer’s instructions
9d1fade5-c92e-501e-a18b-18ac2fa08028 | note | Standard / Specification - PS-22.4.2, PS 22.5.10
abf23280-f13c-55cf-a6aa-6e39377f1bbe | note | Verifying Document - Air Valve & Isolation Valve Check Sheet
8b40e8bc-9068-5d1f-83be-77539b9d503a | note | Testing Quantity Required (based from schedule qtys) - Each air valve
589b57a9-d727-50c5-9c41-121de17977ae | note | Verification Activity: Activity - I
a2ec839f-b485-5400-b239-67ae73b4ef2e | note | ○ Formal inspection activity to be undertaken and recorded.
f833035b-ab6c-55e0-9882-e998288dd32b | note | Verification Activity: By - ENG
67a4ce7b-cc0e-4e68-8cda-2f3b3952d297 | section | SECTION 14.0 - CONSTRUCTION ACTIVITY - FIRE HYDRANTS
99edeaa2-a297-4ecb-a64e-4b75684f083b | checkpoint | 14.1 - CHAMBER LOCATION
1860b317-42a3-5ca3-9d96-1176ecb72b68 | note | Detail / Activity - LOCATION OF HYDRANTS AND AIR VALVE CHAMBERS ARE TO BE CONFIRMED ON SITE WITH THE TCC ENGINEER AND OFFSET AS FAR BACK OFF THE SEAL AS POSSIBLE.
05b09772-6cb9-5296-abd5-9c9ac176eaae | note | Acceptance / Conformance Criteria - TCC Engineer approval
5a10dadc-98ef-5b83-91e7-d15360aaa370 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT), PS 22.4.2 i, PS 22.5.11
6dc47d48-1c0c-5775-8909-926065d0188d | note | Verifying Document - TCC sign-off
b72179e3-91b5-5ced-a1bf-2947daa3d49e | note | Testing Quantity Required (based from schedule qtys) - CHECKSHEET
709bda99-fdc3-5539-9945-909250c3eca3 | note | Verification Activity: Activity - HP
9c5cca6a-36fa-5477-8b30-a6faa42f615c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
57008478-7504-5449-9b29-a95f00380c49 | note | Verification Activity: By - ENG
5235fcc5-c2d2-42e9-ab34-4397017ec18a | signoff | AUTHORITY HOLDPOINT
1745223b-d2d7-4ac8-9179-07f82469c5de | checkpoint | 14.2 - HYDRANT SURROUND BLOCKS, HEIGHT TO SUIT
f8228e7e-766a-566a-9361-1a4bad63cabc | note | Detail / Activity - HYDRANT BOX WITH 150 x 150mm CONCRETE SURROUND TO BE FINISHED FLUSH WITH SURROUNDING GROUND
fe0a9b2c-26cc-5fa3-b80b-916b47476de7 | note | Acceptance / Conformance Criteria - Typical FH SHEET 0322
2d18edfc-3b58-5851-b946-5078679728f1 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT), PS 22.4.2 i, PS 22.5.11
a3ae8082-e873-5cc8-9d29-7879b85c4c3b | note | Verifying Document - CHECKSHEET
f46026a7-991f-57bd-aa8f-9f09fd22b579 | note | Testing Quantity Required (based from schedule qtys) - CHECKSHEET
2bdd9ba9-3a54-55ed-a422-60c57cf93706 | note | Verification Activity: Activity - I
b30a3a1a-341d-592d-aab2-ef6d3d5a1930 | note | ○ Formal inspection activity to be undertaken and recorded.
04cf11be-949b-50a3-b017-0742ba2bd1e6 | note | Verification Activity: By - ENG
2153447b-0442-4205-bee3-11e64f36af74 | checkpoint | 14.3 - INSTALL DUCTILE IRON FH
0c5ced07-2da7-5860-b085-85ee547dbbff | note | Detail / Activity - HEAVY DUTY VALVE BOXI NSTALLED AS PER TCC's CODE OF PRACTICE
f39313ee-687d-5b2f-b1f7-935cbd0ff282 | note | Acceptance / Conformance Criteria - CONTRACTOR TO ENSURE FLANGE DRILLING ON DN80 END OF REDUCER MATCHES FLANGE DRILLING ON DN80 HYDRANT RISER
d09989ba-8589-5be4-8bfb-ee25c2b9fe12 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT), PS 22.4.2 i, PS 22.5.11
ea7afeef-c07c-54bc-a767-59a00ba02468 | note | Verifying Document - CHECKSHEET
d251420b-2870-5a8a-bebc-90aaa0dbd160 | note | Testing Quantity Required (based from schedule qtys) - CHECKSHEET
7fbe0913-0b5a-52d3-aecf-2aed6cf7905c | note | Verification Activity: Activity - I
45ec327d-5e32-53d8-a57f-df2621a8705c | note | ○ Formal inspection activity to be undertaken and recorded.
99f1bfe9-eb07-5336-aa43-ddeda14ff6f6 | note | Verification Activity: By - ENG
26e7739e-f2a2-4022-bed7-bb3bd0eaa509 | checkpoint | 14.4 - Concrete Pedestal on OFFSET bend
1c136d85-86b1-5fad-a7a0-03e55af90c54 | note | Detail / Activity - 3mm RUBBER SEAT BETWEEN BEND AND PEDESTAL 25MPa CONCRETE PEDESTAL
447dfb6b-c0e7-51c3-bb86-a8e8b6d46429 | note | Acceptance / Conformance Criteria - Typical FH SHEET 0322
a6d560a4-96a9-5c7f-8a4e-8299625bd041 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT), PS 22.4.2 i, PS 22.5.11
58194b19-9921-5d19-affe-8c04ed5a2ba4 | note | Verifying Document - CHECKSHEET
bf39c369-22ef-5dca-a40a-a5476378bbb5 | note | Testing Quantity Required (based from schedule qtys) - Per offset
7afa5d08-a3ec-5535-a020-df525626fcd4 | note | Verification Activity: Activity - I
a8e6680d-0728-5ab3-8696-c1488f0b97d5 | note | ○ Formal inspection activity to be undertaken and recorded.
c7ec3ddc-86ea-5297-bc0e-1f44321a5cf5 | note | Verification Activity: By - ENG
1f300676-2f4e-46cd-9773-71beda860a8f | section | SECTION 15.0 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
05de9881-80c6-475a-a5c7-744526f70cb8 | checkpoint | 15.1 - Survey As-Builts
166c016c-0f95-5695-8153-d7b58678eb5d | note | Detail / Activity - Quality Check on Nee pipeline and structure based on the tolerances in RITS
f6002f77-94d7-5321-b66c-8224280f6338 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
7281f098-a1c0-5dbd-8b00-8f7654057b06 | note | Standard / Specification - Project Specifications
150b54a7-bfeb-5aae-9be8-99ce2350fa18 | note | Verifying Document - Red pen markup only
12c5d0d4-7395-548b-8bb6-269a230b58ec | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
8b0e09a6-a71c-54cd-a4d1-e49c03c7e1ac | note | Verification Activity: Activity - H
e6427188-1dc6-5270-8be7-c4401305c065 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
81524415-436a-587b-b969-6631b5e3fdcb | note | Verification Activity: By - SE
9f6ec2ef-01c8-4903-b6e9-f3b30bb82f17 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
8300fe32-9181-580e-a1e2-4b3ad2cd6e34 | textbox | Contractor's Rep Name:
56c6b0a3-83dc-58c9-926d-f09115dc19fe | textbox | Engineer's Rep. Name:
0b18ed68-093f-5e9a-a57a-305a7c12d49f | date | Date:
a5eaf000-d6b6-4d03-9d6a-15820213c0d4 | signoff | Add Signature
96206394-bba7-4b29-b3a0-1c998eee9ee9 | checklist | DN1210-SP2-010.001 ITP Retaining Wall 04 Enabling works Rev 2 | itp | DN1210-SP2-010.001 ITP Retaining Wall 04 Enabling works
e760cf0a-0c99-449b-bd09-940dace7d417 | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
056ee697-7cbc-4c20-afaf-b85c0111d980 | checkpoint | 3.1 - IFC Drawings and Specification
b6cd181b-7bee-580b-88f2-6f0d65d21cbe | note | Standard, Drawing or Specification Reference - Drawings to be issued by DNZ Temporary Works team - IFC stamped
9bf0a0e4-ff78-5af8-8a6c-ff9e3e52e808 | note | Construction Activity Description, Test Type and Acceptance Criteria - A minimum of two weeks prior to construction: document review. DWG’s are for construction or as per instruction
558c6332-2b03-5389-9940-4f4958486a6d | note | Test Frequency - Once
84e3b656-ff8e-5ac6-9dcb-99fbd502b241 | note | QA Record - N/A
4d4b7666-84c8-59f8-acd1-09c9c02dcab4 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
e703e09e-bb4a-41c9-8c7e-c059e17b2a1a | checkpoint | 3.2 - Method Statement & JSEA Development
9818b67d-5620-5063-b338-3ec93f468ce4 | note | Standard, Drawing or Specification Reference - The Downer Standards (TDS)
4795a1d5-a169-5761-a2b8-10ee85e80163 | note | Construction Activity Description, Test Type and Acceptance Criteria - Prior to construction: document review.
852e51a1-a19a-539f-b6e0-6f4a2b3558ae | note | Test Frequency - Once
590155f1-cb23-531b-8920-0f56c80e01f6 | note | QA Record - Method Statement & JSEA Completed & signed by site crew
eae97792-7ad1-5dde-ac5b-b754f7dc3c7e | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
409e6800-f00c-4732-84ae-36eed51e789f | checkpoint | 3.3 - Survey Model
2a10b488-704f-5140-931f-c42f3001b931 | note | Standard, Drawing or Specification Reference - N/A
978f01ab-a27e-5b3f-b1f7-c96895076ae1 | note | Construction Activity Description, Test Type and Acceptance Criteria - Model Review.
aa975301-2d74-5980-88d8-3e13b73a6c91 | note | Test Frequency - Once
97584a38-888c-534d-9ae3-81a7ed559337 | note | QA Record - Visual Inspection & measurement Survey Check set out as per design
01937851-8ee2-52ac-8955-81d569521d38 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
681fb7a4-ca2d-458d-b88d-a4dc52f963d4 | checkpoint | 3.4 - Lift Plan
de2607b1-27d6-55e4-8881-a8c0e4d386ee | note | Standard, Drawing or Specification Reference - DG-ZH-ST047 Cranes and Lifting Equipment Standard
fa0a6913-5d41-5e7a-b101-7d628a9eca97 | note | Construction Activity Description, Test Type and Acceptance Criteria - Prior to construction. For lifting of sheet piles with Excavators.
feb1699c-842d-5983-b80a-854ce09859af | note | Test Frequency - Prior to Construction when required
e1313ad2-13e6-5216-8864-242ac84bf8de | textbox | QA Record - Permit number
4d01df3e-3b2b-543e-836d-ee4c4d3c11a7 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
624f5fac-5304-4756-9ced-961ac11ecbd4 | checkpoint | 3.5 - Hot Works
499036fb-a7c1-5443-8ee1-35b44859414e | note | Standard, Drawing or Specification Reference - DG-ZH-ST041 Hot Work Standard
9a84c509-575e-5e7c-bad5-54f7ba0b2bb4 | note | Construction Activity Description, Test Type and Acceptance Criteria - Prior to construction,for welding, gas cutting, grinding etc a Hot work permit shall be in place ahead of construction. Permit in the work package..
8fb7a461-ffab-51c2-9738-1e1b63f62cac | note | Test Frequency - Prior to Construction when required
e95ca4db-e8a2-5f81-a5b2-d3c721f34282 | textbox | QA Record - Permit number
38c608ad-8e5e-551a-9e01-118e070fb1e8 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
af0f9843-9024-4ae9-9380-c813ccdc5ef8 | checkpoint | 3.6 - Working at Heights
d307eece-7ca4-54ca-880d-d6a59f948507 | note | Standard, Drawing or Specification Reference - DG-ZH-ST042 Working at Heights Standard
e3e2a00b-adec-5930-8d8e-2de9730794eb | note | Construction Activity Description, Test Type and Acceptance Criteria - Prior to construction, permit in work package.
ad51472e-808d-5e88-8d9c-74014600d2fb | note | Test Frequency - Prior to Construction when required
5681d939-49ea-54fb-9ccb-8c88b5a2050e | textbox | QA Record - Permit number
c6c298dd-a8ca-5e5a-9d68-603f1aedfb74 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
6fe57573-bef4-436f-baad-eab07b5b41f6 | checkpoint | 3.7 - Assess geotech reports and confirm driveability for sheet piling
d0cb0f19-7fe6-57a7-91f2-5049bb6049b5 | note | Standard, Drawing or Specification Reference - WSP Geotech Report
d3b5bb56-a140-5813-a17f-ac2c78de486f | note | Construction Activity Description, Test Type and Acceptance Criteria - Prior to construction: document review.
bbfe8db1-f754-5c23-88b3-305725b72308 | note | Test Frequency - Prior to Construction when required
e5d3bde7-220d-55e9-a960-f95a4e17e3ba | note | QA Record - Visual Inspection & discussion with operator on ground resistance profile
ed31930e-3d97-5526-92b2-62f60d5d8f20 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
c878ca3e-c972-46bc-8df0-01f21b48ddb1 | checkpoint | 3.8 - GSI (Ground anchor installation)
047344e1-4404-5d32-b526-1d9aa68dac42 | note | Standard, Drawing or Specification Reference - BS 8081:2015
30392626-4318-582c-97d3-3a4e93167445 | note | Construction Activity Description, Test Type and Acceptance Criteria - Load test schedule, test locations and test sheets are reviewed and approved by GSI Engineer
9f56258c-b425-58fa-afdf-954046d85aa1 | note | Test Frequency - Prior to Construction when required
fa5c71f8-93c4-5bdc-a268-fed1d3b80a56 | note | QA Record - Test sheet and job pack
3529dedb-9e5c-5526-b85e-c8c4c09d123a | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
1358b085-31d9-4a66-984a-b84dd902d508 | checkpoint | 3.9 - GSI (Ground anchor installation)
1f8c2a30-e2a7-5b8d-9d37-850b9f21cae7 | note | Standard, Drawing or Specification Reference - n/a
d4677f7a-8846-51aa-978a-1cf93d8b7c42 | note | Construction Activity Description, Test Type and Acceptance Criteria - Slope assessment completed and reviewed by GSI Project Manager.
e7a36d0b-d76b-5845-b410-67e338e62e9a | note | Test Frequency - Prior to Construction when required
c8a3cacf-d7f9-595c-8d6a-8f2e1d5a3712 | note | QA Record - Slope assessment checksheet
68a6715d-db79-5d63-a3a4-645239811b1c | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
d80aba3e-88b2-47f4-8c9a-d8c170a9d124 | checkpoint | 3.10 - GSI (Ground anchor installation)
dd80617d-6efe-5af0-a8d0-1434853275f4 | note | Standard, Drawing or Specification Reference - n/a
242436e1-051a-5949-a6e4-07b5324b425a | note | Construction Activity Description, Test Type and Acceptance Criteria - Confirm site extents agreed with Engineer and aligns with general intent of the design
96bd27ec-4c21-5ca3-b1a0-a58fc62d12b5 | note | Test Frequency - Prior to Construction when required
b4e13992-6677-5ce9-9e23-921a9af60666 | note | QA Record - Written confirmation to design team
499015d5-20d1-5601-85a1-1dcdd6d345e7 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
d590b8d9-f45d-4eb7-8e56-f562abfd2028 | checkpoint | 3.11 - GSI (Ground anchor installation)
df9c9fc1-e649-51b2-be62-b42d021108d0 | note | Standard, Drawing or Specification Reference - n/a
6c8f27bc-6ea0-5f7e-b6da-74abbb228dc2 | note | Construction Activity Description, Test Type and Acceptance Criteria - Sacrificial test nail number and locations agreed and approved by GSI PDE / PM
d254d380-c1bf-51db-ac9a-5678c1001977 | note | Test Frequency - Prior to Construction when required
0b145590-f4b8-50a1-a003-aedf12c19aa0 | note | QA Record - Job pack signed
e9ffeaf2-a05e-5968-a857-fd48ed279e9b | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
382c32f8-2b2e-44b2-8b1c-1d170d11f58b | checkpoint | 3.12 - GSI (Ground anchor installation)
8e69de22-51a1-5b89-a2d0-317a50b51352 | note | Standard, Drawing or Specification Reference - n/a
0c8fa66b-9bba-5e0b-8fa1-f49d3721e046 | note | Construction Activity Description, Test Type and Acceptance Criteria - Pre-construction sign off - Subcontract agreement signed, TMP approved, all staff and subcontractors inducted , CMP reveiwed and in place.
aab3d6ab-bf07-5b6d-8d5f-fdcd048bf614 | note | Test Frequency - Prior to Construction when required
8553db6c-071c-5785-8fd8-9b1ff830a726 | note | QA Record - Job pack signed
1c63fb37-a3eb-57b7-9c23-2b0538c1b5fa | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
f56851bf-0fb7-445c-886b-ef7aa83d7dea | checkpoint | 3.13 - GSI (Ground anchor installation)
2fb7c696-d13b-572c-89dd-54c0ce674220 | note | Standard, Drawing or Specification Reference - n/a
0e8a9334-aa38-58f4-9d0d-333de5c5128d | note | Construction Activity Description, Test Type and Acceptance Criteria - Plant - Ensure plant suitable for use on site and calibration up to date. Rig capable of reaching all anchor locations.
815e735c-2362-57d8-8c88-912ef4ca62fa | note | Test Frequency - Prior to Construction when required
c7e46041-bb69-56bc-b69c-5b25fe20cfaf | note | QA Record - Job pack signed
85098f92-3b3e-537c-a33b-cb974eece980 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
481affb0-3d23-4108-9d7c-921e827aae8c | checkpoint | 3.14 - Sheet Piles
9f3c8bee-2b83-559a-aebb-9b78cd2c2248 | note | Standard, Drawing or Specification Reference - NZGS Spec SPERW
77ad96a3-a866-524d-8fce-bf860ca14ac9 | note | Construction Activity Description, Test Type and Acceptance Criteria - Sheet Piles are in good condition, free from rust and debris.
6d4fbe15-e5e6-5337-bf3a-f455bff5d1b7 | note | ○ Leading edges cut to assist driving
63e82d03-b817-5772-86aa-997fbf67b869 | note | ○ 40mm lifting eyes cut in side wall of sheets, lengths as per IFC drawings
9587fa43-81c9-508f-8354-c4d40346d1da | note | Test Frequency - Once
63e02ca9-b29d-5ce7-9393-6c485e520ca9 | note | QA Record - Visual Inspection
846289d9-d559-5eaa-8c10-8c7ddf4f241a | note | Verification Method and On Site Responsibilities: DNZ Engineer - R
bb577c93-c67f-409c-a227-43087df70614 | checkpoint | 3.15 - Driving Gates
7cc74072-3e6c-58be-b219-56fd61ef34fd | note | Standard, Drawing or Specification Reference - n/a
ead5f5f9-9d32-5abb-a56c-bbcadd219ebd | note | Construction Activity Description, Test Type and Acceptance Criteria - Check suitability amd alignment
8fa9c902-6386-5b6d-a903-e5b8b01bd824 | note | Test Frequency - Once
71cb932b-b838-5b71-b5ce-7f5a1bb450fd | note | QA Record - Visual Inspection
fb69de81-c75d-5a2a-bab8-5363b5141330 | note | Verification Method and On Site Responsibilities: DNZ Engineer - R
b9440f8e-d9b9-40ac-ab01-15206f20a09d | section | SECTION 4 - CONSTRUCTION ACTIVITIES
6a3e7a1f-c48b-4834-ba57-0c62359bc181 | checkpoint | 4.1.1 - Piling - Pile Set-Out
62cff34c-d4f9-5b2d-b4a1-e3250d8c3a8c | note | Standard, Drawing or Specification Reference - DWG details to be provided
37bb17e5-ed05-5cf2-990a-8653fad84f61 | note | Construction Activity Description, Test Type and Acceptance Criteria - Before commencing sheet piling operations, survey set out wall alignment based on model. Set out to include offset.
a4645f5e-212f-5cb5-a9c4-7766af669778 | note | Test Frequency - 10m chainage
a90e6576-bdaf-53d1-8cec-9e2448c69af0 | note | QA Record - As-Built
08100506-addd-5085-93cb-9fdd99e6081f | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
4771a6b5-fe5b-41be-b241-a8a07a283ac5 | checkpoint | 4.1.2 - Piling - Driving Gates
0da3b05e-a910-547e-a077-208336a56bde | note | Standard, Drawing or Specification Reference - n/a
b97018c4-0095-5207-8efb-a459ddab51a1 | note | Construction Activity Description, Test Type and Acceptance Criteria - Position gates to wall alignment
24fc7d42-8e63-5c0f-8382-56c72bddfbae | note | Test Frequency - 10m chainage
905309c9-ca72-5abd-ad0f-05e926c05843 | note | QA Record - As-Built
a7de42df-7a5e-5352-9620-50544f27070f | note | Verification Method and On Site Responsibilities: DNZ Engineer - R
2749d10a-7993-4212-b37f-fab4d2e0161d | checkpoint | 4.1.3 - Piling - Install sheet piles
e8f27dbc-bbd6-543f-aea6-e05286a4f0f7 | note | Standard, Drawing or Specification Reference - Proposed Access Ramp General Notes: 3235599-SP03-ST-3001-1RW4 Sheetpile Geometry - Elevation - DN1210-05-DRW-001 REV A.4
614a92c2-3a97-554e-892e-8b37cc0ab166 | note | ○ Proposed Access Ramp General Notes: 3235599-SP03-ST-3001-1RW4 Sheetpile Geometry - Elevation - DN1210-05-DRW-035 REV A.4
65df581d-a2fb-53db-89b9-97d4a1234e8c | note | Construction Activity Description, Test Type and Acceptance Criteria - Sheet piles driven to the required depths / embedment
5fa80334-46ea-5eb7-9fc2-007dab74552a | note | Test Frequency - As required
e1b74507-61a9-502d-a2f9-7f36672995b3 | note | QA Record - Written record, sheet length and embedment depth
55fb2470-4700-5a85-b084-35f097f4d20c | note | Verification Method and On Site Responsibilities: DNZ Engineer - R
11c00368-a2f9-40df-b3e1-e2c4f6fce46f | checkpoint | 4.2.1 - Install Tie Back Anchor
ee6b72df-cada-57ac-85c0-70779457f6fc | note | Standard, Drawing or Specification Reference - Drawings
14264d76-6242-5af1-9403-e70cbf69b3ce | note | Construction Activity Description, Test Type and Acceptance Criteria - Confirm drill depth, angle and orientation of tie back anchors - per IFC drawings
8f98ecfd-2b9f-5d9e-9eaa-98baaac786c1 | note | Test Frequency - Each nail
b69c7ee5-8a40-5961-bfba-5acd19188eee | note | QA Record - Drill log
988aa731-930d-5ec4-bf84-eeea03cca297 | note | Verification Method and On Site Responsibilities: DNZ Engineer - R
10b3e915-55d5-4073-a918-c1d1e74c77cc | checkpoint | 4.2.2 - Install Tie Back Anchor
db36a83a-f53c-5401-a440-cb26e73943bb | note | Standard, Drawing or Specification Reference - Drawings
57eb07f2-ee67-5f8a-989b-fab4f9ccc928 | note | Construction Activity Description, Test Type and Acceptance Criteria - Ensure grout sample cubes or cylinders are available and ready for use (1 set of 3 samples per day)
eaef1c6f-2a81-51e0-b773-0b5c34120536 | note | Test Frequency - Prior to drilling
6508f6bb-0c45-5f51-81e5-e1c3c5690356 | note | QA Record - Grout log
957c3d39-a4e7-5b27-956f-f3c0a7e3926f | note | Verification Method and On Site Responsibilities: DNZ Engineer - R
2754c77b-77a4-4e24-ab9f-a1ebd31e8565 | checkpoint | 4.2.3 - Install Tie Back Anchor
862d4321-d902-5c54-8fa5-bdea34e152a6 | note | Standard, Drawing or Specification Reference - FHWA-NHI-14-007-Soil Nail Wall
68668c24-c558-588d-9b61-12e1aaf11fab | note | Construction Activity Description, Test Type and Acceptance Criteria - Drill logs (fully) complete, including hole ID, diameter and length of hole drilled - as well as geology i.e. colour, type (rock/soil), moisture (i.e. dry, slightly moist, wet). Ensure to stipulate which holes are to be used for test anchors - based on D7.
bbd78552-f74b-53d3-bbe9-652554713e79 | note | Test Frequency - During drilling
00e9f2d6-b6cf-5e98-91d7-adc3e7855312 | note | QA Record - Photo, Test result sheet
2cdd3bf3-9da9-50d8-a6f0-e2e5ba0543b8 | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
0ccbf277-0363-41ef-bc10-bc7b86d24011 | checkpoint | 4.2.4 - Install Tie Back Anchor
fbfee12e-7a9c-5813-b4d3-9c40ec734428 | note | Standard, Drawing or Specification Reference - Drawings
241fe62d-a677-531e-a877-f49f304676b0 | note | Construction Activity Description, Test Type and Acceptance Criteria - Grout to have reached at least 7 days prior to testing.
0a6bbc28-34fe-5de1-8098-1ffc29f6c00e | note | Test Frequency - During drilling
dde1eee8-b158-5803-b479-7ddca2b9d472 | note | QA Record - Photo, Test result sheet
044bf9e2-f02e-5301-98f3-7e25197cd1a6 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
193923ec-5d90-4bd7-83da-75849d53987b | checkpoint | 4.2.5 - Install Tie Back Anchor
638fb483-7684-5ffd-8ba5-b6d21eed03c0 | note | Standard, Drawing or Specification Reference - Drawings
fe4da7b9-adad-5b05-bd68-46d1d3f20335 | note | Construction Activity Description, Test Type and Acceptance Criteria - Ensure tie back anchors have the correct debonded length for the sections they are installed in.
1cf09e90-818a-5fea-8d3a-ae296083890f | note | ○ Refer to IFC pages 1 and 2 for respective debonded lengths.
db0f3a4f-d546-5a12-9788-64e1568e43eb | note | Test Frequency - During drilling
f6242ef1-0ad8-599b-aaff-eeff7d55fe6a | note | QA Record - Photos
bebdff87-d9c7-5468-8833-bdbeca1d947e | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
2d9934cc-af83-4b5f-9f76-6340a5c37d7e | checkpoint | 4.2.6 - Install Tie Back Anchor
25d01e42-b029-5d32-9d9e-6a1b79266517 | note | Standard, Drawing or Specification Reference - TBC
3ef9adf2-f5ff-5185-91e7-2051add25e19 | note | Construction Activity Description, Test Type and Acceptance Criteria - Install 2No. 150mmØ open hole sacrificial test anchors in locations indicated in (drawing sheet number, length and debond specs TBC)
245ac11d-2afe-58bd-ad99-0c808a915b86 | note | Test Frequency - During drilling
b91bb7cd-79c3-57d4-b911-21ab5d7471f6 | note | QA Record - Photos, Drilling logs
ee043a75-7a68-5360-a3bb-3e75a0e856b4 | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
adb9b0c0-3965-46c0-bedd-42c86cd4eea0 | checkpoint | 4.2.7 - Install Tie Back Anchor
3d446198-a31a-545a-895e-b4ecc665a62c | note | Standard, Drawing or Specification Reference - TBC
e0e4178a-b607-5c27-971c-49cc4a635ed6 | note | Construction Activity Description, Test Type and Acceptance Criteria - Install 2No. 130mmØ grout flushed self drilling sacrificial test anchors in locations indicated in (drawing sheet number, length and debond specs TBC)
1c24b491-8e42-542d-8a5c-6571050818c0 | note | Test Frequency - During drilling
9b8a63c4-b800-579f-aa18-8a2b0a3af7a0 | note | QA Record - Photos, Drilling logs
bf81f864-0908-5897-9624-ea9f4046f7f0 | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
bc75068c-27ed-45de-ad81-087697a62dba | checkpoint | 4.2.8 - Install Tie Back Anchor
b109c483-f106-5959-89f4-f4a80dbcb014 | note | Standard, Drawing or Specification Reference - TBC
aef253f5-7158-58d0-a639-d1e1e397699d | note | Construction Activity Description, Test Type and Acceptance Criteria - Sacrificial anchors installed with Rockbond A301 Accelerant Additive as per manufacturers instructions. Crush test at 3 and 5 days (TBC)
ad6f1695-2b1c-537f-aa5e-a8e013087946 | note | Test Frequency - During drilling
d158c099-b180-5d1d-b654-7ec22f5d29ff | note | QA Record - Grout log
842f8500-2539-50c3-998e-bd36195fa5ba | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
e8d20ef2-3aaf-4e50-9c4b-5f9c21dee600 | checkpoint | 4.2.9 - Install Tie Back Anchor
8ecc23b9-5ed1-55e1-9852-a2c197d3fd98 | note | Standard, Drawing or Specification Reference - IFC Drawings
1ff6831b-5116-5208-9bb6-fd11f0580c2a | note | Construction Activity Description, Test Type and Acceptance Criteria - Install up to 108 no. of 14.4m long, Galvanised T40 anchors across 2 rows in 150mmØ HOLES.
bf976475-dbe0-5c68-84a4-0fadaf00e447 | note | ○ Check drawings for varying drill angles. Anchor centers and cutting out sheetpiles are completed by others
486a829f-540c-5663-bf39-da272c293a90 | note | Test Frequency - During drilling
028c029b-77f2-5164-9b2e-434d31c10c8c | note | QA Record - Photos, Drilling logs
3060cb24-de09-5ef0-aff1-d87a48ac4228 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
a17e9d55-b21e-4e2c-8826-31d2791816c0 | checkpoint | 4.2.10 - Install Tie Back Anchor
a41a136b-3707-5f07-a16b-07582a662900 | note | Standard, Drawing or Specification Reference - GSI grout sampling procedures
a60566e1-f74b-509e-ab60-6f0c16f30f19 | note | Construction Activity Description, Test Type and Acceptance Criteria - Grout sampling to follow relevant SOP i.e. tamping down in 1/3 lifts, and stored in supplied chilly bin after initial 12 hours of curing. Temperature in chilly bin is to remain as constant as practicable (avoid uneccesarily opening lid).
7d3d2fe0-e2ad-57b8-97cd-4f47293af50d | note | Test Frequency - During drilling
83cd17d8-2288-5f02-b2d0-e6d1f28c755c | note | QA Record - Grout log
601c5c4b-36d0-56dd-88b0-a4dc14a262a0 | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
ce7ec6bb-9f9c-4153-8eb5-cfe9bcfa91f1 | checkpoint | 4.2.11 - Install Tie Back Anchor
bd875e37-92c6-5bcc-903c-e12ddfc0396f | note | Standard, Drawing or Specification Reference - GSI grout sampling procedures
6ccf4bf8-8d5d-5e45-99e9-91a019c10be6 | note | Construction Activity Description, Test Type and Acceptance Criteria - Grout samples to be delivered to the lab within 2 days of sampling, where practicable, or as soon as possible thereafter.
64bca302-dc8b-58ca-bfd4-f18a6e85c873 | note | Test Frequency - During drilling
2afa2e38-fa7f-53d4-a36d-0d26154f3b9f | note | QA Record - Grout log
13ba2f1a-e024-5d76-836c-f40ff48da7aa | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
29549c2f-8141-40c5-905d-4c28d2390535 | checkpoint | 4.2.12 - Install Tie Back Anchor
1902363c-e375-53c9-9818-801acf183575 | note | Standard, Drawing or Specification Reference - GSI grout sampling procedures
fe41ac4b-2b5e-522c-975c-7039890d4c01 | note | Construction Activity Description, Test Type and Acceptance Criteria - Grout mud balance testing - per relevant SOP
b38b7e64-1a43-5d69-9705-77bc0a7f271b | note | Test Frequency - Per hour during grouting session
d6923f71-852f-5866-848c-2647d4f65e26 | note | QA Record - Grout log
3f75a1a2-ef7b-5b21-bdee-f11edc82de7b | note | Verification Method and On Site Responsibilities: DNZ Engineer - R
3bc676c8-7eb2-48e9-bd68-db1f8ce455a4 | checkpoint | 4.2.13 - Install Tie Back Anchor
86697216-954e-59f7-a9f5-8fb1765a7553 | note | Standard, Drawing or Specification Reference - N/A
07598a0f-d83d-50c5-a4f0-dc066518cb59 | note | Construction Activity Description, Test Type and Acceptance Criteria - Grout logs i.e. number of grout bags per hole and total. Volumes to be recorded for each sol nail anchor. Ensure nails are appropriately numbered with relevant ID.
f303ab4d-af12-5717-be77-3850b9a27ce1 | note | Test Frequency - Each grout session
5ed1324c-6902-5a94-8cce-64018b870bb5 | note | QA Record - Grout log
40200080-6884-54ee-90df-eaec8fd2fdb0 | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
fc8b0e5d-4c7e-4b0a-a10b-de495dfbe64e | checkpoint | 4.2.14 - Install Tie Back Anchor
6548e1a3-8b01-5b6d-b60b-7627d46ca870 | note | Standard, Drawing or Specification Reference - N/A
3cda7939-0976-5102-9d29-014b29b3273b | note | Construction Activity Description, Test Type and Acceptance Criteria - Grout top-up complete. Update grout logs with those test nails that have been topped up.
c90fab32-d24e-5970-9acb-a1f2761a410a | note | Test Frequency - Each grout session
3943cf26-7676-54fd-9b62-1abfeabd5b28 | note | QA Record - Photo
50d850d3-9bb8-5919-9733-dd0597a61952 | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
915ee716-3fdb-477f-9357-83fa357892d3 | checkpoint | 4.2.15 - Test Results
ff7de6f5-6014-5bb9-96ce-ab56afac42c2 | note | Standard, Drawing or Specification Reference - IFC Dwg
c411ac45-963d-5312-8844-3329c1cf58fc | note | Construction Activity Description, Test Type and Acceptance Criteria - Verification Testing for minimum 4 tests, 2No. 150mm open hole anchors and 2No. 130mm grout flush anchors. Pullout failure is defined as the inability to further increase the test load while there is continued pullout movement of the test anchor . Record the pullout failure load as part of the test data.
3303b3f6-9e7a-57a2-9a25-8040bffeb30b | note | Test Frequency - After Drilling
380fdd40-970e-5cfa-a60c-53060a01c76c | note | QA Record - PhotoTest (result sheet)
9d66ac30-1b6f-5de8-9912-bece102ddbf4 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
8935bbe0-1b8e-48d6-93a9-69433e3e53fe | checkpoint | 4.2.16 - Test Results
93b80689-783d-53b6-8076-7738e8f7b027 | note | Standard, Drawing or Specification Reference - IFC Dwg
35768f87-6ee3-5272-8ea1-8e54a7584c83 | note | Construction Activity Description, Test Type and Acceptance Criteria - Production testing on 25% of tie back anchors. Duiring the creep test i.e.1.0 Design Working Load, the difference between the reading taken at 5 mins and 10 mins should be less than 1mm. If it exceeds 1mm in this period, the test shall be held at 100% DWL for a further 60 minutes.
a8133445-463d-5433-b0c2-f1ffd09aeb4c | note | Test Frequency - After Drilling
eba5755e-223e-54d4-8abf-9396e447991c | note | QA Record - PhotoTest (result sheet)
77545ce1-ac44-5cf5-9223-1e8b545f8e1d | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
bddbce40-a992-4865-9558-1796d37dd7cb | checkpoint | 4.2.17 - Cut Anchors to Length
0476dde9-76be-52cd-96a9-8fd00b782ff8 | note | Standard, Drawing or Specification Reference - IFC Dwg
b23b8260-d9a5-539d-857a-7b98044ea1cd | note | Construction Activity Description, Test Type and Acceptance Criteria - Confirm length of bar to be left extending from portal of each hole.
a492e558-a252-5ac0-b854-634f430a20db | note | Test Frequency - After Drilling
dbe41024-1e4a-5ea5-8ef2-487b24be6ab0 | note | QA Record - Email confirmation
a759aa36-86a7-5a16-844b-4117a18cb224 | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
935d912c-369b-44c6-8fe8-2cf6a16f55c4 | checkpoint | 4.2.18 - Cut Anchors to Length
77e66f22-ce1f-5caf-b81c-a77ca87859e6 | note | Standard, Drawing or Specification Reference - IFC Dwg
ad9135fd-8030-583d-af89-dcc3cddf5a4d | note | Construction Activity Description, Test Type and Acceptance Criteria - Cut bars to length and leave plate and nut attached
c1d39112-a252-5824-a5c5-9c10ea7e8168 | note | Test Frequency - After Drilling
8d359a05-4a34-5393-af49-42cf7d601a39 | note | QA Record - Photos, Note on day report
73a1638e-40b9-59ed-a6c0-2ad2b372522d | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
b4804661-538a-4032-91d4-f54361c493e8 | checkpoint | 4.2.19 - Cut Anchors to Length
5d81eb7a-c309-5ebe-abf3-691d4d89b644 | note | Standard, Drawing or Specification Reference - IFC Dwg
b41b1216-bb41-5939-bcf1-3dbbe7a87f41 | note | Construction Activity Description, Test Type and Acceptance Criteria - Confirm with client lengths are correct and hand over for waler install
4fb70fb8-9d3d-57ee-a916-cb7f032f0a14 | note | Test Frequency - After Drilling
2e96cff1-ae47-5d9a-b304-0a411e2afd83 | note | QA Record - Photos, Email confirmation
c07ba149-ad97-5c24-8ffe-0bec96ec2c99 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
4bfbc720-a087-4f45-8869-b39d42db35dd | checkpoint | 4.3.1 - Ground Anchor Installation
e6095b68-0a7d-5d14-8ce0-8c4414471747 | note | Standard, Drawing or Specification Reference - N/A
7eca5ed3-3d4a-5ec1-9f80-7261d2179c0e | note | Construction Activity Description, Test Type and Acceptance Criteria - Drill and Grout logs
47c5d5e4-5bf5-5dda-af10-fadbb88de741 | note | Test Frequency - Daily
cc065fe5-47d8-5bb1-bb86-677ae3d8a1e8 | note | QA Record - Drill and grout logs
937df2dc-3a9d-566f-8358-ca52dfd59f29 | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
5dd1b862-6c51-4774-bfc7-042849ff67f0 | checkpoint | 4.3.2 - Ground Anchor Installation
6ffd18d6-cc3d-55ec-b4a4-f224da467eae | note | Standard, Drawing or Specification Reference - IFC Dwg
2edc17d6-4558-59f0-b565-fbe9374916ba | note | Construction Activity Description, Test Type and Acceptance Criteria - Sacrificial and Production test nails
eb142862-77fb-5e0e-89c9-3948cd3b36cf | note | Test Frequency - Per IFC Drawings
e233c4d3-d9ab-5116-bd3e-da28f35f238b | note | QA Record - Test logs
23ef86a9-6ca2-5bff-8af5-03944d6277ac | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
6e2c4ad6-0a4f-429a-9825-bf4a4056fbb2 | checkpoint | 4.3.3 - Ground Anchor Installation
861ba049-58e5-5664-9771-e6cde9830287 | note | Standard, Drawing or Specification Reference - 30MPa at 28 days
f7ecf06c-b3c8-5482-aec9-b9b5a80b0410 | note | Construction Activity Description, Test Type and Acceptance Criteria - Grout crushing test
cc7b6efc-7861-5778-9357-8faf3fd84576 | note | Test Frequency - 7, 14 and 28 days result
ce2f8b1e-b94a-52b3-8989-e55157cc6a09 | note | QA Record - Test Results
6b7dcc58-9d33-52c6-a7e7-2bae69ad9813 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
2f0662df-a9cf-45d0-84e4-ee7a021e8f0d | checkpoint | 4.3.4 - Ground Anchor Installation
f45ca152-f204-51f7-999b-584ff8b0e737 | note | Standard, Drawing or Specification Reference - N/A
d8d2b542-dd44-5fdd-a624-c113f500f892 | note | Construction Activity Description, Test Type and Acceptance Criteria - Photo records
f8a7f9c7-a05e-5a92-9960-4839357ed9b8 | note | Test Frequency - Daily
3f62dc0d-e469-55d6-a489-5d4dc12151ca | note | QA Record - Photos
723aa74f-c81f-560d-a05b-ba0b1620cb87 | note | Verification Method and On Site Responsibilities: DNZ Engineer - W
95feec1d-800d-4cab-be3c-172975717862 | checkpoint | 5.1 - Pinling - Survey Records
d64694c1-8248-5280-9c33-d45ad058522c | note | Standard, Drawing or Specification Reference - N/A
d56df651-ceeb-575e-a024-348e364b2eaf | note | Construction Activity Description, Test Type and Acceptance Criteria - Installed sheet pile wall surveyed and records are assembled for asbuilting
bf9d8b0f-7658-563e-a8e8-f7fe376f622e | note | Test Frequency - Once
a6824d3b-48f6-51d0-bf70-a704fefc97b8 | note | QA Record - As-Built
1d951afb-a1a9-5644-ae16-6daa47de6b55 | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
46a6d139-bf37-4250-b299-e7a82c73c659 | section | SECTION 5 - FINAL RECORDS
6ff9e67c-d802-459b-b038-5336b75b6726 | checkpoint | 5.2 - Ground Anchor Installation
3f70c6fa-f9a5-5f2b-88e7-f79e2b6e3656 | note | Standard, Drawing or Specification Reference - N/A
17c5f236-ba26-5dbc-8f1a-1df2d2d25480 | note | Construction Activity Description, Test Type and Acceptance Criteria - As-Built
aadf0477-0075-57b8-a892-6cd8d3ed056a | note | Test Frequency - Once
ebf64406-37bf-5bd7-9b7e-1eb22a3b165a | note | QA Record - Updated Drawings
65e7f6e8-8050-51b8-9505-83eed811f58d | note | Verification Method and On Site Responsibilities: DNZ Engineer - H
80f40747-fd28-42c9-93e3-536e8ce31eb8 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
186ec40b-5224-5a00-bfce-ca51a5c1178d | textbox | Contractor's Rep Name:
345b9f3c-7ef8-57e7-aa51-78af64f13f34 | textbox | Engineer's Rep. Name:
d53d34f6-d363-56d2-b4be-3af616375eea | date | Date:
a85783bb-8d02-47b9-aeba-735e08c186da | signoff | Add Signature
60e7f47d-6d2d-47c0-9c7f-82790b0c4f5e | checklist | DN1210-SP2-010.005 ITP Retaining Wall 4 Magnum Block Rev 0 | itp | DN1210-SP2-010.005 ITP Retaining Wall 4 Magnum Block
dbe57f7f-a9c1-4a8a-a2e1-4347e3dbf541 | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
1a2df39f-122c-4561-b89a-1edd858c7e16 | checkpoint | 3.1 - Methodology
3fb8224d-672c-58b9-befb-b518a1e4b74c | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points for review and approval prior to works.
3326255a-50af-5a7c-8a79-15f490bf905b | note | Acceptance / Conformance Criteria - Engineers Approval
b107ecb9-9242-5ad9-9acd-c37204f43933 | note | Standard / Specification - Appendix V
6bb1ad70-5fec-52e1-862c-3cb8aca90590 | note | Verifying Document - Approved Methodology
95a868bb-6b56-5ac3-89c1-716aeaf5fc58 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
c46bf828-41fb-5168-ab21-7a9f87ca7569 | note | Verification Activity: Activity - HP
d13464b4-ba44-5f22-93dc-bd8e50e4711c | note | Verification Activity: By - ENG
d1b4a38c-b19d-4a6d-ab0d-23826c3bca5a | signoff | AUTHORITY HOLDPOINT
71f7df98-fdd6-4e90-9c87-e1a71ccfdb9b | checkpoint | 3.2 - Ecology Sign Off
e8aad85d-f5f0-5637-bddf-0d1de89df906 | note | Detail - Confirmation from Ecology that earthworks and sheet piling can proceed
2e4dc24f-d4be-54fa-a85d-143f5b1d6485 | note | Acceptance / Conformance Criteria - Email
34671f96-190d-5196-bd08-23979ad6e692 | note | Standard / Specification - Internal Hold Point
bca8ec74-fe26-528c-b3df-26098e6658fc | note | Verifying Document - Email from Ecology NZ
72818ee4-532c-57e7-b923-b240fae8d07a | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
84d8c3fb-292e-5bb3-87c4-2507236d68fc | note | Verification Activity: Activity - H
9e4f745b-20cb-5932-81e1-47e356768fc9 | note | Verification Activity: By - PE
242af59d-2a1d-484f-acb1-743bfaa9aa84 | checkpoint | 3.3 - Erosion & Sedimentation Controls
0092e68b-f44d-5967-aebc-3a346bb2e80b | note | Detail - Confirm that Erosion and Sedimentation Controls bunds are in place
9f2f85ae-288d-55e9-9e1c-0d3add3649f1 | note | Acceptance / Conformance Criteria - As-built Completed
f9cb7753-af1f-506c-a3eb-57c18003a402 | note | Standard / Specification - Internal Hold Point
131eccb7-ec85-52c2-b2da-e78bd08bf6f3 | note | Verifying Document - ESC As-built
88e460f0-edfa-5ef9-b083-f539333881f7 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
0035cfe1-74db-53fa-a98d-129e01eb654a | note | Verification Activity: Activity - H
2ded169e-0d6e-5d7f-9f2f-92a54cb17a41 | note | Verification Activity: By - PE
0e9842e2-70eb-49c7-94b1-67f41dc9e792 | checkpoint | 3.4 - Geotextile
2825063c-cfe9-5e1a-864d-4aa5a7566cfd | note | Detail - The Contractor shall submit the full details of the Class C non-woven geotextile fabric to the Engineer for approval prior to installation.
e16bae24-537a-5659-8716-e67fe26561b3 | note | Acceptance / Conformance Criteria - Engineers Approval
c3072026-f71c-5ca4-a6a5-aea3b95873c9 | note | Standard / Specification - PS 16.5.7 Appendix V
f0e6c69a-9199-5f4f-a40f-a6f38b758bd5 | note | Verifying Document - Material certificate/NTC
f845be1f-bc72-5a0a-bd6a-067678525c9e | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
185c373d-7a64-5a66-900e-b6e5a4458625 | note | Verification Activity: Activity - HP
a2b07b38-bab9-59c1-8773-008965abdd92 | note | Verification Activity: By - ENG
0d0ce4db-55ce-4193-a3d4-3c8dee9309d4 | signoff | AUTHORITY HOLDPOINT
f2993f2e-90db-41b8-92f9-537543cb61b4 | checkpoint | 3.6 - Crushing Resistance: Drainage aggregate
0c61f59b-2198-533f-a13a-48165572c79f | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
d8640e57-923e-566c-8a23-53165d129b00 | note | Acceptance / Conformance Criteria - >100KN
c1a8c9a3-19e4-5e39-8bf1-085868ceceab | note | Standard / Specification - Appendix XVIII PS.17.6.2
ad0ce1e5-5f0b-525d-9ccc-322dff6a75c5 | note | Verifying Document - IANZ Accredited Report
f9611f5c-f67e-5801-a8fa-417bd188305e | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
d1ea2a7f-c739-55f7-94ac-08e3eb3666f2 | note | ○ Results to Engineer 2 wks before importing
c947715f-26c8-5351-b03a-2674ceeac6ab | note | Verification Activity: Activity - HP
c0d9594b-f391-5e87-b542-59c1c0261674 | note | Verification Activity: By - ENG
e1be538a-4464-4378-b58d-85343896e24e | signoff | AUTHORITY HOLDPOINT
5be068bc-8e26-483e-b1dd-07ebf65dab58 | checkpoint | 3.7 - Partical size distribution: Drainage aggregate
cca27175-cbf4-5ac0-9380-2006fb69bbc5 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
6d3783f7-caf2-5bf4-95a1-df00a1e7bf6c | note | Acceptance / Conformance Criteria - DM40/20 OR DM20/7 Grading Envelope
ec06fc18-ac86-5312-8610-90b2a7387eb5 | note | Standard / Specification - Appendix XVIII PS.17.6.2
fc4bc261-8e2c-50b2-afb6-ecad53b4a21f | note | Verifying Document - IANZ Accredited Report
b8c40f58-cbc7-52eb-9247-a8aa2ced6ea8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3
ff5c1c1c-7739-5cb7-a083-98f3460dd8cf | note | ○ Results to Engineer 2wks before importing
bb75ff81-4ad3-5f60-86fd-debfdc2e703c | note | Verification Activity: Activity - HP
a7560135-d4a5-5904-83de-04ad7d0ecd60 | note | Verification Activity: By - ENG
22066ef8-6bb2-4994-9c2d-4671548c8859 | signoff | AUTHORITY HOLDPOINT
a52a78db-a59b-4706-98e8-e086ca58af39 | checkpoint | 3.8 - Weathering Resistance: Drainage aggregate
375d9f75-66f8-547d-9125-9d9da4829676 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
c113adbb-78b0-57b7-9563-447712897068 | note | Acceptance / Conformance Criteria - CA or better
a27f4ae4-af26-5e8a-b0b2-48e7cc4ee12c | note | Standard / Specification - Appendix XVIII PS.17.6.2
d5580869-bb2c-5195-84c7-8c55f8e60592 | note | Verifying Document - IANZ Accredited Report
41fb2bbd-a0a3-5479-adcf-80ebaa51c0f8 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
cbc40e8a-6145-50a3-94dd-7c4a7c4a5a8d | note | ○ Results to Engineer 2 wks before importing
70a89176-c224-5de8-b596-35117a9fd649 | note | Verification Activity: Activity - HP
b70a6193-db41-55a3-98f7-52087424c741 | note | Verification Activity: By - ENG
6f3febde-f82d-4697-9073-e9260413d603 | signoff | AUTHORITY HOLDPOINT
5967bf14-785e-42ba-b0df-559b1c661df5 | checkpoint | 3.9 - Crushing Resistance: Structural Fill
7943bc76-f31e-5cf8-83d1-e83756d173b4 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
a75329b7-f8be-560f-86e4-6306248c94f8 | note | Acceptance / Conformance Criteria - >100KN
f97be105-428b-580d-89df-288e6f527567 | note | Standard / Specification - Appendix XVIII PS 17.4.3
395f3b73-ade3-5671-97ab-a308643064d7 | note | Verifying Document - IANZ Accredited Report
62f88e7b-b775-5eb7-b64a-92b4a4fdee2b | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
d1751081-fb1b-5248-bfd8-03054e51425a | note | ○ Results to Engineer 2 wks before importing
2175a827-2adf-5f7e-9a15-73f67ddde04f | note | Verification Activity: Activity - HP
6e9a9d85-dafd-5dc1-9777-e7215eba5676 | note | Verification Activity: By - ENG
48d6e870-f152-424e-b3c3-26f57a9146e4 | signoff | AUTHORITY HOLDPOINT
98a59641-9cb6-4168-be02-957a628dde17 | checkpoint | 3.10 - Partical size distribution: Structural Fill
dab1dd7a-d693-5133-b919-df7aa64e5f37 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
e3a97975-420b-57ae-a687-b0377de4c187 | note | Acceptance / Conformance Criteria - Max Particle Size 53mm
461aeadf-c94b-5b03-b446-d2159ff668b5 | note | ○ Max 10% passing 13.2mm sieve
c73b2088-748b-53b7-a0a8-93bad629338e | note | Standard / Specification - Appendix XVIII PS 17.4.3
2a649142-0f57-5b0a-8d1f-59b45a834368 | note | Verifying Document - IANZ Accredited Report
7803a696-6367-5ed4-b038-a65811b3512a | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3
c549abeb-24c1-5d20-b542-1b46c4567fd5 | note | ○ Results to Engineer 2wks before importing
5eff5c6b-283b-54ed-bb3d-a656b5be6a1e | note | Verification Activity: Activity - HP
b8e4d08e-d642-5834-8c62-099be6365289 | note | Verification Activity: By - ENG
4ae476b8-2be4-49d7-a315-a03ed3d94409 | signoff | AUTHORITY HOLDPOINT
383aee62-7877-41cf-85aa-ef4265055d80 | checkpoint | 3.11 - Weathering Resistance: Structural fill
1c268146-b78c-5c07-9a80-7a9fa9b4063a | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
59a415f2-5d98-52b1-aed1-fdac1b9e870e | note | Acceptance / Conformance Criteria - CA or better
55732fd8-bd7b-52c6-a03a-85ac64b177f2 | note | Standard / Specification - Appendix XVIII PS 17.4.3
b5c20e00-ca82-5f1a-89be-f859fa68941b | note | Verifying Document - IANZ Accredited Report
741436b4-8f07-5152-877d-6cad04ba6210 | note | Testing Quantity Required (based from schedule qtys) - 3 Tests Per Material, Per Source
c8841921-fe7f-5fde-99cb-a5aaa6b09578 | note | ○ Results to Engineer 2 wks before importing
c729e56e-4583-56a5-8b8a-cfb47ce367f5 | note | Verification Activity: Activity - HP
176b4bab-199f-527e-aada-6fd97c42993d | note | Verification Activity: By - ENG
2d1963a2-3bef-4e80-877f-f660a386cc82 | signoff | AUTHORITY HOLDPOINT
71b4838f-90e2-451f-9094-872c6418d34a | checkpoint | 3.12 - Magnum Stone Block
f9a458ed-0c77-5bb4-9b05-8f789e9358bb | note | Detail - Magnum Stone blocks are to be supplied by an approved supplier.
132a05c3-390a-5382-b63b-36865d65ed32 | note | ○ Concrete Compressive Strength
bc94ada1-f708-52a0-a543-72c1652c10f0 | note | ○ Moisture Absorption
3b7ea4a7-258e-5e3f-8a45-e35627df3ac4 | note | ○ Defects, chips and cracks
42c124a9-1a66-59e1-98d3-efc046838e22 | note | Acceptance / Conformance Criteria - Minimum 28-day
aa328ad9-ea37-5a81-a82b-92873358f8bb | note | ○ Compressive Strength of 30MPa (min.)
820493dd-a9e2-545e-91e4-1ad9eead3af8 | note | ○ Less than 6%
c56836c4-b006-58d2-b75c-8c5d80979799 | note | ○ Every Block
47141547-db87-52ca-8a32-fecb83a16afc | note | Standard / Specification - NZS 3104: 2003, AS/NZS 4456:2003 Method 14
388e6df0-7929-5021-a128-718c6eab3857 | note | Verifying Document - Supplier to provide QA Documents, Visual Inspection
a5e133bd-c06f-584e-8c57-4c376e94e36e | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
5ca5492a-71fa-56d4-9833-419baab7f68d | note | Verification Activity: Activity - H
afb475cc-7fe2-59f7-9a30-2af06a5a5763 | note | Verification Activity: By - PE
21204fdd-16e7-41da-9f66-1aef633ea8f0 | checkpoint | 3.13 - Subsoil Drainage
23b836d2-9759-57ff-a671-acf18eeb824b | note | Detail - Shall be 110mm diameter NZTA F/2 compliant smooth bore perforated pipe with filter sock
09310f96-e40e-5b71-9f65-8cf8d5dc5b12 | note | Acceptance / Conformance Criteria - Engineers Approval
05ba9036-37da-503f-a706-13d7c9998740 | note | Standard / Specification - P.S. 21.5.17
fd9d16b5-1f57-5845-984c-53aa46046862 | note | Verifying Document - Material certificate/NTC
1abba2a6-2cda-5f01-a049-56559d4c5bc2 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
c2308afa-f685-5c7c-a259-248a960cbffb | note | Verification Activity: Activity - HP
e2153b04-f855-578e-87eb-3a2250902801 | note | Verification Activity: By - ENG
a90125e6-c2ef-4300-a270-9a877d810839 | signoff | AUTHORITY HOLDPOINT
24b79012-99ae-4692-821c-7759795ac249 | section | SECTION 4 – CONSTRUCTION - CUT SUBGRADE TESTING
a56e96d1-73f7-4512-b9f3-75fdb153fc62 | checkpoint | 4.1 - Cut Subgrade Inspection
d5162d97-e86d-5b48-a872-6992e4202b61 | note | Detail - Engineer to inspect all foundation surface inspections
9a1c6f6a-81b8-524a-89de-f44a51373ecc | note | Acceptance / Conformance Criteria - Engineers Approval
abd9b0a2-b995-5706-8096-5ae8af1aa5bd | note | Standard / Specification - Appendix V
c885f374-f95f-55c2-bd6c-66e893d88817 | note | Verifying Document - Visual Observation
ccab140f-5e8f-5d18-976c-36943a2800d2 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
e5cf2846-4af9-5c26-b716-c509aaf37132 | note | Verification Activity: Activity - HP
335e60f0-3421-5d8e-a3bd-c2fdb8abd57e | note | Verification Activity: By - ENG
7707d1e3-d6d7-49cf-b9a0-f09540b103a9 | signoff | AUTHORITY HOLDPOINT
2f57d7f4-be2c-4567-a5ce-b09d139b3e23 | checkpoint | 4.2 - Cut Subgrade Testing - Cohesive Soil, Shear Vane
b38459fb-f6be-5f5c-8b87-4ca3960bfc8f | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
bf5b2847-3929-5afd-a83e-8324efee4f5b | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
0ca18127-1cca-5b81-bd4f-af6064bfb4fb | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
8ef0eb90-e874-54e6-afa8-73b492b8ac9d | note | ○ Single Test Min SU: >50kPa, 2-3m deep
9d4ba0d3-633f-5565-957a-4fd94b78cee8 | note | Standard / Specification - Appendix XVIII
1b10d9a4-def1-57b0-aa0f-4c97e691afdb | note | Verifying Document - Shear Vane Report
0958a484-0957-5ed7-bf07-a87b2f8fbd1d | note | Testing Quantity Required (based from schedule qtys) - 0.5m interval, 4 test per 400M2
dc0f45cf-573d-542f-8cc7-5b2b1a7b0519 | note | Verification Activity: Activity - I
43146430-9d75-5451-bde1-bc8e80e0e9e3 | note | Verification Activity: By - SE
e6e2c49f-86dd-4ad0-a693-03442f40f61c | checkpoint | 4.3 - Cut Subgrade Testing - Non-Cohesive Soil, Scala Penetrometer
5e61f5cd-ed14-5f95-8d65-5add5c9b926d | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
ebdebe13-ad43-5a0c-9ae0-7c37de419a1a | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
758dc7c4-0078-57b7-a3ec-e28627a3d90c | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
6f5f1fd4-c62b-5c50-a58c-03e7e4a8950f | note | Standard / Specification - Appendix XVIII
9c8215b6-c62d-5243-b402-03045b948d18 | note | Verifying Document - Scala Report
d6d8c6bb-40ef-5c2d-8770-ce38b84e94cf | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
e88fa7af-0265-5c52-a1e3-edcd9d117dd3 | note | Verification Activity: Activity - I
21b0b4e0-df1b-5441-9e40-55221a7bb9ce | note | Verification Activity: By - SE
1da3e624-f42a-495f-80d9-7ab7d84b5b2d | checkpoint | 4.4 - Cut Subgrade - Import Structural fill, Release of Hold Point
0410041d-5ea0-5567-96d9-05a08cafed67 | note | Detail - To release the subgrade hold point and be able to start placing the Magnum Stone Blocks, the Contractor shall provide written certification that all inspected and tested subgrade complies with the requirements in PS 16.6
37d35a75-1b10-503c-bbab-2139d4c59da3 | note | Acceptance / Conformance Criteria - Engineers Approval
33b099e9-aa5c-5857-97be-5a26231d8b3b | note | Standard / Specification - PS 16.9.3
db993219-8716-54d0-ac3a-5428a8c2beb9 | note | Verifying Document - CONQA Approval
e28b38ec-c49b-5415-bc9a-928d29eda419 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
75f233b5-d67a-541e-9920-f881e2657f43 | note | Verification Activity: Activity - HP
716e43a5-87dd-52a2-9df0-05cded332963 | note | Verification Activity: By - ENG
39e596e2-4717-43ae-aea9-9e15fc2c35d0 | signoff | AUTHORITY HOLDPOINT
3e6948a3-596e-424a-8456-88fd290fe985 | section | SECTION 5 – MAGNUM STONE BLOCK
39e4f3ae-2fda-4d98-96a0-1dcedddcdf03 | checkpoint | 5.1 - Leveling Pad
aec1489b-2743-589c-bbe5-7ec56a0eb55c | note | Detail - The Contractor shall construct a 150 mm thick levelling pad on top of the subgrade using AP40 to accept the Magnum Stone Block wall.
9e333e18-3339-53d5-98f9-159cb4469f2b | note | ○ Aggregate to be placed on geotextile filter fabric
b5ddc03e-e0d6-514d-81d8-7402c64bbe83 | note | Acceptance / Conformance Criteria - Engineers Approval
f32d636a-a469-53eb-9c56-47b1197c8505 | note | Standard / Specification - As per Drawing (23273502-WSP-DR-GEO-0414)
b6b1c56e-af99-5f8c-adab-bacda9253e9d | note | Verifying Document - Site Photo / Checksheet
c1001b06-cef7-5c2c-8de2-c154b56befc0 | note | Testing Quantity Required (based from schedule qtys) - Prior to Magnum Stone Block installation
c30af990-ff71-57d9-aa86-ed26bada9584 | note | Verification Activity: Activity - I
eda374d5-752d-5fb3-99ea-4ceef3fb531a | note | Verification Activity: By - SE
cd09b626-350b-4218-8020-6a8991c8dbe2 | checkpoint | 5.2 - Installation of blocks
a6836e3a-556a-5073-beac-dd372a18482f | note | Detail - Blocks to be installed to the height and location as detailed on the construction drawings. The table below details acceptable tollerances
9d396c09-58cc-5cd8-a66c-e7bdccac84f8 | note | Acceptance / Conformance Criteria - Engineers Approval
cba86cd4-e3a3-5633-a452-f65aaa1c4ecf | note | Standard / Specification - As per Drawing (23273502-WSP-DR-GEO-0427)
ca3a0513-3eda-5c9f-9737-e6eee7897723 | note | Verifying Document - Site Photo / Checksheet
e7b9db07-c47c-51a9-8ad7-a209f8ac0945 | note | Testing Quantity Required (based from schedule qtys) - Each layer
d88f103e-e6b3-579b-8540-b5ba30c4aa23 | note | Verification Activity: Activity - W
a444af70-6fb9-556b-b994-e0de870e29d9 | note | Verification Activity: By - ENG
477e7e82-30dc-4c9f-a3e2-7b5c6759dd3d | checkpoint | 5.3 - Drainage Installation
5314e1b0-0b59-5aa8-83a0-8005fb17e116 | note | Detail - A 110mm Drainage pipe wrapped in filter sock is to be installed along the internal perimeter of the blocks.
914b75fd-e261-56bb-8167-21793a9fffe6 | note | ○ Core through Magnum Stone blocks at 10m c/c, install PVC subsoil outlet.
136f4816-327e-593d-8966-fc16222d5d9f | note | ○ Internal block void hardfill to be 20/40 drainage aggregate or similar approved by engineer.
9a15ae9f-bde1-55be-aa01-96320409f15a | note | Acceptance / Conformance Criteria - Engineers Approval
c39a32cd-cf17-5d14-ae7c-6e7fab9ce73c | note | Standard / Specification - PS 16.5.8, PS 16.6.10, PS 17.6.3, TNZ F/6
bdad84d0-8316-5f00-a269-4c33fc823af7 | note | Verifying Document - Delivery Dockets/Installation Checksheet
f8388869-5429-5c82-a2be-a4a74fac3e7d | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
b92fca72-5c44-525e-81fe-b89ed7c17de7 | note | Verification Activity: Activity - W
165c3e0b-b6e2-57c1-afc1-c89e28402606 | note | Verification Activity: By - ENG
4b167015-916c-4962-8c6b-ffa6b5b24ce7 | checkpoint | 5.4 - Backfill Installation
c1d7505c-f9c5-57da-b925-1c586d42cf32 | note | Detail - All backfill is to be installed in 300mm lifts and tested as below
d1d90a8c-b45a-5df2-8352-3024f367b156 | note | Acceptance / Conformance Criteria - Engineers Approval
62aa68b6-340b-560e-80dd-bfcd1e9b4a1a | note | Standard / Specification - As per Drawing (23273502-WSP-DR-GEO-0414)
1fb1f622-45e4-5281-8466-beaf57feba75 | note | Verifying Document - Site Photo / Checksheet
6a969ae0-e12c-503f-b3f0-aedce422182b | note | Testing Quantity Required (based from schedule qtys) - Each layer
6b8d5f97-65da-527e-9aca-6cf4085e9d95 | note | Verification Activity: Activity - W
c0658adc-acef-5c12-8207-e0a3c7365be2 | note | Verification Activity: By - ENG
ff388048-4e4f-40b0-8d88-b09b0693169d | checkpoint | 5.5 - Compaction - Clegg Hammer
e963332b-63bf-5333-a0cd-44fbbc61d08f | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
00011752-b142-5300-ba65-fe67afd74d8f | note | Acceptance / Conformance Criteria - Structural Fill
71206277-009e-5df1-a6ef-20b3114a4017 | note | — Min CIV 18
e50d3894-1583-59cb-996b-b31880ef97a6 | note | — Ave CIV 20
d0b75abc-03da-57d0-bf4d-ca24b90f7aed | note | ○ Non-Structural Fill
819ad4b2-d324-51d0-a09b-273288fc79be | note | — Min CIV 10
fdf2f289-af42-51af-9fb4-eb8a4bc384c6 | note | — Max CIV 12
087e8c20-7748-5dc8-a274-98346ebce1a2 | note | Standard / Specification - Appendix XVIII
1468fd2e-07d1-5623-9f2c-36cb2acf207e | note | Verifying Document - Clegg Hammer Report
6f530f1f-bcac-5be2-9dd1-de1de7ae7f0d | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
f4683144-7a08-5895-a86c-231fcaf961a9 | note | Verification Activity: Activity - I
840914ea-c2bb-5704-adc2-d11644f46e98 | note | Verification Activity: By - SE
101e46bf-a223-435f-9b84-20c56e72e74e | checkpoint | 5.6 - Compaction - NDM
a56e8968-0e00-5dbb-ae54-337d2ce19f7c | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
40d7864c-5646-5e86-819b-6154c8da0344 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
7d4fb3a8-82d7-5b6f-9c2b-efa2b9486e76 | note | — Min >92% of MDD
9e8d24b4-a572-54c1-abe5-2eaaef8ed58a | note | ○ Non Granular Material
e5f1528c-aa61-5d0f-ba32-a6050e137dd2 | note | — Max Air Voids 8%
d439e144-04f6-50ea-88bc-24a0b26fb18d | note | Standard / Specification - Appendix XVIII
bdae1113-ee8b-5853-8ba1-b1bc08e6dd80 | note | Verifying Document - IANZ Accredited Report
cf52c6fb-daf8-549e-b648-69122cf231b7 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
a0ded87d-c92f-547c-af72-986713622048 | note | Verification Activity: Activity - I
32178ec0-a701-513e-987f-d4cda1e9ecd4 | note | Verification Activity: By - SE
ac0c73bd-425a-4e96-8dcb-157e88336316 | section | SECTION 6 – AS-BUILTS
a11dd31b-2186-481e-9336-a126f4e38789 | checkpoint | 6.1 - As-Builts
4915ca8f-8236-5733-9e02-dbf802a239bd | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
9a80da68-1653-5f04-958b-f0a2a00d7270 | note | Acceptance / Conformance Criteria - As-build record
89490544-1894-5f80-b33a-7286e59046a3 | note | Standard / Specification - PS 16.7.6
5d8c1ceb-92fc-54a4-bc86-10d79d78b3ec | note | Verifying Document - Survey Records/redpen markups
c56b2c5b-b8a1-5625-8a6c-4b05e7671965 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
25312322-9029-5889-8357-3c62da518dd5 | note | Verification Activity: Activity - D
a37a553e-3e3b-5532-833c-f1738a13b82b | note | Verification Activity: By - SV
64aa3e9a-8c2d-4ed8-918d-d9b8543390fe | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
813ee5ef-8466-5d6f-8fe5-4fe2470d73e9 | textbox | Contractor's Rep Name:
a3336903-98aa-549a-a240-be03a2b952de | textbox | Engineer's Rep. Name:
71dffdc3-9d0d-50ed-8c94-a145b0af95b6 | date | Date:
e9d5c0a1-19be-42b4-a73a-5dd3e4d9f1d1 | signoff | Add Signature
e78d0cf1-e875-45fe-b446-8ac1f6dac104 | checklist | DN1210-SP2-011-001 ITP Northern Access Road & Car Park SW Rev 1 | itp | DN1210-SP2-011-001 ITP Northern Access Road & Car Park SW
e67015af-9410-426f-a746-7cf0f1f5c34e | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
ce545d38-dd19-4cd5-9c0c-069aa4b94094 | checkpoint | 1.1.1 - Extent of Line Setout
a354b213-e455-50c5-a710-b4a5e3bb6675 | note | Detail - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Stormwater drawings.
2c0e9d17-61e1-5b32-ac50-b160bd4bd2ab | note | ○ Identify any clashes before construction.
868704d1-c799-5d53-92c3-81a7e3208e31 | note | ○ Lot - Markup
5bdaa362-b6e6-54fe-bb34-9b0c49a5e20d | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
2e83ccfc-d53e-576a-a0ac-58e327f5803a | note | Standard / Specification - Design Drawings
d8d6ea6e-c72b-52d2-abe4-b5dc685ae003 | note | Verifying Document - ITP Sign Off
58ac4854-ead6-5414-9cb4-a92ef2c0811f | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
4ec5b017-2540-5925-a614-746b4e83e07d | note | Verification Activity: Activity - M
82b4eaba-0cca-5a4e-9e31-11bda341b6ec | note | Verification Activity: By - SE
db17d829-cbbb-4750-8e4e-9f5be3b40664 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
fb5a1504-b6e6-41f5-8b1e-4a502342fb3d | checkpoint | 2.1.1 - Material grading: Materials (Gap65/AP65)
ca133db3-f2da-5ab9-99da-292cc0cef5d0 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
ed893424-ae95-5f77-88ba-ac40a2fc2401 | note | Acceptance / Conformance Criteria - No Particles >200mm
b75911fb-e722-526b-b89a-517e8c7bfb88 | note | ○ Maximum fines 10% passing 75micron sieve
98095def-33c0-5b64-9750-5f48e7489b34 | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
eab337a9-c504-5fce-bc14-d291ffe29438 | note | Verifying Document - IANZ Accredited Report
ed749876-cb89-5e30-915f-4b54a0cc1798 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
9b66dd28-e3b7-5539-9e78-1dfa3979d9a4 | note | ○ 0-400 - 2 tests
9abf8c75-7ed1-5189-b4e4-aaa92b21d8f6 | note | ○ 400-1,500 - 3 tests
cd286d46-a7e8-5122-8676-f17c7991cec0 | note | ○ 1,500-4,000 - 4 tests
92e9f1f7-be4b-576e-b9ec-3bc7555454b3 | note | ○ >4,000 - 1 test for each additional 1,000m3
44ffd20b-cb34-594c-89cb-cf3aca1ac436 | note | – Results to Engineer 2 wks before importing
034f7d73-6be7-5814-b9e9-8efe9c9c21bf | note | Verification Activity: Activity - HP
f751984a-c8b0-5db7-b41f-d15831245ee3 | note | Verification Activity: By - ENG
f91508b0-76a1-4a7b-a559-d675c87e0d23 | signoff | AUTHORITY HOLDPOINT
555ac317-fdb4-4b95-a02e-fa9f54495195 | checkpoint | 2.1.2 - Weathering index: Materials (Gap65/AP65)
36747530-0b25-5286-af61-b41b3a9869ba | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
e95fd968-75ac-5712-b2d1-17bb9ca241f1 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
9b51924f-ecaa-5fbd-bf49-914280c0059a | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
9e2537dd-2243-55d3-ac98-dada22d32ffb | note | Verifying Document - IANZ Accredited Report
2c7f1711-a36b-5ea0-88da-fd530fb0917b | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
37227b3e-d36a-52e5-ac71-d1e77a544d5f | note | ○ Results to Engineer 2 wks before importing
9ff589f3-dea1-56dc-83c7-ab01f35baa92 | note | Verification Activity: Activity - HP
71dcea53-cb05-50a5-915b-f0d2e55052c7 | note | Verification Activity: By - ENG
ca77eadb-999d-4a4f-aa20-532b747a982f | signoff | AUTHORITY HOLDPOINT
cfcbc172-9831-42dd-98b8-5e19a76ff120 | checkpoint | 2.1.3 - Crushing Resistance: Materials (Gap65/AP65)
b4fb472c-b762-523c-935b-900cba38c362 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
f4f525c8-e084-563d-9133-0e8ecbbda65a | note | Acceptance / Conformance Criteria - >100KN
208057c4-aea3-532a-b16e-8558ae893d87 | note | Standard / Specification - Appendix XVIII, Appendix V
06c463e9-3c81-51f2-a466-d17ef69216ee | note | Verifying Document - IANZ Accredited Report
556e5f98-e33c-5123-9cb1-947d9c7f2eb2 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
f0c12eb9-1d1c-5444-bf69-13d986c8e51c | note | ○ Results to Engineer 2 wks before importing
5f5fda4b-a26e-56c3-8c1f-ff170a90a953 | note | Verification Activity: Activity - HP
69fa9c80-a07a-538e-b6e3-0f7b9c1b4ba2 | note | Verification Activity: By - ENG
61434c5c-b91c-4610-a1e6-4435dcc4b6de | signoff | AUTHORITY HOLDPOINT
0b295f03-9af1-401b-8c90-4fc1c4f6a47a | checkpoint | 2.2.1 - Material grading: Materials (GAP20/AP20)
088d0d6e-4c79-5f3b-b87d-731b04ad6b75 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone
c160763b-8a30-5d88-a2cf-06f3c9131bef | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
25946248-f35d-52d8-afc9-733ef11a9a2a | note | 19.0mm ¦¦ 100% passing
247fb18f-a7e8-5b6f-b7ce-35a154454a00 | note | 13.2mm ¦¦ 80-95% passing
68793078-8bad-55c2-8c74-e98b70d0fb17 | note | 9.5mm ¦¦ 64-76% passing
ae7e2c09-cff1-5938-8061-09b5edae9587 | note | 4.75mm ¦¦ 37-58% passing
2fa0c7f5-656d-57e0-8573-5982f374d79a | note | 2.36mm ¦¦ 30-40% passing
210c7458-f16c-5636-9548-3b38ca9422be | note | 1.18mm ¦¦ 18-28% passing
f7ecd939-44c8-5770-a4a3-dd35c2f20c71 | note | 0.600mm ¦¦ 12-22% passing
a4fb4e73-6c52-5da7-9353-2954ea3962ed | note | 0.300mm ¦¦ 6-14% passing
b0b326b4-cb4a-5b5a-88ed-7a9d458dfb83 | note | 0.150mm ¦¦ 2-7% passing
01492f3d-800c-5442-95dc-753cf7bd1654 | note | 0.075mm ¦¦ 0-3% passing
83859514-257e-55b7-9d0d-5d699251e676 | note | Standard / Specification - PS-21.5.7 PS-21.7.2 Table 21.2
0cdeeb9d-7c17-5cb8-ae6f-28fa00a9c827 | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
b5849495-1aa4-50d4-941c-c5677332a952 | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
ea8e6d1c-cd02-5103-b272-f4b4449bb86b | note | 400-1500m3 ¦¦ 3 Test
e05bea5c-df59-52d0-98cb-95a4dc32657f | note | 1500-4000m3 ¦¦ 4 Test
5eb0b367-6793-5d2f-b0ad-f2308a83fc1a | note | >4000 ¦¦ 1 Test Additional 1000m3
58b539a6-8572-588d-997f-796b2fad1e70 | note | Verification Activity: Activity - HP
0ad14b4d-6fb8-5998-924d-a3494603b25f | note | Verification Activity: By - ENG
36e348f6-ce6a-4ca1-862a-33caf9641295 | signoff | AUTHORITY HOLDPOINT
dfa5bff8-fd63-4ba1-9e9e-2e1cb0a904da | checkpoint | 2.2.2 - Weathering index: Materials (AP20)
27eb6be2-12dd-5424-b430-956d38311ebf | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone
c37414b6-e7c2-5ae6-8179-543cc5bb730e | note | Acceptance / Conformance Criteria - AA to CA
b5c6fa7a-e864-5288-94a3-29bc6b809d08 | note | Standard / Specification - PS-21.5.7, PS-21.7.2 Table 21.3
3da1f683-5a9f-554a-b84d-fe1df75a687c | note | Verifying Document - Lab Test Report NZS 4407.3.11
adb85b06-60aa-5496-852f-70e87816c898 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - 2 test per source
605d17ee-0c6b-5cd5-b489-3be9afd027fd | note | Verification Activity: Activity - HP
5bbc5629-3df5-5fb7-85bc-761f457c4008 | note | Verification Activity: By - ENG
5244dc8d-91bd-466b-a2e4-caeb1a74622f | signoff | AUTHORITY HOLDPOINT
8fa0eabb-3a00-4de6-a5de-8b4e0c6df2ca | checkpoint | 2.2.3 - Crushing Resistance: Materials (AP20)
a48c1688-9fbc-5f24-a238-ebb24e8ad7c7 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone
52786acc-b056-5dbf-a23c-65e1c3441ffb | note | Acceptance / Conformance Criteria - >100kN
3f54226f-f618-5718-bc2e-15dfc8cc1573 | note | Standard / Specification - PS-21.5.7, PS-21.7.2 Table 21.4
ad826843-0560-5059-9cfa-cceff466f813 | note | Verifying Document - Lab Test Report NZS 4407:1991 Test.3.10
e74f61fe-0e8d-5bb0-9746-c89326d5f715 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - 2 test per source
197d6552-55c0-51b0-ae0c-aef840f0e8be | note | Verification Activity: Activity - HP
724c4675-e865-5e09-8945-981d9da4a0d8 | note | Verification Activity: By - ENG
5314aaa0-4027-4e68-b7a8-4389b998fcac | signoff | AUTHORITY HOLDPOINT
59c05725-475e-4879-aeff-1c0bc574a784 | checkpoint | 2.3.1 - Pipe and fittings. (Concrete pipe).
2558d6fd-40e1-5144-bf46-f5dbf3f70a79 | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
0103380d-dc6d-5534-a6cb-05556939c46c | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
f6b7b664-7050-55b0-98bd-3f8fd626df83 | note | Standard / Specification - PS- 21.5.1, PS- 21.5.2
ccca0afa-828b-596c-acbe-03eb7c6be4d6 | note | Verifying Document - Delivery Dockets
48ded413-19db-57ac-995a-e3d654f46956 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
4d165fc7-1145-5fa7-8fb9-f9af81544629 | note | Verification Activity: Activity - H
a58c1698-01d5-5b3b-9127-d7a6097aab8b | note | Verification Activity: By - SE
3178a678-01eb-4fac-8495-c5275f5a358f | checkpoint | 2.3.2 - Stormwater- Structure (SWMH, SDMH, GMH, CP, DCP, CPMH, MP, HW)
343701ee-5b62-5f15-a2d4-3af90fb86367 | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the Structure are correct and in good condition.
d81f20f7-f631-5a1e-9c7d-c7467743e2df | note | Acceptance / Conformance Criteria - Confirm diameter and size as shown on the drawings, and that the Structure are correct and in good condition.
09adcd02-a6dc-5111-8986-410cea3c5105 | note | Standard / Specification - PS- 21.5.4 NZS 3109:1997
a4c56a44-063b-5010-b194-b94eb8a4fd86 | note | Verifying Document - Delivery Dockets
76a75beb-819e-53f0-86ad-8b9df59193f3 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
6648e221-a6b4-5bfa-a7fe-7152fc56b7dd | note | Verification Activity: Activity - H
9966992f-130d-5b46-aa92-c40ac5288d62 | note | Verification Activity: By - SE
a2538695-8208-4b95-9c71-3e97ae68216c | checkpoint | 2.3.3 - Granular Material (GAP20/AP20, GAP65/AP65)
dd9bb5f9-e04c-5275-8cbe-68b5c6e706d0 | note | Detail - Confirm Specification and material in good condition.
16584593-20ff-5eea-9877-c78600886553 | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
0393b3a5-0fec-58d2-9c8a-431dde7ea17b | note | Standard / Specification - PS-21.7.2
1d5291ca-c1c0-5a09-841c-3e22c031c3db | note | Verifying Document - Delivery Dockets
b6612a28-aad6-542e-9070-e1f1cbfdd84a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d891804b-c4cd-50d2-8ab7-19a115ce1ae0 | note | Verification Activity: Activity - H
16144a35-7fe8-5ace-be15-931b8747d619 | note | Verification Activity: By - SE
db080fa2-0601-4b96-ac17-bab3dddc9b28 | checkpoint | 2.3.4 - Geotextile/Geogrid
330abe0c-f3e9-5265-b98f-09a83b30d6e6 | note | Detail - TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
f86311be-db7a-5e29-b22c-43da9afd21b7 | note | Acceptance / Conformance Criteria - Minimum Strength Class C & Filter Class 1
f198e79d-4b94-5fca-bcd9-30b21a13af67 | note | Standard / Specification - PS-21.5.9
7d369a58-bfc8-56e6-b548-53e50ea76479 | note | Verifying Document - Delivery Dockets
eb65244a-2589-537d-842a-788768203e6a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
110de767-6f99-5b65-873d-b41ef043b6c0 | note | Verification Activity: Activity - H
9affdf14-c3ec-5ec5-9e07-73afc0437c06 | note | Verification Activity: By - SE
55c5b4d1-c459-4e19-af13-3065cf845652 | section | SECTION 3 – CONSTRUCTION ACTIVITY
9a0a36e7-52d6-47da-a07d-4480f6a7b2f5 | checkpoint | 3.1.1 - Foundation Compliance
937fcdf7-e4bb-5255-bf79-296bc0713ec0 | note | Detail - On Granular or Cohesive Material
10fdd113-e3e6-5081-85ee-de1f56cfc9a5 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
40106a97-807f-5d61-85c3-a48f2dcab21f | note | ○ Cohesive Material: Vane Shear Strength 70kPa
c2fee20b-7eb4-5132-8ee6-1e8b00f64cd0 | note | Standard / Specification - Appendix V Table 21:11
7ff10a2c-7797-5408-823a-ddbba902d5e6 | note | Verifying Document - Shear vane or Scala test result
702ec4cc-1433-51b3-956b-3d2177dd6686 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
d19e8ee4-97de-56a8-b2e1-2d4a54466c85 | note | Verification Activity: Activity - W
034e803f-8389-5e51-8202-5a1a6a6c795b | note | Verification Activity: By - SE
210e6770-a80d-4129-a45c-3690dd50977a | checkpoint | 3.1.2 - Undercut approval
4aebbd4c-e643-585a-b9fc-f8ec1e8fc702 | note | Detail - On Subgrade
23c41b7a-b266-59c5-b02e-df42b857ba90 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
792435f7-15d7-5ff8-9cd1-f79476fbb116 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
3c8ce345-bb81-5c7b-8f9b-1d7fe98d5a60 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
cfdf6d46-a761-59aa-b62d-6390be34bef6 | note | Standard / Specification - Table 21.5
b4e6f30b-7a12-58eb-ad92-47ab36a3a4a0 | note | Verifying Document - Lab Test Report
93fc775b-3bba-50ca-9a27-635695444fd8 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
2903ff19-ff1b-5a7e-968e-a810731fd393 | note | Verification Activity: Activity - HP
e1df720b-d121-5b71-b57f-b8415ce4d5f7 | note | Verification Activity: By - ENG
385fcbd1-ce4f-4782-b96e-ab5ecf8360d4 | signoff | AUTHORITY HOLDPOINT
0c6a9f1a-f550-4069-a628-258be5ed3217 | checkpoint | 3.1.3 - Undercut Backfill Compliance AP65
1df185e7-3525-5248-bf76-e620f0b69baa | note | Detail - On Granular Material
874ab35e-c340-58b6-b357-81cc6e1c72f1 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
bfad3bb0-5dab-545c-832f-4dd89815f8f4 | note | OR
90162b0c-d5c7-5537-908d-393d3c503d4c | note | ○ Clegg 25% CIV
367ac5bd-4e97-5a45-a6b9-a9f6124153de | note | Standard / Specification - PS- 16.5.12
a8f8d3ba-cd4e-55fc-8a1a-121ae73eb76e | note | Verifying Document - Lab Test Report
472b924b-1535-5cd1-a163-c697d6bea27f | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
6433b968-addb-552c-9be1-36cea9ea15dd | note | Verification Activity: Activity - H
66be476b-e0f8-55cb-88de-32306464687e | note | Verification Activity: By - SE
805ffa02-ce56-487a-9e7f-6b68470ca45e | checkpoint | 3.1.4 - Bedding Compaction Testing AP65
edbe44f2-5805-56d7-a965-acc54aff4d07 | note | Detail - On Granular Material
2428c09e-417b-5e38-a1bc-83a0c082e4fd | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
3715b4f0-45ff-569b-a783-dc566eaed846 | note | OR
414f3216-8d46-5f90-af36-fc832d38113e | note | ○ Clegg 25% CIV
8a525aae-06ad-59d3-b212-4618c4bd4452 | note | Standard / Specification - PS- 16.5.12, PS- 21.6.11
bfdc2756-8959-5689-a1d8-e62d8412b0de | note | Verifying Document - Lab Test Report
0202e264-6d54-53db-9bc0-7c62276d6e94 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
32df203c-0c1d-5efa-95d3-a7fa403340ed | note | Verification Activity: Activity - H
f4b93f11-b3d6-5aa2-aebf-ae4ff3c40e74 | note | Verification Activity: By - SE
5f6d267c-48e6-4634-8cbf-9f18df44123d | checkpoint | 3.1.5 - Survey
d8636289-3aac-579e-969e-681e9202b5f9 | note | Detail - Inspection of Structure
3bc72322-f854-58a3-bbe9-160a5d89799c | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
e8838641-08c6-5854-8df5-33b853097d70 | note | Standard / Specification - PS- 21.7.6
fbf613c2-4447-53e6-bd7c-5d77e5005d4c | note | Verifying Document - Survey Data
333fcfa9-d934-5d2f-bf78-133ce117fe15 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
64010ac2-a73e-5557-9aee-4883c6283ca9 | note | Verification Activity: Activity - H
54596e48-f4ea-5da0-bcba-a8de25c009d8 | note | Verification Activity: By - SV
c2b2c59a-1051-4aee-936c-0e105de1fea5 | checkpoint | 3.1.6 - Sidefill Compaction Testing
dc3e7528-848b-589f-9e53-c72a6faf44aa | note | Detail - From the bedding layer to the overlay layer of pipe.
442005f5-f02f-51a3-8d23-04e83f860157 | note | Acceptance / Conformance Criteria - AP20/GAP20
79a2d16d-0034-5984-8485-4b4c0fd4d2d3 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
b18eed63-17c4-5450-9625-bf30a56c3acf | note | OR
a03f7f31-7bf1-5367-b2e4-bbd8104721fa | note | ○ GAP20-Clegg12% CIV
1d36d684-705d-52d4-a5e8-877121ea365a | note | Standard / Specification - PS- Table 21.12
3fd3cf13-e63f-5e46-af1f-88c1bfb9b3e5 | note | Verifying Document - Lab Test Report
fe2607a4-4e4e-521e-8d2f-eb0e88b34b5b | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
e551b49e-b8e8-5bb3-8d0c-202f4f2ecd09 | note | Verification Activity: Activity - H
674b81a5-9cdb-5a6e-aec2-b97ba34451ce | note | Verification Activity: By - SE
c667938c-ea96-47c9-b181-4da2c455a1b3 | checkpoint | 3.1.7 - Backfill Compaction Testing
fde4e242-477e-5e7a-a67c-736c1057ce4d | note | Detail - From Overlay layer to the subgrade layer
6cc647e0-ebd1-53ce-95d1-3ed8db84e3be | note | Acceptance / Conformance Criteria - AP65
4c7d0070-702f-5f4d-8fa3-f6adb133572b | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
b74721ad-6325-5f17-9e89-35f340aa3a13 | note | ○ AP65-Clegg28%CIV
1a89d993-613a-50d2-b0d8-ff7ff33a564f | note | Standard / Specification - PS- 16.5.12
c1a20771-3fe7-5052-8e76-eed083b2c2ca | note | Verifying Document - Lab Test Report
7c0f6435-9305-55a6-b6a0-d5ebb986a78f | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
6ce8624b-3125-5267-8620-f28380a880a6 | note | Verification Activity: Activity - H
bc5c76df-8f4c-563d-95f0-30b6ca074402 | note | Verification Activity: By - SE
f11760d6-9ad9-4665-b7dd-f10a6677be9d | checkpoint | 3.1.8 - Inspection
c4a7cc07-e118-5b2b-8511-6be82c1662ec | note | Detail - Inspection of Structure
a2d1e8d8-3fb3-5b3c-9dd4-59fbcf9a0719 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
3ce69c97-3ae4-567a-ae60-4dd15651c4f4 | note | Standard / Specification - PS- 21.6.11
090863bb-b1d9-5f58-a54b-497f2ceee8a8 | note | Verifying Document - Manhole/Catchpit Record
2be5a458-18b8-559e-8998-2b73014a92b5 | note | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
60ff9b65-ae1c-567b-a756-c166af66f646 | note | Verification Activity: Activity - I
aea640c7-e66d-5f44-b2de-bfc36e2483e5 | note | Verification Activity: By - SE
7ea7e472-2cd6-4f14-bff6-035e93b7e9b3 | checkpoint | 3.3.1 - Foundation Compliance
676a3fda-9be0-5957-9589-769624aea1df | note | Detail - On Granular or Cohesive Material
27a6268c-78e9-5dc8-9f97-d78fedbd80eb | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
cb871c68-ceb3-59b2-8fc7-f70c10788908 | note | ○ Cohesive Material: Vane Shear Strength 70kPa
1772398d-8772-583f-9465-631ee8b009b2 | note | Standard / Specification - Appendix V Table 21:11
e7c83e1e-4ced-582e-b5f3-564707046b64 | note | Verifying Document - Shear vane or Scala test result
5d6d8678-327f-53f8-9981-23f86b4828fb | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
e804da12-4287-5307-96ca-ed7342b869e5 | note | ○ 0-5m: 1 Tests
bc22fff9-6140-51c0-bfb4-ba0308195c68 | note | ○ 0m-10m: 2 Tests
5c9cd6e6-eae1-5278-93bb-677a1a229d6c | note | ○ 0m-20m: 3 Tests
25911c71-7d76-53fd-a5ca-f7270df19f4d | note | ○ 0m-50m: 4 Test
8bca128a-ee20-5b04-b97f-232eb6ea23a0 | note | Verification Activity: Activity - W
0d3334e5-cf3d-577c-8e69-df86637d3d1e | note | Verification Activity: By - ENG
3fcc6695-3f2a-4fc4-8bab-c8a19a48a4f1 | checkpoint | 3.3.2 - Undercut approval
9f85319f-44c8-5a73-be26-b20783e87f30 | note | Detail - On Subgrade
dc7ce754-0672-5590-acd9-a56539200fc6 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
fc94efb9-a47a-54bd-bf32-7bbe0ebc4e6a | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
88362d13-aebb-5b71-a048-6b2c48aa92d3 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
d699d604-670f-56b2-9296-265be757b854 | note | Standard / Specification - Table 21.5
fe28a40d-cbf7-5137-ae8f-0f5ca06dea58 | note | Verifying Document - Lab Test Report
1fbe9172-8a7a-5849-9ff8-b877d52fd196 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
b5e7e3fd-c943-5b68-b9c4-225bc300dae3 | note | Verification Activity: Activity - HP
c6a7ed65-9c61-5ee6-a055-74b0b68060bb | note | Verification Activity: By - ENG
1caa5e2b-8374-4519-9226-2f830ec1fef6 | signoff | AUTHORITY HOLDPOINT
9b1d29aa-06b9-4782-ac32-d43c2dcba590 | checkpoint | 3.3.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
fcb0dd5a-d55f-5ba7-afed-56802fae8e8e | note | Detail - On Granular Material
0cb19960-0f2d-57e9-9070-e07b9cf0eabd | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
c95c5c22-8c98-5fbf-a397-b5ba32ed90ed | note | OR
20060957-994d-5630-b9cd-1fe67757f62a | note | ○ Clegg 25% CIV
6860bdb9-15d0-586e-b050-805afc5288d5 | note | Standard / Specification - PS- 16.5.12
0009d874-5205-53ce-8a91-daa7bf999eac | note | Verifying Document - Lab Test Report
cc7e6d98-d57c-5ac6-bb1a-c3563d7d769b | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
eb3f831a-ddbb-580c-a596-bb0441066785 | note | ○ 0-5m: 1 Tests
46343c54-6320-585a-9de0-140cc419ea78 | note | ○ 0m-10m: 2 Tests
3824edfc-de4f-5596-8d4b-b6fb8c91ac96 | note | ○ 0m-20m: 3 Tests
f070a53b-4f22-59fe-bb99-e36d3a676815 | note | ○ 0m-50m: 4 Test
16043110-61c2-5bca-8882-77fb130a07bc | note | Verification Activity: Activity - H
d71b519c-2e41-5946-8517-177f20d56676 | note | Verification Activity: By - SE
dd59c169-9858-4bc6-a1f5-f25ba968a108 | checkpoint | 3.3.4 - Bedding Compaction Testing
d06c6312-2d7e-51bd-8b7d-dd96abdc2fbb | note | Detail - On Granular Material
9be20c29-d85d-5ce2-8379-3805a923ef38 | note | Acceptance / Conformance Criteria - HS2- 100mm if D<1500 or 150mm if D>1500
caab2628-9468-5096-9d72-f0d178f9f780 | note | ○ Minimum Compaction- Trafficable & Non-Trafficable 95% MDD on metal.
a26afe65-ce2e-5b13-ab50-fde909f77e96 | note | OR
0930649a-2f2e-5929-800d-cfaaf5783f6c | note | ○ Clegg 12% CIV
4edc2446-31be-5a38-821f-4925dff352bc | note | Standard / Specification - PS- Table 21.6, PS- Table 21.12
a0b4b3b1-b9e1-57a1-80a3-8713317df399 | note | Verifying Document - Lab Test Report
db1bfd4d-d47b-5e8b-8c01-6fef25c7e8fd | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
7c8586cc-5c3a-52f9-baad-f7dae2ce2dc2 | note | ○ 0-5m: 1 Tests
bb1ed28d-1b32-5953-90d8-60b1e1a1a279 | note | ○ 0m-10m: 2 Tests
b1fa3ba4-85b5-59b3-abbb-a65ccbfda3aa | note | ○ 0m-20m: 3 Tests
8b7c1345-7081-5667-9ef6-2bd3efc021fd | note | ○ 0m-50m: 4 Test
7bc327c3-776c-512e-8c46-f2cdbdf3284e | note | Verification Activity: Activity - H
b647120e-0219-5db9-8800-1ffea9e42f2f | note | Verification Activity: By - SE
5ab22ab9-4c73-4436-836c-f0fddc48c2a2 | checkpoint | 3.3.5 - Haunch Zone Compaction Testing
b21b28fb-673d-550d-b135-436b7ab6ac83 | note | Detail - On Granular Material
778aa17e-24a1-5609-8005-506185a2ffec | note | Acceptance / Conformance Criteria - HS2- 0.3xD (outer dia of the pipe)
927859d5-1570-5ad8-9277-319791b9fae5 | note | ○ Minimum Compaction- Trafficable & Non-Trafficable 95% MDD on metal.
c28be013-b7e3-50d6-8aff-b2bc0b14f473 | note | OR
ee624cd2-f901-5526-84fb-b773643e7211 | note | ○ Clegg 12% CIV
95e4ba4c-4412-50d4-a549-2c83b2409be6 | note | Standard / Specification - PS- Table 21.6, PS- Table 21.12
03d77240-0aa3-5ab3-8e23-e46fd17c7ef3 | note | Verifying Document - Lab Test Report
e12837ea-18df-5d63-b631-6804803df117 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
2334a296-f8aa-56bb-a540-7a2036e5a7c9 | note | ○ 0-5m: 1 Tests
945adb82-38cb-5ea2-8e61-295b2651d3f9 | note | ○ 0m-10m: 2 Tests
bd54e2ac-07ab-5888-adfd-4d2ae7e4b63c | note | ○ 0m-20m: 3 Tests
cb6ba73c-9b50-5164-bf07-b203e07afe34 | note | ○ 0m-50m: 4 Test
a4e329d1-537d-5df8-a1e4-33c509fbc3cd | note | Verification Activity: Activity - H
5897e5af-eca7-5cf6-9a6c-daf441e21269 | note | Verification Activity: By - SE
cdb89e80-3094-4411-9dfd-9f48c480fd5a | checkpoint | 3.3.6 - Side Zone Compaction Testing
8f312daa-cc06-5acb-8a62-cff80cb5699a | note | Detail - On Granular Material
e2f3eb83-4f9a-59c4-9053-f3bb15e71999 | note | Acceptance / Conformance Criteria - HS2- 0.3xD (outer dia of the pipe)
f741d760-ff6c-5508-918a-34e346feafeb | note | ○ Minimum Compaction- Trafficable & Non-Trafficable 95% MDD on metal.
507e15f4-0918-557d-b3f6-aed26d1caabd | note | OR
38e82186-e7f6-5a3e-8818-46b0b75fe863 | note | ○ Clegg 12% CIV
c274a966-009f-5676-ac19-d0a64d87d6d0 | note | Standard / Specification - PS- Table 21.6, PS- Table 21.12
d0efa61e-fb01-538d-98db-82aaec5631a3 | note | Verifying Document - Lab Test Report
7efdfbd8-9e02-5fb1-8236-4b2e62cfa1f6 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
cd5f6c49-e622-55a8-ac45-74bbc2f62744 | note | ○ 0-5m: 1 Tests
cf80ddcc-fb91-510e-b897-a351e25e096d | note | ○ 0m-10m: 2 Tests
eb4077e8-f854-5060-a1ea-59858537dcec | note | ○ 0m-20m: 3 Tests
4f989d88-4ad8-5d22-b530-d57c0024a831 | note | ○ 0m-50m: 4 Test
970ce5b5-6da5-585a-959d-01219d2fd443 | note | Verification Activity: Activity - H
3c63f871-f658-59b4-ac44-c7e98e1ac400 | note | Verification Activity: By - SE
06941829-6aa6-4128-a663-ad9d70d496e8 | checkpoint | 3.3.7 - Survey
57a15ab2-764f-5927-8f7d-35ac0e09b500 | note | Detail - Surveyor to Setout
576fce27-c751-53e0-a6af-a9938b53cbda | note | Acceptance / Conformance Criteria - Vertical design Setout:
143b8763-b41f-5654-8640-cd751132d7f6 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
4f3964a0-e8ac-5462-a3a8-d534107d0627 | note | ○ Pipes > 1% grade: +/- 20mm variance
e89d610d-d9b9-5f8f-97aa-91f23fb4c15f | note | Horizontal design Setout:
517a120c-408e-56ad-b589-abef7c05dedc | note | ○ +/-30mm variance
bb95b43c-aefb-5b31-b15c-53edf6bf294b | note | Standard / Specification - PS- 21.7.6 Table 21.15
3c589825-4100-5f28-b438-cea4bb392351 | note | Verifying Document - Survey Data
df440cb3-40b7-5736-890f-9b6cb96d31b1 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
0efd7f16-c925-5591-a190-a252375db94a | note | Verification Activity: Activity - H
86bbdb5b-a408-541e-a57d-770a093ab742 | note | Verification Activity: By - SV
200f4304-4ad6-4717-8802-8a5af82721b2 | checkpoint | 3.3.8 - Overlay Zone Compaction Testing
ec2bb660-ccc4-530f-83fa-ff7c79854df5 | note | Detail - On Granular Material
87a918d7-0f5e-5e07-b7dc-48de3f140a8f | note | Acceptance / Conformance Criteria - Minimum Compaction- Trafficable & Non-Trafficable 95% MDD on metal.
6dfb2081-c92e-5696-9f63-3b7262388da7 | note | OR
8c8423e4-943e-5705-90ee-b9e34fe48125 | note | ○ Clegg 12% CIV
1409dad5-e5b6-54ad-9b38-3b6e827c1559 | note | Standard / Specification - PS- Table 21.12
952d1ce4-7c9c-53c8-99b7-ef32ccb0b3ff | note | Verifying Document - Lab Test Report
32dfadad-595b-5ed7-9704-f37039b26399 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
4366ac7e-0779-554a-a4e5-f88780bd8230 | note | ○ 0-5m: 1 Tests
547da90c-779e-553d-a592-64c34ae53742 | note | ○ 0m-10m: 2 Tests
7deb9c38-e01e-5b68-94fb-97f5c154dea3 | note | ○ 0m-20m: 3 Tests
14e7761e-01a2-583b-a235-d0030578ead9 | note | ○ 0m-50m: 4 Test
58856795-38ed-5414-826b-291d9264e75b | note | Verification Activity: Activity - H
b5b5595f-ff93-5502-934d-08cd273f4c20 | note | Verification Activity: By - SE
93695a05-78a7-4211-a8a7-db2d31b0ec32 | checkpoint | 3.3.9 - Backfill Compaction Testing
0572a592-69ff-52ab-a83f-2d8261fd9f1d | note | Detail - On Granular or Cohesive Material
12e38b60-4198-5614-b921-f2e5c56c44e6 | note | Acceptance / Conformance Criteria - AP65
6ef010b7-814f-51fc-b64a-aad507f84309 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
9fd4c50f-4a0a-52ce-9b1a-2bdb83185180 | note | OR
404e1246-4ad1-542f-8ade-66e23691bb37 | note | ○ Clegg 28% CIV
89ae6fab-ffde-570e-82e8-5fd4213fa140 | note | Standard / Specification - PS- 16.5.12
638fbd27-a92b-5b5a-82ec-fc7b7e263c9e | note | Verifying Document - Lab Test Report
219abf95-4c5b-5b4c-acf8-945b2e9bb04c | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
6a78929d-30ad-5b56-82cc-155f57c9bcee | note | ○ 0-5m: 1 Tests
a17ff8b5-e507-5bbb-b789-462db086a6c8 | note | ○ 0m-10m: 2 Tests
133828a5-f5e5-5d94-abb2-869738036f85 | note | ○ 0m-20m: 3 Tests
1894a500-ce10-59ca-a74d-3005847b5430 | note | ○ 0m-50m: 4 Test
9d7e0e54-852d-53c0-9bf1-bd88e602bb15 | note | Verification Activity: Activity - H
e1d00619-d4d4-58a5-a9ab-4b377517a396 | note | Verification Activity: By - SE
95fcd6a7-0477-4946-bcb9-3dc14bdd1b03 | checkpoint | 3.3.10 - Inspection
a556cb1d-da28-5b9f-b9a6-cbe2adce247f | note | Detail - Inspection of Drainage line
cf2a8da9-8b8d-518e-96f8-b22c13df23ca | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
178010cf-fac3-5406-adb8-4778bab6cad1 | note | Standard / Specification - PS- 21.7.6
aca0058f-f393-5154-8a4d-a18d4bff4300 | note | Verifying Document - Drainage line record
d2951276-b8b7-55f6-84b0-66bc4481c8bf | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
7d64dd19-eb2d-5bfb-9195-8d9668dc6950 | note | Verification Activity: Activity - I
60661a30-8eca-5d3e-94bb-8ebe04816d1f | note | Verification Activity: By - SE
9b761284-d9aa-41aa-af8c-2b8a0e87838a | checkpoint | 3.5.1 - CCTV Inspection
d49e80ad-7b2b-52b0-9a75-c455a8036550 | note | Detail - CCTV stormwater pipes at completion of trench backfill but prior to final surfacing (pavements, etc.)
af31e219-6cc5-5cc4-aae9-995c627c91dc | note | Acceptance / Conformance Criteria - Every stormwater pipeline 225mm diameter or greater.
645cebd1-8eee-5879-a375-7f6310ee0f82 | note | Standard / Specification - PS- 21.7.6, PS- 21.7.8
29eee0cd-cf78-5f03-ae1c-df8fb5ae6a6a | note | Verifying Document - CCTV Report
23e103ad-3b74-50dd-b92e-ab4b3d1d9633 | note | Testing Quantity Required (based from schedule qtys) - 1 per line
01397da3-e47a-5972-8b1e-79ec4fca96c0 | note | Verification Activity: Activity - S
c1b94119-e9b5-519b-b5de-ae1fbfe5d36e | note | Verification Activity: By - SE
1fe8e85b-80e7-48f9-8706-b76dff5f06a8 | section | SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
7d4e354c-2cd1-4847-92e5-eb7014956590 | checkpoint | 4.1.1 - As-Builts / Redpen markups
02cde2a5-13d9-541a-b2d1-1828f9b64bd5 | note | Detail - Quality Check on New Works based on the tolerances in RITS
bb7a3b99-a033-5eda-a6a9-a956e9083db0 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
79de9d03-fcde-54ff-a59a-42a9a121a4ad | note | Standard / Specification - Project Specifications
7517caf5-5a88-5063-8cee-ccccc08f7904 | note | Verifying Document - Red pen markup only
6f78fb93-46af-5d19-bc7b-e239d7f2ad52 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
86e11a75-1fdd-520a-badb-413cc5f72891 | note | Verification Activity: Activity - H
6a024b53-00ac-52f8-bc65-90615f7cbf78 | note | Verification Activity: By - SE
3ad58a6a-1bfa-4803-8523-d630fac8e570 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
f91e0457-de9b-53e4-aa43-e31fddd75f56 | textbox | Contractor's Rep Name:
8c0c650d-b74a-505f-b43c-af3f3f2b0c76 | textbox | Engineer's Rep. Name:
12adb2e8-471c-5d34-823b-aa08cb816f76 | date | Date:
fd13ab6e-f7dc-46cd-8d4b-ffcdb8d94ddb | signoff | Add Signature
8ffa08a8-155e-42d3-8089-05e5d8374421 | checklist | DN1210-SP2-011-002 ITP Northern Access Road WW Rev 01 | itp | DN1210-SP2-011-002 ITP Northern Access Road WW
c0516b1f-b74a-4462-ab17-3a2769afa55b | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL , PERSONNEL & THIRD PARTY APPROVLS (P&G / ESTABLISHMENT)
1d1cbe15-ec67-4064-90f3-e62b78146bc2 | checkpoint | 3.1.1 - Pipe Laying
ead4b2f3-f2ea-58e6-a7fa-8282af074ae5 | note | Detail / Activity - Method statement
c09d6444-2e2c-5537-a4d8-bcac2a3d09ce | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
a0d666a0-4ac8-5bb8-a7b1-96949e0cb626 | note | Standard / Specification - PS- 22.3 Appendix V
babfcdf2-fc44-50f3-8b73-9b1a9fd7e63d | note | Verifying Document - Wastewater Construction Work Pack Sign off
7cef4b37-ead9-5b4a-a903-3d1c1f057ef8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
d4b07281-5d86-51b6-a064-4d19d0c7e798 | note | Verification Activity: Activity - HP
c5ae5a47-3ee2-5270-ac62-8694113e3b26 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f3067016-8003-57d0-b66f-033264f53c89 | note | Verification Activity: By - ENG
58442386-f2f0-44f6-942e-4c06807844d8 | signoff | AUTHORITY HOLDPOINT
35124f92-bb12-4899-bede-bbdfea45674a | checkpoint | 3.1.2 - Pipeline Pressure Testing
0a7f8788-cc05-58f7-9c69-73bd273294bf | note | Detail / Activity - Method statement
34ec6b7f-88c8-57fc-839b-d8e05222df0e | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
d1592f40-5d9d-528e-8b55-564cdd46f167 | note | Standard / Specification - PS- 22.3 Appendix V
8dff1487-23a9-58be-9ba1-b6ee28a5b915 | note | Verifying Document - Wastewater Pipeline Pressure Testing Work Pack Sign off
c83ad616-3b90-5220-b35d-609aa56dcfa8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
56b79ddf-3953-5011-951f-b9e4ad921f43 | note | Verification Activity: Activity - HP
cce30105-2790-5872-bff9-cecad9b038ff | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
fb5b4c5a-9411-57f9-b6a5-910687a29ae4 | note | Verification Activity: By - ENG
2bc3466f-1f10-487f-8c05-46d605e84945 | signoff | AUTHORITY HOLDPOINT
1dfda066-2dcf-4b9d-9e54-c32f72aacfd5 | checkpoint | 3.1.3 - Extent of Line Setout
ec6bdcdd-65d1-5b01-b2d1-e7b1472bd231 | note | Detail / Activity - Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings.
a78a4467-d77a-578b-b46d-8ea1a9b67bf4 | note | ○ Identify any clashes before construction.
a759df0b-aac3-50e9-aca2-623c561f2aa0 | note | ○ LOT- markup
3048a279-2e18-525a-a2bc-e14a7ea0f18a | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
2d8c022f-3844-5c2e-bbf8-eb0a4ddcc110 | note | Standard / Specification - Design Drawings
35552e7f-72d6-5794-8f05-b516586b8b35 | note | Verifying Document - ITP Sign Off / Mark-up
a636a4e6-2791-5d0c-b4af-15d91e1c41b0 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
7f5e23f5-d782-5a9b-9355-d9c270463cca | note | Verification Activity: Activity - HP
748cf6b7-f158-5551-b264-50ad1ccf73d0 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0ddfd5ec-ff97-5610-8b14-b013cf14674b | note | Verification Activity: By - ENG
e8175fe1-d598-4478-8d17-83a1642376f8 | signoff | AUTHORITY HOLDPOINT
b677c0f6-2689-47b8-a135-99fac279d4f1 | checkpoint | 3.2.1 - Material grading: Materials (Gap65/AP65)
4b4840ab-7808-5b36-99cc-51c8e792aa35 | note | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
02367490-341f-5d51-b29c-da49f66dc155 | note | Acceptance / Conformance Criteria - No Particles >200mm
8adbbb53-282a-53f8-9566-ac5f0e6f42f3 | note | ○ Maximum fines 10% passing 75micron sieve
52aa14eb-6fcb-59b6-9aef-c8df68ad4648 | note | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
29c4c77f-c265-58c2-a2e2-7a07dbc4739c | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
f99ef5f1-b537-532c-babb-50ec3cb30723 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
a558baf3-6b15-5c28-940a-b9e97e3582c1 | note | ○ 0-400 - 2 tests
242161bf-736a-5c2f-b2b5-36c7c7f95980 | note | ○ 400-1,500 - 3 tests
1af379df-f1ed-5431-b06b-0ae416060dc9 | note | ○ 1,500-4,000 - 4 tests
a7387981-de9c-5dba-ada5-fcbd92b49559 | note | ○ >4,000 - 1 test for each additional 1,000m3
84eba472-2df4-5a64-a4a7-ce243384a7b2 | note | — Results to Engineer 2 wks before importing
3549963f-3ea2-547f-8d4c-a2e806a3a3f3 | note | Verification Activity: Activity - HP
c36f953c-e732-53cf-89de-47efbd118e82 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
def88c4f-b225-53e3-a618-2f39fd8a99c5 | note | Verification Activity: By - ENG
e3abde2f-089c-48a5-a517-603a8ae1c213 | signoff | AUTHORITY HOLDPOINT
a83b8ff8-35ee-4e8f-82b0-137b0e70fa53 | checkpoint | 3.2.2 - Weathering index: Materials (Gap65/AP65)
2a75032f-ff3a-57ba-b58e-954656102a15 | note | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
2cecce28-9392-5ffb-8acd-af24fce87733 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
a79919ac-289e-5413-b00f-07a1a153fbeb | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
e3eb71e6-bba3-56c8-98e4-634da35340e3 | note | Verifying Document - IANZ Accredited Report
08769aa8-54a8-56cd-b591-d0162ac15b89 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
e2c575eb-4522-55df-a1f8-bddcaf90a388 | note | ○ Results to Engineer 2 wks before importing
f19b71ba-c091-5743-bf4f-6b761e22e949 | note | Verification Activity: Activity - HP
2e86112b-6b2b-520e-bbc6-0c31a60685bc | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
23865943-3c67-5e78-a729-4f2cb9f6e976 | note | Verification Activity: By - ENG
cd8a9d66-ac16-48c4-9fd1-68e3ef73f8ab | signoff | AUTHORITY HOLDPOINT
8001771b-2d46-470b-9bbe-4b6d96b63aea | checkpoint | 3.2.3 - Crushing Resistance: Materials (Gap65/AP65)
6b391a0f-795f-5a53-8622-8208007fc264 | note | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
a5213fd9-d47f-5dd5-9ee8-9ff2568764e4 | note | Acceptance / Conformance Criteria - >100KN
777bceae-120e-50b5-87e2-4275c1a61525 | note | Standard / Specification - Appendix XVIII, Appendix V
b6f75132-6c85-5a12-9fd7-6ace066140b9 | note | Verifying Document - IANZ Accredited Report
315e8bf4-b2b9-5633-9afb-1455c15a36f6 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
7e7f975f-5d64-5abe-9c35-4cbaaef25a7b | note | ○ Results to Engineer 2 wks before importing
9c6cac51-b163-517c-84ee-ebbb0c8423b6 | note | Verification Activity: Activity - HP
6b76e79b-11c7-531c-a035-6d7e0b837739 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
2ba63d36-2cf9-55d4-8f8b-880f4051f7be | note | Verification Activity: By - ENG
eb99a4b3-0abc-4d6b-8271-d7b049e56a7e | signoff | AUTHORITY HOLDPOINT
402e8c04-11fb-431e-9d93-d3678ecc6236 | checkpoint | 3.2.4 - Maximum Dry Density and Optimum Water Content
2697c12e-ea11-51c7-9101-9724d2375040 | note | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
6880aa81-b560-5cc4-b69a-29542c6a53aa | note | Acceptance / Conformance Criteria - Report Value Only
be168ce1-cc7d-5294-b54c-03afca3cd7e7 | note | Standard / Specification - Appendix XVIII, Appendix V
8a9a8866-13bb-5bd6-884b-98043824e2c7 | note | Verifying Document - IANZ Accredited Report
0c5221c0-dbea-5570-9f2e-ab50a0447679 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
14b5a25c-f36d-5eed-90cb-4baaaf4c9afd | note | ○ Results to Engineer 2 wks before importing
aae85cda-9788-52cd-8f6b-0f4203000706 | note | Verification Activity: Activity - HP
b2030bbc-e105-54d1-ab6a-3f5a49dfbe0c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
25958770-aaae-59a0-871f-e6eb6e105869 | note | Verification Activity: By - ENG
9c8bdc7c-1f68-4a8a-a17a-5ab5ab20c99a | signoff | AUTHORITY HOLDPOINT
f376a88e-8f7e-45a2-88ce-931c41edd993 | checkpoint | 3.3.1 - Material grading: Materials (GAP20/19mm chip)
65cf6d4c-032a-5d27-9506-2f6f1c131279 | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
8240472f-3d21-594d-8251-c187f2346ddd | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
739ff01c-3f66-5971-ab3e-a6d40a8db598 | note | 19.0mm ¦¦ 85-100% passing
12aa1d1d-a3a7-58ed-86ec-2bf0b21cfcd9 | note | 9.5mm ¦¦ 25-55% passing
f5c33191-d8dc-5e55-a8a7-784deacf6fde | note | 4.75mm 0-10% passing
671fb3c8-23ce-5cfe-bda6-54f4cf5ffaaa | note | 2.36mm ¦¦ 0-5% passing
ccb93253-ae49-5f62-9b14-6dd459f39fcc | note | 0.075mm ¦¦ 0-2% passing
c1cad202-913f-5313-9377-9ba1059aa5bb | note | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
f1db4353-9095-543e-8f0d-333a0d833718 | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
210965dd-d2e7-5dc4-acb7-bab675956888 | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
eea04d66-c2ee-5cb0-b351-0cf85ca8c905 | note | 400-1500m3 ¦¦ 3 Test
58b5f5a5-6e3e-54ec-911d-559dd70cb4d1 | note | 1500-4000m3 ¦¦ 4 Test
21bff47b-09ac-5c51-8533-8dc587b61809 | note | >4000 ¦¦ 1 Test Additional 1000m3
b6641f42-dece-5e3d-afe1-ab071d6a3d5a | note | Verification Activity: Activity - HP
87d7a3a9-8665-503c-a065-0dd4e5de6a6b | note | Verification Activity: By - ENG
471411f1-12b8-42e4-802d-7599b5a56911 | signoff | AUTHORITY HOLDPOINT
38757c07-2a0f-4986-98fd-4ccef0936d26 | checkpoint | 3.5.1 - Pipes (PE/ PVC)
ff652624-6c10-50c8-ac54-7039d30772d2 | note | Detail / Activity - Manufacturer's record and location of extrusion plants.
6aa88aca-822a-5a59-9ac7-adee0deb2328 | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
1305d11e-a493-5479-92f8-089fb47a8d70 | note | ○ Full Traceability information and certification of analysis for the resin batch.
85a935f4-bd08-5499-a85b-80d149876f36 | note | Acceptance / Conformance Criteria - Full Traceability information and certification of Material and resin.
afd094b2-1de8-5ad1-b7a8-f0d9d79c3876 | note | Standard / Specification - PS-22.4.1 (d)
75bb643a-8f24-5a27-a539-c6008a426ecd | note | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets
1e015dfd-bb0e-5f71-b9c1-5b9e81fbeef5 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
d52e9db3-045a-5ab0-97f4-c9bfb771c1b2 | note | Verification Activity: Activity - HP
4e1a0925-2b5c-5b66-a9f9-dcd267510b2f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
559fb6b6-f4ef-5e91-916b-13726559d901 | note | Verification Activity: By - ENG
7fd35a20-f3cb-4d51-a7aa-6df638c6c9f1 | signoff | AUTHORITY HOLDPOINT
dde846cf-111b-4b86-a24b-d2cb1a2342a7 | checkpoint | 3.5.2 - Green Dome Odour Filter
5a3290bd-d40c-50f4-92a9-9951d2c1ba40 | note | Detail / Activity - A Green Dome Odour Filter (Model GDOF36) complete with DN150 ducting.
1d04fdc7-043c-5056-848b-5447f56268a3 | note | Acceptance / Conformance Criteria - IFC Drawing 0324-1
bdd37e1f-5527-5272-a887-fbc36956b167 | note | Standard / Specification - Model GDOF30
d59b86f7-76fd-5c48-ab8b-8b323e7b2e10 | note | Verifying Document - Delivery Dockets
817b4d40-7d53-58d6-ab08-69be7f7c42fc | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
3c432300-0cc9-559e-978c-51f55dd8c45c | note | Verification Activity: Activity - HP
9eef79f6-cf32-5136-ae68-b13db2581077 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a667a7ed-0006-5993-94b6-9d60a21de9c0 | note | Verification Activity: By - ENG
acb27158-b276-4371-aed0-b74241603e91 | signoff | AUTHORITY HOLDPOINT
114deceb-28cc-45cd-981c-32b84c910944 | checkpoint | 3.5.3 - Valves, Adaptors, Flanges and Fittings
13c69f12-edb2-517b-bac6-46701a34853b | note | Detail / Activity - Have a pressure rating no less than the designed pressure.
cecad778-2e71-56a4-911b-dbd724ceedb8 | note | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
1cf76ee7-4280-5d0c-91d8-4498b5dce8e2 | note | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
6a3d1cf0-3f1c-55c4-aae6-fccb0a6b4a33 | note | Acceptance / Conformance Criteria - Engineer approval AS/NZS 4129
a9ff10f2-ed1f-52bf-97ff-7bd57f45f401 | note | Standard / Specification - PS-22.4.2
c9feaefd-aed1-589b-8d08-8a472db6be70 | note | Verifying Document - Delivery Dockets
0ec0c9a5-1043-5189-9e98-68ae413a15cb | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
668fc341-294c-51d0-ae92-b0c368f91de4 | note | Verification Activity: Activity - HP
1158f0aa-5416-53e8-8624-bedd35be7e69 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
2f3e32d5-14ce-511e-8316-5ca557d07a47 | note | Verification Activity: By - ENG
90d6d121-513f-4c5d-8e41-775af9d57b2a | signoff | AUTHORITY HOLDPOINT
3cd86f28-a954-49be-8fe0-d3b4447b9974 | checkpoint | 3.6.1 - Pipe and fittings (PE100- DN250 PN10 RM, DN300 PVC SN16)
4757f810-cbcb-5d13-bb29-7bfbce19b346 | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
d4ed25b8-49ae-5110-830f-4568d0260f44 | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
df9c2a7e-aef0-55e8-b914-7258e0f544d0 | note | Standard / Specification - Design Drawings
e3c17e2f-5f86-5856-9175-40be51413e58 | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
4459511f-8a01-544a-b3ca-acd3689caf7e | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
8029d123-2d07-5bfe-8624-a40c86781d84 | note | Verification Activity: Activity - H
c5ef4ff9-fb9d-5cb4-8c11-6c0275fdcf14 | note | Hold Point (Internal)
20a33b9e-3964-5803-bc56-82e08311ddd4 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
6813215b-e580-5882-97de-1e098796c92d | note | Verification Activity: By - PE/SE
4e2488d4-e545-4d73-b87e-21c7d1f682e3 | checkpoint | 3.6.2 - Valves, Adaptors, Flanges and Fittings
abd2953d-039f-539f-8613-fbcfcc65906a | note | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
eaee87fe-de86-56e4-b41f-bb3a0077088e | note | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
aa0580e5-6fe9-5d44-8a4f-6b5e9daa7eb1 | note | Standard / Specification - PS-22.4.2
722599d5-afe2-5a0d-9902-f8209008b11a | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
c507355f-3ab8-57cd-8bef-9e3b20da72cf | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d58d61d3-4f83-598a-866c-8267aa1e4836 | note | Verification Activity: Activity - H
99de6b43-7ac6-5972-9c16-8923d8ef0eee | note | Hold Point (Internal)
fdf775d7-287e-5867-89f1-7b56e18ec4c7 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
22b0c1c6-b4b3-5651-9205-c9f293c70a4f | note | Verification Activity: By - PE/SE
2cbce9b8-ccd8-44ac-982b-14f25d67207b | checkpoint | 3.6.3 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65)
aefb23a5-de7f-5416-a824-81aa405213ff | note | Detail / Activity - Confirm Specification and material in good condition.
66deb9b8-6e49-5efc-b15e-595dd882b9d0 | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
f30521a9-0dfb-521c-a53b-92dd53deb734 | note | Standard / Specification - PS-22.4.1
23e7bb12-5f75-5bbc-8c32-8421e809ce92 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
be177c13-710d-585b-ac93-a384268050d2 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d89250e3-5b74-583d-be92-0660f89bd112 | note | Verification Activity: Activity - H
9a4a636f-402a-52d6-90dc-e92a0a5441b2 | note | Hold Point (Internal)
4326e7cd-e1eb-540d-aa9f-6646f4b158e7 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
602cf8fe-b1d9-5a9e-855d-3d307d415c18 | note | Verification Activity: By - PE/SE
629923fc-a26d-4362-858b-97b5bf680d0d | checkpoint | 3.6.4 - Bidim/Geogrid
553a8854-97aa-5600-8456-e99262c131b3 | note | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
e0ba7fb6-a386-5b57-8399-23509fe08079 | note | Acceptance / Conformance Criteria - Site Engineer Approval
d9223638-5da5-5afe-81d0-b9ca9bba524d | note | Standard / Specification - PS-22.4.1
9ac542b9-8934-5435-b5e0-cd9433a4a7ed | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
628ea43c-2d39-5ee7-b8b8-d42a32169b37 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
83df0b33-caf5-5556-8c7c-54247162517d | note | Verification Activity: Activity - H
41ae799d-8607-5faa-a3c9-b5cd7bdf952f | note | Hold Point (Internal)
15e8db65-5a35-51c2-9010-e4d3b223cc56 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
00e62b03-f053-579e-901c-09b3442a995a | note | Verification Activity: By - PE/SE
77fdcadf-b66a-4446-a545-7383c1902e82 | checkpoint | 3.6.5 - Manhole WWMH 01
657e779c-909b-517b-8a76-47d53d97f0b7 | note | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
655c1641-4083-5dac-b8f5-552fd1d4ad5f | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
d83edafb-1448-5e32-94ab-8214ef61bb08 | note | Standard / Specification - Design Drawings
2ab6e53f-e702-53fc-a42d-6e80b8e2627a | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
cc4dc670-195d-501d-ba04-b8bf81298b28 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
a4c63441-3d9e-5178-b0bc-e887edc16f54 | note | Verification Activity: Activity - H
21e816ad-b7bf-5831-b03d-51e043626ead | note | Hold Point (Internal)
b078f680-162d-5709-a914-4ea3c899e7c9 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
164a541b-97b5-5b88-8b9c-5d6b9f2cd220 | note | Verification Activity: By - PE/SE
b9e3c59a-5a52-4f22-8f4b-585e08c9d2d4 | checkpoint | 3.6.6 - Manhole WWMH 02
fadc3e1f-6725-5091-8572-fea19ec23633 | note | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
0f660c0e-8529-5aad-a603-6ccf5b85b835 | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
8f163d68-172a-5efd-8ea2-154080288e50 | note | Standard / Specification - Design Drawings
bbb83f2c-aa81-5d6c-9a77-f4c22093e16e | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
906f5f3f-d295-5986-8c96-db2eb52289e2 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
7c67c85c-95f8-5583-8d8f-21ef60810685 | note | Verification Activity: Activity - H
2520ba42-c1c8-58d2-b11d-1ee164e0530d | note | Hold Point (Internal)
c89a0c68-15c8-504f-8509-d1d02b950f70 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
36bfe218-68e5-51c7-b485-7181a1e060ad | note | Verification Activity: By - PE/SE
1746c8f3-3a05-4c87-9b72-4281761e2b33 | checkpoint | 3.6.7 - Manhole WWMH 03
c0add20f-06fe-52a1-a369-8312e4433d0c | note | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
97818500-3554-54be-8469-c8f04326c4f0 | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
6eadcbcc-760e-506f-9e73-ea4cc8913825 | note | Standard / Specification - Design Drawings
f927d4cb-e6fe-5a1b-84f0-5208f3f74e43 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
ec3ff957-b815-5f5b-95ca-658cfaa89a1f | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
0265fad3-557d-5294-a3ff-5b6043bca33f | note | Verification Activity: Activity - H
0ae95610-a8df-5492-8f7b-ba355a81b891 | note | Hold Point (Internal)
56113643-d56e-5b4c-9a10-f803083d886a | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
de060e5b-ef23-5929-ba02-afd7c9be078e | note | Verification Activity: By - PE/SE
dc23b481-cf66-4d19-82bf-eb7d6150cb63 | section | SECTION 4 – CONSTRUCTION ACTIVITY
af48393f-9754-4763-9891-0883f2036017 | checkpoint | 4.1.1 - Foundation Compliance
bd8b3e1b-36e0-594c-94f9-437cc5d7bea2 | note | Detail / Activity - On Granular or Cohesive Material
fc12acd6-a2ec-5a7a-9cbf-9722eb60f3cc | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
6336771d-9d4e-533b-b07a-ab2715854055 | note | (Or)
6abf5b2f-9b80-574e-993a-1b7c2ec6a2ec | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
0b8da93d-1874-58e3-9f4f-dfce4bb50cc1 | note | Standard / Specification - Appendix V Table 21:11
781bd98a-3f9e-597f-93d7-c2316c55e426 | note | Verifying Document - Scala/Shear test result
6d75be24-fada-5a01-887d-264b5995217d | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
036b9dd8-573d-52f9-b0c8-5925f596e73c | note | Verification Activity: Activity - W
dbef2c2d-61b4-5724-9065-363d3d01272e | note | Review of text reports/records or other evidence of compliance
b395777c-c2f3-5542-acf5-af187e3f0d2e | note | Verification Activity: By - SE
9486ab52-052a-4a85-9d6f-68d18e6306ea | checkpoint | 4.1.2 - Undercut approval
ead2071f-ee3e-51f0-87b9-551863fcf7f3 | note | Detail / Activity - Trench Foundation
294d8292-0082-5451-8f85-831a6889ea09 | note | Acceptance / Conformance Criteria - 300mm Max cut
b09bba4e-880c-589f-b3f8-3ce6b0c92d19 | note | ○ IFC Drawing Sheet 320
d317b588-1725-5e71-a431-6b7b5660175a | note | (Or)
d15f99ac-5c4f-5608-8f76-cd463c943922 | note | ○ Engineers approval
4c054d5d-6183-551b-866c-9448336c0383 | note | Standard / Specification - IFC Drawing WST 0320. AS/NZS 2566.2/2002
f121ba9f-965a-5cb7-b2ec-8ffad48e7ef7 | note | Verifying Document - Lab Test Report / Wastewater line record
55275edb-cb1e-5d66-a9d8-bf6b9561c72d | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
99c9dc51-b807-5ca9-9c8e-d278bdfb5bbe | note | Verification Activity: Activity - H
327d9a82-4780-5d88-98c2-5384b6d136be | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
bbfeb864-a1b7-5e64-a645-326bbc23ee4a | note | Verification Activity: By - SE
cb1c11fe-6edc-43a2-84db-cd20217d3fb1 | checkpoint | 4.1.3 - Undercut Backfill Compliance (PAP5)
d3361011-2ac4-504b-bd0b-5d8ff8b776b8 | note | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
452e3a86-c0a1-5183-8407-0e794815c0fd | note | Acceptance / Conformance Criteria - Visiual Inspection
6bfbe2e0-1160-52c8-acee-cb0083916478 | note | Standard / Specification - IFC Drawing WST 0320
aadf2393-2fb7-5476-b28a-e661ecf64de0 | note | Verifying Document - Lab Test Report / Wastewater line record
37e68202-b20a-5e85-91ce-4d699229e14a | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
474475dc-0a34-52c3-8591-7772d69b0543 | note | Verification Activity: Activity - H
8c12e806-5098-57eb-b745-b900c2b1cb6b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8a4e319e-baba-53f7-9d42-bda9ce6f28a1 | note | Verification Activity: By - SE
974b066c-4c95-425e-bcf6-18fa4ea599de | checkpoint | 4.1.4 - Bedding Zone Compaction Testing
bdae344a-54a8-5426-ac65-5216f364debc | note | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip)
ed6e436c-b189-5204-883d-7496e7d19588 | note | Acceptance / Conformance Criteria - Bedding Zone:
826510c0-c115-5386-8aa8-05e473d4e16f | note | ○ 100mm minimum thickness (compacted) over the bottom of the trench.
0615b4e3-0701-581e-acf5-66e6457ff6b8 | note | ○ Minimum Compaction- 85%MDD
5f098d0c-e0b0-5d27-b5ec-5ffc44c3b3b4 | note | Standard / Specification - IFC Drawing 0320-1 AS/NZS 2566.2/2002
8fcf1eef-c593-599f-b5d1-efb5dd71a3a8 | note | Verifying Document - Lab Test Report
045dd9dc-5681-5460-8642-16fab1fe2aa2 | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification.
7c3728ee-d1d1-5d46-a38c-7480498a8295 | note | ○ One test per 10m evenly spaced intervals.
07417a90-69d9-5e46-91cb-58891784c23f | note | Verification Activity: Activity - H
e684dbeb-15db-581b-a651-23708f087859 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
31ded663-bd05-5279-af9c-dfd9773e8bbc | note | Verification Activity: By - SE
a39986fa-d3a8-45e4-8aba-fe1871b59905 | checkpoint | 4.1.5 - Laying of Pipes
995f0c9e-6f21-5349-896f-f9f19407fd09 | note | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
04e398f0-c320-53b0-ba0a-5f9ec8ed8647 | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
776182c3-2044-5188-b61a-208d27006419 | note | Acceptance / Conformance Criteria - As Per Drawings.
274e7074-7e98-5d4e-89e9-79f32364bbf3 | note | ○ Facing upwards
fda410a0-f4d7-54e6-a342-b036bc8b36fb | note | Standard / Specification - PS22.7.1 C
03d59a0c-04d7-5ec4-89ab-3fc9aec1819a | note | Verifying Document - Visual Inspection / Wastewater line record
7b675b19-b106-5a66-a0e0-0fc50b8689aa | note | Testing Quantity Required (based from schedule qtys) - Every Line
8fb06e13-82e1-5545-a1a3-a15413994ed1 | note | Verification Activity: Activity - H
b526eaa6-201b-5676-8235-1f375eb995ca | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f03af113-1401-5b94-805f-b2a8659f2bb0 | note | Verification Activity: By - SE
228cd2fd-e5df-48e2-8318-17528084970e | checkpoint | 4.1.6 - Pipe Installation on Curved Alignments
0d99ee6e-e7d5-5e9f-932a-2b315553ad2a | note | Detail / Activity - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
76e6ad64-aac5-5d20-89b5-610c66292a0a | note | Acceptance / Conformance Criteria - AS Per POP 202
88728cb9-16ed-53e6-8a4a-51882675eac5 | note | Standard / Specification - PS 22.7.1 D
a3236dd8-e84e-51c9-a130-45e9f7643b14 | note | Verifying Document - Visual Inspection / Wastewater line record
bc77f7d0-8c17-5249-ba93-80d87ca72442 | note | Testing Quantity Required (based from schedule qtys) - Every Line
b4d1d0b8-ff73-5e97-9b31-81d00cc14903 | note | Verification Activity: Activity - M
c4dada3c-56b5-54ee-8efd-dbe84ecd6e5e | note | Monitor on Random Basis
087e6df1-6d78-55b1-a89a-c9dccc40d441 | note | Verification Activity: By - SE
b108be29-0e8b-40a8-a449-0ae907c50a1e | checkpoint | 4.2.1 - Flanges
1c4109e4-0cf5-53a3-a37a-eeec08936b1b | note | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
5f2f74b1-0823-5102-9533-540ee78932d7 | note | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
301c3302-f208-516e-a7a7-eb00d180c536 | note | Standard / Specification - PS 22.7.5
2a2d52c4-afb2-5f20-8914-d72fa8d75f94 | note | Verifying Document - Visual Inspection
1eb1a01b-44cd-5ef0-9b4b-8bd2b3e3084c | note | Testing Quantity Required (based from schedule qtys) - First flanged joint
b173298c-a5da-5168-a002-0d80684c73fa | note | Verification Activity: Activity - HP
713c931d-95f2-588e-8f89-7e012e56bbc8 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4a454086-1231-5a87-b666-1870b5fc6888 | note | Verification Activity: By - ENG
f602cc95-2333-4b2e-a189-eba5eceb8aef | signoff | AUTHORITY HOLDPOINT
98db74f7-e232-49e8-aa6a-20e49e2934cd | checkpoint | 4.2.2 - Bends
216b8f91-ab3c-5ba2-9568-b768abda2c84 | note | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
8f9d9bac-a609-52f7-a767-2645d8001a8c | note | ○ Fitting must meets the same PN rating as the adjacent PE 100.
bab7f45a-19cc-5e70-9205-6429aa8a67cc | note | ○ Fittings must be suitable for producing the joints shown on the Drawings.
882cfbf0-6af4-5752-881f-ffdd03d31721 | note | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
42107285-bf9c-5988-b2ca-26fbd55f28a6 | note | Standard / Specification - PS 22.4.2
3b62ad90-0c18-5a9f-8e07-47d2affe9d76 | note | Verifying Document - Visual Inspection
0b0340c0-edd3-5f44-8cab-00eaa93fd4ab | note | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
e60be245-5f17-5910-ae93-71777ec39a1f | note | Verification Activity: Activity - H
fd802314-309a-5dc2-879a-43ba9abe824b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5f5dc600-3418-537d-ae4b-ab8c9db0d83a | note | Verification Activity: By - SE
d0f75895-51f2-4e0d-8eb0-5fdc0fcd119d | checkpoint | 4.3.1 - Butt-Fusion pre construction weld test
60325f8e-e993-57ef-975a-fe3ee83b3da4 | note | Detail / Activity - One weld on the most common size of pipes used for the project.
c1de82af-111b-509b-9abe-3a9392fac026 | note | ○ One weld on the thickest wall (highest PN) pipe
1fe0debd-039d-5f25-b059-dd27f9d21576 | note | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode.
cdbe2a66-c61a-59a2-b385-bb280b25bd11 | note | ○ WMS Report
da7d94c3-d797-59a7-9763-182a9248333c | note | Standard / Specification - PS 22.9.6 (a)
7c834271-9302-530c-b858-8545e79896d0 | note | Verifying Document - Visual Inspection
62d43d0c-d989-5dd1-b88f-232424d755c9 | note | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
9ddf650e-25fb-5b64-a7c1-1ee6f30a02f2 | note | Verification Activity: Activity - HP
8b901bec-adc2-5202-8300-fa2be6b14887 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5e3d03b1-1631-5826-9a1b-d539c2c45e79 | note | Verification Activity: By - ENG
ab21dba3-6c0e-4385-97dd-46458829a63f | signoff | AUTHORITY HOLDPOINT
0bc99c3e-2226-4102-8328-554475a3dda7 | checkpoint | 4.3.2 - Butt-Fusion Welding
e93c8534-031a-5a94-8a73-bd4c62de61e4 | note | Detail / Activity - Use only semi-automatic or automatic welding machines.
6f8fbfe1-02c9-535b-a64f-b760a7211d29 | note | ○ Maintain a site record for all butt-fusion welds.
48bab746-e6b3-5f26-9d26-ce4cadbf049e | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
ce4ff63d-879c-55a8-bf60-e965b8d7c049 | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
31e75dd5-ffdb-503b-9c62-89f9a39844b9 | note | ○ WMS Report
59f4202f-f69a-51db-9f57-d97b604ecc7b | note | Standard / Specification - Appendix 22. PS 22.9.4 C
6da83553-d927-5c3a-8ee2-1d7a2e177e86 | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report
88e08a7a-481d-557e-96f0-8edb3f463d7e | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
5cd7d0f7-ae3d-55c9-b9fc-bd1619fe1654 | note | Verification Activity: Activity - HP
a0dc07bd-440b-5e95-b7ad-0d0caffbf455 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f5d2c2ed-793c-5183-b8ac-d14b886545e8 | note | Verification Activity: By - ENG
123deaaf-b61c-4d84-84c6-0e2a5a1d763d | signoff | AUTHORITY HOLDPOINT
3b891ad1-b7d7-4812-a58c-a1eb56d1e4ce | checkpoint | 4.3.3 - Butt-Fusion Construction weld test
b48dbab9-a859-57be-9b3b-f1a0b4541d3f | note | Detail / Activity - Test at least two welds from the first 50 welds.
83eb6616-f6f5-5a06-bd43-fb0b67dcb6db | note | ○ One of the welds to be selected by the Engineer for satisfactory result.
5d25a591-bfde-50e1-b529-cb29aa78bacf | note | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
c41c8cac-cd4d-5aa3-baeb-92bd2e958d39 | note | Standard / Specification - PS- 22.9.6 (a) (iv)
2e003e17-453a-5698-8ad1-fbdac8658f6b | note | Verifying Document - Test report
5d5e78b4-5c03-5de2-b7fa-4ffb51b9b0de | note | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
5d5a25ff-1945-5c94-8838-b228ddd6b697 | note | Verification Activity: Activity - HP
f484591e-5087-5c45-b057-0801bfe34907 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5c2a9e5a-7e3d-5313-a9a9-82bb4ff1db7d | note | Verification Activity: By - ENG
c391b6aa-c427-47ea-ba87-c8f1dd092ac0 | signoff | AUTHORITY HOLDPOINT
75690a12-f335-46a6-b302-78338ea292d6 | checkpoint | 4.3.4 - Survey
0aa28952-e46b-5093-ba14-85771247e15b | note | Detail / Activity - Inspection of Pipeline Inverts
74e95553-2a80-5545-8316-fba6a27ba5b2 | note | Acceptance / Conformance Criteria - Vertical design Setout:
85ca7ac8-aa17-538c-923a-da2ec66310ca | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
176feb79-b399-5a8a-84c3-559f2c240f4a | note | ○ Pipes > 1% grade: +/- 20mm variance
d94c08f1-016f-5884-aace-e562c6df1e88 | note | Horizontal design Setout:
a651e72d-a63b-5f57-85ea-2d5c44e09bd6 | note | ○ +/-30mm variance
b6029646-d110-5cf8-a5e0-dff3fed2c099 | note | Standard / Specification - PS- 21.7.6 Table 21.15
7bef993d-efc7-582c-9dab-d3ab580a28c1 | note | Verifying Document - Survey Data / As-built record
8c1db5c5-8b5b-58ea-917c-2180098e34a4 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
464bf7d6-1492-5dc5-a1b6-9a09ad7b86aa | note | Verification Activity: Activity - H
14e75a60-8002-522c-807e-8ffa04c05497 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
455b0b04-3432-5743-8f15-68baba75e281 | note | Verification Activity: By - SE
932064c4-33d9-4d8b-8136-a3363b7e0da7 | checkpoint | 4.4.1 - Electrofusion (EF) pre construction weld test
32f41b2c-fefb-5b60-b1b7-4a7372200d95 | note | Detail / Activity - Use the designated welding equipment and the approved WMS.
01ecfe28-c148-5e1e-ba05-255eee4cc7b1 | note | ○ On the largest size of PE pipe used in this Contract
54f83e1c-6bd3-57cf-a2e3-2f18237b6152 | note | Acceptance / Conformance Criteria - ISO 21751 (strip-Bend test) or ISO 13954 (Peel-decohesion test)
7d2d1d23-7fa6-5ded-98a9-bf449aafc693 | note | ○ WMS Report
1d7e6ddc-eeae-534a-a1b0-d95795a15066 | note | Standard / Specification - PS 22.9.6 (b)
1c32501c-1e5e-5008-a050-786357e44537 | note | Verifying Document - Visual Inspection
6d860ce3-46a5-5d33-ab1c-2cd32aab2c08 | note | Testing Quantity Required (based from schedule qtys) - One test welds per operative(Welder)
f44bc6c0-6130-5e89-9679-f0722bba9540 | note | Verification Activity: Activity - HP
dbce0976-0d0d-5fb7-af12-84aba29ce2cb | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5a5238cd-f39c-5a6a-b33d-1765e79d5b28 | note | Verification Activity: By - ENG
d886145b-08cf-494e-ab6f-cab0c2c33375 | signoff | AUTHORITY HOLDPOINT
b579593f-f634-4b90-b44a-e162a0a9986a | checkpoint | 4.4.2 - Electrofusion (EF) Welding
44e671b6-3cf8-5ac7-b8b0-c98a5a5bf87a | note | Detail / Activity - Required if Butt fusion welding cannot be perform.
5fdbe8a5-1c86-58c6-9c3e-c41d903dbd7e | note | ○ EF Jointing in accordance with PIPA POP 001.
1414a4e8-3ae0-54d5-9142-13f70c94e656 | note | ○ The lead welder or welding supervisor must verify on the site record form.
8dee2dde-809f-5a57-ade1-b5c859881658 | note | Acceptance / Conformance Criteria - WMS Report
d8df12d7-1795-54e3-b443-d38abbae2bc6 | note | ○ Checklist (refer to CWP).
7bc7e14b-b00f-55cc-9118-03679d163e4e | note | Standard / Specification - PS 22.9.5 Appendix 22
96b0d7ab-9eed-58f8-a375-d0dda79b28b2 | note | Verifying Document - Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report
2136b5d7-1e47-5d93-bb52-e12030e2fe9e | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
81a31914-96f9-57a6-9dbb-56bba9271224 | note | Verification Activity: Activity - H
91093ad3-f150-54b0-8ae5-6b2f047d677c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d9f74468-35b5-5ea4-9884-2ac73c982903 | note | Verification Activity: By - SE
1a9bf83c-1e42-4b0f-aacb-9dcd5d438f44 | checkpoint | 4.4.3 - Electrofusion (EF) construction weld test
563e64da-a581-5b54-966c-b1335716fd83 | note | Detail / Activity - EF weld quality to be maintained.
44b67138-8d2d-5274-94da-59613770e30f | note | Acceptance / Conformance Criteria - EF coupler and EF saddle testing
1b0778b1-b1d3-58a2-9a26-c6da5d42d8e9 | note | Standard / Specification - PS- 22.9.6 (b) (iv)
dd7b240a-f622-5a5f-94bf-5af394066266 | note | Verifying Document - Test report
7bad6a20-3883-5bbd-b433-f85e78b1b50f | note | Testing Quantity Required (based from schedule qtys) - 1 in 10 test
414de24d-26a8-5c3b-9a0f-0f79a381a71c | note | Verification Activity: Activity - HP
cb22cf5d-580a-551b-8fb4-1ab3b7c8987c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
9c222beb-338e-5eca-b6e6-092a50b30454 | note | Verification Activity: By - ENG
e7649e0b-256b-4cad-bd6c-25c38871d1bf | signoff | AUTHORITY HOLDPOINT
b272261b-883a-4381-96bb-b05c3920b017 | checkpoint | 4.4.4 - Survey
a08be5f4-63fe-5267-82b5-bf8327760f4a | note | Detail / Activity - Inspection of Pipeline Inverts
4e2c4c79-4d3c-53a6-a3fb-f557940f3281 | note | Acceptance / Conformance Criteria - Vertical design Setout:
25cb1311-955f-5783-bb1a-086de2cfa445 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
0ed717d0-2766-518b-a102-93367f0533e3 | note | ○ Pipes > 1% grade: +/- 20mm variance
8db63213-23ad-54ea-930e-c637d09b020b | note | Horizontal design Setout:
065b7bc1-8c74-59b0-80ea-634dba528b63 | note | ○ +/-30mm variance
0f702a45-7b00-50ef-8044-242c7288f023 | note | Standard / Specification - PS- 21.7.6 Table 21.15
9fd7f01e-777a-52f5-9fc9-143a7a8f60ad | note | Verifying Document - Survey Data / As-built record
b197d83c-5f78-5aa0-ad3a-4c7d3afcf4a0 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
5a67890d-74f3-5119-96ff-ac78042ea0e1 | note | Verification Activity: Activity - H
549499f4-2542-59e9-9cca-32d3a94621ad | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8c929077-1cb3-59ac-8d62-a6b1ca00802c | note | Verification Activity: By - SE
cdcdcbd6-7cff-4f2c-8b48-6ac7e1002866 | checkpoint | 4.5.1 - Emebment Zone - (Side Haunch Overlay)
d5060312-fa13-5188-b1a8-4b053fb31b17 | note | Detail / Activity - Granular Sand backfill Compacted in 200mm Layers.
6605fdd4-a4f1-58ab-9c53-dda650741e1b | note | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays .
b092e768-a731-5591-aa4b-710d1e25fffa | note | ○ NDM BS to be Carried Out
33e346dc-aeb3-5f1e-95d7-0d746afb7bde | note | Acceptance / Conformance Criteria - in 200mm layers.
99012fb0-9b17-5df7-99c2-08b43863eec4 | note | ○ More than 85% of MDD.
3b2220eb-798c-5c57-86bf-35904fd57990 | note | Standard / Specification - IFC Drawing 0320-1
7f5c0cb5-8e86-57a4-958d-7e4749e70764 | note | Verifying Document - Lab Report / Wastewater line record
1f01faa1-1786-5c1d-83ff-4d06647c3b8a | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals. 200mm lift
223044de-8342-5355-8ad1-fd86b5410476 | note | Verification Activity: Activity - H
cdd7bace-8a94-57e1-91e4-b1e1b7056171 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6c4b8f9f-df8a-5c09-af79-8ef345092547 | note | Verification Activity: By - SE
893a92ee-a409-4a1d-86a7-357802b46037 | checkpoint | 4.5.2 - Pipe Markers
1b457342-8334-5743-98cd-0f8e743d871f | note | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
f9c94fda-ac4a-5b29-8cc0-e3d883d8f732 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
2a2ac21c-e7e2-56eb-a025-d778d404568e | note | Acceptance / Conformance Criteria - AS Per Drawings.
73937214-0bbe-5770-985e-0bd69c1df086 | note | Standard / Specification - PS 22.7.3 a
fce93087-39b1-5f4b-9d23-22667f9d993c | note | Verifying Document - Visual Inspection / Wastewater line record
67e58c13-d1fe-5023-863e-885faeb7529f | note | Testing Quantity Required (based from schedule qtys) - Every Line
db1d6a43-e67d-5f46-a4f2-5c5e6d5afd09 | note | Verification Activity: Activity - H
3e273fe9-bb82-5752-b1c5-d2778c2c24cd | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a34cecd3-b6a3-560d-bcda-4bade173203a | note | Verification Activity: By - SE
166718ae-4dbe-492f-9150-0027474680f4 | checkpoint | 4.5.3 - Backfill Compaction Testing
f869bf35-4276-54e3-8387-b9d686cd1a38 | note | Detail / Activity - GAP65/AP65 Backfill Compacted in 200mm Layers.
4d6f78e1-87ca-53b1-9f65-ab57ee935665 | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
63cbedca-db88-525f-b92b-d099d00115ca | note | Acceptance / Conformance Criteria - GAP65/AP65or site won material Backfill Compacted in 200mm layers.
ee335472-735b-5595-8adb-ee4a9c741ca7 | note | ○ Testing to be completed on maximum 200mm lifts of backfill.
28dc3675-a898-5ff0-8d46-37faecefce6b | note | ○ 95% NDM on Shared and Carriageway. OR 28% CIV
9a80db0e-e938-5309-9274-d161d9f25788 | note | ○ For site won min >60kpa, Ave > 80kpa
b715515a-dced-5ac2-acc5-bd26eea20062 | note | Standard / Specification - PS- 22.13.5, NDM Standerd 25832 NZS 4402 Test 4.1.3, IFC Drawing 0320-1
269d6aa5-52b2-5053-a0eb-d071f01f4c1f | note | Verifying Document - Lab Report / Wastewater line record
0798346b-9d75-559b-ae94-2994402fcc51 | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification.
934a6d3f-5235-55cc-a019-72f0b208508f | note | ○ One test per 10m evenly spaced intervals.
be6e7f36-50a6-590d-a35b-f87a592b2e7f | note | Verification Activity: Activity - H
5c11062c-e441-5117-b5f0-92ff30f352cc | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
54adb574-f285-511c-8f8b-9557ae0e9b66 | note | Verification Activity: By - SE
1a2ccce8-3d72-45e9-9e88-90a654ba12d6 | checkpoint | 4.6.1 - Pipe Inspection
49f1d504-8232-5956-a77d-33b1c59c527c | note | Detail / Activity - Inspection of Drainage line
6e4d45f2-9760-5f96-a329-bca590002ef5 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
72d1826b-462c-5db2-8b0c-4e9fcdc43aa6 | note | Standard / Specification - Internal
1498391d-5082-572d-b756-9863305ee58f | note | Verifying Document - Wastewater line record
02ef55f3-d12e-5406-a618-7e947eb504e9 | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
cbbeb824-9083-56be-828a-a2c4f38cc97d | note | Verification Activity: Activity - I
2eda687e-24e7-53d9-96cf-decd46fc2644 | note | Formal inspection activity to be undertaken and recorded.
6e4f57f3-81ce-5cd5-8eca-9bb475e62e6f | note | Verification Activity: By - SE
6974b115-4308-4081-9761-eb35a7707b9f | checkpoint | 4.7.1 - Pressure Acceptance Testing
6ad192ba-7988-5528-ba01-d8a535756473 | note | Detail / Activity - Backfill/cover with embedment before testing
6e410f39-56df-52ef-ab6e-de2719ea12ac | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
3110ec1c-0ea0-5010-8882-0ed8bec525b8 | note | Acceptance / Conformance Criteria - Wastewater Rising Main Pipelines – 800kPa
44568659-054d-59d2-b648-8eea65648f5e | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
02150fd2-e4e0-5ecb-a09d-fa2b0a8d0731 | note | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
7599de9e-bbf0-55bb-9980-ee528a8e5ceb | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
6a8fa749-bc38-5a18-b7f5-9702fabbef75 | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
4789688b-7217-5a94-9e85-08d9b1dc4916 | note | Verification Activity: Activity - HP
900e9d95-8364-5e46-b6eb-44e71fda442c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d87a311f-2a3a-5267-b761-09a34977b8f8 | note | Verification Activity: By - ENG
94cd1790-f206-430c-8fd0-e2cd06374814 | signoff | AUTHORITY HOLDPOINT
1b832d71-dbbe-48bf-86b0-c3f0c66ad81f | checkpoint | 4.8.1 - Foundation Compliance
cc143bbd-c699-5023-a507-a808dca40701 | note | Detail / Activity - On Granular or Cohesive Material
188f5ef3-0e34-5be8-ab7f-b78a2b20f422 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
8d508d31-3804-50f2-ab65-872e5bab2d6b | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
5888d505-3aa0-5d4f-8c4a-f1c71c65f67d | note | Standard / Specification - Appendix V Table 21:11
13c61497-ebcd-5c64-8d57-adb6f6b8577b | note | Verifying Document - Shear vane or Scala test result
59f89559-1282-50da-a2d7-7cec2124639f | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
dc522a05-6706-5298-84a6-9598f459fb8b | note | Verification Activity: Activity - W
cd1f8ca8-558f-50a1-a823-ba0deaf0a46c | note | Verification Activity: By - SE
475ef639-f597-4168-948c-ad09649666db | checkpoint | 4.8.2 - Undercut approval
d75247d8-0015-59a6-ab24-c289eecbd20c | note | Detail / Activity - On Subgrade
25e49d58-a77f-559b-83c5-4799668ac36d | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
c41f23d4-d280-526a-a83b-e9da400b9471 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
c57b1cf4-06b2-536e-a07b-858937eba07b | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
6ee7a4d9-21d5-5600-a0cd-6ecaf7a523b0 | note | Standard / Specification - Table 21.5
00c0e2bf-5d39-59a0-b28a-8f5f32a2493a | note | Verifying Document - Lab Test Report
d6ecef3a-e70c-59d8-a005-e25474ce628e | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
efd6a449-24fb-5e36-b369-247045c06c98 | note | Verification Activity: Activity - HP
83cc9b8c-aada-5cb2-8bdb-0d4b584ddc01 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7c2d40a0-34cc-5271-a678-e77a79143555 | note | Verification Activity: By - ENG
a053de1a-95f9-4937-8684-85c0ba642d8a | signoff | AUTHORITY HOLDPOINT
5cd65eec-29ec-4811-8a1c-a48c2f310857 | checkpoint | 4.8.3 - Undercut Backfill Compliance AP65
0ef229c6-1b4c-565f-a65f-3e54d866b52e | note | Detail / Activity - On Granular Material
062c5565-96ce-530b-902d-6abbcad98904 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
31fbe298-47e9-574a-94f0-bef7a60beb20 | note | OR
e1936de9-36cc-5670-806e-2929acd1a317 | note | ○ Clegg 25% CIV
b392f4dd-de53-5acc-bba2-1496cb3d3e8d | note | Standard / Specification - PS- 16.5.12
7fb9b722-9065-5f21-b5bb-04c6504faa6e | note | Verifying Document - Lab Test Report
f3ad9a9d-051c-5276-a54d-611518eceb2c | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
3955d0a4-a569-585a-8a8d-a06ebe6abc87 | note | Verification Activity: Activity - H
a21d8bcd-a661-586c-9737-a183d29c8eac | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c7bcbb33-6ec2-5c44-9b42-ea5ecda6b789 | note | Verification Activity: By - SE
f347a213-f945-4f5b-b45f-f94a61bacb66 | checkpoint | 4.8.4 - Bedding Compaction Testing AP65
2a23fd20-fa50-51c0-8566-17f1b9130311 | note | Detail / Activity - On Granular Material
643ac9d2-26e7-5907-8706-ba832e036cd7 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
aac7e285-8ab2-5427-aaf5-49be0edeb3a9 | note | OR
1775630d-a176-5ba2-9ea5-ba0949260f77 | note | ○ Clegg 25% CIV
df12bb90-e801-5bae-bf71-be4014057208 | note | Standard / Specification - PS- 16.5.12, PS- 21.6.11
ec7d6373-1ca1-56f5-9c30-04f133492827 | note | Verifying Document - Lab Test Report
03958b9a-7167-5d3e-890a-7952ca77b9fd | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
42caec1e-10e5-551b-a163-270f2975b733 | note | Verification Activity: Activity - H
b3b2c7da-4149-581d-ae79-96ee28fea04e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
bffa6f8f-5c3a-5f3a-ba4c-3a5196e8b8ea | note | Verification Activity: By - SE
5ec8156f-d7b1-4275-9f9e-48a1524c41bc | checkpoint | 4.8.5 - Survey
9fc57d18-d96f-59e3-bb56-67c2930ddc25 | note | Detail / Activity - Inspection of Structure
5e6676a8-e730-50c6-8c39-ac5d2eba472d | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
515d7e3d-3dea-573b-ad71-aecc71dd7ba9 | note | Standard / Specification - PS- 21.7.6
391a2570-9a8a-5869-b3e8-add187730e11 | note | Verifying Document - Survey Data
1f15abf8-76d8-5273-9987-dcdee7d1c90b | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
aefa4b96-0b62-5664-992d-e346bc3e83bb | note | Verification Activity: Activity - H
6e311e33-364b-5467-89fe-2650bb8275f1 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f0f626e1-79d6-5cc9-a962-bdd8676e4ce3 | note | Verification Activity: By - SV
33030b79-fb7c-4966-9dfb-ba9fa6cbf372 | checkpoint | 4.8.6 - Sidefill Compaction Testing
18db0549-7380-5ba9-bd49-b5d65addb045 | note | Detail / Activity - From the bedding layer to the overlay layer of pipe.
050dbce8-2831-5a2b-9d97-18f9b3e809b7 | note | Acceptance / Conformance Criteria - AP20/GAP20
adfef9cb-1b15-5f5f-897f-498f92dd2854 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
eee63bc4-009c-505d-b1bc-523e31cfaf3f | note | ○ AP20/19mm chip
d05830f6-50fe-5292-9072-48299f22047b | note | Standard / Specification - PS- Table 21.12
e8f756d5-0e4e-5e4d-886e-3136f4182f3b | note | Verifying Document - Lab Test Report
660d9190-de3c-5589-a7ac-28f6ccffebcd | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
255d2526-7c88-5d11-a1f6-f768a1a9ad9e | note | Verification Activity: Activity - H
370ef5be-6146-5953-a689-013e43da3692 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
2fed9b5c-7c9f-5128-b27c-0901b4b88e89 | note | Verification Activity: By - SE
c64a1066-8e9d-483e-af5a-176f4f6bf970 | checkpoint | 4.8.7 - Backfill Compaction Testing
716465f2-df93-5474-95ab-69491aa8199e | note | Detail / Activity - From Overlay layer to the subgrade layer
50d3d62f-46f9-5f75-8794-9c75c3faa863 | note | Acceptance / Conformance Criteria - AP65
870f193a-2113-59c5-b972-b273acd24b43 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
cfbd2f6c-f5bc-5912-be09-a191b9bea852 | note | ○ AP65-Clegg28%CIV
a00a1d3e-d3ea-53d6-b531-2b2fc1e8ed0d | note | Standard / Specification - PS- 16.5.12
ae445e0f-53b6-5c1e-a7c7-8bb2dcc73815 | note | Verifying Document - Lab Test Report
443bf8c8-638d-5741-a8e1-3c618b9bd8fd | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
2f21108d-9739-5c92-ae3e-6c5853475c78 | note | Verification Activity: Activity - H
e2e853e3-afb3-5628-b408-106cf62bd0c0 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
eb5b4a38-14f2-5aad-a7db-290606100d20 | note | Verification Activity: By - SE
2fafd856-6825-4e8e-8739-c9de24e9f189 | checkpoint | 4.8.8 - MH joints inspection
3ca03a9b-5d9b-579b-a376-d72a6e0ca857 | note | Detail / Activity - Inspection of joints
ff2cc497-dddf-583a-9956-935ea143898e | note | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
33e35f45-a261-5056-8ca4-ee1d01f0fd15 | note | Standard / Specification - PS 22.7.10
83c0073d-89ba-5463-a0a1-1c7463897594 | note | Verifying Document - Visual inspection
7becfb35-142e-5b9b-9139-78270e51af33 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
8098d0ce-3f71-52f9-bea5-723380ccb743 | note | Verification Activity: Activity - HP
fc56b680-0439-54cb-9d89-029a5dfdb8e3 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4624135b-70eb-59f9-972f-309daa597cdc | note | Verification Activity: By - ENG
73459d90-0466-476c-a4c7-b60edeac4ae6 | signoff | AUTHORITY HOLDPOINT
a91bf100-84ef-451d-a7f9-ff0143d7be93 | checkpoint | 4.8.9 - Inspection
f7cdd320-c1bc-50be-8acd-fa2d3a480179 | note | Detail / Activity - Inspection of Structure
cc9ea066-a790-52ec-abeb-1aa95a911802 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
3634834b-544e-548f-b126-207bd07ad184 | note | Standard / Specification - PS- 21.6.11
b5bb861d-72c4-51d9-8cc8-8fa5e2a6d5f5 | note | Verifying Document - Manhole/Catchpit Record
9511835a-90b0-5365-8958-294bf49f7dff | note | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
9ca0b3c6-c0d6-5340-bc45-bc6beeec2540 | note | Verification Activity: Activity - I
bc68975f-6b64-50d9-a41e-5f88f7f8333e | note | Verification Activity: By - SE
aab4a225-b850-48c8-b894-da7e7af9d022 | checkpoint | 4.8.10 - Plumb
2d609172-7027-504c-93c3-3631d95ab117 | note | Detail / Activity - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
0f54af0b-6edb-5431-9305-fffaedd9765d | note | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
8c34db28-429f-553f-8b5f-71890d9977bb | note | Standard / Specification - PS-22.7.10
051d060b-7a6b-5ea3-bb62-08321ab40034 | note | Verifying Document - Survey Data
83f373d4-be8e-566a-a094-02851f389923 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
8e0e2b50-1d66-56bc-81b5-4c794f93576e | note | Verification Activity: Activity - H
439df04f-17fe-5660-935e-3b842b2bf658 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
300b4e35-44e3-5169-a2b8-c17f03829b01 | note | Verification Activity: By - SV
83ed5d57-f629-4b15-be0d-29b6b53f0009 | checkpoint | 4.8.11 - Step Rungs
7c864916-d4b5-513f-a995-2cb501426a29 | note | Detail / Activity - Step rungs evenly spaced at nominal 300mm vertical intervals
ebbfff10-233f-571c-b0cd-e737b5dea8fb | note | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
362ba4e7-faaa-5ffb-b99c-9aae20899817 | note | Standard / Specification - PS-22.7.11
8863ed34-58e5-5862-966d-9b9f6ad2a677 | note | Verifying Document - Visual inspection
140d188d-aec5-5a92-80a5-4e037a10d0d2 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
bdb089e7-ad05-5b03-a4fc-c66d94ba5af3 | note | Verification Activity: Activity - H
1e34d60f-1bfa-5e44-b12a-378eb209df2b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
95221e28-8daa-5d0e-8c0e-0c4ff6639fe6 | note | Verification Activity: By - SE
1c8ef1fd-3c2f-47e6-a058-4fa16409a04e | checkpoint | 4.8.12 - Manhole frame and covers
4cd7aac3-f50f-5bf5-92ff-d694ab8db6c5 | note | Detail / Activity - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
cebfa828-9b84-53b2-925c-e9ffc3b806bd | note | Acceptance / Conformance Criteria - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
017c843e-10e4-556d-a994-753379328f9f | note | Standard / Specification - PS-22.7.12
0d2882b2-406d-5f96-99ab-9279c84e81cd | note | Verifying Document - Visual inspection
f3e2ac67-816d-551a-b600-a337c6e7d6d2 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
15cc930f-954e-5ec7-93b0-4c26f2cb8f13 | note | Verification Activity: Activity - H
4057ae97-f856-5e79-9138-2f05a2a60e20 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3fae0408-abf9-5d13-a22f-9e2250b10149 | note | Verification Activity: By - SE
8358caba-b022-44a7-908b-e9f0b3698b00 | checkpoint | 4.8.13 - Manhole lateral connection
43c539b1-57eb-50a9-a1ed-75acebd553fd | note | Detail / Activity - DN150 PVCu connection for future lateral.
5811b621-8dab-56b9-b3c5-196e2975c408 | note | ○ 800mm above manhole outlet invert
c42f3bdc-68f5-5e4b-a455-f93ee68f4fef | note | ○ DN150PVCu end cap
ef3f916d-936b-574a-9ef5-ca4a81631c7e | note | Acceptance / Conformance Criteria - DN150 PVCu connection for future lateral.
e1703037-0d57-5e6c-a5e2-91b48b3547b1 | note | ○ 800mm above manhole outlet invert
fa184abc-766d-53b7-b30d-407666104908 | note | ○ DN150PVCu end cap
ab4a575d-29ee-59ac-b80a-2345fe6e77ce | note | Standard / Specification - IFC Drawing 0320-Rev 03
fe2f3fb7-2d56-58f0-9f09-b8600a696e9c | note | Verifying Document - Visual inspection
7c55c7a6-ddf6-5da5-a1ba-b131a92381af | note | Testing Quantity Required (based from schedule qtys) - Per connection
d835c460-9253-59ed-b4f7-f2ea420e7ad0 | note | Verification Activity: Activity - H
9b065e5b-fd35-5ff5-9b42-168d44672b61 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0fde02de-bf4a-5905-bfba-44319422edf5 | note | Verification Activity: By - SE
93fe9ca9-b5e1-4f37-9857-e65142e516e6 | section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
0b568b49-65ed-4455-8e10-d122133bd7f2 | checkpoint | 5.1 - Survey As-Builts
510aceea-0cf7-535b-b4a7-fd78b76b58c5 | note | Detail / Activity - Quality Check on Nee pipeline and structure based on the tolerances in RITS
393bdf34-8872-51d3-9d74-b3c8f1b60bd0 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
90ee35f4-1228-5a44-b881-0813430caf30 | note | Standard / Specification - Project Specifications
66e061e0-0469-5083-a5cc-747482b039f1 | note | Verifying Document - Red pen markup only
7551054c-44bb-569c-9804-d1d8fb355442 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
db8079cb-ff58-53d3-9416-1279a3f45a5b | note | Verification Activity: Activity - H
d4152a4a-182d-528a-a2a0-f91830a042fc | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
884e7b4e-3caf-58c5-80ed-5a16d7b8f9a9 | note | Verification Activity: By - SE
5c6cfe97-d101-4575-bd27-a4ed6c955213 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
7ffc65ab-3b58-51a6-987f-cba706424671 | textbox | Contractor's Rep Name:
c20d47de-02a2-50ff-b679-6d83919853ad | textbox | Engineer's Rep. Name:
0f6e1810-9f87-5b2e-a95c-77b01b98e6bb | date | Date:
f09ab567-1cec-42f1-a29f-9894e8b70a9c | signoff | Add Signature
c6365681-7689-40ec-9d46-19afecf42342 | checklist | DN1210-SP2-011-003 ITP Northern access road Watermain Rev 1 | itp | DN1210-SP2-011-003 ITP Northern access road Watermain
8d1f90b4-807e-47fd-9600-b8028a436de9 | section | 3.0 - PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS - ALL TESTS TO BE NO OLDER THAN 3 MONTHS
f5853264-6691-4e11-b8fb-d2ffe23ada5f | checkpoint | 3.1 - Extent of Line Setout
4de0d519-89a4-5e10-bed4-dd7873cd4d5e | note | Detail / Activity - Ensure line and level of Watermain has been marked out and agreed with Engineer in accordance with Watermain drawings.
8b983b21-0d61-56d3-b3ff-40fcd804efb4 | note | ○ Identify any clashes before construction.
bb168bbf-5033-5059-bca9-71c62d2658cf | note | ○ LOT- markup
0dd2f046-78d8-5c06-814f-a3230208ecc1 | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
05ac03bd-5433-53a4-80dc-06202394a3c0 | note | Standard / Specification - Design Drawings
eb87f5f1-2e6f-53e5-82e8-a6c19559daf6 | note | Verifying Document - ITP Sign Off / Mark-up
795ba30d-9cd8-564e-b0fc-d7da0aedc574 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
f2bcd828-06f9-5e04-8ae7-2ebf55984e05 | note | Verification Activity: Activity - HP
af97a09e-f788-54bf-80ce-3dfb08c934c1 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1e884ad1-b2da-58eb-bd9b-63860a53fc25 | note | Verification Activity: By - ENG
666ef1a6-0d1d-4f5c-8d27-5f4c1253ba39 | signoff | AUTHORITY HOLDPOINT
6aadd748-c4e7-44d1-a5f4-13953a5f2102 | checkpoint | 3.2 - Pipe Laying
44e2de23-200d-5700-9cb4-0a11c7e60b3a | note | Detail / Activity - Method statement
2e1946fd-f894-500f-9919-e2e121d417fc | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
21556b79-f4c5-50ef-aef6-542d23474386 | note | Standard / Specification - PS- 22.3 Appendix V
b7893e64-9dac-5069-ae0d-8328c37a26ae | note | Verifying Document - Watermain Construction Work Pack Sign off
3f0d9286-e1a1-5aa6-95db-273ea55abfe4 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
334ca78b-4a24-50a9-bf2a-e743990311d2 | note | Verification Activity: Activity - HP
5d86c5cc-871a-5f9e-b18f-b2ad55c8f633 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b2d70cda-8ce3-55ad-8392-860eb255dd47 | note | Verification Activity: By - ENG
2c80a905-8fb4-4219-9bf9-a8c7862bc57c | signoff | AUTHORITY HOLDPOINT
e9e6e530-961e-420e-abfa-4a1a82ec3f83 | checkpoint | 3.3 - Pipeline Pressure Testing
2a6c3fd9-f90e-538d-8fac-710db069c0a2 | note | Detail / Activity - Method statement
d5918306-fdfd-5ab7-91c0-b0880f390ba1 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
e34fc6bc-d638-52c7-836b-21cf94e98ed8 | note | Standard / Specification - PS- 22.3, PS 22.7.12, Appendix V, Appendix XXI
1bb0ec5e-0a24-54af-846f-0de79ae76621 | note | Verifying Document - Watermain Pipeline Pressure Testing Work Pack Sign off
3dbd041b-aa00-5b84-b3d3-ed6bb5ae8801 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
84ce57c2-0b2f-513f-a324-c6536283b5f3 | note | Verification Activity: Activity - HP
456acd3f-2963-5155-8602-ef4b83d949e5 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0ad44175-082e-55ab-9404-0bec2e9fe2f1 | note | Verification Activity: By - ENG
456f8172-78b7-4896-b297-2e398f08d1d3 | signoff | AUTHORITY HOLDPOINT
b821f25c-1350-4940-b33b-3beea114f875 | checkpoint | 3.4 - EF Pre Construction Weld Tests (if required)
1543c63a-4b67-5272-9903-8d3e377d319c | note | Detail / Activity - Passing result in accordance with ISO21751 (strip bend test) tested by an IANZ accredited laboratory).
c9be0f3c-23b0-55e7-b367-001b635b622c | note | ○ There should be no EF weld test without prior approval from TCC.
f641c5b1-f0c6-57cc-bfce-154760fa5c23 | note | Acceptance / Conformance Criteria - Passing result in accordance with ISO21751 (strip bend test) tested by an IANZ accredited laboratory.
1cc71547-ee4f-5c43-9014-99d4ecb2b811 | note | ○ TCC Approval Prior to Works
7e29af3a-25fa-5da1-8885-bce6e85cc49a | note | Standard / Specification - ISO21751, TCC IDC DS-7.6.4.b.ii, PS-22.9.6
37dbcb5e-9b39-5d32-aae8-f3259be0b37d | note | Verifying Document - Laboratory Test Report
17b566ba-e22f-535b-8d41-d24de725b633 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
5b28f513-eff4-5d5c-9f3f-785daceb51d0 | note | Verification Activity: Activity - HP
2e7366cf-ba87-5df6-966f-ca38ea103052 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
898a585c-2641-597e-8a05-88edceb421f2 | note | Verification Activity: By - ENG
df156da5-229c-448b-bfe9-160b8bf8a091 | signoff | AUTHORITY HOLDPOINT
37a4feb9-bb2c-4d5c-bdee-5388f6d9c08e | checkpoint | 3.5 - Butt-Fusion pre construction weld test
624988d9-3522-5374-8486-555db2cd5ba4 | note | Detail / Activity - One weld on the most common size of pipes used for the project.
903fac1b-e997-543c-b74e-69b6fd84431e | note | ○ One weld on the thickest wall (highest PN) pipe
e4173eda-960e-5c7e-99c5-28e9e3838ce3 | note | Acceptance / Conformance Criteria - Test to be down in accordance of ISO 13953 for tensile strength and failure mode.
b10db9e2-19e4-5df4-b703-51ed04680ba5 | note | ○ WMS Report
e7ac2c4d-6e85-5b68-9686-aec1cb7c4bf0 | note | Standard / Specification - PS 22.9.6 (a), ISO 13953 Standard
321aad4f-6d99-57f5-9207-46eb45a8fe46 | note | Verifying Document - Visual Inspection
fa6e887f-3523-5823-a891-ba26c0111080 | note | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
29a522b5-cd4b-55b7-bfc6-6cfd7f55f50a | note | Verification Activity: Activity - HP
539db0b5-03a0-5862-95dd-d915bf14bba1 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
57736de5-d350-5271-9b6b-5f759f40398b | note | Verification Activity: By - ENG
2f1d952f-91a5-4517-9f15-5e4d8c7998b2 | signoff | AUTHORITY HOLDPOINT
09bccf82-485e-4b5a-ac80-2727bbcd2db8 | checkpoint | 3.6 - Material grading: Materials (Gap65/AP65)
8a87b120-3d4a-588f-b411-dc6723b469ba | note | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
f7b9f9c9-0191-550f-b914-1a2077a8a43a | note | Acceptance / Conformance Criteria - No Particles >200mm
f6563462-62b2-50c5-bd33-46a3ba9e370f | note | ○ Maximum fines 10% passing 75micron sieve
a226dd11-e161-53ad-803c-c2880c9f6f4b | note | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
4f659294-318e-5158-98a6-98a5314214cc | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
5f767a05-05e3-5267-b26e-975431a40afd | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
d84d6778-6f84-5275-8037-943fa7b33b04 | note | ○ 0-400 - 2 tests
4e9aa1da-dabc-5526-a952-7026479fa7b1 | note | ○ 400-1,500 - 3 tests
5c4e6cd8-909f-54f9-9fb4-ee6eed16a4c1 | note | ○ 1,500-4,000 - 4 tests
de1e6734-435a-50fd-8286-bdd7750ffc6a | note | ○ >4,000 - 1 test for each additional 1,000m3
ba7d4539-07a0-5f83-8aac-a126dcde2a96 | note | — Results to Engineer 2 wks before importing
1f956d55-9890-52b5-8f69-28ab735a3c3b | note | Verification Activity: Activity - HP
ca425f27-7811-5b34-ae43-4cd99187e9ad | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
92822e28-5b1a-5e67-aef5-8f6948118e0b | note | Verification Activity: By - ENG
f0e0b511-96df-4888-8e76-8740b76a01e9 | signoff | AUTHORITY HOLDPOINT
04bfb254-441c-4e20-aea8-2db3d0cd5ff9 | checkpoint | 3.7 - Weathering index: Materials (Gap65/AP65)
05cb40e6-7214-58b9-997c-c6b3607e2b62 | note | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
95e5c098-adf8-5a40-bb33-81d9b2ecc159 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
7b366288-6006-51c5-a832-402e347585ce | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V NZS4407:2015 Test 3.11
dece8089-8d13-587b-9a33-53841bd4d46c | note | Verifying Document - IANZ Accredited Report
ba3febc2-84b5-599a-a8e3-6522047fe806 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
843e0386-6619-5d17-a8b9-8823b295c960 | note | ○ Results to Engineer 2 wks before importing
756b4e0e-2fca-5ceb-b183-1cdf8a195273 | note | Verification Activity: Activity - HP
d327e8fa-e2fb-5bff-811e-5c1a41aa5ba6 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ae25714f-7a5e-5f6e-ab55-f58b6eae3c25 | note | Verification Activity: By - ENG
0851a9a1-f8b6-4a7e-8391-1ea755066693 | signoff | AUTHORITY HOLDPOINT
26a8a849-df82-4cc6-aa70-adc034ed4265 | checkpoint | 3.8 - Crushing Resistance: Materials (Gap65/AP65)
087f035e-bc99-565b-b891-97628c0002c6 | note | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
501090a7-4bd5-5cc7-af3b-3a914c043e8f | note | Acceptance / Conformance Criteria - >100KN
f8a94096-a870-5da6-9868-06514d9b0b62 | note | Standard / Specification - Appendix XVIII, Appendix V NZS4407:2015 Test 3.10
f101ce06-0674-516d-9087-ca79edcf09c5 | note | Verifying Document - IANZ Accredited Report
49165d1b-9fae-5d61-b308-1e4f04ec8a64 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
e9071ad9-b9ed-5342-93db-0847bc6bea6d | note | ○ Results to Engineer 2 wks before importing
9711a833-79dd-5290-b97c-3251be9000f0 | note | Verification Activity: Activity - HP
1e6037e2-708e-57fb-8d33-e45add8daeff | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6ca032cd-e7ec-5882-84da-91e041be61f7 | note | Verification Activity: By - ENG
a02e6fa7-88e9-4e53-8001-77ba1a6a4288 | signoff | AUTHORITY HOLDPOINT
7dd261e9-88f1-40a1-839f-3e8a81c5883f | checkpoint | 3.9 - Maximum Dry Density and Optimum Water Content
b4ee0191-d2b7-534f-b56a-5960edcd1338 | note | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
9b27476f-0dfc-5af0-a3ac-d995c22ecac0 | note | Acceptance / Conformance Criteria - Report Value Only
5bb66ab5-bf42-553f-861a-03dd8572422a | note | Standard / Specification - Appendix XVIII, Appendix V NZS4402:1986 Test 4.1.2
26c365bb-ae71-51ac-82c0-0067bee91894 | note | Verifying Document - IANZ Accredited Report
4c3b122f-ece1-58d6-8bfa-a5f788cb341f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
68dac065-79a5-5500-8ce2-6746e7844d10 | note | ○ Results to Engineer 2 wks before importing
12f59be3-c42d-53fe-9ca4-cac1502a5977 | note | Verification Activity: Activity - HP
788e4d03-373c-59c1-804f-318300d976b3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
67ea0bc6-48a5-5ef4-af22-0f902a5b0b55 | note | Verification Activity: By - ENG
7a39588d-71cc-4b6d-a750-aac39476519c | signoff | AUTHORITY HOLDPOINT
7ec6fd33-63f9-4f1a-8cd1-fd51ad44fb0f | checkpoint | 3.10 - Material grading: Materials (GAP20/19mm chip/Sand SAP7)
0a4053f7-807c-58d8-96d1-e34b035f2cfa | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
749bc614-0a04-5582-baa3-fc4067d6f51e | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
28296a8c-5485-592d-bfc1-07fd6a0801af | note | 19.0mm ¦¦ 85-100% passing
0566f7d5-9246-5bf6-b335-2577115cc7a1 | note | 9.5mm ¦¦ 25-55% passing
f94ad828-c2a1-54a3-8fad-8556d000470c | note | 4.75mm ¦¦ 0-10% passing
a8318743-2159-544d-b8ec-b06d2fccc1f6 | note | 2.36mm ¦¦ 0-5% passing
9efe7d6c-168b-5108-82fc-10131f6e4f1f | note | 0.075mm ¦¦ 0-2% passing
42050099-c552-561f-a332-0a3361916988 | note | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
15fae443-cfe3-59d8-8936-2be6e6157485 | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
a061bc7b-8914-5b10-9f58-ee14f5f9968a | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
d69c0528-1c18-5705-951c-c94848414d93 | note | 400-1500m3 ¦¦ 3 Test
f8807a8b-dcff-5144-9b50-c5863691b0d4 | note | 1500-4000m3 ¦¦ 4 Test
6bf9f0c5-c4be-5e4e-b196-feadce234e48 | note | >4000 ¦¦ 1 Test Additional 1000m3
05c11a51-e805-5aa5-9e7b-a3df9f762e63 | note | Verification Activity: Activity - HP
ee77c10a-b73f-53ab-9765-fcd840743ee7 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
02f4d0e2-5f2a-530b-873b-1e668aed35c8 | note | Verification Activity: By - ENG
28510250-fc54-4193-a71e-7ec1914a23e4 | signoff | AUTHORITY HOLDPOINT
a9cfa43c-ca6d-45d1-bb30-e6da70cb9f7b | checkpoint | 3.11 - Soaked CBR
449334ff-cbdf-5299-942c-c736f7140ffd | note | Detail / Activity - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
bcdb4493-567f-5190-a2f0-595b28717132 | note | Acceptance / Conformance Criteria - >80%
4bf9a52d-b359-5102-a543-723c8a658499 | note | Standard / Specification - Project Specifications 20.9 TCC-IDC IT-4.8 table 4.6
5ddc258b-d9e2-5e4a-8d96-09dac9aaf391 | note | Verifying Document - IANZ Accredited Report
7563118b-20fd-5ca7-9026-7bd4ef5a0fdd | note | Testing Quantity Required (based from schedule qtys) - IANZ Accredited Report
bf72cbaf-e7e3-5003-828a-c77d1f58b860 | note | Verification Activity: Activity - HP
1d17e581-ec8d-577c-a052-2a03806cfbc6 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
46be96ed-2e18-5440-9962-e1caa75e358c | note | Verification Activity: By - ENG
f530badb-f6e9-45c5-9187-435ac611bd27 | signoff | AUTHORITY HOLDPOINT
9152d86f-8fea-47f9-abfc-743828747e2e | checkpoint | 3.12 - Pipes (DN315 PE100 PN16)
1f52db04-e5a4-56a6-ad3c-b72d706d96a4 | note | Detail / Activity - Manufacturer's record and location of extrusion plants.
748cd62c-5346-5633-8974-0c8957595834 | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
adc4a421-3b26-5050-b8a7-bf287715c32b | note | ○ Full Traceability information and certification of analysis for the resin batch.
d084943f-f218-5b55-a4de-09c671cf66fe | note | Acceptance / Conformance Criteria - Full Traceability information and certification of Material and resin.
252ccf1b-3b0e-51b6-b320-6bde8215b5d2 | note | Standard / Specification - PS-22.4.1 (d)
64be6828-e3ac-5e68-826d-2a2ae6fa5861 | note | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets
c51115c2-41be-5952-a590-9b0720db1297 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
d64f3b7d-345d-5665-a801-de7f1c5cfcfd | note | Verification Activity: Activity - HP
2029c075-6e96-53bf-8c94-4f62668e865b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c8fa6c4c-64be-5c61-a19b-b73323a9134e | note | Verification Activity: By - ENG
a516465f-d64b-43f1-bcf9-e70a2884c843 | signoff | AUTHORITY HOLDPOINT
624f998c-6bae-48ae-8f51-16287db60aad | checkpoint | 3.13 - Valves, Adaptors, Flanges and Fittings
13be42ae-f646-55f1-ac67-a6f91f4e9f74 | note | Detail / Activity - Have a pressure rating no less than the designed pressure.
bba5cf35-3fbe-5682-a6f7-1443d8de0e41 | note | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
80dd8dac-9dd6-56b3-b6de-c8f9f2b97876 | note | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
61024ff4-ee57-50db-8498-41be6d1abc29 | note | Acceptance / Conformance Criteria - Engineer approval AS/NZS 4129
8243839f-13e1-5a3f-8c39-df7dd9f97331 | note | Standard / Specification - PS-22.4.2
1d71f409-1d3f-5a21-b06d-9dedc5640992 | note | Verifying Document - Delivery Dockets
efa49267-9b96-5e72-82ab-014d7276dc59 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
f3ee85f8-16e8-5b5e-a22f-fff26193fc9b | note | Verification Activity: Activity - HP
9a71ddd4-06cd-5042-bace-0e7ac753060a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ed1ad5bb-f576-515c-b081-6d987e62cb8d | note | Verification Activity: By - ENG
380cc28c-7de2-4209-b53e-00c46677cf07 | signoff | AUTHORITY HOLDPOINT
8bd21351-e9d7-4907-a76a-ab110cacddd6 | checkpoint | 3.14 - Fusion Joint Compatibility
04879e88-a3a1-5f6c-b565-b398cebaebbf | note | Detail / Activity - Confirm pipe and fittings compatibility for fusion welding
df7e9a92-7fa3-56f1-9618-4c2eb24ce010 | note | Acceptance / Conformance Criteria - No defects, compatible resin types per NZS/AS 2033
fe2d4de7-5e46-5bf3-bf72-ce5d1233c4cf | note | Standard / Specification - NZS/AS 2033:1980, Clause 4.2
f4c9b305-0d99-5709-a106-1d8b5c904880 | note | Verifying Document - Test Report
d7bf7494-8279-56ff-af38-91a21ce2f96f | note | Testing Quantity Required (based from schedule qtys) - 1 per material type
551ba6e0-cc4a-5bea-b2e6-cc4df3412bcc | note | Verification Activity: Activity - H
efec8abd-0b76-5bf5-98a1-d73258f145ca | note | ○ Hold Point (Internal)
90866beb-ac77-591b-b0ce-817e5c0d11db | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
56735b37-cabb-507e-923e-800e64f09f69 | note | Verification Activity: By - ENG
68a27126-4522-43e2-90ad-e04d2b278f1f | checkpoint | 3.15 - Pipe and fittings.
69c376c5-9367-555f-af66-cd20a9c2841c | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
f337d2d4-6e71-5b6a-8389-4c0e003b159b | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
6c4be083-bf2d-5c88-b259-ae066437a53d | note | Standard / Specification - Design Drawings
9319541b-dbbc-5b86-986e-b9251ed5deeb | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
33a7984d-a58d-5c83-80a5-2ee00e5be96e | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
343aa0d0-3b0b-54d5-9dd4-93d4e43b6e2f | note | Verification Activity: Activity - H
6b197679-6560-5715-849e-0eef09429fec | note | ○ Hold Point (Internal)
7fe101d8-d4aa-5a3a-bdfc-d5b00642431d | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
7e4d1ac2-2a70-5474-b03c-19ab9b27b8e0 | note | Verification Activity: By - PE/SE
b3102a0d-8377-443e-9400-4453a01a29ae | checkpoint | 3.16 - Valves, Adaptors, Flanges, Caps and Fittings
2dfe6b33-4ee6-565a-96eb-38bd104828bd | note | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
88faa536-fc76-585b-8852-92130bf890b6 | note | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
91bcf9e1-affb-5885-be5a-895b013716c8 | note | Standard / Specification - PS-22.4.2
e8a786cc-7d99-5a00-9189-eed8b20322e9 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
f14ee2d5-81db-52da-868a-3863bf0b4fec | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
046f0319-7829-59ed-9d5e-80eb078f3c40 | note | Verification Activity: Activity - H
cc5f08f7-2710-540c-9952-8ab5a29c823f | note | ○ Hold Point (Internal)
85b86197-a3ea-5d27-a3c6-1177d1919057 | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
0cce663c-14c4-55cf-8c09-60a7d6b7b286 | note | Verification Activity: By - PE/SE
33d7488c-7fcb-4efb-ad32-d3c5d4571144 | checkpoint | 3.17 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65)
633109f2-54f4-5b62-a829-3736b6eb3964 | note | Detail / Activity - Confirm Specification and material in good condition.
1f9d9258-949b-5607-9208-8b7ec3d28a1a | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
206ef4b6-1007-5e68-a48d-5e5a29ad7b52 | note | Standard / Specification - PS-22.4.1
f731cadf-455d-5eb3-ad4a-ef66af022992 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
07414775-dd25-51e4-8084-63987320e9d1 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
a7366b01-112f-5e7a-a6c6-7760c4624bd0 | note | Verification Activity: Activity - H
998c0cd7-876a-5c5c-a592-5fe90537d97a | note | ○ Hold Point (Internal)
9755b978-d282-5da9-8c3a-6eabfbb43e7e | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
d8eee452-cd53-5506-a620-b4fbaafe8daa | note | Verification Activity: By - PE/SE
b078dd5b-8aaf-41a2-85ad-18394889ca0f | checkpoint | 3.18 - Bidim/Geogrid
336cf1f2-7f41-5ff1-a8ba-8f2530ae2fbc | note | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
b086505c-61d8-5390-a659-8e8390b12567 | note | Acceptance / Conformance Criteria - Site Engineer Approval
64195522-8279-53c6-885e-9c0989638759 | note | Standard / Specification - PS-22.4.1
c171d94a-fb1c-5ebf-844e-1d2a74ff8b32 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
788d3212-ba20-5f11-9ef1-f65638754e01 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5b993b9c-02d3-5989-b986-5daa5b69ab2a | note | Verification Activity: Activity - H
5ce6cc06-31fb-5923-a75c-24b27608b760 | note | ○ Hold Point (Internal)
3033ab4c-71dd-51fe-822a-a7870bc53046 | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
51e64d6b-f825-5dd5-b67d-8114606eb596 | note | Verification Activity: By - PE/SE
23f97589-35fd-4351-9e77-f5249b4ce674 | checkpoint | 3.19 - Pre-cast Manholes
9afbeaf9-0536-566e-8321-b7027bd6768e | note | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
a4dc9190-5595-5f80-9aee-82789078116f | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
2be786fb-253d-5c90-8928-0e9e198b1ca1 | note | Standard / Specification - Design Drawings
59af999c-3be1-5c8a-b092-8d7c1c322e94 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
b6800181-ae1f-5224-855c-7ff069ec8b3f | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
37f9a341-abdf-53ec-a778-1f40f5314334 | note | Verification Activity: Activity - H
4c4dea34-9cbe-5d4e-8f57-7ecfdaf4b755 | note | ○ Hold Point (Internal)
6c095f53-ebf8-5f7e-88b8-c3ad9481be16 | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
5f0fb6a2-485d-53f3-ad8a-1e39632979c9 | note | Verification Activity: By - PE/SE
0c2076dd-3b7d-4652-9608-80302cec8b56 | checkpoint | 3.2 - KWIK Spacers
9599be8c-1a33-58ec-ae59-0329657c98f8 | note | Detail / Activity - Placing spacers on DN315 pipe when being inserted into DN560 sleeve
f00e51df-012d-5b7c-b495-7d33689e1f1e | note | Acceptance / Conformance Criteria - Model: HDXT43 (43mm). 1.5m spacing
45100318-c479-53ca-a653-9abed33ae162 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT) Sheet 0312
5f20c569-bee5-50a8-82bb-4eaf4fdf191e | note | Verifying Document - Visual Insepction, Photographs
b5142463-cc11-53b1-9b01-f109e7375987 | note | Testing Quantity Required (based from schedule qtys) - Pipe under NAR
e525ef16-af73-5ebf-b1d5-b724784dcc08 | note | Verification Activity: Activity - I
90a08579-c5b0-57b5-8b12-76bba00b125a | note | ○ Formal inspection activity to be undertaken and recorded
f2920ce2-ace2-528b-a2d1-aed78bc6bbf5 | note | Verification Activity: By - PE/SE
855594eb-e2b2-4cc9-85fa-a59398cbd0cd | section | 4.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE INSTALLATION - Excavation and Laying
7e37c8e1-fa5a-4b60-812f-2800f8c3ad1f | checkpoint | 4.1 - Foundation Compliance
2a0f2d84-305c-533f-bba7-69c3aa3cb937 | note | Detail / Activity - On Granular or Cohesive Material
d7bd298d-800e-5747-9f16-6571d71c7dbc | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
f53b0b0c-469a-52c1-9a72-e7c9c80d74af | note | (Or)
85c9d776-cd62-58fd-adad-1758185a1580 | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
82305d74-e6cb-5db4-bff4-6b102d7a2b9c | note | Standard / Specification - Appendix V Table 21:11
10d84876-973d-51dd-a90e-b77664362f17 | note | Verifying Document - Scala/Shear test result
0286ccdf-3c73-5631-a100-d90b556240d1 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
f25a4426-8d58-5cc2-b124-8acfe397cf77 | note | Verification Activity: Activity - W
d2f3a6aa-1b8b-55b3-b081-415d47889fa2 | note | ○ Review of text reports/records or other evidence of compliance
f837de7a-e742-58c3-ad9b-94a0eee9bc01 | note | Verification Activity: By - SE
49d5e48a-5c37-41cd-bbb5-042adc512848 | checkpoint | 4.2 - Undercut approval
1d06f3c7-5b84-5a55-a054-e15169e6cabb | note | Detail / Activity - Trench Foundation (subgrade)
2ac3c122-9b9d-579e-a946-1cc504a5f87f | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
db64166c-90ce-54da-8241-d303113133cb | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
6919c987-a9f7-5865-a1f2-7b8876c569b2 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
e8fa3abd-9023-5c6d-80a2-35bb7e79fba1 | note | Standard / Specification - PS-21.6.5 Table 21.5
bb952943-88c9-576d-a3b9-02eac5807966 | note | Verifying Document - Lab Test Report / Wastewater line record
1fb4ff03-60be-5b6b-a372-e5f80b83a0cb | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
8f50c74a-ccfd-5b95-80fe-d4f14fc4cbad | note | Verification Activity: Activity - H
d9fe1b37-96fb-530d-9c71-125eb45ac0a4 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
fefed304-bdf3-5cf5-9899-f6fb33a8ae71 | note | Verification Activity: By - SE
e0a4e981-255a-4d4f-be1c-b79959306aca | checkpoint | 4.3 - Undercut Backfill Compliance
0a749cc7-4ca7-5abe-b657-cddd4ac1788f | note | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
88922427-5274-55af-950b-85b63f97cefd | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
33171a1b-c6f8-5c2d-88f0-e36437dd49a6 | note | OR
fdefd2eb-e1e0-588a-8ab3-a575d42a6bb2 | note | ○ Clegg 25% CIV
e0477687-70bf-5ed8-86ca-73aebbf2b89d | note | Standard / Specification - PS- 16.5.12
4fdf3ee4-b26e-5c2c-bc79-eeb032bf8414 | note | Verifying Document - Lab Test Report / Wastewater line record
348c2530-4c2c-522a-8a70-0251a9bd86a2 | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
69af6e59-3b85-563a-bb6d-6744adfe743d | note | Verification Activity: Activity - H
9c0e2504-4b1e-5a5f-aa1b-481ca1bd2d04 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
cb166d6b-bdf0-508e-b207-92bc71cde1dc | note | Verification Activity: By - SE
c6e26249-6784-4e1c-aeac-09a7a0f8bf71 | checkpoint | 4.4 - Bedding Zone Compaction Testing
8a771d64-3ab1-50a1-96d2-96435dde443a | note | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip)
e8c63766-c5a3-5287-a79b-647fefb6b42e | note | Acceptance / Conformance Criteria - Bedding Zone:
b7968bd3-ee93-5995-8ff3-57e0fdd4d003 | note | ○ 100mm minimum thickness (compacted) over the bottom of the trench.
6420654c-9aff-5e3b-bbdc-6a9c07e22a82 | note | ○ Minimum Compaction- 85%MDD
6c40b49b-c651-5d7f-8a8e-ac418482b8e4 | note | ○ Paeangaroa Sand - 9 average CIV, 7% min CIV
0e259190-6871-5d86-9d3f-69248746187b | note | ○ Wilson No.2 Sand - 4% CIV
641b81ad-2f92-5d63-b4fb-d1f8a0cf1b85 | note | Standard / Specification - IFC Drawing 0320-1, AS/NZS 2566.2/2002 Appendix XVIII Site Instruction
0de6072d-3273-593b-b3d3-28b383c8286f | note | Verifying Document - Lab Test Report
02f8c01e-a2a5-5c56-81c3-c6e6c13137ec | note | Testing Quantity Required (based from schedule qtys) - As per WM Specification. One test per 20m evenly spaced intervals.
6d299e04-17de-50fb-99ef-ca743ed072dc | note | Verification Activity: Activity - H
44973ad0-8423-576b-8a86-d1f1042fc0ca | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e62e182d-aef0-5473-8840-a26c8421a56f | note | Verification Activity: By - SE
f67310e2-5f7d-42ed-8a41-4f4c5a73c66a | checkpoint | 4.5 - Laying of Pipes (DN315 PE Pipe)
7a47bd33-0fa5-5cd5-8e7d-c6a5000dc60a | note | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
a6dfea9f-5bab-501e-940f-682977224191 | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
089cc7cc-996c-54c8-a216-779eb11e3ebc | note | Acceptance / Conformance Criteria - As Per Drawings.
131910c8-7f6f-59cf-8e6b-da05e2a3e23c | note | ○ Facing upwards
5dfc0f90-aa57-56b9-867f-fd0ce9f941e0 | note | Standard / Specification - PS22.7.1 C
9f74074d-09fe-5c4a-a370-e80378fc9cc5 | note | Verifying Document - Visual Inspection / Wastewater line record
7b54afcc-8a93-5169-995b-27dbe35e2c36 | note | Testing Quantity Required (based from schedule qtys) - Every Line
4b8e3a34-c8b8-5672-87f9-f2cbac91822e | note | Verification Activity: Activity - H
c6ebe5fb-eb59-50b2-b0f5-99a341f31f00 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3f5b3686-6fdd-5c44-8906-b963bac1568f | note | Verification Activity: By - SE
8ba891d2-03fc-4fab-bb89-1635c8351104 | checkpoint | 4.6 - Compaction of Pipe Embedment Material
20c36103-5953-5f8a-a1b4-bba8fd7c724b | note | Detail / Activity - Compact embedment to required density
d87bfedc-37d5-5961-acfa-65dbdd73f7a5 | note | Acceptance / Conformance Criteria - Achieves 85% MDD, as per project drawings SHEET 0320
cbb66781-3612-54df-8f20-bfd7e5953c70 | note | Standard / Specification - Project Specification 22.13.1
1f1e2a9b-7da8-5e0d-ba2e-c9d7659a01f5 | note | Verifying Document - BACKFILL Check Sheet
7eaae33b-5653-5bf8-b57c-06e4f68ec48e | note | Testing Quantity Required (based from schedule qtys) - Every 20m, 200mm lift
914a1910-4647-5b73-b1e4-c22d6efbd87f | note | Verification Activity: Activity - W
6c6b15a7-f379-5f6a-bb43-55851dace2ee | note | ○ Review of text reports/records or other evidence of compliance
6ba52c1f-b22c-55f4-903b-c8a7186c3d21 | note | Verification Activity: By - ENG
bcefbfb3-efb8-4b9c-88ea-fb9d0efde334 | checkpoint | 4.7 - Cold Bending of Pipe
1fb15dd3-fb61-5269-a780-9a5ec1cdb05a | note | Detail / Activity - Verify minimum bend radius
cf5710a2-17d5-5a9b-9956-eb1accd0d5a3 | note | Acceptance / Conformance Criteria - Min bend radius 50x pipe diameter (31.5m)
33c47d51-96d9-5b8f-b23b-870da22484f3 | note | Standard / Specification - Contract Specification 21.6.6
8e437878-3ac8-5967-91d4-a72ea851892c | note | Verifying Document - Survey As-Built Records
e8762662-8725-5ccf-adab-4868146b8f48 | note | Testing Quantity Required (based from schedule qtys) - Every cold bend
608b29b6-b77b-51ba-98c5-dccb2ffe43eb | note | Verification Activity: Activity - I
d2606859-e14c-5de5-b72c-c1c63bc2b131 | note | ○ Formal inspection activity to be undertaken and recorded
f8eef60d-80da-59f9-a807-9324b3264f8d | note | Verification Activity: By - ENG
1ac1a44b-e779-4b75-bb64-8f8f7ec285ac | checkpoint | 4.8 - Pipe Installation on Curved Alignments
28980dee-2f34-53ba-a4eb-0b4fbf633f91 | note | Detail / Activity - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
24ec0258-a37f-54aa-9cb6-db18f59fc81f | note | Acceptance / Conformance Criteria - AS Per POP 202
55a3638b-6ae8-5d5a-bf3b-de2cc1067cac | note | Standard / Specification - PS 22.7.1 D
339bd724-3aca-5994-b89d-206afa03f08f | note | Verifying Document - Visual Inspection / Wastewater line record
77a4ac95-0fa0-5902-95cb-3053dae6ec6e | note | Testing Quantity Required (based from schedule qtys) - Every Line
6a6ca3f0-f27a-5788-a3aa-76c5f32dc245 | note | Verification Activity: Activity - M
d1e61c27-cf29-56cc-8261-39c861586cdc | note | ○ Monitor on Random Basis
f850e663-366d-51ee-965d-8fb982a0ba7a | note | Verification Activity: By - SE
4d37b3fb-49f6-4c74-bf3b-37e4c36fd6b9 | checkpoint | 4.9 - Tracer Wire Installation
88c7137d-faff-5c45-985f-161db4d861cd | note | Detail / Activity - Install tracer wire along pipe
ea09b2dd-ed82-51b7-9ac6-edfbc030e327 | note | Acceptance / Conformance Criteria - 4mm² multi-strand polythene sleeved copper cable, strapped every 3m with slack
0b464b7e-c0b6-53d5-933b-1d9cd0186b5e | note | Standard / Specification - Project Specification 22.7.3
1501e9e8-51d6-54be-ab8a-ee7e492b8464 | note | Verifying Document - BACKFILL Check Sheet
e6747fe2-704b-5ed6-933b-464cfbaf8678 | note | Testing Quantity Required (based from schedule qtys) - Every 20m
c11c0c2a-7ec5-5718-b208-9bb9bfb26a89 | note | Verification Activity: Activity - R
72864b9c-a8db-5286-8c08-72de3a7d36b4 | note | ○ Review
2a6e108c-0023-5b07-9b98-8a3f56384245 | note | Verification Activity: By - ENG
5bc79775-3e91-4486-a2c7-38a0662f109a | checkpoint | 4.10 - Northen Access Pipe Caping
6d0af6b2-e2e9-50cf-a829-08e9544f3edd | note | Detail / Activity - PETROLATUM WRAP SYSTEM
1a2336b4-7ebd-55d0-9119-ec90ddf9c47b | note | Acceptance / Conformance Criteria - IN ACCORDANCE WITH PROJECT SPECIFICATION as per sheet 0307
210c1766-2aed-5102-88b8-94d4cbc3b9f8 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
525076ff-9dfa-5c7d-b868-800c59ab53eb | note | Verifying Document - Photographic Evidence
5bc5453f-0214-51e6-a2f4-b9a97893f8db | note | Testing Quantity Required (based from schedule qtys) - Pipe end
35f33c77-b709-5597-96ae-b10067481ff8 | note | Verification Activity: Activity - W
baec4958-9534-522c-aa99-2802c29e4770 | note | ○ Review of text reports/records or other evidence of compliance
685055cd-d2fe-5473-a3ce-f27a8ae5dcd9 | note | Verification Activity: By - ENG
73249d69-206f-4204-a0cc-7f780cc5ecd6 | checkpoint | 4.11 - Northen Access Pipe Caping
0098b167-3f5e-551f-b05c-ec4ae5c5c1e0 | note | Detail / Activity - STUB FLANGE AND GALVANISED BACKING RING (PN16)
bc0d5b9d-a76a-5a76-9166-e97522a15899 | note | Acceptance / Conformance Criteria - IN ACCORDANCE WITH PROJECT SPECIFICATION as per sheet 0305
266e24ea-211a-539e-a91e-f49b841f516e | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
e0407057-2074-5535-bf3c-924c06716d31 | note | Verifying Document - Photographic Evidence
beb86dea-b8c4-5e32-9b71-2f4e3f2c3824 | note | Testing Quantity Required (based from schedule qtys) - Pipe end
27402a38-0923-5ee9-804c-33d098bd84ac | note | Verification Activity: Activity - W
f8b47527-e4a5-52ca-a57a-6d64475c5c4c | note | ○ Review of text reports/records or other evidence of compliance
3b455e13-e92d-5602-a6f6-fde7abe31a9e | note | Verification Activity: By - ENG
02a81974-3a7f-4d3a-8faf-cf7a347f4770 | checkpoint | 4.12 - DN315 SLEEVED ROAD CROSSING (Sleeve is already installed only pulling DN315 through)
d53a628e-6323-5efc-9560-23312ec91efa | note | Detail / Activity - THE OUTER ENDS OF THE SLEEVE ARE TO BE FILLED AND SEALED WITH EXPANDING 'PU' FOAM. ANNULUS TO BE GROUTED AFTER INSTALLATION.
64af1ec3-0b3b-5a50-b458-eccc7d03a5a6 | note | Acceptance / Conformance Criteria - REFER TO SHEET No's 312
b5478d95-622c-540c-be52-a1c3d75b43de | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
bd2e4bac-7999-5a67-b66c-22646fdef6cb | note | Verifying Document - Photographic Evidence
3c8fa5b2-2930-5819-9f9d-11f84ba41ea0 | note | Testing Quantity Required (based from schedule qtys) - PIPE SLEEVE ENDS
4b5044a7-ecbd-57d1-82d2-025aec6588a3 | note | Verification Activity: Activity - I
20e31a9e-7991-5174-84b1-77647b945679 | note | ○ Formal inspection activity to be undertaken and recorded
42d8631e-c33b-544f-8e46-6946b03987bd | note | Verification Activity: By - ENG
0dea1580-64ed-4c67-beb7-1b83d40f3b11 | section | 5.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Joint and Connection
9b365d12-1019-4a00-8013-3953fb9da7c6 | checkpoint | 5.1 - Flanges
d6a41a8e-8d84-53a9-b207-973ac80cef3d | note | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
0db143fc-9279-5fc0-9e58-56f358d59e09 | note | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
4390020e-6ae3-5dbf-955d-e134dde5f788 | note | Standard / Specification - PS 22.7.5 Appendix XXII
faf9dab9-d86f-5908-9d6a-2eb46806629d | note | Verifying Document - Visual Inspection
d2856cf9-b7e0-5199-a00f-7a1bd0c45efe | note | Testing Quantity Required (based from schedule qtys) - First flanged joint
e616c494-44f5-5d8f-8f0e-fd1d13e202da | note | Verification Activity: Activity - HP
ff03e527-be52-5e6f-b644-479652825eac | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3981cc0f-827e-5dfc-ab56-7aa2331567da | note | Verification Activity: By - ENG
d0303b39-9a12-44e6-93e2-4868f9522665 | signoff | AUTHORITY HOLDPOINT
c676f113-96aa-4990-9fe7-540bfafa9f52 | checkpoint | 5.2 - Bends
ddb5a6f8-45aa-54c8-bbed-4ba1ab9d8562 | note | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings or approcval from engineer.
da9ada77-fe4a-5b31-ab91-506020bc2ee0 | note | ○ Fitting must meets the same PN rating as the adjacent PE 100.
7194822f-c3da-58e9-ae78-35d20d4e36a6 | note | ○ Fittings must be suitable for producing the joints shown on the Drawings.
907bac13-93de-5c4b-b8c9-29ac4e28bb6c | note | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
783a2de8-5628-5826-9319-f559d735fd39 | note | Standard / Specification - PS 22.4.2 Appendix XXII
a203487b-191b-5534-bcc1-e2dc9252ed58 | note | Verifying Document - Visual Inspection
70a24b3e-e88d-50bc-971a-bf6c807562c3 | note | Testing Quantity Required (based from schedule qtys) - Project Drawings (232735.02-WSP-DR-WAT SHEET)
7b908a9b-5430-5aa5-8575-971d410a1c64 | note | Verification Activity: Activity - H
1751d4e4-356e-5ba2-9d03-f1f786a21b1e | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a8b3b0cf-b3ae-565d-91d0-0c22c8dc5afe | note | Verification Activity: By - SE/ENG
d92abc45-026a-484e-aaa7-a1764746b683 | section | 6.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Butt-Fusion Welding
14bf2f8f-bc2d-43fb-8058-d7785955b01f | checkpoint | 6.1 - Butt-Fusion Welding
90e29a73-a9a7-5084-a557-97c85afd65a9 | note | Detail / Activity - Use only semi-automatic or automatic welding machines.
273c97a8-0178-5e60-abc0-4f8a92fd34c6 | note | ○ Maintain a site record for all butt-fusion welds.
df764211-fd29-59fa-90fc-4b7be4053784 | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
77611649-58f1-5051-8700-80784f55a1a5 | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
9838e255-10f1-5ea6-9ad9-52f8f5461aee | note | ○ WMS Report
f5884cca-2915-59d3-af84-26325de40806 | note | Standard / Specification - Appendix XXII PS 22.9.4 C
e8bae7d9-18d8-5897-a605-064449c1b746 | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report
b1c55a27-1b0b-50e4-80ad-6b3e77f3c778 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
40ca3770-588f-5727-bfe5-f96b73936bc9 | note | Verification Activity: Activity - HP
39c8e0e6-2409-5a28-b060-f0a9fbba5a18 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e3d7dc3d-6759-52b7-a7e8-b54a3868549f | note | Verification Activity: By - ENG
cde867be-19c1-421f-9ffe-e52eb4dd3b0e | signoff | AUTHORITY HOLDPOINT
33f53859-92d3-445a-bb76-8eec925f467d | checkpoint | 6.2 - Butt-Fusion Construction Weld Test
bdc85d49-490c-5a15-8c56-afbaa8b85d15 | note | Detail / Activity - Test at least two welds from the first 50 welds.
22028126-b5c0-5f41-aa8d-3fd0d9cc4e15 | note | ○ One of the welds to be selected by the Engineer for satisfactory result.
657b9d57-36db-5b48-9292-4b529c80ca98 | note | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
c915428d-c87a-5d72-82cf-03c9148f1828 | note | ○ 95% tensile strength; welds aligned
33d29faa-c6f1-57cc-a1ce-5b9d73aab7c2 | note | Standard / Specification - PS- 22.9.6 (a) (iv)
599e6e53-99f3-5aa9-8136-02964e443f2c | note | Verifying Document - Test report
378b4710-30c5-5455-98cc-264262484057 | note | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
572482f3-6a94-5b20-a9d9-fcf6fdb36301 | note | Verification Activity: Activity - HP
1000d718-a19b-5c8b-b9fe-fd7eaefe9b36 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1faa8a34-6b58-5ab8-8ab5-4bcbeb65ccdf | note | Verification Activity: By - ENG
01e1c259-eafd-4f1b-9a09-dd9e124e66a8 | signoff | AUTHORITY HOLDPOINT
5f8dc8df-b5c5-421c-a395-3470050a1e36 | checkpoint | 6.3 - Survey
21878394-c62e-5f59-8e0e-38a47ad3e7b7 | note | Detail / Activity - Inspection of Pipeline Inverts
280b620a-1e37-5bf1-baa9-9ca2b32bb4a9 | note | Acceptance / Conformance Criteria - Vertical design Setout:
7f941860-ff56-5f9f-b78d-987816f93059 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
ada33788-759f-5465-b509-c6fa8b41631b | note | ○ Pipes > 1% grade: +/- 20mm variance
49e0c54d-4681-57f3-b395-04b54c62210c | note | Horizontal design Setout:
e0af0061-a77c-5c6b-9544-13263b06c666 | note | ○ +/-30mm variance
561d61fc-05e1-52ad-8de9-a0abdefce0d4 | note | Standard / Specification - PS- 21.7.6 Table 21.15
a1329a28-75fd-5b95-8705-9d28d0f07206 | note | Verifying Document - Survey Data / As-built record
f65bb9a9-b4e3-58ab-8117-0f60ee3f4877 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
d2548337-9372-542a-b93f-79c46f769f6f | note | Verification Activity: Activity - H
19cb7a09-677c-54d7-aaa2-077c5f474b5d | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
04a5fd74-dea4-50be-9ba2-61d280eafcb7 | note | Verification Activity: By - SE
bc44795a-f294-475c-88a7-9129fdc74e27 | checkpoint | 6.4 - Photograph of Each Weld
2823f444-922b-5690-a643-a127adebdf63 | note | Detail / Activity - Take sharply focused photo while clamped
7744d954-7ed5-598e-a3de-6844a2de3d1c | note | Acceptance / Conformance Criteria - Unique weld identifier visible
3ca5db58-f6dd-5061-848b-d9745a07ea76 | note | Standard / Specification - N/A
0569fc0f-8019-5c3b-a2ef-12a54eb08a86 | note | Verifying Document - Weld Records; Photos
8cebcbb9-a4e9-52ad-bfc5-d6c8e2521067 | note | Testing Quantity Required (based from schedule qtys) - Each weld
95f46dfc-907a-59fc-b8a6-8785d7c186ae | note | Verification Activity: Activity - I
b1d193f6-5070-5562-a470-284247471343 | note | ○ Formal inspection activity to be undertaken and recorded
2cc786cc-9f9d-5dd5-9207-43f5a643d3b8 | note | Verification Activity: By - SUB
5e4a4fc0-6219-46e4-ab24-e0c04d4c164a | checkpoint | 6.5 - Weld Treatment for Corrosion Resistance
20c95951-8fb5-5f09-8301-f82062ff5757 | note | Detail / Activity - Treat welded areas to restore corrosion resistance
64696f3a-04ce-5152-b3d1-519ef4b0864a | note | Acceptance / Conformance Criteria - Treated weld areas
cbe4f0f5-21a3-5e2f-9156-aeef2b60c0f5 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
54a546c3-0914-5d0c-9900-0730154a7458 | note | Verifying Document - QA Documents from Welders
34f8f621-3dbf-5364-ac1d-e82a96645914 | note | Testing Quantity Required (based from schedule qtys) - Each weld
6d9e952c-eb8d-5544-84f0-56b774f759eb | note | Verification Activity: Activity - W
f6602dab-cbfe-543a-8887-81eac5a83383 | note | ○ Review of text reports/records or other evidence of compliance
921efa27-618c-5402-b129-4b703f8dc363 | note | Verification Activity: By - ENG
606fb8df-8f66-4190-a6b5-c3252aa930c8 | section | 7.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Backfill
adda3746-9e96-48fa-b043-37af1ad7c3ee | checkpoint | 7.1 - Emebment Zone - (Side Haunch Overlay )
0395a1d5-5263-54a1-a5ba-199f314eff0f | note | Detail / Activity - Granular Sand backfill Compacted in 200mm Layers.
79cd4d8e-3655-541b-9c6d-3bf3aec7bd38 | note | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays.
588f3bc7-888c-534e-8e5a-9089bf6b6b8f | note | ○ NDM BS to be Carried Out
1f0abb27-437e-544a-8407-5b79b3a44d11 | note | Acceptance / Conformance Criteria - in 200mm layers.
3c42051c-e942-560f-aa0f-064bdbb56282 | note | ○ More than 85% of MDD
854ea9f9-0004-5243-b5ce-9facf0f02e6a | note | ○ Paeangaroa Sand - 9 average CIV, 7% min CIV
8ba87c65-1632-5db6-be6b-b55171f9902d | note | ○ Wilson No.2 Sand - 4% CIV
d415a984-6495-5e4e-9812-24fbfb94cdc3 | note | Standard / Specification - Project Drawing 0320 Site Instruction
5cbf9408-6e36-56d0-a475-f691e2563739 | note | Verifying Document - Lab Report / Watermain line record
07bd8ff2-ee67-5646-8ed9-0de75f861986 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals. 200mm lift
9ba39a3b-d330-5396-aae3-6dc814565bb6 | note | Verification Activity: Activity - H
04f0a95c-5cce-5a9e-8a07-2f1ad08e91d4 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c63b2a75-c169-5699-b361-23485b56ee4b | note | Verification Activity: By - SE
a0c10605-ff42-4ba6-8743-cc9ea5e96ba6 | checkpoint | 7.2 - Pipe Markers
60175142-07ce-5580-bcea-c49de208e190 | note | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
a0a083e2-d350-5d17-be92-af49071e0423 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
f770e492-6c01-5ee5-89ef-b115055a49eb | note | Acceptance / Conformance Criteria - AS Per Drawings.
9d2a1ded-064a-544a-8308-52bb4bfdee9c | note | Standard / Specification - PS 22.7.3 a
10751ef2-6b20-57f4-9bb6-1f72193d6083 | note | Verifying Document - Visual Inspection / Watermain line record
02e07aa4-db14-57d6-807b-bd4fd9840c09 | note | Testing Quantity Required (based from schedule qtys) - Every Line
273a3d07-c79d-5ad9-a47f-b2ed7bd96c4b | note | Verification Activity: Activity - H
52546b47-2062-597f-8936-823827f82ee3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0708930b-0721-5e6a-8170-dfe7274f76ab | note | Verification Activity: By - SE
6aca7fa2-ce16-433c-8aa3-e37a87b6b696 | checkpoint | 7.3 - Backfill Compaction Testing
257d5492-fc87-5153-a0ac-d56647a021bc | note | Detail / Activity - GAP65/AP65 Backfill Compacted in 200mm Layers.
9fff2f64-8959-5b74-9860-f0251fe97972 | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
47b73a36-b6f1-5d89-b7ab-55eea65e4b73 | note | Acceptance / Conformance Criteria - GAP65/AP65or site won material Backfill Compacted in 200mm layers.
ca3fe3df-da58-5521-882d-f5a5641993dc | note | ○ Testing to be completed on maximum 200mm lifts of backfill.
a9acf3b4-1192-5edb-ad5d-0c61661b21e5 | note | ○ 95% NDM on Shared and Carriageway.
ba267663-36cd-5762-81a3-af6e74d62678 | note | OR
8a74987b-f15f-5fb4-92f9-2cf6a1ebe0f7 | note | ○ 28% CIV
1cb1422c-4342-5aef-afc7-2e4c28beb14b | note | ○ For site won min >60kpa
92c242a3-9f0f-58d6-8e9b-e2f4ec864043 | note | ○ Ave > 80kpa
ee05aaf3-4453-5543-8036-9dcb48b12b87 | note | Standard / Specification - PS- 22.13.5, NDM Standerd 25832, NZS 4402 Test 4.1.3, IFC Drawing 0320-1
088e356a-5303-5225-88a6-1c23b92acee0 | note | Verifying Document - Lab Report / Watermain line record
6aefd8e4-e6d2-577a-8129-5cb9de88a74b | note | Testing Quantity Required (based from schedule qtys) - As per WM Specification. One test per 20m evenly spaced intervals.
f9212dff-2c01-5f85-939e-24f516aa57fb | note | Verification Activity: Activity - H
4188d4bc-3c8f-5d98-8b86-6d4289c2099a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1666bc08-f496-54e7-9e31-7fa32b6042f9 | note | Verification Activity: By - SE
5287c055-0c2e-4e28-b3bf-7ee5625e8ee9 | section | 8.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Inspection
3491e2f5-5cae-4ae1-b62e-60453a087cc8 | checkpoint | 8.1 - Pipe Inspection
ab857563-97c3-516b-bb2c-8aa78e4d19bc | note | Detail / Activity - Inspection of Drainage line
045f408c-fa24-5a6d-82ba-d1a778ff09d5 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
8032f40b-980d-54a3-93a5-da9876eb4112 | note | Standard / Specification - Internal
b1226beb-a82d-5b20-a059-eacb02684505 | note | Verifying Document - Watermain line record
43ff1373-6913-52ea-bedb-de91d9c8ccdd | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
547d88c7-6a98-58e8-8f91-cfc6b6a5350e | note | Verification Activity: Activity - I
64b1d57a-bf77-516b-8588-02d4959e689d | note | ○ Formal inspection activity to be undertaken and recorded
a5b19b9e-dfeb-5aa4-be50-76d89d3ec013 | note | Verification Activity: By - SE
4f32dc08-c963-44ad-b5ae-10f1d2f5eb56 | section | 9.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE TESTING
c18f471c-f977-4982-8e17-edfa404d7be8 | checkpoint | 9.1 - Pressure Acceptance Testing
9309ad23-9420-5bfc-8e92-843c9bc08134 | note | Detail / Activity - Backfill/cover with embedment before testing
408aae81-f80a-511b-a5f8-fbd955142e1a | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
a74854ee-6336-57eb-909d-7a2636ce2d04 | note | Acceptance / Conformance Criteria - Potable Watermain Pipelines – 1250kPa
e6928431-a733-5f54-9ad3-d05bf754b147 | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
0c6cd679-6286-50f1-aa94-f52d7dae2d5a | note | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
2f275a4b-9e6d-5b74-acfc-72b68c9d2b47 | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
cadd6a24-9a4d-54c9-8abd-3db8533e9527 | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
e296a074-a4dc-552a-b0c7-88950ad8b6a4 | note | Verification Activity: Activity - HP
5e2445d1-7e0f-5557-a1e0-c2ed94519d14 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d6799bc7-25bb-550a-a0b4-5ef0d7897d63 | note | Verification Activity: By - ENG
5aec365d-4c75-466a-80c0-3cf4e49bf14d | signoff | AUTHORITY HOLDPOINT
c8cab789-41ea-4847-b28d-a8c20a4a8d54 | checkpoint | 9.2 - Swab New PE Watermain
30ea0951-9bce-57a6-a359-2501f767d7bc | note | Detail / Activity - Swab to remove debris and air
7342dc34-dfeb-5b61-aa4a-6ac632ffbad5 | note | Acceptance / Conformance Criteria - Water running clear & removed entrapped air
d7d372d1-5b70-5e11-8e06-810e0c0d1532 | note | Standard / Specification - TCC IDC TS-7
5d11e483-0323-5308-88fa-7c171d23bc3e | note | Verifying Document - Swabbing Check Sheet
bf31b9d7-8774-51a1-b7e0-2ffd8da425ba | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed
9e35da18-4335-5309-8282-f1fa4383e92b | note | Verification Activity: Activity - H
22a182f3-8428-5382-8e44-44e278dc14ec | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a8ed0071-8f30-53f8-9e1d-973ae3cac0b3 | note | Verification Activity: By - SUP/SE
296dfbed-1bdc-4cdb-8d4e-82e3f6e75748 | checkpoint | 9.3 - Pressure Test New PE Watermain
7838e757-9a0e-528b-af40-ed9a95647c34 | note | Detail / Activity - Conduct pressure test. Due to not commissioning the pipe until later in the project, CB will complete our own pressure testing upon installation of the pipe, with the full pressure testing and chlorination to be completed once the pipe is ready to be commissioned.
b39fd60e-1bbb-5bd6-bace-aac71c15f0fa | note | Acceptance / Conformance Criteria - No leaks, no failure of any pipe, fitting or other pipeline component.
d22a3b46-a0ae-55d5-8f8a-a9455a7ebc01 | note | Standard / Specification - TCC IDC TS-7.1c Pressure Rebound Test Method; TS-7.1a Constant Pressure Test Method
eb607391-f697-5437-9bc3-ef2d824b7bb5 | note | Verifying Document - TS-7.1a/c Pressure Test Method (Test Report)
ca9a81be-e0d0-5e87-91cc-180fb1cc45b8 | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed & swabbing passed
6f07dab6-3775-5c8a-b187-816595f708b3 | note | Verification Activity: Activity - H
9c1a69d0-95f7-5400-b369-9c5eab881464 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5423d946-57fc-5ead-abe5-cf74746a1c83 | note | Verification Activity: By - SUP/SE
c6893128-6676-4694-8fe7-8883c8cbfed4 | checkpoint | 9.4 - Chlorinate New PE Watermain
cd01670d-5a94-5051-8216-f8df88807b19 | note | Detail / Activity - Chlorinate watermain
1c588cc7-8d6f-5bfc-bb25-5ca4bbb6b41b | note | Acceptance / Conformance Criteria - 5+ pH on chlorine tester
9734b9e2-53fb-585a-8cc6-6610a89783ba | note | Standard / Specification - TCC IDC IT-7.4.1 Disinfection Procedure
95cf0b00-02f5-5cd2-afc6-0d86798dcf74 | note | Verifying Document - Picture; Signed Chlorination Check Sheet
b4bf1e9b-7291-5697-ac58-b06b13a8710e | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed & pressure test passed
e28b2052-4664-5483-8378-1f51bdbde6b4 | note | Verification Activity: Activity - H
e3e8868c-28d4-51b5-9b74-2c4558e327d3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8c3bb1e7-572f-509f-a25b-dba33426bd14 | note | Verification Activity: By - SUP/SE
143616b8-7eef-4ae5-b525-4ba0b2b935bc | checkpoint | 9.5 - E. Coli Test New PE Watermain
a5c7b62c-e1bd-5ba5-bb32-2fe67446c385 | note | Detail / Activity - Test for bacterial contamination
988c6706-0c81-5808-898f-d7b3101d0c94 | note | Acceptance / Conformance Criteria - <1 E. coli; <1 Coliforms
af9b61f0-f805-59a7-85a2-abc476989b3d | note | Standard / Specification - TCC IDC IT-7.5 E. coli Sampling
424e6583-4f84-5201-816a-9866ead5e73e | note | Verifying Document - E. coli Test Report
0f540263-a4b0-531f-ae4c-b0994872c183 | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed & chlorine test passed
121d7921-36b8-504b-bba3-9154e1c66388 | note | Verification Activity: Activity - H
863d59b7-8912-5bf6-af5d-ec77d363d587 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5faeb940-1ead-57e5-91de-4807ef0baae2 | note | Verification Activity: By - SUP/SE
fb6750f6-b524-4f11-9e00-5fd245efc488 | section | 10.0 - CONSTRUCTION ACTIVITY - WATERMAIN Manhole installation
8a446ba5-2e2c-4ecf-8e88-8ea0b329ef45 | checkpoint | 10.1 - Foundation Compliance
dcb43dd3-d8db-5d69-8815-277e1ada2f10 | note | Detail / Activity - On Granular or Cohesive Material
317004ad-7169-5b8f-8b77-17bdb19fd3e8 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
1cc1233c-a410-51a2-a30d-d8482a16c66c | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
d15a7da5-a32d-5801-aac8-2c7c725a9079 | note | Standard / Specification - Appendix V Table 21:11
d23fad93-458e-503f-9572-190411237ee5 | note | Verifying Document - Shear vane or Scala test result
f64d4f45-bdb0-56cd-8253-48fc3cdae8e0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
365d6070-37d6-5677-b4f8-c07bcdada90a | note | Verification Activity: Activity - W
53e02dfa-7b92-53fa-a13f-4594f627a852 | note | ○ Review of text reports/records or other evidence of compliance
22034ab8-1c79-56a5-816a-a46e3e3a9242 | note | Verification Activity: By - SE
eac67216-0688-40d4-adb1-8ff053883ef6 | checkpoint | 10.2 - Undercut approval
cfb85291-c348-5455-9c63-00e07cee4a17 | note | Detail / Activity - On Subgrade
9514fa7c-8042-528c-90b7-4ac1c2424ed3 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
040457a9-6b43-5c98-9bf8-5c13aae3d493 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
5a2389cd-4fb8-5b1b-a69e-c1ddd76686b5 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
2d33d7ce-d632-51aa-adc0-34e6ac2eebdb | note | Standard / Specification - Table 21.5
dcabd807-f4c6-5ad8-a5c0-47b3dea8a910 | note | Verifying Document - Lab Test Report
6d9d00cd-c94a-5bf5-b1f3-aba90de04d9a | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
1378207d-24ca-54f4-8d02-d47978936028 | note | Verification Activity: Activity - HP
6adac04c-cd0e-5916-af34-95375881112e | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
398f6cc3-d353-5655-bd98-94992b138a6c | note | Verification Activity: By - ENG
83c0df00-b212-4e80-a7b3-cd92c7b24484 | signoff | AUTHORITY HOLDPOINT
6d33cbf5-8018-4864-b378-78d296dcc24f | checkpoint | 10.3 - Undercut Backfill Compliance AP65
5ff071e0-29b5-578b-996e-83722f38d571 | note | Detail / Activity - On Granular Material
02a04785-18e2-5bea-bbe7-224632c83a13 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
54f82909-82d1-5aa6-a391-3a66ee984f87 | note | OR
f16e9b31-1800-5e06-8f2d-49fbee80cfc4 | note | ○ Clegg 25% CIV
f34a8362-a59c-5e8e-944f-35e89cc5a9ea | note | Standard / Specification - PS- 16.5.12
458cdaac-9c94-52a4-ba05-76ebe1d312a5 | note | Verifying Document - Lab Test Report
c18cf0b9-5af2-5ec5-9e56-a02a998edab2 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
3fcc35ca-2b4c-5a9b-bec2-77c959880404 | note | Verification Activity: Activity - H
e57f4b73-0309-515d-8af9-2aa741e091ec | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
fa31cec3-a212-5bda-b6d0-d424066b6712 | note | Verification Activity: By - SE
d52bcbb7-aaff-4978-90d0-c2ee5bff7f78 | checkpoint | 10.4 - Bedding Compaction Testing Sand/AP65
e1b9ec2f-f97a-553a-8589-642915a74814 | note | Detail / Activity - On Granular Material
d00df76f-5d25-5fd4-a3fd-1cc01f5982b3 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
67ab8430-63ba-5b72-9ebd-d82d4daa3c54 | note | OR
894efc39-ccfe-5e3a-a26f-87a4a38726fb | note | ○ Clegg 25% CIV
7cfd9d9c-e8c5-5355-aa9b-2d9dd9f9c6ca | note | ○ Paeangaroa Sand - 9 average CIV, 7% min CIV
909a97d0-a4ed-5d11-a114-70ee6faea3de | note | ○ Wilson No.2 Sand - 4% CIV
99c49917-b652-5c78-b410-97aef3527ac0 | note | Standard / Specification - PS- 16.5.12, PS- 21.6.11
36a04ad1-d866-51b4-aa9e-3cc11b06a403 | note | Verifying Document - Lab Test Report
4238b720-239a-525d-a7e4-e8b03efa4ab7 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
cba5d684-7dc1-57db-a9d3-04ab16ed33f3 | note | Verification Activity: Activity - H
162bea11-a80b-5c5b-9843-7e1831e32878 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
cb19c3ac-ccd5-5b50-8b8d-d5013e45c00c | note | Verification Activity: By - SE
df62b43b-40e2-49cd-85ae-99997d78a60c | checkpoint | 10.5 - Survey
589c24b0-782e-52b7-9369-a7c096df4f16 | note | Detail / Activity - Inspection of Structure
effda697-27ca-59c3-8b68-e69b1224d434 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
d0580be5-695d-5ed9-9d19-f23a267bcab3 | note | Standard / Specification - PS- 21.7.6
af15ceac-aae0-5dfd-8273-e9254d8608b6 | note | Verifying Document - Survey Data
fda0cbb2-9eda-5e8b-a41b-af9e0c9adfd1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
110c9839-8ebe-5e14-9e04-89a81784cc30 | note | Verification Activity: Activity - H
27636530-5134-5350-81bf-207d0997a7fe | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8d22a48a-9cc1-5e34-984a-7977331eb8d7 | note | Verification Activity: By - SV
49d7690e-0404-4937-86d6-25872ff2c164 | checkpoint | 10.6 - Sidefill Compaction Testing
77286194-b078-5543-af44-4e0af3264378 | note | Detail / Activity - From the bedding layer to the overlay layer of pipe.
889d32d9-3c70-5a48-8b95-867dc078d294 | note | Acceptance / Conformance Criteria - AP20/GAP20
23e9b403-9f76-5a7a-9a0c-c0242c94b180 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
6fa524ed-c525-5af1-a3eb-094358af061a | note | ○ AP20/19mm chip
9774fcf0-28e2-589b-883b-1d93ecc2a080 | note | Standard / Specification - PS- Table 21.12
78a06213-a609-5a04-9bfe-f766c0ff2c40 | note | Verifying Document - Lab Test Report
1e6d9ed6-aef8-53ef-a9f9-ea836ac94df4 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
c3bd13c3-45de-58e2-822a-e1684b6eae9c | note | Verification Activity: Activity - H
d5285227-33be-5337-88b7-796177435bb4 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
84fa393c-8af8-5a23-9f8c-9a6c7eadc3b2 | note | Verification Activity: By - SE
1585b80d-cd29-4266-8a46-cef0cb0aba69 | checkpoint | 10.7 - Backfill Compaction Testing
eb344bb4-f7aa-5c0f-9bbb-e1edd00d4d1e | note | Detail / Activity - From Overlay layer to the subgrade layer
77304758-6fce-5704-b7b2-b35d983037e7 | note | Acceptance / Conformance Criteria - AP65
c63c1dc4-6219-5612-a988-254d0b5cad94 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
34475cf1-5a5b-5b7f-bb1c-e849ab96ca88 | note | ○ AP65-Clegg28%CIV
cd4e61ae-5e6c-5287-a900-9461ceb19171 | note | Standard / Specification - PS- 16.5.12
7b3a1e2b-03f2-502f-ba3b-d58d8f160373 | note | Verifying Document - Lab Test Report
c6ca100f-d9d9-50fc-9d23-7526ef9d616d | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
bbcc56fe-8044-5b66-af9c-f04788e2b879 | note | Verification Activity: Activity - H
4c8783fc-29fe-588d-8729-fc61eaa7ab40 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d75ddca2-f856-5258-bf15-01ac2852ece6 | note | Verification Activity: By - SE
3f6b4cdf-8294-4e2a-b81e-cef9183e3c74 | checkpoint | 10.8 - Manhole
a3d48955-c67e-5f02-b288-71d74736aaf1 | note | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
05240014-a2c9-5cc7-8d8a-501004cd3098 | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
8b0b183a-4bec-5da9-b19e-b0672121bb9d | note | Standard / Specification - Design Drawings
4cd16f4f-6cdd-5937-b3d3-e021f3a36828 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
42f87319-020c-5b17-b41f-4c75413bef2c | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
9a10c0e8-4a18-5d93-860f-b7c38f160bac | note | Verification Activity: Activity - H
c8333ac8-ed27-5567-ad87-824f1e30aa1d | note | ○ Hold Point (Internal)
163c9f28-180d-5029-a480-261eb1bec57e | note | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
18530acb-8f6c-5fa2-9405-59e8dc6400ad | note | Verification Activity: By - PE/SE
922dc297-1ee9-4451-8690-6590577aad1b | checkpoint | 10.9 - MH joints inspection
9929c7fa-4c76-5811-a211-45fef5f9dd09 | note | Detail / Activity - Inspection of joints
56e659f2-59bb-5220-a200-dd12aca34829 | note | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
cef53c7b-d49f-54d0-8b75-e32e02426ffa | note | Standard / Specification - PS 22.7.10
03c5edbb-9d5d-5bc9-913b-ac0ce80205b4 | note | Verifying Document - Visual inspection
abcaac80-f2e1-5767-9897-6e484f808320 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
9a572744-69d6-51e3-9b66-a8e428a076fa | note | Verification Activity: Activity - HP
3d7c6665-13e0-56e2-83e4-4aee9cbcf1ce | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a3f3cbfe-8465-5894-807d-bfae04d2e440 | note | Verification Activity: By - ENG
36e9f160-6928-414b-8f7a-7fb794a06936 | signoff | AUTHORITY HOLDPOINT
24c00551-fe2f-4687-93e1-bd2a59d57cb6 | checkpoint | 10.10 - Inspection
3093bff9-f338-5d7f-ab64-06b62f091767 | note | Detail / Activity - Inspection of Structure
02e5463b-e11d-5596-831c-5a8a6bb991e6 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
f697eef2-d213-56ed-a49c-c8ad2bae4da1 | note | Standard / Specification - PS- 21.6.11
1ee9c9bd-3dff-509d-b841-1b38a49dcbfe | note | Verifying Document - Manhole Record
6f2f9788-eb4f-5fe2-82c5-25368c3862d1 | note | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
d60de17e-6bcd-5186-9d5d-52e274c40751 | note | Verification Activity: Activity - I
4427dfb9-33c4-52b5-a3c5-01b150eb09ed | note | ○ Formal inspection activity to be undertaken and recorded
e16aaf0a-5295-59b2-b866-3741436db4d0 | note | Verification Activity: By - SE
3fc4fe61-21fc-4110-9585-3e4e261575fc | checkpoint | 10.11 - Plumb
55d5bd3b-cc23-5dd3-aea0-92b6b6e138f6 | note | Detail / Activity - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
1a656caa-90bb-5990-8e37-fdb6793344b5 | note | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
a0689ad0-3e2a-55c4-990f-f7850b1150cf | note | Standard / Specification - PS-22.7.10
057b5b3c-ae15-535b-a1b0-7dd39caedc00 | note | Verifying Document - Survey Data
4c52163a-e881-5783-9045-100a1c7b01ed | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
4c639ac8-880a-5999-a99b-92fc4ab47b42 | note | Verification Activity: Activity - H
8c6a7ccb-4c39-52f6-ada6-41625e498073 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
dfac666c-a6ea-59cd-a4e1-f01f8f4209e9 | note | Verification Activity: By - SV
370e7411-cfae-4fbb-a6d9-3cd33133528f | checkpoint | 10.12 - Step Rungs
bb28ebc2-c9a5-5d71-b924-f3784fd6df15 | note | Detail / Activity - Step rungs evenly spaced at nominal 300mm vertical intervals
53ee2dc8-10d6-53e9-b0e3-adb5a86d9266 | note | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
a4b60483-054b-5719-8b08-3c19df267b36 | note | Standard / Specification - PS-22.7.11
b052ee01-3953-5afc-95de-98a8ad8a0d87 | note | Verifying Document - Visual inspection
13806247-250a-5b4f-979d-1384ea630ccb | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
63cddc94-96e3-59a7-8ec0-168e6f8e9759 | note | Verification Activity: Activity - H
dada3430-e64d-5023-a343-437a3a64e7c2 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ab818838-1d19-5e42-bfad-0fd2251295a5 | note | Verification Activity: By - SE
f6cb4351-17d2-4f31-a790-013293efe5cd | section | 11.0 - CONSTRUCTION ACTIVITY - AIR VALVES
21909534-a743-41ce-98d9-77ef30032b1f | checkpoint | 11.1 - Installation of Isolation Valve
558bbc15-d351-582c-b772-86e65de9d10b | note | Detail / Activity - Verify installation per manufacturer’s instructions
a479ce5a-0f36-5e2d-a240-f050118f59ef | note | Acceptance / Conformance Criteria - Installed as per manufacturer’s instructions. Project Specifications
325e28a2-98f9-5c2d-ab77-5c639156ab28 | note | Standard / Specification - PS-22.4.2 Project Drawings (232735.02-WSP-DR-WAT SHEET 0314 to 0316)
6cf83721-988f-5446-b703-53cfb57cece3 | note | Verifying Document - Air Valve & Isolation Valve Check Sheet
ae4bd7cc-985b-5d57-b985-f9f9f9b47285 | note | Testing Quantity Required (based from schedule qtys) - Each isolation valve
d300c027-f183-5a5f-8126-03c6a137db6c | note | Verification Activity: Activity - I
b5c58421-c8ce-5000-b1b8-6225ab5b59f7 | note | ○ Formal inspection activity to be undertaken and recorded
ee3917d9-69e6-52ed-80a1-09b88107e960 | note | Verification Activity: By - ENG
f5ead15b-11d1-4b3b-ae74-a99382abaf81 | checkpoint | 11.2 - Installation of Air Valve
5e80afd5-1a05-5115-abab-17d6d2dfa281 | note | Detail / Activity - Verify installation per manufacturer’s instructions
023da151-1417-5f63-b6c3-082d050af728 | note | Acceptance / Conformance Criteria - Installed as per manufacturer’s instructions
6f1cef4e-d836-5a26-bd8e-7fcf05f51487 | note | Standard / Specification - PS-22.4.2 Project Drawings (232735.02-WSP-DR-WAT SHEET 0314 to 0316)
9445346b-7746-585d-ad74-004b7dbc8f2e | note | Verifying Document - Air Valve & Isolation Valve Check Sheet
d753886c-3c89-5d5f-9703-59dcdf4efb97 | note | Testing Quantity Required (based from schedule qtys) - Each air valve
dc44413a-a649-5091-95b3-9047296ba3ba | note | Verification Activity: Activity - I
54fd2061-acee-59ec-be4c-b142d724be81 | note | ○ Formal inspection activity to be undertaken and recorded
c24e1b4f-cfe7-595e-bc2d-abdfc0b03963 | note | Verification Activity: By - ENG
7989d23f-4fea-4d66-a1f7-b90e43c0cf23 | checkpoint | 11.3 - Backfill Compaction Testing
7e4a99ef-ac28-5c5a-9c49-835e5047237f | note | Detail / Activity - From Overlay layer to the subgrade layer
ee3b47ef-9666-5346-a9d6-266fa0d210ae | note | Acceptance / Conformance Criteria - AP65
b6f4cdf0-2200-59dd-a05d-64f695cc5b44 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
ab0ee8c9-1295-53a7-8fdc-136be4fcf2ee | note | ○ AP65-Clegg28%CIV
5becfc84-76c8-5841-bed4-a2e8b7f36fb5 | note | Standard / Specification - PS- 16.5.12, PS- 22.13.5, NDM Standerd 25832, NZS 4402 Test 4.1.3, IFC Drawing 0320-1
193bb1c8-46bb-5a84-b3e9-87aead91a882 | note | Verifying Document - Lab Test Report
3058ca6b-ba21-5c0f-8d7f-a2b5bc059f6a | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
bbaaafb7-26b0-5d57-9435-4cdf29c828b7 | note | Verification Activity: Activity - H
3d96031c-7127-55a6-89dd-dde072eb4772 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a6f4e6d7-cddd-5a64-b2cc-c3f186146fa3 | note | Verification Activity: By - SE
801b3f81-f633-4810-a1fd-4ca9363b0618 | section | 12.0 - CONSTRUCTION ACTIVITY - FIRE HYDRANTS
7ea74258-5592-4e6b-9021-3f4f73a79ef3 | checkpoint | 12.1 - Chamber Location
ab1497fb-b2f1-571e-ad57-b8091cf627a0 | note | Detail / Activity - Location of hydrants and air valve chambers are to be confirmed on site with the TCC Engineer and offset as far back off the seal as possible.
81763ef4-78c8-5000-8a73-a109f7c00ae7 | note | Acceptance / Conformance Criteria - Engineer to confirm onsite location
6e858308-13e7-54d4-a865-b1382d50888e | note | ○ TCC Engineer approval
87711939-ce26-54e5-a79c-b57e091f12c3 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT SHEET 0322)
8c3a2324-54f8-5bb3-8743-e0732b7a4301 | note | Verifying Document - PS-22.5.11 TCC sign-off
d67d87e5-c66f-5124-8041-abc45a2ba5c2 | note | Testing Quantity Required (based from schedule qtys) - Checksheet
e9c34eb1-75d2-5a8d-b524-28b9858dc4ca | note | Verification Activity: Activity - HP
99026907-7e89-587f-bdb5-0582696d5c6a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ca415fa2-7433-5f3d-96a4-f5024f6fdae2 | note | Verification Activity: By - ENG
e68527b5-ec3c-4cd1-873a-f715669322af | signoff | AUTHORITY HOLDPOINT
ef535941-971f-4130-938b-fe72c92bd589 | checkpoint | 12.2 - Hydrant Surround Blocks, Height to Suit
43ae7a82-a590-57c1-aade-b1bddbba16b0 | note | Detail / Activity - Hydrant box with 150 x 150mm concrete surround to be finished flush with surrounding ground.
dac05ff1-d3d2-597c-815a-e473ca36f648 | note | Acceptance / Conformance Criteria - 232735.02-WSP-DR-WAT Typical FH SHEET 0322
fcf5abb4-41a1-523a-a3f6-6907ae7e8c2e | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT SHEET 0322)
248ecc55-98dd-53a8-b651-763e2c9f00d9 | note | Verifying Document - PS-22.5.11 Checksheet
4030a856-c485-5831-82b4-f55a814e14ba | note | Testing Quantity Required (based from schedule qtys) - Supervisor to check. Checksheet
ea94e8c3-7468-54e8-96fb-76dd66005fb7 | note | Verification Activity: Activity - I
3e5b595e-2032-5867-856d-c2d127317b0b | note | ○ Formal inspection activity to be undertaken and recorded
9a7df52b-7f6e-59ec-9324-db1ff8db874a | note | Verification Activity: By - ENG
ce9a3178-1d60-48bc-bb89-e87ccf1f5869 | checkpoint | 12.3 - Install Ductile Iron FH
50fd7f38-a54e-561f-af19-e432c5d5544f | note | Detail / Activity - Heavy duty valve box installed as per TCC's Code of Practice
140a2328-146e-50a7-a1b7-d3a68400e50f | note | Acceptance / Conformance Criteria - Contractor to ensure flange drilling on DN80 end of reducer matches flange drilling on DN80 hydrant riser
df55b1a6-37d3-5383-b0d2-94c51af7b237 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT SHEET 0322)
2390aa9c-a86a-50b0-9753-d3280037fb9e | note | Verifying Document - PS-22.5.11 Checksheet
27c3c625-fcf8-568c-87eb-2bd8c4f203b5 | note | Testing Quantity Required (based from schedule qtys) - Checksheet
0bf83d3e-be0d-5ae7-aa6a-cb720da67070 | note | Verification Activity: Activity - I
674d34f2-05a6-58ae-ab45-164f032e3354 | note | ○ Formal inspection activity to be undertaken and recorded
d54b327d-a4c5-5b70-bca8-b3132970ab15 | note | Verification Activity: By - ENG
a28b7faf-0ea7-46c6-815b-5e0e6071258d | checkpoint | 12.4 - Concrete Pedestal on Offset Bend
33852085-d87f-53b9-9c57-607faa39126d | note | Detail / Activity - 3mm rubber seat between bend and pedestal 25MPa concrete pedestal
ace0ee21-b843-5b70-bac6-2ba140a9caab | note | Acceptance / Conformance Criteria - Typical FH sheet 0322
27d56ca7-8525-5803-aa30-14e24eaf04a8 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT SHEET 0321 to 0322)
befb1a4b-14f1-5c9a-9701-ec03e5661fe5 | note | Verifying Document - PS-22.5.11 Checksheet
cff57a20-1d7b-5733-a532-b119db1a39a5 | note | Testing Quantity Required (based from schedule qtys) - Per offset
0f99c761-45fe-518f-a0a7-e126012fe316 | note | Verification Activity: Activity - I
78c9a53e-0014-5afc-88de-092648afd9db | note | ○ Formal inspection activity to be undertaken and recorded
eff8a16a-7784-5c2c-97a0-4239ed92b3a5 | note | Verification Activity: By - ENG
8b231e93-fb1b-4012-bd8c-3160473fe20e | checkpoint | 12.5 - Anchor block and to extend past edge of concrete
16426158-b165-5306-b10f-e840e0cdf99d | note | Detail / Activity - DN315 - Type 1 Anchor 2000(L) x 600(W) x 2500mm deep concrete anchor block
ff401b37-dc33-5122-a314-3e86eabb095d | note | Acceptance / Conformance Criteria - In accordance with project specification as per sheet 0307
8641326d-edbc-5d19-ba51-858a5cbd13bd | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT SHEET 0321)
a2542504-aef0-5685-b00c-35d5063d7661 | note | Verifying Document - Engineer Approval
2c571c9f-5b70-58ae-b1e9-57d1eb8baace | note | Testing Quantity Required (based from schedule qtys) - SH29/Northen Access Rd intersection
5253bcee-de0c-5ddb-a575-fd4bfd2ba555 | note | Verification Activity: Activity - H
7ca0798d-0ce6-51e7-8a05-17a8adb2f9c2 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b8919eec-87ad-5526-a828-444096b53282 | note | Verification Activity: By - ENG
ce9a35e2-c711-4708-bf85-0b4e19268c05 | section | 13.0 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
f2b46918-9d20-46c0-a98c-555e7bf1e989 | checkpoint | 13.1 - Survey As-Builts
4d53ee63-22d1-5068-9a96-46c51cf2b326 | note | Detail / Activity - Quality Check on Nee pipeline and structure based on the tolerances in RITS
fb45d347-fb7c-5656-8a89-4033262926b5 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
c27f7118-981f-56c4-8557-5be00e361296 | note | Standard / Specification - Project Specifications
a7fa35dc-bc2e-5b3e-bee3-aacbea5b5331 | note | Verifying Document - Red pen markup only
4115c295-ee8b-54e1-a4e0-1781eccfde73 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
7c60742a-7328-50ea-b7a3-29bfb0113956 | note | Verification Activity: Activity - H
52d97a58-fcbc-50d8-9019-8e72463d7bdd | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ee4506a9-c643-5895-9740-7d203b4e19e6 | note | Verification Activity: By - SE
9e67b1d4-97d6-48f5-a7cd-448478032e17 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
3174952a-da63-5dbb-8823-7cb2f5853193 | textbox | Contractor's Rep Name:
39911419-2c8a-5265-9220-5e3b326569d3 | textbox | Engineer's Rep. Name:
67a67b9b-ea24-53b4-b4e9-034567f0aa46 | date | Date:
5a020de5-62ef-4e81-b823-1201f34b76e6 | signoff | Add Signature
c8e2d9e3-7c44-435f-b078-8e85d81e2bef | checklist | DN1210-SP2-011-004 ITP NAR Car Park Utilities Rev 0 | itp | DN1210-SP2-011-004 ITP NAR Car Park Utilities
31416e6a-1a72-4f8b-b3bc-05629fe7f60f | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINT - MATERIAL, PERSONNEL AND THIRD PARTY APPROVALS (P&G / ESTABLISHMENT)
167f622a-53ec-48a0-8105-17db1ce9c1f4 | checkpoint | 3.1.1 - Trench Profile
dc4d0c16-94af-5952-8c60-1d6cf1cf3128 | note | Detail - Tolerance of +/- 100 mm of the planned horizontal alignment and the maximum deviation shall be 1 in 20 in both the horizontal and vertical planes.
ee82d394-bdd0-51c3-8c22-3a5e3aa44416 | note | Acceptance / Conformance Criteria - Survey Set out
12181ef3-79af-5208-8ee0-84f2d135c3e5 | note | Standard / Specification - PS 25.13.2 a (1)
64eee00e-0abd-5b8a-94e8-3138d907b0be | note | Verifying Document - Survey Data
a9bf09be-d208-5319-8f36-911fe9ec2e58 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
7fdc1ebf-808f-54a3-b850-3017db2ed449 | note | ○ Review existing service location drawing supplied by WSP.
287eb33f-630b-5340-bff7-dec878fe4b1a | note | Verification Activity: Activity - H
88520a36-2fba-59e3-97c3-46e82b8bbd81 | note | Verification Activity: By - ENG
316c9d20-46ff-4781-aa1d-8e4435637e07 | checkpoint | 3.1.2 - Underground Services
27f9e143-6c45-582a-bc05-8ffc53769c28 | note | Detail - Pothole all services within traffic management prior to commencement of trenching. Accurately record the location and reduced level of each service and forward Engineer.
78923098-685c-5ec7-9600-61944c7ec611 | note | Acceptance / Conformance Criteria - Surevy Data/Existing utilities Drawings
cff41f64-9f2c-5446-88de-de56cd5617b2 | note | Standard / Specification - Appendix V
aabcacf6-b6a8-520b-8801-3922a7c90eb0 | note | Verifying Document - Survey Data
a8808826-bf2a-52d8-b6d3-faa61eb580b4 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction, Review existing service location drawing supplied by WSP.
4240013d-c11a-5dc6-9855-0398e7a60dd5 | note | Verification Activity: Activity - H
7a12e789-b68e-5ccd-b8c9-bbdd0bb7c59a | note | Verification Activity: By - SE
47a00fcb-0e57-4eab-85aa-7c19e3662e20 | checkpoint | 3.2.1 - Bedding and Overlay Material: Sand
dac8ace9-f63c-5383-89d9-2393cf90d07d | note | Detail - Material grading:PSD
841d7a98-16c9-5a22-9275-3b8ebf2ac36d | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
71e12e95-e5fe-54ea-b342-a0b1edc2082d | note | Standard / Specification - PS 25.13.2 g) & h)
36e25d7b-3c86-5c4b-9154-e426a6b3753e | note | Verifying Document - Delivery Dockets/Material Certification
88ac9573-f62d-5056-8230-59cb562f457f | note | Testing Quantity Required (based from schedule qtys) - NA
be61cd61-37f4-514c-97b2-5a286ed93406 | note | Verification Activity: Activity - HP
c6ca17e7-8520-5605-bd76-870254a2ee7b | note | Verification Activity: By - ENG
a2402fa9-bc5b-48b6-a49e-d3ea9b1bfd60 | signoff | AUTHORITY HOLDPOINT
fee5f329-edce-4d1b-9d03-648a034c4faa | checkpoint | 3.2.2 - Material grading: Materials (GAP20/AP20)
a64d99b1-1b0b-5ab6-9f6e-20f0110cdd95 | note | Detail - Material grading:PSD
8c4a3cb5-2bd0-5a66-aac5-68f3f3c4b48a | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
76383437-3bca-575d-9eb9-850c21e657dc | note | 19.0mm ¦¦ 100% passing
d9279f09-72fe-55fd-9b63-8822dd4453f0 | note | 13.2mm ¦¦ 80-95% passing
29b50c41-0f3d-5948-a92d-e51fe9b01f3c | note | 9.5mm ¦¦ 64-76% passing
5cc81ecc-8708-5eba-a00f-95ae0b7288bd | note | 4.75mm ¦¦ 37-58% passing
b16f4844-1d12-5427-979b-c0122a86805f | note | 2.36mm ¦¦ 30-40% passing
a2564649-e2f4-5094-8a5a-001cd0e761dd | note | 1.18mm ¦¦ 18-28% passing
891aacc1-85cb-5737-b4ae-49a00bbe149a | note | 0.600mm ¦¦ 12-22% passing
e2f51132-9510-5c73-8b80-b8f42ddb6bb5 | note | 0.300mm ¦¦ 6-14% passing
391aeb1a-1b92-5d0b-ba4d-9b522d956394 | note | 0.150mm ¦¦ 2-7% passing
8c2a6877-9f41-5eb4-a1fd-d2171bf6db89 | note | 0.075mm ¦¦ 0-3% passing
43e704f7-15f2-5dc3-bab6-458d0cbe9bd8 | note | Standard / Specification - PS-21.5.7, PS-21.7.2 Table 21.2
e00bc39b-c277-50f4-ae09-2b6d4fdfea47 | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
655b71c1-3359-5aa9-8626-be07708842e7 | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
578ce12b-e235-590e-b55c-aeeb8373872a | note | ○ 400-1500m3 ¦¦ 3 Test
3b7fd4f2-df3c-5515-a43a-e9589ebb7db8 | note | ○ 1500-4000m3 ¦¦ 4 Test
a6c0daa3-8d00-550e-85c0-24502cd64bbd | note | ○ >4000 ¦¦ 1 Test Additional 1000m3
b8217abc-03d6-51a5-983b-f2c0a1e26083 | note | Verification Activity: Activity - HP
89613215-39bd-52dc-92dd-e5a885b6fed8 | note | Verification Activity: By - ENG
b536c440-617c-4206-b5f2-d33235373da0 | signoff | AUTHORITY HOLDPOINT
7141088f-bd2f-444c-9e14-80ab15c65f7e | checkpoint | 3.2.3 - Weathering index: Materials (AP20)
32713f92-6f62-5663-95a8-2ee377ba89fb | note | Detail - Weathering index:
88ed4439-c756-5b80-8cfa-345e6ff47663 | note | Acceptance / Conformance Criteria - AA to CA
e3427a65-cfae-56d9-ac6f-ef9e44267feb | note | Standard / Specification - PS-21.5.7, PS-21.7.2 Table 21.3
2a56127a-aa5d-5a69-820d-522450eed185 | note | Verifying Document - Lab Test Report NZS 4407.3.11
1079d856-e5c3-5c85-b16b-1fe58a811ae8 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - 2 test per source
1028389f-da2e-579b-aaf2-e9d635677b97 | note | Verification Activity: Activity - HP
e508eb89-8246-5008-bb39-93d86489803c | note | Verification Activity: By - ENG
da02661b-02e0-4cc3-9554-fef061888aa0 | signoff | AUTHORITY HOLDPOINT
e5fa7ad2-cea7-42b3-a506-9325b2c57c1d | checkpoint | 3.2.4 - Crushing Resistance: Materials (AP20)
76167ff8-66c9-52f8-8399-946e257e5aa6 | note | Detail - Crushing Resistance
c7f599a1-defe-5b4b-9460-8d321f55136c | note | Acceptance / Conformance Criteria - >100kN
7fba4832-18c0-5c26-be3b-df246fc828a1 | note | Standard / Specification - PS-21.5.7, PS-21.7.2 Table 21.4
2f2d3802-c3f9-5a2c-976f-5c4af148f967 | note | Verifying Document - Lab Test Report NZS 4407:1991 Test.3.10
45c621e4-3bb6-530a-8a98-36209fd22a3d | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - 2 test per source
684709a3-97a6-54b2-9035-eb1e35a9e7bc | note | Verification Activity: Activity - HP
65736009-7460-5b78-b148-12c20e07ac40 | note | Verification Activity: By - ENG
aec6d19e-0f81-4ba5-906b-872228954b60 | signoff | AUTHORITY HOLDPOINT
7a8baf28-01ca-47b2-8410-10bc27706613 | checkpoint | 3.2.5 - Material grading: Materials (Gap65/AP65)
d097d48f-4a14-568b-a304-00471af53708 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
056fdc37-d9df-5e44-ad14-57b8ea405605 | note | Acceptance / Conformance Criteria - No Particles >200mm
e49e12a2-6b18-5b21-93cc-7de9e8eb6e02 | note | ○ Maximum fines 10% passing 75micron sieve
60c742e0-05e8-55f8-bed1-a8e04ddd9e6b | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
896f30cf-a791-5482-86ca-1715c020cfa6 | note | Verifying Document - IANZ Accredited Report
125cf9d9-0085-5172-93ab-7f11ab5b3ac4 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
52095d33-cd13-530b-998b-b8427c204ba5 | note | ○ 0-400 - 2 tests
0c8fd824-ba43-544b-a3d4-de5f69ab4628 | note | ○ 400-1,500 - 3 tests
460e6d0a-3c3b-597d-9e3d-2a1f1b266557 | note | ○ 1,500-4,000 - 4 tests
6f16e5e7-0623-50bf-a348-c7e992ac39a1 | note | ○ >4,000 - 1 test for each additional 1,000m3
bc141245-b7c0-5434-82a8-8c364ebcd534 | note | — Results to Engineer 2 wks before importing
9e2c70b5-61fb-58e5-832c-4effa2bf618d | note | Verification Activity: Activity - HP
2eec481f-9cf4-5686-b060-ed7b0150e446 | note | Verification Activity: By - ENG
95c0b86e-689f-4e2e-a3a7-1fff1891c8cd | signoff | AUTHORITY HOLDPOINT
1b9dc31b-0042-48b2-93f9-2de5d3abf9c8 | checkpoint | 3.2.6 - Weathering index: Materials (Gap65/AP65)
3191f2d5-78d8-5e48-a19f-bd9da7ac5601 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
3ddb57d0-cb3e-5e19-a877-c604c84ead6c | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
f8405833-59ed-59a6-bddf-5df856a91df5 | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
66b4ecba-ea93-5a40-aa35-4ab75b678738 | note | Verifying Document - IANZ Accredited Report
a874eea7-4c69-55ed-99f6-b9dbe2ed0d26 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
d4825e41-94b1-58c6-a1a2-0421be986acc | note | ○ Results to Engineer 2 wks before importing
f614a62c-2d2b-5fec-8005-75c57652cf9f | note | Verification Activity: Activity - HP
54eb6868-22fd-5d12-baa3-df9d482f9a87 | note | Verification Activity: By - ENG
cd743370-b4b7-4a07-8f7b-c7686628dcc8 | signoff | AUTHORITY HOLDPOINT
4bb39282-3764-40f9-a798-108956f652a0 | checkpoint | 3.2.7 - Crushing Resistance: Materials (Gap65/AP65)
702ce64f-1529-563e-b8ef-5cffbdbb2101 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
87ce7e29-fc9f-5e28-9a39-4952a0836c45 | note | Acceptance / Conformance Criteria - >100KN
4a1a4758-50b7-50d5-b206-d566aef1391b | note | Standard / Specification - Appendix XVIII, Appendix V
8459cf06-578e-5efb-8563-23b3e5b109d2 | note | Verifying Document - IANZ Accredited Report
14947551-f5f8-5393-a2e3-adbd4a71352e | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
c402c280-bb53-5f3f-915f-f9903e78c6e6 | note | ○ Results to Engineer 2 wks before importing
f6c1897e-6a74-5fda-b870-70be7a136160 | note | Verification Activity: Activity - HP
48bfdc18-e999-5eea-bdd7-8ef37d509144 | note | Verification Activity: By - ENG
d5a54716-54e5-4c65-bbd5-7297e10c538b | signoff | AUTHORITY HOLDPOINT
31c3cbe6-3c05-4de3-93ca-4a0a4cd539dd | checkpoint | 3.2.8 - Materials Approvals
0709e550-36fc-5563-8a64-0218e4a41dda | note | Detail - All works and materials are to comply with the National Code of Practice for Utilities Operators' Access to Transport Corridors, and Individual Utility Providers Requirements
aa544c6c-e323-5b9e-b73c-fc0350e5684f | note | Acceptance / Conformance Criteria - Prior to Commencement and throughout construction
d4d6c877-27d4-5976-8cbe-06d341d4d5a9 | note | Standard / Specification - Project Specifications
56512c1b-55ba-52ab-acd8-fb7d7f4d29a2 | note | Verifying Document - Utilities Providers Approval/Material Certification /Delivery Dockets
87fe9419-ff35-5ea2-8b98-8e99d6121749 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
59e18e1f-a749-5d8e-8791-6e87f0761818 | note | Verification Activity: Activity - H
ab3b4aa2-1cdd-5ad9-927d-b74a4f36c0af | note | Verification Activity: By - SE
0289ae13-60f7-4159-a5c8-d5e3cf4a9c44 | checkpoint | 3.3.1 - Pipe and fittings. Ducts
91c805c1-5a07-5dbc-b9d5-bb694ae1b0ba | note | Detail - Duct Pipes shall be of the size, material and class nominated in Drawings.
48bceb27-4a1c-544c-8244-6d9049e72d0e | note | ○ Ducts shall be high impact uPVC
06cebdf2-168e-5383-aaff-ee74a17a9270 | note | ○ Duct colours shall be to local authorities requirements.
67409894-38f2-5d9e-9908-4973fa875861 | note | ○ Duct colours for the different Utility Structures must be in accordance with the guidelines.
da4eaef7-e478-59c1-9bf7-c7552f7fbb78 | note | Acceptance / Conformance Criteria - Duct Pipes shall be of the size, material and class nominated in Drawings.
63c90ff3-2a7d-5262-bc5b-332ff20d0269 | note | ○ Ducts shall be high impact uPVC
0cd623af-a077-51ff-a39b-aab2abc37658 | note | ○ Duct colours shall be to local authorities requirements.
cae3dd00-d779-5071-9656-d05b1a23dbdd | note | ○ Duct colours for the different Utility Structures must be in accordance with the guidelines.
e7e07244-2b5b-5f51-be7f-90e6a6b8f927 | note | Standard / Specification - PS 25.13.6 b)
fb0bf198-2fd9-590c-b3f7-0e9190f1e008 | note | Verifying Document - Delivery Dockets/Material Certification
ab712562-830e-5dbf-82c1-e75081b37b56 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
43d6b342-3e2c-5638-b941-db90ab06cb21 | note | Verification Activity: Activity - H
8b6ca9a4-5817-5714-aac2-33b0bad5aed3 | note | Verification Activity: By - SE
082d9395-a088-498e-9b02-6ca968486ea7 | checkpoint | 3.3.2 - Bedding material
e6b9d287-ec67-53d8-be95-ac44f96fed47 | note | Detail - Free of larger sharp particles conforming sand
1024ac67-cfbe-5382-80b9-aad9ad85fadb | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to sand
fc7c32a5-8d81-5eb0-b373-9f4f2fc342bb | note | Standard / Specification - PS 25.13.2 g) & h)
6f25c904-eea5-5983-9b58-0f795255c45b | note | Verifying Document - Delivery Dockets/Material Certification
2dd8b0bf-77ef-514a-ab16-6ca2671e5e50 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
0b57a5ee-b09e-5f4c-88eb-3dd41d5b6c75 | note | Verification Activity: Activity - H
c4c76df3-ead0-5f98-8acf-4001b7d1552c | note | Verification Activity: By - SE
f200b634-b945-4913-aea4-9871adbdae57 | checkpoint | 3.3.3 - Backfill Material
a3b2dce0-0fef-5868-b674-68cadd2ce464 | note | Detail - Under roads, driveways and footpath - refer to pavement section for appropriate materials and layer thickness.
3eb87d15-4ef9-50d6-a930-2952cc7e385c | note | ○ Under berm or grass areas - site Won materials to be approved by Engineer or GAP65 to be used if site material does not meet Specs
812b4976-8086-561a-ba97-bd38bfb9f1c3 | note | Acceptance / Conformance Criteria - Comply with Project Specifications
62f93ed6-d72e-58e2-9fb8-6992e47f02d2 | note | Standard / Specification - PS 25.13.4 a)
d4935597-45a8-5b88-a337-2d58dfde51d2 | note | Verifying Document - Delivery Dockets/Lab Test reports
eff45966-461f-56bc-a55b-636a5a239a7d | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
a71a7b90-eace-5845-aa50-3878a8895392 | note | Verification Activity: Activity - H
7e467d1c-5b57-52ad-86f2-198dcb1d6cac | note | Verification Activity: By - SE
944617d9-759b-4d9f-a6dd-6edc65b4101d | checkpoint | 3.3.4 - Pits Covers
2f75e167-ba7c-582a-a53d-8eebc5ca9046 | note | Detail - Jointing and pulling pits shall have slip resistant surfaces complying with AS/NSZ 3661-1-1993. the cover set load rating shall be in compliance with AS3996.
e566db8a-3708-5d81-ab0e-4d5ec58cd684 | note | Acceptance / Conformance Criteria - Class A-10kN loading - footways and areas only accessible to pedestrian and cyslists.
1df244f0-6c91-5e9d-9484-650cdaf6da9a | note | ○ Class B - 80kN loading - footways that may be mounted by vehicle or livestock and light tractor paths. (Light duty)
08428316-6b0b-5921-ad47-56f93ca95a2c | note | ○ Class C - 150kN loading - grass verges or other areas open to slow moving commercial vehicles such as tractor mowers etc (medium duty)
76e19a74-7662-5314-be3d-b35e2a8cb417 | note | ○ Class D - 120kN loading - Carriageway of roads and areas open to commercial vehicles (heavy duty)
037fac23-ecb9-52a1-931b-42a7cb90e7a3 | note | Standard / Specification - PS 25.13.6 c) AS/NZS 3661-1-1993.
dc509168-57d9-57a6-89b3-4515d40ca755 | note | Verifying Document - Material Certifications.Delivery Dockets
0522ead6-942a-5944-a8d4-c8d9a1957f03 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
e7bca34c-5bae-5b97-af84-d8d4f734f09c | note | Verification Activity: Activity - H
3422f6cc-e495-5f02-b129-17add8ca67c5 | note | Verification Activity: By - SE
c66b8e43-4ba1-43af-81b4-55b491e56873 | section | SECTION 4 – CONSTRUCTION ACTIVITY
ddf370f5-a150-42bc-9701-f0fa5b606c30 | checkpoint | 4.1.1 - Trench Excavation
ab84c873-9849-512f-8aaf-ef621e5e06d5 | note | Detail - To be excavated to within a tolerance.
c1f32f91-3c9e-5a98-b53c-2b5368c4935e | note | ○ Not more than 100 metres of trench associated with each site shall remain open at one time.
fcca6ea9-d116-516a-8a61-72d9d2d1a9a1 | note | Acceptance / Conformance Criteria - +/- 100 mm of the planned horizontal.
fef1ee4c-a650-561e-8d8a-50c53beba3e6 | note | ○ The maximum deviation shall be 1 in 20 in both the horizontal and vertical planes.
f15b5e68-b7d6-554b-be03-6287f8fb9007 | note | ○ Less than 100m
dc92b061-ebff-5d3b-b8b7-ba9504c6a521 | note | Standard / Specification - PS 25.13.2 a) i
abcef8df-02e3-5a66-9e9e-356c51a470e5 | note | Verifying Document - Survey
4f795888-ba94-5741-bef7-a958e74c6df1 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
1d4b1903-38b8-5de1-b2b0-eb24a5abf4ab | note | Verification Activity: Activity - M
a1401de3-b44b-5d94-987b-adca085b4a50 | note | Verification Activity: By - SE
3844db9a-a65f-408e-bcca-c236ad92facc | checkpoint | 4.1.2 - Unsuitable Materials
4ea1518b-edcb-5348-80d8-2b1187c3a110 | note | Detail - All confirmed unsuitable material shall be excavated down to suitable materials.
8552d543-c189-5b5e-a386-2f1171475bde | note | Acceptance / Conformance Criteria - Dig Down to Get Suitable Materials or get Engineers Approval.
da4d3711-ba2a-5664-99de-be806b2a5f75 | note | Standard / Specification - PS 25.13.2 b) ii
65e7d462-019f-5017-b36d-f83f16d04168 | note | Verifying Document - Checklist
d846b0b4-fb3e-5962-a686-f18fd7022b8b | note | Testing Quantity Required (based from schedule qtys) - Each Cable
9eadc343-d98b-593a-b7bd-d9c68484309a | note | Verification Activity: Activity - M
4f1f0345-8381-5db3-aff6-8f3d2df47358 | note | Verification Activity: By - SE
3cd54d43-0ac5-4e07-9b18-f6c163bb65f5 | checkpoint | 4.1.3 - Foundation Compliance
62e1ffa1-0f88-5f4c-9112-a477fae9d802 | note | Detail - It shall be de-watered prior to installation of bedding material.
4df8b94f-0f6e-5a17-964b-8c53aa6e4d7f | note | ○ If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
1010a3a8-fc93-5052-851f-db1ffd22543f | note | Acceptance / Conformance Criteria - 50mm granular layer shall be laid and compacted before the bedding layer is laid.
822bad2f-256a-539f-8da2-9a8444d2f894 | note | Standard / Specification - PS 25.13.2 c) and g)
88302294-04b9-50ce-bcf7-c9c9faab0a18 | note | Verifying Document - Checklist
54573829-ddfe-5515-b211-89c54f5093ee | note | Testing Quantity Required (based from schedule qtys) - Each Cable
662e5ee8-9767-5952-a2d0-11dc6e9438a4 | note | Verification Activity: Activity - M
f8846e9d-ddd1-55e5-ba9e-2f57dfd0fb5d | note | Verification Activity: By - SE
8693ae5e-d63d-4887-9f2d-89cca0268b12 | checkpoint | 4.1.4 - Bedding
54073dec-6c1e-529f-b449-7ac3a32abe78 | note | Detail - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
9ebc9059-666e-5918-8085-f265f83e3797 | note | Acceptance / Conformance Criteria - Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
81e0d7c9-c23f-55b2-a7c8-1ccccff13a6a | note | Standard / Specification - PS 25.13.2 g)
3d2937f3-a5c5-5cd1-86f8-714c0ffa7556 | note | Verifying Document - Checklist
58dcd6c4-571d-5d9f-85fc-9f5265aa1127 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
8c65e9be-b0e9-54cb-b4e7-049fef8a06eb | note | Verification Activity: Activity - M
1623ec63-c466-51c2-87d1-74b3f6084865 | note | Verification Activity: By - SE
e552c628-fba7-4388-a984-c01b061a91d6 | checkpoint | 4.1.5 - Installation of Ducts
a3e2cabc-4daa-51c4-8597-1d9dc0873a58 | note | Detail - If more than 2 ducts are being placed.
a94a2c63-b2be-5d4b-833d-f15563764093 | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
79e3389e-5e4c-5196-8c09-ddbe84b8cafe | note | Standard / Specification - PS 25.13.7 b) iii
41f73cc7-2ff7-563b-9c8e-229d3fb060c9 | note | Verifying Document - Checklist
e15dca10-38cd-5628-817c-6019ac2f7c92 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
f4fb0981-c0e3-54ad-8bab-971714c6dd77 | note | Verification Activity: Activity - M
ab3c604a-e849-5bd9-be32-60ed766775f4 | note | Verification Activity: By - SE
0fb7599e-ba20-4c38-b425-d4523e0b279c | checkpoint | 4.1.6 - Draw Wires
22531199-839d-5cf0-8baf-fd0439c39d5d | note | Detail - A draw wire shall be intalled in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting.
68257d4a-a886-5675-87b5-4ed3513a0d5f | note | Acceptance / Conformance Criteria - Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load.
7430857a-6d06-5233-b696-5dc2f89ab587 | note | ○ ≥20 years design life.
b5b0f480-877f-5526-87ad-1a541a7842ba | note | ○ The ends of draw wires shall be made fast within the pits and be secured to the duct plugs.
c2612497-eec6-50c7-b939-0aa4400efb93 | note | ○ Blue colour wire
35c492cb-b95b-53b2-9a05-c0664bbd5242 | note | Standard / Specification - PS 25.13.7 e) ii to iv
09d0aa99-2027-5ff3-bcfa-b4f7c6ba3a11 | note | Verifying Document - Checklist
d102bc8d-7553-5d6a-850a-dde1f547bcd5 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
ce7a3af2-9e76-57fa-b906-f03d264d7322 | note | Verification Activity: Activity - M
e6e5031e-3ac1-5559-841d-4f81387f015f | note | Verification Activity: By - SE
7f65f78a-fb06-436a-a08d-56a7a4dc09b5 | checkpoint | 4.1.7 - Caps
fa796ca0-ff90-55e9-88f3-c48ca1f6a9fd | note | Detail - All duct ends shall be capped
0ffab495-4da1-50ca-932d-38b284c84048 | note | Acceptance / Conformance Criteria - Capped ducts
37a7f948-6d24-5aa4-8853-4fda17702d9a | note | Standard / Specification - PS 25.13.7 e) v
125e0c2c-3443-509a-a878-19982f3c13d2 | note | Verifying Document - Checklist
1e912a07-12e2-5cf4-b58e-a3911de827ea | note | Testing Quantity Required (based from schedule qtys) - Each Cable
a02f1021-fd36-50db-888a-101b805a43ef | note | Verification Activity: Activity - M
4422b74a-36ac-57d7-9366-3d8fa5e354c8 | note | Verification Activity: By - SE
0d3f09d0-a71d-4f11-aeb1-18df725b0204 | checkpoint | 4.1.8 - Warning Tape
d350cf75-8eaf-5ad2-9481-3731aa33da51 | note | Detail - Warning tape to be placed above services.
8acac456-f941-593b-9f85-26b7e9ad2764 | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the topmost duct
e1cc7675-fe69-5a9e-93fa-fc7b43d76f1f | note | Standard / Specification - PS 25.13.7 b) iii & f)
5dc10d0b-5183-5d7a-a742-c514152c50bf | note | Verifying Document - Checklist
dd480cfe-05ee-55ff-b88d-d4c614ee8071 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
c23cae98-cc43-543a-95b2-edf3f3055238 | note | Verification Activity: Activity - M
da39d855-d558-586c-904f-e14d70cf7cb1 | note | Verification Activity: By - SE
0ae51120-62b9-42f1-b0d4-dbf152a190e5 | checkpoint | 4.1.9 - Overlay
b7106ee9-8a86-5f96-95c9-3814e1230a70 | note | Detail - 99 mm minimum sand placed on top of duct.
c9480878-2f2a-5740-bf40-769305c7bbb5 | note | ○ No mechanical compaction will caarry out till 300mm drom top of duct.
1bf80e5f-0556-55d4-9abb-49aa6a6e11ea | note | Acceptance / Conformance Criteria - 100 mm minimum sand placed on top of duct.
b863583b-e7c1-563d-af2b-1655415e1372 | note | Standard / Specification - PS 25.13.7 b) ii
6fcc59b9-067c-5a80-8d6a-6633ae97020c | note | Verifying Document - Checklist
8b054213-4d2e-5c97-8516-104f302f109f | note | Testing Quantity Required (based from schedule qtys) - Each Cable
6dc62bde-5c89-5a1d-9c0e-9b2485a1581c | note | Verification Activity: Activity - M
40a30c9e-63df-522b-a341-86086019c866 | note | Verification Activity: By - SE
a9d569ae-364d-49de-9f9b-ae9a1a9703bd | checkpoint | 4.1.10 - Backfill
e43a0fdd-f75a-54e5-a961-de786fbb006b | note | Detail - GAP65 to be used if site material is not approved.
f41a82af-78a8-53e6-a3e3-34b691180235 | note | Acceptance / Conformance Criteria - Clegg Test every 200mm compacted layer of GAP65
3ef0f6df-3eaf-556e-baa7-87408a1fc0cb | note | ○ clegg >28CIV
0f63fde2-a483-53a3-925c-434d15de5151 | note | Standard / Specification - PS 25.13.10 a) modified
97c6cc71-8989-556b-b6a0-6174b90e9859 | note | Verifying Document - Lab report
ec6c3332-4570-519d-8651-7234b43b0fca | note | Testing Quantity Required (based from schedule qtys) - Every 10m
f4348b82-30be-5ee4-b483-06b9642b274c | note | Verification Activity: Activity - H
a4d8fad5-952f-577d-89a9-c7a9634f77ad | note | Verification Activity: By - SE
43715943-78e1-4a1f-93a2-faf6af1d098a | checkpoint | 4.1.11 - Pit Installation Location
c8accd72-402c-5001-9c46-f1d34e002de7 | note | Detail - Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid .
3e0760e7-7f8c-508e-8beb-68dfa86c2fe1 | note | Acceptance / Conformance Criteria - Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas.
bfc80804-552e-5c9c-95b3-23a1f8ea99e8 | note | ○ When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side.
a0c2c12d-fc0a-55e3-95ee-b8ed90987a3e | note | ○ When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side.
e74a7882-2125-5df7-b65a-3633d70917f3 | note | Standard / Specification - PS 25.13.8 a) i and ii
00b50438-70d6-584a-bbf3-bf2236baab3b | note | Verifying Document - Checklist
991671f7-d07e-5524-8bc2-79447df48ef6 | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
5396610d-e091-5cba-a3e9-1f5f2eaaf942 | note | Verification Activity: Activity - H
bf2b1c36-bdec-559f-9b90-3760eeb60e65 | note | Verification Activity: By - SE
b1c211bb-fa4a-415f-b39a-a37a7ecdda61 | checkpoint | 4.1.12 - Pit Installation Bedding
113e6082-da1d-5950-9461-afafe240093c | note | Detail - Bedding with 150mm compacted GAP20 hard-fill coverd with 20mm compacted sand. Pits shall be carefully lifted into place and lined up with the ducts to penetrate the chamber.
bac1358c-cca1-5bcb-938d-13a385d7d9a7 | note | Acceptance / Conformance Criteria - 150mm compacted GAP20 hard-fill covered with 20mm of compacted sand
8c813f01-dd34-55f8-b228-4343cda46156 | note | Standard / Specification - PS 25.13.8 d)
dfb1b4b8-acf3-5aa2-ac62-77fc2c30ab8d | note | Verifying Document - Checklist
f90f9f99-b223-5d0a-9459-47fe73fdd38e | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
86d13315-daa3-55bf-bc56-93ff252eb623 | note | Verification Activity: Activity - H
ce437c6e-3699-578c-aead-84e075195be8 | note | Verification Activity: By - SE
9328e34b-f52f-4484-87a2-6a567e23ea07 | checkpoint | 4.1.13 - Pit Installation Sidefill concrete
71fe444b-5086-5535-bd11-f2ecf787d102 | note | Detail - Plactic pits shall be cast into the ground with 150mm concrete surround
0fbd21aa-b15a-59fe-83fd-8344040c25df | note | Acceptance / Conformance Criteria - Plactic pits shall be cast into the ground with 150mm concrete surround
fddf33c3-cb07-5b4a-a4a8-86b0bd6e7fad | note | Standard / Specification - PS 25.13.8 d)
8925ae1e-fb4f-5f98-abf0-a2dcc00cb681 | note | Verifying Document - Checklist
45473d2e-c884-5527-8187-303137e55bab | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
033249f4-0882-5e9a-85c8-21f741b8cf84 | note | Verification Activity: Activity - H
5812a820-ca30-5f90-9789-78c4dc3e8079 | note | Verification Activity: By - SE
a55d7731-d3fd-4c6a-b5f7-b547bbffd764 | checkpoint | 4.1.14 - Pit Installation Backfilling
18ae6a93-ebb6-5e62-8128-525c21fc4eda | note | Detail - Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts in 200mm layers of GAP 65.
0284acc2-3ac2-55e3-8db6-85827d558253 | note | Acceptance / Conformance Criteria - Min 92% compaction rate and Average of 95%.
724fe611-be2f-5293-8d93-bc666cb9641d | note | Standard / Specification - PS 25.13.10 a) modified
b5931af2-c9b7-5a39-8da6-275dcb7c0391 | note | Verifying Document - Checklist
553d8bc3-0c77-59dc-8c0f-77e4b35efcc8 | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
8e920a81-75b5-5d8b-b03d-5239835e7a4c | note | Verification Activity: Activity - H
8ac86b86-f72d-5f37-864e-dc95786273f9 | note | Verification Activity: By - SE
d6e55f62-984b-41f7-9d08-d20dc8cdf22d | checkpoint | 4.1.15 - Pit Installation Concrete
094f3ed2-42bd-5f91-a41f-23a08cd64cee | note | Detail - Top 300mm of pit shall be concreted around with a with of 150mm with a 20MpA concrete.
43036d5f-0cf1-5dee-96e4-52f5274a995a | note | Acceptance / Conformance Criteria - 20 mPa
afe4335a-86ff-5e36-b09e-1b3ab6f2bf7f | note | Standard / Specification - PS 25.13.8 d) iv.
abde0cb0-a7b2-5e5c-8e30-e959681c7662 | note | Verifying Document - Concrete Dockets
3b129df5-a387-5321-ba1c-3878ca3df5e0 | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
ea28dd8e-3079-5426-9e3e-39e7f86590a6 | note | Verification Activity: Activity - H
b2c8f36d-0261-55f7-a2cf-1bbb83e96890 | note | Verification Activity: By - SE
cc16ca0c-509a-4e7b-89bc-d5c24eb68cec | checkpoint | 4.1.16 - Pit Installation Clean up
4a489216-ef2a-5be7-b210-4ab573ab050f | note | Detail - Clean out all pit after completion of the work
57a29d11-a28c-52ac-9ac3-3420bf695755 | note | Acceptance / Conformance Criteria - Pit are free of dirty, mud,water and foreign materials
c26938c1-0e9c-567e-8754-b33db44410b9 | note | Standard / Specification - PS 25.13.8 e)
2af6c27f-926d-54b3-908d-b4105bce9058 | note | Verifying Document - Checklist
41edabb5-e1c0-5a7f-9210-60693a8f249a | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
a85f185c-0770-5ea2-ba9a-a7db5cbff8cc | note | Verification Activity: Activity - M
af687a6d-e58f-5fe8-b054-3ab412f79e20 | note | Verification Activity: By - SE
83548c21-f8e6-49a3-8cc8-796c99215b60 | checkpoint | 4.1.17 - Survey As Built
8af9e28f-4e32-5c2f-a06e-7ace49dae2a8 | note | Detail - As Built every ducts joint before backfill
690a404c-67c4-58f0-a1b6-55a448b4d02f | note | Acceptance / Conformance Criteria - Completed as per drawings
a334f3d9-5773-566b-b5e0-440ed3bfae9a | note | Standard / Specification - Standard Practise
1f32b525-b685-5a1d-96ea-e92c6c9bb391 | note | Verifying Document - Survey
ce9f0aea-248f-5d35-8055-cb105eeaba99 | note | Testing Quantity Required (based from schedule qtys) - On going
72ebe140-dc58-54ed-aec8-718c44d0a828 | note | Verification Activity: Activity - H
22ee518e-aa25-5cc9-b92e-3ce057bbec72 | note | Verification Activity: By - PE
77234c98-f060-4443-98c5-98d142a371ee | section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
67e97709-1151-4db1-baaa-751e8db568bd | checkpoint | 5.1.1 - Survey As-Builts
b42277e5-51e8-5c69-a3d1-8933ff1bfc08 | note | Detail - Quality Check on New Works based on the tolerances in RITS
2254ceb7-fe6d-5223-87f5-e6341df1292f | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
1c5d8866-d3db-534d-9028-5682f3e0a634 | note | Standard / Specification - PS-21.7.7
cca34496-ac16-59fc-b49a-81e83b153283 | note | Verifying Document - Red pen markup only
15162872-2dbb-53a3-a627-dc952dc8c223 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
01db14c7-ff05-5aa1-b2b8-09478c901dea | note | Verification Activity: Activity - H
3925c53e-4232-5d9e-b3b9-13ad37525517 | note | Verification Activity: By - SE
9728b770-f763-4039-9633-963f66147ddf | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
95b2f467-5e52-5860-8874-b8f74cf0d5bf | textbox | Contractor's Rep Name:
fe31fa60-f01f-5b03-b890-e515997f3445 | textbox | Engineer's Rep. Name:
e2889202-ab50-5e19-a60f-53090371729c | date | Date:
0d3db660-c2c4-42c8-a0af-35a620286a0b | signoff | Add Signature
b7eebc14-04e9-4f56-9c39-712d57e463f2 | checklist | DN1210-SP2-011-005 ITP Northern access road Watermain sleeve Rev 2 | itp | DN1210-SP2-011-005 ITP Northern access road Watermain sleeve
bf8c1766-5e05-4055-9111-7614835feb92 | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL, PERSONEL & THIRD PARY APPROVALS
cc637c93-fb32-479b-a2b6-4f281377353f | checkpoint | 3.1.1 - Extent of Line Setout
f744146d-f576-542a-80bc-09cb827ea48f | note | Detail / Activity - Ensure line and level of watermain sleeve has been marked out and agreed with Engineer in accordance with water RM drawings.
457d40a3-6033-5cb6-a0fb-9bd2ac11911c | note | ○ Identify any clashes before construction.
c33bcac3-eb3b-5ab2-830b-b347610473c6 | note | ○ LOT- markup
719ea9f6-7d11-58aa-a5b6-385841dc23ad | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
941de75c-6439-5c9a-913f-056307b2d48c | note | Standard / Specification - Design Drawings
365148d8-631b-5314-923f-a99ab4b13341 | note | Verifying Document - ITP Sign Off / Mark-up
0704e4e5-8507-50d2-82f0-5e2bc1b4315f | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
4a607ac6-3f5c-5578-bc6d-bc83c0cfab79 | note | Verification Activity: Activity - H
ad2fb1f8-0fba-5ac6-b65d-cd46b287d9c3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
58c8edc2-ee9d-5a6a-a167-dfc790d5b76a | note | Verification Activity: By - SE
fa6be313-6383-4594-811c-4e23a5d08463 | checkpoint | 3.2.1 - Material grading: Materials (Gap65/AP65)
40ff8022-3b76-5d8f-b492-a9c527d49bd7 | note | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
2529c8db-b528-53c5-87d8-6b2a42248a0f | note | Acceptance / Conformance Criteria - No Particles >200mm
f942094b-ae74-5297-826b-e18cdecabd33 | note | ○ Maximum fines 10% passing 75micron sieve
bcc5b3c9-6dda-59b1-b608-20b299fcf905 | note | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
0f7a9cb3-4846-5097-9a92-e0826b8f4101 | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
6754abad-5dc6-56bf-8d8d-2df912126bf2 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
b8625c5c-2dd8-5af8-b514-a485e4e5b7c7 | note | ○ 0-400 - 2 tests
b1e229e4-9d78-5761-9864-3cb591ff119b | note | ○ 400-1,500 - 3 tests
b7c876a7-4540-52b9-8c21-9ce33a6ee393 | note | ○ 1,500-4,000 - 4 tests
56482d76-b107-511e-91a5-1385c5e38cc0 | note | ○ >4,000 - 1 test for each additional 1,000m3
e91f67cc-dcc1-5554-9722-2dabcd7b6a9b | note | — Results to Engineer 2 wks before importing
436c5173-4e5a-52c7-b55f-809a86603bf5 | note | Verification Activity: Activity - HP
a88c3b18-a13b-53ae-9bce-ede2341e818e | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4e7884b6-935d-5f92-935e-d948126062d1 | note | Verification Activity: By - ENG
3011c7ab-663e-4115-97e0-95d4534163e7 | signoff | AUTHORITY HOLDPOINT
c5c37694-dde7-48a2-a891-15e74ca88277 | checkpoint | 3.2.2 - Weathering index: Materials (Gap65/AP65)
1858ca53-034f-515e-804f-daa74c20ad8e | note | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
b4b4b75b-5101-5017-9faa-d12f5b1d8f1d | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
88f4352c-db3c-5e58-aa08-a8fddf4e095c | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
5b21c3ce-543d-58b6-a8b5-a38ecf067a60 | note | Verifying Document - IANZ Accredited Report
623713c5-71b5-50ae-89ae-e6fcd6565194 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
e3d978ef-904b-5703-a163-622e5477c199 | note | ○ Results to Engineer 2 wks before importing
b9c2ad94-e0cc-529f-87ae-1f3e7cc0466e | note | Verification Activity: Activity - HP
caffc650-d894-5ffa-a06f-1d171e53e415 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
abc28a9e-d868-5fdc-8ef0-eac487c69b20 | note | Verification Activity: By - ENG
121d264f-b031-4b47-a227-8aabd2aca061 | signoff | AUTHORITY HOLDPOINT
28164105-f00c-436f-ac87-1b75827ef859 | checkpoint | 3.2.3 - Crushing Resistance: Materials (Gap65/AP65)
8941ebee-d7ac-51d8-a479-838d5d1d11dd | note | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
f1acf76c-c525-5392-a341-abadd08f3d00 | note | Acceptance / Conformance Criteria - >100KN
5e726a33-beb9-5f4b-836b-6438b9ee6589 | note | Standard / Specification - Appendix XVIII, Appendix V
cfd0a34a-0538-5f77-8511-461b10da9a0f | note | Verifying Document - IANZ Accredited Report
bae3ed2e-0d13-5688-ba04-1d2a29c77f0c | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
7be7f32a-9889-52ba-8678-5d6176b053d5 | note | ○ Results to Engineer 2 wks before importing
2accc84f-61a2-5898-ba97-aa7d7e00a013 | note | Verification Activity: Activity - HP
183c02ee-d9ca-57fc-9607-02ee137a34ed | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0f11ba60-7e39-5545-b9f8-33660928a1a2 | note | Verification Activity: By - ENG
256cef98-b9f1-4366-9fd7-327d6576de28 | signoff | AUTHORITY HOLDPOINT
c545e355-a9c3-4656-b99d-70d5266404c9 | checkpoint | 3.2.4 - Maximum Dry Density and Optimum Water Content
a37a1a10-1fbf-535c-8a90-988fb05b1132 | note | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
436ed1e8-c5d3-5f0a-9542-9ddf908169ba | note | Acceptance / Conformance Criteria - Report Value Only
26d5ce7f-122f-5274-952d-aae41834a757 | note | Standard / Specification - Appendix XVIII, Appendix V
1c4da7f1-6f21-5455-bcc7-43ca662d3bdd | note | Verifying Document - IANZ Accredited Report
35e2f914-4319-596f-aeb9-77b01aeac8e9 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
5f14c276-7bb7-54f5-b775-9d7b108af985 | note | ○ Results to Engineer 2 wks before importing
74e76f46-22f7-5b0d-98d4-c3ae984f4d46 | note | Verification Activity: Activity - HP
160329eb-6975-5184-b60b-db7a0be2e3ea | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1eb8da23-5f22-58aa-b041-a44a01b0d081 | note | Verification Activity: By - ENG
98c8d37a-652a-4767-85cf-0e6cbe9ffab2 | signoff | AUTHORITY HOLDPOINT
f095df5d-1fa8-4dd4-9663-d39d1e6fe47e | checkpoint | 3.3.1 - Material grading:
9cab2234-0db1-5525-84b8-c45f85e75c1b | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
059cf3ce-9361-5526-a5d6-bdb0850dd5cc | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
f57ff874-c409-5d50-bef7-73ba2d94bd79 | note | 19.0mm ¦¦ 85-100% passing
d82ccd7e-0ae1-51d9-bcbf-8042653ceb3a | note | 9.5mm ¦¦ 25-55% passing
ce49e2b8-b81f-57ed-8b90-2a6ee205ab98 | note | 4.75mm ¦¦ 0-10% passing
fa71e144-3e7e-58f0-8e6a-e820547288ce | note | 2.36mm ¦¦ 0-5% passing
0f6f54ee-8aed-5256-bb67-3d5ffe8cdee2 | note | 0.075mm ¦¦ 0-2% passing
d29aadf5-94ea-501c-a1ba-fad26d750772 | note | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
8c1e6bc8-52f7-5700-9326-aaaf104820c8 | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
40e9b545-14c1-5901-9f5e-04e4e23c6cf2 | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
080995f2-e293-5769-b465-8a72f4bf42bd | note | 400-1500m3 ¦¦ 3 Test
6f4c2823-d96b-5988-baa7-dc5498d86e2d | note | 1500-4000m3 ¦¦ 4 Test
dd8d7a19-5a1b-5c6e-aa9d-0e107596a9b2 | note | >4000 ¦¦ 1 Test Additional 1000m3
a551b49f-4300-5652-955a-748068fd0507 | note | Verification Activity: Activity - HP
443a4fd0-eede-5d3d-8c43-432c42ad2780 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
9e172bf1-7748-5d0d-b73f-873b21d76e55 | note | Verification Activity: By - ENG
928b6cde-74da-4d8b-ac90-ff1f92679f26 | signoff | AUTHORITY HOLDPOINT
6b7d5e71-1519-4fd1-b158-a2fb901ba84b | checkpoint | 3.3.4 - Geotextile/Geogrid
b2ef0781-06c5-54ce-b0d9-40af145e640f | note | Detail / Activity - Minimum Strength Class C & Filter Class 1 or TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
429902b1-21b2-548d-af22-5299529d9596 | note | Acceptance / Conformance Criteria - Engineers Site Representative to inspect trench.
59e91ecb-81a5-5a19-9ebc-2a909da88be5 | note | Standard / Specification - PS-16.5.7
56593005-98ac-5083-bb66-2db2b44fed52 | note | Verifying Document - Certification
1a34d86c-8237-5e6f-bf56-79649865f573 | note | Testing Quantity Required (based from schedule qtys) - 1 time
01235e95-ab01-5c8b-b8d1-3d7829421ae7 | note | Verification Activity: Activity - HP
e33f9b7c-65e7-5520-8f04-0a98ec7177ff | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
68f9b4dd-6a83-5f42-8d39-15e0bc50daf9 | note | Verification Activity: By - ENG
07bd9b1f-ee33-4d4a-8b5a-e8a227da5a40 | signoff | AUTHORITY HOLDPOINT
30ce3fa3-ca07-46f1-bc15-9c7fdd4bedbe | checkpoint | 3.4.1 - Pipes (Sleeve)
cec94c38-2874-5279-a0ba-5e431e1b0eed | note | Detail / Activity - Manufacturer's record and location of extrusion plants.
49a10d9b-81ae-5022-8eef-3b7aacfd1fb0 | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
9268d7ba-53c1-53fe-8682-91b8bd645d5e | note | ○ Full Traceability information and certification of analysis for the resin batch.
81f52e54-3269-5384-aa57-2f4d090958dc | note | Acceptance / Conformance Criteria - Engineer Approval
4a35ee32-72de-559c-aedb-54acf92241a7 | note | Standard / Specification - PS-22.4.1 (d)
571b15bd-3d3f-535d-b7a7-569c0e431221 | note | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets
488058f7-d948-5898-838c-69169a98d1f3 | note | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
39df7cbc-d3ab-54fd-8e64-ada2f66dc398 | note | Verification Activity: Activity - HP
1150cd50-6218-5af3-b9dd-6a985c5192d2 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f825bdf7-0b41-5b43-b5c0-f23e068cb22b | note | Verification Activity: By - ENG
3dc95f6a-e60d-46b5-9aa4-0586948e9588 | signoff | AUTHORITY HOLDPOINT
6c016203-23c8-4a8b-b829-a8390e40531e | checkpoint | 3.4.2 - Electrofusion (EF) coupler
deaeb05b-71b6-5b80-95e1-edad2130b5a5 | note | Detail / Activity - Confirm the diameter and size and the EF coupler
07966355-8216-5ec3-bca5-db14b2a6ecf3 | note | Acceptance / Conformance Criteria - Engineer Approval
ad254086-356d-5b4d-ad1d-461ec385b34a | note | Standard / Specification - PS- 22.9.5
9b201f16-796e-5322-8147-10773a0e2649 | note | Verifying Document - Manufucture records
e517815b-18d4-5e53-a21a-3e9c16137bc8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
bba58b6c-0f81-519f-8341-70a0420c5043 | note | Verification Activity: Activity - HP
ed27e1ac-2d6a-538b-bfd0-b9030ff3dffd | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6c9dae92-10bc-5ab8-a3c9-585b20a52186 | note | Verification Activity: By - ENG
97a65fde-d7bd-47c8-bd03-7af035871030 | signoff | AUTHORITY HOLDPOINT
f8c6aebf-44bb-4b7e-b399-632d99365a60 | checkpoint | 3.5.1 - Pipe and fittings DN560 PE100 SDR 11
e4e1d2cd-d3a8-5583-9ca7-ed6863b22a0f | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
1f53bb9b-fe10-52d6-8f2f-d8f83b3dc5b7 | note | Acceptance / Conformance Criteria - As Per Drawings
db8fb25d-930f-5af1-927f-fb90afd54366 | note | Standard / Specification - Design Drawings
dcfe60be-82fb-5354-aef4-ada3cb638766 | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
b7c609aa-88fa-5194-8e2a-7785b8a3dc69 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
767f2866-3da4-5a26-854b-ea2bd6017d25 | note | Verification Activity: Activity - H
b322fd8c-79d5-50ca-aa7c-d2b50163c61b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e32ccc74-dc13-51d9-9879-61dccd947dfb | note | Verification Activity: By - SE
9696216c-8184-4f90-b5ed-2f15a20b2303 | checkpoint | 3.5.2 - Material delivery
bb356086-33d2-5c77-89eb-fe144c56e42f | note | Detail / Activity - Embedment and beckfill
a6c06628-7f03-508c-a7a2-8d9418870971 | note | Acceptance / Conformance Criteria - Embedment and beckfill
db583e34-6ef3-5150-a934-eac8b20ac126 | note | Standard / Specification - Design Drawings
e4e2a2b0-5cd6-581b-ba7d-0b511c0bdcab | note | Verifying Document - Delivey dockets
6b1a1243-e105-524c-838a-8e85ebf62aa0 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
36aced72-f08b-5cd0-bd5c-aa62cd43f886 | note | Verification Activity: Activity - H
99335fac-b294-5d5b-8abe-c9a72d7d8b84 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
987c2e86-d06e-58bc-a214-8824ad2097df | note | Verification Activity: By - SE
858a5d63-0903-4902-abb8-014379b7f624 | section | SECTION 4 – CONSTRUCTION ACTIVITY
3dce1efd-d765-4e82-bdd0-5346244a71ac | checkpoint | 4.1.1 - Foundation Compliance
20915fff-83b3-5c93-96e5-e7119e173794 | note | Detail / Activity - On Granular or Cohesive Material
36072193-a24e-50f0-818f-b5b12afe89b8 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
2a82d50e-2dd1-50e9-a387-ca166823b5a4 | note | (Or)
7a2674c8-15d4-5983-b4fd-12afa5f24ae2 | note | ○ Cohesive Material: Vane Shear Strength 70kPa
2edbfa31-388e-5fcc-a71e-63e13d83d66f | note | Standard / Specification - PS 21.6.5 and AS/NZS 2566.2
f44597f4-6cfc-50fe-927b-c29bcd91c895 | note | Verifying Document - Scala/Shear test result
141e5253-42bc-5d1e-b502-1d470c666ec6 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
544c60f7-c639-52be-baf9-0528a8442753 | note | Verification Activity: Activity - W
0df33b33-9d0f-5d20-b144-8234bedce813 | note | ○ Review of text reports/records or other evidence of compliance
c68405ba-a2a9-5291-98e6-4079ac040e4a | note | Verification Activity: By - SE
5e79402a-ae1e-4424-bc11-c85513b66221 | checkpoint | 4.1.2 - Undercut approval
eb7796d0-c054-5889-858d-ec18216d12fd | note | Detail / Activity - Trench Foundation
d5414fd4-d612-5144-8085-891c6a5163d5 | note | Acceptance / Conformance Criteria - 300mm Max cut
60242597-d490-50f0-8cd4-0cc72be1efc5 | note | ○ IFC Drawing Sheet 320
3a168bb3-2c6f-5057-b76a-679be1b7808d | note | (Or)
27000a65-32c7-5028-8d0f-90a779d27db8 | note | ○ Engineers approval
0df338b4-03b8-59e2-a221-043281bc44b8 | note | Standard / Specification - IFC Drawing WAT 0320. AS/NZS 2566.2/2002
670ceadd-a2e5-574c-90cf-da4e613845aa | note | Verifying Document - Lab Test Report / Watermainline record
078302c3-70de-544f-a798-4156a65b0dae | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
d654a5a4-902b-510f-ac33-e42c1f0ae8af | note | Verification Activity: Activity - H
6544746d-0c58-5607-b869-3a39be7f76b5 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3fb8dad4-3324-5b13-b9bd-ebafb2f1772c | note | Verification Activity: By - SE
e33fb1e8-0145-4ffa-89df-1c07f49fa754 | checkpoint | 4.1.3 - Undercut Backfill Compliance
0d6a7870-6d3d-5c12-9761-6aa12ae33cc1 | note | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
e6ba920c-332b-5f66-a51d-8f58c218027a | note | Acceptance / Conformance Criteria - Visiual Inspection
8b835c34-2274-5fb2-ba98-18b303decc09 | note | Standard / Specification - IFC Drawing WAT 0320
51d6f2d0-e766-5b6a-a58e-ba9b3fde6a16 | note | Verifying Document - Lab Test Report / Watermainline record
ff69de17-674d-54ce-8e44-5f104894e744 | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
9cc377bc-2d22-59b7-ae7c-27603ed0a7a2 | note | Verification Activity: Activity - H
6143ef96-cb95-5028-985e-a517000179fa | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3f734a93-f448-5f60-877e-81707406203c | note | Verification Activity: By - SE
72e56a1a-f8d3-4c1d-a463-4678bacdf722 | checkpoint | 4.1.4 - Bedding Zone Compaction Testing (PE Pipe)
9282adfd-cfbc-5200-9fca-65602e3a4d52 | note | Detail / Activity - On Granular Material / On each layer as per specification (19mm chip) NDM testing as per NZS4407:2015, Test 4.3
9ada5893-481c-5869-acca-8cd783cb6def | note | Acceptance / Conformance Criteria - Bedding Zone: 150mm minimum thickness (compacted) over the bottom of the trench.
c2989831-b6bd-5434-869b-49110275b35c | note | ○ Minimum Compaction- 85% MDD
ea2ae7c4-c7ae-5767-be91-d792988d6e47 | note | Standard / Specification - IFC Drawing 0320-1, AS/NZS 2566.2/2002
d2290c92-24e1-54ab-a466-85c8aea23632 | note | Verifying Document - NDM:Lab Test Report
49724380-5e00-51f1-ab80-0d3e58abc014 | note | Testing Quantity Required (based from schedule qtys) - As per Water Specification. One test per 20m evenly spaced intervals.
9eb5bf8f-c601-57c9-b065-ec20946f5fed | note | Verification Activity: Activity - H
7e1391a6-0d24-5d23-8306-a923fffeffe1 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a1782413-d0d2-5ddc-bb44-4a2950ac8754 | note | Verification Activity: By - SE
70c28329-fa9c-44cf-b2fe-fb62f7a012eb | checkpoint | 4.1.5 - Laying of Pipes
6ea81c65-9e95-5aff-a976-807d1c062248 | note | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
3d1a958c-e762-539a-a705-f986ed83abb9 | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
869e2ed0-220b-5000-a2e8-eb107b2ad9cb | note | Acceptance / Conformance Criteria - As Per Drawings. Facing upwards
bce55180-e089-5245-93d6-e83fc27eed95 | note | Standard / Specification - PS22.7.1 C
588fd4c7-2ef6-50da-8eb7-59b88a58a8a6 | note | Verifying Document - Visual Inspection / Watermain line record
2712e528-2ac6-5d9d-8953-75e697119da8 | note | Testing Quantity Required (based from schedule qtys) - Every Line
45046439-3cbb-586a-8446-0ea3a94497b1 | note | Verification Activity: Activity - H
8443f933-849d-5241-845f-0bffc3a4db3c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7e71bde8-499d-5467-b8e8-96a0a1a91591 | note | Verification Activity: By - SE
565a5c27-0416-42f7-ae13-49fc61e28085 | checkpoint | 4.2.2 - Electrofusion (EF) Welding
029923ed-91a4-5004-b767-cd0f46d675fe | note | Detail / Activity - Required if Butt fusion welding cannot be perform.
27c10ea1-c67d-5928-8156-fb46c267ba74 | note | ○ EF Jointing in accordance with PIPA POP 001.
192d6265-3bca-52ca-a078-352494afd1e5 | note | ○ The lead welder or welding supervisor must verify on the site record form.
fb5764c4-6662-5ec1-9ec5-916c3c31e548 | note | Acceptance / Conformance Criteria - WMS Report Checklist (refer to CWP).
72eda0b7-5ef7-547e-b947-0c81f7b61d71 | note | Standard / Specification - PS 22.9.5, Appendix 22
df773c06-e049-5832-a106-895883236c5a | note | Verifying Document - Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report
1292a51c-5c43-513a-82aa-2504e3bfd5fb | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
3e88319e-7883-52bb-ac6e-089769466dac | note | Verification Activity: Activity - H
3ada9534-9f69-5db7-81d5-ae2bf9c9677d | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
eb9965cc-add3-54a9-887c-f7f836a89a6c | note | Verification Activity: By - SE
677ac436-e2e7-4739-8ddb-e3fca3f6b3ec | checkpoint | 4.2.3 - Electrofusion (EF) construction weld test
777b467e-0628-5f27-9f8d-aedbd886e404 | note | Detail / Activity - EF weld quality to be maintained.
ba45155e-0315-58e8-acbb-9612089ec2c7 | note | Acceptance / Conformance Criteria - EF coupler and EF saddle testing
ecbf7e7f-5dc8-5dc6-918a-239a51a75015 | note | Standard / Specification - PS- 22.9.6 (b) (iv)
8e5be0f2-e478-5e41-970b-5089b5877b22 | note | Verifying Document - Test report
16d9ea3d-8790-5fd1-a1ec-8ae89f4f715e | note | Testing Quantity Required (based from schedule qtys) - 1 in 10 test
cb8739a5-f3fd-5c4a-9b00-fac2faf07031 | note | Verification Activity: Activity - HP
2d91e493-a0be-5b83-b03f-576cdbfd5f91 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3326f379-8bcd-5e69-b9d3-8f85a9d8ff03 | note | Verification Activity: By - ENG
02354e7a-a2cc-4261-961f-ea3faed47ef3 | signoff | AUTHORITY HOLDPOINT
dc228e24-660a-4a7a-90ef-d4051bb156de | checkpoint | 4.2.4 - Survey
6c466f10-39ce-53d5-9d27-eb8e0ec4a709 | note | Detail / Activity - Inspection of Pipeline Inverts
9bdae5e9-9c0e-5b09-b7ab-4af8266dd2b6 | note | Acceptance / Conformance Criteria - Vertical design Setout:
2af490eb-e0d6-58fc-8a97-ef2ef15d4c87 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
fd46e707-1c72-5a63-8931-9883eb7d7bb8 | note | ○ Pipes > 1% grade: +/- 20mm variance
64d2edb5-84a2-538b-b923-0cd5dc9be45e | note | Horizontal design Setout:
7c138480-ffc7-518a-859a-e4612b57ad9d | note | ○ +/-30mm variance
09e51b65-064b-5e1e-8e4b-3c66b4e702d7 | note | Standard / Specification - PS- 21.7.6 Table 21.15
5afaef95-8def-50ef-9267-866f2ca30ee1 | note | Verifying Document - Survey Data / As-built record
02e4f857-27f3-5dea-88ea-0847d34be7b2 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
7119d199-9172-5b15-b59e-5525d1c129fc | note | Verification Activity: Activity - H
fb4071b4-45ce-51c8-a4f7-83daaaccbd9a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0651dd3b-63ac-527b-b633-c94effe6ff26 | note | Verification Activity: By - SE
57ee7abc-100e-4868-a095-9e9d4bde8fec | checkpoint | 4.3.1 - Emebment Zone - (Side Haunch Overlay)
6bc41ce6-2578-538a-8fd3-522eea6aa108 | note | Detail / Activity - 19mm chip backfill Compacted in 200mm Layers.
31aeeb78-b408-5b19-bc17-9973513567f8 | note | ○ NDM/Clegg Testing to be completed on maximum 200mm lifts of overlays .
f0df3d26-6dbd-52c5-a9a5-9126ed7cfe87 | note | ○ NDM BS to be Carried Out
f80571e4-d466-505c-8d74-6c44722e3a5a | note | Acceptance / Conformance Criteria - in 200mm layers.
c890c387-4332-5a66-89f0-532429b41d66 | note | ○ More than 85% of MDD.
3614f9e4-69ba-5e56-8f0b-afebbb3d73ac | note | Standard / Specification - NZS 4407:2015 Test 4.3 Nuclear Moisture Density Gauge; BS
ce9d232c-4274-5a48-90f9-102e21ae23cd | note | Verifying Document - Lab Report / Watermainline record
b691983c-5444-5790-9e20-11d312fa2282 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals. 200mm lift
2f0784e6-705e-5877-b551-ab86ad304bee | note | Verification Activity: Activity - H
986cc824-5217-5a1a-8bc9-21d6620c3ff8 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ba944d4d-20d7-5ae6-b99b-fbd2a3ea917e | note | Verification Activity: By - SE
3e94e2c0-533e-428a-aaa1-efa8e0836108 | checkpoint | 4.3.2 - Pipe Markers
036287ab-4b67-5456-911f-8b0e692d60e2 | note | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
d0097ba5-7d3b-5db1-9dfe-f587fdbb6b75 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
308dcfd5-3151-5d2d-9fc3-0a51b2e62754 | note | Acceptance / Conformance Criteria - AS Per Drawings.
fefdbf13-f501-5fc8-8cf0-6afd287453ec | note | Standard / Specification - PS 22.7.3 a
dbef0ed8-6479-51cb-9582-ac8f0f4dcf24 | note | Verifying Document - Visual Inspection / Watermainline record
6be69c44-2719-5ce9-aacb-3a4ac1a3726d | note | Testing Quantity Required (based from schedule qtys) - Every Line
795c5bba-b958-50f7-928b-1166328ccfb8 | note | Verification Activity: Activity - H
78d183b3-ed21-52e5-8127-7f44147748d1 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7323ce2a-a394-57e3-951d-cf3850e27cc8 | note | Verification Activity: By - SE
96a6befe-656f-41f1-beee-293802f7ad1d | checkpoint | 4.3.3 - Backfill Compaction Testing
90b7d1cd-18f5-50e7-8d71-89773369de72 | note | Detail / Activity - GAP65/AP65/LRAP65 Backfill Compacted in 200mm Layers.
e05d4c26-a4e4-5f7e-af0c-409063cb947d | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
8b30f31a-6e13-5276-9d1b-a2e07f864894 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers.
b6207069-fcba-5e58-ab4b-149687080166 | note | ○ Testing to be completed on maximum 200mm lifts of backfill.
e624b8a2-ace7-5cfa-b059-58ede67a4593 | note | ○ LRAP65- achive 90% NDM on Grassed Area and 95% NDM on Shared and Carriageway.
631abfea-ab1b-5c7a-ba04-7f7a87d7c4ab | note | OR
d2456e51-12ab-5d5a-a328-380cb16a470a | note | ○ Clegg 28CIV
2f8cfb00-6be4-5b67-80a2-22242c1e49de | note | Standard / Specification - PS- 22.13.5, NDM Standerd 25832, NZS 4402 Test 4.1.3
7c410a9a-4e3e-58d4-88cd-b5eb6bd5a5d6 | note | Verifying Document - Lab Report / Watermainline record
810283e7-3bd7-5a0d-afd9-c9c042a0589b | note | Testing Quantity Required (based from schedule qtys) - As per 200mm lift, One test per 20m evenly spaced intervals.
9ed33b2a-206b-58cd-bbe2-9c5dde5484de | note | Verification Activity: Activity - H
c97d226c-2393-5b85-9ce1-5884682ff4db | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
fa05c6b4-7223-5c7e-a225-ac679ca24365 | note | Verification Activity: By - SE
8ef8957d-19c0-4b41-8b44-8bf82a5bf248 | checkpoint | 4.4.1 - Watermain sleeve inspection - Pipe Inspection
fb36d09c-7a63-5459-9e40-f4ff02783a09 | note | Detail / Activity - Inspection of Watermain sleeve
d9a27fb5-a66a-58fb-83e5-98cf26a895d8 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
78716884-2bcb-583a-9409-80d2419ba583 | note | Standard / Specification - Internal
a4e2811d-92e7-59d6-a9d3-cf9834baac58 | note | Verifying Document - Watermain line record
b782f6f4-8035-5a7c-93d5-3d694ea45322 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
184eae8e-9374-561d-86d7-ab55c345a485 | note | Verification Activity: Activity - I
7aa08693-00e4-5ab3-b4f9-8b2637e1cad4 | note | ○ Formal inspection activity to be undertaken and recorded.
8ff6c09f-0e97-5607-8918-308cecc94200 | note | Verification Activity: By - SE
a37e4d8b-32ea-41be-921d-557c691b3675 | section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - ACCEPTANCE BEFORE COMMENCING DISINFECTION WORK
541680de-3a30-4414-b79a-37d4914bd0f6 | checkpoint | 5.1 - Survey As-Builts
1fc1fd1a-3e3c-5c28-a8e1-3d16257d86d4 | note | Detail / Activity - Quality Check on sleeve based on the tolerances in RITS
75eabc16-1d90-552e-ab16-1870a6aa46cb | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
4e03868d-0fc0-54cb-9e9b-c8ad7526369b | note | Standard / Specification - Project Specifications
86cf81d3-ff11-5d53-9517-5e3c8e3235c5 | note | Verifying Document - CAD File as per PS12.3 and Red pen markup only
30b6ae78-bb1c-5ba6-b557-da3632260704 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
2c581a52-ba92-5d91-9d3e-b7e2e8b4e36b | note | Verification Activity: Activity - H
b7c715d9-3631-51c9-87a6-85fc10f59a98 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3fb12612-1918-57f7-81a9-1f09b3268479 | note | Verification Activity: By - SE
bd989b1c-9b98-4372-bda7-02aed6a2a3da | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
b112e2a8-f09b-5b39-b405-9269457475cb | textbox | Contractor's Rep Name:
ba6dfd6a-f028-5d77-8522-d29a83c92e64 | textbox | Engineer's Rep. Name:
fe31e9b2-46c6-5c6a-9e1e-f4d5298eecb2 | date | Date:
591c9a0f-55d3-4a22-ae27-9cd0bcfbff34 | signoff | Add Signature
c9c674d1-d1ef-4b49-8dda-5988f8739a36 | checklist | DN1210-SP2-011-006 ITP NAR & Carpark Streetlight Rev 1 | itp | DN1210-SP2-011-006 ITP NAR & Carpark Streetlight
b2e655d0-d56a-4e3c-abb9-1fba5c875acd | section | SECTION 3 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
ab297505-5950-412c-9d33-06444ad0103f | checkpoint | 3.1 - Location of Lighting Poles and Cameras
0bac97fb-1fba-55d7-ab29-c5d5a951e8ae | note | Acceptance / Conformance Criteria - Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation.
0a2e8c25-7110-51b3-a009-5995bb66f23f | note | Standard / Specification - IFC Drawings
01ad42bd-bc23-5a3d-9390-df88739de4cc | note | Verifying Document - Survey data/Comms with Client
da3af408-6ced-5aa1-82ee-6027400c0f61 | note | Frequency - Prior to Installation
0a1c9e7e-9b1b-5885-b594-5fe145a27de9 | note | Verification Activity: Activity - H
afeadc99-bc8d-5985-83a0-b2d8ce20b59f | note | Verification Activity: By - PE
224847fb-35b2-413a-b4e9-901a61a14daa | checkpoint | 3.2 - Material grading: Materials (GAP20/AP20)
a0bec223-4c6d-50a1-bf1e-98554ad39862 | note | Acceptance / Conformance Criteria - Material grading:PSD
18c67c72-a4c5-5db4-ae98-3e6d74ebae6b | note | Standard / Specification - Sieve Size ¦¦ % Passing
39374b8b-8554-52d0-abcb-afe2a6f47d4a | note | 19.0mm ¦¦ 100% passing
efba4a16-c1a1-5777-8f05-72f0da7495bb | note | 13.2mm ¦¦ 80-95% passing
47c90edd-ee9e-5c32-996d-97a4f5e729a9 | note | 9.5mm ¦¦ 64-76% passing
84685802-bbb7-5611-8ef2-ba9a0e524875 | note | 4.75mm ¦¦ 37-58% passing
2a45c071-1d3c-5fca-9205-44df24db1d50 | note | 2.36mm ¦¦ 30-40% passing
310973ba-127b-5895-8c91-7a60e7cab398 | note | 1.18mm ¦¦ 18-28% passing
3d6b3f7e-5635-5784-9b3c-6e11eb99fb57 | note | 0.600mm ¦¦ 12-22% passing
bb1f17bd-438c-50f4-b26e-88cafa907ce2 | note | 0.300mm ¦¦ 6-14% passing
6a0b3ec3-d13a-5929-81ff-b4b4e3793db7 | note | 0.150mm ¦¦ 2-7% passing
edca1378-d2f5-531c-8828-f081db9dd0f6 | note | 0.075mm ¦¦ 0-3% passing
5ee73e22-c1f5-5a69-90a1-da5fa73fa6a2 | note | Verifying Document - PS-21.5.7, PS-21.7.2 Table 21.2
bc86ce02-aa71-57c7-ab06-e6bdc3e1992e | note | Frequency - Lab Test Report NZS 4407.2015 Test3.8.1
0d81d8eb-f3a6-5243-8ba2-9c36a2e1cd78 | note | Verification Activity: Activity - HP
8cc224b4-2d52-5d0b-a5ad-2c4eb4fa0917 | note | Verification Activity: By - ENG
c553d957-9d83-4626-9ddf-b9e32a78eb79 | signoff | AUTHORITY HOLDPOINT
e79bf130-0004-4b6a-a434-3b7a701cbd52 | checkpoint | 3.3 - Weathering index: Materials (AP20)
015077bd-176b-52af-9f29-537a30b44af4 | note | Acceptance / Conformance Criteria - Weathering index:
c07a5a4a-e008-5dba-a369-c25625800f07 | note | Standard / Specification - AA to CA
e7b53ba8-d0fe-5f71-ad66-ea1deb741dc3 | note | Verifying Document - PS-21.5.7, PS-21.7.2 Table 21.3
eeeda0e0-7bc0-54b2-91d6-760f7aff93be | note | Frequency - Lab Test Report NZS 4407.3.11
e730e324-5d99-5332-bf03-b441b477de6d | note | Verification Activity: Activity - HP
2829dc55-c43b-5948-80e8-63a4b91c353d | note | Verification Activity: By - ENG
4b0c9983-bc40-46bf-8969-5e9bfcb316bc | signoff | AUTHORITY HOLDPOINT
fef05ed2-4ac1-43d9-abdf-89a55cf729eb | checkpoint | 3.4 - Crushing Resistance: Materials (AP20)
2d27d3d6-f209-5db6-a5a5-3c0bc2d81365 | note | Acceptance / Conformance Criteria - Crushing Resistance
c051e154-39d6-5ba9-81a7-89b40c28e9d7 | note | Standard / Specification - >100kN
4962a28a-9ed0-57c7-a379-5cd22c3f74a7 | note | Verifying Document - PS-21.5.7, PS-21.7.2 Table 21.4
ea2bdfc1-ac70-5670-90ab-9dcd7a547cf9 | note | Frequency - Lab Test Report NZS 4407:1991 Test.3.10
dbf2d523-3f81-51c5-9f3a-d323074f62e6 | note | Verification Activity: Activity - HP
0505e4b6-b1de-576e-a585-5d5b9633e789 | note | Verification Activity: By - ENG
669ba2e8-0833-4924-9134-38ae1ebda244 | signoff | AUTHORITY HOLDPOINT
714278f8-9075-4d75-9193-c0809bbec890 | checkpoint | 3.5 - Luminaires & Poles - WK & TCC NAR & Carpark
63268919-7b68-568c-ac1a-a7803fabf875 | note | Acceptance / Conformance Criteria - Luminaire and Pole types shall be supplied and installed as detailed on the drawings or as per instruction of Client
c280c22d-1163-52d0-96b1-e410185efcd3 | note | ○ Luminaire Controller - PDL- 56SS10.
26e84ab3-cc95-5155-b913-0e27310841ca | note | Standard / Specification - PS 23.1.5 g) & Drawing 0411, 0412
7c25218e-6461-5cd2-938c-72647ab8dc72 | note | Verifying Document - Material data sheet and engineers approval
30cc4b14-3ad3-54fb-bfe3-b2dec4ba6aa0 | note | Frequency - Before each Installation
27428da5-525e-5b21-92e1-12fbab9dd3db | note | Verification Activity: Activity - HP
17c26afa-604e-5127-a8c3-2919d546c84d | note | Verification Activity: By - ENG
d6c2d315-a5fd-4a44-a9fe-415925fec27c | signoff | AUTHORITY HOLDPOINT
cbaa0e8f-381c-4b5c-b244-7ca155c1006e | checkpoint | 3.6 - CCTV Cameras and DIN rail-mounted switch board
175fdc84-85ce-5a2c-aa30-5338540fd285 | note | Acceptance / Conformance Criteria - TCC Approved IP67 IK10+
faaec53e-d41a-5903-8cd5-67bf0ca4c791 | note | ○ With Weatherproof Housing , Vandal Resistant and PoE Dome (HD1080p, 2MP), Sensitivity down to 0.01 lux
3dec0d21-5965-51ca-b95f-924694e2e020 | note | ○ Have intelligent auto exposure to offer front and back light compensation.
6f8efef4-16ff-53a5-ad10-447b123601b2 | note | ○ TCC IT-approved DIN rail-mounted switch board min 8 ports and 2 SFP ports
85cb8362-3a4e-50d6-aa11-932a1d8f92a0 | note | Standard / Specification - PS23.1.5 n)
0e727453-34b0-545f-bce1-9a2277c55f31 | note | Verifying Document - Material data sheet and engineers approval
19f8ce8b-c904-5ed1-a3b0-8d0235f93884 | note | Frequency - Before each Installation
687432b3-9ab1-5d98-9b1b-2ad72aeb8d35 | note | Verification Activity: Activity - HP
713eda3c-ce61-5fff-a1fe-9dd93cdca3b2 | note | Verification Activity: By - ENG
fb0b70c6-a50c-4319-9a6e-7215f307ec61 | signoff | AUTHORITY HOLDPOINT
3eda8f51-2516-424e-af6c-8d68e4d558ea | section | SECTION 4 – CONSTRUCTION
99ef840b-48d8-4fed-b6d3-733d8b19adab | checkpoint | 4.1 - Lighting Equipment-Luminaires & Poles (WK & TCC)
12d2df6e-0998-5891-a575-61a224f2a155 | note | Acceptance / Conformance Criteria - Types of luminaires and poles shall be installed as per details on the drawings or as per instruction of Client
6fb2d8fe-6ce1-5834-883a-1cf403b244b0 | note | ○ Luminaire Controller - PDL- 56SS10.
47ef3b24-21ca-5ad1-a86c-06639a57cb01 | note | ○ Luminaires shall be fitted with Shorting Caps.
5486749e-238b-5a67-a1f3-7d7f5171ea67 | note | Standard / Specification - PS 23.1.3 c-d); 23.1.5 f-g) & Drawing 23273502-WSP-DR-LIG- 0004; 0112; 0410
ff5d569f-b6ca-563d-9654-de1f98d4cd4f | note | Verifying Document - Photo/Visual Inspection
497624ac-2686-5fb6-bebe-4bbeb010c480 | note | Frequency - Each Installation
f8ff094d-ecc5-57f9-89a2-9807a0fa4945 | note | Verification Activity: Activity - I
d1178f23-9834-53f3-8be5-2645e5776e7e | note | Verification Activity: By - PE/SE
f481bb43-fbdb-4963-9203-e0e948c3a04a | checkpoint | 4.2 - Lighting equipment- Circuit Cabling (WK & TCC)
c27d9ec5-4daf-5930-8318-a2e019492b17 | note | Acceptance / Conformance Criteria - Supply and Install final circuit cabling to Luminaires from via underground ducts and conduits as per Drawing
b1f0fec1-1985-5225-8bd6-5d628f88d015 | note | Standard / Specification - PS23.1.3 g); 23.1.5 e) & Drawing 23273502-WSP-DR-LIG- 0112
8b8802d6-9667-5b6f-8902-60bf516aa0b4 | note | Verifying Document - Photo/Visual Inspection
7ecc0f17-2b7b-50f6-8959-f8cbc18aadf7 | note | Frequency - Each installation
2221044c-f61a-5c22-aca9-d13cde592f9d | note | Verification Activity: Activity - I
a424cd76-3075-5b4c-ae8b-3e4f8f6df527 | note | Verification Activity: By - PE/SE
318449e4-ad6e-4418-80c5-dcb539ff30d6 | checkpoint | 4.3 - CCTV- Camera and Cabinet Location
f2f95a79-3e61-5a06-b228-70f19a2dcf2c | note | Acceptance / Conformance Criteria - All CCTV cameras will be installed at a high level, either on lighting columns or other designated high-level mounting points, providing optimal coverage
429a2308-6b44-5e70-ba30-d98583f1518a | note | ○ The CCTV lockable cabinet will be securely mounted at a high level on lighting column TC94, ensuring a stable and protected enclosure for network and power components.
2b434841-ad89-5704-82ff-9f56fc2ff689 | note | Standard / Specification - 23273502-WSP-DR-LIG- 0410
d0bc30db-5858-59b6-ab28-4bb5a8729e7c | note | Verifying Document - Photo/Visual Inspection
e5cde7a3-2475-52d1-919e-e9828fdd8dbc | note | Frequency - Prior to installation
b9922a3a-e4cc-53e8-b421-4d5740815102 | note | Verification Activity: Activity - H
473a51cb-02e1-565b-b4ba-99b64d7d246f | note | Verification Activity: By - PE
9b737b77-f62e-4f5e-ae48-271d81f148fc | checkpoint | 4.4 - CCTV- Circuit Cabling
b7eba36f-ef39-5353-b1b4-ff35e161c90a | note | Acceptance / Conformance Criteria - All CCTV cameras will be installed at a high level, either on lighting columns or other designated high-level mounting points, providing optimal coverage
0a87ac94-28d5-5c35-a855-6a4caeb72d85 | note | Standard / Specification - 23273502-WSP-DR-LIG- 0414
261e0cd8-0ef4-5112-8a4c-33f0f8bf2522 | note | Verifying Document - Photo/Visual Inspection
fce5b699-67bb-5eac-b850-544d9c4f8b2d | note | Frequency - Each installation
6b3c4007-7b3c-5fdf-87c8-72574bac6690 | note | Verification Activity: Activity - I
f883b74b-8a85-5d83-bd3a-97022a27b08f | note | Verification Activity: By - PE/SE
4b17fe7e-258c-4478-a08e-2a8f7b2f91e4 | checkpoint | 4.5 - CCTV- IP Addressing, Programming of PoE Network Switches
90713142-ca59-5e8d-bf20-754609a689eb | note | Acceptance / Conformance Criteria - Liaison with TCC for IP addressing and Programming of PoE Network switches.
eb161eb3-5860-51d4-8798-91261bb16633 | note | Standard / Specification - PS 23.1.4 m)
bff1f8d0-80c8-5f3f-81f7-af06a04c72bc | note | Verifying Document - Comms Record
768b8437-1507-5d97-9d44-7dff72e1a9fa | note | Frequency - Prior Installation
471eaf48-515a-5cad-afcc-76d65dc4e08c | note | Verification Activity: Activity - H
1a504e33-7008-57a4-863c-c86251b6951f | note | Verification Activity: By - PE
a73cd30f-681f-44e3-850b-847662c3cb6b | section | SECTION 5 – Commissioning and Testing
a24016c1-bd94-45cd-bf9e-9038d793ebe9 | checkpoint | 5.1 - Luminaires (TCC)
5243eacf-baf4-5e40-9426-4e213995fa2a | note | Acceptance / Conformance Criteria - Carry out full commissioning of the Light Controls as detailed on the drawings.
d8be7a0c-f636-5fcf-8e68-9e38889b9e58 | note | ○ Also record "Benchmark" energy meter reading from the lighting switchboards of all levels to demonstrate power consumption when ALL luminaires are running at 100%.
331fe4b5-f873-589c-820f-99be3d73f585 | note | Standard / Specification - PS 23.1.5 g) & h)
96f50694-6ff1-5a7f-a549-2cf0b27230a1 | note | Verifying Document - Photo/Visual Inspection and Commissioning Records
98ccbcf9-cb28-5814-bb5e-af51837d118a | note | Frequency - Each Commissioning
5b55c312-e4ad-5fa8-8ab5-3de78bfcb870 | note | Verification Activity: Activity - W
6911629b-ae13-5201-8cac-bfd14737f578 | note | Verification Activity: By - ENG
af5e7f52-2f6d-488d-96d7-672138410ffc | checkpoint | 5.2 - CCTV- Cameras
0ab8766e-7ca1-5012-809e-51a5052f2a8c | note | Acceptance / Conformance Criteria - Testing CAT6A U/UTP Cabling from CCTV Cabinet to each CCTV Camera.
f0ebaadd-308d-5a71-858b-58d1d2b1d551 | note | ○ Liaison with TCC for Commissioning and Testing including camera adjustment to achieve the desired FOV.
5f76ad36-d9d3-5a5e-93d1-5390bee019b9 | note | Standard / Specification - PS 23.1.4 m)
aa5705b5-a624-567d-81ea-20a3e13d761b | note | Verifying Document - Testing/Commissioning Record
b6f573ab-c03f-5032-9c01-950d75316770 | note | Frequency - Each Testing/Commissioning
55745f10-70ce-5218-a5ac-376d605cc902 | note | Verification Activity: Activity - H
5879bb87-307c-5d49-9276-3ba939d38a18 | note | Verification Activity: By - PE
3174d0e6-432f-455f-9bc3-14ef8327021a | section | SECTION 6 – POST CONSTRUCTION ACTIVITY
0e79f238-8da3-40be-b9e5-c9d9c525eeca | checkpoint | 6.1 - Electrical Certificate of Compliance (CoC) & Record of inspection (ROI) Electrical Safety Certificate (ESC)
9b7ae942-923c-57f3-b42d-275bc0380d05 | note | Acceptance / Conformance Criteria - Obtain final certification of the installed systems by an independent electrical inspector approved by the Electricity Workers Registration Board.
879e0b2c-6834-5c19-bcf3-d5918467cc0a | note | Standard / Specification - PS 23.1.5 p)
ad1bbcbe-ad1d-5370-9886-0e4fb98e2daa | note | Verifying Document - CoC,ROI and ESC
97bc8f3d-f260-529d-8ed6-28ef1fa968db | note | Frequency - Post commissioning
a181d0e5-02c2-5ccd-95d5-7617216a6da8 | note | Verification Activity: Activity - R
e37edc9d-2758-5197-8d15-58474ebf4af3 | note | Verification Activity: By - PE
0822c39e-afb7-4bd2-a63f-a21cca3c1cd7 | checkpoint | 6.2 - As-Built
46020dd2-5176-538f-9fab-00f72bbbbde3 | note | Acceptance / Conformance Criteria - As-built drawings with
97b92551-f22e-501c-9e57-4fade6c587db | note | 1) ducting routes.
e8a9acd7-50a7-5c88-898d-0004db943edc | note | 2)) control groups,
9e2381ff-b7fa-59c4-886f-0dad62ca2d80 | note | 3) scene settings
83323b1f-983f-5547-afc7-89c6166bc042 | note | 4) override sequences,
a8480db8-a6c6-5baf-8438-cf4df741112d | note | 5) luminaire and pole locations,
7eea6712-3cd8-59ea-870d-d32b63e08f05 | note | 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes.
ba61a961-a542-5120-ae64-9cb3b0c5ba5e | note | 7) All changes to design to be noted, highlighted or markup clearly.
e886ea1c-b698-5de3-b74b-29cded0e3d55 | note | Standard / Specification - PS 23.1.5 h) & 23.8.5 a)-b)
9c28e84e-da6d-58c2-bdd8-fe9b85790ca1 | note | Verifying Document - As-built Drawing/Survey Data
d9dcc91f-601f-538a-a034-590ac731c4e3 | note | Frequency - Post construction
b5dafbd1-a812-5fb7-bc12-b8e9fbd1fc09 | note | Verification Activity: Activity - H
fb270353-8b81-5834-ba75-2d06067ce47d | note | Verification Activity: By - PE/ENG
0b1bc759-fd4d-4df1-8c20-6eda3354dc5b | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
0f1f7245-9fde-538a-b193-11d66ee7b13b | textbox | Contractor's Rep Name:
d5d7d3a8-616c-5948-943f-6807f6b4ec0a | textbox | Engineer's Rep. Name:
2486dd00-dd75-51aa-ad8e-74141e29a5a5 | date | Date:
e47cb9c5-77b8-4de4-95b7-05dc026360b1 | signoff | Add Signature
65a73c7d-d8ec-44d4-8bc6-37ff5031b64d | checklist | DN1210-SP2-012 ITP DG7 Surfacing Rev 0 | itp | DN1210-SP2-012 ITP DG7 Surfacing
c98c7b76-1c59-4a88-83f3-ff075c28ec34 | section | 1.0. Pre-Commencement Activities
dc6a67fa-e827-4e87-b8b1-9a7d727c565c | checkpoint | 1.1 - Approved JMF for Asphalt Base or Wearing Course
f004e099-7c6d-5047-82d5-6a76aa8c52d3 | note | Detail of Activity / Test - As Per DN1210-WSP-GCO-0160
9effdfdb-ffdd-5b79-b87e-ba12fcf7435d | note | Action (Hold, Monitor, Witness) - H
51dae84c-e1ff-53ce-8692-cb8400b82d87 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
bfb7ce90-7a48-53a8-8739-d770119fbbb0 | note | Inspection / Test method - Confirm requirements are followed
a60a5483-62ef-5653-9abf-aa26d5d886a5 | note | Acceptance Criteria - JMF Validated in accordance with NZTA M/10:2020
559aa766-91b4-560f-8fd9-8f8893cf0e7d | note | Record documents (QCP - Quality Control Portal) - Mix Design Report
d771e345-5fd2-57eb-ad39-09cc586dd914 | note | Responsibility - Paving Contractor
a21afbf6-221e-53d0-b240-1d1958cb6ad1 | note | Project Specific Notes / Instructions - JMF expiry date and validation details in here
06e64250-d460-53ef-a10a-84a2618e1a80 | note | Designer - A
a238bbb6-578b-5bfb-a02d-b72aad2bdcab | note | Eng. Rep / NZTA - I
506d7d1d-6df5-5f6f-bd7b-22174a2857b5 | note | Contractor - R
3be74bd5-0e49-42a2-971f-b6d8d02fc9b0 | signoff | AUTHORITY HOLDPOINT
0ed99536-8210-4596-a0f4-cc16bf0efef4 | checkpoint | 1.2 - Site Conditions
fab90163-e1be-5e89-becb-18880150e590 | note | Detail of Activity / Test - Weather suitable, Site extents marked, surface suitable for paving (Depths/milling/cleanup complete etc), Environmental Controls in place
795e3bd7-ce40-5124-9e91-03fd88fbc77d | note | Action (Hold, Monitor, Witness) - H
c4f56981-1a85-5d00-b412-c59a11b8720f | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
4b6d55c9-2ee9-5e93-bc43-08ca7782eff6 | note | Inspection / Test method - Confirm requirements are followed
bb54cb41-9713-5392-8a41-929aafe438d3 | note | Acceptance Criteria - Weather conditions and Site is suitable for paving
174fa05d-d65e-52bf-8444-2084aefe9617 | note | Record documents (QCP - Quality Control Portal) - Site Diary
182e9d5d-c1c8-5875-9890-39746b9300b4 | note | Responsibility - Paving Contractor
6a5e9bbe-b765-51cc-a3fd-9635625b74b9 | note | Project Specific Notes / Instructions -
044ff021-e999-5ced-80de-c3a2c8def8de | note | Designer -
23d573f1-5f75-581e-a467-20e6182bbdb0 | note | Eng. Rep / NZTA - I
2d6e44d8-a94e-54fe-a6a6-71b7840029c3 | note | Contractor - R
b34051a0-4f63-4bea-aa67-07d4720d5241 | signoff | AUTHORITY HOLDPOINT
ae639d50-a6c0-4584-bd29-7a7bb008fb89 | checkpoint | 1.3 - Traffic Loops
f5fe97fc-5131-5688-87d6-059eeefb7014 | note | Detail of Activity / Test - Communication with affected parties
eb6aeccd-35b7-5c09-a57e-a8d31e0cee82 | note | Action (Hold, Monitor, Witness) - H
9f97efae-60e6-5aad-a7f7-3bacd90e4bc1 | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 7 days Before Works commence
f018d7d5-5c1d-5cd9-9f22-90b2b7344194 | note | Inspection / Test method - Visual
d0c08fec-2eaf-5c5d-bc53-b5a1c642edfa | note | Acceptance Criteria - Notify RC at least 7 days before surfacing is programmed
10966086-db13-5391-9992-50e6adababf4 | note | Record documents (QCP - Quality Control Portal) - Communication
4539ff0a-fd1e-5a27-8a7a-9e51c6966a64 | note | Responsibility - Paving Contractor
7069bae8-4ae8-5bec-be55-bcb2a17b9044 | note | Project Specific Notes / Instructions - only required where existing traffic loops are present
082375a4-f6fc-533f-a0ea-5740d0277242 | note | Designer -
f3d1e13d-7162-5f44-8b94-c434756d134e | note | Eng. Rep / NZTA - A
a24c8895-4bd6-526a-bfb7-270c37535747 | note | Contractor - R
ecf2de29-cf11-4f28-843d-2c7d86d42114 | signoff | AUTHORITY HOLDPOINT
41c3d67d-142c-481d-bf0e-1819d613cd16 | checkpoint | 1.4 - Paving Plan
46691a00-d588-5228-b903-ddc47fa335fe | note | Detail of Activity / Test - Paving Plan to be completed
9112723f-51e9-53c9-aa7e-bf4d7e4f42c1 | note | Action (Hold, Monitor, Witness) - H
9d28b7cb-b11a-5bd2-85e8-b6ab71919a3c | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
f6aa6068-0971-5ef0-86fe-f82ef13a9b3f | note | Inspection / Test method - NZTA M10: 2020 Clause 9.5.1
809081cc-a172-5e67-9365-784a7f774cbb | note | Acceptance Criteria - Paving Plan to be completed for each shift with dimensions, location and type of (hot/cold) joints, areas and tonneages
e365a3d0-ac51-53d2-8bce-8ddaaaf586ea | note | Record documents (QCP - Quality Control Portal) - String Sheet
5ed2501e-6466-5852-809a-12e79f42283a | note | Responsibility - Paving Contractor
3b430796-ec31-50b3-a270-66303caa4731 | note | Project Specific Notes / Instructions -
d438faa3-6a61-5302-b9cb-96540654b857 | note | Designer -
b25f3095-06d3-51cb-bc95-d8f984153d5c | note | Eng. Rep / NZTA - I
2d135831-6795-503a-931c-2f888c4cb722 | note | Contractor - R
f1725d6c-e0c2-4f10-86de-a25fe3bd9e24 | signoff | AUTHORITY HOLDPOINT
6976c6a4-7b67-46ea-bb30-00328510fe00 | section | 2.0. MANUFACTURE OF ASPHALT
2983d29b-bc27-41a8-b018-c8ecde3fbad3 | checkpoint | 2.1 - Temperatures
83931027-d44e-5683-95fc-ce40b0a77ce1 | note | Detail of Activity / Test - Mixing of aggregates and bitumen
31c0bc38-43d3-53eb-8ba1-a27414395551 | note | Action (Hold, Monitor, Witness) - M
90c76d99-e605-5eac-aa81-a86faa7ca150 | note | Minimum Test Frequency (Lot = 1 day’s production) - Constant monitoring of temperature by calibrated euipment
c1b996d0-9205-51f8-9996-3f4bb576ce13 | note | Inspection / Test method - Plant temperature probes
5e00105c-fa9e-5c70-9297-30c34f6838a2 | note | Acceptance Criteria - PNZTA M10: 2020 states max. 170 deg.C
d41d14b4-bdd4-55b2-a9cd-f41d95a6bcb9 | note | Record documents (QCP - Quality Control Portal) - Plant site diary
89e58816-f9e3-5883-87f2-3be843cc84b5 | note | Responsibility - Asphalt Manufacturer
03d14830-a780-5176-8520-88f32a7e508d | note | Project Specific Notes / Instructions -
dbff1282-8020-5fd2-9da3-f3eb3dc2dd46 | note | Designer - I
b93ca26a-61cf-593d-9669-6b60781d208b | note | Eng. Rep / NZTA - I
2345feb6-0e6e-59db-ac83-528a1d244666 | note | Contractor - R
ab431936-11fb-4149-9d92-7c4d04bd0136 | checkpoint | 2.2 - Production Asphalt
4e5d83b1-b334-5a16-9712-8b51df5975bc | note | Detail of Activity / Test - Particle Size Distribution
21e158fe-4544-5923-90dd-5f3133b9518e | note | Action (Hold, Monitor, Witness) - M
ee9f84ff-38de-5546-b47a-b45858149ac0 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
a69dbcd5-541b-53b8-bdbe-c6bd93ba0746 | note | Inspection / Test method - NZS 4407 Test 3.8.1
34766c8c-b51f-5386-8704-6ce141992e67 | note | Acceptance Criteria - NZTA M10: 2020, Refer to Table 5.3
cd2dd1e9-2f00-56be-b07d-fac0d80bf706 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
87044c20-2ee6-5f55-b0ff-592739d21d90 | note | Responsibility - Asphalt Manufacturer
240e8b0d-531e-5153-928d-9b2a1e8a4305 | note | Project Specific Notes / Instructions -
7dcbe210-3a0c-5900-afd8-b55f5e9af32b | note | Designer - I
e2842986-f941-54e2-a89a-e81247f3f6c2 | note | Eng. Rep / NZTA - I
6dc606df-ac45-5415-a1fb-2dea75c9c2f7 | note | Contractor - R
de042fb1-a779-4b8c-b7d2-0b7335620ab8 | checkpoint | 2.3 - Production Asphalt
49081114-d3f0-5f61-bcb0-6a55cf1dc671 | note | Detail of Activity / Test - Binder Content
4b7487e5-9fcf-5534-8479-4cd083b83eca | note | Action (Hold, Monitor, Witness) - M
a019c963-fbc8-54a2-ad27-4059945f7cc1 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
99cbf149-7aa8-5f5e-90c3-7185917502a5 | note | Inspection / Test method -
3b60c29f-1b48-5e17-9d96-0cab8bad233e | note | Acceptance Criteria - NZTA M10: 2020
d95a8bb2-a3ac-5a5d-a2c1-b327fc0b8031 | note | ○ Individual Test Result: ± 0.5
c19b9909-7ec8-59f0-8e74-2ec7a849df59 | note | ○ Mean of Three Test Results: ± 0.3
5f83234c-dad8-5825-a85d-b7f919e4bf47 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
77f7d156-f6ab-5c28-beaf-4fe131be08a1 | note | Responsibility - Asphalt Manufacturer
0034f5d9-9e46-5e6b-9063-4833bb9e7170 | note | Project Specific Notes / Instructions -
2aaccf7e-1e4d-5fa5-880e-23c7bcdead0a | note | Designer - I
b1d6e25f-eed7-5871-9bb7-a2d84b34931b | note | Eng. Rep / NZTA - I
6eb18b76-61e2-58a3-ace2-3aaf25b69bbd | note | Contractor - R
6dec1aad-5a21-41f7-aee2-dcf34b0fae4c | checkpoint | 2.4 - Production Asphalt
7b14b7ec-eb76-5a1f-92b9-00b815266e0f | note | Detail of Activity / Test - Max. Specific Gravity (MSG) of mix
ede450da-266d-5b99-a2b4-ddc4b8cf258a | note | Action (Hold, Monitor, Witness) - M
eb2e3b89-74a8-5942-bf0b-8afc89c9a0b7 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
03228b0b-e4b0-59d7-8802-b32ed9577d3f | note | Inspection / Test method -
093310bd-0b9b-5cda-8679-3b2ce97ecad7 | note | Acceptance Criteria - Report
a40cb9db-9c6e-566f-a7ae-7d942f04b94a | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
1f3cd02f-7c22-5336-abb6-b00cbf48ef1f | note | Responsibility - Asphalt Manufacturer
9b5762d4-8c75-507c-ac5b-e98f09ca83a9 | note | Project Specific Notes / Instructions -
00fdf505-e3bc-5d04-a4e9-65264d0a73a0 | note | Designer - I
4f50432a-6e0d-5b92-a8d3-358c7b888272 | note | Eng. Rep / NZTA - I
91012ce4-712c-5430-8ff0-eb8875a27a03 | note | Contractor - R
a8e5365f-87c8-4a1e-bf8e-52654e96d57c | checkpoint | 2.5 - Production Asphalt
30e843f0-ed74-5b79-b88a-6852e6f93520 | note | Detail of Activity / Test - Air Voids at lab design compaction
2cfc468f-d3e6-549e-8efd-216957b4596b | note | Action (Hold, Monitor, Witness) - M
54e4e9d5-763d-5a8d-b22b-d83a47af7ddd | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
7b31a1f0-5f30-5ef0-b06a-0ebd99eb18ee | note | Inspection / Test method -
2071fada-b86a-5c38-bde0-8b6665d0858d | note | Acceptance Criteria - NZTA M10: 2020:
98ee270c-4536-5faa-bc74-db44dce8bc7c | note | ○ Individual Test Results: +2.0, -1.0
321e9678-7ba7-5e3f-bb95-ed24fba30625 | note | ○ Mean of Three Test Results: +1.2, -0.6
6135898a-6b50-54fc-b2f2-10a60ddc5067 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
d0900a7f-ab64-5ecb-a577-8fe828d540ac | note | Responsibility - Asphalt Manufacturer
53e27727-5f61-59c6-9ce8-2051c502bfbb | note | Project Specific Notes / Instructions -
ba8ac78d-49dd-5b29-a61c-ff0f6bbbd750 | note | Designer - I
c8ff5161-6e3a-579a-9ea8-ab152789ada0 | note | Eng. Rep / NZTA - I
f3b85c70-f6f8-5ab0-83e1-753ad28da2c4 | note | Contractor - R
0fa83a97-c462-4aec-b230-f3779e6afed6 | section | 3.0. PLACING AND FINISHING
254ddadb-90c4-4e03-a3cf-9d49a5d831a5 | checkpoint | 3.1 - Membrane Seal
b6f99193-81ba-51de-af43-0d03e5edd9ce | note | Detail of Activity / Test - Application of Membrane Seal
e4e88723-6e8a-57b7-8b7c-d5ee1c44e687 | note | Action (Hold, Monitor, Witness) - M
c9c4ba8e-e68a-521e-b550-e03e695b3f78 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
6a701ba3-2e25-51d9-82a4-d16941e8d1dd | note | Inspection / Test method - Sealing Records
29d9a00e-8994-5da3-b5df-5b2a645ef3a3 | note | Acceptance Criteria - Application rate, chip type and binder as per membrane seal design
7b21275c-d9bb-53f7-b688-2a26e3b017c3 | note | Record documents (QCP - Quality Control Portal) - Sealing Records
a2e43994-58d8-5599-8eb4-bdeffa8d088e | note | Responsibility - Paving Contractor
b230af07-5c17-55f4-a385-b2b194158151 | note | Project Specific Notes / Instructions -
268f06e3-8528-5d32-9f95-c7ed9dec01c8 | note | Designer - I
ad9491b4-c3f7-5a35-8fdd-8acce9beab90 | note | Eng. Rep / NZTA - I
a3e6d48a-c075-590a-adfe-164c297cbc52 | note | Contractor - R
cfec8004-e229-4c62-a21a-faf5404777bd | checkpoint | 3.2 - Temperature
18286516-afb0-5f27-9298-83cb92f576cf | note | Detail of Activity / Test - Asphalt Delivery temperature
936532cc-024e-54e3-a04b-efede34a5ba8 | note | Action (Hold, Monitor, Witness) - M
e55fdb5a-36c6-5338-bf00-e519be7a8ddd | note | Minimum Test Frequency (Lot = 1 day’s production) - Every Load on delivery to the Paver Hopper
e5efd902-06d8-5ea6-b0c5-4c667e9995bc | note | Inspection / Test method - Temperature Probe
8d6e1f7e-af51-5d88-8470-a78bd83f9d1c | note | Acceptance Criteria - Target ≥ 150 deg.C. in the Paver
a8666bba-2379-5a82-a4bd-c3d9692e24c2 | note | ○ Min. ≥ 130 deg.C in the Paver
b9142d58-1b15-5ea8-8071-11c1c167f091 | note | ○ <130°C to be Rejected
2663255c-63f4-54f3-85f8-b4281d3c6a43 | note | Record documents (QCP - Quality Control Portal) - Site Diary
a7d7af1c-b7e2-55b8-a468-05f98031d96a | note | Responsibility - Paving Contractor
25860ca3-4c63-5279-9068-bea5dd7bf633 | note | Project Specific Notes / Instructions -
679cf4b9-2be7-5648-a7a0-7fbe23f4ca05 | note | Designer - I
c1390d20-4744-5f3f-8255-be73fedfef08 | note | Eng. Rep / NZTA - I
fc030b11-d56f-534e-92a9-7c42d07dc80a | note | Contractor - R
a53731bb-def7-4560-bffb-61e1b3bb4a8f | checkpoint | 3.3 - Temperature
045ecb81-3b8f-5cae-955a-0127a1cc89b5 | note | Detail of Activity / Test - Compaction Temperature
160bf609-21df-5ca5-ad73-0d0e9bc5f70c | note | Action (Hold, Monitor, Witness) - M
61408e6f-4034-5f09-a0c4-95e4118520f4 | note | Minimum Test Frequency (Lot = 1 day’s production) - During compaction
0bc1797d-8b82-52ab-8579-d62fc5a1442a | note | Inspection / Test method - Temperature Probe/Infrared gauge
70a84293-1736-568c-a2e9-a1de5fd3a056 | note | Acceptance Criteria - ≥ 125°C at commencement of compaction.
4d19d37d-2820-5aed-90ea-37f2bef6fbb0 | note | ○ < 80°C - Stop Rolling
c5d2559f-2e48-5081-bdcd-cba377ca8600 | note | Record documents (QCP - Quality Control Portal) - Site diary
71cb372a-d187-509b-91e3-2982d8590120 | note | Responsibility - Paving Contractor
b5140fc1-42fb-5eec-b64d-5e947e909a60 | note | Project Specific Notes / Instructions -
5ac42203-822e-55d2-a272-15939c0ebf8a | note | Designer - I
ac04f317-9289-54e7-8429-b3079353d5aa | note | Eng. Rep / NZTA - I
4d52007e-b20a-59e2-937d-1c1bfbdcf972 | note | Contractor - R
1fb2b6aa-294e-4922-8768-61c88479d0ef | checkpoint | 3.4 - Mat
bc9a5af2-a4a8-589e-9fdc-09a71ae07847 | note | Detail of Activity / Test - Load Locate
f681c831-49c3-5ba8-87db-ef477fe12860 | note | Action (Hold, Monitor, Witness) - M
d9c9f387-443b-54cd-9d15-d559a7b8bee8 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each load
1a19bc18-2b90-5a6e-b45c-225a3566f4b1 | note | Inspection / Test method - M/10
64ba9660-bff7-5a5d-b848-d25f81b124ec | note | Acceptance Criteria - Each load can be indentified to a location using a diagram. Record includes:
ca0f4d3b-cad2-59a2-855c-3c594cb6c272 | note | — Truck ID/Rego/Driver
c5b66062-9785-5fd5-81b7-185d932c1bb4 | note | — Depart Plant Time
453f1e02-0358-561f-a6f0-e530483caabd | note | — Arrive Site Time
8ed9e8c3-22c8-5e2e-bed0-c47616052dab | note | — AC Temp on Arrival
9a660cf6-90c0-5e34-9d3d-c13e9384daca | note | — Tonnage
63f33566-a92f-5547-9ddb-f636e0d32bf8 | note | — Run Width
52ef0580-4c4a-57ac-89b4-a4199f6df442 | note | — Estimated Run Length
0e266398-a11c-5898-b1be-325b74d290f3 | note | — Calculated Area
04a4e7dd-b2ae-55f9-b5a9-b819a03c15e4 | note | — Calculated Average Depth
6e1ceb2b-007d-527e-b2e7-84656469c0b5 | note | Record documents (QCP - Quality Control Portal) - Paving Run Sheet
df15b125-89df-5d57-85aa-c740dee752d8 | note | Responsibility - Paving Contractor
110b39a4-48bc-582c-9a65-2438be5fc380 | note | Project Specific Notes / Instructions -
e98b5246-1770-5771-a8db-797952cc3e99 | note | Designer - I
4a230108-a28a-579c-ae63-c9b685a8debb | note | Eng. Rep / NZTA - I
bcad1ad6-d667-5722-b4ac-ab3ce4bc4336 | note | Contractor - R
e5cc62d2-2c50-4518-b3b6-12f6734f7d2e | checkpoint | 3.5 - Mat
b03bf005-d559-5bf9-923a-bb9a485d4f12 | note | Detail of Activity / Test - Thickness Monitoring
8efc1847-1c04-5724-bdcc-e46884db1939 | note | Action (Hold, Monitor, Witness) - M
02cd3da0-8d86-5f75-8fa7-ac0b4b106121 | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
f416876a-9f50-59db-95bf-0ff756d77dc9 | note | Inspection / Test method - Dipping
d4db4261-515d-59c3-9f9f-4b1249fac640 | note | Acceptance Criteria - Target Loose Thickness -0mm / +10mm
a152d3e0-84ac-5f4f-9e5e-74967fa354f3 | note | Record documents (QCP - Quality Control Portal) -
2ecc7e2f-7b8d-5c43-a1d4-7277642f8fb7 | note | Responsibility - Paving Contractor
d88f242b-b3c0-5841-ba28-87501b741fc4 | note | Project Specific Notes / Instructions -
aee39824-077f-5b6e-a4d3-e490a8b2f875 | note | Designer - I
b471b379-f29e-5a55-989a-b5a726935706 | note | Eng. Rep / NZTA - I
38ac10e2-549b-541a-bca2-e04f59f7f28f | note | Contractor - R
35dd66e4-5123-460c-814b-45991e6aeeef | checkpoint | 3.6 - Mat
17f82e38-3a91-53ed-a970-cf7c7f69663d | note | Detail of Activity / Test - Compaction - NDM
2a9eac60-7a10-5026-a2f1-6b3af61d3ffa | note | Action (Hold, Monitor, Witness) - M
b3f6bee5-7778-58a4-9bc3-d6fc81b9b469 | note | Minimum Test Frequency (Lot = 1 day’s production) - Plateau to be completed on 1st run, thereafter monitor compaction/roller passes to achieve target density.
cd889bfd-2585-5a46-a5c3-f7e852eeb6a6 | note | Inspection / Test method - Insitu density and air voids
4c03239e-77e7-59f8-aa67-844b1e8ade18 | note | Acceptance Criteria - NZTA M/10: 2020 - section 9.9
67c0f041-7895-5617-904c-c3795db57528 | note | Record documents (QCP - Quality Control Portal) -
77c59f75-a538-5d71-89fc-669a8c36f394 | note | Responsibility - Paving Contractor
9a395e88-7d3c-5831-b604-319a22db686a | note | Project Specific Notes / Instructions - Use a calibrated NDM with established core correlation. Locate and mark cores, record NDM Bulk density by core location (including any offset used).
cf58367a-ca7f-54dc-abf8-e1e6d0c772f0 | note | Designer - I
2019e436-49ec-51b6-8b05-29289a123137 | note | Eng. Rep / NZTA - I
4d709b87-2ad7-5233-9b1b-1a4a022ca811 | note | Contractor - R
d52297e4-2845-44e2-ae3c-050acbf6d55f | checkpoint | 3.7 - Mat
3dfadf55-041d-5bc7-a92b-2c52cb459f2f | note | Detail of Activity / Test - Compaction
796c7ee4-0fc5-51a3-ab0f-19bf52e858c7 | note | Action (Hold, Monitor, Witness) - H
a2f10f66-f910-5845-9de3-fd34f9fd178e | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 1 mats and 1 joint
50ffddab-b0ee-5220-848e-e4f450d97897 | note | Inspection / Test method - Insitu density and air voids
31ac0184-464a-52c5-8d64-11c3bc04aebb | note | Acceptance Criteria - NZTA M/10: 2020 - section 9.9
acd5ecb2-289b-5c62-98ed-a81b5d77582c | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
7f046f7d-4e93-590f-a9cd-3d9d32673e6e | note | Responsibility - Paving Contractor
7962a415-ff07-5701-ace6-d98b6d9ee91c | note | Project Specific Notes / Instructions - A pavement lot shall be an essentially homogeneous section of work completed within a shift of production.
da0c8df6-9661-544b-8e6d-cb3928be2aed | note | ○ The lot shall be divided into an appropriate number of approximately equal sub-lots and a core shall be taken randomly within each sub-lot. The Engineer or their delegate shall use a random method for locating each core position, such as ASTM D5361 or a similar process.
989571b7-3a6a-5d83-9b53-ae2aadef0385 | note | Designer - A
b2de4d43-8303-59a2-a786-d4dff049af21 | note | Eng. Rep / NZTA - I
5079bf89-e59d-58c5-a05d-109df44439b8 | note | Contractor - R
97bb6f80-d4db-4e5a-a2ab-a6b5086e0246 | signoff | AUTHORITY HOLDPOINT
32a8cfb4-1ff9-42e9-ad52-f882d33f18dd | checkpoint | 3.8 - Mat
b08aece8-4b45-591a-8e61-1c869086ed0c | note | Detail of Activity / Test - Thickness
3f1a4f39-3775-52ff-ac91-64dd19f9a0af | note | Action (Hold, Monitor, Witness) - H
cf16f2ae-7536-5c25-9f3c-5047f281179d | note | Minimum Test Frequency (Lot = 1 day’s production) - Each load
05c3ef6f-db5f-5c2b-941c-c30bd5b97e5b | note | Inspection / Test method - M/10
381807b0-00b1-531d-8fbb-36e08c58e145 | note | Acceptance Criteria - Calculated average Deth from run sheet
b534b714-fa21-51b4-8846-ced0b1e264e6 | note | Record documents (QCP - Quality Control Portal) - Paving Run Sheet
e181b4d8-a65a-51b2-b79f-e431e97143ba | note | Responsibility - Paving Contractor
3aa4b0ca-948e-51be-b7d1-748de9e13faa | note | Project Specific Notes / Instructions -
f5415c3d-8efa-5d95-b54e-995fc886b8c7 | note | Designer - A
1f35dbbe-030a-596f-9fbb-b7b2be5fe6f1 | note | Eng. Rep / NZTA - I
b3ba1e5f-f16b-57bc-960c-e1631d37348f | note | Contractor - R
d9de76a2-97e8-403f-adda-c91fe6259782 | signoff | AUTHORITY HOLDPOINT
cd470b51-e537-4ea8-9aad-81fc95fd40eb | checkpoint | 3.9 - Mat
cc8d9859-c147-53d2-ba46-f86226989f3c | note | Detail of Activity / Test - Shape
2872816e-7307-5d7b-9bf2-e746530364d2 | note | Action (Hold, Monitor, Witness) - M
85aebd34-a3af-500b-a5c9-1cbaca1d8eb6 | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
e4124b4f-8105-5463-af97-6690f4aa6075 | note | Inspection / Test method - 3m Straight edge
47b849ec-6849-5ce2-8bfe-3358aecf8c17 | note | Acceptance Criteria - Where the length of the site or the geometry is such that a road roughness-measuring vehicle cannot be used then the straight edge can be used for checking the surface shape. Refer NZTA M/10: 2020 - section 9.8.
158225bc-7a2c-570f-baa2-ac23b55ba1f5 | note | ○ Not more than 5mm under a 3m Straight Edge.
a2402476-7086-5edf-87fd-a29a2b44b743 | note | Record documents (QCP - Quality Control Portal) - Straight Edge Record
f6d93181-0d1b-5048-9971-d811636bd7cf | note | Responsibility - Paving Contractor
3d8cb422-5fdb-5a8b-b9d0-faa43d27684c | note | Project Specific Notes / Instructions -
dbc7f2aa-e781-5557-9469-0ac284527e5e | note | Designer - I
20f8330d-9c8e-52e7-8d9b-8cadb13c30d7 | note | Eng. Rep / NZTA - I
c85662bc-217b-5bdd-96a9-5dbc9a951a4c | note | Contractor - R
ae943655-63d5-4201-8ed2-b0f5d9a6632d | checkpoint | 3.10 - Paving Quality
b2324f05-e80c-5c33-8c98-dc6f7e756e00 | note | Detail of Activity / Test - Level
4e96cad9-6935-5290-818a-93ccba665ade | note | Action (Hold, Monitor, Witness) - M
1628fcba-175c-5604-84bd-6f44d2335005 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site
6e83e395-3f86-55bd-8457-ebd27bc7ee1f | note | Inspection / Test method - As Built Survey
22714974-a505-5503-a485-15d63d7066f4 | note | Acceptance Criteria - -0 < +5mm from Specified Level
4cc96957-a90d-505d-95af-f6a17a4f5f5c | note | ○ Where there is Kerb and Channel shall be flush with or no more than 5mm above the LOC.
5d2049a1-ec03-53e3-a70c-aa888af6ec98 | note | ○ NZTA M/10: 2020 - section 10.2
cf43bc5c-29c7-598c-a5d3-11e323e83d10 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
3e053f2f-2ff1-5f24-9775-71b411b63967 | note | Responsibility - Paving Contractor
c95af17c-0d40-592f-878a-f4bcf8ec2a44 | note | Project Specific Notes / Instructions -
1e80218a-86a8-59a9-8911-7d7a96581bff | note | Designer - I
d3ae7a48-4ec6-53a5-95f3-9e4826c5ca00 | note | Eng. Rep / NZTA - I
fa8ef262-87f5-50b5-8810-1ba608fa8313 | note | Contractor - R
a687c8b7-9370-46eb-af2b-65f21309aa55 | checkpoint | 3.11 - Paving Quality
240ed702-f2b0-56e7-b005-092bcf3d77f1 | note | Detail of Activity / Test - Alignment
891e9bff-f3fc-58ef-9c22-21ed69a54f18 | note | Action (Hold, Monitor, Witness) - M
773f8ca9-504d-59ac-b18e-4d84e83a985d | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site
e4011764-6a93-5dcf-93eb-2baa5be37a9a | note | Inspection / Test method - As Built Survey
2d720186-ee6c-509b-a431-a7aa6c654f9c | note | Acceptance Criteria - Kerb to kerb
0b3d62fa-57e2-534b-a3a2-0c89dc42c81f | note | Record documents (QCP - Quality Control Portal) - Survey As builts
efa56964-0c4f-56dc-885b-df60cf388daa | note | Responsibility - Paving Contractor
9247df49-129b-5b6f-babd-9ea8e7f7995b | note | Project Specific Notes / Instructions -
739fd771-1376-55cd-9696-978401b7b0a3 | note | Designer - I
f1287440-495a-5001-94fb-e7fe20a0b2c9 | note | Eng. Rep / NZTA - I
9b67348c-b824-5fdd-a089-3c8854ca06c5 | note | Contractor - R
8ea52687-afdd-4521-ad9b-6e0113b2cc33 | checkpoint | 3.12 - Post Paving Completion Checks
03f47821-41f2-53f2-adc2-2b26218a69fb | note | Detail of Activity / Test - Site clear and cleanup
f9cdc30b-13b9-57b7-858e-5f2b2c85045a | note | Action (Hold, Monitor, Witness) - W
d5e12e7c-f483-51b3-9b0e-bf0a199bba26 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
aba9970c-aade-5f68-8ac2-da0f868d7229 | note | Inspection / Test method - Visual
746961c4-585d-515b-9cf3-f74b7841d275 | note | Acceptance Criteria - Site is cleared of plant (or parked in safe location) cleanup of all waste mix, paper and detritus is complete
6989337a-05a3-51e8-b79f-db55aa1c06ad | note | Record documents (QCP - Quality Control Portal) - Site Diary
a4130eaf-9d10-5a3a-a8fd-be2b06857691 | note | Responsibility - Paving Contractor
6d8cbe67-5038-54b9-b988-05b22332095c | note | Project Specific Notes / Instructions -
8e5e1aa4-3ed8-5aa0-a53e-f96885b99c44 | note | Designer -
eb6dc028-6980-5a40-9416-c95ef92a2440 | note | Eng. Rep / NZTA - I
3ebd17d8-b5d2-5cb8-a42c-d8e1992cd40b | note | Contractor - R
84b3f7d5-fcb0-4ec9-9238-1fbe3cd7183d | section | 4.0. As Built Records
3a9dcb1c-e138-4e9d-93d5-d1e477295472 | checkpoint | 4.1 - Assessment of all test results for conformity
2f537d16-264d-56d7-825c-decdc2e184a3 | note | Detail of Activity / Test - Review against ITP Requirements
b7c41d90-a521-5935-9a9a-5bc595ff6b78 | note | Action (Hold, Monitor, Witness) - H
a4497175-7ab7-5234-bf4b-49f2fee346c1 | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
e530b68f-d314-5a5c-b3fa-8b07ef87d0c6 | note | Inspection / Test method - Review
09c6c459-44b4-5471-932e-09fefa79ed4e | note | Acceptance Criteria - Reporting of any non-conforming results to Engineer via NCR
da62f5ae-967d-5fa2-9937-73ecd2dd4668 | note | Record documents (QCP - Quality Control Portal) - NCR
0911415f-69c1-5993-b1ba-8df1f5c26d54 | note | Responsibility - Paving Contractor
12c0afd7-3c1b-52cc-8298-8259f77b7fad | note | Project Specific Notes / Instructions -
313cb1a2-0b2c-5c4c-8601-44e2a1e49937 | note | Designer - I
574796fd-86c2-5a97-87cd-902914dd76b8 | note | Eng. Rep / NZTA - A
ee918de5-478a-50a1-a993-3d454f2b632e | note | Contractor - R
0a2cab0d-699c-423c-bef6-dcb398d5f3bb | signoff | AUTHORITY HOLDPOINT
cbf37fb7-7497-4b6a-9cb6-61e12d81d0a6 | checkpoint | 4.2 - RAMM pavement and surface records
fd5dbf61-3bc3-5218-9d06-5258ca1f71d6 | note | Detail of Activity / Test - RAMM surfacing pavement data spreadsheet updated
70835cb5-fd11-57e2-9cae-f93c79902519 | note | Action (Hold, Monitor, Witness) - W
900a997c-082e-5ae2-a05a-72b10e1e5a39 | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
56ba2cbb-cef4-5c54-be96-f72ef6a5fc8f | note | Inspection / Test method - Prepare Data
ff251ec2-2f96-5c3f-9294-06286639cc3c | note | Acceptance Criteria - Over milled and Deep lift extents recorded and verified by Contract Engineer / QA
c0dc764b-5a6c-51cb-8042-22082f9ca07c | note | ○ Spray sheets for membrane area received by Contract Engineer from Sealing Team.
9d9a93f8-ec65-54fd-9665-2ef49c80c6b4 | note | ○ Surfacing layer extents recorded and verified by Contract Engineer.
853684e9-cddd-5a88-ac95-576a6f137318 | note | Record documents (QCP - Quality Control Portal) - RAMM Spreadsheet
f4301b09-680b-54c2-bfdf-256e49925525 | note | Responsibility - Paving Contractor
7cf0a8d6-a946-5d3f-8ea7-0b4a48553595 | note | Project Specific Notes / Instructions -
ed46f7ab-2460-5acb-9051-d41f82331a28 | note | Designer - I
438c153b-5a7a-5595-9e3a-d1c56ebb441d | note | Eng. Rep / NZTA - A
1aa8e36b-3fb5-5745-941c-a590e48fc964 | note | Contractor - R
98458b3f-d654-4310-a626-55acda5e7720 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
9fb5d32b-6e8f-5366-bd78-700eb3802a57 | textbox | Contractor's Rep Name:
f6147fae-b59e-5709-bc71-707557bfa83c | textbox | Engineer's Rep. Name:
e25b73fb-34f0-54c2-8ed0-12b4e7b0e042 | date | Date:
1c16b665-1f76-486d-a44b-fe66e892f73d | signoff | Add Signature
b709d4a0-6ff2-4f3b-9444-eda9191de9fb | checklist | DN1210-SP2-015 ITP Acoustic Improvements Rev 0 | itp | DN1210-SP2-015 ITP Acoustic Improvements
9a9ec31f-d043-4667-aaeb-d640b7f9ec45 | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
d173a912-186b-4b58-b114-6908bf8b6268 | checkpoint | Pre-Construction Surveys
5389b129-ef65-543c-945d-4005c7e9e788 | note | Detail - Photographic record and inspection of existing property conditions prior to the commencement of works.
cadf59f5-7f55-58a8-b8ea-57074259c37f | note | Acceptance / Conformance Criteria - Building Report
4d3d06da-deb7-5c5e-979d-bdfc98744c7e | note | Standard / Specification - PS 2.9
8400d035-08db-53ca-8379-6c58015e1cde | note | Verifying Document - Building Report
c837e8e9-8e4e-5760-b796-52f7a507b0de | note | Testing Quantity Required (based from schedule qtys) - Prior to commencement of works
3b75097d-ebcb-53d2-895c-1b880a262a5b | note | Verification Activity: Activity - ENG
dc0e94b4-dba1-5a38-9191-7e58d052ede7 | note | Verification Activity: By - HP
fa0d33b3-1125-4832-a98a-4f81ea18c1d8 | signoff | AUTHORITY HOLDPOINT
7af61baf-2f3f-4845-8b41-f77b622a9706 | checkpoint | Omega Windows & Doors
77395b26-bd0d-56d0-9dae-3d5fc0ef1062 | note | Detail - Product specifications to meet the requirements of WSP's acoustic survey of each property.
163e58db-a944-5b48-b6c9-a722bcfc75c4 | note | Acceptance / Conformance Criteria - Engineer's Approval
44e3d9d5-4a1a-5717-ac73-190de0385c4d | note | Standard / Specification - Signed LTOs & Acoustic Property Surveys
faac6b8f-8e23-52f3-94e0-7f9bcba1d60d | note | Verifying Document - Manufacturer's data sheet and Engineers approval
8bc378e1-e027-57c7-8782-d396d1b8e4ac | note | Testing Quantity Required (based from schedule qtys) - Prior to commencement of works
fc5ce875-4378-5f8a-81d3-fec8f7a910be | note | Verification Activity: Activity - ENG
72e4ea62-87e5-52e6-bb4c-a982c9d005c2 | note | Verification Activity: By - HP
74545448-3435-4f0f-8801-3d1d75d4ccf6 | signoff | AUTHORITY HOLDPOINT
1cca48f8-355c-4be0-bcc5-9c1525e011e4 | checkpoint | Kiwi Double Glazing
a4c8c8e5-99b1-5418-8581-e2a4fb53ed6f | note | Detail - Product specifications to meet the requirements of WSP's acoustic survey of each property.
e439c2b1-b9b5-592c-8200-2e26dd931dc6 | note | Acceptance / Conformance Criteria - Engineer's Approval
ff2f2a95-7da8-5e24-a86a-33eda8c33cde | note | Standard / Specification - Signed LTOs & Acoustic Property Surveys
7a26979c-bc78-5125-9bce-517618fa1c75 | note | Verifying Document - Manufacturer's data sheet and Engineers approval
79d2ab91-52fe-5b2f-ad33-7298b73753e0 | note | Testing Quantity Required (based from schedule qtys) - Prior to commencement of works
f77eb35d-d51a-5281-825b-e85731a38cf8 | note | Verification Activity: Activity - ENG
4e59fb61-5d3f-50ac-a417-e0382584ff48 | note | Verification Activity: By - HP
6cad18ab-0683-4c14-a87f-35391dc2f4b1 | signoff | AUTHORITY HOLDPOINT
49bb740d-50a8-4a9a-bd9d-db10e70b3c71 | checkpoint | DVS Ventilation
997742ed-f39b-5d8b-b515-e0a25729bc7d | note | Detail - Product specifications to meet the requirements of WSP's acoustic survey of each property.
33081d2a-0605-56ed-ab31-894b5b67e116 | note | Acceptance / Conformance Criteria - Engineer's Approval
b7de6473-0b88-55c6-b10f-6294d452702e | note | Standard / Specification - Signed LTOs & Acoustic Property Surveys
d09a9b99-5e43-5810-9271-adaa26e0a919 | note | Verifying Document - Manufacturer's data sheet and Engineers approval
2d926416-5187-5ff4-be87-c0630d224328 | note | Testing Quantity Required (based from schedule qtys) - Prior to commencement of works
eb368da3-21dd-557a-88af-9bc2ddf69fe5 | note | Verification Activity: Activity - ENG
278876b8-5c3e-56e1-8d8c-9f897b25f883 | note | Verification Activity: By - HP
aeb2e1c2-b0cf-44ee-879e-b731627ea03a | signoff | AUTHORITY HOLDPOINT
6ef9c66f-e532-4114-b957-c8e97f803fde | section | SECTION 4 – POST CONSTRUCTION (HANDOVER)
96895415-86bf-488b-8b8d-7a8eb2ff35ba | checkpoint | QA Check list
47d226de-ab6b-5a24-a3d3-ebc9fca489d9 | note | Detail - QA checklist covering the extents of all the work including the openings of windows & doors, new doors & windows, double glazing installation, ventilation system, installation & painting.
443ce2ec-ae11-5570-854e-af1609483ccd | note | Acceptance / Conformance Criteria - All the scope of works stated in the signed LTO's of each residential property will be visually inspected.
95ec5845-40e2-56b4-93ed-2c30d2bf38dd | note | Standard / Specification - Signed LTOs & Acoustic Property Surveys
304d04b0-99ec-51d1-8068-6486a12705ee | note | Verifying Document - QA checklist, Visual Inspection
f036bc57-0715-5dde-8d0e-42d6a0901c3d | note | Testing Quantity Required (based from schedule qtys) - Pre-construction, During construction, Post- construction
9bd29241-d893-55a8-a42c-a8a5505206e5 | note | Verification Activity: Activity - WP
994118b0-72a9-58c9-9371-e3961dcca186 | note | Verification Activity: By - SE
513a260e-8e4d-482f-9235-b78c22496847 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
c56b2fef-7ac7-59d5-9522-026994611c63 | textbox | Contractor's Rep Name:
fe2983a8-7dc6-5e0c-b2fd-ea17c551b77c | textbox | Engineer's Rep. Name:
bba4ce60-7b51-5fef-bc3e-af00043c162c | date | Date:
eff128a9-f78a-4601-aefe-9fd26afb97ba | signoff | Add Signature
ae028973-bbe4-48db-bb5a-b32dd5261c6d | checklist | DN1210-SP2-016-002 ITP SH29 Wastewater (MH 05-MH 12) Rev 3 | itp | DN1210-SP2-016-002 ITP SH29 Wastewater (MH 05-MH 12)
7f4dc871-4f43-4ac7-b20d-42ed7c34cee2 | section | SECTION 3 - PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
b4b61edd-5db4-475c-8974-ef8681ce9714 | checkpoint | 3.1 - Extent of Line Setout
535aab0a-baba-5108-897e-8519ad071a90 | note | Detail / Activity - Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings.
8d94cd6e-d85b-56f9-9847-f444ad6f4f05 | note | ○ Identify any clashes before construction.
9ff311ff-f913-52f7-b18c-72879cbfcb26 | note | ○ LOT- markup
ea2acaab-66ae-5d99-87bb-a35e6b6dc380 | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
fe4c22fa-7f73-5ad9-9e72-7fdf4c75894d | note | Standard / Specification - Design Drawings
64f4bf5e-77af-5e23-a6a6-e352792eebf4 | note | Verifying Document - ITP Sign Off / Mark-up
c6444086-cdf9-59cf-b403-d63496892c93 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
0dd987be-3796-535c-9e41-17bd85117498 | note | Verification Activity: Activity - HP
209ccbea-7dfd-5e5d-8419-52f752e3e2a1 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b0f28492-d848-5456-9c34-4b5b0eced496 | note | Verification Activity: By - ENG
fc6e0be6-7c97-4598-85fc-90c57119028b | signoff | AUTHORITY HOLDPOINT
ff418cf6-a9e6-4e7d-8e0e-c6ef9c876ea2 | checkpoint | 3.2 - Pipe Laying
de25ad60-e8a5-5242-a06c-fc7401070f7c | note | Detail / Activity - Method statement
2b750a95-ed80-514c-8663-5479712597fd | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
8e36c6d0-c245-557f-99f3-35cf925974c2 | note | Standard / Specification - PS- 22.3 Appendix V
82c79773-c980-5433-b95c-ae4370503db1 | note | Verifying Document - Wastewater Construction Work Pack Sign off
ca85cf61-7472-5c49-88e8-b155c4508e06 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
47cad8b8-ca70-57a9-a0d6-97534c34e1ab | note | Verification Activity: Activity - HP
ace063f1-69c6-57d3-9c13-4ba869fe6b38 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
bb702228-ba38-5772-bb9d-d76be8fd6448 | note | Verification Activity: By - ENG
3ba424d5-7fa1-44ed-a9a9-3352afb07c2b | signoff | AUTHORITY HOLDPOINT
859fa3f6-de8a-428d-938f-f061d30bb07f | checkpoint | 3.3 - Pipeline Pressure Testing
435fd52b-6bde-5be3-84db-eb1ad0840a20 | note | Detail / Activity - Method statement
6257e8dd-ee8c-5215-8aa6-c1c148ee058d | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
5264e70e-6a8b-588f-a517-27aa6405a6bd | note | Standard / Specification - PS- 22.3 Appendix V
a77fd629-2f8f-5abf-84d3-80cc9c8e3758 | note | Verifying Document - Wastewater Pipeline Pressure Testing Work Pack Sign off
b2f6a8d7-fed8-5fcd-ba9e-d8a0c2ae7045 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
d578c4ad-ff25-51c9-b0a6-6c8f7d2d2564 | note | Verification Activity: Activity - HP
1d6686b8-122d-51fc-a7e5-e68e46bed086 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8aefce8f-be8e-5c54-b83a-66af96b338cc | note | Verification Activity: By - ENG
d1f95329-9729-45e2-9ded-e42b45c40625 | signoff | AUTHORITY HOLDPOINT
73e9566c-5cd4-418f-b6f5-9c5e89687655 | checkpoint | 3.4 - Material grading: Materials (GAP65/AP65)
25829091-27d1-5346-8a6e-08a7ed142744 | note | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
82479ba5-a3b6-5566-a119-94f0f9ea9b06 | note | Acceptance / Conformance Criteria - No Particles >200mm
4cffcd0b-3e92-527f-a344-fbfcc98cb4e0 | note | ○ Maximum fines 10% passing 75micron sieve
d9b6b41e-8a13-5c3f-8a13-c3d961cff621 | note | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
5b7f6bbc-043d-5693-97b9-2cea04b8b718 | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
1b690b7a-6111-5002-90a0-1faf7587985f | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
dcd11345-54cb-5af4-9644-2be61f8e174d | note | 0-400 - 2 tests
18e60561-9cb1-5dfb-b9a4-6244c492dbbb | note | 400-1,500 - 3 tests
7a618175-5e6d-53fd-830d-2ca970ba085c | note | 1,500-4,000 - 4 tests
bf3daacb-96a0-5387-8c1f-0ec8f6dca165 | note | >4,000 - 1 test for each additional 1,000m3
648c0374-5e2e-5ab3-b617-c2aeb1d17d42 | note | ○ Results to Engineer 2 wks before importing
c62c1de8-f0b2-50dc-abf7-695c4b9b720d | note | Verification Activity: Activity - HP
d6838521-e057-5f92-8fca-320715cd8cdc | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
cfd8e693-86b8-5a30-813c-393c9cfbf4ef | note | Verification Activity: By - ENG
6efcde62-d925-4013-a863-e5a365c5aea6 | signoff | AUTHORITY HOLDPOINT
75b11946-682c-4b0d-afec-5f41acd9cb69 | checkpoint | 3.5 - Weathering index: Materials (GAP65/AP65)
fb0df822-2013-5e7c-8233-ac88e1f12aaf | note | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
79b862ee-6c3b-52eb-bf41-085a2ab36b52 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
bdc82844-6e98-5ba6-8f11-b81d42359d8a | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
f93a0cd2-3ef6-545e-987d-079021e4dc8d | note | Verifying Document - IANZ Accredited Report
6a1f6eab-981e-5843-8a6b-504a23411b04 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
f5e825d3-1682-5b34-9b5e-2092c049ca2d | note | ○ Results to Engineer 2 wks before importing
bddfcb9f-220e-5dee-9018-febd47333209 | note | Verification Activity: Activity - HP
e4e4d266-6f68-56ca-8b7a-38865c49f275 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
72ec44d3-c674-5d93-a3b6-f57477762dcd | note | Verification Activity: By - ENG
26a49527-bbd1-4dfe-b660-3e89b04ba32e | signoff | AUTHORITY HOLDPOINT
e36305d5-23e2-47b8-a1ff-c4762d8bd2ce | checkpoint | 3.6 - Crushing Resistance: Materials (GAP65/AP65)
67e4c694-ee2e-585c-851f-564d345fbce2 | note | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
18bc0e4d-2a4d-57b7-b1d2-197c5bd9874a | note | Acceptance / Conformance Criteria - >100KN
e53141fa-18cc-599b-9df1-53eea86d34ea | note | Standard / Specification - Appendix XVIII, Appendix V
7d43695d-829f-5645-adc3-701de2dabeac | note | Verifying Document - IANZ Accredited Report
18e3daca-ba0d-53e8-9cbf-c50e8c5087d6 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
0d1d8d2d-2fe6-5571-a5d0-3c2412facc80 | note | ○ Results to Engineer 2 wks before importing
c500d7ba-1e63-5e05-8dcd-de99d7f806f1 | note | Verification Activity: Activity - HP
fd37f603-c7bc-574e-be15-418b0e1aadac | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a4c3c808-7a7c-56c7-95cd-98b4e0bb4967 | note | Verification Activity: By - ENG
954cdae4-87e6-4825-a038-3f99723945e2 | signoff | AUTHORITY HOLDPOINT
b24c1539-203c-49f6-977d-62ae1bdd7639 | checkpoint | 3.7 - Maximum Dry Density and Optimum Water Content (AP65/GAP65)
cd112fba-bc98-526f-90cc-fed3e40dc5b2 | note | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
af250975-24d0-5ebb-be69-3bdb81d814fd | note | Acceptance / Conformance Criteria - Report Value Only
aaeab612-da67-59f6-854a-c8e0255f3b23 | note | Standard / Specification - Appendix XVIII, Appendix V
7b687c06-1c1b-58e9-88f2-f710308d3038 | note | Verifying Document - IANZ Accredited Report
65c687f0-9dae-55f2-beb7-977b8f58e887 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
8db0a350-0b3c-5153-86d4-36838146b1d3 | note | ○ Results to Engineer 2 wks before importing
54573c91-c4b7-58a1-9802-04ceb49710ac | note | Verification Activity: Activity - HP
0bc1b6a8-0aa7-5c71-8733-ad76dfdf404b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
44facc05-a30e-5791-a845-f6dc3ff41c46 | note | Verification Activity: By - ENG
a0d3c936-e25c-454d-9956-561a982a23e7 | signoff | AUTHORITY HOLDPOINT
03340093-73c1-4197-8393-7ce85774f042 | checkpoint | 3.8 - Material grading: Materials (Sand)
ce84e9a7-900a-5724-9a3c-ee7ac409640c | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
621e4a3e-1ee4-54bf-9897-f7b18f5eac18 | note | Acceptance / Conformance Criteria - Sand: Sieve Size ¦¦ % Passing
4c638c59-d31d-5908-be1a-8b4ae65c2369 | note | 4.75mm ¦¦ 100% passing
61840643-6c46-5309-bf6e-efc58327ee52 | note | 2.36mm ¦¦ 90-100% passing
17f201cf-812e-53c2-998a-943353e02481 | note | 1.18mm ¦¦ 85-100% passing
04075114-24de-556d-9744-a705e6c3bb93 | note | 0.600mm ¦¦ 70-100% passing
3a0a59ba-9f43-53ab-8dbe-a0d907761569 | note | 0.300mm ¦¦ 50-100% passing
5388daa2-cb66-5777-9ac9-2d3a952e4ba2 | note | 0.150mm ¦¦ 0-40% passing
f9b6c5bb-1c91-5080-94df-00a7249ecd6e | note | 0.075mm ¦¦ 0-5% passing
3647430a-897d-54ed-9af9-da52b4ec5d0a | note | Standard / Specification - AS/NZS 2566.2 Table G3 PS 22.4.5
cb7c9bfe-c044-5e68-a5ea-bc02fe23b67c | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
8e040da6-7288-5145-b94f-443f5e42abb5 | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
5ee24ccd-bb0d-5597-ab74-31da46bac93f | note | 400-1500m3 ¦¦ 3 Test
871a00a7-2570-5f2d-9f3a-ca4a9c4eca6c | note | 1500-4000m3 ¦¦ 4 Test
1328cc86-5b12-5193-9aad-64429d8edcee | note | >4000 ¦¦ 1 Test Additional 1000m3
891b4882-354a-52a8-8c64-a04020a7b49d | note | Verification Activity: Activity - HP
2ea49c89-afe2-5ae3-8c09-d082369d1b2b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ffc29da7-3d16-56d7-a822-69677def33f1 | note | Verification Activity: By - ENG
ea2da0a9-6ff6-44ab-a843-4582e7094751 | signoff | AUTHORITY HOLDPOINT
aba32e2f-9de5-495e-ab34-8a4b88290509 | checkpoint | 3.9 - Pipes (PVC/PE)
ef9900c5-08a3-55e7-94f1-e7e8f0b188fa | note | Detail / Activity - Manufacturer's record and location of extrusion plants.
f1b769ce-c980-5a9f-adba-531e56fa358d | note | ○ PVC pipes must be Series 1, plain wall construction, rubber ring jointed pipe, unless shown otherwise on the Drawings.
e36c1f26-acb9-5945-abdd-a69413fd7510 | note | ○ All PVC-U (Unplasticised) pipe must conform to the requirements of AS/NZS 1477.
61388c1d-4ced-5529-8fce-6e833bd1bc4d | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
c4d35ea7-bf71-5e00-b01a-b2fa014c8a97 | note | ○ Full Traceability information and certification of analysis for the resin batch.
ceb33d64-5fe7-5cf0-a7f6-d22c43a7b99b | note | Acceptance / Conformance Criteria - Full Traceability information and certification of Material
ccedc239-8e13-5f49-bb45-789771b9d6e3 | note | Standard / Specification - PS-22.4.1 (d) AS/NZS 1477
2db4e325-fa1c-5899-95cb-a5f2da3a797f | note | Verifying Document - Delivery Dockets
d2cc2006-1100-5df5-8df3-10f4e2496fea | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
2e9e44f4-ddef-5a6d-9415-dac60247a9f2 | note | Verification Activity: Activity - HP
66903a22-a224-5a65-9fa2-d9df4d627df5 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7fd8ef08-3306-57bb-b2b9-ea4e0d5c615b | note | Verification Activity: By - ENG
4ef3be5d-3c59-46ec-831b-af6b381cd883 | signoff | AUTHORITY HOLDPOINT
c1c34367-4af7-4f2d-b9de-3ebc38ac8f4b | checkpoint | 3.10 - Flanges, Fittings, Bends
5ddd6c4a-daee-5cc1-b539-e5f0005579bc | note | Detail / Activity - Have a pressure rating no less than the designed pressure.
b14e6f7e-1a48-56f5-a0f6-6b1ed555bfb5 | note | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
b1dfa8ea-3a84-5eda-8373-e982d1e30c54 | note | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
1d5dcf76-3f19-50ad-be3c-17d7b1d26c59 | note | Acceptance / Conformance Criteria - Engineer approval AS/NZS 4129
3b99f7aa-8f17-5d84-9c92-0ddd47b25fdb | note | Standard / Specification - PS-22.4.2
01750003-9a04-5859-9da6-8246f66d023f | note | Verifying Document - Delivery Dockets
8649e11e-b767-502d-9874-7119a009b688 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
ee6fb2ba-a039-5781-9e1e-ebfea7e38f49 | note | Verification Activity: Activity - HP
bf6f2590-8b10-51a9-93e5-a72d985c1e0f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
44ddedee-2ee7-5d54-a5be-aad748083da7 | note | Verification Activity: By - ENG
6ac8ae85-d4c0-4583-8680-4caeb57e222b | signoff | AUTHORITY HOLDPOINT
0df65c4e-0276-4d56-8a3c-d0ce86257032 | checkpoint | 3.11 - Pipe and fittings/bends
ec8e628a-33b2-537b-972b-ed5b77a63ab9 | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
4cc4541b-7c8c-50ce-bb3a-dcca6988a627 | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
2d35e349-1efc-501a-90c8-e5ff1c3840c2 | note | Standard / Specification - Design Drawings
b2f521c0-2759-5ffe-9a5e-0b16e992ba1f | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
80024508-7f29-5602-94ad-026344b1990a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
4436ea29-a346-54ba-8145-fdbf506e112c | note | Verification Activity: Activity - H
9e455e0b-4965-58f0-b781-4ac14da3fad7 | note | Hold Point (Internal)
582bb970-d952-5fad-a78e-ff847c8d16fc | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
b6aa8341-a322-59f1-b157-a1a8bba5d562 | note | Verification Activity: By - PE/SE
ccff0afa-a8f2-4c39-a283-1eddbd6cffdd | checkpoint | 3.12 - Fittings
1493d7a4-5f39-5780-9d0d-033da4ce994e | note | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
ae239dd4-b2ce-50d2-9229-62eafbbe70f8 | note | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
8152d7e4-f84c-51c5-a9c5-00dc7b29f52f | note | Standard / Specification - PS-22.4.2
51d7deb9-7aaa-54b6-850f-58cb27d288d5 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
f81062b5-60f9-5efc-bf7c-834a86b65488 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
ba09ad91-4754-5863-86fa-bfed7c802bac | note | Verification Activity: Activity - H
8a1d79cb-b2a5-5961-be8d-118a65f2c847 | note | Hold Point (Internal)
a73e061b-8ab2-503d-8c11-3221d7eabf75 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
bce8a403-b104-5a4d-8f08-a16c0245e055 | note | Verification Activity: By - PE/SE
cf3570d8-0419-4195-bfb7-26a47c3cc028 | checkpoint | 3.13 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65)
71b0c94c-cd4b-5bf9-bb6e-1d17029a952c | note | Detail / Activity - Confirm Specification and material in good condition.
f1da2f60-4ced-5fea-ab38-71fff0ce6c0c | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
ce261adf-71df-5f0b-8c41-7fb8e412dc01 | note | Standard / Specification - PS-22.4.1
6bdc787a-4438-5844-bce1-e88aa9764b67 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
e935b14e-48b9-538b-8c03-d91c9a38a715 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
535daf5c-3f03-5ec9-bb0b-e82e000c5fcf | note | Verification Activity: Activity - H
97ff45f9-3110-5e5b-9f96-779857b37794 | note | Hold Point (Internal)
a699704e-d525-5553-aa47-c7544486280a | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
cbd5d228-6aef-5c69-b64d-d5288d78b909 | note | Verification Activity: By - PE/SE
0b257daf-3699-4564-8409-291a11d82a00 | checkpoint | 3.14 - Bidim/Geogrid
2b94d4cb-7776-54a5-a073-68a1af7e569e | note | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
5c7716e5-e053-50d8-bfab-6abf76a3f3cd | note | Acceptance / Conformance Criteria - Site Engineer Approval
9dc66696-c9ba-588e-828c-b9e26014760e | note | Standard / Specification - PS-22.4.1
c20eab1d-3f05-5011-8e41-4555f45cae91 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
e2613fa8-527d-5b37-9767-b94f49fd0921 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5642b7a3-a384-540e-aa93-993970f8ce5f | note | Verification Activity: Activity - H
34514308-70e5-584e-ac99-f3d51abc7f27 | note | Hold Point (Internal)
4acc8219-7939-572a-a766-20b7ea07a5d4 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
b9981926-273a-5cc4-8871-c5012758eb8d | note | Verification Activity: By - PE/SE
b4307277-a8a9-4be9-bc1a-3290fa3d5314 | checkpoint | 3.15 - Waste Water Manholes
33f99b16-6740-53b1-918d-694951ed8d0b | note | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
5b3c8640-21ae-5236-b651-c4bd33eb59fb | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
86394223-cd4f-50a6-80d1-b221e69e9b38 | note | Standard / Specification - Design Drawings TCC IDC DS 6.5.12.1
429a10bf-ca62-57e5-8a9e-a5ee9c759d5d | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
2cfa7d37-056a-5bc7-ab6e-830f4af5e772 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
6b61072f-4a85-5944-8471-5986e260bacd | note | Verification Activity: Activity - H
eb7936da-74d7-50a5-b6ec-b9a1d85f1961 | note | Hold Point (Internal)
774dfc90-de16-54c2-a498-c472428f3686 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
1308a29a-c84f-5663-848b-37815141fe76 | note | Verification Activity: By - PE/SE
ea70837c-1d95-40cc-badd-68abafcb9aec | checkpoint | 3.16 - Reinforcing steel (manhole ballast)
3d25f628-f863-52d8-8cd9-3ba97c4a0638 | note | Detail / Activity - Manhole ballast reinforcing steel.
32a9bc18-5625-5a9f-8f92-ca3d39678231 | note | Acceptance / Conformance Criteria - Grade 500E, Confirm the class and type as shown in the drawings.
6eab4f4f-3ab6-58d0-8a95-5dc56b733357 | note | Standard / Specification - AS/NZS 4671, PS 22.6.2
8989d817-d433-5c66-aa5c-a1b1659915cf | note | Verifying Document - Material Certifications. Delivery Dockets
c568e959-2f5c-5bc2-927d-345a5e51a702 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
f3013721-c1dd-59dc-a11f-8fa86e3d7683 | note | Verification Activity: Activity - H
a1e28bb9-0d51-5537-8db3-13d2c1af52a2 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
efbc9e37-d6ee-5a19-a7e0-7a24d3cd9baa | note | Verification Activity: By - SE
5db60d28-7fa6-4b7c-b325-43ea2eb1cfc4 | checkpoint | 3.17 - Horizonal Directional Drilling
4f35a67f-76e0-5134-a2a4-698d66e1821d | note | Detail / Activity - Detailed methodology of directional drilling
d7317ba1-f22d-517c-9617-996f59490fe9 | note | Acceptance / Conformance Criteria - Engineer Approval
c2f46e77-e35d-5c5b-ad58-76768efd4749 | note | Standard / Specification - PS 21.6.6a
6f859094-aa07-58ed-8db8-74e76de194e5 | note | Verifying Document - Engineer APPROVAL
f799be10-395e-5177-a88e-340f82be18f4 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
39231bfe-187b-5bf5-bd63-ce3707734993 | note | Verification Activity: Activity - HP
e0424958-b971-59d2-a887-fae5a9a5dba4 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
22917363-e3bd-5060-827e-8c261c672f92 | note | Verification Activity: By - ENG
5e556783-7dc2-492d-9e3b-5176b097a6e6 | signoff | AUTHORITY HOLDPOINT
dd606504-3c8e-4b66-a71d-b9aff05b1340 | checkpoint | 3.18 - Grouting Methodology
4cfd3dba-d429-5766-be12-68dcdbadc7d6 | note | Detail / Activity - Cement grouting the sleeve annulus
c9ed2d94-4363-5ce2-beaa-150648312d5c | note | Acceptance / Conformance Criteria - Enginner Approval
ca3c3a01-8864-55a1-ada4-b67d5ec4b4ae | note | Standard / Specification - PS 21.6.6g
f404d578-f87a-5da4-888b-f6816dbb0d4d | note | Verifying Document - Engineer approval
207972a8-4b8a-552c-a8bb-0f1cd793e74d | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
c5ac40ea-1d3f-5a9f-ba11-76aa053919c8 | note | Verification Activity: Activity - H
0cdaffe5-1f00-58c0-b739-0282a18af951 | note | Hold Point (Internal)
e0ff1453-39e0-5437-bb71-60a38f7ae1bd | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
2b55d413-c306-5174-978d-be5aa8b7e375 | note | Verification Activity: By - ENG
34da4da2-4207-4c1a-8c0b-d55dd96de899 | checkpoint | 3.19 - Pipe and fittings. Ducts
982d6c11-62bd-5d8f-af2f-906d9da80ee8 | note | Detail / Activity - Duct Pipes shall be of the 50mm
d41f93eb-7c78-51e7-8b68-91177577747f | note | ○ Ducts shall be high impact uPVC
8d469a51-fcb6-5baa-8bf4-acd85ab45d71 | note | ○ Duct colours shall be Salmon3
0ef3b6c4-292b-586d-bb7e-2984c2725b4a | note | ○ Duct colours for the different Utility Structures must be in accordance with the guidelines.
1ab18daf-1997-544f-be18-caa664128af8 | note | Acceptance / Conformance Criteria - Duct Pipes shall be of the 50mm
7b915fc9-baa2-58cb-9c50-e2b88b5767ca | note | ○ Ducts shall be high impact uPVC
89370868-14f3-5861-86b7-6aa7adf72f1d | note | ○ Duct colours shall be Salmon
0cdcce6a-3852-5f3c-be7b-a46d98d1a2eb | note | ○ Duct colours for the different Utility Structures must be in accordance with the guidelines.
7ebb7706-88be-5b8d-9900-c1291af8eba6 | note | Standard / Specification - PS 25.13.6 b)
e0d8e223-4039-5cca-aa7f-a18b928e400d | note | Verifying Document - Delivery Dockets/Material Certification
958d5777-6c53-523b-ae7c-3818f18b772a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
f20ab41e-fbda-5334-adb3-3988b8b153d8 | note | Verification Activity: Activity - H
f7678ce4-7858-55bf-b4d7-a514fc846403 | note | Hold Point (Internal)
dd2947f5-fbfc-5d00-b4aa-a864fc5ea315 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
e800f013-f027-5c6e-8336-31d355b62313 | note | Verification Activity: By - SE
cf6c00b0-7aac-4105-b8ce-5e643aee402c | checkpoint | 3.20 - Pits Covers
3322073b-cd5e-5bde-9db4-28c7cc926eff | note | Detail / Activity - Jointing and pulling pits shall have slip resistant surfaces complying with AS/NSZ 3661-1-1993. the cover set load rating shall be in compliance with AS3996.
ca711f77-43c8-537f-b310-1fd1c7118269 | note | Acceptance / Conformance Criteria - Class A-10kN loading - footways and areas only accessible to pedestrian and cyslists.
af385ab4-318d-527f-b23c-9942445b510a | note | ○ Class B - 80kN loading - footways that may be mounted by vehicle or livestock and light tractor paths. (Light duty)
7d9803f1-840c-53aa-85c0-3746094c8f79 | note | ○ Class C - 150kN loading - grass verges or other areas open to slow moving commercial vehicles such as tractor mowers etc (medium duty)
67597efe-c295-5c8b-8b19-763291f787a8 | note | ○ Class D - 120kN loading - Carriageway of roads and areas open to commercial vehicles (heavy duty)
6dbebfc3-6e56-5a37-86a7-837f10cf1ea0 | note | Standard / Specification - PS 25.13.6 c) AS/NZS 3661-1-1993.
543515f0-2e80-51f6-8261-20b0ea0e26a9 | note | Verifying Document - Material Certifications. Delivery Dockets
35b67f44-4f86-5c25-9e14-1a5e8e801b40 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
832b5314-8817-5b0f-8266-2307d8ae7f93 | note | Verification Activity: Activity - H
b90cb7cb-dd64-5cca-bc0e-24a4d3bfb124 | note | Hold Point (Internal)
44aaefd2-3f53-5d0e-a4cd-ceaae20c32f1 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
0b9949f8-1dea-5162-b837-ab4c241b8bb4 | note | Verification Activity: By - SE
20edc35f-d0e5-4489-a62f-e579cddc0b48 | checkpoint | 3.21 - Butt-Fusion pre construction weld test
b5a61ac2-ee82-5ad5-bac4-10c8a78c94fa | note | Detail / Activity - One weld on the most common size of pipes used for the project.
2f73688d-33ba-5f58-b690-ada2015559cc | note | ○ One weld on the thickest wall (highest PN) pipe
3c5d4ea8-4232-5116-b751-6ce4ab49769e | note | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode.
cfe191c2-129c-5227-ad38-f263c3f83695 | note | ○ WMS Report
fef72b9b-0b01-5a0d-b09a-1dbd97cbfd22 | note | Standard / Specification - PS 22.9.6 (a) ISO 13953 Standard
6b202172-3406-55a5-86f7-30d7289c40a5 | note | Verifying Document - Visual Inspection
2d2ac486-3c1d-510f-af9b-11983afd5aa1 | note | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
167a7163-575e-588c-8ed7-5a647750224c | note | Verification Activity: Activity - HP
b2e6f79b-cc22-5269-af97-abda57ee81f0 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
faaf767b-86b5-5831-9832-450674440c2e | note | Verification Activity: By - ENG
5eb88265-92f4-41c3-bae8-c74a9d303ccb | signoff | AUTHORITY HOLDPOINT
35d98ded-63d9-45cc-aac3-9d07d92da11f | checkpoint | 3.22 - KWIK Spacers
afdf3049-7fc4-5b25-aa94-e97826b882ed | note | Detail / Activity - Confirm Specification and material in good condition.
95dc65ad-94b8-5daa-ac96-03143739bfd4 | note | Acceptance / Conformance Criteria - Installation: Centred and restrained
1c1b05b8-9251-59ac-b02e-7c410830515d | note | Standard / Specification - Manufacturer’s Installation Guide. IFC Drawing 0312
3bbf42cc-cf7a-54e2-a381-3750e92269d9 | note | Verifying Document - Photographic Evidence
a218e362-14d8-52d4-8f22-691d066c4d51 | note | Testing Quantity Required (based from schedule qtys) - Every spacer
3e1d1f3c-46bb-5c75-a8b2-f9321456d65b | note | Verification Activity: Activity - W
674315e3-7e9f-5287-a18f-0b85540b521b | note | Review of text reports/records or other evidence of compliance
ee21b6d7-26ff-5dfa-9fa9-ae8dfd90eeb6 | note | Verification Activity: By - SE
d13ac7f0-808f-4084-a2d1-ebf91033fd22 | section | SECTION 4 - CONSTRUCTION - WASTEWATER PIPELINE - Excavation and Laying
84433016-943a-4b93-b5d0-2531787b2443 | checkpoint | 4.1 - Foundation Compliance
61387c7c-adf2-5b0e-a142-a93b40156adc | note | Detail / Activity - On Granular or Cohesive Material
9699ab58-ad42-5451-b331-ab607a5015c2 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
cc41d7fd-0350-538a-a3a2-4c72d8320ea9 | note | (Or)
d00c6075-1f2d-5c9e-86ec-5d964f7ea79f | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
879e6056-62e0-5d7f-ba00-484b2f84db89 | note | Standard / Specification - Appendix V Table 21:11
a5e2af99-26f2-50c8-b4a3-f5429febf2a3 | note | Verifying Document - Scala/Shear test result
bcdcb509-2716-5c61-a8a5-9eb262fb9c49 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
f39d6efc-17eb-5f09-9175-9e28fcce8b97 | note | Verification Activity: Activity - HP
270c7022-9904-5025-941f-ba26ef0f8a83 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c537c556-0c3f-5531-be9d-0f4c43a153f1 | note | Verification Activity: By - SE/ENG
8c2d945e-c68d-4edb-a497-b91344ece899 | signoff | AUTHORITY HOLDPOINT
29168614-babb-4aef-ac95-7ede00d53396 | checkpoint | 4.2 - Undercut approval
7ee77645-21e6-5e5a-9e31-b9ea8851dac9 | note | Detail / Activity - Trench Foundation
fcb54c2f-188a-5bdf-a9ff-a7fa07dc3d33 | note | Acceptance / Conformance Criteria - 300mm Max cut
36984d03-dc4e-5355-9f04-ac6c6742d921 | note | ○ IFC Drawing Sheet 320
b6289ba0-c703-5ed9-a093-2fc34e1be95e | note | (Or)
af67cf6d-5e10-58a8-9ba0-84dfd7a756c7 | note | ○ Engineers approval
952a99f5-8a5b-529e-8ccc-c2d719328a46 | note | Standard / Specification - IFC Drawing WST 0320. AS/NZS 2566.2/2002
1c3c5972-339b-5178-bed9-55f0a7c8360b | note | Verifying Document - Lab Test Report / Wastewater line record
2ab23b07-b886-5c6a-a028-cabefc7c93b4 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
cfb1101d-a391-5a3f-bb35-e5927ac85f21 | note | Verification Activity: Activity - H
0edd02b2-48f2-5c73-a7a1-72996fc4d31e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
57ea7e6c-3456-5a9d-af70-0d53dd851e4a | note | Verification Activity: By - SE/ENG
b53a83d3-273f-43a1-a1b8-c364b7269680 | checkpoint | 4.3 - Undercut Backfill Compliance (PAP5)
24a532aa-e79d-5fbe-a7df-58c7af6a39bf | note | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
35376820-7c18-57a3-bff4-2f56e766f0e0 | note | Acceptance / Conformance Criteria - Visiual Inspection
210664a8-5aad-5ca7-aeae-afa77a6f3e5c | note | Standard / Specification - IFC Drawing WST 0320
56a234f3-f48a-5f51-aca8-20784e19aa6a | note | Verifying Document - Lab Test Report / Wastewater line record
4f02b4cb-f3fe-5aea-a266-2fea616d4843 | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
44493f0c-9ca5-51e4-9d47-b28d42c54218 | note | Verification Activity: Activity - H
b0eb5ba9-ecd0-5d14-bf69-60bd7fbf16c1 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c3d797ac-d24f-5471-a37b-c5b2fb454e09 | note | Verification Activity: By - SE/ENG
0f30c421-6bc3-4fdb-87f1-e5f10195dd8a | checkpoint | 4.4 - Bedding Zone Compaction Testing
29fb19b5-ee21-5f2f-a89c-d7b6a7551436 | note | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip)
9fdafc1b-32b5-56b5-9b8e-7fd4db6bee25 | note | Acceptance / Conformance Criteria - Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench.
08b9a159-8658-5351-a69c-b70a9c17e79d | note | ○ Minimum Compaction - 85%MDD
268dbe0d-c3e0-5a78-b295-5840fb7d239d | note | ○ Paeangaroa Sand: clegg of ave 9 CIV and min of 7 CIV.
1d2532d6-143d-5ead-844c-943c7e6d6276 | note | ○ Wilson Sand No.2: clegg 4 CIV
84440ab3-aef5-5ffc-8770-aaaf79406d92 | note | Standard / Specification - IFC Drawing 0320-1 AS/NZS 2566.2/2002
2d5247f8-1c70-53c9-963e-3a3a90189716 | note | Verifying Document - Lab Test Report
ac0751b7-be44-5c05-b281-434963ea7956 | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification.
c29ce232-b137-5058-a9b4-95e571928e66 | note | ○ One test per 20m evenly spaced intervals.
34884c85-2e94-5e62-a0dd-2ecfdbbb7163 | note | Verification Activity: Activity - H
d2a13075-7f2f-56d7-a50f-5b50ffa42a26 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1a54a831-647a-5a6b-adda-2273a386abf8 | note | Verification Activity: By - SE
cfb8b49a-0743-4222-ac92-697f99c8f973 | checkpoint | 4.5 - Laying of Pipes
208c0f49-36cf-559d-ba89-d0192c0172cf | note | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
8c117578-2366-5099-8286-e541ec3631a0 | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
0192792e-0516-523f-b4ae-9ecf40a05aac | note | Acceptance / Conformance Criteria - As Per Drawings.
1343ac9f-474a-5c88-bf7b-c894e9a47926 | note | ○ Facing upwards
538f7bdc-f4ac-56e1-8800-c424d91b0e4f | note | Standard / Specification - PS22.7.1 C
cef57648-1fb5-519e-bd1f-d0d4673751a7 | note | Verifying Document - Visual Inspection / Wastewater line record
b647f799-b093-50f6-abc1-9aa7b3287ebb | note | Testing Quantity Required (based from schedule qtys) - Every Line
4d59582c-02fd-582a-8403-0534f69c2b46 | note | Verification Activity: Activity - H
e9d5d67e-1e6f-53fa-aad4-3fafcc25ae90 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
59878058-9a0f-5463-9bbc-2b055a861f60 | note | Verification Activity: By - SE
bced5107-55db-40c7-b43e-4aeeac8517e7 | checkpoint | 4.6 - Pipe Installation on Curved Alignments
e675e959-9bba-5004-9cca-81687acfac9d | note | Detail / Activity - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
5908f31f-c4fa-5eda-981e-a07b35b7cff8 | note | Acceptance / Conformance Criteria - AS Per POP 202
d62785df-9d79-55aa-b08b-b9b4b866e8ff | note | Standard / Specification - PS 22.7.1 D
548bcfa9-b48f-5218-b65b-2b2533cd23ff | note | Verifying Document - Visual Inspection / Wastewater line record
7fc129a5-bf03-5a0e-8e1f-1fe29351d88a | note | Testing Quantity Required (based from schedule qtys) - Every Line
e32fada7-217a-54bd-b7d4-81fd1b203419 | note | Verification Activity: Activity - M
a0864ab3-d8a6-5454-8066-b421f8ee2cf4 | note | Monitor on Random Basis
8391e3ce-4b3f-531a-bb89-c7434cd5014c | note | Verification Activity: By - SE
3c1f082a-7a14-4c18-b562-dd02b79a6852 | section | SECTION 5 - CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE (Joint and Connection)
646325e4-c475-41e6-8b3f-ba212bd58d5f | checkpoint | 5.1 - Flanges
57d78d11-fe59-5483-8fa7-7a33172798a3 | note | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
c169bfc8-f2d4-5a91-910c-0cd7e243c723 | note | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
bc7c326e-371c-5dca-ba30-52f173312274 | note | Standard / Specification - PS 22.7.5
c7c124cf-a0be-54a2-ad4e-24e2b37200c5 | note | Verifying Document - Visual Inspection
8d9b91fa-42e2-593c-ac1a-14106ec68884 | note | Testing Quantity Required (based from schedule qtys) - First flanged joint
bb226620-507d-5756-abc8-1bd52c63697a | note | Verification Activity: Activity - HP
df0c40ac-29a1-53fd-b5cc-d0df7f09f695 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f62510ed-ef9f-5461-8e85-f55f97651a7b | note | Verification Activity: By - SE
87bb795f-bb71-4ade-9e6a-c84f2bc3ed90 | signoff | AUTHORITY HOLDPOINT
7d943fcc-dcb4-44cb-9bee-3fdabc4b2423 | checkpoint | 5.2 - Bends
776657ad-0797-5d2f-92be-083f9b4b0f49 | note | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
5273303f-2f9a-57d0-898a-1590432b0d61 | note | ○ Fitting must meets the same PN rating as the adjacent PE 100.
efb295c0-94bb-5483-8795-693f1d188e3a | note | ○ Fittings must be suitable for producing the joints shown on the Drawings.
83918b41-5942-56bd-ab11-a105bb79b54c | note | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
f959d4d6-26ba-5885-8910-ea21e47469b2 | note | Standard / Specification - PS 22.4.2
4a10fa91-6d11-5886-b7a3-e1bb3d20a71e | note | Verifying Document - Visual Inspection
de18f583-aea6-5ba2-a5ae-86f4a0b8b772 | note | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
311f6310-25c7-5a1a-a64c-1a21c13ab81e | note | Verification Activity: Activity - H
8e2e02ed-b6f1-5261-bc81-e52c7cfc174e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
182d46fa-bd64-5423-99a6-f7dd6a324172 | note | Verification Activity: By - SE
b00038cd-a759-4288-bc8e-4c030ef41694 | section | SECTION 6 - CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE INSTALLATION - Directional Drilling
ceb7ea97-55c7-4bbc-9a07-0ce999e93fda | checkpoint | 6.1 - Check levels while drilling
f2d56429-fca9-593e-95a8-90e5b2e8f9ec | note | Detail / Activity - Inspection of Pipeline Inverts
4e794a4a-8f5f-58db-a0e3-69f263ee53c4 | note | Acceptance / Conformance Criteria - Vertical design Setout:
7b001664-ebcf-56cc-b424-d2441c88858f | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
0c72a8d1-d997-58fc-a0a1-c6d3e8afff55 | note | ○ Pipes > 1% grade: +/- 20mm variance
65a652d2-d3ea-5fbf-a688-0c9997b7e2f2 | note | ○ Horizontal design Setout: +/-30mm variance
9ffecd18-8007-55c2-97e8-59af9bf09f9b | note | Standard / Specification - PS- 21.7.6 Table 21.15
b03b61e8-1935-5c05-93a5-bf00d84d3c30 | note | Verifying Document - Survey Data / As-built record
f895368a-3db2-57e6-ad45-1c89ba410505 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
ccd18d9e-427e-51d9-bb31-42ad2abc187c | note | Verification Activity: Activity - HP
79befb83-017b-5500-9718-bcfd85f84c83 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f29db70c-d2c1-55f3-a3e4-c3186546c753 | note | Verification Activity: By - ENG
f8c5fe78-b1be-4ba5-9589-aba0b813d789 | signoff | AUTHORITY HOLDPOINT
233b7fdf-092e-48f0-a796-fe23fc4956ab | checkpoint | 6.2 - Drilling Fluid Mix
19de4f6e-7bd9-546f-a9e4-83a9b8f8920e | note | Detail / Activity - Viscosity record
c7c832a1-21ad-5d55-8862-bde93da302e1 | note | Acceptance / Conformance Criteria - Viscosity record
1fa37813-0b2a-5d9d-abe9-aa472b0410f0 | note | Standard / Specification - PS 21.6.6
c79e845b-9a15-5063-ad04-900ab678b416 | note | Verifying Document - Viscosity record
d62f6d0e-7daa-5150-9911-4c0ace4b3922 | note | Testing Quantity Required (based from schedule qtys) - Every shot
af863a97-8098-5bea-ae23-bfba107db080 | note | Verification Activity: Activity - HP
7589735d-2aec-50e2-8b7a-eb70a088228e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
543e7dbc-b33a-57da-a7ee-cef8c26887ba | note | Verification Activity: By - ENG
4b8f20ec-27a2-4ef5-b298-6b606c43fc26 | signoff | AUTHORITY HOLDPOINT
69eaad1a-a8d2-4ac5-8ba8-4b3b07c7d488 | checkpoint | 6.3 - Correct Reamer used
d39a1952-84de-5ac7-8c7e-3c88de6f41d1 | note | Detail / Activity - Reamer size to confirm on site
030ee385-b615-522c-92c8-258fecc51025 | note | Acceptance / Conformance Criteria - Reamer size to confirm on site
db410fde-bf3c-5347-af78-f88223987fbc | note | Standard / Specification - PS 21.6.6
5a9c6db6-ecfe-52eb-afcd-c30f853e679f | note | Verifying Document - Visual Inspection/Photo
fd8c4789-b308-5b4b-bdd6-a435ca3305cd | note | Testing Quantity Required (based from schedule qtys) - 1 per drill shot
e654fc8f-0bba-5053-aa48-9546c9f6d09e | note | Verification Activity: Activity - HP
5b2a630c-8aba-5f79-8b97-2783780d3ac8 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ad571fc6-dfe9-582c-8505-98bd9bf47eda | note | Verification Activity: By - ENG
86f15288-377b-4dd2-b420-fd7d6c5736ae | signoff | AUTHORITY HOLDPOINT
8b0764b8-4453-4a9a-aab2-d8653ecab2fb | checkpoint | 6.4 - Pipe Damage
0fa39ff6-8eaa-5767-b2ed-7f5310d5c8db | note | Detail / Activity - Damage <10% of wall thickness
b4c84162-87ad-5802-8927-0327f5a0cc39 | note | Acceptance / Conformance Criteria - Damage <10% of wall thickness
c531d902-e01e-550c-890b-117c6d8b6910 | note | Standard / Specification - PS 21.6.6
3db5985b-4d42-572b-bc0c-81fce153b7c2 | note | Verifying Document - Visual inspection
55931d68-37ed-5e5f-a76d-85da616b1f43 | note | Testing Quantity Required (based from schedule qtys) - Each pipe
08962be1-e454-50e8-a5f7-2bcd2d5341ec | note | Verification Activity: Activity - HP
76179ab3-a7f9-554d-ad1e-e37dcea80638 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b47fab87-2765-5e1b-8173-dafde531ea70 | note | Verification Activity: By - ENG
e58a9c79-c19e-4756-8d7c-cf1f2a9a68fb | signoff | AUTHORITY HOLDPOINT
b8fe4863-c468-497a-82f4-e2d4b48c27c1 | checkpoint | 6.5 - Tracer Wire
db9d7a71-78dc-5b67-99e3-af76cc73a355 | note | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
c417c2ed-640b-57cf-a3b4-7844a6e1e549 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
021fe445-e427-52d6-85c9-f61f06a1158d | note | Acceptance / Conformance Criteria - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
b25afcf7-8770-59fe-9679-60e823013a23 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
564f41df-bc4a-57d8-b5f6-6357a5649451 | note | Standard / Specification - PS 22.7.3 a
d8ec58f2-4d04-550f-9069-3c618b0d1791 | note | Verifying Document - Visual Inspection / Wastewater line record
f8b5079a-d289-57f3-9341-9cd3e479538f | note | Testing Quantity Required (based from schedule qtys) - Every Line
f37b9cfb-8e1b-5b90-a632-bb11a0df9638 | note | Verification Activity: Activity - H
1ab472e7-c40d-56f4-b120-7b1c60db1364 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
98d2ee6a-b307-5614-a9f5-c4e58a844330 | note | Verification Activity: By - SE
a6e51d6c-2b50-4ebb-9280-c296c33f24fa | checkpoint | 6.6 - Drill Report
63074e80-381a-5b87-972f-b97bd378ae2e | note | Detail / Activity - Drill report to be submitted
2f2201e4-d1af-5546-a657-eef07648ec57 | note | Acceptance / Conformance Criteria - Drill report to be submitted
40314102-0426-56cc-9e49-f32f395160ae | note | Standard / Specification - PS 21.6.6
e0373849-b3af-5f8d-94b0-9e179e587c60 | note | Verifying Document - Report
c0abcca9-99f4-59b0-be96-f8dcdaede638 | note | Testing Quantity Required (based from schedule qtys) - Every Line
c560f9e0-0c58-5aaf-ab57-6e8807626adb | note | Verification Activity: Activity - HP
eda5f747-d93c-5953-9d15-9bbf62c31955 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
33e56700-bd1c-59b8-89ba-c1cd368f42de | note | Verification Activity: By - ENG
53161c60-99df-4fec-b04c-2e64279e37bd | signoff | AUTHORITY HOLDPOINT
752ee806-aaca-46d0-ad84-91d2c6fd7b13 | checkpoint | 6.7 - Settlement monitoring and ground deformation (Baseline measurements)
401cc929-b1ce-5ede-838b-4f6fa651b342 | note | Detail / Activity - Topo survey completed before and after drill shot
97ccd1cf-61f8-505b-b949-cb3b0e3c30d6 | note | Acceptance / Conformance Criteria - Topo survey completed before and after drill shot
6adccf31-31bf-5069-9e9e-dbfe60ea0fc9 | note | Standard / Specification - PS 21.6.6
7eef74ea-2d46-509e-a4e3-c492dac5b507 | note | Verifying Document - Survey data
eccf86bd-159d-5dc7-a9d6-d7425b708f21 | note | Testing Quantity Required (based from schedule qtys) - Every 6m
6b740460-a178-5fa5-9a2b-c0e6159b28e3 | note | Verification Activity: Activity - HP
b2be8776-0e90-53bc-ad87-1767b95040d8 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3dbf2c40-65d5-51bb-94a6-441a4f495367 | note | Verification Activity: By - SE
880234c3-d2b3-4700-aeb8-cfc4a4d12410 | signoff | AUTHORITY HOLDPOINT
7e45a594-6e74-4358-9a7d-38298eeb546e | checkpoint | 6.8 - Cement Grout - Annulus
be2f9e83-6772-5bbf-a912-b2f81c24814d | note | Detail / Activity - The sleeve annulus are to be cement grouted after installation to prevent settlement.
2242b8de-fc29-53b8-8be6-845a84cd7531 | note | Acceptance / Conformance Criteria - The grouting mix is to be:
9e08f075-ec77-54a5-adc9-7e40efe99946 | note | 1. 1:1 Sand/cement ratio 1 : 1
a559ab0a-03be-5b69-adf1-6b4f2aba45e8 | note | 2. Water/Cement ratio 1 : 0.67 by weight
36dd8a37-48ca-5891-bfbe-90dfcc886ba7 | note | Standard / Specification - PS 22.5.8b
00863199-678d-54a8-ad84-af46f649889c | note | Verifying Document - Visual inspection
5d429915-b8b2-5d7d-bdea-417cff124b7c | note | Testing Quantity Required (based from schedule qtys) - Every Grout
f0c5f276-21ee-556c-b2b1-ca207e4f25e1 | note | Verification Activity: Activity - H
1890383e-e3ba-53b6-9e28-4496df5f04bb | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
729a8085-5fd4-58ec-8d28-ab583bf34c9c | note | Verification Activity: By - SE
f36ca60c-6e80-46d6-bbff-1c9ee3c44e2f | section | SECTION 7 - CONSTRUCTION - WASTEWATER PIPELINE - Inspection
a3f79577-d984-49c7-9910-c22b0fe313ea | checkpoint | 7.1 - Pipe Inspection
20f8933f-e4ad-55ae-8d4f-13f1fcab4fbe | note | Detail / Activity - Inspection of Drainage line
2b486f2a-c101-55a9-b76c-87e179a79e36 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
146a54de-dccb-5e1f-aa7f-a6f76531985a | note | Standard / Specification - Internal
96bd3318-a8f7-57f5-a1fa-ed541c4702e9 | note | Verifying Document - Wastewater line record
05f7aac1-3948-594e-a162-67298edff070 | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
c3d9a883-9724-5856-8771-4898d375fcba | note | Verification Activity: Activity - I
4e898c83-0786-548c-b94c-8746b21f9886 | note | Formal inspection activity to be undertaken and recorded.
245c5ea5-d96e-5650-b8c2-848c981b170a | note | Verification Activity: By - SE
b190c550-0a1c-4bf3-afa2-9aceb145b984 | section | SECTION 8 - CONSTRUCTION - WASTEWATER PIPELINE - Backfill
bafd6c4a-442e-4645-a12e-cb45ea02553f | checkpoint | 8.1 - Emebment Zone - (Side Haunch Overlay)
673761e9-97dc-59c6-b26f-ad78c0674681 | note | Detail / Activity - Granular sand backfill compacted in 200mm Layers.
27c1e29c-1f62-531d-8e03-97b868d43be8 | note | ○ NDM/Clegg Testing to be completed on maximum 200mm lifts of overlays .
60a7fd65-25d6-5bda-978f-fa436d607265 | note | ○ NDM BS to be Carried Out
c920cfed-50fa-5b8c-a2f0-ebb96acad54f | note | Acceptance / Conformance Criteria - in 200mm layers.
dceda96f-bca3-5ab6-8e4b-021fb68c4d3d | note | ○ More than 85% of MDD.
6641906c-1ecd-5876-9de5-a2b49225a9b3 | note | Standard / Specification - IFC Drawing 0320-1
dfe80ae1-4a61-5f07-81a8-e9ba95876c9b | note | Verifying Document - Lab Report / Wastewater line record
047f4177-3acc-51dd-9b88-8b3ba63d1ebb | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals.
41104a74-b030-5b98-8d7c-db77a1f24ee8 | note | ○ 200mm lift
0b3778b5-9826-5cb3-bc3e-253f44ed1805 | note | Verification Activity: Activity - H
5eff9637-3c62-58b7-896e-4cbb876cfb5d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
69a5ded6-b763-5bd8-9c2d-f11507c39367 | note | Verification Activity: By - SE
9ccd4407-7b04-45d6-84f4-253f78027804 | checkpoint | 8.2 - Pipe Markers
4b190adb-13a6-5b4d-ba69-c2998eaf8451 | note | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
590b01cd-387a-5cc8-957e-266b88984ccd | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
bb1dae33-a819-5e2a-86b4-2c7c12badba8 | note | Acceptance / Conformance Criteria - AS Per Drawings.
402f58a3-097f-53e3-aa02-ab422586e0de | note | Standard / Specification - PS 22.7.3 a
6dfd348f-4e38-5fa3-b017-21efa15a402b | note | Verifying Document - Visual Inspection / Wastewater line record
d3d27dc8-9fed-57f5-a60b-dcf1d26a2d57 | note | Testing Quantity Required (based from schedule qtys) - Every Line
55c92ba9-1abd-539e-bfc1-dacdee32aa0a | note | Verification Activity: Activity - H
299220e4-8a4d-5455-94bc-60f732c5f2a6 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
369fd1d0-ec13-552a-b64b-c3015bff701f | note | Verification Activity: By - SE
aff642fc-32f6-42c2-bae5-29d46fb2cfaa | checkpoint | 8.3 - Backfill Compaction Testing
1cbade39-3baf-5224-a2a0-2b5c1e7e8cc9 | note | Detail / Activity - Backfill Compacted in 200mm Layers.
885efdda-910b-569f-a806-d9bf336795d8 | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
63426a3d-153b-5b64-8121-a1d162f9d0f6 | note | Acceptance / Conformance Criteria - GAP65/AP65 or site won material Backfill Compacted in 200mm layers.
18258970-2c47-5b45-ae93-9140ba1335ab | note | ○ Testing to be completed on maximum 200mm lifts of backfill.
87707261-8e24-50b8-9b78-05a7364147f3 | note | ○ 95% NDM on Shared and Carriageway.
ea2aae52-9aee-56b7-a448-2772fad47b8a | note | OR
1bb1d68a-ea2b-58c6-a725-84057720f131 | note | ○ 25% CIV
529d22f1-4740-5bce-b721-eb40285a5e65 | note | ○ For site won: Shear Vane min 125kPa
f0ba7475-4cbc-553b-bc81-134300111946 | note | Standard / Specification - PS- 22.13.5 NDM Standard 25832 NZS 4402 Test 4.1.3, IFC Drawing 0320-1, PS - 16.5.5
c36b9c33-ef2d-5e49-9975-39b9843168d2 | note | Verifying Document - Lab Report / Wastewater line record
def51c3b-0bf6-5ec5-95ed-b5c8a8317016 | note | Testing Quantity Required (based from schedule qtys) - As per WW Specification.
027afe5e-982c-5e4f-b8d6-8176b3f2efa7 | note | ○ One test per 20m evenly spaced intervals.
0a868cd8-6b5d-54f2-8175-a608302fe62f | note | Verification Activity: Activity - H
e21c07f8-cb23-5735-8219-ba4501d5af60 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1dd7868f-2763-5890-9096-7958a9cee288 | note | Verification Activity: By - SE
9cc6762a-556d-4d94-aa28-1f59d698026e | section | SECTION 9 - CONSTRUCTION - WASTEWATER PIPELINE TESTING
acaa9c60-8c49-4a9c-95c6-5c018ba7bb27 | checkpoint | 9.1 - Pressure Acceptance Testing (air)
0efd7a76-6292-5d41-b224-d2c60635dfc5 | note | Detail / Activity - Backfill/cover with embedment before testing
4c2ec2a4-dc5c-5086-b180-1fd72f9039d3 | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
4a83d502-b448-51b2-ab71-cf5251279e88 | note | Acceptance / Conformance Criteria - Wastewater Rising Main Pipelines – 800kPa
ae3ce805-0510-5934-af06-e6f787bd4fad | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
419e7d3c-5305-51bc-9d26-8afb19fc8039 | note | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b), PS 22.7.15
b157cd45-c2b7-58f3-a055-494f4ff5e781 | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
db7d752d-2d00-5260-9d37-7bfd57f7b4d1 | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
8d534cb4-534b-5cdb-b959-3266296ab2b6 | note | Verification Activity: Activity - HP
052b9fa6-f348-59da-a120-01cc5acf43b6 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3e3c144e-e22e-5fd9-9027-b5ed77bd750f | note | Verification Activity: By - ENG
10e4697d-ff48-4544-8dd2-90140ae2142c | signoff | AUTHORITY HOLDPOINT
01384e61-b488-4120-a61e-59a664fbf50c | checkpoint | 9.2 - Constant Pressure Testing (water)
f759ed03-0981-56cd-85e6-903fbfb25f5a | note | Detail / Activity - Backfill/cover with embedment before testing, plan for where water will be diverted or sent to
1f3e5381-b1cc-5618-8c53-3212f3d5353d | note | Acceptance / Conformance Criteria - There is no failure of any pipe, fitting or other pipeline component.
1bc4f51f-5289-517c-9c42-5a7427446778 | note | ○ There is no visible leakage at pipe joints or other fittings.
eedee6f5-49e5-54e3-aa71-ab69ad90ae3f | note | ○ The make-up water volume does not exceed the maximum allowable quantity as calculated. Q ≤ (0.14 x L x D x H).
958b61b5-b805-57eb-88c1-f206d24cc889 | note | Standard / Specification - PS 22.7.15
3c34f0bc-6a67-5575-a0e5-3dddb50b2d7d | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
f5c942c6-3c39-54f8-aa02-086be0ab15c4 | note | Testing Quantity Required (based from schedule qtys) - All Pipeline
963e2a22-d677-58c6-8302-6a7b054dda52 | note | Verification Activity: Activity - HP
060cb7e8-2ee6-50f5-a27b-6cf66619ab84 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
30a78802-706b-51cc-b4a9-884779821005 | note | Verification Activity: By - ENG
42da5f15-b629-48ed-93f0-8286358d7e4f | signoff | AUTHORITY HOLDPOINT
43074a8b-4f38-46e1-a4de-c2fd63c72b24 | checkpoint | 9.3 - Pressure Rebound Test
b434c568-f749-550b-a6aa-a14e192a76d2 | note | Detail / Activity - Backfill/cover with embedment before testing, plan for where water will be diverted or sent to
fe3e6886-f2b5-56a7-8422-ad9c5fd263ba | note | Acceptance / Conformance Criteria - There is no failure of any pipe, fitting, or other pipeline component, and
dae8348b-8ba5-50fe-833d-8928185961e8 | note | ○ There is no visible leakage at any joint or fitting.
f5ab19f4-f2dd-5782-b651-0d383654f1c5 | note | ○ The volume of water bled off (ΔV) is less than the calculated ΔV(max allowable air), and
068ef7d1-9f2d-5a77-baad-22bbfecf06f8 | note | ○ The pressure has not dropped below the rebound peak within 30 minutes, or
25de2f9a-59f0-5693-91fa-fdffbc847820 | note | ○ The test has been extended to 90 minutes and the pressure has not dropped more than 20 kPa below the rebound peak value after 60 minutes.
4465dde4-2dac-5607-a7d4-adfe9cbcd90f | note | Standard / Specification - PS 22.7.16 TCC IDC IT-6
9850036f-beb6-576c-bfea-8ae93b115ec8 | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
5c106ed1-4360-5f45-beaf-7d1d9223d30c | note | Testing Quantity Required (based from schedule qtys) - All Pipeline
e761723c-e09e-57b8-977f-1251358ed4a3 | note | Verification Activity: Activity - HP
cb983e2d-9241-5129-8504-111aa66783c5 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6ddcbe39-aa75-557b-8703-8dafca5b205c | note | Verification Activity: By - ENG
6aaa2f9f-101d-4c5a-ae24-c1afadc1e40e | signoff | AUTHORITY HOLDPOINT
89036666-6ba5-4a3a-91b7-a40efa9d3cfb | section | SECTION 10 - CONSTRUCTION - WASTEWATER Manhole installation
e97361bb-8218-4009-b668-ec6e0e00bfc1 | checkpoint | 10.1 - Foundation Compliance
9dbee6a5-cc4f-5c34-954d-cb77f8a13184 | note | Detail / Activity - On Granular or Cohesive Material
5e7a86c1-98a0-5460-a577-bed841b9bf0f | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
a81962be-3ad5-5485-aff3-9667d7ca4c6d | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
0eb8a7b3-2796-5c59-8065-105321303888 | note | Standard / Specification - Appendix V Table 21:11
08204518-4102-511c-9715-394b289a61d1 | note | Verifying Document - Shear vane or Scala test result
59bff82f-d624-59b5-a909-ffb2226b106a | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
ebb08df7-3860-54dc-9a2a-8c8ffb1d9efd | note | Verification Activity: Activity - HP
26c0f354-3a68-5822-a716-a42fca1b4a64 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0e3532e5-6f73-55de-959b-dbd410d3f37a | note | Verification Activity: By - SE/ENG
779839bb-40b7-4e5c-b7a2-7f0833a86e4c | signoff | AUTHORITY HOLDPOINT
5eab70fb-a1a8-48e3-b4f2-0ed4e4f325b5 | checkpoint | 10.2 - Undercut approval
3c5073e0-8e4a-5c60-81a7-f17f34ac2498 | note | Detail / Activity - On Subgrade
40b866fe-3a0e-5135-bb8f-d7bc2cf723d0 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
27120284-e591-5f45-bd6a-30d79b772b7a | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
1224df02-a79a-5ad5-9bb8-1dfb97b3b876 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
6f76cedb-8348-5e5d-a495-6a8e76fbb00b | note | Standard / Specification - PS 21.6.5 Table 21.5
49d30c5a-08b5-5321-8b36-2560e66fb3b3 | note | Verifying Document - Lab Test Report
b1f4384a-ae81-5c9a-929d-d6023ba31873 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
b9798584-afeb-59a1-9483-b5b3a71ad9ec | note | Verification Activity: Activity - HP
8715583f-5db8-579a-9266-3c91c068b6a6 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
424a884e-db34-543a-8b7f-c1a142088654 | note | Verification Activity: By - ENG
78a0730d-36ea-459c-b4dd-0a00511912d6 | signoff | AUTHORITY HOLDPOINT
f3801612-20fe-4cc2-af64-d5bf41108686 | checkpoint | 10.3 - Undercut Backfill Compliance AP65
46af40b2-9311-5e96-a2a6-a6666ee4d860 | note | Detail / Activity - On Granular Material
a8932932-94af-53f6-a6e1-5b19d8146cb8 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
278d37a6-03b5-5e93-8b97-d2f7dce7f0f6 | note | OR
12b761a7-80bc-53f9-98c7-2f950461a8d8 | note | ○ Clegg 25% CIV
1af75d44-4f66-5a9b-bafe-fdbf040692c6 | note | Standard / Specification - Appendix XVIII
75c39ad1-c357-5799-8e80-faa726221c35 | note | Verifying Document - Lab Test Report
b23ad54a-54db-53c7-8778-ffa67a096465 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
b960630b-0fbb-5b52-b936-271bee49db46 | note | Verification Activity: Activity - H
5ee60e62-0485-52f2-9e57-2d80e5ec4f6b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a9511dfd-21e0-5a02-ac57-3df29edbabf5 | note | Verification Activity: By - SE
fb809ad6-ace1-4655-beb1-df5aecdb8501 | checkpoint | 10.4 - Bedding Compaction Testing AP65
d1f406e4-e7ba-58bd-b239-2392e9ac15d7 | note | Detail / Activity - On Granular Material
cfbf123b-9dfb-5aaf-9012-5a291b76b49c | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
ef54d365-a66b-59a9-b557-a451c6ab5207 | note | OR
64522705-2bfa-5c89-a9c9-248c78d8e1c7 | note | ○ Clegg 25% CIV
aa4f8f9c-848d-5220-b8a9-3e4c0f684222 | note | Standard / Specification - Appendix XVIII PS- 21.6.11
d249063e-277c-5999-8559-85d88c06d8a6 | note | Verifying Document - Lab Test Report
fdd9ed0f-ac5f-5465-a15e-7f8dc77918cd | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
34b397c1-50cd-5e4f-bc16-291e79e677c4 | note | Verification Activity: Activity - H
421252a6-bb2a-5d61-bd08-0c90a3c36dd7 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1f3a1990-718d-5d66-85f3-3f9e24aed833 | note | Verification Activity: By - SE
600cb761-3154-48e9-9bc9-811d43a2a5ee | checkpoint | 10.5 - Survey
f12e6b44-2efb-5f70-a63d-286e0118b24b | note | Detail / Activity - Inspection of Structure
fb3baed7-2c3e-5799-9154-3468836034c2 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
46689cc8-5fa7-5b45-8e1d-79910cf94d4d | note | Standard / Specification - PS- 21.7.6
d98bcb43-a238-5440-a742-93fef25f0097 | note | Verifying Document - Survey Data
f5587495-0809-57b1-818a-e656c2afba3a | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
8ec8555c-3bfc-591d-995e-95fa99fd2e5f | note | Verification Activity: Activity - H
9947bfb3-d2ed-53e7-8131-48bb8ceef728 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
9447d20d-864b-5294-b589-88cf4c2bd2a9 | note | Verification Activity: By - SV
2b4ae2bf-cdac-4031-a469-5f9c5085b7e3 | checkpoint | 10.6 - Sidefill Compaction Testing
7869e21e-b3bb-5795-a62b-da12c6625305 | note | Detail / Activity - From the bedding layer to the overlay layer of pipe.
46298f0e-e8d7-5c0a-b43d-0a5fcaf4a4c4 | note | Acceptance / Conformance Criteria - AP20/GAP20
261506e7-c436-57a5-ba2a-175ff7bab370 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
3210d69c-0d5f-5de4-9d28-850da6641b65 | note | ○ AP20/19mm chip
4e3f5f46-c4e5-5cbf-b47a-33392031840f | note | Standard / Specification - PS- Table 21.12
82c82380-7b33-5a70-b592-0cbc79af780c | note | Verifying Document - Lab Test Report
b422560c-9424-53be-bf7c-e7ddef71e5f1 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
9a0eb8dc-6128-5c42-a73b-c0c677426f03 | note | Verification Activity: Activity - H
c4371f82-beb5-5a73-8d77-a3ae9f81e4f9 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6e37ba6d-ce60-50cb-bff8-d004ae621fba | note | Verification Activity: By - SE
b5e9ae43-fd33-40d9-a987-eb3a3eba09f4 | checkpoint | 10.7 - Backfill Compaction Testing
dbfb2cff-830a-5f0c-bf9d-487ea1ab68cb | note | Detail / Activity - From Overlay layer to the subgrade layer
bfcaf764-4a91-515f-8d19-4d37035d8e90 | note | Acceptance / Conformance Criteria - AP65
05e9eedf-248e-5461-b7fa-e8d732b10f18 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
c6d54466-242b-5462-b9b7-384d3d9ec986 | note | ○ AP65-Clegg 28%CIV
aa906e2b-dc51-528c-81a0-a6ac9cf708cc | note | Standard / Specification - PS- 16.5.12
3dcf7fc0-c7de-55bf-a1a7-4f8a02f438fd | note | Verifying Document - Lab Test Report
e404abd0-2082-593e-b583-fd6142810a90 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
6d6fb89b-e7b3-531b-9c58-d42b5ece9309 | note | Verification Activity: Activity - H
a486fd17-7b6a-5177-97ec-7e5df140a91b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0fa08b31-06af-52d6-a06f-93fc542fb21a | note | Verification Activity: By - SE/ENG
5838efb0-2ada-4800-a540-c5078798dd01 | checkpoint | 10.8 - Man Hole joints inspection
c52a772b-5b25-50ca-a32d-0c7848ac4cc4 | note | Detail / Activity - Inspection of joints
1f28b362-742d-5a00-ae82-f1f03630045e | note | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
62c74a0b-5cac-52be-ad7e-53982e29ca67 | note | Standard / Specification - PS 22.7.10
37a9f26d-3027-5f16-b76c-1b7d1802c42c | note | Verifying Document - Visual inspection
e90c5628-8c5a-58ce-849d-a95c85c3a046 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
c01f5d40-502b-520d-a425-1370e0e3717f | note | Verification Activity: Activity - HP
662cef28-bd6c-5d62-b96a-ca4618d54061 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c77cbcda-553a-5d97-9293-8da8c6adc6b9 | note | Verification Activity: By - SE
992d5e86-d202-439d-a821-8954c27cfa08 | signoff | AUTHORITY HOLDPOINT
555b3bac-b475-40f2-9ee2-9a9395393246 | checkpoint | 10.9 - Inspection
c02b334d-aae8-51d9-9d3e-b2d0e9c8a692 | note | Detail / Activity - Inspection of Structure
db83d20a-d335-5c87-be33-c2a02ac0021a | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
d8f1292f-0e6a-5521-af34-ce10baef8df6 | note | Standard / Specification - PS- 21.6.11
6a1caa8e-92cf-5cb5-bfd2-f8886b6c39f0 | note | Verifying Document - Manhole/Catchpit Record
be0fdee5-c420-5e89-912e-0cef9f898df8 | note | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
a8ec1cda-c195-5825-9bda-dd731be4e25f | note | Verification Activity: Activity - I
a63c0ca0-1e53-5ba5-b872-75e9bd5e4be7 | note | Formal inspection activity to be undertaken and recorded.
4ac2c90b-fcbf-5efc-bc55-3ab5853f6aca | note | Verification Activity: By - SE
075b9a07-e663-48ae-afa6-ec0e21d9b7f6 | checkpoint | 10.10 - Plumb
c953cfa5-cc46-5281-a3c6-5a77b05b2d49 | note | Detail / Activity - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
e526077c-cf31-5bb3-bc0d-e159fc886bc9 | note | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
ec396d89-6a21-57e0-84c2-31f1df3c4e24 | note | Standard / Specification - PS-22.7.10
224649b5-0470-5c40-8c4e-573cd489cbe1 | note | Verifying Document - Survey Data
f32e86b2-6d11-58ea-89da-5010b629cd86 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
f5cc3a52-80d8-5ff5-b8ae-213c0a940176 | note | Verification Activity: Activity - H
bad816e5-7717-51d9-9622-2f5f3d143821 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7ab23a2d-185c-553a-a6d4-92147830e7ba | note | Verification Activity: By - SV
a3059430-2e2a-446d-9a59-c61d57148696 | checkpoint | 10.11 - Step Rungs
37c65c28-f7d1-5c16-bd19-f4b492d2e65e | note | Detail / Activity - Step rungs evenly spaced at nominal 300mm vertical intervals
8e15b306-79a9-514c-8614-fad05c11362b | note | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
11155448-2efb-54ec-8b01-e3375fa85b59 | note | Standard / Specification - PS-22.7.11
3ccb0771-ba43-5fe2-8a55-c488be112d8c | note | Verifying Document - Visual inspection
ce815882-d045-53d4-8c4a-bdfca3f43f68 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
fddc4e2b-5e42-54e1-befb-65ced36c1119 | note | Verification Activity: Activity - H
83b62e8e-ce75-5998-9b5a-e9fec9a11fe1 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
00e02e56-a7a3-527f-9eca-9e041ea4f7d6 | note | Verification Activity: By - SE
3b1c2622-4d3b-41fa-a87e-a7791ee9e874 | checkpoint | 10.12 - Manhole frame and covers
464d9054-0003-5615-bcd8-5a0e3a75313c | note | Detail / Activity - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
9b18e353-b06d-521d-ae5b-4c398c094721 | note | Acceptance / Conformance Criteria - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
7ca42020-d052-5912-ada6-07614f113d4a | note | Standard / Specification - PS-22.7.12
c4e58dd5-837f-577c-9f09-9448a0e32241 | note | Verifying Document - Visual inspection
667ba0da-5634-524a-851e-533f9d040bbe | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
022062d8-5482-5057-9e3b-b00e136cbe43 | note | Verification Activity: Activity - H
d51bd318-2dc9-56df-b91d-e0c8ce6bdc32 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
277024e9-78d6-536b-adf1-0b989f9b0660 | note | Verification Activity: By - SE
a1b3752f-0962-4a95-b780-2530afd20173 | checkpoint | 10.13 - Manhole lateral connection
7624eaf6-d785-5027-b46c-b42205b3e0df | note | Detail / Activity - DN150 PVCu connection for future lateral.
79eab660-bc61-5c53-b0bf-644440fb94ec | note | ○ 800mm above manhole outlet invert
b3df2568-c834-5a96-a5c9-462b7226c10d | note | ○ DN150PVCu end cap.
dce05dac-5d71-5dfd-a739-705ce43c3269 | note | Acceptance / Conformance Criteria - DN150 PVCu connection for future lateral.
b8ab9539-5a94-5cf7-9ee9-26225459110a | note | ○ 800mm above manhole outlet invert
37db1b87-5e9f-5a52-b586-d67e199cbedd | note | ○ DN150PVCu end cap.
7c166507-7820-59c8-bc6a-a420ce5a566e | note | Standard / Specification - IFC Drawing 0320-Rev 03 TCC IDC DS6.5.12.4b
61285080-aeac-57f3-8acd-5403e9256e15 | note | Verifying Document - Visual inspection
4fcdbcf1-80b4-53ef-8654-ce3441c5db48 | note | Testing Quantity Required (based from schedule qtys) - Per connection
67ff6ef7-f3ce-5afe-a972-3d715a61ccbf | note | Verification Activity: Activity - H
1fb6edd0-f501-5f70-96f0-7f92c2755678 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a3e49e45-8690-573e-bb63-cea7c8ec6317 | note | Verification Activity: By - SE
48db86d0-bc4e-4f9c-ba6b-e7f68b9006a8 | checkpoint | 10.14 - Concrete Formwork - surveyor to check
b49515f4-230b-5be1-bcf4-4b5f722b5b2c | note | Detail / Activity - Equivalent to check the position of the formwork
bd1b3fcb-e62f-5ba5-83f5-612329cb56d9 | note | Acceptance / Conformance Criteria - +\- 100mm of design
48b73e62-be96-520e-bb7a-484d1e78a757 | note | Standard / Specification - Project Specifications 27.4.5 (b) NZS 3109:1997
48fda580-ad56-5387-a3cb-381a32b8f544 | note | Verifying Document - Pre-pour Check Sheet
56b77bd0-5b49-5dac-9d70-2fbc4e3dea5c | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
b0254939-19d3-5cc0-a7f2-feddbba631ad | note | ○ 1 set = 5 tests
adb05126-8d89-5bde-8d90-00801a84ef20 | note | Verification Activity: Activity - H
2cbb53e0-945e-54c7-bf20-163af0207e9b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f83b5e60-ef0c-5016-9986-1abdc7599bb5 | note | Verification Activity: By - SE
307c3660-8480-4c50-b866-9919f1536916 | checkpoint | 10.15 - Concrete Formwork - surveyor to check
14640245-1f40-533f-a074-96d111777b73 | note | Detail / Activity - Equivalent to check finished height of framework
63a05c68-9524-5e33-a793-f75b711131eb | note | Acceptance / Conformance Criteria - +\- 10mm of design
21d6d5da-af87-5aa1-a941-509a59e9e565 | note | Standard / Specification - Project Specifications 27.4.5 (b) NZS 3109:1998
a3323e21-9d2f-5718-9ae4-d15c604c225f | note | Verifying Document - Pre-pour Check Sheet
8837872f-6443-5785-8b14-2916bec714cc | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
de5e91ae-95cc-55ac-bd15-fd201d009744 | note | ○ 1 set = 5 tests
a0beed3f-4e95-5eec-9ca6-3b95d29a98de | note | Verification Activity: Activity - H
7511c258-d374-5768-84fe-f684e75f8742 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4650c918-3daf-5f5a-80d3-39d2458890d6 | note | Verification Activity: By - SE
ad45a29d-e27d-4ba6-b2bb-4c65eb4bf10b | checkpoint | 10.16 - Pre-pour inspection
703b3912-946e-5a01-a841-792753856479 | note | Detail / Activity - Pre-pour inspection of manhole before ballast
7ced85eb-4cc5-52c1-88a1-046166440425 | note | Acceptance / Conformance Criteria - Stable form work, ready for pour
cc9e777a-86a9-5599-964f-ccbae7808bf3 | note | Standard / Specification - Design drawing
4d57fd9e-e112-5d46-8345-401adeb90e35 | note | Verifying Document - Visual inspection
18c64b65-3ecf-562b-9cc8-b7084b26fe4d | note | Testing Quantity Required (based from schedule qtys) - Pre each manhole ballasts installation
db14642a-2acd-5d13-aba1-490c2dd8b9be | note | Verification Activity: Activity - HP
49fe2f67-19bf-53bc-8af6-b4272427fd99 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6a44b75e-9a27-5619-b1d2-e8ede7326ac5 | note | Verification Activity: By - SUP/ENG
912ac496-c7a3-4450-b28d-0f786a0abb18 | signoff | AUTHORITY HOLDPOINT
59fded4b-4d1a-4caf-947f-a7752a3afb76 | checkpoint | 10.17 - Manhole Ballast WWMH06 to WWMH10 (concrete & reinforcing steel)
d18352a6-e74b-5bba-b264-82a89173a3d6 | note | Detail / Activity - Additional manhole ballast.
3a3600e0-45f2-511b-b193-5e4cb1b7e859 | note | Acceptance / Conformance Criteria - All Concrete to be 25MPa at 28 days.
db0df36a-d4f9-549c-8398-cfcd1f9d530d | note | ○ Minimum cover to steel = 50mm.
a9778579-5578-528c-b01f-9a9f8537c8ec | note | ○ Reinforcing steel to be grade 500E and to comply with AS/NZS 4671.
18ca943d-dfc2-5b61-a6a9-a96841508020 | note | Standard / Specification - IFC Drawing Sheet WST 0321 NZS 3109 5.6.3(B). AS/NZS 4671 PS 22.6.2 PS Table 22.4 specific manhole requirements
5e112d30-9a52-5f0a-8414-3ff58b7bbe4a | note | Verifying Document - Visual inspection
f70af5ca-353c-5fa8-bddd-2e2f21366dbb | note | Testing Quantity Required (based from schedule qtys) - Per manhole
75cf830e-8fe1-508a-a33a-0c13f96ebea4 | note | Verification Activity: Activity - H
3b9d92fe-5219-5f47-b57f-162a0b73a65d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0340738e-209e-526f-a3b2-c9f123264778 | note | Verification Activity: By - SE
253063ee-5afa-4d5b-b40c-79cdd7e0dc06 | section | SECTION 11 - CONSTRUCTION ACTIVITY - COMMUNICATION DUCT INSTALLATION
d26cd6cf-ac90-4540-a00a-6d325d542a64 | checkpoint | 11.1 - Bedding
0f4d2d4a-5f9f-5c3e-863a-c2d271392c51 | note | Detail / Activity - In wastewater trench ensuring 50mm of beeding over wastewater pipe
2eacb652-94ab-5eab-9c53-d9a233682731 | note | Acceptance / Conformance Criteria - Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
050a1010-dd97-5ed4-a151-2bd29b53445a | note | Standard / Specification - PS 25.13.2 g)
d6ca09dc-d1ab-5506-b05e-af4331d774d9 | note | Verifying Document - Checklist
07afcc82-dd96-5ce9-9227-ba94a32e9623 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
84d46a4c-c510-5af2-9bf3-8166de01420b | note | Verification Activity: Activity - M
eaceb50f-0050-4a0b-b59f-f8fd949a7dd6 | checkpoint | 11.2 - Installation of Ducts
e5488029-66e6-5fb7-b01c-d7d4777f9d2b | note | Detail / Activity - Layed in same trench as wastewater with sand cover.
3e0bf5f3-feb8-5aff-b333-f4df543248dd | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material
30ab0c87-d0ba-5df2-9c7c-614e05e51d30 | note | Standard / Specification - PS 25.13.7 b) iii
966899da-7927-53bc-a135-bab7255a9fd3 | note | Verifying Document - Checklist
79e035e9-8f96-5d21-b25f-b2b88fcfc8d1 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
7b4e2d79-f444-59a2-97cc-d2608670e592 | note | Verification Activity: Activity - M
81432ae0-5838-4032-9829-4f3e22fa27f8 | checkpoint | 11.3 - Draw Wires
aeb6e947-0d60-5432-8573-b46855aa97b9 | note | Detail / Activity - A draw wire shall be intalled in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting.
37753c05-3a35-5930-bf8b-239edb8de796 | note | Acceptance / Conformance Criteria - Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load.
1b398461-d7ac-5939-9f8f-e15f312cb451 | note | ○ ≥20 years design life.
ec01c851-6fb5-5f5b-828a-cb089800ce0c | note | ○ The ends of draw wires shall be made fast within the pits and be secured to the duct plugs.
31dc0aa5-c827-53fe-be6c-ee4c56e05e5b | note | ○ Blue colour wire
38d0f3ac-bbfd-5c5f-b72e-4a818a892cb5 | note | Standard / Specification - PS 25.13.7 e) ii to iv
197a8656-544c-51ff-bb69-b075f9dbd19d | note | Verifying Document - Checklist
69d74324-8ad3-5cf5-b097-959230ce2414 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
911c3591-9288-534e-8bb3-36fbbad45ee5 | note | Verification Activity: Activity - M
ecf02d09-df7a-44bb-a037-2419706e2aac | checkpoint | 11.4 - Caps
a1a58071-36c9-5b49-8f46-4eb9c203f698 | note | Detail / Activity - All duct ends shall be capped
2ce73e99-a223-5533-98e7-88bd4ac22380 | note | Acceptance / Conformance Criteria - Capped ducts
4d6aa083-28f7-5b67-bbab-6ed6e8e9e048 | note | Standard / Specification - PS 25.13.7 e) v
7e9d5c1e-f628-5be5-baa4-3af8c5cb358b | note | Verifying Document - Checklist
817abca3-c026-51ec-b528-3a79de3a7a09 | note | Testing Quantity Required (based from schedule qtys) - Each Cable
ac614e21-879c-5eea-bb8b-83b09c108433 | note | Verification Activity: Activity - M
1c6c5821-dd17-478f-8449-e5b28fc74054 | checkpoint | 11.5 - Warning Tape
0280b80c-a24c-5046-908a-07f1645b1307 | note | Detail / Activity - Warning tape to be placed above services.
9a4316dc-3ae8-5971-8be8-a26c9fc8a5c1 | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the topmost duct
2bede550-82f4-552b-9edb-666d894933d0 | note | Standard / Specification - PS 25.13.7 b) iii & f)
8bdd92d0-3435-5d22-a263-e1651068f2eb | note | Verifying Document - Checklist
daa088d7-22d4-5dae-a6eb-d676633ed66f | note | Testing Quantity Required (based from schedule qtys) - Each Cable
9fd37a61-c06a-528c-a59a-826d777de842 | note | Verification Activity: Activity - M
5c34ff09-b585-4c8a-a2ad-5b4b29736114 | checkpoint | 11.6 - Overlay
0dcbed29-088d-5554-bf06-b707eace3bdd | note | Detail / Activity - 150 mm minimum sand placed on top of duct.
abbfdf46-624f-5c6b-8b37-ec4f2e83f629 | note | ○ No mechanical compaction will caarry out till 300mm drom top of duct.
11c63731-2d39-56ad-b3a9-995311156c3d | note | Acceptance / Conformance Criteria - 100 mm minimum sand placed on top of duct.
a2ff827e-1084-50c5-acc6-ac67ff3ba23e | note | Standard / Specification - PS 25.13.7 b) ii
de11fd91-da35-5192-b34e-3d3a220a0fde | note | Verifying Document - Checklist
0ae42586-89a4-5d4a-b68b-b3324e29aa0f | note | Testing Quantity Required (based from schedule qtys) - Each Cable
107fcc43-4eda-51ce-9df5-d983b8365f25 | note | Verification Activity: Activity - M
f72054ac-a52c-484d-9ed0-19efc9377484 | section | SECTION 12 - CONSTRUCTION ACTIVITY - COMMUNICATION PIT INSTALLATION
52640ec5-e8d7-4611-859d-1c3c72860d82 | checkpoint | 12.1 - Pit Installation Location
fa88f659-f461-5750-9776-83336710714d | note | Detail / Activity - Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid . Confirm on site with engineer,
98522b27-27b9-5e16-afae-802a3a5e47db | note | Acceptance / Conformance Criteria - Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas.
ec8b4880-268c-5cb8-b188-387db7c5844b | note | ○ When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side.
4557bfa2-04d9-576e-b4b6-eaa6ce6602f9 | note | ○ When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side.
7371fd2c-39a1-5afb-8988-6b98a44c379c | note | Standard / Specification - PS 25.13.8 a) i and ii
3194f6bc-7c3a-5b0c-8de9-d10b3ea31e5c | note | Verifying Document - Checklist
58d563ee-8c63-5058-93a0-f19ef4d3590b | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
e9770e2d-971f-58cd-afc3-0854f90ce0ed | note | Verification Activity: Activity - HP
975876b2-4210-55d3-bc9e-b8f45a5c0124 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
fcecb419-e654-5a1d-b10a-6edb52212adb | note | Verification Activity: By - ENG
92857973-31c4-4670-b66c-54842ee570ff | signoff | AUTHORITY HOLDPOINT
f970d875-75c5-4718-ad80-dc00b2bfdef8 | checkpoint | 12.2 - Pit Installation Bedding
1a607b1f-de75-52e5-857d-18d78c63a3a3 | note | Detail / Activity - Bedding with 150mm compacted GAP20 hard-fill coverd with 20mm compacted sand. Pits shall be carefully lifted into place and lined up with the ducts to penetrate the chamber.
6cb64e9a-d9c2-57f0-8eca-d9a9d21f32c1 | note | Acceptance / Conformance Criteria - 150mm compacted GAP20 hard-fill covered with 20mm of compacted sand
d26fac1b-15a5-5c36-980a-5c545712188c | note | Standard / Specification - PS 25.13.8 d)
d1acbe88-0980-5da0-831e-75a268e7dbc7 | note | Verifying Document - Checklist
9df9a7dd-1492-57f1-a881-5491d2657049 | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
42648de9-8df9-5beb-8503-f4067adde2a5 | note | Verification Activity: Activity - H
ced215d4-494a-5096-8f14-86c87d8d1738 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
05a289a9-e713-525a-9638-b34afd27dfb9 | note | Verification Activity: By - SE
1a9c2ee0-5c5e-46ea-8b31-b2753462079d | checkpoint | 12.3 - Pit Installation Sidefill concrete
a0cabb64-1d98-5541-a7a0-cd370d1864fb | note | Detail / Activity - Plactic pits shall be cast into the ground with 150mm concrete surround
78c9798a-459a-5e2b-b69d-c04da08ad71c | note | Acceptance / Conformance Criteria - Plactic pits shall be cast into the ground with 150mm concrete surround
8f31f99c-04ce-511a-85e8-db202972bdaf | note | Standard / Specification - PS 25.13.8 d)
dd120032-f4d6-50f6-b6fb-4d1996d0ff0e | note | Verifying Document - Checklist
d422f348-7626-565b-8f4d-53dcc60dd54f | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
84c64e19-0b8a-5207-ae70-ff329cba26fe | note | Verification Activity: Activity - H
c92720f2-549d-51d2-a68e-4bbbcc5de68f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
24c24ecb-f0be-5a29-bbe7-2b17a423e51d | note | Verification Activity: By - SE
51a16ae4-dc35-4e91-8b5e-d98d74e3d2a7 | checkpoint | 12.4 - Pit Installation Backfilling
a70a5b25-f46a-5945-ab7d-16c2ecc5d16f | note | Detail / Activity - Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts in 200mm layers of GAP 65.
7a51c89d-b03b-5608-9176-feb1647f62ed | note | Acceptance / Conformance Criteria - Min 92% compaction rate and Average of 95%.
f2968ff2-c746-5264-8f9d-cffabe661c10 | note | Standard / Specification - PS 25.13.10 a) modified
bee3f25c-0d6b-5289-b595-774f1f01d96c | note | Verifying Document - Checklist
f8469124-6f74-5b39-a94e-cd26ed373b79 | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
51ea5f99-0620-551c-a543-7f1069888e62 | note | Verification Activity: Activity - H
ae883cd9-0b56-5cf0-9abf-f7d294970e5b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a6cbfcdb-3fed-5179-a730-592e41599394 | note | Verification Activity: By - SE
ce3e537e-3005-4a31-974d-89afeced6c9b | checkpoint | 12.5 - Pit Installation Concrete
44309ca4-504f-5ebc-988b-034d59347be0 | note | Detail / Activity - Top 300mm of pit shall be concreted around with a width of 150mm with a 20MpA concrete.
7c629f1d-6d1a-5a67-a2f4-2817180dce54 | note | Acceptance / Conformance Criteria - 20 mPa
e830a2fd-b90a-5851-a464-76a9c4c2e93d | note | Standard / Specification - PS 25.13.8 d) iv.
4811a493-babd-5f42-bfb4-b266c1326844 | note | Verifying Document - Concrete Dockets
8bf283eb-0cdb-5571-a48e-ff796946dcac | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
b60fe7eb-74fe-5d60-a1ac-a166830e8cf3 | note | Verification Activity: Activity - H
ee5bde1b-3bac-59bf-8b84-a8aac2adec6c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
acecbd77-b751-5705-9b39-ca153bca17a4 | note | Verification Activity: By - SE
76939087-c196-4405-a5ef-2e21af3ade40 | checkpoint | 12.6 - Pit Installation Clean up
a7acfa56-284f-550c-b496-923af6299268 | note | Detail / Activity - Clean out all pit after completion of the work
935b0efb-5d0e-5d2b-931e-589ad3fe65d9 | note | Acceptance / Conformance Criteria - Pit are free of dirty, mud,water and foreign materials
0e85da16-b343-5a2f-bba4-e3cd02d0b4b1 | note | Standard / Specification - PS 25.13.8 e)
6495bef1-d7a6-5103-a327-3b78a07d1902 | note | Verifying Document - Checklist
3b4af721-1967-5c02-b057-2a5e5ef8641b | note | Testing Quantity Required (based from schedule qtys) - Each Pit Location
417c29cf-748c-5578-b1f5-042b2241a2b3 | note | Verification Activity: Activity - M
c57294de-6d30-54e8-b477-e4ecaf6083bf | note | Verification Activity: By - SE
80307103-758e-4b20-92a9-5f603b2fd949 | checkpoint | 12.7 - Survey As Built
7188bed5-df33-5bbe-9283-4f4f0ccc4592 | note | Detail / Activity - As Built every ducts joint before backfill
a2411b5e-9505-56fc-9504-72b4f090708e | note | Acceptance / Conformance Criteria - Completed as per drawings
d2612ddb-b92c-5d54-8306-08ca9fe3cc95 | note | Standard / Specification - Standard Practise
0b64bf42-bd37-537c-b4a4-d1b47986b74d | note | Verifying Document - Survey
5f47dee2-6889-59ea-a41b-bc074b8566c3 | note | Testing Quantity Required (based from schedule qtys) - On going
5b84d16b-978f-50b2-860a-a18a037cc5e4 | note | Verification Activity: Activity - H
ac37cfdf-f71e-58a8-b47d-4477244f34c4 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a0e305a3-1972-59b1-9225-ea7f520b2a2a | note | Verification Activity: By - PE
894c82d5-d3fc-40fa-bb81-bb30ffa43eb0 | section | SECTION 13 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Butt-Fusion Welding
eec4d8b5-b2a6-4276-ad2f-4fdc4ade154d | checkpoint | 13.1 - Butt-Fusion Construction weld test
ec093ceb-b29a-5f40-b6f9-42adbe53d7b0 | note | Detail / Activity - Test at least two welds from the first 50 welds.
bce34a22-a0eb-5bca-98a4-3e239bcba759 | note | ○ One of the welds to be selected by the Engineer for satisfactory result.
8038f76c-dab9-582b-bbf3-b0c3df6615a2 | note | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
6e02f5cb-a1f0-5631-a384-1720161b1ba1 | note | ○ 95% tensile strength; welds aligned
a296f1bc-8385-5724-a450-6fc425f963fd | note | Standard / Specification - PS- 22.9.6 (a) (iv)
514c4692-50e2-505a-926d-ccfbd6dad77c | note | Verifying Document - Test report
a42f55c3-df51-53b2-be87-434d6996a978 | note | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
cd501cb6-e6f6-58c9-b29f-5b2cd7589f0e | note | Verification Activity: Activity - HP
b8a91b9f-b43f-5653-9bcd-3711d639d06e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0a913f83-57bb-562c-89f7-fc72314b2be1 | note | Verification Activity: By - ENG
2c5c1fbb-3652-4ead-8283-1e27529f1ceb | signoff | AUTHORITY HOLDPOINT
16a2d72d-c2e5-413b-bfab-29198c98a648 | checkpoint | 13.2 - Butt-Fusion Welding
f4b1e1f2-2f6b-57af-8e84-20d30b58aa02 | note | Detail / Activity - Use only semi-automatic or automatic welding machines.
5881f3b8-0b65-5b20-af40-064f8fc9c9c8 | note | ○ Maintain a site record for all butt-fusion welds.
b45de0e9-269a-535b-b640-97233bfd2c47 | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
7c469fd6-a85c-5b7f-a97a-e456fc08f9b1 | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
d21fd5c1-10e2-5a06-8d29-860e41e2772d | note | ○ WMS Report
fd8b57ed-02fb-5325-8d16-59d1a3dd8d1f | note | Standard / Specification - Appendix XXII PS 22.9.4 C
94178097-1591-5ac1-a39e-7375c0b5c196 | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist.
54ee2db2-1828-5e43-8d11-a4bdb312f854 | note | ○ WMS Report
7d4e019b-f83b-5091-b6cb-68847ce14c36 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
9a541fb5-78b0-5cf3-90ed-9c699582b998 | note | Verification Activity: Activity - HP
c8bba071-a344-507e-8e4c-9ce577b28f70 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
95bca6b8-6fd3-5b3f-acab-00a3d5b42f20 | note | Verification Activity: By - ENG
f276f82e-5d03-4ddc-87bb-6c07c700a0a5 | signoff | AUTHORITY HOLDPOINT
44023284-d4d4-4e7f-90e5-9a87b3f04d72 | checkpoint | 13.3 - Survey
e1ce771c-4769-52af-93eb-769727bc16f3 | note | Detail / Activity - Inspection of Pipeline Inverts
dddcf620-c3d2-5b63-a4b6-9ffae6daf179 | note | Acceptance / Conformance Criteria - Vertical design Setout:
118acc9a-0b79-524b-8048-73601f529b3d | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
ddd70cc2-14ea-5296-99b7-7ef70fe25dfd | note | ○ Pipes > 1% grade: +/- 20mm variance
410fe3e6-ecee-5ddf-9c52-163a725829e3 | note | ○ Horizontal design Setout: +/-30mm variance
ba50a90b-e8a0-533b-a8df-922f7371c95e | note | Standard / Specification - PS- 21.7.6 Table 21.15
822a6290-e19a-59d7-89f7-1088f50db076 | note | Verifying Document - Survey Data / As-built record
d72a3e33-76ad-5a6e-85bd-9a76d487e2a9 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
420407a8-53fd-5c86-ad1d-ac9ffd76d11e | note | Verification Activity: Activity - H
7aef3da8-760a-5fc8-9a8d-c6c9e906f795 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
88f4603b-d04c-5555-ab2b-7a429ae9e68b | note | Verification Activity: By - SE
41ede405-be08-4d2e-9a1a-8bc3da0e06a9 | checkpoint | 13.4 - Photograph of Each Weld
3d9f52d9-fb78-5f1e-84b4-073136613893 | note | Detail / Activity - Take sharply focused photo while clamped
6d0b1aeb-5d21-5939-9e0d-f7117844d0a0 | note | Acceptance / Conformance Criteria - Unique weld identifier visible
f8137ba9-38f4-535c-8445-190758766488 | note | Standard / Specification - N/A
a6dfe73d-66e5-576e-a265-1b51ad7907ca | note | Verifying Document - Weld Records; Photos
27669d9d-4c19-547f-bb1e-18c2fe546ebe | note | Testing Quantity Required (based from schedule qtys) - Each weld
e44ba889-16b3-5643-abce-03a4f5325979 | note | Verification Activity: Activity - I
a65e089c-24e1-51a6-9460-f9f4efaa67df | note | Formal inspection activity to be undertaken and recorded.
96b52b6b-2874-5ddf-a095-761f70b48fb2 | note | Verification Activity: By - SUB
7528e24b-7fb2-418b-8ab1-9fc6e0d4e163 | section | SECTION 14 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
855fe6df-83f9-446b-8c31-e648683e1101 | checkpoint | 14.1 - Survey As-Builts
2ca6b127-b281-5511-9fd1-e807293c400b | note | Detail / Activity - Quality check on the pipeline and structure based on the tolerances in RITS.
cdf6fa8d-5cf8-5f37-8444-2f4483174991 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
4d226a9f-69f1-514f-b471-08f5911a4e89 | note | Standard / Specification - Project Specifications
996f1726-8c33-561a-a77c-f9af6f76ff63 | note | Verifying Document - Red pen markup only
314d4a39-fe04-5863-8845-ba5d830f59a7 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
5195eba4-b036-5831-abfa-23d4d16e3c88 | note | Verification Activity: Activity - H
c544262b-fc7e-594c-a487-7ae81a3a6065 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8256dcad-f575-5e15-bfe3-39533e884487 | note | Verification Activity: By - SE
73ae2bb9-0fb4-4c42-85f3-3ae7cda176b2 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
5f95c8cb-77d1-5506-924a-1e3743e3ab6c | textbox | Contractor's Rep Name:
c045c75e-af12-5b71-8641-5d4ffc22fbf3 | textbox | Engineer's Rep. Name:
bb321f7f-cdc7-5fc8-84a6-92b8a1028100 | date | Date:
48cbc46f-bd2b-4385-ae65-d67d7109238e | signoff | Add Signature
d83d7f58-07fe-4132-9c4c-8c9422d85121 | checklist | DN1210-SP2-017-002 ITP Retaining Wall 3 Magnum Block Rev 0 | itp | DN1210-SP2-017-002 ITP Retaining Wall 3 Magnum Block
9858e912-2edd-4d1b-bcdc-12b185b6e491 | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
0f60b3e2-f9d0-479d-ba10-f862489243e2 | checkpoint | 3.1 - Methodology
a07dc0cf-5690-5e9e-b08f-7abce5e7531f | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points for review and approval prior to works.
b8b54222-919b-5e8c-9a9d-4ea158ec3580 | note | Acceptance / Conformance Criteria - Engineers Approval
2f31cd6b-50f8-5516-adef-14578ecf5802 | note | Standard / Specification - Appendix V
135709eb-db02-583a-807e-446ac695e00d | note | Verifying Document - Approved Methodology
b2dbf583-4129-5587-afba-7d339ee85f03 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
31eb68a9-7951-5b12-917f-9b7e03b52b41 | note | Verification Activity: Activity - HP
7690b3ce-bf57-5093-ac5b-ec1a3ce99e11 | note | Verification Activity: By - ENG
a32c5ad1-73fc-446b-9fcb-01077cbf3131 | signoff | AUTHORITY HOLDPOINT
d835381c-d89c-46ca-9eb5-269949be9eb5 | checkpoint | 3.2 - Ecology Sign Off
eb39ed70-3067-561b-ab52-c0dd31267864 | note | Detail - Confirmation from Ecology that earthworks and sheet piling can proceed
46db86a2-d4bc-599a-b597-cb538604f215 | note | Acceptance / Conformance Criteria - Email
b123d67e-ea8b-5d50-9412-250c11acb9e3 | note | Standard / Specification - Internal Hold Point
8c983656-37ce-56c7-a25e-a836df0e5fd9 | note | Verifying Document - Email from Ecology NZ
7f02d17b-3168-529b-aef5-4ce97c6e71ed | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
73559ede-69c6-5a67-a67c-151ce5bbb3f1 | note | Verification Activity: Activity - H
a93b2455-fb37-5e67-af53-7b8db59fd41f | note | Verification Activity: By - PE
d6b96f49-e696-4e5c-a12a-e10c14f7f13d | checkpoint | 3.3 - Erosion & Sedimentation Controls
7064999f-7a16-59fc-aeff-5d6af59430c4 | note | Detail - Confirm that Erosion and Sedimentation Controls bunds are in place
24e1749d-098c-5633-b8f7-52dd30781149 | note | Acceptance / Conformance Criteria - As-built Completed
b2244651-1130-53f8-819a-503264a18ad3 | note | Standard / Specification - Internal Hold Point
18b3627d-e5e6-5e98-9124-8923d19a61d9 | note | Verifying Document - ESC As-built
e34abb2b-7d31-5a72-8d36-73ca44f14e03 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
973c0068-2e5f-5538-a71a-b6a35215053f | note | Verification Activity: Activity - H
4d57d33f-3ad7-5991-ba8b-648c3cb5fa38 | note | Verification Activity: By - PE
983fc4ef-4eff-406e-b305-22945f7c74c7 | checkpoint | 3.4 - Geotextile
72120312-43fa-5e24-b509-847a91c97e2b | note | Detail - The Contractor shall submit the full details of the Class C non-woven geotextile fabric to the Engineer for approval prior to installation.
f0f9d8dc-6c8d-59d4-847d-2765d52b0e4d | note | Acceptance / Conformance Criteria - Engineers Approval
44e9a790-cfc7-5485-aada-2f8ae889a48b | note | Standard / Specification - PS 16.5.7, Appendix V
431d386c-dba0-52b3-9bac-51502f38cb1a | note | Verifying Document - Material certificate/NTC
a8529494-4d70-569e-83b8-e2cb1b12ae55 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
c083cd39-5f02-52b4-b9f6-a134ed1eb8c0 | note | Verification Activity: Activity - HP
a21c09fa-32cb-56d6-a566-e3f454ee8c6c | note | Verification Activity: By - ENG
76b39f8c-eb8a-448b-90be-ac41c40a1474 | signoff | AUTHORITY HOLDPOINT
afa7b7e3-74cd-4703-b468-466f558f00e1 | checkpoint | 3.5 - Duraflow Drainage Mat
ad988f2a-0211-5e32-bb6f-d11fdf27a73c | note | Detail - The Contractor shall submit the full details of the Duraflow Draininage fabric to the Engineer for approval prior to installation.
71a92b92-ba96-5638-9b25-313d2319e5df | note | Acceptance / Conformance Criteria - Engineers Approval
d39e7856-93e5-5bb2-a501-cb1055fc1f5f | note | Standard / Specification - PS 16.5.7, Appendix V
323c8c16-fe51-5c8d-a22d-7bdae058d8c6 | note | Verifying Document - Material certificate/NTC
6155101e-37a4-5616-af22-7a2631ed011e | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
726f1324-e4b9-5a5f-b2b7-2c21ad36bed9 | note | Verification Activity: Activity - HP
cedc9b99-de25-5968-90b8-b886afd4a022 | note | Verification Activity: By - ENG
5b9b3cc7-fa29-40bd-b379-0c477dfc52c1 | signoff | AUTHORITY HOLDPOINT
491f2df2-14dd-45db-b9ab-8ad8e0db6266 | checkpoint | 3.6 - Crushing Resistance: Drainage aggregare /Structural fill - Used in subsoil fill
1ddeea52-8896-5ef9-8381-40ab8b5a9d56 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
36939094-9238-562c-a65a-aeb011eb4e92 | note | Acceptance / Conformance Criteria - >100KN
70867b77-31c3-5a05-819f-3d1c0e1b0434 | note | Standard / Specification - Appendix XVIII
56202429-6b36-503d-b5ba-ab524af21276 | note | Verifying Document - IANZ Accredited Report
2cb33ebb-8149-598d-ae4e-935e1dd4b62c | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
76b025eb-f5b4-53f7-9677-4a45a1e46745 | note | ○ Results to Engineer 2 wks before importing
15183fac-c8f6-5b7a-85ae-69b012afcd67 | note | Verification Activity: Activity - HP
112acec3-2e2e-5a99-8d75-8eddf89a2786 | note | Verification Activity: By - ENG
911c80ec-3964-447d-9eaf-80484a3bdb89 | signoff | AUTHORITY HOLDPOINT
88256858-1ec6-4c0f-a430-e7830270b840 | checkpoint | 3.7 - Partical size distribution: Drainage aggregate/ structural fill - used in subsoil fill
11b8918c-58c6-5094-ad77-7fb177c88478 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
49cad921-1028-5aae-92c9-afbd03368fa8 | note | Acceptance / Conformance Criteria - Max Particle Size 53mm
dabaf062-81e3-5ff4-ba78-e11549a7f587 | note | ○ Max 10% passing 13.2mm sieve
5fd89330-db66-585a-8590-ae9dbf70441e | note | Standard / Specification - Appendix XVIII
844e1ed0-2425-575d-aca3-51f51fb9d671 | note | Verifying Document - IANZ Accredited Report
5a120142-74db-5779-ae9c-200f24a70b14 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3
17bf6f32-9ab4-55c4-8a83-2a1de4ef2e73 | note | ○ Results to Engineer 2wks before importing
4d6cea27-8388-5e14-a79d-5445a48bd686 | note | Verification Activity: Activity - HP
8857a922-7e8e-58bc-b895-fac8cc4c35ec | note | Verification Activity: By - ENG
3ae9d08f-8f9d-4c21-ac1c-6646542d952c | signoff | AUTHORITY HOLDPOINT
a0a2a071-cc79-441a-90cd-a8d97dc63dee | checkpoint | 3.8 - Weathering Resistance: Drainage aggregate / Structural fill - used in subsoil fill
a24cfd60-b354-5d33-8faa-600a4d172012 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
ff9216a3-a6d2-5a98-b680-f742ebd04506 | note | Acceptance / Conformance Criteria - CA or better
5a2c7eed-f2a3-5c87-aa55-e1a0edaa0a28 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
fafd30cd-e1a3-529b-b7f1-8582b2e72400 | note | Verifying Document - IANZ Accredited Report
d6b4979d-239a-5b52-be8f-3f19a190a6a6 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
e13a9f1d-a759-5777-9321-17027bd10d3d | note | ○ Results to Engineer 2 wks before importing
b6fb1f49-da37-5a22-9cb1-defa8baebfbd | note | Verification Activity: Activity - HP
bc95ee94-45b2-570b-b609-86d28ecc5a2f | note | Verification Activity: By - ENG
4c9530d2-03f6-4129-a5aa-c0debadc9201 | signoff | AUTHORITY HOLDPOINT
4c4b55ef-4ea3-49da-8017-a0f230b1f04b | checkpoint | 3.9 - Magnum Stone Block
e0b87f9b-c4bf-5b59-88e8-fdddeca6dff8 | note | Detail - Magnum Stone blocks are to be supplied by an approved supplier.
830306b8-1877-585c-b7ad-c018c344a7bb | note | ○ Concrete Compressive Strength
59187c6b-7645-5b13-8120-590ee59ad420 | note | ○ Moisture Absorption
a9be04c3-c484-53b5-94a8-8b12f16e666d | note | ○ Defects, chips and cracks
31f406a1-b5db-5eb2-9b96-7817de0ceb4a | note | Acceptance / Conformance Criteria - Minimum 28-day
cdb9f17b-b944-5b20-9ffb-02da50d681af | note | ○ Compressive Strength of 30MPa (min.)
b8756c88-77e8-59b4-8d41-21e37d501aec | note | ○ Less than 6%
3576d09f-12d0-5e28-bd0b-cd3601702c5a | note | ○ Every Block
507dab5b-315e-513d-ae6d-85d790739fba | note | Standard / Specification - NZS 3104: 2003, AS/NZS 4456:2003, Method 14
989cc3e0-e5af-54f3-b668-a3dfee54e9ab | note | Verifying Document - Supplier to provide QA Documents, Visual Inspection
d2e569ae-cf9b-50a0-a605-c215d1011b6f | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6bade04b-73d8-5bac-b2de-912661f2cce7 | note | Verification Activity: Activity - H
2efc1210-762d-5f69-b76a-d711fbd15fb9 | note | Verification Activity: By - PE
08f0cb62-aaf7-4938-8dbd-b97c37218a2b | checkpoint | 3.10 - Subsoil Drainage
90d04f4b-f55c-5ff4-8481-cd0d00a921cd | note | Detail - Shall be 110mm diameter NZTA F/2 compliant smooth bore perforated pipe with filter sock
3bd6accf-aa5d-51b4-a664-711e94c280e2 | note | Acceptance / Conformance Criteria - Engineers Approval
c2d41482-4ac9-5ef9-a642-62af9e918217 | note | Standard / Specification - P.S. 21.5.17
4bb32816-e944-5b8a-ab5b-6b9813c51d2b | note | Verifying Document - Material certificate/NTC
3ccdd567-7fbe-5c34-8fbd-0785610058ad | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
ed8e0ab3-9801-5fe6-ab0f-4ab2496c0c69 | note | Verification Activity: Activity - HP
c9baab86-e95d-5e31-9456-5671e67b3170 | note | Verification Activity: By - ENG
96090585-f721-48ee-959e-6bd7fb7d68ec | signoff | AUTHORITY HOLDPOINT
832f4818-beab-4687-ae2d-7147593d3f51 | checkpoint | 3.11 - Concrete Footing
93c4e86a-57de-5e9d-857f-b895c2b2f191 | note | Detail - Concrete strength shall be min. 17.5MPa
83306119-6578-559d-8f44-60a6298eb333 | note | Acceptance / Conformance Criteria - Engineers Approval
ef292971-ea19-5d30-aa0e-6c288a51c5ca | note | Standard / Specification - A s per Drawing (232735.02-WSP-DR-UDL-0407)
e7af1078-c633-5c17-b785-634f78cd286f | note | Verifying Document - Material certificate/NTC
936e9d23-0a16-5824-9682-30a86ecfa8d1 | note | Testing Quantity Required (based from schedule qtys) -
410da659-16b2-512c-8046-99e37714a8d5 | note | Verification Activity: Activity - HP
ae2e3604-361b-56e9-8bb3-35b6b83b0dc5 | note | Verification Activity: By - ENG
cb66c10a-ce59-4574-9aff-c755643a3259 | signoff | AUTHORITY HOLDPOINT
c88d95a0-7e78-40bb-8d50-70978ce5ac03 | section | SECTION 4 – CONSTRUCTION - CUT SUBGRADE TESTING
078e9bfa-e324-4d24-8b86-6d1a7453860c | checkpoint | 4.1 - Cut Subgrade Inspection
4966c503-0a6d-5648-99e3-90a70400a06a | note | Detail - Engineer to inspect all foundation surface inspections
91345166-63f1-5988-997f-d09c745d21d7 | note | Acceptance / Conformance Criteria - Engineers Approval
2b04e581-c92d-51b5-8511-e66b964979ea | note | Standard / Specification - Appendix V
e70d6cb5-69f1-51bd-86de-ea94cfeed630 | note | Verifying Document - Visual Observation
334cd124-7b15-55b7-915a-e09b3974aa6a | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
2155ff44-7eb3-5623-86bf-400acf9f13c4 | note | Verification Activity: Activity - HP
7338238c-9d14-5d20-bd79-84ae18185867 | note | Verification Activity: By - ENG
f6e7d2f7-a794-435c-8b8d-f6c6d405c203 | signoff | AUTHORITY HOLDPOINT
8fa5bca7-0d2a-4a2e-a698-91adbc618e4f | checkpoint | 4.2 - Cut Subgrade Testing - Cohesive Soil, Shear Vane
a313f818-4790-5965-a58b-108a1afcaf39 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
7deb2482-3c4b-5823-9933-da63dc2545e3 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
bf43be66-61aa-5312-a538-0ebe3cbb382c | note | Acceptance / Conformance Criteria - Average Minimum SU:
c9cb7131-8463-5479-8b44-3b1be5b2f276 | note | ○ > 60kPa
90151947-e617-569c-8e38-091edc58b011 | note | Single Test Min SU:
1f0c0f5d-076d-537e-912b-b7afc4bbeaab | note | ○ >50kPa
01ae60de-5343-549f-a734-20fe6426bf36 | note | ○ 2-3m deep
3a2d0cc3-8ede-5917-becb-53ef2b7f24e2 | note | Standard / Specification - Appendix XVIII
008f2704-7e3f-5b28-b1ab-89b8f5a899f8 | note | Verifying Document - Shear Vane Report
72e49f0a-6098-527d-987c-140f889bb147 | note | Testing Quantity Required (based from schedule qtys) - 0.5m interval, 4 test per 400M2
31e1930d-0fc2-5ced-9b37-6eb44dd6d6ac | note | Verification Activity: Activity - I
f97a6418-d192-554d-9b7b-48eb3b74f1fe | note | Verification Activity: By - SE
2b9161e3-e4dd-4fc8-b3a1-978d55c490a5 | checkpoint | 4.3 - Cut Subgrade - Import Structural fill, Release of Hold Point
d856b3b9-8cc2-59c4-9a8d-c72f9e02b2d3 | note | Detail - To release the subgrade hold point and be able to start placing the Magnum Stone Blocks, the Contractor shall provide written certification that all inspected and tested subgrade complies with the requirements in PS 16.6
56a57b8b-9912-585d-a90b-3893e111c49f | note | Acceptance / Conformance Criteria - Engineers Approval
638c4425-2e3f-52fa-8422-578cae93afdf | note | Standard / Specification - PS 16.9.3
4383f110-fb20-5311-953f-acdce342b7bf | note | Verifying Document - CONQA Approval
d242baa9-6ede-5d3e-b1c0-2ba24bad9c8d | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
1a0e1cdd-20d4-548b-92a8-7a83df31f5f2 | note | Verification Activity: Activity - HP
881c4259-8065-5d84-b109-899872330194 | note | Verification Activity: By - ENG
81760649-5314-4d63-96a7-87293c54b60f | signoff | AUTHORITY HOLDPOINT
de1defa7-5737-4133-8b51-163b228021db | section | SECTION 5 – MAGNUM STONE BLOCK
91ca2aef-e4ce-4f31-8f7e-1420e679a032 | checkpoint | 5.1 - Leveling Pad and Duraflow Drainage
b3ab0cf7-9a52-5f32-99ee-2ef21e1b4eb7 | note | Detail - The Contractor shall construct a 150 mm thick levelling pad on top of the subgrade using AP40 to accept the Magnum Stone Block wall.
f17895f1-0805-5d9a-87d2-b0f892382cf3 | note | ○ Aggregate to be placed on geotextile filter fabric
72118142-85c1-5947-bb15-4b376d61710d | note | Acceptance / Conformance Criteria - Engineers Approval
e7893ad2-aeaf-5d76-bc7c-8c9cfeeee559 | note | Standard / Specification - As per Drawing (23273502-WSP-DR-GEO-0427)
f7f2e81e-c954-5467-ab58-b1000fae4a88 | note | Verifying Document - Site Photo / Checksheet
b778ae58-0778-5b1c-8e51-abb2ee35ff78 | note | Testing Quantity Required (based from schedule qtys) - Prior to Magnum Stone Block installation
f676e992-4bf1-5457-bf7a-ea19a3db3b17 | note | Verification Activity: Activity - I
7a09a04e-edfd-5bbb-a88b-34743ea8cb86 | note | Verification Activity: By - SE
c9851b31-eab8-4ad8-bd83-8c40455b2b36 | checkpoint | 5.2 - Installation of blocks
f3ec08db-17d9-55d9-8f45-05ce62dfa9fc | note | Detail - Blocks to be installed to the height and location as detailed on the construction drawings. The table below details acceptable tollerances
9f7f7479-c3a0-5278-abfc-260b3bd1ad4f | note | – – – – – – – – – – – – –
6e6ae7c1-b852-5973-bc64-9e85e633cd29 | note | Table 4: MSE Tolerances
5984e9aa-5632-5195-993c-b66e3089bfb6 | note | Element ¦¦ Vertical Position ¦¦ Horizontal Position ¦¦ Vertical Alignment ¦¦ Horizontal Alignment
c76fe8f1-9e44-5bdd-be57-adc2f12e43af | note | – – – – – – – – – – – – –
32c0ca44-056d-55fb-b74a-5debe8667437 | note | Soil Surface ¦¦ ±100mm ¦¦ N/A ¦¦ N/A ¦¦ N/A
b267021c-2ab5-5e0b-b6d6-e1e21a31a8bb | note | Facings and wall structures ¦¦ ±50mm ¦¦ ±50mm ¦¦ ±20mm in 30m ¦¦ ±20mm in 3m
112292a5-5655-57cf-8925-55f7fd390669 | note | Footings or supports ¦¦ ±50mm ¦¦ ±50mm ¦¦ ±20mm in 3m ¦¦ ±20mm in 3m
02bfb0de-fee4-5734-abf0-a5bad677b13f | note | – – – – – – – – – – – – –
91906c69-ce71-56ce-a928-d1dbe82d2e71 | note | Acceptance / Conformance Criteria - Engineers Approval
cf83a15b-3af1-5918-95d2-af5c89ce17ab | note | Standard / Specification - As per Drawing (23273502-WSP-DR-GEO-0427)
abb846c9-6839-5cb8-b646-f98aecc58793 | note | Verifying Document - Site Photo / Checksheet
7654ebbf-ebf0-5d24-bf62-f0b3af56cacb | note | Testing Quantity Required (based from schedule qtys) - Each layer
85840090-dd3b-525a-9961-792048a95504 | note | Verification Activity: Activity - W
59b7baf3-1624-57f4-9b5d-ac633db4c7bf | note | Verification Activity: By - ENG
9b89b6c4-492b-4a41-9212-66eee073f4a8 | checkpoint | 5.3 - Drainage Installation
4390c31f-834c-5a6a-a2c9-caea694e3e10 | note | Detail - A 110mm Drainage pipe wrapped in filter sock is to be installed along the internal perimeter of the blocks.
c7e31b03-4e9e-5552-b89c-80266729b564 | note | ○ Core through Magnum Stone blocks at 10m c/c, install PVC subsoil outlet.
330634ae-7fe5-52d3-9d3b-8a5dfe9934a7 | note | ○ Internal block void hardfill to be 20/40 drainage aggregate or similar approved by engineer.
da12628e-6da3-5a4a-9b7c-b19f3ea0ccaf | note | Acceptance / Conformance Criteria - Engineers Approval
1c5cd7d9-6be5-5569-8901-3542324e8e32 | note | Standard / Specification - PS 16.5.8, PS 16.6.10, PS 17.6.3, TNZ F/6
bdda7823-9ad3-5811-afb9-b138feeb45c7 | note | Verifying Document - Delivery Dockets/Installation Checksheet
24ced945-ad5f-5859-a4f2-aebd8d7b93d4 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
604cf055-3884-5471-a5ae-ab64b6a3b0b8 | note | Verification Activity: Activity - W
ae8e9771-113a-5a21-b87f-f3d54c1366cb | note | Verification Activity: By - ENG
33d15790-135b-498d-bef2-6ef3d7bcf711 | checkpoint | 5.4 - Duraflow Drainage Mat
40f038f5-cc47-53c5-a3d4-cf7fef00eb8f | note | Detail - Side-to-side overlap: Ensure at least a minimum of 500mm overlap between adjacent rolls and at any joins.
94219197-e7ce-5adc-94c1-fc73dcc5dc61 | note | Acceptance / Conformance Criteria - Engineers Approval
b83f13d2-8a72-5163-8e65-5074e24e50d7 | note | Standard / Specification - As per Drawing (23273502-WSP-DR-GEO-0414)
1b6df36b-9034-54ea-b58b-23fed381034b | note | Verifying Document - Site Photo / Checksheet
a72d53c6-aaf1-57bc-ae12-af5e06963d46 | note | Testing Quantity Required (based from schedule qtys) - During Insallation
eb4dec72-357a-5f8f-aaaa-3f5910c5e24c | note | Verification Activity: Activity - W
603cd737-27d9-51a2-a653-cc3a82d83025 | note | Verification Activity: By - ENG
5ef79124-5b22-481b-9ae3-949ba0dbb841 | checkpoint | 5.5 - Backfill Installation
9c322c76-e8d3-595b-8fa3-10bfa90e8da5 | note | Detail - All backfill is to be installed in 300mm lifts and tested as below
86cb3e73-4cec-5c38-a9f4-dce9df37fb61 | note | Acceptance / Conformance Criteria - Engineers Approval
673b2d64-006a-5f70-876c-d6d4407a0c3a | note | Standard / Specification - As per Drawing (23273502-WSP-DR-GEO-0414)
d2a11830-8bb3-5d46-8a45-e24579870d4c | note | Verifying Document - Site Photo / Checksheet
4d7beec3-a462-5be0-9964-b17d7e1e5ffa | note | Testing Quantity Required (based from schedule qtys) - Each layer
3d3e6737-bab7-523c-817e-43d52a94e5c7 | note | Verification Activity: Activity - W
cfebde07-3d0f-5cfc-bfae-adb8b3be00ee | note | Verification Activity: By - ENG
b088797d-c358-4ea6-9b93-321591ecccde | checkpoint | 5.6 - Compaction - Clegg Hammer
1d8caae4-dabc-5828-80ff-2dee8d37358d | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
7eed011c-92e3-5062-b353-1c0291087290 | note | Acceptance / Conformance Criteria - Structural Fill
7c0c214c-a72d-5d8e-ab22-5d3d13647d23 | note | ○ Min CIV 18
a63682ba-b983-5330-b0cb-79175889696a | note | ○ Ave CIV 20
22b6e4ec-f381-5f7f-8500-a8da62345d7c | note | Non-Structural Fill
ea2e75cc-c5f2-5b87-a15e-7664bf51ba6a | note | ○ Min CIV 10
9c80677b-30ca-511c-8631-1acbcf384bc8 | note | ○ Max CIV 12
76251f90-8b1d-5c7e-b3d9-82360ddb86c1 | note | Standard / Specification - Appendix XVIII
3a234527-abca-5419-8d55-6a1965b1dffb | note | Verifying Document - Clegg Hammer Report
aec4a792-fc32-538c-8cd4-1ac82dbd69e1 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
92110cc6-e993-5993-ad69-218ca49d2051 | note | Verification Activity: Activity - I
e3c6a2f9-ad0e-5983-9f52-2ae8b91833ca | note | Verification Activity: By - SE
dab6dd41-c927-4d0e-adf2-40dcbc8d5348 | checkpoint | 5.7 - Compaction - NDM
b3cb1a54-fe43-57b6-bb25-a88ff2304c96 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
a969f7b4-9c13-509f-ba95-37b977c1a2a3 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
3619edac-8b2d-592b-89ac-37f989fab0ff | note | ○ Min >92% of MDD
e2a08f5c-ad1f-54b2-aa68-bb45db779135 | note | Non Granular Material:
750252d2-9b25-513a-9723-9ebfb34b5842 | note | ○ Max Air Voids 8%
639cc8c9-98ff-5bc7-8bd1-15e78619c94d | note | Standard / Specification - Appendix XVIII
63ec25f7-88f3-5035-9bab-b1f6fa76b256 | note | Verifying Document - IANZ Accredited Report
2e3494d6-707e-5cfb-b482-44674cac65aa | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
86c4efab-cb27-5ffe-84e9-c95ccc3a5a92 | note | Verification Activity: Activity - I
c79460b5-5c1c-57e5-ac2b-1dc1935e1ef1 | note | Verification Activity: By - SE
da68e9dc-43cd-4fc1-8d39-190e7c1f8bc1 | section | SECTION 6 – AS-BUILTS
7c8dc8b8-44c8-4813-aa6d-bece4413ffeb | checkpoint | 6.1 - As-Builts
4e553997-2b67-529e-8958-300ea4f7c4cc | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
a37e1df5-e2ee-5a37-b035-45a8a9a76664 | note | Acceptance / Conformance Criteria - As-build record
45894fc8-137a-5021-af95-1d44f34c2b62 | note | Standard / Specification - PS 16.7.6
acf19db7-6320-5327-a5aa-a5629606adc1 | note | Verifying Document - Survey Records/redpen markups
80617891-f2aa-5bd9-a31f-91cdb0f09003 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
98d2478e-c7de-513d-b007-0c91f4f5a031 | note | Verification Activity: Activity - D
6970ac0f-cf1d-5b9c-bb36-f593a6112319 | note | Verification Activity: By - SV
39585a62-3fde-4f11-87f2-2077e1d39344 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
9b83c706-5358-51e6-abd9-9638b7689e66 | textbox | Contractor's Rep Name:
17e73e83-df1a-59a0-a8e5-08ece97c472f | textbox | Engineer's Rep. Name:
03cc225a-fc97-5e9b-bab4-610aac83189c | date | Date:
42cb9a47-2b8f-4efc-a345-87597bbbb30e | signoff | Add Signature
09e5c33d-27b2-4c25-a35c-69f98c50f0a2 | checklist | DN1210-SP2-019 ITP Wetlands 02 Earthworks Rev 1 | itp | DN1210-SP2-019 ITP Wetlands 02 Earthworks
37629b45-952c-4808-9f38-fae45d9093c7 | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
a793eec6-6446-4104-93e4-3bdc478e1d6f | checkpoint | 1.1.1 - Earthworks Methodology
054bfca3-ed7d-5366-af16-91667b128c8c | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points for review and approval prior to works.
30b83990-6d71-51c5-a738-b4acbb787635 | note | Acceptance / Conformance Criteria - Engineers Approval
eff19231-0fb2-5f2f-bbba-97d8d79a10b1 | note | Standard / Specification - Appendix V
bad25b23-25ab-53cd-9a6e-9789f511488e | note | Verifying Document - Approved Methodology
40248654-9682-5e83-96fb-ec293a3ef194 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
d78cbda9-4d99-5480-8467-03be47834dcd | note | Verification Activity: Activity - HP
1944120b-61f0-5993-b0b0-cb0e4986bf3e | note | Verification Activity: By - ENG
cf1a4ab2-d6ec-4cbb-b54e-c2e123edaf87 | signoff | AUTHORITY HOLDPOINT
5daa1a5d-988b-439d-9467-9fa83b4cc2e0 | checkpoint | 1.1.2 - Ecology Sign Off
72fe5da5-a92d-5aa2-8dfc-4d26b9f17596 | note | Detail - Confirmation from Ecology that earthworks can proceed
b8bb37d9-1da1-5aa0-841a-d5c0f4a43ed2 | note | Acceptance / Conformance Criteria - Email
6b4606ed-94c8-55ea-8edb-37590ffc906c | note | Standard / Specification - Internal Hold Point
8e05bae5-e101-5ba7-8bc1-22f58df77337 | note | Verifying Document - Email from Ecology NZ
9f4c9b79-7bc2-563a-bf6f-89c5576176c9 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
c9d907e8-df7d-539b-a295-48ce9022d643 | note | Verification Activity: Activity - H
f1989a6a-e6f2-5ff3-b5f1-fd036567607b | note | Verification Activity: By - SE
02a8bf25-5734-4b24-b5df-8e1bc983c85f | checkpoint | 1.1.3 - Erosion & Sedimentation Controls
aff695f1-6a1c-5601-b681-c161ccc471bf | note | Detail - Confirm that Erosion and Sedimentation Controls are in place prior to earthworks proceeding
025a52eb-d22c-5c3e-877e-80fccfb35971 | note | Acceptance / Conformance Criteria - As-built Completed
7c158ba9-5143-51cd-847d-75311f49c03c | note | Standard / Specification - Internal Hold Point
66d66516-14ff-5957-bd5d-e2d636c238d8 | note | Verifying Document - ESC As-built
57d8885d-d820-5f05-badf-f83e88d4f60d | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
e84a5ae4-e612-53ff-8056-b7d388ebe80f | note | Verification Activity: Activity - H
3235e971-98a4-5ffc-9870-8492a6f5e938 | note | Verification Activity: By - SE
21a56b3a-5ab6-49cd-8f6b-3a6129c28be8 | checkpoint | 1.2.1 - Design
5b51ed1f-6309-5c0b-820d-f4cc94d2e0b9 | note | Detail - Ensure that Design is approved and Drawings are of the latest revision
9847076c-63c1-5d7b-878b-8e80f5ae73ac | note | Acceptance / Conformance Criteria - Visual inspection by Engineer
6245df46-07cd-5b4c-93a5-1d919d5e3acb | note | Standard / Specification - Internal hold point
70e12f02-e4f3-56b3-889a-1dfa70f4420d | note | Verifying Document - Check Drawing Register
694c6596-80b0-5aee-8df3-bf884f6b4bfa | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
31ed6ca8-85a3-5640-ab2c-f536891e1e5d | note | Verification Activity: Activity - C
69298d3b-706d-5943-a1df-97d7dbc09c2d | note | Verification Activity: By - SE
18457d1d-bed1-40fd-a576-b5735d61b4ad | checkpoint | 1.2.1 - Design
53960b40-4248-5327-9425-699eb9db9953 | note | Detail - Site check for service features, any required design amendments to be resolved on site
44ce6bfa-437e-5019-a6c0-50198f17e2d5 | note | Acceptance / Conformance Criteria - Visual inspection by Engineer
75d7258b-b738-5018-bcda-462c44435095 | note | Standard / Specification - Internal hold point
8684122c-1718-5d10-9c43-a83bc9fd7a09 | note | Verifying Document - Engineer notified of design amendments to be resolved
b0540ec2-8d7a-5a65-89a1-aac9ab6a12de | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
ca198581-659f-58a8-90bb-b72e5b761c56 | note | Verification Activity: Activity - C
9fb5636c-2327-516b-82b4-ba87fe953941 | note | Verification Activity: By - SE
e963df2f-3a54-4cce-869e-2c9d639090da | section | SECTION 2 – IMPORTED MATERIAL TESTING - ALL TESTS TO BE NO OLDER THAN 3 MONTHS
480bdf53-333f-488f-bef2-248dc5ce6ca4 | checkpoint | 2.1.1 - Weathering Index of Coarse Aggregate
9c046ca7-1f00-5735-840e-4529c90ee713 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
3328a187-ec42-5c71-a3e2-ab60bd216b2a | note | Acceptance / Conformance Criteria - AA to CA
6f942fdb-01c2-5efe-86b1-5a975fc4f305 | note | Standard / Specification - NZS4407:2015 Test 3.11 PS 21.7.4
2cf66c83-becf-51cf-b8e0-72fa96e356f1 | note | Verifying Document - IANZ Accredited Report
8fcf24e8-a741-5a0f-a214-c858aa4197ba | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
998325a5-cf91-594b-b920-e3380e8ba598 | note | Verification Activity: Activity - HP
a8c8d104-df2b-5499-8c2c-0eca2c3e4feb | note | Verification Activity: By - ENG
978ff36d-8dfb-43e3-be4e-eff6540a44a7 | signoff | AUTHORITY HOLDPOINT
9ea418a4-62be-495a-8007-d6a3f9be79da | checkpoint | 2.1.2 - Crushing Resistance of Course Aggregate
ffd79e96-5594-51a2-9135-c8cfa9b12fc9 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
f035a9b9-ca60-5f72-b29a-22c71e82fdfe | note | Acceptance / Conformance Criteria - > 150kN
dec26252-8190-546f-a345-e8f47c977158 | note | Standard / Specification - NZS4407.3.10 PS 21.7.4
6e868565-68ee-533f-86d9-b1df5f2767d9 | note | Verifying Document - IANZ Accredited Report
3215b048-1224-5946-873b-1403b6d0004d | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
ddbd72ac-eed5-5737-8402-5db813376ccc | note | Verification Activity: Activity - HP
5eea8492-42d8-572a-b870-9a83bb4b5306 | note | Verification Activity: By - ENG
a4cc46e9-dfac-4eac-b99f-c267632d1949 | signoff | AUTHORITY HOLDPOINT
3dbf686b-2b4f-415b-a93f-ff6b17d5638f | checkpoint | 2.1.3 - Solid Density of Aggregate
543b9469-6ec4-5923-b4ae-76e3c23b802d | note | Detail - NZS4407:2015, Test 3.7.1 - The Solid Density of Aggregate Particles
1b2bf71c-0c85-538e-952d-b659a49057ee | note | Acceptance / Conformance Criteria - ≥ 2.65 tonnes per m3
04a61247-fe37-59be-9724-49f579f02133 | note | Standard / Specification - NZS4407.3.7.1 PS 21.7.4
1ef0c93d-4e40-526a-b5b4-7a936a0470fd | note | Verifying Document - IANZ Accredited Report
4eb364db-7fa8-5936-a767-21fafc36aa57 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
6f0b3b02-94cd-5160-b974-65e81873ced6 | note | Verification Activity: Activity - HP
b5ffebcf-a3f4-5f60-b321-4900a6f31c1c | note | Verification Activity: By - ENG
f662e7e7-264f-4961-878c-3b48feae604f | signoff | AUTHORITY HOLDPOINT
41573884-7f79-4608-b5e3-c9e4d746b348 | checkpoint | 2.1.4 - Grading
98a07fb6-a8ac-5c6f-8922-965278691cb0 | note | Detail - NZS4407:2015, Test 3.8.2 - Grading of Aggregates by method of dry sieving.
627950e8-500f-5ecd-9ee5-6a943f3c3968 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
b5d73ab5-b896-58e4-9e73-4e4185311196 | note | 230.0mm ¦¦ 85% passing
60e8bfff-e7cc-5f2e-9bcb-8135786b4f7d | note | 150.0mm ¦¦ 50% passing
178f7810-3feb-546d-ac52-e07cde2354ac | note | 95.0mm ¦¦ 15% passing
87f71e25-0f0c-50ac-8685-66c14af5bd75 | note | Standard / Specification - NZS4407.3.8.2, PS 21.5.14
a0b2caf9-4afd-5566-ba2e-ec3c497725f5 | note | Verifying Document - IANZ Accredited Report
ddb68d71-154d-543d-954c-4c12ce88f0aa | note | Testing Quantity Required (based from schedule qtys) - Percentage Passing %50
5cf5e1d7-b75f-5c05-ad40-4918e15d56d1 | note | Verification Activity: Activity - HP
90af3d17-128b-5c80-a023-c332ce0e6817 | note | Verification Activity: By - ENG
10633f23-9529-43cc-943e-8a37dbd7afff | signoff | AUTHORITY HOLDPOINT
51367c4f-9cc8-4086-b86d-f8efb79bd9b0 | checkpoint | 2.1.5 - Point Load Strength
47b788b9-c779-52a7-85f2-b9402caf2a30 | note | Detail - ASTM-D5731: 2017, Standard Test Method for Determination of the Point Load Strength Index of Rock and Application to Rock Strength Classifications
959b7c39-51c8-5db9-a1f8-1c8d737a71ce | note | Acceptance / Conformance Criteria - >1.5 MPa
f3bb8b69-0fae-53d8-a86f-8c4090adb164 | note | Standard / Specification - ASTM D5731 PS 21.7.4
6db4ff7f-1f3e-5fba-8c58-0e88d0f95ad9 | note | Verifying Document - IANZ Accredited Report
48fdb930-8d42-584e-bad4-a7ccd3eade6e | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
00456052-6219-5c6b-bc59-8108bbc93b30 | note | Verification Activity: Activity - HP
b829e64b-a0ab-5e4c-affe-fe179b78dcf8 | note | Verification Activity: By - ENG
097b3afa-27b8-4410-8213-4cde76f32369 | signoff | AUTHORITY HOLDPOINT
5ff9aa1a-1b3d-446a-9d31-5cdf0fa386eb | checkpoint | 2.1.6 - UCS Rock
7868e5c4-1d72-59de-9486-e06a860f734c | note | Detail - AS4133.4.2.1: 2022, Method 4.2.1: Rock strength tests – Determination of uniaxial compressive strength
3f8e1f25-84bb-51bc-81bc-14f7fd6d7458 | note | Acceptance / Conformance Criteria - >30 Mpa
0a06586b-721d-5825-9a73-59e804235c4f | note | Standard / Specification - AS4133.4.2.1 PS21.7.4
105359d2-6be3-51bf-b3b2-67ad9f696dc1 | note | Verifying Document - IANZ Accredited Report
56290866-b907-5a31-8ff9-491674bb8388 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
02b81d9c-52ad-5ec1-9cad-c90ccf45b27e | note | Verification Activity: Activity - HP
95cba049-2161-5e6f-bb3b-e68cd2c5209c | note | Verification Activity: By - ENG
bdea4eab-e673-4009-a243-d5e9dd3f7c5b | signoff | AUTHORITY HOLDPOINT
51fd0b81-43e1-466d-9e19-1eed5591a19d | checkpoint | 2.2.1 - Crushing Resistance
04dbeeac-a7c3-5051-9a22-23fe8deccdd8 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
6dfe80b9-de4b-5de9-9e98-0c451c4a064b | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 100kN
ebc3c30c-bc55-5c48-99f8-745210f1a865 | note | Standard / Specification - NZS4407:2015, Test 3.10, TCC-IDC-IT-4.3.1-4.7.1
58fd2c68-631f-57fc-8367-8e71604e13a4 | note | Verifying Document - IANZ Accredited Report
80a41d29-7e78-5fbb-94f0-42bf14f35910 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
32fa437c-ead6-571c-9e44-2c2c0c5f9bfa | note | ○ Results to Engineer 2 wks before importing
63c208fd-6d0a-5269-a764-d99992802e18 | note | Verification Activity: Activity - HP
8917d98c-899d-5903-9463-991c637a1e01 | note | Verification Activity: By - ENG
aca737f4-3833-41b1-8cea-27a4b75383f0 | signoff | AUTHORITY HOLDPOINT
09e9fce1-90cd-41dc-bfb3-b63be2eb3cd1 | checkpoint | 2.2.2 - Soaked CBR
83a65585-4da5-5543-91c5-bb43e721f73b | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
402a0bd5-cbb3-5c91-bb35-754219c7c662 | note | Acceptance / Conformance Criteria - ≥60%
d4f3c7ec-1a69-508f-baef-fd9a6ccc3d3e | note | Standard / Specification - NZS4402, Test 3.15, TCC-IDC-IT-4.3.1-4.7.1
b913ae4a-ce8d-59bb-9225-14cc3570086d | note | Verifying Document - IANZ Accredited Report
d8775afa-cfa0-54cd-9546-fa3554645c6c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
1cd393f8-2569-5b03-a0e5-a30841da812a | note | ○ Results to Engineer 2 wks before importing
f57c5c64-6a33-5273-a6dc-3f0096a40599 | note | Verification Activity: Activity - HP
6ca5dbd9-0a56-564d-8b0b-31ff01ff03b1 | note | Verification Activity: By - ENG
f7ead76e-2a9a-4aa3-8bb6-4b72b9f4fd82 | signoff | AUTHORITY HOLDPOINT
1e70df83-4a9c-449f-9861-193a459ed90f | checkpoint | 2.2.3 - Weathering Resistance
d4309649-a7af-5830-9f86-02e476e9c8e9 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
02c758b9-49b2-5384-ac6d-932ab602e126 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, CA or CB
2b0ed91a-1bf7-5f5f-b1a2-76e1d6354d92 | note | Standard / Specification - NZS4407, Test 3.11, TCC-IDC-IT-4.7.1
adbcbd27-c578-5db1-afa7-4f8658f45d12 | note | Verifying Document - IANZ Accredited Report
867d4db3-27b8-5af9-bf14-c5d2f58c727e | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
ca394b77-6e09-561e-8e0e-c72224bcf4d2 | note | ○ Results to Engineer 2 wks before importing
f37000e3-3001-5419-911a-5f26e9817717 | note | Verification Activity: Activity - HP
d6593a13-b479-542d-bbd9-758a4867ba2e | note | Verification Activity: By - ENG
4767f5c7-fec0-4238-9a58-88015bb47e98 | signoff | AUTHORITY HOLDPOINT
23ca1bc4-dca3-498a-94bd-6cf201509220 | checkpoint | 2.3.1 - Particle Size Distribution
3b37e9ba-0523-597c-9b2a-d31cb582dc7a | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
8e36e6a5-804d-555f-9886-41ba957596cb | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
2ff99ff5-7ad7-5b7a-bb96-fda1bfc2f670 | note | 63.0mm ¦¦ 100% passing
8bd4c7d3-c4d8-55be-92d5-526a626bce8c | note | 37.5mm ¦¦ 68-90% passing
3dd4ac12-e27c-5767-8f5a-5999ed0f0100 | note | 19.0mm ¦¦ 42-76% passing
53ec1b71-d3b2-5cd6-af57-9c1f6e9e255d | note | 9.5mm ¦¦ 26-58% passing
a754f28b-1f90-5e47-9afd-77d9b9f5833d | note | 4.75mm ¦¦ 16-44% passing
d568da2c-a1f3-5416-9121-1c4882dda331 | note | 2.36mm ¦¦ 10-33% passing
b2ed8a69-5f6a-55d2-ba5b-3f4816f9fdeb | note | 1.18mm ¦¦ 6-24% passing
3ae7a040-85b3-53f4-9ce6-74a92409ba44 | note | 0.425mm ¦¦ 3-14% passing
425078b0-c6b8-5b3e-94cb-819c12007780 | note | 0.075mm ¦¦ 1-6% passing
1e5c3c4e-df29-51d9-bd60-bfab2672cbb1 | note | Standard / Specification - NZS4407, Test 3.8.1, TCC-IDC-IT-4.7.2
f3541fa0-4826-5c5a-b00c-c7f8f5afb0f1 | note | Verifying Document - IANZ Accredited Report
dc5ee125-5d87-55da-8c72-54941962afd1 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
1938c9f0-e0b9-531f-aadf-a0c4fee5f2b6 | note | ○ 0-400 - 2 tests
91637deb-8859-528c-b167-4bfd1d66f339 | note | ○ 400-1,500 - 3 tests
48edabc0-ae7c-5276-b461-a0a48ff421fa | note | ○ 1,500-4,000 - 4 tests
6f7f7321-6581-5ba3-bda1-71e22d58ba5f | note | ○ >4,000 - 1 test for each additional 1,000m3
5e3326e3-9c7d-520b-b4e4-af97791c570b | note | – Results to Engineer 2 wks before importing
8cadcbb8-fec0-5966-b1fa-cbd7d4aebb5c | note | Verification Activity: Activity - HP
80da9f6a-1528-556e-8273-79c085abc177 | note | Verification Activity: By - ENG
4190f52f-6c96-48f6-8c6e-8238e2dcbf7b | signoff | AUTHORITY HOLDPOINT
566d0d2c-57b6-4fa2-86a8-0d365013caf6 | checkpoint | 2.3.2 - Shape Control
c93277c8-b922-52b5-8457-2cb761f22efe | note | Detail - Tolerance allowed from approved grading curve (%)
1ac5ef67-ac3c-5148-a46e-41d64af9b98f | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
ee811c16-9831-58b9-8425-70c1b59248ef | note | 37.5 – 9.5 ¦¦ 34-50%
a4cea1cf-abde-5bde-95ba-33ecfc3f2791 | note | 19.0 – 4.75 ¦¦ 18-40%
fc2a5b0c-b396-5f53-9634-0cd7a3cd2d47 | note | 9.5 – 2.36 ¦¦ 12-32%
e739334f-e88f-5fce-8304-5d634cf80eef | note | 4.75 – 1.18 ¦¦ 6-24%
8a4e249e-7d07-5ebe-ad58-951d868f72ae | note | 2.36 – 0.6 ¦¦ 2-20%
6b2fb0ba-ae22-5628-97e9-3d0be8a2ffca | note | 1.18 – 0.3 ¦¦ 0-15%
6ac16e51-70bc-5894-b1c0-d4e3a7846394 | note | 0.6 – 0.15 ¦¦ 0-12%
ec4fb6d3-e81e-5def-b6e5-76de13f7cc18 | note | Standard / Specification - TCC-IDC IT-4.7.2
553cd738-9eef-59b0-a7d1-f1ec95ee4abf | note | Verifying Document - IANZ Accredited Report
c43a763f-9512-5758-86b0-a341c4350711 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
a8d1f02a-c177-54b7-9f11-9e1f163c4e1a | note | ○ 0-400 - 2 tests
82b464de-513a-5f74-a190-32fa53ed4a6b | note | ○ 400-1,500 - 3 tests
e18569db-7510-584a-83fc-fd40d4dac848 | note | ○ 1,500-4,000 - 4 tests
62d78c89-5104-5396-8a49-951c77fc4fa1 | note | ○ >4,000 - 1 test for each additional 1,000m3
80bd5215-580f-54ef-b80d-b23be18d3183 | note | – Results to Engineer 2 wks before importing
9cf5a8c4-8b46-504f-8b9a-2ecb5987ef08 | note | Verification Activity: Activity - HP
56114f9c-bc07-5715-9cc2-26894a8a1f48 | note | Verification Activity: By - ENG
8405f5aa-9238-49cd-ad74-77c8d4d4bbbd | signoff | AUTHORITY HOLDPOINT
fbfda797-5857-4673-8f56-ed616c5cabe2 | checkpoint | 2.3.3 - Maximum Dry Density and Optimum Water Content
39c102fb-7fbc-508e-b230-36584e78cbb7 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
3f19dfbb-91a1-5389-8497-d762aa849937 | note | Acceptance / Conformance Criteria - Report Value Only
0390d678-b27c-5783-8bab-054eae1d6d6c | note | Standard / Specification - NZS4407, TCC-IDC-IT-4.7.1
f59493ab-efdc-5702-8b1a-5f4d243b613f | note | Verifying Document - IANZ Accredited Report
0e81b4a3-cae1-5d79-85cc-2d0016791fd5 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
6e666336-99f0-5f5b-b579-8aeeafe30c80 | note | ○ Results to Engineer 2 wks before importing
3a5452e0-ec17-52bb-b9e8-b5a5c3cb47b8 | note | Verification Activity: Activity - HP
1ed1b80d-7304-5378-92d8-4bd2475eca1c | note | Verification Activity: By - ENG
3fc893c8-10c8-4e27-bf66-21bf6b7f9736 | signoff | AUTHORITY HOLDPOINT
7a529ab9-784f-4aca-93f0-12bde6f83f43 | checkpoint | 2.3.4 - The Solid Density
4fbdafe8-5f7b-5c57-8e39-7c7f89ea5757 | note | Detail - NZS 4407:1991 Test
ce8896c0-d787-5b78-b328-a9291ecc2797 | note | Acceptance / Conformance Criteria - Report Value Only
68059677-a683-51cb-9446-00cfdbf735b8 | note | Standard / Specification - NZS4407, TNZ B/02:2005 7.5, TCC-IDC-IT-4.7.1
3c86b167-6ff3-5150-8dbb-fc769ce49253 | note | Verifying Document - IANZ Accredited Report
25efee8a-a902-5c1e-a303-255a8af94b42 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
8788a7f3-04f4-530a-a047-42501f0cdc00 | note | ○ Results to Engineer 2 wks before importing
9095cf2c-11aa-581f-8732-1129a631bff5 | note | Verification Activity: Activity - HP
91973882-4cf6-5ac5-909b-03cc13ab7926 | note | Verification Activity: By - ENG
b8c75961-dfbe-4291-8e42-c13ded17e628 | signoff | AUTHORITY HOLDPOINT
8f1dda74-8e70-427a-b50e-da08910ea5a6 | checkpoint | 2.3.5 - Plasticity Index
a7b15c35-4a1a-5a56-b8dd-0e6cab2c358c | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
9d54aa0d-bf74-5d50-ae89-22122caacfdf | note | Acceptance / Conformance Criteria - ≤ 8
b9c6fa81-a192-52c5-a87a-21f33f3018e3 | note | Standard / Specification - NZS4407:2015, Test 3.4, TCC-IDC-IT-4.7.2
2d508ba0-8390-5b8e-8c7f-3f606910fefa | note | Verifying Document - IANZ Accredited Report
6897d98e-2b01-53a3-aa07-27eed9ff8b2f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
79d83b33-ab16-5edf-a673-a0c5e03a0218 | note | ○ Results to Engineer 2 wks before importing
c527f5d9-2b81-5405-901c-7867fbbb9383 | note | Verification Activity: Activity - HP
f90d9867-0f3e-58a1-be55-84e15133b69d | note | Verification Activity: By - ENG
e4caf99a-d4a5-43ea-b74b-3ca329b4c1c1 | signoff | AUTHORITY HOLDPOINT
fdd320f2-c145-44f0-bd20-ad02e82a7c4e | checkpoint | 2.3.6 - Sand Equivalent
1fa61eaa-f293-588d-96ed-9cc9b47f7bc8 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent Washing method
1ec847ff-6ca4-508c-8cac-34b5122439d1 | note | Acceptance / Conformance Criteria - ≥25
87e076a9-720d-5f14-90d8-9ac7a31289e8 | note | Standard / Specification - NZS4407, Test 3.6, TCC-IDC-IT-4.7.2
100e01df-85b8-5cf7-b305-13ab0ec31c95 | note | Verifying Document - IANZ Accredited Report
29e0711c-e997-59f6-8079-b9a3010c4b57 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
023c34ea-842b-5d96-b894-e8a50f8698ca | note | ○ Results to Engineer 2 wks before importing
a70b7149-649b-589a-8efc-d9b7a1755342 | note | Verification Activity: Activity - HP
775ccc29-687c-5ff9-9bc4-8edfc6f25582 | note | Verification Activity: By - ENG
c7d8ee43-a5d7-4bac-8ba2-6624629b069e | signoff | AUTHORITY HOLDPOINT
bd2ef073-8648-4d6a-8376-6982b047a813 | checkpoint | 2.7.1 - Geotextile
f6e6075f-7f64-5d40-9a7b-1e1fa776c679 | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation. Class D
522efb4e-e63b-5705-b407-baa20ed2b7d4 | note | Acceptance / Conformance Criteria - Engineers Approval
cf5000de-3d05-5f51-b51e-5d4dacfdf305 | note | Standard / Specification - PS 16.5.7 Appendix V
54116a82-8133-5adc-b65a-9a86ce5a484b | note | Verifying Document - Delivery Docket/Material certificate
62572eea-ca35-590e-8c08-3c2c18b1bf37 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
4722a875-5e56-5f06-9fb8-7fb5970abbdb | note | Verification Activity: Activity - HP
333e1703-fa2d-5442-8c5c-b27d466c856d | note | Verification Activity: By - ENG
aa26a82b-595c-4399-a5a0-8aa9e247e55d | signoff | AUTHORITY HOLDPOINT
48c98f8f-1a77-4e44-820a-31941193b1c4 | section | SECTION 3 – Imported/Site Won Material Testing - ALL TESTS TO BE NO OLDER THAN 3 MONTHS
1203e129-ba33-4c71-9d94-59fc5c1b724e | checkpoint | 3.1.1 - Laboratory Testing for Soil Suitability
41e741bb-0fc4-577a-9dd0-9f319ef2614c | note | Detail - Soil Test Results from Hill Laboratories to confirm that topsoil suitable to for reuse
37fc3909-2db0-52a0-8abe-4aa1ea993bfa | note | ○ Soil Reaction
9b950e01-e4c7-5428-ba41-bf8755bcef4c | note | ○ Electrical Conductivity
489678af-1633-56c8-a91e-a15c29b7fd0e | note | ○ Mechanical Analysis (texture)
48233cab-e994-58c8-89c5-b2fcb56d6f5f | note | ○ Stone Content
86cf66e5-8acf-5026-8d65-9d70977469a9 | note | ○ Nutrient Levels of nitrogen, available phosphorus, available potassium and available magnesium
1745f027-828c-556f-a534-e6887e8f35b6 | note | ○ Organic Matter Content
309047de-0e56-54cd-af21-440008c2385d | note | ○ Check for Toxic or Hazardous substances
fb7ba00e-ef85-5f2a-b3e7-15fdd2ba3dab | note | Acceptance / Conformance Criteria - Engineers Approval
12fea58c-1f47-5327-83dc-5af7e1d3b166 | note | Standard / Specification - NZTA P39:2013 3.1
cc806d1e-681f-5e0a-abc6-f70f8c1cbfda | note | Verifying Document - Laboratories Test Report
a50736b0-0ca6-5807-8757-f703722bca81 | note | Testing Quantity Required (based from schedule qtys) - 10 equal samples taken from site, mixed together, then 1kg of soil sealed into a plastic bag and sent to lab for sampling
620ad0ec-9a36-5e41-b112-07c0c117b3a2 | note | Verification Activity: Activity - I
f47dd9ab-5b72-5ada-9e2c-d48eab11691d | note | Verification Activity: By - SE
33a7d9c0-5c10-4daa-b627-a51a9e580638 | checkpoint | 3.2.3 - Maximum dry density optimum water content air voids and shear vane strength (su) with range of mositure contents
edb29b8e-49bf-5824-8068-fb66bc14d9ab | note | Detail - NZS4402:1986 test 4.1.2 heavy compaction test
104ae718-8a98-5ed4-a86d-3113c7cc33dc | note | Acceptance / Conformance Criteria - Results from test
75ca6200-53f2-5c4e-ae91-8320f06455ae | note | Standard / Specification - Appendix XVIII
d05510aa-26df-5153-ac1e-460b0d01236d | note | Verifying Document - Report
44ec9fe9-462a-5e4f-931b-d5dbfe9b4d6c | note | Testing Quantity Required (based from schedule qtys) - 1 set (3 tests) per material type and source
a8df4158-78da-599b-b0e9-ef202d8d8828 | note | Verification Activity: Activity - HP
11b8e1f6-c0d3-5ee4-a781-ba5eb79b7f7c | note | Verification Activity: By - ENG
e01d63be-21cc-4fda-9cbc-acac7d078ca1 | signoff | AUTHORITY HOLDPOINT
f76d8006-efca-4cb7-a8a5-5450f2ccd12b | checkpoint | 3.2.7 - Organic content
2945e776-445c-5555-99b9-77505d51e98b | note | Detail - Visual observation
b2213ce5-327c-52a1-954d-fd020a2a03cd | note | Acceptance / Conformance Criteria - Fill shall be free from organic, calcareous or other deleterious materials
6f3021eb-23f2-562d-b56e-4fa4377ce360 | note | Standard / Specification - Appendix XVIII
34c280c2-f1fc-5f69-a461-cc29c7657627 | note | Verifying Document - ConQA
f1caae9f-9e5b-5b6a-82a7-6fcb6dfc4ad2 | note | Testing Quantity Required (based from schedule qtys) - Fill shall be free from organic, calcareous or other deleterious materials
db53fde9-3423-57f0-9fed-b7dcd80d01f8 | note | Verification Activity: Activity - HP
1ce5a06b-438c-5d05-946b-aac2df922cf2 | note | Verification Activity: By - ENG
93aedab6-07f1-474e-b57e-bf16a99533d7 | signoff | AUTHORITY HOLDPOINT
85d51e5e-6a73-465c-b2cc-9e89dfbc76db | checkpoint | 3.2.8 - Soil Permability
ffc1dde4-986e-54d6-9fb6-5dae38b62ca1 | note | Detail - maximum soil permeability
5a4995e8-8ce9-5db4-ab58-f8b778764a10 | note | Acceptance / Conformance Criteria - 10-7 m/s
51102317-6a8a-5f6f-944a-50bce2e18107 | note | Standard / Specification - PS:16.5.5 Appendix XVIII
f73f1b34-b486-5372-9f04-93357e1ef664 | note | Verifying Document - Report
5c4fa537-f795-5710-80fd-00e99939d44a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
73b21f84-6b08-52b8-ac72-b2526199ecda | note | Verification Activity: Activity - HP
d5b7c463-e580-5272-94fb-15c80d56e5cb | note | Verification Activity: By - ENG
f8c93144-46b0-47c2-8b09-ce77d4bced64 | signoff | AUTHORITY HOLDPOINT
7a864530-6db4-42a1-a96d-5520cd9ced6f | checkpoint | 3.2.9 - Liquid limit
2b4b2310-0013-5905-a44e-93ac7b05ad05 | note | Detail - liquid limit
a088b3d9-2646-501c-8a02-d3275bb69a90 | note | Acceptance / Conformance Criteria - less than 65% (Engineers Approval)
36d3c867-0e0c-5b4f-acbe-df3756693198 | note | Standard / Specification - PS:16.5.5
891e57a7-23f4-5e78-8a82-08a3116d02dc | note | Verifying Document - Report
0c0e095c-d956-5a83-9323-a75cd0aa5ecd | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
950f9f5f-0ac8-5ea9-bc51-a6d395e79c8e | note | Verification Activity: Activity - HP
ad1be44f-d61b-5739-b87d-409ebfb8442b | note | Verification Activity: By - ENG
fc3efbd7-873b-4237-a95a-114321f68113 | signoff | AUTHORITY HOLDPOINT
8a1733d6-8bca-4872-bea4-5b249016ec84 | checkpoint | 3.2.10 - Moisture content
1c99e381-4f98-5bc3-a975-ce9becb6c051 | note | Detail - maximum moisture content
58441e05-be11-504d-aecc-af3b28c49334 | note | Acceptance / Conformance Criteria - 6 % above (Engineers Approval)
4bbd32ea-c1ac-5a04-893b-f46c3dd193a7 | note | Standard / Specification - PS:16.5.5
c56da5c4-e06f-5806-acc1-515795477078 | note | Verifying Document - Report
745177d4-0b9e-5000-9f60-a2395285b7d4 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
171e8ea7-1679-5f19-9ed3-d4f7312a2d4e | note | Verification Activity: Activity - HP
4ac5e1bd-d697-5fd2-89c0-85a206eb11f9 | note | Verification Activity: By - ENG
a7ec5e9f-2278-489b-a9d0-ba5c0f82791c | signoff | AUTHORITY HOLDPOINT
f3b28e2e-9437-4bac-9d44-0e29dade0255 | checkpoint | 3.2.11 - Prohibitied materials
4c9c6914-9387-50d5-906d-e4a26f4019be | note | Detail - deleterious materials
1eaec089-02bd-59b9-9917-3321328f62b9 | note | Acceptance / Conformance Criteria - Not containing allophane, organics or other deleterious materials. (Engineers Approval)
1bae70f2-1897-5afb-8da9-c783f34deae7 | note | Standard / Specification - PS:16.5.5
835b99bc-8330-55fb-afc3-40c2a5561e76 | note | Verifying Document - Report
95f37edc-d1f2-50e9-8fd0-5182ef0ac97d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
97a9c2bd-7e3c-58eb-83c1-95f98550e1eb | note | Verification Activity: Activity - HP
632017ac-b4ec-5c56-8cbe-30375261943f | note | Verification Activity: By - ENG
2f0ca610-67f0-4b4c-85d2-f2441599820e | signoff | AUTHORITY HOLDPOINT
f7d90ee7-35f1-4b1f-9645-2439a8469d34 | section | SECTION 4 – ACCESS TRACK
b0444a3f-ee68-4219-a883-48a85f3d6c7f | checkpoint | 4.1.1 - Subgrade Level Confirmation
275b0d0a-6bc0-5436-906b-afc05f0e4e31 | note | Detail - Confirm subgrade is 400mm from finished height
6224332a-9eab-557d-a553-4ec3a80a46c3 | note | Acceptance / Conformance Criteria - String lines - or equivalent are 400mm +0mm/-30mm
af5c6fdc-f44c-5fd5-b9f1-6e92355850e2 | note | ○ Tolerances width -20mm +100mm
35d8c1f8-0a50-55b4-96bb-cdf0f33d4abc | note | Standard / Specification - PS 20.14.5
c869bc44-b146-55f4-af95-f1fb3b38a7bf | note | Verifying Document - Survey as-builts
e93304e7-194d-53fb-9abc-c78a19eb94bd | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage
9694be54-3e54-56f1-bdf4-e659932d0a88 | note | Verification Activity: Activity - I
df86d691-0c0e-5a23-8c90-5e3299e28d0d | note | Verification Activity: By - SE
30762dbf-da52-4215-add7-d176c72e5d12 | checkpoint | 4.1.2 - Subgrade CBR Testing
cc8b3c44-1753-5bbf-ad9f-91a7f807505f | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
5d210999-d267-57c5-95d9-0ec8b0bce856 | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
f02b2fc0-7bac-57c4-ab71-71a8e52b34db | note | Acceptance / Conformance Criteria - CBR >7
983f62d9-7504-58c4-b8c6-240debcf6d98 | note | ○ Min 3 blows / 100mm
c639656a-816f-5fee-b710-4d1b66404a1f | note | Standard / Specification - PS 27.4.2 Appendix XVIII
1874ab4a-0cdf-5782-974f-23bbad25af2c | note | Verifying Document - Scala Report
fecf91c2-d565-5d09-a927-6ae5880f2329 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
04885457-4612-5722-88f5-295b0ec8709a | note | Verification Activity: Activity - I
98d4163d-c88b-5e0f-88c8-3d95672399d7 | note | Verification Activity: By - SE
c93c701b-229c-4d07-a792-e0d67b473224 | checkpoint | 4.1.3 - Subgrade CBR Testing
83ad3c21-46c8-54eb-b3af-99eac5a9a664 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
2e7d90ef-2437-57a8-8922-80a7376c054a | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
9db7eef3-ddba-53b6-9d98-0870dfc284ff | note | ○ Hand auger hole is required
64819d62-9f09-5ad2-a45b-8517b43e22c6 | note | Acceptance / Conformance Criteria - Average Minimum SU:
0de62792-e953-5895-9e5d-464ae748fc95 | note | ○ > 60kPa
bb1f80f3-cca7-5e1a-b897-25f18e964aba | note | Single Test Min SU:
9be63bfc-b865-5f5c-880b-841daaf11218 | note | ○ >50kPa
1450577d-b0a6-5ef7-9536-d04b45b600cf | note | ○ 2-3m deep
5149aabd-c62e-5f07-8c00-950957d8fa68 | note | Standard / Specification - PS 27.4.2 Appendix XVIII
af78a3cd-390b-589a-a0ca-393649d052c0 | note | Verifying Document - Shear Vane Report
b493afe8-a095-56cb-bfbc-b7da2ccd655d | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
b755b49d-ae5a-5e8f-9899-854d2fec5eec | note | Verification Activity: Activity - I
bfe48025-f14d-5fd5-8fb8-7d4f3aab0604 | note | Verification Activity: By - SE
6103e445-c32b-4eac-a9ce-264dc29a2d74 | checkpoint | 4.1.4 - Proof Roll
216ed65b-a8c8-549d-807c-5ce4b02f8e3d | note | Detail - Visual Inspection of Proof Roll
46194969-13fb-50cc-b299-51f4cca2ce62 | note | Acceptance / Conformance Criteria - Displacement <15mm
80df856c-a013-587c-aca4-ba9d432b882b | note | Standard / Specification - Appendix XVIII
e6ffa13a-26f1-5052-9226-5627fc458f6b | note | Verifying Document - Visual Observation
679cedfa-3902-5e94-aa63-70d672945acd | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
78d81222-45d0-5d2f-9a0e-79f6fbda08df | note | Verification Activity: Activity - I
2181c86a-b533-5619-8ae6-7e1aa6927237 | note | Verification Activity: By - SE
66d82edb-ac11-485b-bc5f-85aa6169015f | checkpoint | 4.2.1 - Subgrade CBR Testing
e906d7e1-a64e-5c80-88bd-68266624f3d2 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
8e687ecf-264f-5b3c-86dc-d6c9ee415433 | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
3ff283ae-3ce0-5ab9-ad17-1c4e4125695e | note | Acceptance / Conformance Criteria - Min 2 blows / 100mm
18ab283d-5c3b-57ce-9ead-3f31d19c3fb4 | note | Standard / Specification - Appendix XVIII
1980f85a-e4bb-5672-a620-966c80766f74 | note | Verifying Document - Scala Report
62ce66b4-a35a-5144-8594-e3a4a5af0a96 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
0ed00510-cd06-5566-bc2b-b923fb11be4f | note | Verification Activity: Activity - HP
d8b6fb4a-f923-550a-ae70-d5cb28830c3a | note | Verification Activity: By - ENG
a741da3e-2638-47ff-a63d-0c9432a82bce | signoff | AUTHORITY HOLDPOINT
78076299-ace6-49cc-9f9c-15271d8cc1e3 | checkpoint | 4.2.2 - Subgrade CBR Testing
23faf815-b331-5f56-b0b5-1df7b7b77762 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
87b4ed45-6d9c-57fc-ba28-79991d1a26d0 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
b0c9d1b9-2705-5d54-ac21-3eae6a734439 | note | ○ Hand auger hole is required
0cc978dc-a21c-5fd5-94f6-cc144c35873e | note | Acceptance / Conformance Criteria - Average minimum Su > 80kpa
aa593894-8a20-5320-9e08-da4b50cadfd8 | note | ○ Single test minimum Su > 60
f2d9c7d0-720b-50eb-824b-e3d8709ded94 | note | Standard / Specification - Appendix XVIII
ae647513-81ee-55ee-bf59-c92888e66f33 | note | Verifying Document - Shear Vane Report
a9590d11-d799-52d0-874b-84d38ce4d13a | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 test) per 500m3 of fill placed per area worked per day per lift
a3e25720-eef1-521b-9e11-13712ab6a5a3 | note | Verification Activity: Activity - HP
3b758fe5-f520-5d56-95d8-7bd620911de1 | note | Verification Activity: By - ENG
ad772f8a-33dd-4226-9ba6-f56e14b1d219 | signoff | AUTHORITY HOLDPOINT
026b6710-ee71-4215-a120-d59e8f3d2d19 | checkpoint | 4.2.3 - Bulk desnity, Dry density, Air voids
f8897702-5c72-55ab-a0b8-ce76d17effa7 | note | Detail - NZS4402:1986 - Test 5.1.3 sampling tube method for determination of the in-situ density
49ccdc27-44f7-5387-8c60-34ca5cfe6d44 | note | Acceptance / Conformance Criteria - Results from test
ce51b0f6-2845-5a63-be97-1479f5b5dbc0 | note | Standard / Specification - Appendix XVIII
0e1bb2d3-bdef-5f88-a766-ba892660b7bf | note | Verifying Document - Report
fa2e016e-a738-5ee4-bdbe-d575b7555b4b | note | Testing Quantity Required (based from schedule qtys) - 1 Test performed for every 10 NDM
e9144616-cadf-5e1d-8315-74c51d543f09 | note | Verification Activity: Activity - HP
2b34e023-3457-577b-88e0-b2f21992e80a | note | Verification Activity: By - ENG
85daffc7-11ad-4b81-ae34-5a6580b95968 | signoff | AUTHORITY HOLDPOINT
550b05c5-c9b3-4c20-b816-2bd74ee2efe6 | checkpoint | 4.2.4 - Water content
de8ccf5c-23fc-50d4-8dc1-519b0701a097 | note | Detail - NZS4402:1986 - Test 2.1 water content
4a246ed8-9e68-5f93-9740-56f21a3b5cd2 | note | Acceptance / Conformance Criteria - Results from test
562432f3-8197-5830-8dcd-2325ceae40f5 | note | Standard / Specification - Appendix XVIII
367363b6-da26-5f18-8c8f-de5bfe8156d6 | note | Verifying Document - Report
f75ca5ad-31f0-50a7-8d6c-afce8fdd39e2 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 test) per 200m3 of fill placed per area worked per day per lift
576978dd-2bc2-55a9-a64c-c1dc1f4345c6 | note | Verification Activity: Activity - HP
da4309c7-7af1-5efd-9d71-6fedc00049dc | note | Verification Activity: By - ENG
20190b5f-32ea-4d1a-aeeb-70a12b24e208 | signoff | AUTHORITY HOLDPOINT
46122cf5-3d43-4212-865f-195df2ba5ded | checkpoint | 4.2.5 - Insitu density insitu compacted dry density insitu water content
8d4a1b99-4c9a-5cba-a49c-9a984e0c0513 | note | Detail - NZS4407:2015 – test 4.3 nuclear moisture density gauge (ndm), direct transmission mode
63668174-83ef-52fb-ab12-4075a9ffaed7 | note | Acceptance / Conformance Criteria - Average maximum air voids < 8%
c137b0ee-a868-588c-87ad-871a5e8f5f28 | note | ○ Single test maximum air voids < 10%
37227aba-785a-55f1-a972-691848af0f6f | note | Standard / Specification - Appendix XVIII
91bb1d8d-f103-5ee1-8f3d-42ef7f0f62af | note | Verifying Document - Report
6e992d17-efd2-52dc-8204-d2a1144b9f4d | note | Testing Quantity Required (based from schedule qtys) - 1 Set (5 Test) per200m3
2b769bfc-e11d-5591-bd3e-deb4baa0c50d | note | Verification Activity: Activity - HP
fda48039-7489-56c6-8b12-c65bb9ad9782 | note | Verification Activity: By - ENG
975a599a-d7a6-447d-a4f2-54925661ce57 | signoff | AUTHORITY HOLDPOINT
912e392c-a6f0-42ba-8244-6f7ef826f608 | checkpoint | 4.2.1 - QA Submission
06132941-25f5-54f3-85bb-7bbe7011e718 | note | Detail - Submit all Subgrade QA before proceeding with next pavement layer
db4ed6f5-fc68-5ed8-bd9d-ee78d816e7f7 | note | Acceptance / Conformance Criteria - Engineers Approval
0856d183-1d8d-5270-a292-62e4bb7d9424 | note | Standard / Specification - Appendix V
b285bd73-8f00-536c-a976-3b58a48b659f | note | Verifying Document - Conqa Siggnoff
21d62688-d208-5419-ac02-d1a8e989adfe | note | Testing Quantity Required (based from schedule qtys) - Once
e6f68db3-9385-58bf-83c7-dc457e34a71c | note | Verification Activity: Activity - HP
8af2c363-d6d0-5012-b2e4-539209b53981 | note | Verification Activity: By - ENG
00e8190b-1b0d-459d-87c8-ed0d20056e1b | signoff | AUTHORITY HOLDPOINT
2a02be65-4371-4026-aa57-c6c47e410471 | checkpoint | 4.3.1 - Placement of Geotextile Fabric
d821796e-01d1-5711-9fd2-deb2c34a9a9f | note | Detail - Place Geotextile Fabric Strength Class D across pavement area, with 500mm overlaps
c14c42be-1fc2-5a90-be50-ce071d3d236f | note | Acceptance / Conformance Criteria - Visual inspection
a8d4cd33-656d-56f5-a4e7-50d1eb894307 | note | Standard / Specification - 232735.02-WSP-DR-STW 0302
5f6bc0ba-573f-50ef-a11e-0b4230286c68 | note | Verifying Document - Visual Inspection and photos
18089d0c-d353-5f7d-8065-d826b1f7ab72 | note | Testing Quantity Required (based from schedule qtys) - During construction
97a68676-fd03-5490-b69a-b4964adbeac9 | note | Verification Activity: Activity - WP
237d7eb2-1cd0-5d12-b40d-5cab180686a7 | note | Verification Activity: By - ENG
3ae20800-da84-4b60-ad2a-a5c34622e76f | checkpoint | 4.4.1 - 3m Straight Edge
1d4fc1fb-3f5f-5521-9a42-95d8c6fcc717 | note | Detail - Formation check to ensure surface is smooth
26cc6f03-6c1e-53e5-9f3b-e9f3a73fc308 | note | Acceptance / Conformance Criteria - +/- 15mm
b01d8f6d-e12d-56b1-874c-acaa77c30442 | note | Standard / Specification - PS 27.4.1
a542bc2a-db92-5f38-a1cc-1d6b23db6965 | note | Verifying Document - Check Sheet
8c2a43f9-0c70-54a5-a4e9-60b4efd84a81 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
87adefc5-910e-59ce-a222-b47035e45c91 | note | Verification Activity: Activity - I
d4d60c20-52c0-501b-90fa-cc620a8687d9 | note | Verification Activity: By - SE
760f8c07-3a61-4525-8808-d17c9a444510 | checkpoint | 4.4.2 - Stringlines or equivalent
41fa054b-eedd-5f82-ae81-8e3f353d87e5 | note | Detail - Stringlines or equivalent to check finished height of surface
a690e7fd-7b68-5071-b640-206dd5ef114b | note | Acceptance / Conformance Criteria - String lines - or equivalent are 150mm +5mm/-25mm
02bcf037-2723-50b1-8292-e32a6652bd83 | note | Standard / Specification - TNZ B/02:2005 5.1 232735.02-WSP-DR-STW 0302
3926790a-ac0e-5292-aa5c-e2d61fef8ca9 | note | Verifying Document - Check Sheet
77ffe626-cbbb-5c81-9744-ec86fecbec05 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
242ace7e-82fb-5dcb-a7b8-8da0031acd95 | note | ○ 1 set = 5 tests
af1ef63f-8f52-518a-853a-4f7851297b5b | note | Verification Activity: Activity - I
911ff913-39a7-51d1-add2-4712271f3663 | note | Verification Activity: By - SE
4b43f12e-eee2-405d-84f1-548ef7148e4a | checkpoint | 4.4.3 - Compaction - NDM
ec40bd6c-ddeb-5525-8c6d-3b7536bc146f | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
82531054-d3ee-5a5d-b007-80533362b878 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
be7655b5-0bc0-5b05-85cd-a18561177642 | note | ○ Min >92% of MDD
192a1da9-37eb-54bf-b912-4c0adda56c33 | note | Standard / Specification - TNZ B/02:2005 7.5
d6ce904c-9f10-54e8-97c7-3ff2589da6c6 | note | Verifying Document - IANZ Accredited Report
ec115a33-4f0a-5397-a445-7be8cf04b8fb | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
6767d7d0-ef5a-55b7-a157-4ecd5eb2fdf7 | note | Verification Activity: Activity - I
adeed43d-e426-5179-ac33-49c2489b6ab5 | note | Verification Activity: By - SE
ff01ff05-6704-4182-afe8-61cd7bf9c88e | checkpoint | 4.5.1 - QA Submission
e6d5944b-b564-54be-9cf6-5ea377890377 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
cd322087-ce27-5123-a5c1-820295abe973 | note | Acceptance / Conformance Criteria - Engineers Approval
8f9e01f1-b812-5be2-88db-789048a3620e | note | Standard / Specification - Appendix V
d874f29a-d4d0-5eb8-a1e2-ae288433510b | note | Verifying Document - All test reports, Material Test Results, Laboratory MDD, NDM results
faa538db-4d3b-56f4-bc9b-0fdfea1bd14b | note | Testing Quantity Required (based from schedule qtys) - Once
e0fd5a45-1e89-537b-b773-13f039399d10 | note | Verification Activity: Activity - HP
b3a5dbb5-bafa-5522-9785-59da038dd0b6 | note | Verification Activity: By - ENG
0be0701f-270d-4513-a18d-8137ed8567b9 | signoff | AUTHORITY HOLDPOINT
906f9920-5bef-4117-8b12-6dc23518cb0b | checkpoint | 4.6.1 - 3m Straight Edge
cc1a07bb-5b38-555e-ba66-fafb1345e95b | note | Detail - Formation check to ensure surface is smooth
6c8429b5-8d14-5d44-9271-0f260c55e0e6 | note | Acceptance / Conformance Criteria - +/- 15mm
d2fcbe01-c63d-5b4f-805d-8e4be7102c17 | note | Standard / Specification - PS 27.4.1
888d35cb-ec05-5ffb-8fc4-5ea92aba4b22 | note | Verifying Document - Check Sheet
2569800c-8756-54bb-8a9a-1590b07c4538 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
a2b33130-d20e-532f-8515-3352d9285ee0 | note | Verification Activity: Activity - I
ef671787-26db-5fbb-8c57-c8a1785cadf4 | note | Verification Activity: By - SE
0e98a7dc-a412-46f6-bc52-2d9e2dd77747 | checkpoint | 4.6.2 - Stringlines or equivalent
f00ba01b-baba-524e-8244-095bdd683378 | note | Detail - Stringlines or equivalent to check finished height of surface
942c6e01-182a-5745-9799-71a2ad529223 | note | Acceptance / Conformance Criteria - String lines - or equivalent are 150mm +15mm/-5mm
85c732a9-209a-5150-9793-2294c404ead6 | note | Standard / Specification - TNZ B/02:2005 5.1 232735.02-WSP-DR-STW 0302
33d9b006-9afa-5d38-b824-2b88ca39dd1a | note | Verifying Document - Check Sheet
2a70e7cf-3489-57e8-8dee-fb1cd4a97bf8 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
ce921c9e-6e14-5842-b261-984b9cfcf65a | note | ○ 1 set = 5 tests
bfbbc15e-7158-5626-a8b1-62dacff59397 | note | Verification Activity: Activity - I
0f0d5ba0-3b7a-5511-aed1-f6c04d5efd62 | note | Verification Activity: By - SE
46a935f9-e0c6-44e7-934d-ae569b5c95ff | checkpoint | 4.6.3 - Compaction - NDM
7b498ac2-544b-5624-8a1e-fe35b3e1eb62 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
fbfd762f-9e30-5729-9dcd-9a651e62d30e | note | Acceptance / Conformance Criteria - Ave >98% of MDD
1dd263e1-5fe7-5483-862e-9eb1c88756ce | note | ○ Min >95% of MDD
aa0713c4-d7a3-52f7-8f4d-593deac4210f | note | Standard / Specification - TNZ B/02:2005 7.5
dec974ca-1c16-52e9-9174-4b5a7ba6059f | note | Verifying Document - IANZ Accredited Report
691d89a6-9a11-51ef-9597-252aab1eaba1 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
a81313f7-5dd5-5c5f-8a9f-3c5793f0d475 | note | Verification Activity: Activity - I
19cd0b3a-14bf-5a88-92c4-6f14a701ccc5 | note | Verification Activity: By - SE
618ce7d2-f8a4-40ee-9b62-5a599cf6eb00 | checkpoint | 4.7.1 - QA Submission
4ebf544e-c72c-5ca7-9e84-1d830c892937 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
bdd6a480-74f2-57ff-9fcf-c7dd27698944 | note | Acceptance / Conformance Criteria - Engineers Approval
a7678562-7b46-551b-84d4-89a2ace828d0 | note | Standard / Specification - Appendix V
a4ec6ce2-34f4-51c7-bca9-399b030de8aa | note | Verifying Document - All test reports, Material Test Results, Laboratory MDD, NDM results
498d2dbb-ada8-5374-aa71-8358fda6da10 | note | Testing Quantity Required (based from schedule qtys) - Once
b30846ca-6c73-59b4-9459-3cecfa447d4b | note | Verification Activity: Activity - HP
07b9a388-5b92-5082-8f5e-160c39f1ed6c | note | Verification Activity: By - ENG
0d904402-8103-4fe6-a000-d4d782668488 | signoff | AUTHORITY HOLDPOINT
dc7af9cb-707c-407a-a111-5072fbccff71 | section | SECTION 5 – EARTHWORKS
06a402f4-9feb-4cec-915c-02f5027262fe | checkpoint | 5.1.1 - Subgrade Level Confirmation
c807a62b-a6e0-5481-aa1c-feb4f27b3941 | note | Detail - Confirm subgrade is 300mm below from finished height
f38ac10d-4ea5-592e-a4bc-6363ed3b57d2 | note | Acceptance / Conformance Criteria - String lines - or equivalent are 300mm +0mm/-30mm
73a60a8a-8b71-5aca-9c8b-0d907b3db432 | note | ○ Tolerances width -20mm +100mm
8a768cf9-e280-570c-8088-fb8bdf38b0c4 | note | Standard / Specification - PS 20.14.5
195724a9-2a59-5d9c-a454-1a064cda3353 | note | Verifying Document - Survey as-builts
68aebb51-ebab-5126-8478-c7f56414e026 | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage on all major contours
06ac5ec5-3aa6-5164-b9c6-8344e577cd07 | note | Verification Activity: Activity - I
df237028-523d-549e-bdb8-055f91129348 | note | Verification Activity: By - SV
042a5186-ed2b-4bfb-a3a1-6aa0bf61a089 | section | SECTION 6 – FOREBAY
cb34cab7-f5ae-476d-8a45-eb2c49180a6e | checkpoint | 6.1.1 - Checking of levels
c93df8c8-551b-5e50-ba80-42618bdc58c5 | note | Detail - Confirm that the thickness of the riprap is 300m
c6647004-5e42-5c97-a433-04ef9b116dbc | note | Acceptance / Conformance Criteria - String lines - or equivalent
f37452c8-aac9-50d3-a9c5-124f6817d95c | note | ○ Tolerances width -20mm +100mm
d8d83c7a-9ad3-5ec3-a2a8-d35be56c9c10 | note | Standard / Specification - TNZ B/02:2005 5.1
de15e864-112a-5565-ac76-bef3c71d9df5 | note | Verifying Document - Survey as-builts
c0709151-2bd3-5614-ae74-944b6068e2a0 | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage on all major contours
847fa363-97db-5475-b260-838b630a30f4 | note | Verification Activity: Activity - I
294d887f-f429-5e0b-9f9d-5297208c513b | note | Verification Activity: By - SV
97179ea2-d0c6-4618-927d-caab3ad5cd76 | checkpoint | 6.2.1 - Placement of Geotextile Fabric
82fe394a-7a3d-52e3-8875-9bcb7d410acc | note | Detail - Place Geotextile Fabric Strength Class D across pavement area, with 500mm overlaps
db53f6f0-a70e-5441-8dd6-dc4f04bf5870 | note | Acceptance / Conformance Criteria - Visual inspection
626b32ef-f071-5efe-acef-b781dff1b1ae | note | Standard / Specification - PS: 21.5.15
898acdcc-c860-54b2-a795-907f4f01e058 | note | Verifying Document - Visual Inspection and photos
69518f1a-a36d-5aea-8756-cb9ba5423df3 | note | Testing Quantity Required (based from schedule qtys) - During construction
300d8e0f-4316-53aa-8d3f-2d6c1df1ec27 | note | Verification Activity: Activity - W
82cfbafb-34af-5eb2-ade0-3e9eae5264ec | note | Verification Activity: By - ENG
194c8e55-c2b8-4e16-929a-33c86970bb96 | checkpoint | 6.2.2 - Checking of levels
19e13546-3c85-5780-8590-f648dd989c36 | note | Detail - Confirm that the thickness of the riprap is 300m
d059e3e1-8813-51e5-a32b-b72192c62000 | note | Acceptance / Conformance Criteria - String lines - or equivalent
1bdc9f77-38c0-5c67-853f-b1445ddce3b0 | note | ○ Tolerances width -20mm +100mm
7fa8c68c-8407-5b07-ab3b-21d347d521b9 | note | Standard / Specification - TNZ B/02:2005
cd3b5b1d-8d14-5b13-b0d1-db454e82bdf2 | note | Verifying Document - Survey as-builts
116eada7-5e9c-5e0d-81a9-7368f19f73ee | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage on all major contours
8da35361-f19a-586f-93c4-5d9d36282682 | note | Verification Activity: Activity - I
b9e0ae30-eb51-58b9-94c6-2fd9d7ff2352 | note | Verification Activity: By - SV
28755fc6-ef2a-4a06-963e-d2497f7dde8c | section | SECTION 7 – AS-BUILTS
48d157a1-a4ce-4d27-bee1-b3a914c39e9c | checkpoint | 7.1 - As-Builts
4b10c050-c681-553a-b69e-830e5238768d | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
2e61511d-4a31-5acf-bf3b-a77721689fdb | note | Acceptance / Conformance Criteria -
22b286b9-fbe3-5d34-844c-f0907f9ecded | note | Standard / Specification - PS 16.7.6
bf5a6662-50d3-5e22-9e73-0e30f5eac771 | note | Verifying Document - Survey Records/ Redpen markups
28db6946-f898-56ab-85dd-bc01e3dd2fb6 | note | Testing Quantity Required (based from schedule qtys) - Post Earthworks
54276f87-d17a-5ada-8f57-865dbbf032d2 | note | Verification Activity: Activity - D
ff187f26-9d92-56a2-bea5-9543c5cef0d9 | note | Verification Activity: By - SV
c56bd523-7fe4-4b60-8d9a-1d66266baee9 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
f0c09f77-38e4-5661-8fa2-3bd6d8cacd40 | textbox | Contractor's Rep Name:
664c5666-57bf-5bfa-83f7-c80a3202a390 | textbox | Engineer's Rep. Name:
c0229e69-a6ba-56ed-b439-9ba358017907 | date | Date:
6d0294db-498c-4ba7-80d7-fde0d5f12e8a | signoff | Add Signature
3747219a-be72-473d-9166-a0fa65ea6f18 | checklist | DN1210-SP2-019-002 ITP Wetland 2 Stormwater Drainage Directional Drilling Rev 0 | itp | DN1210-SP2-019-002 ITP Wetland 2 Stormwater Drainage Directional Drilling
7cbd4f7f-e3a5-4fc7-a736-fbb0fe70fee0 | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
34653f1d-df0e-45ad-827a-560e9c95448e | checkpoint | 3.1 - Extent of Line Setout
f4883b6a-3d56-550e-a224-0c3aa593c441 | note | Detail - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Stormwater drawings.
3d0e022d-1120-5d36-9721-b59950a878c9 | note | ○ Identify any clashes before construction.
c7c3f049-1842-55bc-a3eb-92c46fd531d9 | note | ○ Lot - Markup
88760576-cbcd-54a5-b4bd-f6d89e693c9e | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
f9e7b4d0-ab3b-540f-b540-bdd1a246d37d | note | Standard / Specification - Design Drawings
fc8454b6-4997-50fb-91f3-be072abf91c9 | note | Verifying Document - ITP Sign Off
188a0d14-5f67-57dc-8afe-090e3ed3b6f8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
f00a3d2f-c929-579f-8619-791d90ad7e3c | note | Verification Activity: Activity - M
c8bd3a3b-f73b-55cf-94fb-e34094bc9a6a | note | Verification Activity: By - SE
236434c2-4505-48ba-967b-150d80a2a08e | checkpoint | 3.2 - Material grading: Materials (Gap65/AP65)
42159255-0f06-5ff7-a6d6-02dfcdea582d | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
02b6c8f7-a97d-5d7f-80db-d77c2d1f9340 | note | Acceptance / Conformance Criteria - No Particles >200mm
270bbe98-f3d4-510f-b921-27164e42d21e | note | ○ Maximum fines 10% passing 75micron sieve
40b1edf3-118f-5577-9883-974437f0923d | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
2f3f443f-8305-5207-bbcf-9268cadae2a3 | note | Verifying Document - IANZ Accredited Report
fcfa2f4f-0ad1-50fd-a018-4cc65d869531 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
2236d41b-80de-5ecf-bce3-6b7bbe1c2aa6 | note | ○ 0-400 - 2 tests
09592790-28f5-5295-b7ba-2a2f70169c91 | note | ○ 400-1,500 - 3 tests
e00ce16e-5420-59f0-9838-c51915454b16 | note | ○ 1,500-4,000 - 4 tests
764e6525-65b0-5fe8-a127-8b06ec9eb05c | note | ○ >4,000 - 1 test for each additional 1,000m3
c10b6ef2-696f-5c6d-ac12-38c578b232eb | note | — Results to Engineer 2 wks before importing
b643b426-e483-5bab-8a75-9765e87b6c89 | note | Verification Activity: Activity - HP
cff7ac9f-0d44-5826-92db-1d9c0fdf449b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
bf4e5618-234b-5644-8a09-2786e823c23f | note | Verification Activity: By - ENG
07284ac2-6ac3-496e-9583-ff567e52055f | signoff | AUTHORITY HOLDPOINT
7fddec9f-5622-432a-bd0f-729865547cc9 | checkpoint | 3.3 - Weathering index: Materials (Gap65/AP65)
43194a66-f295-557b-8d06-af2a349be8d5 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
1defa27f-edcf-5075-8ccc-d953c3160484 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
d8cbcc8b-9aec-55ff-a0b0-15ea9ad471ab | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
77e2ac1b-417c-565b-8216-5961c7212d9c | note | Verifying Document - IANZ Accredited Report
e0470f33-e878-5f23-8277-4939acb2aff5 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
8eab7090-d146-55d7-8293-33d6cc7d6c81 | note | ○ Results to Engineer 2 wks before importing
2bd54d1f-21ca-56ae-90e8-7513b9153103 | note | Verification Activity: Activity - HP
33785e6e-2503-5626-a197-dd3a7cfb7a9f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6a4f04ce-f043-5708-9d04-870a5c9de5a2 | note | Verification Activity: By - ENG
643fffa7-e770-486f-b295-55c77975bf90 | signoff | AUTHORITY HOLDPOINT
24b4d6d7-c5cf-46d7-b31c-d06d2115e97d | checkpoint | 3.4 - Crushing Resistance: Materials (Gap65/AP65)
dac54fcd-a735-55cf-8802-111a911d9521 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
72c3df2a-79ff-5cfe-938d-7db9943a5b34 | note | Acceptance / Conformance Criteria - >100KN
3ce8cee3-e70c-5e67-9938-bc194733d146 | note | Standard / Specification - Appendix XVIII, Appendix V
a1272ff1-67da-502b-ae10-a1ba4eafe337 | note | Verifying Document - IANZ Accredited Report
cc081f50-da88-565b-acc6-b8b91efb283f | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
26e5a5b6-bbfb-5b0d-a4b5-c177f17e0153 | note | ○ Results to Engineer 2 wks before importing
c8727a46-5823-5625-90e3-10dd1038f0c7 | note | Verification Activity: Activity - HP
598addc3-1b9b-54eb-a6f2-ff3d02b209c4 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6241b981-dd85-5627-bbd2-53a975424488 | note | Verification Activity: By - ENG
66950949-eb03-47db-9ab5-1526941b9c0f | signoff | AUTHORITY HOLDPOINT
ab42a577-5307-4917-8db2-7ec16b94adb3 | checkpoint | 3.5 - Material grading: Materials (Sand)
431bf7b1-c795-5c5c-869a-e98dc39c81f5 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone
ac6a2232-850a-5f5d-bd40-5ec4e207ba5c | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
66c36594-6b3c-5df2-96f5-8d2b82fd674b | note | 19.0mm ¦¦ 85-100% passing
dbf5578e-a708-5841-ad40-9704308bf13d | note | 9.5mm ¦¦ 25-55% passing
4483bda5-9abb-54e4-bc03-1906ff626a58 | note | 4.75mm ¦¦ 0-10% passing
ad12ecc8-d00a-5c47-b1ee-86d0e7c3681e | note | 2.36mm ¦¦ 0-5% passing
2fcf639b-fac0-5d35-83ff-b31af4342662 | note | 0.075mm ¦¦ 0-2% passing
9af79e9d-5238-57cb-bdde-e91182c80372 | note | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
71eef727-208e-5d9a-92d1-dbba9be4cb23 | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
a0c78821-aa23-5e3a-bf15-01880fd79dc8 | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
f7047fa1-4c9b-5fa7-a238-29d25297c642 | note | 400-1500m3 ¦¦ 3 Test
5cece299-3a10-5af5-bf32-8145f2ba4fce | note | 1500-4000m3 ¦¦ 4 Test
5db8cdfb-1f88-59c1-b07d-f5e5e7389538 | note | >4000 ¦¦ 1 Test Additional 1000m3
cf8c9366-5e35-5450-8106-1697ab6ec685 | note | Verification Activity: Activity - HP
cf771d8e-d853-5697-9d95-f38783667f57 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c3a902a2-8350-5ce1-81f3-de10c1104745 | note | Verification Activity: By - ENG
9ba375ed-8021-4dae-bf06-d524e36c3abc | signoff | AUTHORITY HOLDPOINT
3b9a8db9-b619-410d-bc51-e5dfad1f08eb | checkpoint | 3.6 - Pipes (PE)
8f5c1a82-1f4c-5a5d-a3a8-f2163409d34f | note | Detail - Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
775d43a2-71b5-5430-921b-b05de251c756 | note | ○ Full Traceability information and certification of analysis for the resin batch.
99cadf29-6740-50c6-a01a-c338b96a8cb9 | note | Acceptance / Conformance Criteria - Full Traceability information and certification of Material
6d3315df-1951-5ecc-b836-4798577870f9 | note | Standard / Specification - PS-22.4.1 (d) AS/NZS 1477
78342ea5-65c7-5001-b7ca-0957c048907e | note | Verifying Document - Delivery Dockets
bb3cb874-ca97-53f9-b620-5f69f1bdc616 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
16ea648b-73b1-5c8f-803d-992fa05088a4 | note | Verification Activity: Activity - HP
55728fe9-0d9d-5e23-a163-8defcbf49d2d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
01ac8c90-f402-5527-915d-0ef2b06386f5 | note | Verification Activity: By - ENG
7f539d03-2bc7-4f0e-854a-c342a9aadb91 | signoff | AUTHORITY HOLDPOINT
6e7eb6c1-b0db-40fc-94a0-5d18ee428944 | checkpoint | 3.7 - Pipe and fittings.
d420eaaf-6856-54bd-836c-8e8e26fab71b | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
6287f2b9-a86e-5f5a-a627-49388dd6b3de | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
bc497184-476f-5256-9c52-917b80878767 | note | Standard / Specification - Design Drawings
dde10433-150e-5ebf-86f9-fb09d4bc121a | note | Verifying Document - Delivery Dockets / Inspection Checksheet
60efa501-553e-5407-9bb2-dfa2221db2b4 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
7caf3662-574f-54fb-b93f-2ba3034fa3f6 | note | Verification Activity: Activity - H
2c300f77-2810-5a4e-b5d7-ae110a34207b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1d8a9c21-1bec-53f8-a62a-7ab357449da3 | note | Verification Activity: By - SE
ec0e6343-9bda-4285-a3be-8c5a64d08fa5 | checkpoint | 3.8 - Granular Material (Sand, GAP65/AP65)
6f4d5629-e017-5e4a-9650-6743442cb592 | note | Detail - Confirm Specification and material in good condition.
bf4c0604-d2b7-5f87-b892-5901ee20e724 | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
f51c3fe1-6b5d-51f1-973d-6aa8381300a9 | note | Standard / Specification - PS-22.4.1
b7664f7f-73c4-5230-a9a0-e36091db1405 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
df8fd374-3c7e-5a28-9152-a1e04bc35efa | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
0269500f-4445-5a5f-8b4f-c54609328906 | note | Verification Activity: Activity - H
d416682a-29d9-5bf6-b735-9de6eadd709c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
27d70ddd-1294-5397-8829-f2426773bb6d | note | Verification Activity: By - SE
36ceca26-d086-4edf-a12c-99c97ba867fb | checkpoint | 3.9 - Bidim/Geogrid
38bfcf19-b668-5431-9d03-95f272464e3b | note | Detail - BIDIM A29 Durogrid 30/30 or similar.
4cd03b26-6443-5155-812d-2ee6c5a0e53c | note | Acceptance / Conformance Criteria - Site Engineer Approval
f3ed6e52-d337-5385-81cb-6898c1041544 | note | Standard / Specification - PS-22.4.1
dc076877-fdcc-5b92-8094-ccec4518a5fb | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
91e4e6a6-c71c-50e5-ba94-088fab919a32 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
1d9a1651-5254-5b13-a689-e27a2c5fed91 | note | Verification Activity: Activity - H
af125af7-645d-5106-a8e8-46e5097d2dca | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
18092749-0293-5185-bf7b-19baf36a3b56 | note | Verification Activity: By - SE
56f47112-db70-4edf-90a3-4e5f2c818f66 | checkpoint | 3.10 - Tracer wire
1077a064-c9cc-5477-b627-af8ecb35e29d | note | Detail - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
9e7abc88-52c4-55b1-8e79-ffa44eb6a299 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
64cc7039-0fe9-59be-9a03-a4da570a0d71 | note | Acceptance / Conformance Criteria - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
5a8fb947-dc77-53d9-bb68-12a7eb64a666 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
e100c055-9013-56ab-9dcb-c7090d42ac1a | note | Standard / Specification - PS 22.7.3 a
401b00fe-cad8-58b3-8d81-5209501da14c | note | Verifying Document - Docket
eac4fe36-bd07-509a-9d9e-8cfb62683d43 | note | Testing Quantity Required (based from schedule qtys) - Every Line
14f511cf-dc87-524c-9dd8-75f1a75047a9 | note | Verification Activity: Activity - H
15a9d97d-59dc-53b1-8213-d54b8c042278 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d9bf22a4-7a05-555f-bbb0-44f9d9e700e7 | note | Verification Activity: By - SE
7772a115-dbfa-4685-aebf-dad5a8e933fa | checkpoint | 3.11 - Drilling Fluid mix
359c6f7f-3f29-5f44-958e-5d54accf1042 | note | Detail - Fluid design to be submitted to engineer before start of works.
e0889aea-6d83-5203-8aba-24012e5554f1 | note | Acceptance / Conformance Criteria - Fluid design to be submitted to engineer before start of works.
4b715005-0ef1-5622-bdca-ba60a2386126 | note | Standard / Specification - PS 21.6.6
98a6e7fd-845e-5eab-8c1f-8fed2ec32eb7 | note | Verifying Document - Visual Inspection
af338a29-87b7-55d3-b48a-b4adbe8a561b | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
72ccf1cc-554e-5510-bbdf-da82e5dd736c | note | Verification Activity: Activity - H
c6e97c9d-6e88-58ca-acfc-80c1a973a604 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
47c5d1f2-4941-585b-ab1d-8e4c8ba29684 | note | Verification Activity: By - SE
e6bf93f4-f943-4fff-af14-9b922b6ec5ce | checkpoint | 3.12 - Reinforcing steel (Stilling Well)
1a68740d-f1d9-5cf0-a4d2-a58658054ccf | note | Detail - Wetland 02 Stilling well detail (SDMH11.1.1)
d62d74f2-a0f4-5b8b-aa2b-3ffd7c35d0a4 | note | Acceptance / Conformance Criteria - LAPS TO THE 16mm DIAMETER LONGITUDINAL
00530833-29e8-515f-859a-044c22d30e63 | note | ○ BARS TO BE MIN. 825mm AS REQUIRED. REFER TO CONCRETE SPECIFICATION FOR FURTHER REQUIREMENTS AND HOLD POINTS.
afc84dfd-b1fa-5f4c-b090-771fb417fdfc | note | ○ DRILL AND FIX 6 No. M30 HDG G8.8 THREADED ROD ANCHOR STUDS WITH NUT AND WASHER USING EPCON C8 EPOXY OR SIMILAR APPROVED.
d6a3325b-dff1-5caf-aee8-cd162f30b085 | note | ○ MIN. EMBEDMENT OF 210mm IN CONCRETE PAD. LENGTH TO SUIT MIN. EMBEDMENT AND THICKNESS OF MANHOLE FLANGE BASE.
9b5ba8aa-5c9f-5c70-b5f9-73befaa141c9 | note | ○ ANCHORS TO BE EQUALLY SPACED.
4b980a1e-9551-5c44-a4ae-a65289a47b5d | note | Standard / Specification - PS -IFC STW 0411
43caa7ad-9bfb-5e90-8bc4-5cec9cd6e70c | note | Verifying Document - Material docket
318cf3a2-5c53-54f2-8c3b-e05af4205101 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
74bc2982-0130-52d2-b419-306d59b17f95 | note | Verification Activity: Activity - H
74112e15-3bfb-5c0a-bdb6-a71602a7d87d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e68bc530-0f00-59db-bbf6-e64758ea4d4e | note | Verification Activity: By - SE
036f8f68-4cd7-434a-afb0-3a0e52ad44a9 | checkpoint | 3.13 - Concrete
7efc476a-5fe9-537e-a099-5d9bdb2bc88d | note | Detail - Wetland 02 Stilling well detail (SDMH11.1.1)
caa4a405-1eb3-5f68-8a62-109f6bf688e2 | note | Acceptance / Conformance Criteria - Concrete should have 40MPA 28 day strength
31efb4ae-6f42-5eda-9437-6cc0e26b6ee6 | note | Standard / Specification - PS -IFC STW 0411
e1390dc2-84e0-537c-82df-21ec394dce79 | note | Verifying Document - Material docket
f972b343-6ad0-5def-829b-e653e0176bfc | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
b7539943-e8ab-5ba3-87ba-4e2391d61b2d | note | Verification Activity: Activity - H
e6c7a4fe-e191-5acc-862a-3e2f618c6708 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4f4ca85e-542c-5d33-9d44-1af3689f53bc | note | Verification Activity: By - SE
8fdea4c9-ed01-4eed-bca0-49ef5ceb401a | checkpoint | 3.14 - Stormwater - Structure (SWMH, SDMH)
1b8a7462-7d28-50ef-9abc-f709a36e2a6e | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the Structure are correct and in good condition.
734a6268-170b-5264-b261-bffd23ae4b90 | note | Acceptance / Conformance Criteria - Confirm diameter and size as shown on the drawings, and that the Structure are correct and in good condition.
3b9a5dca-dd88-559d-a586-73c0781cd840 | note | Standard / Specification - PS- 21.5.4, NZS 3109:1997
83a7317c-9b78-54aa-83ea-a810756ac8fe | note | Verifying Document - Delivery Dockets
f179f23b-39e0-5201-af85-467e05bd913e | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
49ac8dbc-b07a-5b75-bc1b-b488ef47c004 | note | Verification Activity: Activity - H
4bc875b0-768e-5b0c-af6d-27fe69ca4890 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7d104a95-b828-586f-9c6f-abb471a7ef7f | note | Verification Activity: By - SE
3a800c7e-f56b-417a-aa58-be31227845a4 | section | SECTION 4 – STORMWATER MANHOLE INSTALLATION
0f74e26d-886d-40cc-8d20-95e97dd68374 | checkpoint | 4.1 - Foundation Compliance
e3ca5ee8-ae68-505f-b3c9-cfea9b1f72c9 | note | Detail - On Granular or Cohesive Material
91f665b3-a9bb-5aa5-a2ad-c2f19fc78bf8 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
b283c1af-507c-596c-b0a7-960cdaf6614c | note | ○ Cohesive Material: Vane Shear Strength 70kPa
19082f37-2343-5fdb-a60f-81ea6f0ae602 | note | Standard / Specification - Appendix V Table 21:11
31b81c97-5df2-5a78-baad-1b62afd14948 | note | Verifying Document - Shear vane or Scala test result
62a8065c-d002-535b-9260-c0eebc1cd711 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
b19d32b7-ae9c-55ee-a5b0-4296fd7810b6 | note | Verification Activity: Activity - W
847ebf83-1aaf-58c4-98c5-d46da3641740 | note | Verification Activity: By - SE
355bdf55-05a5-4ca1-9c74-6fe49111c9a7 | checkpoint | 4.2 - Undercut approval
1d01efb9-b26a-55bf-9093-ba5126572ce4 | note | Detail - On Subgrade
c1285da9-1f5c-5f41-a5d5-2afc0fa33f18 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
bbef2a4d-cf33-5922-b67a-373ca53c63c5 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
0bd928d1-ecf3-5e94-b43f-d5b31cee2ae0 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
36d3cffc-5fd4-5791-8674-21c39747ec54 | note | Standard / Specification - Table 21.5
eff36e28-7aca-55ad-acb6-cb79a5119178 | note | Verifying Document - Lab Test Report
b3bf3e92-16a5-5f86-bcf0-f60eeb22567b | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
1d6fd074-b7a0-5261-9da6-15ee23083954 | note | Verification Activity: Activity - HP
7676fd72-0a75-5f50-be34-48a46887e138 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
15ffd634-2d96-5542-82e5-a9f05dc53cc5 | note | Verification Activity: By - ENG
84ca83b5-e5c0-46e0-930a-17801a6d3c52 | signoff | AUTHORITY HOLDPOINT
ca866dc1-e9be-4b7a-a6e6-63af79011466 | checkpoint | 4.3 - Undercut Backfill Compliance AP65
311bbad7-490a-5adf-ae61-c421934b6c2f | note | Detail - On Granular Material
6c875342-dd00-54c8-a750-90e49c40551c | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
7fa1bd73-134f-589f-b8ea-d86839fc4ffa | note | OR
247550f7-f5b7-5478-a82e-b2c6aaf5d8ed | note | ○ Clegg 25% CIV
5954a901-914a-5326-a624-c7ac95126bdb | note | Standard / Specification - PS- 16.5.12
90da41e0-89f4-5deb-8ead-8a5899996769 | note | Verifying Document - Lab Test Report
90daec68-c45f-5bc1-afab-3d20f0c155b3 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
3a0463e4-cb53-5200-83ca-cc80f9ebd6e5 | note | Verification Activity: Activity - H
a1432a3c-eb4a-5ce1-9599-ad7f5d856672 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a2f33659-cf7a-5b5b-aa85-63ef861db9d9 | note | Verification Activity: By - SE
0a525cee-369e-480c-8e1e-f94ed1edf217 | checkpoint | 4.4 - Bedding Compaction Testing AP65
03f76ecb-a59a-5c5e-9aea-a226c66b6602 | note | Detail - On Granular Material
266a893c-d06b-56fb-96f6-a50489d4dc3a | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
89ec1779-a2a2-5d1e-910a-0217ce5e38bc | note | OR
b40242e5-86bc-5e91-844f-93012774ab0b | note | ○ Clegg 25% CIV
c5551e87-4b22-535c-9805-97cc92f97e6e | note | Standard / Specification - PS- 16.5.12, PS- 21.6.11
f6b1c228-9a04-5e7e-9e91-2e01e7841575 | note | Verifying Document - Lab Test Report
5c29ffd9-559a-5568-9b21-850c7fb8914c | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
f99ce76b-f8b7-546c-a977-6b22662d3c2c | note | Verification Activity: Activity - H
0786a5ca-2831-55c0-b81f-5c2cb1810cec | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
407c8f8e-7c0e-5ae0-acec-da6f9a9dfbdf | note | Verification Activity: By - SE
16fd6919-bca5-4e79-a7b1-0ca852971d16 | checkpoint | 4.5 - Stilling Well SDMH 11.1.1
a76d2435-12b3-51fc-8089-07bbc6360c89 | note | Detail - Wetland 02 Stilling well detail (SDMH11.1.1)
326011bf-31c7-5d13-bf0d-f0510fb17571 | note | Acceptance / Conformance Criteria - DN1800mm
657136ae-fb5f-5123-8bd6-82635b0775b7 | note | ○ Sump depth > 750mm
618c32cb-f4bc-532b-a817-9484ba9c144a | note | ○ Concrete structure
5d4ec1b7-9bd3-5994-bd23-8590c21f534c | note | ○ Concrete slab constructed
c337e8ee-f90c-5213-b965-4f15f57791bf | note | Standard / Specification - PS -IFC STW 0411
4edd691d-1031-5330-9ca2-6257482800b5 | note | Verifying Document - Material docket
845a8297-d3a6-5f72-b70f-4acde24b5d82 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
bd5bda4b-6338-5091-bc65-13ce354db81b | note | Verification Activity: Activity - HP
016dbf63-b6d1-5c84-aed3-886bda0360f4 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
723da742-8be6-5309-8179-5b5725cb8b10 | note | Verification Activity: By - ENG
e81a3900-34fd-4f57-b098-567c85b618aa | signoff | AUTHORITY HOLDPOINT
b532878e-112f-4174-8438-f94385ee1f7b | checkpoint | 4.6 - Survey
138323d7-1012-5a67-8af6-2d424a67a231 | note | Detail - Inspection of Structure
edd9b1a6-1e51-57bf-9595-d8f8c323ca04 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
820063e9-bd16-56e0-8c34-1e4d5e143f54 | note | Standard / Specification - PS- 21.7.6
6d8878a6-c705-5e8b-8da8-f28a76fe4b8b | note | Verifying Document - Survey Data
cb07de3b-30c1-52b2-99ba-e220b8ba6aca | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
c2fc761d-31c7-55c4-b08a-b50940e9c8e6 | note | Verification Activity: Activity - H
4cb551c8-276f-570c-8041-8fe707ec8783 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
97774ed9-e059-52bd-95d9-95abd702c2d7 | note | Verification Activity: By - SV
d6bb18c4-1062-4f96-b1d1-410226dd6488 | checkpoint | 4.7 - Backfill Compaction Testing
fb859958-46b3-54e4-9674-75e2cfa96fdc | note | Detail - From Overlay layer to the subgrade layer
9b546314-0561-5549-b62d-5ae2eb9f2eba | note | Acceptance / Conformance Criteria - AP65 Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
ab0a2577-c060-5a8b-abb8-703b7c104b53 | note | ○ AP65 - Clegg 28% CIV
f4e9fa6f-5071-5a27-9165-66301a52a4a6 | note | Standard / Specification - PS- 16.5.12
acb5a869-a679-5718-abef-a66e21295e2e | note | Verifying Document - Lab Test Report
3a9f6248-b42b-5cef-b187-03b0bb59311c | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
1ee01d9f-b374-5134-85a6-46be13c141ec | note | Verification Activity: Activity - H
fc8d90d9-1cc5-51b6-9f41-e4d09f310e8e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e37d06b5-288c-51f9-8746-af8bcda12193 | note | Verification Activity: By - SE
fa80ecf0-65ae-4296-8e30-2805b9359902 | checkpoint | 4.8 - Inspection
ab45ca37-83ea-5b88-a113-3f611e5cea00 | note | Detail - Inspection of Structure
b1f072d7-3796-59e2-b909-eae2199b7e2e | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
159cae1c-2abd-550c-ae34-6b62a7801d8a | note | Standard / Specification - PS- 21.6.11
76f063b8-b20b-5707-86a0-14724630ad48 | note | Verifying Document - Manhole/Catchpit Record
fca0b826-5278-5b37-aafb-3cd393bc3238 | note | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
f7393849-7c43-57f2-beef-5984ba665227 | note | Verification Activity: Activity - I
e5cd6a75-9a5a-5466-aaff-e7cc79e8d804 | note | Verification Activity: By - SE
abdf4512-28e3-4310-9d77-791008b6087d | section | SECTION 5 - STORMATER PE PIPELINE CONSTRUCTION
11fe6ee9-a4ff-439d-928e-12d8a61ef35b | checkpoint | 5.1 - Survey
3a95ebae-a0a8-5e74-80fc-1af0afd3536c | note | Detail - Surveyor to Setout
99f00b00-771c-56b6-8bc9-9822bda3d3f1 | note | Acceptance / Conformance Criteria - Horizontal +-100mm
7c602528-b919-574d-8873-4441d18525eb | note | ○ Vertical +-200mm
7af670bf-03dc-57ed-a6fc-39a05acaf4cb | note | Standard / Specification - PS-25.13.5
e51414ae-a8de-5af9-bebd-1bcab640ca9b | note | Verifying Document - Survey Data
df443373-3524-50c4-82ef-8f34705cf39a | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
7be0a470-1a95-5f88-8893-d0d3ce213f0d | note | Verification Activity: Activity - H
7396ed50-e8de-57b1-8a29-d36d6aeb82a9 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8d77753b-d27a-513e-8aed-985ed300dfba | note | Verification Activity: By - SV
8802911d-88f3-4632-ad9a-84a9a0f35eef | section | SECTION 6 - STORMWATER PE PIPELINE (Butt-Fusion Welding)
17b365fc-6ed3-4a5b-801a-64bbb0f811b1 | checkpoint | 6.1 - Butt-Fusion Welding
58065e78-2e3b-5be3-8311-5b62d04fef9e | note | Detail - Use only semi-automatic or automatic welding machines.
698f5001-1c44-5034-b9e4-efbc7e09508c | note | ○ Maintain a site record for all butt-fusion welds.
f33f089d-0e7c-5132-bc87-89cc39a8cb20 | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
613b7b64-5d49-5858-bf80-5f7ab4b9dc5f | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
98a8acbe-2ba7-534b-ae59-94c4b3e346e4 | note | ○ WMS Report
4dbfa37d-066d-5274-b70c-55de2dfaa5c6 | note | Standard / Specification - Appendix 22. PS 22.9.4 C
6ed14af3-c46c-52f9-8e97-1a70d5a9bbff | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report.
0dbe65c5-58ed-5057-9d83-897a54a31272 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
c4dc8896-4d9d-5fc6-b595-996f26fb997c | note | Verification Activity: Activity - HP
e1ab06bd-211e-5719-b8c4-31195621c173 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
55a84597-541a-5e7f-be6f-5f350033741e | note | Verification Activity: By - ENG
dde29abb-fa6a-440e-8c4e-d7a579779c87 | signoff | AUTHORITY HOLDPOINT
457ad58e-aa43-4028-bd4e-9ce3c8b1aa66 | checkpoint | 6.2 - Survey
70d2c213-9e9b-5087-aa1a-da5e563d2df9 | note | Detail - Inspection of Pipeline Inverts
11c0f882-359e-50fd-9f84-118728f1ce18 | note | Acceptance / Conformance Criteria - Horizontal +-100mm
7ba3265c-470b-599f-ab47-6fe312bb00d5 | note | ○ Vertical +-200mm
7bf9bfba-33cd-5a2a-83ee-865fb1cdfe31 | note | Standard / Specification - PS-25.13.5
28578d6b-5e58-5e45-bbbf-de4ca4ad2261 | note | Verifying Document - Survey Data / As-built record
d4b8d4ed-882f-5f0c-9ffc-f97a20d96b1c | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
978fde1c-da35-59d4-924f-e64e87eb736e | note | Verification Activity: Activity - H
923b7e64-dbb5-5b47-9570-9ebcefc98200 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
283e44ac-33ab-55cd-af0e-1bfcbbaf95a7 | note | Verification Activity: By - SE
8248929a-0f2f-4151-aa9b-8cdebc5e1d2d | section | SECTION 7 - STORMWATER PIPELINE DIRECTIONAL DRILLING
556f0354-7943-46bf-8ffa-506ce0acad97 | checkpoint | 7.1 - Drilling level checks
854bc481-f1c0-5b70-8e7e-8277b8acdbc5 | note | Detail - Inspection of Pipeline Inverts
47a74bc9-c747-58b4-8b41-14f2886c037a | note | Acceptance / Conformance Criteria - Horizontal +-100mm
d848b049-9b92-5c52-b4cf-d2d55a954824 | note | ○ Vertical +-200mm
afadb67f-3715-5166-b3a6-82636a817156 | note | Standard / Specification - PS-25.13.5
bfa6e0a4-8ab8-5f32-b5c0-3571996b8789 | note | Verifying Document - Survey Data / As-built record
fbeb149e-aeb5-597a-a079-240ae42006ca | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
8bcf2951-6a51-5655-ad64-077c55e02788 | note | Verification Activity: Activity - HP
90b70e5d-e15e-5a1b-952e-aebeb4d757b6 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6d82bcad-8460-5997-ad09-3e80c43b27ee | note | Verification Activity: By - ENG
06e11ac5-eaa5-4779-b63b-3a7c6add51bf | signoff | AUTHORITY HOLDPOINT
bb3e21a0-7723-490d-9b50-56f9aca9e6b6 | checkpoint | 7.2 - Drilling Fluid Mix
b049973f-9faa-5f77-b14e-af26f96a77f4 | note | Detail - Viscosity record
44db34e1-2e42-5eac-8117-d1c2b0610f3b | note | Acceptance / Conformance Criteria - Pump rate on eam 450L/min
4fb2a03a-81ec-53c9-bf0f-8237f912afc6 | note | Standard / Specification - PS 21.6.6
4f7fbded-e8ce-5ade-9d38-e29c76e11c28 | note | Verifying Document - Viscosity record /checksheet
4819aab3-0cd0-548b-a413-95398908e1b5 | note | Testing Quantity Required (based from schedule qtys) - Every shot
ac9c5f9c-0dde-5f37-a209-af33954c93d6 | note | Verification Activity: Activity - HP
6bdb80e4-8aa4-5ad6-9e27-aadc4ecee646 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
687f10a8-40fb-50b0-a116-0f8f788f0b0d | note | Verification Activity: By - ENG
dd828510-10a7-4374-8d6e-d4391ea57a0e | signoff | AUTHORITY HOLDPOINT
06df876c-1e30-4296-8f63-d9879423be92 | checkpoint | 7.3 - Correct Reamer used
61ce0179-6d8c-5aad-a0b3-9fcb4b306a0d | note | Detail - Reamer size to confirm on site
e6bf8996-a12d-5c43-98a1-0fe03c2f5d43 | note | Acceptance / Conformance Criteria - Reamer size to confirm on site
d58d68a8-4aad-57db-a04a-98c4e2c2b5f9 | note | ○ Reamer must be >1000mm
14097e5c-35e7-5dd6-9e90-b821b7c1befb | note | Standard / Specification - PS 21.6.6
7f2bba3e-9ad0-5a65-921d-2c119abaebc7 | note | Verifying Document - Checksheet
79e5fefc-654f-5382-8e70-0972460cbbe5 | note | Testing Quantity Required (based from schedule qtys) - 1 per drill shot
7f009a24-d8bf-5859-9175-1d9327102905 | note | Verification Activity: Activity - HP
818ab1a9-f3f4-5039-ba59-bc2793419b78 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
89bf9283-1e8b-5420-8447-208c91c1df8b | note | Verification Activity: By - ENG
735f9e43-9f47-4c11-8856-c2cd21bbdc76 | signoff | AUTHORITY HOLDPOINT
bba8ccff-dc19-4fc6-b6ec-263cf85fcc82 | checkpoint | 7.4 - Pipe Damage
4a1fdbdb-5eb2-5980-a390-0ba66716278a | note | Detail - Damage <10% of wall thickness
88d874de-3bdf-5f2f-a5b1-1a5a44a5a7fe | note | Acceptance / Conformance Criteria - Damage <10% of wall thickness
529ae58e-67e3-53fa-a2ba-9129f2e18ec9 | note | Standard / Specification - PS 21.6.6
ae9b7036-d4e5-58d2-b73a-ab9491294129 | note | Verifying Document - Visual inspection
fd9b848a-1eea-5906-9608-0a2fe51e415f | note | Testing Quantity Required (based from schedule qtys) - Each pipe
bdc4866e-433e-59ac-b69f-43c3abd5a2c2 | note | Verification Activity: Activity - HP
1599da5b-88ce-5bee-8742-31f52ed7ed2a | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8652d973-8191-5313-bea4-23d04e1ea57f | note | Verification Activity: By - ENG
2ca02cd0-fa60-4faa-8138-4e6dc82bad28 | signoff | AUTHORITY HOLDPOINT
e6a52b6a-9394-413d-a5a6-3200c2df876a | checkpoint | 7.5 - Tracer Wire
dbb2b08d-ec5d-5b41-ac28-cff89ec2e8e8 | note | Detail - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
381833c0-efde-5e7c-9756-c5e2cbe1c2e6 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
ebcdfff2-e329-5206-b7a1-4794c7e9c471 | note | Acceptance / Conformance Criteria - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
83d704aa-7580-58d0-b14d-fdf682e70f4e | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
cd482e13-a7e1-52f5-bf19-ee992e6929d3 | note | Standard / Specification - PS 22.7.3 a
4e7b4946-7d0a-5f6d-927b-ecb6cada9279 | note | Verifying Document - Visual Inspection
f1dd8ef3-9603-52bc-a0d9-a9bc4b09e07a | note | Testing Quantity Required (based from schedule qtys) - Every Line
2c26ab7a-bfa9-521c-b0db-1a5633a015c6 | note | Verification Activity: Activity - HP
1b1414e2-d663-529f-9747-487bf4492c10 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8eae0432-3145-597b-8d1f-2e43c3411434 | note | Verification Activity: By - ENG
7ac94490-603a-484d-85ff-1141d1f1e49e | signoff | AUTHORITY HOLDPOINT
145ac630-35e7-46a7-8390-5a4148d1874c | checkpoint | 7.6 - Drill Report
a27ba61c-aaab-5988-93d5-4cfcf6de95f2 | note | Detail - Drill reportr to be submitted
07192244-ba38-531d-a00d-01c24399a2d1 | note | Acceptance / Conformance Criteria - Drill reportr to be submitted which shows the all information of the drill works in one report
79d2447d-88c1-5ea2-acff-cf5a070b5ee9 | note | Standard / Specification - PS 21.6.6
aa7d859f-06fb-5792-8921-d143d8d8de04 | note | Verifying Document - Report
1c29dbe8-e1f8-52a7-95fc-eda03a11f5f5 | note | Testing Quantity Required (based from schedule qtys) - Every Line
fe1dd2ea-fdde-5bfd-8d0f-c8688ac48bb5 | note | Verification Activity: Activity - HP
9cf66fc0-d9c6-5a43-90ea-ee88dab1a188 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8a35fdbf-2ce7-5113-b709-3d582b9e4db6 | note | Verification Activity: By - ENG
6562c9ff-5178-4410-b8ed-f765b327766c | signoff | AUTHORITY HOLDPOINT
d0c56c4f-3af6-44f6-a851-c4297ba61146 | checkpoint | 7.7 - Settlement monitoring and ground deformation (Baseline measurements)
273e4ee5-67f6-5a2a-aa48-a06142ac0103 | note | Detail - Topo survey completed before and after drill shot
e05d2ae2-e8c3-5e8d-9477-f24fe7371334 | note | Acceptance / Conformance Criteria - Topo survey completed before and after drill shot
5b0a3d0c-0202-5c1c-bdb2-4abbbcdde93f | note | Standard / Specification - PS 21.6.6
0ff166db-cabb-5ffd-bd4c-3adc29106a9a | note | Verifying Document - Survey data
57840977-ca95-5788-ad5b-fe9d6ef8c2cc | note | Testing Quantity Required (based from schedule qtys) - Every 6m
7c3bdfac-9509-53b7-8b16-b476ee7d0095 | note | Verification Activity: Activity - HP
0195eb16-f9e1-52a2-ae60-b1f7576412b6 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
cee4121a-15d8-55f6-a089-2bfd3e7ac108 | note | Verification Activity: By - ENG
b4f94595-fe47-4aaa-9362-d1a8275d443f | signoff | AUTHORITY HOLDPOINT
782cc862-00ea-49a6-8b95-426959285215 | section | SECTION 8 - CCTV
52805f3a-4bc5-4948-9a51-e452e4a60c2b | checkpoint | 8.1 - CCTV Inspection
8ce16826-3120-504e-8a22-9111927e5299 | note | Detail - CCTV stormwater pipes at completion of trench backfill but prior to final surfacing (pavements, etc.)
6f100f26-8c9c-5089-8750-1ca4018bcf2e | note | Acceptance / Conformance Criteria - Every stormwater pipeline 225mm diameter or greater.
15cec1ee-09dd-5268-bfab-8a3db8bfef54 | note | Standard / Specification - PS- 21.7.6, PS- 21.7.8
6b1d7217-a8fd-55fa-8c0a-1da45109d3ed | note | Verifying Document - CCTV Report
20089747-3331-54bb-82a8-178d61985244 | note | Testing Quantity Required (based from schedule qtys) - 1 per line
76cafc0b-2e0b-565d-a5c4-57beeb73e883 | note | Verification Activity: Activity - S
bd6a76a9-9130-5d8e-b4eb-48608c546767 | note | Verification Activity: By - SE
fc6b9fd1-f2e6-4587-9ef8-584df4f5c3ce | section | SECTION 9 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
10ee1fa9-9a2c-403b-881c-67d18c65b63e | checkpoint | 9.1 - As-Builts / Redpen markups
7e83dd1e-00ff-5c05-9b5b-e395131103a8 | note | Detail - Quality Check on New Works based on the tolerances in RITS
b48eff9a-7e1f-5a0b-9759-23d7f9047cfe | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
be00c091-6dbd-59da-9335-68c3c07a2bfe | note | Standard / Specification - Project Specifications
869d354c-69d5-5241-a221-864cae2cd4cc | note | Verifying Document - Red pen markup only
a618e09c-9e84-5de7-89f2-07da9d5ac913 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
8d058b51-f0ab-5456-ac76-8227b8012b0b | note | Verification Activity: Activity - H
f200bf75-b012-50e2-8a6f-0bb2db9ee2e5 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d35f4163-b686-5832-803d-3486437af003 | note | Verification Activity: By - SE
f3d2a8ca-cf97-46eb-a767-2ab1d3febf6d | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
405660f9-fdc6-5d11-8e3e-34cf9dd0ce3b | textbox | Contractor's Rep Name:
4eb7c320-6a12-5e1a-91f4-81c59aeb86b9 | textbox | Engineer's Rep. Name:
75dc5c24-c0e5-52f3-a0db-5bdb65519f12 | date | Date:
041e62b8-37f7-4762-90f2-91fbcb7a78f4 | signoff | Add Signature
739f1626-cb5b-4474-b8eb-59a8bd182d79 | checklist | DN1210-SP2-020-002 ITP Earthworks Wetland 03 Rev 1 | itp | DN1210-SP2-020-002 ITP Earthworks Wetland 03
911fa88b-1f05-4c66-ac58-3f556a9d445b | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
c9592e96-0868-43b1-8ab7-ec27458dbb63 | checkpoint | 3.1 - Erosion & Sedimentation Controls
7656bc3e-8691-521e-a921-8910a9505b3e | note | Detail - Confirm that Erosion and Sedimentation Controls are in place prior to earthworks proceeding
164dbb8d-43be-5b29-ad8f-e57a0b5e739f | note | Acceptance / Conformance Criteria - As-built Completed
4ffff8b2-3726-5805-bcbc-828a86b181da | note | Standard / Specification - Internal Hold Point
e52451e6-adbd-5aab-aac1-e4abd77b9999 | note | Verifying Document - ESC As-built
ceccf717-de0f-53d4-a802-c891e57fdcf8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
ed396de7-0e7e-5f84-8db3-9315ff7c2920 | note | Verification Activity: Activity - H
ab68baf3-66c2-57ae-9677-1c41627862ce | note | Verification Activity: By - SE
38201533-a6c2-486b-a07f-fb987e067589 | checkpoint | 3.2 - AP65-2 - Source material testing - Crushing Resistance
559901eb-b3a4-5e3d-9610-f5bbe6556d18 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
ce9bf265-c2cd-5d57-954c-0387656f4df6 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 100kN
3898dadc-74b5-5dc4-9cae-a6b3bb35a2e6 | note | Standard / Specification - NZS4407:2015 Test 3.10, TCC-IDC-IT-4.3.1-4.7.1
986c5e5b-9e0a-588f-9171-994ddebe6a28 | note | Verifying Document - IANZ Accredited Report
b77f4048-a881-5633-b666-cd3fb1eb6e55 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
23c7d83f-7280-5d1b-8b17-8c8639d685dc | note | ○ Results to Engineer 2 wks before importing
cd3b316d-dfae-5daa-8af5-93e210daa382 | note | Verification Activity: Activity - HP
436dd72e-68a8-5366-8cbb-d650bf70ce29 | note | Verification Activity: By - ENG
2d9ba417-d2b3-49ba-a4ac-eff4c5eb5374 | signoff | AUTHORITY HOLDPOINT
09ca9bac-f0c3-4bbc-b988-dcb1a3b89567 | checkpoint | 3.3 - AP65-2 - Source material testing - Soaked CBR
8e03863e-8fda-5e91-aaf6-a1df366c20bd | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
54178a16-82a4-5722-9bd7-48b07c447f8f | note | Acceptance / Conformance Criteria - ≥60%
ce928d11-660b-5a51-a923-d200f8bc3740 | note | Standard / Specification - NZS4402 Test 3.15, TCC-IDC-IT-4.3.1-4.7.1
d30171bd-98a8-5741-8bdf-935e821c50ab | note | Verifying Document - IANZ Accredited Report
3cdf0b3b-e2f7-5215-9bf5-be0b74b7ff06 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
f27376c5-9c51-5229-a426-b0947e97db4b | note | ○ Results to Engineer 2 wks before importing
3d01d750-d2f2-5515-a0d7-132817b0e079 | note | Verification Activity: Activity - HP
f323b60b-f172-5237-8c41-ba7140a07712 | note | Verification Activity: By - ENG
6d47ab3f-4d17-43bb-9eb2-4dc7a838b0fd | signoff | AUTHORITY HOLDPOINT
1758fa0c-4598-4e1b-9e76-4e5752f17910 | checkpoint | 3.4 - AP65-2 - Source material testing -Weathering Resistance
4fb672d4-4862-5410-844b-b501b20954c1 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
6ff4acde-6f0a-5e39-9ff7-84778c0d007d | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, CA or CB
965480e5-38a6-51e3-b227-7e137e32f8a1 | note | Standard / Specification - NZS4407 Test 3.11, TCC-IDC-IT-4.7.1
99c65124-5694-5341-9ff8-152b4f39be07 | note | Verifying Document - IANZ Accredited Report
e07a7195-0169-503a-8f2e-adb4b2c90465 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
98f30d71-f8f4-50a4-8e41-6e4ae7bde0fb | note | ○ Results to Engineer 2 wks before importing
cbe06db2-dc7d-5307-b034-52bbf97947e2 | note | Verification Activity: Activity - HP
06073531-1c97-557b-ac70-b511df67ed63 | note | Verification Activity: By - ENG
c7f542a0-05cc-4cb3-81f2-b659a2975284 | signoff | AUTHORITY HOLDPOINT
6e40c564-0ba3-4b24-b40b-70ba3e1bcf94 | checkpoint | 3.5 - AP65-2 - Production testing - Particle Size Distribution
996c7550-3d54-517c-a00d-b9c82a9a0b1a | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
0e891d8a-dcde-5b03-b17b-842549a58abb | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
6c33cecd-8029-5cff-b5a6-9959676cbd50 | note | 63.0mm ¦¦ 100% passing
c5a630e3-0311-5ef7-ae48-c054f9e205a4 | note | 37.5mm ¦¦ 68-90% passing
e306d344-289c-5c56-ac50-ad4b6eda1bbb | note | 19.0mm ¦¦ 42-76% passing
6f20cf1c-513e-5bb0-8ed9-f0f7876f6dc0 | note | 9.5mm ¦¦ 26-58% passing
aaf10446-ee54-5952-99f8-5883b680b44f | note | 4.75mm ¦¦ 16-44% passing
9034dcd8-291d-56b9-a6c5-aa5419d3667f | note | 2.36mm ¦¦ 10-33% passing
c974f0b5-534a-5418-a795-b4843efa00c6 | note | 1.18mm ¦¦ 6-24% passing
8e43ae87-0d9a-537d-97f9-df8ac57ce0ed | note | 0.425mm ¦¦ 3-14% passing
20f69c2d-d517-52a4-bb24-b5861442c4e9 | note | 0.075mm ¦¦ 1-6% passing
06226c42-f8f7-5e95-a5c7-abd487bdf164 | note | Standard / Specification - NZS4407 Test 3.8.1, TCC-IDC-IT-4.7.2
9b602693-f76b-5ac7-a53d-472e83c8a2eb | note | Verifying Document - IANZ Accredited Report
54520cfa-cbef-5c5e-9940-55af366f0dde | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
58bad373-3cc0-5e27-960c-9d9c3efdb3a1 | note | ○ 0-400 - 2 tests
289e6389-3a79-51a1-b98b-3be7a8a81d15 | note | ○ 400-1,500 - 3 tests
42d66246-7236-5525-9fa2-ef0d995fac1b | note | ○ 1,500-4,000 - 4 tests
e9bcc3be-6d5a-5e20-bf63-4701613e3890 | note | ○ >4,000 - 1 test for each additional 1,000m3
e1970975-db84-586c-94f9-3cf0ed6d66ab | note | — Results to Engineer 2 wks before importing
a3232d9b-2db4-599d-a34d-c36f907716cd | note | Verification Activity: Activity - HP
ead631dc-01cb-57f4-b050-3515bc7fd15a | note | Verification Activity: By - ENG
1bbc6f3c-f456-4984-b979-3616325a6a11 | signoff | AUTHORITY HOLDPOINT
dac6082e-a68b-4d83-a379-5a269778a0fe | checkpoint | 3.6 - AP65-2 Production testing - Shape Control
450b800d-1296-5e2a-8599-41673f663685 | note | Detail - Tolerance allowed from approved grading curve (%)
4cdca67b-869f-5a1d-8ed8-a50cf847f7b5 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
b3f27bca-994c-5587-89ff-021969e9a731 | note | 37.5 – 9.5 ¦¦ 34-50%
e7046975-895d-5c57-af89-f49a35a9d521 | note | 19.0 – 4.75 ¦¦ 18-40%
282c15dd-8c47-5c6d-af94-8bb95543115d | note | 9.5 – 2.36 ¦¦ 12-32%
e6cd6cb5-9677-571f-9561-9475bb119ba3 | note | 4.75 – 1.18 ¦¦ 6-24%
9e6e40bf-7f73-5536-a511-6aae446046f2 | note | 2.36 – 0.6 ¦¦ 2-20%
ed434596-4418-5fdd-9d02-d811b45e9f30 | note | 1.18 – 0.3 ¦¦ 0-15%
7a805a95-3e90-5675-a603-167ff10163c5 | note | 0.6 – 0.15 ¦¦ 0-12%
060d967e-9e68-5601-9031-4ad4fb240f2e | note | Standard / Specification - TCC-IDC IT-4.7.2
6cd909d4-c943-52ae-b0fe-2fd8ac5aba20 | note | Verifying Document - IANZ Accredited Report
948c78ef-c8dd-5282-80dc-e4575af49941 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
b24cdd74-4af7-5b5c-9dc8-ae397beac988 | note | ○ 0-400 - 2 tests
7babe843-1aa1-541b-96aa-28db78e5a7b5 | note | ○ 400-1,500 - 3 tests
9ed9f78e-7f2e-5a96-9604-726c3c618184 | note | ○ 1,500-4,000 - 4 tests
64aee5b9-0155-5743-86d0-4647200d0081 | note | ○ >4,000 - 1 test for each additional 1,000m3
0cad9195-2ab9-5150-9669-77633d254ef4 | note | — Results to Engineer 2 wks before importing
36500245-0b99-5abd-b696-45fa20e2d17c | note | Verification Activity: Activity - HP
1e2f029c-3dbd-52a6-9da5-632b773c1c9e | note | Verification Activity: By - ENG
469de2d6-c2fa-4af4-afb7-41491dc569df | signoff | AUTHORITY HOLDPOINT
c0f0d6c3-c27c-408d-9222-9bac9d74d25c | checkpoint | 3.7 - AP65-2 Production testing - Maximum Dry Density and Optimum Water Content
989c91b2-5f6b-505b-a2ed-00e80c1e10c0 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
420aa77b-5d75-54a2-a9e6-367fa694f94b | note | Acceptance / Conformance Criteria - Report Value Only
6a3f3376-b9e1-5ce4-b791-ba981fcbce62 | note | Standard / Specification - NZS4407 TCC-IDC-IT-4.7.1
9364ce2e-428e-5343-9da7-ac56b7d6174c | note | Verifying Document - IANZ Accredited Report
462eb516-c56f-5f3e-a509-7440adc9da37 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
b1d48dfa-297b-5f78-a262-a746dd741a3a | note | ○ Results to Engineer 2 wks before importing
be271d41-5e31-553b-b551-0137d7b9ec50 | note | Verification Activity: Activity - HP
a79ac3e6-6bff-5173-bda4-c3badef4a963 | note | Verification Activity: By - ENG
dbb3de6c-a798-45e0-ba69-05a1274fb050 | signoff | AUTHORITY HOLDPOINT
00879170-8fed-4d93-96e6-d8797c39e693 | checkpoint | 3.8 - AP65-2 Production testing - The Solid Density
f09de597-5c98-5a38-bce9-d468bd3d7c30 | note | Detail - NZS 4407:1991 Test
dc80862c-7980-561d-b778-7aa8a2c5b25b | note | Acceptance / Conformance Criteria - Report Value Only
a8a2eaa5-fd6c-5d00-82bc-7fee21948a72 | note | Standard / Specification - NZS4407 TNZ B/02:2005 7.5, TCC-IDC-IT-4.7.1
50ec33ab-ffce-58bc-ae30-65feea71dd09 | note | Verifying Document - IANZ Accredited Report
112da9d2-ae81-5fe7-8269-a0f9cef38f7f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
c5179435-2f2f-5ad7-a11f-b0fa53aa6d26 | note | ○ Results to Engineer 2 wks before importing
87a4d87e-9bac-53ef-8b42-9b2d268d15c2 | note | Verification Activity: Activity - HP
2e6b67b0-1977-5e42-be59-c8c1a273606d | note | Verification Activity: By - ENG
3512e48b-e8af-45ea-b19d-647ef543f08b | signoff | AUTHORITY HOLDPOINT
ef57964b-2514-4ec3-b0a7-efea2e5a221c | checkpoint | 3.9 - AP65-2 - Production testing - Plasticity Index
c8d8d4f4-9900-5408-8bc2-c3d12b0774c9 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
2e0dee62-f5cf-5d39-a7f3-edf5de1f21d9 | note | Acceptance / Conformance Criteria - ≤ 8
7567c0bf-4eb4-5847-9ef6-cac1e7b4c59b | note | Standard / Specification - NZS4407:2015 Test 3.4, TCC-IDC-IT-4.7.2
d1ad766c-540d-5da0-8b22-e17b265f1428 | note | Verifying Document - IANZ Accredited Report
f3ac5415-c7c2-5cc5-80fc-5a2435ea6cc7 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
f655a07a-e3bf-588a-8472-4b6b910879e3 | note | ○ Results to Engineer 2 wks before importing
666a97d3-cc64-5676-ac6d-230522968159 | note | Verification Activity: Activity - HP
3fdbd9b9-e1bb-5356-bfae-a7ffb75a4d43 | note | Verification Activity: By - ENG
e7db3ded-f8fd-42cb-b4d1-e7e50205b173 | signoff | AUTHORITY HOLDPOINT
f1e8fd2b-4001-4958-ae9e-ba36d2005957 | checkpoint | 3.10 - AP65-2 - Production testing - Sand Equivalent
0ee04e30-fdc0-53fe-8683-8345edaeccbb | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent, Washing method
6da80c15-4c16-5ffe-8faf-4abe6295e8b4 | note | Acceptance / Conformance Criteria - ≥25
7324eff5-f692-59ab-bb56-46e898a8ef07 | note | Standard / Specification - NZS4407 Test 3.6, TCC-IDC-IT-4.7.2
557649b3-fb65-5b93-89d6-8dbd8c08f43a | note | Verifying Document - IANZ Accredited Report
3f90de70-d2e8-566c-93de-6311d2eb0da2 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
fbdf62f8-81be-5dc8-b976-8a5dded0b885 | note | ○ Results to Engineer 2 wks before importing
94539b16-1521-58ee-9554-a87863052c9b | note | Verification Activity: Activity - HP
0010f573-db33-5dd6-8d6c-643ca636349d | note | Verification Activity: By - ENG
9b1e9221-caf5-4e29-bee4-bbeb519ecd41 | signoff | AUTHORITY HOLDPOINT
581e7048-1f0b-4884-ae3a-9566abd069f6 | checkpoint | 3.11 - Geotextile
3f9d763c-d25b-5a5e-917f-45b96ec1209f | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation. Class D
d97f97bb-11e0-59d2-95dc-21ed47b1da33 | note | Acceptance / Conformance Criteria - Engineers Approval
127fda03-198a-5d87-8958-398f30a1aec6 | note | Standard / Specification - PS 16.5.7 Appendix V
39bf43e8-f8ce-551a-aaea-1c02f239b844 | note | Verifying Document - Delivery Docket/Material certificate
cdf232af-70c4-5f47-b1fd-ea2f76a85ab8 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
d2afb6de-2045-5672-9945-0ed0522f6605 | note | Verification Activity: Activity - HP
49b14894-410c-51d4-810b-af83cfab94c0 | note | Verification Activity: By - ENG
e30e2e71-ede1-469e-bc01-125ba43dc7f7 | signoff | AUTHORITY HOLDPOINT
d83356fb-ff9b-4420-9d8b-84d12b7a17e4 | section | SECTION 3.2 - Imported/Site Won Material Testing - ALL TESTS TO BE NO OLDER THAN 3 MONTHS
ed4cdbc6-8353-4382-929c-ddc39e2af942 | checkpoint | 3.2.1 - Site Topsoil - Laboratory Testing for Soil Suitability
1ea93a16-ffcc-5ed1-b9bf-c740df311e90 | note | Detail - Soil Test Results from Hill Laboratories to confirm that topsoil suitable to for reuse
935bd365-1136-52ea-93b1-2fa9d5f47ee4 | note | ○ Soil Reaction
7467352c-ad81-543c-b8bf-f71261f895e6 | note | ○ Electrical Conductivity
047c79be-f969-5048-9387-2982d5b744ca | note | ○ Mechanical Analysis (texture)
72d79b04-1469-5834-b317-811b73e07fca | note | ○ Stone Content
893bdda7-2dfe-5b36-a664-e4bea065718a | note | ○ Nutrient Levels of nitrogen, available phosphorus, available potassium and available magnesium
a4a85abe-f938-5104-9799-7fcd20126708 | note | ○ Organic Matter Content
9da0f534-a68a-5c0a-badb-3cd9635470cb | note | ○ Check for Toxic or Hazardous substances
500358b1-abd4-5ec2-99fe-81d40b622210 | note | Acceptance / Conformance Criteria - Engineers Approval
987ff1f6-07fd-5a81-a5f2-b61814e60803 | note | Standard / Specification - NZTA P39:2013 3.1
cc595a1a-b2c8-5a90-ae48-0685ab0ebbb9 | note | Verifying Document - Laboratories Test Report
fa25b035-7158-57b5-a5b8-ee17b03f6aa3 | note | Testing Quantity Required (based from schedule qtys) - 10 equal samples taken from site, mixed together, then 1kg of soil sealed into a plastic bag and sent to lab for sampling
5fd20d26-8905-5907-a500-191694fc1318 | note | Verification Activity: Activity - I
cb3e046a-e477-506d-b93f-8ad97b630484 | note | Verification Activity: By - SE
428f85fe-bf20-4368-a1aa-cd3918eb457b | checkpoint | 3.2.2 - SITE WON MATERIAL (TYPE A2 NON-GRANULAR)- Maximum dry density optimum water content air voids and shear vane strength (su) with range of mositure contents
366abda3-d5cf-574b-8086-7b375fc99843 | note | Detail - NZS4402:1986 test, 4.1.2 heavy compaction test
9d08f8ba-b1ab-547f-afc0-772a8a45a3bd | note | Acceptance / Conformance Criteria - Results from test
33806d19-7994-5328-ae18-baa6c9081f9f | note | Standard / Specification - Appendix XVIII
b6cf3b85-3cb6-5d7d-9cfe-dd07a997a1b4 | note | Verifying Document - Report
71eee27a-e254-5acd-8817-ec81b66d9531 | note | Testing Quantity Required (based from schedule qtys) - 1 set (3 tests) per material type and source
6dc674a9-4ce8-5db8-8c84-408db08eed07 | note | Verification Activity: Activity - HP
cbe5f7b7-e746-523e-8eb5-77972b9799fa | note | Verification Activity: By - ENG
0b14d331-29d5-483c-9c50-56c97770c5cb | signoff | AUTHORITY HOLDPOINT
4c99cb67-535f-4b5b-8591-bda76fec44bb | checkpoint | 3.2.3 - SITE WON MATERIAL (TYPE A2 NON-GRANULAR) - Organic content
23189d9d-0b82-5846-bf7b-bdf3178f8d17 | note | Detail - Visual observation
51b65e5b-4aa3-5e3c-98dd-94da553c4cf2 | note | Acceptance / Conformance Criteria - Fill shall be free from organic, calcareous or other deleterious materials
4df3c7e9-48fa-5685-8d97-f2208d917a1d | note | Standard / Specification - Appendix XVIII
e768575a-150b-5699-88bd-1f04d973f29b | note | Verifying Document - ConQA
6c91360f-3db7-5fc7-9c6d-ca3e3492a164 | note | Testing Quantity Required (based from schedule qtys) - Fill shall be free from organic, calcareous or other deleterious materials
ce125177-9668-55f5-a0ae-c432c2deb3c0 | note | Verification Activity: Activity - HP
da2d60b6-3e21-5117-8671-fd13d14d478c | note | Verification Activity: By - ENG
f164994e-dceb-4e52-b0b4-f3990076d70d | signoff | AUTHORITY HOLDPOINT
622ea3fd-6d72-4d34-bdd7-d1a8af0073da | checkpoint | 3.2.4 - SITE WON MATERIAL (TYPE A2 NON-GRANULAR) - Soil Permability
7a63f1f2-d06d-5eab-b092-b1c05796c20f | note | Detail - maximum soil permeability
e13e8ec9-07f8-5678-9f9f-9487e929b29b | note | Acceptance / Conformance Criteria - 10-7 m/s
1aeb4bbb-2606-54ad-a14f-546015d847a8 | note | Standard / Specification - PS:16.5.5 Appendix XVIII
faa20389-b4bc-5748-8c0f-efaa65c213ae | note | Verifying Document - Report
44f87d00-a510-5c52-a6cf-14cfd9efbc22 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
80ca2aa3-6f4f-55fc-8301-35ae70ea3748 | note | Verification Activity: Activity - HP
c2899abc-0fd1-57d6-b9dd-8c41baba9c10 | note | Verification Activity: By - ENG
a49f89f0-f917-4ddf-bd47-67fe5acd2e65 | signoff | AUTHORITY HOLDPOINT
ef3efaad-ec92-46dc-8e35-2cb3893cf202 | checkpoint | 3.2.5 - SITE WON MATERIAL (TYPE A2 NON-GRANULAR) - Liquid limit
bb7da9cd-9422-5e4a-b8d0-5e8429de7a9f | note | Detail - liquid limit
d15fac55-4c84-57fb-94ce-ae5c90658552 | note | Acceptance / Conformance Criteria - less than 65% (Engineers Approval)
37114a27-2081-5540-9c75-1dbe58eea652 | note | Standard / Specification - PS:16.5.5
8bb701e7-7c9a-5a9a-bc70-b1e77d1b4088 | note | Verifying Document - Report
b77efab0-4de5-50e1-9504-a4a3efb96ee8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
1ea536bd-0448-5e28-bad8-87a3f88a9035 | note | Verification Activity: Activity - HP
2aa29d02-fdb9-5591-b178-9a531f6d177d | note | Verification Activity: By - ENG
68878a62-b455-4a60-ad50-1ed0036dcacc | signoff | AUTHORITY HOLDPOINT
6cfd553b-93bc-4e19-bbea-f46960c0f3b3 | checkpoint | 3.2.6 - SITE WON MATERIAL (TYPE A2 NON-GRANULAR) - Moisture content
a96cd762-4b37-5517-bd6d-8eaf7d49218b | note | Detail - maximum moisture content
423ce998-4ec0-5992-802b-d6ee0e0370e6 | note | Acceptance / Conformance Criteria - 6 % above (Engineers Approval)
abb1303a-222f-5f79-8809-32e8a9e6dc07 | note | Standard / Specification - PS:16.5.5
4fc6c5b6-15b9-5f58-8592-6f04f23fe833 | note | Verifying Document - Report
1370a3fe-7616-5f57-9b0f-6fd84606ab9d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
97ac3297-49f3-5406-9285-844666421706 | note | Verification Activity: Activity - HP
ddd19d18-f039-5e60-8a02-27926a771e9e | note | Verification Activity: By - ENG
b871f39f-44f3-42f4-b67f-3586f9ac37cf | signoff | AUTHORITY HOLDPOINT
eed018de-e7b4-4ef7-8db3-3a3dae0b33fa | checkpoint | 3.2.7 - SITE WON MATERIAL (TYPE A2 NON-GRANULAR) - Prohibitied materials
0db1c174-5165-5381-bf05-811482ef4229 | note | Detail - deleterious materials
1c96a4c7-da47-50ba-accd-8e08d592bce4 | note | Acceptance / Conformance Criteria - Not containing allophane, organics or other deleterious materials. (Engineers Approval)
baa27b27-b7eb-5588-a6df-d51163aefff1 | note | Standard / Specification - PS:16.5.5
7aeca19b-f911-5002-a24e-a2ab3d293924 | note | Verifying Document - Report
5af9a4ac-d5d0-5c8d-802a-bbea751bd776 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
9776b9fa-d51a-531f-a7cc-665431b8d505 | note | Verification Activity: Activity - HP
f41d8f4d-c98a-527d-b6f0-2b60590644bf | note | Verification Activity: By - ENG
17c999af-9d29-4933-97ca-bcb78628420d | signoff | AUTHORITY HOLDPOINT
fa07fc56-a847-4284-846e-248c8f230740 | checkpoint | 3.2.8 - Pumice sand - Maximum dry density optimum water content air voids and shear vane strength (su) with range of mositure contents
5282de1f-a168-5740-9627-44ae5dd7ac11 | note | Detail - NZS4402:1986 test, 4.1.2 heavy compaction test
7a4192e7-db47-5d59-a7ab-abb4c895603f | note | Acceptance / Conformance Criteria - Results from test
78777c97-394e-54e6-bac0-a46d07418c32 | note | Standard / Specification - Appendix XVIII
b6eb1c19-777b-5493-891e-484b32798f30 | note | Verifying Document - Report
f31397c0-1618-5a17-89f8-80f216581770 | note | Testing Quantity Required (based from schedule qtys) - 1 set (3 tests) per material type and source
0f914e1a-3a2f-515f-b913-ac0a31770194 | note | Verification Activity: Activity - HP
58f7bede-2f6b-5bb7-bbc1-cb75e662db1a | note | Verification Activity: By - ENG
c64d67b2-2c0e-49aa-a4ef-ded515769685 | signoff | AUTHORITY HOLDPOINT
4d90f6df-8983-406f-b975-aeff316bd397 | checkpoint | 3.2.9 - Pumice sand - Organic content
9679a672-ad71-5403-ae78-333a3583e26d | note | Detail - Visual observation
002512d7-1c7f-5ba1-9651-6f05fa9028b9 | note | Acceptance / Conformance Criteria - Fill shall be free from organic, calcareous or other deleterious materials
0a1b9a7b-0fe1-548d-b181-b1d5928d4acd | note | Standard / Specification - Appendix XVIII
406e4244-d86f-50c1-abd4-1289e3f23853 | note | Verifying Document - ConQA
531a1072-3d13-503b-ace8-df2a154af8f8 | note | Testing Quantity Required (based from schedule qtys) - Fill shall be free from organic, calcareous or other deleterious materials
b200d3eb-e85b-5529-9dd4-0a8ac4ca3673 | note | Verification Activity: Activity - HP
7274adc7-3019-58c2-8413-c559795e3598 | note | Verification Activity: By - ENG
65354a9a-1e32-479a-9a0d-d4f3e53e1dcf | signoff | AUTHORITY HOLDPOINT
33898553-a1ee-416b-b6b1-d2e79ac7d8b4 | checkpoint | 3.2.10 - Pumice sand - Soil Permability
8e1f45a8-acd7-5e0b-a770-c8c027849d00 | note | Detail - maximum soil permeability
9e324d55-7eb8-5e9a-a841-8f4deface90e | note | Acceptance / Conformance Criteria - 10-7 m/s
6b8e45c0-2889-502e-a3c8-9bbcba88d8d1 | note | Standard / Specification - PS:16.5.5 Appendix XVIII
3ff3e8da-42c8-570f-8796-9029eaedc62c | note | Verifying Document - Report
c56c60e3-2c12-5c36-a92e-85fec25da676 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
bc58e565-2edb-5a2e-a64f-3c8ad3c5dae8 | note | Verification Activity: Activity - HP
baf208e5-be9b-5a61-a30d-562606849e78 | note | Verification Activity: By - ENG
f1346f25-0ca7-4e48-9d92-7e463ac8bd4f | signoff | AUTHORITY HOLDPOINT
1b2688cc-faa0-4276-8060-733851cc74e8 | checkpoint | 3.2.11 - Pumice sand - Liquid limit
9a874f88-b6ee-548a-9427-897074420fcf | note | Detail - liquid limit
cff13a49-d65c-5c8a-8889-35591394425f | note | Acceptance / Conformance Criteria - less than 65% (Engineers Approval)
9e0a52e6-0cee-575a-943b-d959bb60aaa6 | note | Standard / Specification - PS:16.5.5
b97b272b-b2ea-5bc1-bac0-4cd8597f16f7 | note | Verifying Document - Report
ee178cff-6d08-5df6-bb4e-f60e1988a029 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
d78b0d81-caeb-5d29-88ce-152da50fa8a0 | note | Verification Activity: Activity - HP
fbc3f4fb-e7f5-5ea9-9bc5-50b7798c49c8 | note | Verification Activity: By - ENG
e942afc3-77c7-4f7e-9d2c-05726ee01d58 | signoff | AUTHORITY HOLDPOINT
a4ab37e9-1361-48e5-9783-23d8cda393eb | checkpoint | 3.2.12 - Pumice sand - Moisture content
bf5b0cc8-bb6d-5cf2-9b12-3a35cd562267 | note | Detail - maximum moisture content
26dbcd0b-6677-58bf-ae82-8f2d098ec21a | note | Acceptance / Conformance Criteria - 6 % above (Engineers Approval)
cd0854b8-3870-5f23-a1c2-93e7cd948a28 | note | Standard / Specification - PS:16.5.5
95d41cf2-6b03-552e-97ca-21015a4c7f2a | note | Verifying Document - Report
376cb40a-393d-5dbb-bd76-2034ae28ac1a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
34afe685-4744-5ff8-bbcb-468bbb869251 | note | Verification Activity: Activity - HP
2ec75321-96f0-5796-96ce-cbb7a0d076dd | note | Verification Activity: By - ENG
cfba3c87-9aab-449e-aab1-23d51ddef750 | signoff | AUTHORITY HOLDPOINT
4803e557-3ef7-4200-ba7b-a299644cecdc | checkpoint | 3.2.13 - Pumice sand - Prohibitied materials
df8b0d1d-ab37-544d-97f0-493cb559a55f | note | Detail - deleterious materials
01c0cb8b-1bb3-507c-84ff-1a077da0bb52 | note | Acceptance / Conformance Criteria - Not containing allophane, organics or other deleterious materials. (Engineers Approval)
8350f849-c812-57da-a299-1b0304f74d84 | note | Standard / Specification - PS:16.5.5
1071900c-d32b-5f82-b8a2-f0198c3b261d | note | Verifying Document - Report
09163658-3e76-5d71-a66a-2b2a0b8411d8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Source
3cbe65b1-6193-5e69-81f4-ecc5dd7f355c | note | Verification Activity: Activity - HP
93b93d67-e127-563a-838c-a1cbfa0b6d67 | note | Verification Activity: By - ENG
cb662a6e-2a50-4831-ab09-f3c18e9dfe53 | signoff | AUTHORITY HOLDPOINT
d2c02f8c-87f5-475b-8285-abf643726456 | checkpoint | 3.2.14 - Pumice sand - Compaction
ecdf93d2-3c1a-528d-93fe-9f6283e8cfdb | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
75c9bbee-5f90-5df8-b512-1d14f002a955 | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
f7b6ce7d-b0eb-5d8f-a9b9-8bdc8a7163f8 | note | Acceptance / Conformance Criteria - Scala blows >3
11f80198-48f9-5b00-ad0d-3e57237e839a | note | Standard / Specification - PS16.5.12
9c4f5e77-6b21-5711-a94b-674e2c54eada | note | Verifying Document - Report
7a4f3841-edb2-588a-945d-ea346959775e | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
e3ac9bfe-5858-50c7-b286-c6b36c3032fc | note | Verification Activity: Activity - HP
e467b643-51c3-5efc-a283-b494a2a74332 | note | Verification Activity: By - ENG
23d26916-6964-4e0b-9376-5ebd7e8f4f50 | signoff | AUTHORITY HOLDPOINT
96b3028f-025f-40af-927b-9893ee9ab938 | checkpoint | 3.2.15 - Pumice sand - Bulk density, Dry density, Air voids
cdbe6ed1-2ac4-555f-836a-370d892ee498 | note | Detail - NZS4402:1986 - Test 5.1.3 sampling tube method for determination of the in-situ density
09cc1250-e76d-5eca-b750-12e6606e613b | note | Acceptance / Conformance Criteria - Results from test
4b7153c4-2d01-5f6b-a3b8-2c1429f0d4c6 | note | Standard / Specification - Appendix XVIII
76709202-43ac-57b8-9cd2-1d776999d20f | note | Verifying Document - Report
b2307f83-1c55-59c6-9a69-0468ea90631c | note | Testing Quantity Required (based from schedule qtys) - 1 Test performed for every 10 NDM
491c4572-d416-5377-b9a3-24e0d9648b0a | note | Verification Activity: Activity - HP
3e656eed-103a-5c72-b4be-9825db414f47 | note | Verification Activity: By - ENG
5c471d62-389b-426b-81eb-02c9978a6e9d | signoff | AUTHORITY HOLDPOINT
2f8cf704-cf1f-44fe-bbee-dcbf44dea56c | section | SECTION 4 - CONSTRUCTION - ACCESS TRACK
61cf71ab-c7ad-451d-8045-5973859be593 | checkpoint | 4.1 - Subgrade Level Confirmation
e29614c8-4158-510b-822f-004e7c061a3d | note | Detail - Confirm subgrade is 300mm from finished height
b7abef2a-38cb-5c5b-a281-075ec7f0ede6 | note | Acceptance / Conformance Criteria - String lines - or equivalent are 400mm +0mm/-30mm
31f3ffcd-74be-528b-a61e-7f8b4dd0f9c9 | note | ○ Tolerances width -20mm +100mm
3e1f6da0-d4c9-5e89-8bfd-34fe94bf8c59 | note | Standard / Specification - PS 20.14.5
1d13bf82-0e86-5853-aaf7-9875672e7b9e | note | Verifying Document - Survey as-builts
0e62b209-f35b-5acf-b731-4aa665d20bf5 | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage
b6d59a17-f826-5dba-9a79-6e4a58bec2c5 | note | Verification Activity: Activity - I
1f1797d4-70d7-5032-88d6-5f04293c1748 | note | Verification Activity: By - SE
81f8c66a-01f4-40ed-85fd-f64d72025206 | checkpoint | 4.2 - Subgrade - CBR Testing
4acf944a-f11a-5112-a6c8-24ba77881787 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
0711c3f0-937e-5d0c-b655-4353842f9c46 | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
7547c264-6765-5e7d-9fdd-1acdcb601fec | note | Acceptance / Conformance Criteria - CBR >7
5fefaf6d-9b90-57d4-9b89-97dbbb4c96d1 | note | ○ Min 3 blows / 100mm
92a58ab8-a4a0-5c61-af4d-db30e1829bc6 | note | Standard / Specification - PS 27.4.2 Appendix XVIII
f4018e4a-5f55-5df1-9fd1-ad2556394158 | note | Verifying Document - Scala Report
25fb5f9b-c77a-5210-815a-b07fe3e5c9af | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
51418a1c-3030-596c-88ed-ac72de034064 | note | Verification Activity: Activity - I
dc432f66-5228-57ed-b9e8-19e0a1405f42 | note | Verification Activity: By - SE
40abc8c7-a995-4e72-9a12-f0be788c4502 | checkpoint | 4.3 - Subgrade - CBR Testing
aa59c272-249b-518e-b3e8-cb4d49da77b5 | note | Detail - "NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
3e09efcf-5652-5354-9057-2004c6081292 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
7128d7dc-c48b-561b-9dc1-332ebd6f8386 | note | ○ Hand auger hole is required
678eef45-dccd-5662-bbeb-649e7bd08a6d | note | Acceptance / Conformance Criteria - Average Minimum SU:
18b19ca6-f802-59a2-a1c2-6e2c946906d7 | note | ○ > 60kPa
4b7bbe57-3deb-531a-845e-e85ce71528f6 | note | Single Test Min SU:
5591989e-ccb9-57f2-8283-37bd60c63d6a | note | ○ >50kPa
203b08e4-b1ba-54fa-8569-b907dfed1216 | note | ○ 2-3m deep
9a661b94-ce52-54bb-9c16-30878f41219c | note | Standard / Specification - PS 27.4.2 Appendix XVIII
18e84f2d-8df5-5dbb-85ba-09240079c672 | note | Verifying Document - Shear Vane Report
21651c8e-4a06-500e-aab8-c6f3b9e7c802 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
2026251d-10f4-5dd3-b1fd-2c6af2aab2fc | note | Verification Activity: Activity - I
281cf84b-6428-5a96-9420-bf6d8b636eb8 | note | Verification Activity: By - SE
d39692de-8397-4f5d-bc08-8c936372057d | checkpoint | 4.4 - Subgrade - Proof Roll
0165ae81-b2d8-5ab5-a6c4-c54814d056ff | note | Detail - Visual Inspection of Proof Roll
14aefd80-430b-58e9-afc1-2a584a12f9aa | note | Acceptance / Conformance Criteria - Displacement <15mm
15155540-a3b7-5630-89e1-116db94a7f95 | note | Standard / Specification - Appendix XVIII
5ca02a6f-b2ce-5a61-9009-fc9675a34ee2 | note | Verifying Document - Visual Observation
629cd62a-b0b0-5766-b3e5-bff2da5c59fc | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
d184036b-1471-5f15-b82f-9d2e4c53b98c | note | Verification Activity: Activity - I
de7a844f-9dca-5a51-b3f4-3aa2adfdc597 | note | Verification Activity: By - SE
058474da-ef41-4de7-be90-27c41c4b3420 | checkpoint | 4.5 - Hold point- QA Submission
b3f3516d-83e3-563b-9e10-6cb14bf7d542 | note | Detail - Submit all Subgrade lift QA before proceeding with next pavement layer
a9ad25f8-fa54-5285-be20-e19cf594dfc1 | note | Acceptance / Conformance Criteria - Engineers Approval
726b9164-f2e1-5197-8a2d-bb93ff3faf42 | note | Standard / Specification - Appendix V
cb3035aa-5c5a-5fd2-9596-5b5967838437 | note | Verifying Document - Conqa Siggnoff
fbe613d0-79ba-558d-902a-cc8588c5d7f7 | note | Testing Quantity Required (based from schedule qtys) - Once
02ed72a7-ca8c-5184-99bd-8166de2115a9 | note | Verification Activity: Activity - HP
3a2be46a-05af-5125-8c8a-a699c89ac59e | note | Verification Activity: By - ENG
e6594af9-c15b-4b24-b60f-1a8f5d8ee869 | signoff | AUTHORITY HOLDPOINT
7ad396be-042d-4a3e-9263-d770e2391690 | checkpoint | 4.6 - Subgrade Fill - CBR Testing
21a00723-2fb2-50ca-b3bf-8dcb249507e4 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
b04e9431-c4a4-544a-acf1-ced539b04a32 | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
081d3b94-16c7-5fc6-b751-6d35e40beee8 | note | Acceptance / Conformance Criteria - Min 4 blows / 100mm
ce1837c8-0254-56ba-a4c2-dcf235abaaa6 | note | Standard / Specification - Appendix XVIII
3fa755dc-e26f-5dcc-8557-a600dd869830 | note | Verifying Document - Scala Report
cdfe27d4-1633-5ca5-ab74-5d33cb8a203a | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
82ec694c-67bd-5203-9986-ec375730a3a2 | note | Verification Activity: Activity - HP
e4271938-c37e-58b4-86d2-797a178b8760 | note | Verification Activity: By - ENG
4ee3fa45-6469-4560-b5f7-cf5d525710cd | signoff | AUTHORITY HOLDPOINT
bebd4cab-5b56-4e99-b3e7-35e57796a4fe | checkpoint | 4.7 - Subgrade Fill- CBR Testing
587a72f1-914b-567a-8c6e-1917271d4184 | note | Detail - "NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
7b5d5afa-3e48-564a-86c5-8ba06d4b6bc8 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
bf663392-98e2-5a63-8699-5c4ef3652ec3 | note | ○ Hand auger hole is required
225d49cb-31d2-5781-a5ff-149f095ba609 | note | Acceptance / Conformance Criteria - Average minimum Su > 125kpa
38872e07-6052-51c5-ba43-6707c4373434 | note | ○ Single test minimum Su > 100kPa
3de35e85-1456-588e-b1e0-f24d1916afad | note | Standard / Specification - Appendix XVIII
5f25c0e9-7868-5219-bb19-2f1f5ee24754 | note | Verifying Document - Shear Vane Report
fb49c8ab-19f1-52e4-8a82-bd0d2262c852 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 test) per 100m3 of fill placed per area worked per day per lift
a057278a-7654-5b14-bb88-2275f0b0a105 | note | Verification Activity: Activity - HP
5644373f-61e6-502b-bd8d-8eb37c22f700 | note | Verification Activity: By - ENG
e98e45ab-9bd2-4139-b60a-939ef69ab93e | signoff | AUTHORITY HOLDPOINT
e3f3a54e-9433-4756-87c2-a544e8e32308 | checkpoint | 4.8 - Subgrade Fill - Bulk desnity, Dry density, Air voids
f11409e2-787b-518f-9d8d-66cc7757c143 | note | Detail - NZS4402:1986 - Test 5.1.3 sampling tube method for determination of the in-situ density
9da32f85-00bb-5068-bdca-654baf7c13fb | note | Acceptance / Conformance Criteria - Results from test
5808fde7-6d26-5dc7-a3e4-ce5c41ddc5d2 | note | Standard / Specification - Appendix XVIII
7ceb23a3-0801-538a-b553-82f7246cdc72 | note | Verifying Document - Report
e9a28fab-84da-50fc-af9c-a07bf2667b09 | note | Testing Quantity Required (based from schedule qtys) - 1 Test performed for every 10 NDM
49d5f2bc-2e92-505d-8fb3-7783f402abd2 | note | Verification Activity: Activity - HP
eb350068-3de0-5bdf-a314-ef886d961c7d | note | Verification Activity: By - ENG
97b3f14f-a1ba-42a2-b8fa-b9d3516da0eb | signoff | AUTHORITY HOLDPOINT
c2dd4dbc-db10-4d3c-9dd4-dfdf25bb7e54 | checkpoint | 4.9 - Subgrade Fill - Water content
c909e3c6-fd0c-5d1a-ba61-18dee6eea4b4 | note | Detail - NZS4402:1986 - Test 2.1 water content
26445333-b6ce-5c2f-9afa-58400f380084 | note | Acceptance / Conformance Criteria - Results from test
6881ae7e-11db-5dc6-9eb3-ca89c241aba4 | note | Standard / Specification - Appendix XVIII
029be071-a620-55b7-aea3-181b7a8fe2f4 | note | Verifying Document - Report
5330455c-9f1b-55c9-b240-1379c1ada3d4 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 test) per 200m3 of fill placed per area worked per day per lift
ac098ebb-5f82-59ee-98cb-66fb6a64bb8f | note | Verification Activity: Activity - HP
53214582-0a93-5e87-a9bf-9f33ff4131ca | note | Verification Activity: By - ENG
fbe12110-72e4-47e2-940e-68235d14e0f3 | signoff | AUTHORITY HOLDPOINT
b09ce22f-65ef-46e5-af0b-71d024162162 | checkpoint | 4.10 - Subgrade Fill - Insitu density insitu compacted dry density insitu water content
42ca1660-980b-508d-8332-4c39ed033f31 | note | Detail - NZS4407:2015 – test 4.3 nuclear moisture density gauge (ndm), direct transmission mode
c6ed354f-9b1f-5ff5-9b4f-ddf6e901266d | note | Acceptance / Conformance Criteria - Average maximum air voids < 7%
643ef126-71d8-5328-ae4c-d7be4a219b94 | note | ○ Single test maximum air voids < 6%
26ca110c-3526-516f-98b8-b163e82436f8 | note | Standard / Specification - Appendix XVIII
4a829b2c-99de-5ed0-8d99-b6708739deaa | note | Verifying Document - Report
2e62deb7-108f-5c35-9060-c3c7d084de2e | note | Testing Quantity Required (based from schedule qtys) - 1 Set (5 Test) per200m3
e3332987-e014-5d10-a5dd-f495a1b86805 | note | Verification Activity: Activity - HP
cbf41767-53d9-5e0f-9ef2-16045f615dc5 | note | Verification Activity: By - ENG
ef1544ea-7005-4657-9d09-e9c2d579d4ea | signoff | AUTHORITY HOLDPOINT
cc702a6e-cfff-422e-b0d9-0671c55bcfa3 | checkpoint | 4.11 - Subgrade Fill (Pumice sand) - Compaction
b3ab163d-7589-5842-af08-6649b0614910 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
52543440-5a8a-5bfb-9172-75ed2808f274 | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
19d1bbb5-5a7a-5a21-ad3e-e50d71f53186 | note | Acceptance / Conformance Criteria - Scala blows >5
bd2246c1-0ab6-5602-95cf-c40a6b1447e8 | note | Standard / Specification - PS16.5.12
15a5efe3-5f83-5ab7-a420-ed2eaf2e55fd | note | Verifying Document - Report
d0d715ec-1752-511c-ba85-2cce21aa793a | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
586f2f0c-06ca-5436-b0b2-0c1429c3092e | note | Verification Activity: Activity - HP
c6439596-3cc6-5b08-9c7c-87418b900795 | note | Verification Activity: By - ENG
ef1166f0-7135-4c3f-9ebd-d4af04b69d36 | signoff | AUTHORITY HOLDPOINT
c1f1004c-3973-4f47-8b21-1dc0b574fb99 | checkpoint | 4.12 - Subgrade Fill (Pumice sand) - Bulk density, Dry density, Air voids
6af015b5-48d5-514e-87d2-806075b9ee2c | note | Detail - NZS4402:1986 - Test 5.1.3 sampling tube method for determination of the in-situ density
65797605-bf5a-5e4c-84d6-74475b5150f9 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
3ff294f6-3c2c-58ce-ab84-231b2cb8d7d3 | note | Standard / Specification - PS16.5.13
d175bd03-e5d7-538a-bcde-41d87e12203f | note | Verifying Document - Report
414cded8-d2af-514c-9bf6-42f9a1e128bb | note | Testing Quantity Required (based from schedule qtys) - 1 Test performed for every 10 NDM
a9c54239-b262-5554-82bf-cd2530b666c1 | note | Verification Activity: Activity - HP
c20820f3-7c79-59e5-bcfd-df01bcee4e08 | note | Verification Activity: By - ENG
87b747d1-6437-48a5-a980-ae21ce37fdf6 | signoff | AUTHORITY HOLDPOINT
06dcc0ff-68ae-4cec-a4eb-0d9f2c9d12be | checkpoint | 4.13 - HOLD POINT- QA Submission
c1b43cb1-7b56-5381-be2f-40f44ac05721 | note | Detail - Submit all Subgrade lift QA before proceeding with next fill layer
c700286f-0f4a-50fc-941e-94848adfd010 | note | Acceptance / Conformance Criteria - Engineers Approval
be509d37-ec62-57e9-a07b-616441af2087 | note | Standard / Specification - Appendix V
7e32c33a-68f6-5f2c-a54d-abcdb4e9c8ee | note | Verifying Document - Conqa Siggnoff
bfa0e95a-6b37-5258-b2f6-ac30df124c8e | note | Testing Quantity Required (based from schedule qtys) - Once
cecf9bf3-6e5e-5243-84f0-6be30d7a3709 | note | Verification Activity: Activity - HP
ac75b34b-7ea6-533a-a8c4-4603948365d6 | note | Verification Activity: By - ENG
ccb65370-0006-42e4-be3f-39825e499a7d | signoff | AUTHORITY HOLDPOINT
ced08b4f-cd8f-432a-9738-353ae2b2b2da | checkpoint | 4.14 - GEOTEXTILE FABRIC - Placement of Geotextile Fabric
ed24797d-ba89-51f5-8c03-ce8d387dfac0 | note | Detail - Place Geotextile Fabric Strength Class D across pavement area, with 500mm overlaps
9339e68c-ff0a-55ef-bb63-ab7b778ab24d | note | Acceptance / Conformance Criteria - Visual inspection
77af990c-2d92-5267-9d84-1ff566534246 | note | Standard / Specification - 232735.02-WSP-DR-STW 0302
8f142acf-3a6d-50af-b31b-0adcdbe0f609 | note | Verifying Document - Visual Inspection and photos
4eb28fcb-f932-5cc1-beb4-49b221c587e1 | note | Testing Quantity Required (based from schedule qtys) - During construction
723ce4dd-8bec-5dc9-8812-e95c7404994b | note | Verification Activity: Activity - WP
7f4474b3-51fb-5f45-8187-4b22c4dc914d | note | Verification Activity: By - ENG
47c01096-cb49-4275-b342-79f101b1b36c | checkpoint | 4.15 - SUBBASE (TCC AP65-2) - 3m Straight Edge
d12fe267-e3d5-5193-aeca-d926fa50fada | note | Detail - Formation check to ensure surface is smooth
f9339258-9ab0-5ba5-ba6f-e122fea00950 | note | Acceptance / Conformance Criteria - +/- 15mm
5712a1f7-9e23-5b60-b97d-75f5607b250a | note | Standard / Specification - PS 27.4.1
dae9e02b-7534-5599-bcb7-89e9b0db91b1 | note | Verifying Document - Check Sheet
3c74d018-cba7-500e-876b-14e3915942ae | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres
a65ff8ad-659a-50d5-9b98-b590f1a8961d | note | ○ 1 each lane
a7815511-29f3-5d50-9e41-8f8d875a0a28 | note | Verification Activity: Activity - I
070be900-fca1-5793-aaa4-d4003e7bc1ba | note | Verification Activity: By - SE
76535c77-9a3f-4521-a6f7-b6207311f4d6 | checkpoint | 4.16 - SUBBASE (TCC AP65-2) - Stringlines or equivalent
047ba95f-26ff-59a1-9138-a49225a483a3 | note | Detail - Stringlines or equivalent to check finished height of surface
346f3dab-ee2e-57c6-834a-3483b14987b2 | note | Acceptance / Conformance Criteria - String lines - or equivalent are 150mm +5mm/-25mm
6bd4c9fb-b257-5f6e-befe-1303d5ec8788 | note | Standard / Specification - TNZ B/02:2005 5.1 232735.02-WSP-DR-STW 0303
367255b2-770a-5fe5-8f4c-99947c7890e0 | note | Verifying Document - Check Sheet
27562afe-05ab-5b3e-9447-2803c2114699 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
48043dad-8a76-5965-9584-e6b9962e0fca | note | ○ 1 set = 5 tests
5457e91b-b606-5c7b-a458-546f56b308c6 | note | Verification Activity: Activity - I
c40ed372-266b-5904-8d55-d7b92a7b4283 | note | Verification Activity: By - SE
fa0c1868-3ea8-4191-9cb1-cbc72a400f50 | checkpoint | 4.17 - SUBBASE (TCC AP65-2) - Compaction - NDM
efd517ee-8172-55f6-9b2b-6ae410b19bc3 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
299e0d38-075c-5b46-8fb9-c75b9ab0ae28 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
f8c72b57-9c6b-541f-91e1-1429555593f3 | note | ○ Min >92% of MDD
c23e2250-a0bb-5905-b153-d7a498049c6d | note | Standard / Specification - TNZ B/02:2005 7.5
22560594-77ef-5c58-bc4e-9e4c184f6dd7 | note | Verifying Document - IANZ Accredited Report
3e17419b-9d7f-5591-8d36-000cb3848288 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
bc978623-f13d-55bb-bee2-f6c2d17d5855 | note | Verification Activity: Activity - I
b9c4a62e-f132-5c87-9ad1-e91707832ed9 | note | Verification Activity: By - SE
3f2aa7e5-8617-4bbc-995f-cfba65f1911b | checkpoint | 4.18 - HOLD POINT - QA Submission
22268736-3d77-5546-b6d8-9fcb99a7ddc7 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
d3398257-3c15-506d-86ea-d01e8adf246d | note | Acceptance / Conformance Criteria - Engineers Approval
df42020d-d556-56a0-b403-973915732c62 | note | Standard / Specification - Appendix V
7aa2f326-1ead-538b-876d-a2b1411b8bd9 | note | Verifying Document - All test reports
39d7dd77-ced8-53ad-ae01-737677997e8f | note | ○ Material Test Results
f72fb6a9-ebcf-5a49-8050-5b939fb9b16e | note | ○ Laboratory MDD
7146b95a-4c94-54d5-afe2-1de8780e2fa4 | note | ○ NDM results
9856e82e-9d23-590f-abaa-48941144f260 | note | Testing Quantity Required (based from schedule qtys) - Once
3a55768e-c754-5c4f-b405-89e97b13c5d8 | note | Verification Activity: Activity - HP
e36b888d-ad24-5f63-aa96-7cab62a746d7 | note | Verification Activity: By - ENG
cb8caff1-a0cb-4c60-89d4-09324571f12f | signoff | AUTHORITY HOLDPOINT
f85d3bc0-78ab-4a63-8b2a-5ec65c92eff3 | section | SECTION 5 - CONSTRUCTION - EARTHWORKS
87ffe3e3-c9e6-4d5a-aecf-f5e2196786bd | checkpoint | 5.1 - Subgrade Level Confirmation
5a7b3215-fd65-5321-967e-c92262b097b7 | note | Detail - Confirm subgrade is min 500mm below excisting ground level.
26a98590-5d1e-555b-a06f-bbe21091cad0 | note | Acceptance / Conformance Criteria - String lines - or equivalent are 300mm +0mm/-30mm
ca1ce6e8-7f9a-59dd-ba7d-dc5b42f57a55 | note | ○ Tolerances width -20mm +100mm
039951cc-16ec-51b9-9b10-48ac20429d38 | note | Standard / Specification - PS 21.5.15 e)
9f8e6034-6223-55b6-ae1a-a303fdd841ba | note | Verifying Document - Survey as-builts
f4cfdcc6-36ea-5c5a-b875-208d245f88cf | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage on all major contours
b522257e-1632-5f71-a372-62a1f6c9b84b | note | Verification Activity: Activity - I
3578842a-08a1-5d14-9aea-db454b84608e | note | Verification Activity: By - SV
56f7053b-a81a-4af7-97a8-3f025faeafc3 | checkpoint | 5.2 - Subgrade CBR Testing
00b10059-a83a-5334-a490-e9048c2307e8 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
3943d26f-ae2e-533a-93b8-bff8f907c087 | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
df3e9a8d-e3b6-519d-bb14-b9c61e72f995 | note | Acceptance / Conformance Criteria - CBR >7
5a386faf-8bad-5a98-ab7a-3f8558585142 | note | ○ Min 3 blows / 100mm
4432d378-2534-5989-a198-f1d82554ddf0 | note | Standard / Specification - PS 27.4.2 Appendix XVIII
c3b99ae2-6c20-5998-819f-e310bc22f81e | note | Verifying Document - Scala Report
50eaaf08-1881-58ac-890c-de35a9cd2604 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
43dac090-f396-5ab6-b350-229de166ae5f | note | Verification Activity: Activity - I
652db790-ee38-55d3-ba1e-1c20ebaa922d | note | Verification Activity: By - SE
51887923-7eab-4fb7-932d-d6e94d1fd1ef | checkpoint | 5.3 - Subgrade CBR Testing
25c20b71-fe8e-5b49-9727-37a9b0345b7e | note | Detail - NZ Geotechnical Society 2001 - Guideline for Hand Held Shear Vane Test
d5469566-d186-5c19-8332-dd101a907d0d | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
be45506f-8f78-58dc-93b1-5e52692a2d16 | note | ○ Hand auger hole is required
12693360-dcd3-5fbc-9148-ac93bb13ffea | note | Acceptance / Conformance Criteria - Average Minimum SU:
7d2060db-4924-59c2-9477-393dbbbff1f8 | note | ○ > 60kPa
7c17a7b6-7c9c-53f9-9b15-6ae2eebd9869 | note | Single Test Min SU:
fb14f8ae-e19e-53da-8471-24dda7661513 | note | ○ >50kPa
6490093b-0b07-5ea5-b657-db1e737e16ad | note | ○ 2-3m deep
90ad133c-dd7e-5b6f-97d2-dc87facd35cd | note | Standard / Specification - PS 27.4.2 Appendix XVIII
c00e1305-f3b5-5871-9e83-63617463679b | note | Verifying Document - Shear Vane Report
9c1bfba4-5b0a-55ad-95ad-fef64a51fe22 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
1d192f42-e423-51f7-8561-fea714131c85 | note | Verification Activity: Activity - I
490f3840-ad7d-5fcb-819c-3ba691d778cd | note | Verification Activity: By - SE
069225ad-b59e-4400-9647-399b521ef7ad | checkpoint | 5.4 - Subgrade Proof Roll
5bb0ffd5-1897-5a80-8314-7c75e9e39e50 | note | Detail - Visual Inspection of Proof Roll
00b2136d-9ed5-50d4-8ce1-84dcb97c9086 | note | Acceptance / Conformance Criteria - Displacement <15mm
be3f79c7-9d26-5738-b6c1-623622a7df63 | note | Standard / Specification - Appendix XVIII
ad49889a-bdc0-5f1a-8d5e-a4f1c3ef534a | note | Verifying Document - Visual Observation
c8ca8fbd-b3a5-584d-91fb-d6bc4a307165 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
5bb0b99e-81cb-599b-8704-7dc4217647ca | note | Verification Activity: Activity - I
6a677447-40a0-5d95-9541-08f571b14ae5 | note | Verification Activity: By - SE
864fe1dc-bb10-47d5-8ede-a4e135c2bc03 | checkpoint | 5.5 - FILLING A2 COHESIVE MATERIAL - Subgrade CBR Testing
528df404-1e6b-5d55-b271-567b5f179f0f | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
da066ac7-adaf-5378-ac35-be906340d122 | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
be475ec4-80b6-5812-9c41-439363205459 | note | Acceptance / Conformance Criteria - Min 2 blows / 100mm
3598ce84-2bfe-5ca8-99c7-2b3263e759da | note | Standard / Specification - Appendix XVIII
01aa8616-75ad-51dd-9e9b-08915b7efe3f | note | Verifying Document - Scala Report
fe6b9957-d2a1-57a1-8d74-55bd1f9a0c0e | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
5c1807ba-1d09-5b26-b7d5-bb6b42a2f98f | note | Verification Activity: Activity - HP
76166400-90af-5d9a-ad3a-5f3cdbebaaa2 | note | Verification Activity: By - ENG
8c2ff948-689e-4b6a-9769-38b6ca5c8504 | signoff | AUTHORITY HOLDPOINT
dc156f82-e922-4c09-9c09-1e137e40c4f4 | checkpoint | 5.6 - FILLING A2 COHESIVE MATERIAL - Subgrade CBR Testing
898ce6de-2110-59bd-ad07-7d328c3c8061 | note | Detail - NZ Geotechnical Society 2001 - Guideline for Hand Held Shear Vane Test
f9dce0a7-e5f4-517f-9d62-a9df239e32f7 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
11619dff-9b9f-564d-951f-f07592d8650e | note | ○ Hand auger hole is required
05a6617f-aefe-5900-9bb4-b03e91ea2d3e | note | Acceptance / Conformance Criteria - Average minimum Su > 80kPa
8184d9e0-6b5e-5a49-93e7-b01003f2989a | note | ○ Single test minimum Su > 60kPa
7448695c-5f4e-58f5-8237-7f0e85c3b8bf | note | Standard / Specification - Appendix XVIII
e62450a6-11b6-53fa-a7db-8466eaf67c61 | note | Verifying Document - Shear Vane Report
821231c5-4bc1-5848-ab6f-b5e5336786ea | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 test) per 500m3 of fill placed per area worked per day per lift
bff72eb3-e4f6-5c0f-8902-b2fdb6b3f5c2 | note | Verification Activity: Activity - HP
40288777-3ecf-547f-bd82-e34c5e028a46 | note | Verification Activity: By - ENG
0704df9c-65e6-42c4-9c0f-56991b0d5a3c | signoff | AUTHORITY HOLDPOINT
35c6f4ba-fca6-469c-b2a3-9ccbad6f53ff | checkpoint | 5.7 - FILLING A2 COHESIVE MATERIAL - Compaction - Clegg Hammer
2283e7d9-4854-5329-ae44-3bfa5b0b6cf0 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
9390be8e-f289-58fc-a35c-a639e8327eb9 | note | Acceptance / Conformance Criteria - Non-Structural Fill
48ccd62b-91ea-560c-86fc-7b9740701a5e | note | ○ Min CIV 10
6c613b76-cefb-5210-b67a-bdedd3c6d724 | note | ○ Max CIV 12
fed1fa57-3bad-570e-97dd-4c0b2e484f5e | note | Standard / Specification - Appendix XVIII
6065c618-eff5-559c-8ca7-f4de79cfaef9 | note | Verifying Document - Clegg Hammer Report
8405f261-44a3-51ac-8906-1167083d562f | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
888d6450-bfdd-500b-9eb7-5285621a59c9 | note | Verification Activity: Activity - HP
33900360-5dc2-52af-a17f-fd96f91e845c | note | Verification Activity: By - ENG
496be9f6-a6ff-44b0-b435-6289d8feaae4 | signoff | AUTHORITY HOLDPOINT
189e743f-6d4d-4889-a742-3d786c69db59 | checkpoint | 5.8 - FILLING A2 COHESIVE MATERIAL - Bulk density, Dry density, Air voids
3ec84a60-fe12-5f87-bf80-88479246d986 | note | Detail - NZS4402:1986 - Test 5.1.3 sampling tube method for determination of the in-situ density
061db7fb-f60a-5cb7-afe8-4a2878495667 | note | Acceptance / Conformance Criteria - Results from test
ca5ba9d8-6b4f-5583-a563-4b17071bea87 | note | Standard / Specification - Appendix XVIII
fdf09337-8b94-5d9f-bb65-57e25f14fd32 | note | Verifying Document - Report
e6b5034f-295e-58e2-bc79-f147a1b3a1a3 | note | Testing Quantity Required (based from schedule qtys) - 1 Test performed for every 10 NDM
2fe6db72-ec87-5d17-a3d9-ebfe7987fa9b | note | Verification Activity: Activity - HP
82651660-ef70-5125-a07b-d0e83acc1213 | note | Verification Activity: By - ENG
dd726103-7bb8-48d8-b711-180de27b16ab | signoff | AUTHORITY HOLDPOINT
73ad8399-4a07-4ca2-a6a8-fe96dab89f89 | checkpoint | 5.9 - FILLING A2 COHESIVE MATERIAL - Water content
1a513dd2-0e37-5833-b384-90fde2c472c4 | note | Detail - NZS4402:1986 - Test 2.1 water content
194cc372-e7a1-5126-a483-f7dc4eeb4fa0 | note | Acceptance / Conformance Criteria - Results from test
7d8adea5-619d-565a-950d-0b7b6069a198 | note | Standard / Specification - Appendix XVIII
0dc884ee-3998-5835-aa29-fc0e35891921 | note | Verifying Document - Report
e8da776d-3290-54dd-9052-4641e758b3a6 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 test) per 200m3 of fill placed per area worked per day per lift
91103ae0-65e2-5b96-8b37-fe0e4c29fe1c | note | Verification Activity: Activity - HP
74d230f8-49c3-530b-8bcd-26c5e8faa450 | note | Verification Activity: By - ENG
e1f145ce-dbe7-4b16-979a-148b15cded18 | signoff | AUTHORITY HOLDPOINT
90db7415-65b8-41e0-9563-b3ac9920b228 | checkpoint | 5.10 - FILLING A2 COHESIVE MATERIAL - Insitu density insitu compacted dry density insitu water content
497d3699-cdb0-5fe1-9891-2a3a67701b02 | note | Detail - NZS4407:2015 – test 4.3 nuclear moisture density gauge (ndm), direct transmission mode
f7c2ec84-efc5-5f87-9930-b87c48e55f58 | note | Acceptance / Conformance Criteria - Average maximum air voids < 8%
63836e6f-c885-5faf-add3-d12039795433 | note | ○ Single test maximum air voids < 10%
6fa514db-19ba-580c-b200-dd0b8f89b938 | note | Standard / Specification - Appendix XVIII
885dfd93-2468-5cd1-a38a-979e0b5eaf92 | note | Verifying Document - Report
65662644-42b9-5968-adfe-ced1fab2775a | note | Testing Quantity Required (based from schedule qtys) - 1 Set (5 Test) per200m3
8298cffb-7e40-5af8-bfbd-89d292d4fd6f | note | Verification Activity: Activity - HP
0c4ffa59-c530-5d20-b862-c01df472d54e | note | Verification Activity: By - ENG
6d84ca6a-9cf4-4205-b89e-98124dd13819 | signoff | AUTHORITY HOLDPOINT
905db57a-9dc6-4d7d-8875-977173b988c0 | checkpoint | 5.11 - FILLING A2 COHESIVE MATERIAL - Final Level Confirmation
987e62b2-5b5d-5fae-a749-9c314542976a | note | Detail - Confirm subgrade is min 300mm below final level for topsoil
58413cae-78f6-5cef-80e2-cfd9137893bd | note | Acceptance / Conformance Criteria - String lines - or equivalent are 300mm +0mm/-30mm
8d17662d-8ca4-5e88-ba02-63a2b0b83146 | note | ○ Tolerances width -20mm +100mm
9d6ae931-e357-5708-b915-9432b9448352 | note | Standard / Specification - PS 21.5.15 e)
8ca168d7-a299-5350-aa79-30820b2868c8 | note | Verifying Document - Survey as-builts
e5147ef9-d290-54ec-9aa0-acf6a2889ba7 | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage on all major contours
06a31a8d-86c0-5fcc-a265-27338fccfe01 | note | Verification Activity: Activity - I
8b9629d7-8ff5-5ad2-a969-6e9de521d989 | note | Verification Activity: By - SV
18e0292d-a78f-4322-bd29-b66bfd8cf4a4 | checkpoint | 5.12 - SUBGRADE FILL (Pumice sand) - Compaction
f8f7d90f-0216-5d3f-aab3-145d6d41b958 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
824d870a-c261-562f-b8be-35aadaa03ccf | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
b3412136-2077-5f3d-956a-cfd4502468b9 | note | Acceptance / Conformance Criteria - Scala blows >5
a5fbd843-c95a-5b41-830e-5dc66776e6a9 | note | Standard / Specification - PS16.5.12
27a842d3-a547-51d1-a5d6-55af78c076c0 | note | Verifying Document - Report
27f4f824-e6f6-5499-8f65-08543bfce408 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
1c660105-b57d-524c-b727-5b3a49bfcbf9 | note | Verification Activity: Activity - HP
dae9f1c8-2427-5bc8-a80c-8569bbbe8932 | note | Verification Activity: By - ENG
42816eae-6186-41b0-91ad-2289b16c03ba | signoff | AUTHORITY HOLDPOINT
5ad0f034-228f-4cf1-a72b-4a9c20c2036a | checkpoint | 5.13 - SUBGRADE FILL (Pumice sand) - Bulk density, Dry density, Air voids
04c76140-1681-542e-8414-a789d27d526e | note | Detail - NZS4402:1986 - Test 5.1.3 sampling tube method for determination of the in-situ density
35f32050-e667-52b3-aae3-e4094776cac5 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
747032f5-6ff7-50c0-884b-b714e26a8537 | note | Standard / Specification - PS16.5.12
a5f56d7f-89f2-5666-b5f4-d32b4dc71e61 | note | Verifying Document - Report
0954a8ef-9768-5343-a89f-a5e5ba304371 | note | Testing Quantity Required (based from schedule qtys) - 1 Test performed for every 10 NDM
6774aef1-bdf0-552d-8877-7d06988532f5 | note | Verification Activity: Activity - HP
85918318-8c00-5a6a-8bd1-948cd59df86c | note | Verification Activity: By - ENG
bb864c83-8a09-4eee-8613-8c0a76d81c2b | signoff | AUTHORITY HOLDPOINT
8dc34cd8-182f-469f-948f-c5653ffe32b7 | checkpoint | 5.14 - HOLD POINT - QA Submission
b5ec8aea-2181-5756-8763-0dbb14d15d34 | note | Detail - Submit all Subgrade QA before proceeding with next pavement layer
c05d6d08-a827-5f77-a84c-eacc547ada84 | note | Acceptance / Conformance Criteria - Engineers Approval
664609ec-a22c-5113-8342-55f95d44d112 | note | Standard / Specification - Appendix V
4bcb92a5-4de6-583f-9d8a-9045eee4150a | note | Verifying Document - Conqa Siggnoff
ed8556b5-9fe4-5800-90bf-dd3bcfda8305 | note | Testing Quantity Required (based from schedule qtys) - Once
391478be-09e4-5d91-b510-4999d7d1722b | note | Verification Activity: Activity - HP
3955fd85-0f66-5420-92bb-cbb5a2850e10 | note | Verification Activity: By - ENG
10a1234c-1133-45ed-ab25-92f65e820602 | signoff | AUTHORITY HOLDPOINT
6a744d67-beb5-45f9-8d75-6322e90d863e | section | SECTION 6 – AS-BUILTS
d6672642-a2de-4561-8e27-d124869a8270 | checkpoint | 6.1 - As-Builts
c86345b7-6fe3-5417-8dd9-16c3f00858ac | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
c5da21c2-0188-55b3-9f2f-c96e29f17132 | note | Acceptance / Conformance Criteria -
cf1816f2-3e3e-5be2-802b-a997af10e744 | note | Standard / Specification - PS 16.7.6
6ec2ffd0-461e-5c89-8006-c65c1cc6f4f2 | note | Verifying Document - Survey Records/ Redpen markups
f7c522f1-a332-5672-9cfc-e0b22b099b7f | note | Testing Quantity Required (based from schedule qtys) - Post Earthworks
3337891a-42db-5181-9500-8438a58c2e80 | note | Verification Activity: Activity - D
a8f629f2-9883-58f0-8cf1-6d645c769d2e | note | Verification Activity: By - SV
6c47af1e-256c-4dfb-b142-c2298098d64f | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
63a434cb-7c21-5184-88ad-f86b0f0ad49b | textbox | Contractor's Rep Name:
48180150-74a1-5bc2-bde4-f583ff2566c0 | textbox | Engineer's Rep. Name:
bc71f46a-bd94-55db-a941-79e261649ee3 | date | Date:
12b7b2f8-a8c5-4dd8-8345-a2ac1d30e6e7 | signoff | Add Signature
6696c6cf-58c9-4e6c-9e4f-2e23ef3198af | checklist | DN1210-SP2-021 ITP AC14 Surfacing Rev 0 | itp | DN1210-SP2-021 ITP AC14 Surfacing
aaf25a2d-94d3-4e09-8045-744fa6f2be60 | section | 1.0. Pre-Commencement Activities
e508cb0a-631e-4913-8930-e0e23a29f279 | checkpoint | 1.1 - Approved JMF for Asphalt Base or Wearing Course
3eb3869b-a113-5e5c-ac42-4c75514865cb | note | Detail of Activity / Test - As Per DN1210-WSP-GCO-0160
16f52a33-eb71-5638-bcd5-116f1ae34db8 | note | Action (Hold, Monitor, Witness) - H
8b1d1886-b026-5d40-a5a9-e6b4f718f0d0 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
af06acb3-9f5a-588e-aadc-10671f6094e2 | note | Inspection / Test method - Confirm requirements are followed
13137efe-79ac-52cb-b611-ce905997e1b4 | note | Acceptance Criteria - JMF Validated in accordance with NZTA M/10:2020
dae8b348-0d1b-586d-9d1c-75f0841e3843 | note | Record documents (QCP - Quality Control Portal) - Mix Design Report
f23846e4-fe2e-5ca2-8479-cc14f9c9f0de | note | Responsibility - Paving Contractor
02be02d0-4ab7-56a2-a785-c2885529514b | note | Project Specific Notes / Instructions - JMF expiry date and validation details in here
67737ebf-b570-5b47-ada7-1aed2de3e4fa | note | Designer - A
f18cce55-30a5-5736-8daa-261657f38c99 | note | Eng. Rep / NZTA - I
f223e95e-e415-5e7c-84bc-b611df6db385 | note | Contractor - R
33b09777-2df9-4b07-9c30-946a31df8afd | signoff | AUTHORITY HOLDPOINT
06426129-d4ba-495f-a0e2-1c7ad125eec6 | checkpoint | 1.2 - Site Conditions
69b1feed-d590-5afa-8d48-72071035e508 | note | Detail of Activity / Test - Weather suitable, Site extents marked, surface suitable for paving (Depths/milling/cleanup complete etc), Environmental Controls in place
865478f4-50d6-52e9-be85-ec9558d9865c | note | Action (Hold, Monitor, Witness) - H
9af67ebf-0e9e-5920-b25b-378d767bd4b2 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
f854f963-4778-580f-ac29-edce14b8b1cc | note | Inspection / Test method - Confirm requirements are followed
bdd823d0-d3e8-5a52-a88f-8514a58f8ade | note | Acceptance Criteria - Weather conditions and Site is suitable for paving
cec1361c-d828-5849-ae1e-922ff7c59468 | note | Record documents (QCP - Quality Control Portal) - Site Diary
1cab5e47-bb22-5586-b99f-cdbdb531894b | note | Responsibility - Paving Contractor
927af425-54a0-5a1e-8e68-457429159ada | note | Eng. Rep / NZTA - I
ee4d628b-5149-5690-b692-43ac23a6b031 | note | Contractor - R
fc91bc91-2ed4-4230-b5bc-2db0ad3d599e | signoff | AUTHORITY HOLDPOINT
e140ec78-99a2-4e8c-b744-d6106e5f59df | checkpoint | 1.3 - Traffic Loops
8d9b4e27-c495-5a87-aa0f-118e5f35a414 | note | Detail of Activity / Test - Communication with affected parties
15350a23-bc91-5ba9-a54b-d7742bc1ed90 | note | Action (Hold, Monitor, Witness) - H
c3cb611f-4c83-5541-a4c9-5c944adacb30 | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 7 days Before Works commence
b70332d8-6cc5-5af3-aad0-9e5f4b435656 | note | Inspection / Test method - Visual
64987d94-bbba-5ed0-bc30-056de4ce8547 | note | Acceptance Criteria - Notify RC at least 7 days before surfacing is programmed
35241fc9-4df8-5b61-a0d8-0cab963254da | note | Record documents (QCP - Quality Control Portal) - Communication
7024c751-ef8d-5076-a333-f8314e38e70d | note | Responsibility - Paving Contractor
114e8bfb-037f-5120-b708-70b249e84676 | note | Project Specific Notes / Instructions - only required where existing traffic loops are present
5838a336-1833-5ce6-9be9-9e1bb3509108 | note | Eng. Rep / NZTA - A
b98c6624-4a1e-55ea-8e81-c8e5ff57ac42 | note | Contractor - R
e49ab6d8-dd47-482a-9dc3-f4dbd74902f5 | signoff | AUTHORITY HOLDPOINT
2671b479-f408-4383-9f60-0c354a515cd2 | checkpoint | 1.4 - Paving Plan
42458cbc-af02-5f42-802b-5db44e9fcf8c | note | Detail of Activity / Test - Paving Plan to be completed
dbbfa71f-ef8f-50e5-a35b-04c8b7d249fb | note | Action (Hold, Monitor, Witness) - H
eab23d45-07c7-5e47-bed6-2e420298288a | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
3b9cb944-060d-55a7-907d-acef5ccb5480 | note | Inspection / Test method - NZTA M10: 2020 Clause 9.5.1
a772c59d-7cd9-5d4e-9c06-978ca16fde05 | note | Acceptance Criteria - Paving Plan to be completed for each shift with dimensions, location and type of (hot/cold) joints, areas and tonneages
f75dedb4-5d84-53ee-9226-1c163bd506ee | note | Record documents (QCP - Quality Control Portal) - String Sheet
1d8a25f5-448d-578f-8482-b6afdadabe18 | note | Responsibility - Paving Contractor
70a318e2-e771-5f88-b079-280be20418bd | note | Eng. Rep / NZTA - I
71d07bdc-9677-5794-8bd8-0f59fc3b574e | note | Contractor - R
73a6c226-6119-4420-9a5f-b09358a26458 | signoff | AUTHORITY HOLDPOINT
50659d73-5e46-4786-af92-590951281437 | section | 2.0. MANUFACTURE OF ASPHALT
3aba1376-2454-4b38-b0e1-61679d1ea641 | checkpoint | 2.1 - Temperatures
f1999345-24f8-5286-94c5-db430c9a7769 | note | Detail of Activity / Test - Mixing of aggregates and bitumen
8be08a54-1112-5a07-8db9-6698a1304da4 | note | Action (Hold, Monitor, Witness) - M
b9a57955-2e52-50be-8be7-ad671c8153d4 | note | Minimum Test Frequency (Lot = 1 day’s production) - Constant monitoring of temperature by calibrated euipment
361de95d-d1d1-521e-b300-763ffc96df9f | note | Inspection / Test method - Plant temperature probes
8bcf2dca-6e8e-5ab6-8b40-3ef0740437ac | note | Acceptance Criteria - PNZTA M10: 2020 states max. 185 deg.C
90b8afa7-d548-5433-8b49-beac5cf529a4 | note | Record documents (QCP - Quality Control Portal) - Plant site diary
1481da04-5b14-529c-87d7-7c9d9d2a39a8 | note | Responsibility - Asphalt Manufacturer
40d11778-bc18-53ad-8681-56222d858ec3 | note | Designer - I
e91ae6d8-cdec-520c-842b-1554d2885e73 | note | Eng. Rep / NZTA - I
7156aa62-3475-552e-aa80-e56690da0d1c | note | Contractor - R
292983da-0a65-4d14-9d69-057e5b74aa91 | checkpoint | 2.2 - Production Asphalt
737426fd-086d-55e1-94b6-d677a2d432da | note | Detail of Activity / Test - Particle Size Distribution
e11d11ba-7d59-580d-9107-afd107336ca5 | note | Action (Hold, Monitor, Witness) - M
c0904e07-402c-5798-8cbf-ffc8c649a9fe | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
fb14382d-4879-5047-b5a3-e051c17ddcee | note | Inspection / Test method - NZS 4407 Test 3.8.1
cbbaa973-281f-59b8-b23e-e21324bc2a4d | note | Acceptance Criteria - NZTA M10: 2020
71430297-c9a8-5f48-8140-c7ff9ce3d1d1 | note | ○ Refer to Table 5.3 (Refer to CWP for image)
bd059007-7abf-5b66-8c50-d2588e918b14 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
6ff4b39a-4740-57f3-b927-134463d11b62 | note | Responsibility - Asphalt Manufacturer
be142a87-7f38-5f23-8587-8fe6e38462d3 | note | Designer - I
8ddc9a2e-893c-509c-a90a-9ced5d850de7 | note | Eng. Rep / NZTA - I
c8d2a7b9-5fe0-5403-a726-2f1ec2f6ef95 | note | Contractor - R
ced6b4fd-e0b0-45cf-84c4-22b6f6ab44cc | checkpoint | 2.3 - Production Asphalt
ad5fe61f-99a3-5a5a-8de1-a119866599fb | note | Detail of Activity / Test - Binder Content
ae6290a4-00ac-5e06-8959-2d9005aa0692 | note | Action (Hold, Monitor, Witness) - M
9bb7baf1-94c8-5aa9-8f0c-5b9032f97447 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
bad82e17-d541-57af-80f2-287eef51078a | note | Acceptance Criteria - NZTA M10: 2020
61cbd5f8-af53-582f-a4ce-560fde37dd9d | note | ○ Individual Test Result: ± 0.5
89bbdddb-fa0c-55b6-bc92-0d3947532f87 | note | ○ Mean of Three Test Results: ± 0.3
ed556c7f-46fc-5439-8f03-3bfd74b39cef | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
de2f724c-0628-5f86-8e6e-28285c479f59 | note | Responsibility - Asphalt Manufacturer
a40cc783-115c-5d11-8750-ede149a093fe | note | Designer - I
d86b7ff5-0b34-533d-b928-42775fd2fe35 | note | Eng. Rep / NZTA - I
f3b66c94-8690-5885-8d7f-1a4006bd2da0 | note | Contractor - R
613dc699-461e-4df0-baf1-f706e14b7b09 | checkpoint | 2.4 - Production Asphalt
21c3c358-a1be-5e10-b27c-2837bdc0cdcd | note | Detail of Activity / Test - Max. Specific Gravity (MSG) of mix
37048f39-e771-541b-94e4-8df91569d6a6 | note | Action (Hold, Monitor, Witness) - M
874d79ab-1d0e-5c5e-bdbc-9a345982d7d5 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
a27b93bb-1412-52a8-84d5-23a51ace4d87 | note | Acceptance Criteria - Report
28fe7498-fee9-5de6-9158-35d957c696b8 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
6e50125e-0191-57c9-a700-7cc39d9ce0f7 | note | Responsibility - Asphalt Manufacturer
f37b48df-591c-5ff4-9b12-91bb5224dc01 | note | Designer - I
25c5f5d5-3df0-5a70-b808-0ebbffd682e4 | note | Eng. Rep / NZTA - I
e46b8ad6-7818-548a-8c47-b307b8253438 | note | Contractor - R
fb56aa31-3b62-4907-addb-9d91a46b493f | checkpoint | 2.5 - Production Asphalt
44fd86cf-36bf-5957-9da4-38540ec743e2 | note | Detail of Activity / Test - Air Voids at lab design compaction
4eedb4e8-582f-5352-bf0d-9085cac98613 | note | Action (Hold, Monitor, Witness) - M
4c2897d5-1723-599d-9948-96e43ca6839f | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
59bddfef-cd92-51ba-952a-4360c66133d5 | note | Acceptance Criteria - NZTA M10: 2020:
0b962fc8-e207-55d6-bba5-9203a5d748f7 | note | ○ Individual Test Results: +2.0, -1.0
32abffb9-6432-5250-b970-7b43e96d330d | note | ○ Mean of Three Test Results: +1.2, -0.6
f153e3aa-0a9e-53ef-9528-e08df3418057 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
e5b4a401-8d9c-574c-bfc4-323f005a4d62 | note | Responsibility - Asphalt Manufacturer
6c517538-1b0c-5bb7-b6ab-fa36cf7b5cf4 | note | Designer - I
69639b23-0bb9-5331-b976-db64ad937f83 | note | Eng. Rep / NZTA - I
ba953ff5-35c3-56ef-abc1-77aed1348d29 | note | Contractor - R
11acffb6-d9e2-4c0a-a520-ea0d265dca71 | section | 3.0. PLACING AND FINISHING
000dd8fc-643d-4c1d-910f-1b9a195cda3d | checkpoint | 3.1 - Membrane Seal
0dc1ccc7-acfa-59a6-9732-c8f49968baac | note | Detail of Activity / Test - Application of Membrane Seal
15533580-1f08-51ee-ad2e-335af08b0733 | note | Action (Hold, Monitor, Witness) - M
ef7fbcfe-00b9-57ee-a39d-b81e951dc0d6 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
fad88c6a-c435-5b35-8c30-7e08238d147b | note | Inspection / Test method - Sealing Records
80fb983c-1102-5ff4-a75f-d9066039ca4e | note | Acceptance Criteria - Application rate, chip type and binder as per membrane seal design
7f6ec2fb-9042-5137-bfe7-6d6c1a51cc62 | note | Record documents (QCP - Quality Control Portal) - Sealing Records
172b7f5a-1de4-5a53-a22d-7aa72547741f | note | Responsibility - Paving Contractor
7b4885da-9e10-5a7d-9302-6dca6f7f7d62 | note | Designer - I
38f4ded9-3e4e-5efb-89db-cf9e069fd8fb | note | Eng. Rep / NZTA - I
a6b49753-5d35-5b93-9772-d428eebfc94b | note | Contractor - R
c0ae199b-10e2-458d-8da2-f252a7b75d1f | checkpoint | 3.3 - Temperature
8da2f9dd-1e29-519d-83f9-a772d5c38e03 | note | Detail of Activity / Test - Asphalt Delivery temperature
5c853e71-e432-5a95-b059-fb403fa9ae5f | note | Action (Hold, Monitor, Witness) - M
045fd72d-4c7c-5b63-aa01-d0f6330d6947 | note | Minimum Test Frequency (Lot = 1 day’s production) - Every Load on delivery to the Paver Hopper
9e461756-aedc-50ab-92bb-eef3bc8dab71 | note | Inspection / Test method - Temperature Probe
dcf0d4f3-6888-5392-9714-6f4ffbb48388 | note | Acceptance Criteria - Target ≥ 150 deg.C. in the Paver
b8297d36-ae50-511e-b4b8-d2b7ecf1a224 | note | ○ Min. ≥ 130 deg.C in the Paver
7bd3f1c5-4351-514f-94b9-969bf166009f | note | ○ <130°C to be Rejected
e8b6ea97-388c-55da-b5de-2d04804ed533 | note | Record documents (QCP - Quality Control Portal) - Site Diary
c1573bfb-3301-5926-add4-71c95e3a5a3d | note | Responsibility - Paving Contractor
e8469629-7d6d-56e2-860c-406bfb5c0709 | note | Designer - I
36d6de19-1395-556e-ba50-e66c1d392aea | note | Eng. Rep / NZTA - I
c5906e9f-12bb-5310-812a-bb6ae604d7da | note | Contractor - R
94801dc3-1154-4583-b60a-18a7830b194f | checkpoint | 3.4 - Temperature
dc12c7c5-5113-5e1b-a8af-56d4bcd3dba4 | note | Detail of Activity / Test - Compaction Temperature
1f96e9c5-876a-5cf7-b519-cb6e26ec97c9 | note | Action (Hold, Monitor, Witness) - M
56d006e6-6e99-591e-8a12-45a4e5d6cd5e | note | Minimum Test Frequency (Lot = 1 day’s production) - During compaction
07225298-835a-577e-b48b-d35c36f9eb4c | note | Inspection / Test method - Temperature Probe/Infrared gauge
3c250aa5-9748-523c-8eff-5bfb44cef785 | note | Acceptance Criteria - ≥ 125°C at commencement of compaction.
14024ddf-4f51-56f7-ab15-4aa7f99d2341 | note | ○ < 80°C - Stop Rolling
61015314-7b18-5700-bca3-37b80e54c5a1 | note | Record documents (QCP - Quality Control Portal) - Site diary
34143e6e-806d-53b4-adba-e55c744fff37 | note | Responsibility - Paving Contractor
b8f059be-e906-5e87-a6d0-6f87f83fb702 | note | Designer - I
422ad302-fabd-54c1-b352-6f9d54be2924 | note | Eng. Rep / NZTA - I
a22157a1-2811-52d0-b2b5-732a7927b634 | note | Contractor - R
c0c4ad3c-0188-4fa0-8e94-d2fcf7353a42 | checkpoint | 3.5 - Mat
29792225-0a01-52f2-a4c3-fc48789c8e2d | note | Detail of Activity / Test - Load Locate
9e46a3f7-7675-5cca-a1c9-34fe5c24a1a6 | note | Action (Hold, Monitor, Witness) - M
a042e5b6-917c-5190-8451-749c51793282 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each load
ddda51a3-abc8-5121-923e-17b65bd86503 | note | Inspection / Test method - M/10
3eaf4933-f24c-58f9-af35-22a300e84cad | note | Acceptance Criteria - Each load can be indentified to a location using a diagram. Record includes:
d1d3de2c-74f1-52b7-b529-311f86e481c1 | note | ○ Truck ID/Rego/Driver
34b567f5-872b-5a89-8ab2-f65244a2c2a5 | note | ○ Depart Plant Time
f1e7e86f-e419-54fd-9849-01bf1ae80a42 | note | ○ Arrive Site Time
60f4f231-f652-5799-a4db-27f91896047f | note | ○ AC Temp on Arrival
093de0b0-a2b3-5a14-ba33-ff351d1d7c26 | note | ○ Tonnage
0c56abd3-9558-506f-a968-2d16813e4225 | note | ○ Run Width
09027a32-8d02-5022-89ef-9bc79a282705 | note | ○ Estimated Run Length
ed970e8f-da8a-5397-a1a0-b39e30ae210b | note | ○ Calculated Area
c527835c-4852-576a-9eed-b0bb102a1626 | note | ○ Calculated Average Depth
e464434b-8bc2-564e-a330-4c76c0794612 | note | Record documents (QCP - Quality Control Portal) - Paving Run Sheet
e78ad234-3f31-5a83-87ca-735ffadb69e8 | note | Responsibility - Paving Contractor
20cdab4b-c4ec-55ff-b7f6-eb38d4f307fb | note | Designer - I
538e54df-ead4-505d-99db-7706a6e3534e | note | Eng. Rep / NZTA - I
4181abd8-7551-52f5-be56-423830d4c003 | note | Contractor - R
15d47d63-76b9-461d-8d31-0e874de2a809 | checkpoint | 3.6 - Mat
c572525b-2d16-5e15-b2a7-570710d3e11d | note | Detail of Activity / Test - Thickness Monitoring
f57acbf0-13b1-5e4e-ad23-1c4320900e8c | note | Action (Hold, Monitor, Witness) - M
b8b637de-1215-5c43-9272-a626d5fafa59 | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
72e3dd74-9bf3-5e6f-9a30-36d7efd3f5d8 | note | Inspection / Test method - Dipping
f41aa420-c0f1-55ed-942c-8ad1a57228cd | note | Acceptance Criteria - Target Loose Thickness -0mm / +10mm
7ad6e7c4-a5bd-5645-adf3-1b7815442cd9 | note | Responsibility - Paving Contractor
781b9fb0-b732-59f5-8c54-6aefa8281361 | note | Designer - I
ca3b8007-41c1-5fe2-9064-11bf7dabe913 | note | Eng. Rep / NZTA - I
70d39825-0922-53e8-8b77-91fd288f2258 | note | Contractor - R
87253230-c921-4297-a6b2-04461783643b | checkpoint | 3.7 - Mat
f5ef186d-56ca-5f8a-b4fe-49a74763afab | note | Detail of Activity / Test - Compaction - NDM
1aa4fd4a-9443-5219-adfa-0bd7808235ae | note | Action (Hold, Monitor, Witness) - M
868bf060-811a-573c-9162-591f13881d52 | note | Minimum Test Frequency (Lot = 1 day’s production) - Plateau to be completed on 1st run, thereafter monitor compaction/roller passes to achieve target density.
79f53cad-7653-5665-afef-9fba72753ee3 | note | Inspection / Test method - Insitu density and air voids
36b2f2a9-5a9a-53a3-8684-cce0a18894bb | note | Acceptance Criteria - NZTA M/10: 2020 - section 9.9
873603ba-760a-55ab-9210-424c3b6a5d66 | note | Responsibility - Paving Contractor
84fa85eb-50db-51cc-933b-b22f3353cea7 | note | Project Specific Notes / Instructions - Use a calibrated NDM with established core correlation. Locate and mark cores, record NDM Bulk density by core location (including any offset used).
e7c3ab14-0aa0-59ed-99f6-188c0d4d26ff | note | Designer - I
eb547f10-a197-5d6e-97e9-42c5c545a0b1 | note | Eng. Rep / NZTA - I
fe8f199d-b812-5b30-b4db-ca68b2dcd765 | note | Contractor - R
a74758df-bea0-4d2b-b2d5-228b423de91f | checkpoint | 3.8 - Mat
365a5c3a-2075-5859-ac70-7ca27fa914c4 | note | Detail of Activity / Test - Compaction
612b18b4-cf98-5b69-8550-6a5eb575ec70 | note | Action (Hold, Monitor, Witness) - H
41dd6fa4-20c7-598f-86dd-f76032c8ed40 | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 1 mats and 1 joint
99d944fe-866e-5e3d-b453-effe60c49698 | note | Inspection / Test method - Insitu density and air voids
6cef12c6-9471-522b-b2a2-5b45f1cc5d7e | note | Acceptance Criteria - NZTA M/10: 2020 - section 9.9
22f586a4-eec5-5a16-a8a7-e978c9ce49a9 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
8786e367-32d1-5ab0-939a-2db8da9a3954 | note | Responsibility - Paving Contractor
edbe1fa2-7226-5107-a3ff-05ca9e40b70f | note | Project Specific Notes / Instructions - A pavement lot shall be an essentially homogeneous section of work completed within a shift of production.
194e1e04-c522-5459-b5cd-95a16ae28045 | note | ○ The lot shall be divided into an appropriate number of approximately equal sub-lots and a core shall be taken randomly within each sub-lot. The Engineer or their delegate shall use a random method for locating each core position, such as ASTM D5361 or a similar process.
f5e6a2b4-5d21-561b-8aff-574638a704b3 | note | Designer - A
1693dc42-5e02-51b8-9b46-737d4f5865ba | note | Eng. Rep / NZTA - I
6e857e90-8359-5ad3-800a-44afaad105f7 | note | Contractor - R
e4c44afe-433b-4fd6-af54-1b61165a75c9 | signoff | AUTHORITY HOLDPOINT
54ba1006-94a4-4af2-8ca8-2b797bb82239 | checkpoint | 3.9 - Mat
fd4845e5-4a2c-573e-80a4-ee0cae041a06 | note | Detail of Activity / Test - Thickness
7a2c2ca7-eda5-5fff-8b96-6758a887942e | note | Action (Hold, Monitor, Witness) - H
cbb5d4da-dede-5f91-a792-1e1f640548b2 | note | Minimum Test Frequency (Lot = 1 day’s production) - Average of 3 measurements per core
d3ef4462-44b4-50a6-b772-3217be00705a | note | Inspection / Test method - Measure Cores
2c972343-8af2-5017-bade-abe7e3dd85c8 | note | Acceptance Criteria - Average Thickness > Specified Depth (Nominal)
44d0338f-df82-5723-8303-3c15a6271225 | note | ○ NZTA M/10: 2020 - section 9.7
e74d9d3e-4d15-51ad-b54d-4fb710fcbe18 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
71b7fa9c-af4b-5c32-9c44-76040c73bc5f | note | Responsibility - Paving Contractor
cbfc9a40-0e3e-57a8-85ad-b8a8ed66d7c7 | note | Designer - A
80b8fa0b-f3ec-56c5-9bf1-99d1a7317d3a | note | Eng. Rep / NZTA - I
9db252cd-e65b-5f5f-bc94-bd1df36ae9e2 | note | Contractor - R
ddb5b28f-9ec1-490b-9ba4-45752c48c4c9 | signoff | AUTHORITY HOLDPOINT
be81a42f-3876-4f26-9fe8-3188c5f66db3 | checkpoint | 3.11 - Mat
8a7b1ccb-722c-5fc1-9f53-72ef9af5326f | note | Detail of Activity / Test - Shape
23ddd8d3-1b22-5f96-a88d-42179b320f63 | note | Action (Hold, Monitor, Witness) - M
d8bd2d09-2657-52cb-9df3-716fe006720c | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
9d2d6c2b-c558-5121-b85d-7cb27c6cba29 | note | Inspection / Test method - 3m Straight edge
c15dc696-3085-5d11-a327-61779d1cd6d6 | note | Acceptance Criteria - Where the length of the site or the geometry is such that a road roughness-measuring vehicle cannot be used then the straight edge can be used for checking the surface shape. Refer NZTA M/10: 2020 - section 9.8.
89c45adc-5a50-58d8-87e4-8130cb6cba56 | note | ○ Not more than 5mm under a 3m Straight Edge.
f53c8b6f-1c15-519a-8f46-ca4b1cbcba01 | note | Record documents (QCP - Quality Control Portal) - Straight Edge Record
09431aaf-3838-5b01-b6bd-88b622ffa0e2 | note | Responsibility - Paving Contractor
e7c97d13-88b0-5f4f-a00f-d206394c7e26 | note | Designer - I
6942c900-450f-5a9a-aa68-de5c41c8fb42 | note | Eng. Rep / NZTA - I
d495050e-f354-5932-8c55-60d4b02f6636 | note | Contractor - R
21704bfd-46b8-4f28-9ed4-788a31c50f6d | checkpoint | 3.13 - Paving Quality
4b075a07-47cb-5761-bf87-39dd21b27f37 | note | Detail of Activity / Test - Level
67228311-76cb-56cb-ab2e-3b0ed164ff71 | note | Action (Hold, Monitor, Witness) - M
17ac1810-112d-5c9d-b6d5-dfdd52ccc36f | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site
9c9d4c1e-ad02-5ca5-8bfe-4def098cf9b0 | note | Inspection / Test method - As Built Survey
2c0766c5-d1fb-5d80-a136-9f94904fb413 | note | Acceptance Criteria - -0 < +5mm from Specified Level
04d6b464-a156-51b8-9525-6f19ba49c149 | note | ○ Where there is Kerb and Channel shall be flush with or no more than 5mm above the LOC.
0b39a64d-e226-5e88-8713-6a31eb9e29c5 | note | ○ NZTA M/10: 2020 - section 10.2
6b840413-b2ae-5b09-8169-eb20c87baba1 | note | ○ Note: Minumum 55mm not nominal 55mm.
372c2ef4-342d-57ec-912a-38f9942e76a9 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
93568c46-b867-5d20-9cde-9ff4ae21bf8c | note | Responsibility - Paving Contractor
85c32c66-c022-5f1e-b8b3-5539f5bf085c | note | Designer - I
453f08c7-75fd-5c57-8857-8f9290111d2b | note | Eng. Rep / NZTA - I
573a35e1-49b1-5c5e-94f5-f0cee17f32f4 | note | Contractor - R
0484f753-6ad4-4826-8c4f-507a010cf9b5 | checkpoint | 3.14 - Paving Quality
53dda3d0-aa1f-5233-84eb-2207299ce77d | note | Detail of Activity / Test - Alignment
8f708f96-1461-5332-8081-1ea6a68f6ea2 | note | Action (Hold, Monitor, Witness) - M
7fc1d8b7-c0a6-5363-a340-14cc3da6091d | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site
7c23a877-22a9-55c9-b921-784df261ac3a | note | Inspection / Test method - As Built Survey
e877f5b1-4ee0-507b-a967-8bcc71d4bfe4 | note | Acceptance Criteria - Kerb to kerb
9a6afdab-32e2-5259-92d9-d5e91623e1b4 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
abb0de71-c376-58c8-babf-e0c192ef050a | note | Responsibility - Paving Contractor
ae97f81a-4863-5c36-97e5-f25f99107eea | note | Designer - I
95ed866a-c644-537d-be66-3ca4a6e90c14 | note | Eng. Rep / NZTA - I
c90c2c92-58ef-58e2-b0ba-0e4913af986a | note | Contractor - R
47a3f423-1e52-4827-8bcc-d4a77b882f63 | checkpoint | 3.15 - Post Paving Completion Checks
475d9d69-81ed-5350-825e-2b051fdc97cc | note | Detail of Activity / Test - Site clear and cleanup
240aa02c-7e7b-5987-b3e9-fb84b8ad0dd6 | note | Action (Hold, Monitor, Witness) - W
38f0b8c7-fea0-5741-b544-b380ccd8dcc0 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
2e4bc8c4-0ef3-58e3-ac14-4705b7036881 | note | Inspection / Test method - Visual
f27b8916-bc37-5955-9f76-dda192a3716b | note | Acceptance Criteria - Site is cleared of plant (or parked in safe location) cleanup of all waste mix, paper and detritus is complete
d393ee18-2ccc-51c6-ac24-c09cc6f28508 | note | Record documents (QCP - Quality Control Portal) - Site Diary
f308f1c7-e1ce-51ef-b74e-cfad6db9e2ad | note | Responsibility - Paving Contractor
032b16fe-6509-5e4f-b076-afb4866e09e9 | note | Eng. Rep / NZTA - I
cac8cfe6-e97c-5bc8-b46e-bd3e3b87a55a | note | Contractor - R
44b77ec9-c080-4c54-af18-b1c07da3b271 | section | 4.0. As Built Records
f88236bf-21f5-4088-997d-6f9dcd7228fb | checkpoint | 4.1 - Assessment of all test results for conformity
0cb68e00-6e4e-5bb5-9ba5-4ab439505480 | note | Detail of Activity / Test - Review against ITP Requirements
50a5f044-5546-5f75-8687-e3365b49a036 | note | Action (Hold, Monitor, Witness) - H
16da4320-cd00-564d-9246-b0580e29109d | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
aa3e23cc-85ac-5c87-b593-c669e4fdc0ed | note | Inspection / Test method - Review
9bae6ed7-8351-508f-ac52-2a4f8bf0890b | note | Acceptance Criteria - Reporting of any non-conforming results to Engineer via NCR
871e60e4-ae62-5446-b783-44809da186e5 | note | Record documents (QCP - Quality Control Portal) - NCR
a5aa8825-bb18-5255-a577-ae4917847268 | note | Responsibility - Paving Contractor
26f7f185-a85c-52bc-b31a-10ef08bc0319 | note | Designer - I
4c84ce05-e35d-553f-8397-17c3873e0966 | note | Eng. Rep / NZTA - A
7a2c3168-b4d4-50b9-9736-f00a90a6db2b | note | Contractor - R
3caa6d12-526c-41ef-9e32-23233e793085 | signoff | AUTHORITY HOLDPOINT
c2ee233c-b8e0-4f4d-89ae-33902941d572 | checkpoint | 4.2 - RAMM pavement and surface records
d894a553-51ab-58d3-9a48-bb213eb2f56e | note | Detail of Activity / Test - RAMM surfacing pavement data spreadsheet updated
bad35ebd-4054-5d7f-9175-c460ec356393 | note | Action (Hold, Monitor, Witness) - W
5149a6b1-56c9-5fe8-aaf6-0c15b1056e64 | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
23829cd3-7a24-5d65-aa19-2b958f902bbd | note | Inspection / Test method - Prepare Data
6ea6c58e-647f-5433-8ea2-e50ed9d33672 | note | Acceptance Criteria - Over milled and Deep lift extents recorded and verified by Contract Engineer / QA
086570a6-9666-57ec-97bc-d4841317d9eb | note | ○ Spray sheets for membrane area received by Contract Engineer from Sealing Team.
5ea07acf-f742-54ca-8d39-2ea648c6ebc8 | note | ○ Surfacing layer extents recorded and verified by Contract Engineer.
30a45611-2bba-5811-adb6-e8ca31d6f616 | note | Record documents (QCP - Quality Control Portal) - RAMM Spreadsheet
c337ddf4-c0f2-5024-93bc-e1d6e9fdde46 | note | Responsibility - Paving Contractor
502ee336-7c5a-5792-bfb8-474de667765a | note | Designer - I
77dfcfc0-8433-5a0a-9f6b-d514320cee3e | note | Eng. Rep / NZTA - A
61dc8359-a0d3-5f7c-9590-1932bfe825f4 | note | Contractor - R
f7957fc5-779c-4a4e-bcb5-5ed3e1ec9fbb | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
e9dae8b0-5c40-5627-8e73-6e034fc08027 | textbox | Contractor's Rep Name:
eb42e148-7bc9-58be-bf45-1c467fd80b1a | textbox | Engineer's Rep. Name:
0861458c-0519-570b-8a3a-3e289b2aaa28 | date | Date:
82c9bd3e-66b2-447d-ae22-5ecff4ed31f2 | signoff | Add Signature
39d0ec04-a329-4130-a9b7-2679a34d4059 | checklist | DN1210-SP2-021-001 ITP Gargan Road/SH29 Watermain Rev 1 | itp | DN1210-SP2-021-001 ITP Gargan Road/SH29 Watermain
a62bab27-2ebd-4f36-92e1-95e08a63d9e6 | section | 3.0 - PRE-CONSTRUCTION HOLD POINTS - MATERIALS/TESTING, PERSONELL & THIRD PARTY APPROVALS
981ff1df-8e7f-486c-b2a1-c9e4367fda85 | checkpoint | 3.1 - Pipe Installation
35113511-62f3-5301-ba21-08ebab392d3c | note | Detail of Activity / Test - Method statement
a9582611-a56b-5361-a266-2e8c7cefb551 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
a3019739-cc8e-546e-bea9-e55fd4270aff | note | Standard / Specification - PS- 22.3 Appendix V
eec811d0-314b-57f9-8fa7-a1061d7e02e9 | note | Verifying Document - Watermain Construction Work Pack Sign off
a445436f-21d7-5af1-832f-05d398511ea6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
28f86ade-94be-52df-a43a-8391fda8110d | note | Verification Activity: Activity - HP
b70b8c83-af79-5d3d-8c8e-1fc4ef1a185d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3a5537a4-4272-5f45-a0eb-4fd8ec5bd783 | note | Verification Activity: By - ENG
c745e26c-fdcb-4a3b-9be9-fe7a939e5daf | signoff | AUTHORITY HOLDPOINT
23cc9fe1-549e-4fbd-be54-9c1c941cecb9 | checkpoint | 3.2 - Pipeline Pressure Testing
cb4bd910-d4c4-5753-80fa-ef26e6b74452 | note | Detail of Activity / Test - Method statement
6fd18c4a-96af-5586-ac88-c40bb340666f | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
0b923d2d-43c7-5940-8173-2e8e803a5777 | note | Standard / Specification - PS- 22.3 Appendix V
33c13fc6-90d7-5308-8ff7-59d6abdbfadb | note | Verifying Document - Watermain Pipeline Pressure Testing Work Pack Sign off
0af7698d-6b3e-5ab4-9ed0-762bbc72580c | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
bfce6ad4-16b0-53c5-9aef-6a9bff1a7024 | note | Verification Activity: Activity - HP
9bac417b-fbc4-52e6-bea6-632a5f6eed7e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
467e39b7-3a0e-5de3-be32-fa2602679f60 | note | Verification Activity: By - ENG
b0170e30-811c-470e-bcc4-ced0e860c706 | signoff | AUTHORITY HOLDPOINT
3855f248-8892-4b5f-9055-21865cd98ef0 | checkpoint | 3.3 - EF pre construction Weld Tests
bc7174cb-98d9-5057-b9fa-4449a0fee2aa | note | Detail of Activity / Test - Use the designated welding equipment and the approved WMS.
96fd7b0f-19b7-55d0-b5ef-8c80c12d6b5f | note | ○ On the largest size of PE pipe used in this Contract
d19d0fe5-5e95-5e21-99af-167b741b856f | note | Acceptance / Conformance Criteria - ISO 21751 (strip-Bend test) or ISO 13954 (Peel-decohesion test)
b5df9f7b-3350-5b6c-aa5d-c67ca0bab2f0 | note | ○ WMS Report
10235e77-8d7a-5bbf-9b13-98b1bae86290 | note | ○ TCC approval is required before works start
a76e22e6-6914-5765-953e-73f295b9cf97 | note | Standard / Specification - PS 22.9.6 (b)
b7e38cfd-c8d8-5d89-86a9-58d784e85baa | note | Verifying Document - Laboratory Test Report, Visual Inspection
175a91ad-0d28-52a5-a0b8-483b110a7261 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction. One test welds per operative(Welder)
6245e6ff-b7b1-5767-ab72-c6aea2c7bbc3 | note | Verification Activity: Activity - HP
8981e095-485a-5258-a6fd-1839184d0873 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7fbe9a82-1249-595b-a924-aa1bc671aef5 | note | Verification Activity: By - ENG
81811e62-7d4d-4fb5-a1a6-d6368d9f0ffd | signoff | AUTHORITY HOLDPOINT
df07791f-9cd7-4fc1-b2e4-070930100235 | checkpoint | 3.4 - Butt-Fusion pre construction weld test
da669c8a-68f3-5631-8af3-dde8b616ef0c | note | Detail of Activity / Test - One weld on the most common size of pipes used for the project.
494db117-bf9e-5af0-8162-34b3c7af4f63 | note | ○ One weld on the thickest wall (highest PN) pipe
ee538338-af5c-565c-bcdd-fc8c2f397e65 | note | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode.
3963b318-4f65-5a87-a2b5-dd0890237cd3 | note | ○ WMS Report
5c42f68e-ebef-51bf-81cc-23b39d34c73d | note | Standard / Specification - PS 22.9.6 (a) ISO 13953 Standard
0d8b7507-38f9-55af-a029-005f47c237f6 | note | Verifying Document - Laboratory Test Report, Visual Inspection
cf66e1c7-8e0f-530c-8854-39c70dfe1811 | note | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
b05acd2e-febf-5716-a3b6-253db1f021fd | note | Verification Activity: Activity - HP
16d5e66d-6543-50fc-85a3-d43b95d02c8d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b8ea26f6-7428-5d9c-b8ea-186b5a683ec9 | note | Verification Activity: By - ENG
42d1e1e6-8e5f-4eaf-bc5d-083b18af3654 | signoff | AUTHORITY HOLDPOINT
d65184c0-a32a-4486-ab25-2f6c6e3d9311 | checkpoint | 3.5 - Extent of Line Setout
a32b5690-cd0e-5526-bf59-470fa404bbe6 | note | Detail of Activity / Test - Ensure line and level of Watermain has been marked out and agreed with Engineer in accordance with Watermain drawings.
c21269ed-827d-59c9-920a-d4b736e8fa6f | note | ○ Identify any clashes before construction.
1b10b41e-3cb9-52bd-88d0-de3975a64b93 | note | ○ LOT- markup
3fab7048-a449-5e7d-b6a0-e0c513cb4fc5 | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
578b8669-0ac0-5c16-9699-b6c2e8d9936d | note | Standard / Specification - Design Drawings. 32735.02-WSP-DR-WAT
0eb3f496-b855-538c-a73d-cf96ce55c8ac | note | Verifying Document - ITP Sign Off / Mark-up
fad25dcc-4bf8-5a2a-a25d-3fd637bf8035 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
6782613a-ff7e-5796-a027-171ca7620e1b | note | Verification Activity: Activity - HP
09938fae-4b68-517d-8963-d9e9316cd54f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
56f02ffa-0d57-578a-bcb7-31173d135505 | note | Verification Activity: By - ENG
aaddcff8-4797-4351-860a-7ba89c58dce3 | signoff | AUTHORITY HOLDPOINT
f505458d-f31c-45aa-8baf-36b65caeaaac | checkpoint | 3.6 - Pipe and fittings.
b62b8611-c618-5807-87bf-b3436b28a9ec | note | Detail of Activity / Test - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
d8d326bc-64f2-555b-af61-b17e73525e35 | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
0960d996-8ae6-5269-b2c3-e0d4f5b204cb | note | Standard / Specification - Design Drawings. 32735.02-WSP-DR-WAT
31b14675-d779-541c-9d39-fe59876999be | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
5976d2ac-2151-5fe4-b0f2-7c34f1aacfa7 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
3e7a9f7d-98c9-5939-824e-16c092775f19 | note | Verification Activity: Activity - H
c0e53c61-0c4b-5b08-9bb0-9f8603334bac | note | Hold Point (Internal)
c5b518c7-9665-56f2-87f9-be1a1c335c3e | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
600544d3-e025-54e8-a5a9-b91faacebaf1 | note | Verification Activity: By - PE/SE
20e86138-6858-489d-8082-54b86bc8f07f | checkpoint | 3.7 - Valves, Adaptors, Flanges, Caps and Fittings
f5e4024a-63e1-5478-ade4-3c343b38fa4d | note | Detail of Activity / Test - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
b0ec0a14-ffd4-56be-aaec-7025c7aa933b | note | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
08ff14f7-d291-5582-a00d-a8585174d42e | note | Standard / Specification - PS-22.4.2
887190f5-a136-5690-8395-3568250f39b2 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
ef443b8f-0d3c-5c4c-9d40-0c1cfb5b9220 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
69bd5adc-4d16-5d94-8923-9cf624b997ac | note | Verification Activity: Activity - H
d13f5232-94dc-5437-8410-a1dd0a1835ff | note | Hold Point (Internal)
8c768e19-4f8a-52d3-a1c9-9b443a308cbd | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
e3256402-6d8d-5da9-89e1-df7bec3ba71c | note | Verification Activity: By - PE/SE
9da3505c-8c1a-4d3e-99db-08bdaa5e0031 | checkpoint | 3.8 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65)
4e57247c-f82b-5d4e-acd8-fd5e9556b815 | note | Detail of Activity / Test - Confirm Specification and material in good condition.
3a819800-fb50-5942-b940-7d59aee22d4a | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
d9c75441-6fd1-52ba-b648-dbab5817eb67 | note | Standard / Specification - PS-22.4.1
64e08a58-87f1-5d95-acff-405f998baec4 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
82760fe2-73eb-59ce-bbca-e39b50781248 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
9237899a-294e-5afa-833f-345894ea694a | note | Verification Activity: Activity - H
0968d251-55f0-5058-81bc-1eec0effba0c | note | Hold Point (Internal)
8d1adb4d-c27c-5107-ab1f-a708d148a7cb | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
2a893372-2aab-50b2-a131-6b47527bdf05 | note | Verification Activity: By - PE/SE
dad98047-6d1a-4291-ada3-5daf3287f9d8 | checkpoint | 3.9 - Bidim/Geogrid
88be170c-53a6-5a32-9e9c-c54c75ccf646 | note | Detail of Activity / Test - BIDIM A29 Durogrid 30/30 or similar.
ef6e3ec2-0fdb-5e17-93ee-e0f78abe5aad | note | Acceptance / Conformance Criteria - Site Engineer Approval
7e6057bf-f980-5623-92ac-c6ec0d0e6500 | note | Standard / Specification - PS-22.4.1
8647a756-74d8-5a7d-af4d-03261d04f0c9 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
d133a3a8-47e8-5f93-a897-f9a57fc1c22b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
35e5bfe6-95c5-5deb-81ec-73bf51aa6d7b | note | Verification Activity: Activity - H
de65b1d0-edfa-5052-a33e-ad1e56f6c5aa | note | Hold Point (Internal)
a09cb864-ab00-5fb8-80af-25997934c0c4 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
546d61d3-9b2a-5b80-8bbd-9454435f2a3b | note | Verification Activity: By - PE/SE
69807190-1c68-4c70-8f9d-0a9a9b79bb16 | checkpoint | 3.10 - Pre-cast Manholes
956ec965-6146-5bdf-9dbe-cc4f0f01c864 | note | Detail of Activity / Test - Confirm the class and type as shown in the drawings, and fittings required for MH is same
a781bb60-acb6-5876-b7fe-13a9577277e8 | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
525a8b46-4003-58b9-855f-01451838a3ce | note | Standard / Specification - 32735.02-WSP-DR-WAT
9fe9ac86-b5d3-55ba-9e87-560e34a18263 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
ca32b4cb-b834-5cb3-8831-3f94de75951b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
3b627ba6-2c40-5889-bcc9-dd8e00f7bb14 | note | Verification Activity: Activity - H
55d2546f-16af-5fae-87d3-6e52d1737dbd | note | Hold Point (Internal)
66734627-d4a6-5fc4-8c63-6257b1604546 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
a8abd57c-6619-5808-a203-fda8bbf15072 | note | Verification Activity: By - PE/SE
d593cbcf-1ae9-4b8d-8493-61b9028b3c23 | checkpoint | 3.11 - KWIK Spacers
53c3baca-66d7-52f2-8d71-8780a022e845 | note | Detail of Activity / Test - Confirm Specification and material in good condition. Spacers for DN315 pipe and DN560 sleeve.
1307455b-dead-5dd2-a713-48bc0547832b | note | Acceptance / Conformance Criteria - Model: HDXT43
bd16e10a-3f90-58fc-9b7c-05fc6d69ca62 | note | ○ Height: 43mm
5875d3bb-c8bb-50dd-bc00-83cdcabfa0ee | note | ○ Spacing: 1.5m
7f079e65-4dd6-52e4-857b-bc2c49c9a41f | note | ○ Installation: Centred and restrained
27abe47e-5fc8-53b5-9961-c16f28adf616 | note | Standard / Specification - Manufacturer’s Installation Guide. 32735.02-WSP-DR-WAT
8bd6d036-c2c2-596d-a6ef-3edd8c32cb5f | note | Verifying Document - Photographic Evidence
ce09d63d-0f74-5d75-9a4d-f09f06bec119 | note | Testing Quantity Required (based from schedule qtys) - Every spacer
640d3725-b75f-5144-ade0-f9c689670812 | note | Verification Activity: Activity - W
3c10201b-f47d-5ea1-b856-7bce75bb2669 | note | Review of text reports/records or other evidence of compliance
6475912d-fb3a-5884-a548-51300a5587c2 | note | Verification Activity: By - SE
246eeffd-c15d-4494-9ce2-e7074d849e4e | checkpoint | 3.12 - DN560 Sleeve
b52567b2-16b6-5abb-8b24-9fcabd43cce3 | note | Detail of Activity / Test - Confirm diameter, class & jointing type as shown on the drawings, and that the sleeves are correct and in good condition.
ae4a57e7-02d5-5887-9b83-29e45e829852 | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
a66f7e44-6e33-5c56-a66b-dc9a825640b0 | note | Standard / Specification - Design Drawings 232735.02-WSP-DR-WAT (Sheet #0312)
45ecbb32-4aa8-5293-bef8-f92b7add9399 | note | Verifying Document - "Delivery Dockets / Inspection Checksheet (DG-QA-TP019)"
07e0d570-9842-53a8-9b12-a46270d4fdce | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
64a60235-8cd4-5b74-9afc-ce45a595aa5f | note | Verification Activity: Activity - H
a5d8fc02-5ae6-5b0a-a257-a1ec5407bed6 | note | Hold Point (Internal)
eafaf0b1-71b9-576b-9782-72573221e847 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
2ad7d543-73a3-526b-bd12-626bbc04b05a | note | Verification Activity: By - PE/SE
bfcb0652-ecd8-4191-90d1-3e3ddb4fc73b | checkpoint | 3.13 - DN400 Sleeve
d378ddb4-94dd-57ab-a268-87b18d6b4d00 | note | Detail of Activity / Test - Confirm diameter, class & jointing type as shown on the drawings, and that the sleeves are correct and in good condition.
7072ca48-a44f-5643-9cbe-dbc6d7d05577 | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
87c540bc-1017-51eb-a4d3-e246c403d02d | note | Standard / Specification - Design Drawings 232735.02-WSP-DR-WAT (Sheet #0312)
0b281cd5-a026-5b30-a30a-bc46925d757d | note | Verifying Document - "Delivery Dockets / Inspection Checksheet (DG-QA-TP019)"
96788bdf-87fb-587e-9eae-ed8f7c5bdf30 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
3e7c80af-462c-52b1-b64d-99593717d720 | note | Verification Activity: Activity - H
a4ee6742-127e-5687-a5db-980c3b217873 | note | Hold Point (Internal)
9e8c0f3f-6831-5d4a-bd8f-17d57171f864 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
020aba80-0d04-5305-b610-47f263a3c151 | note | Verification Activity: By - PE/SE
e75d9e4d-6c99-4b3e-9da2-09b04e259cc7 | checkpoint | 3.14 - Material grading: Materials (GAP65/AP65)
caa6080c-84b0-5394-bde2-ba613725d1f9 | note | Detail of Activity / Test - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
bb1c438e-ad6f-594b-9b99-cd14c1f75907 | note | Acceptance / Conformance Criteria - No Particles >200mm
4a36b0be-d3f0-5510-b520-56f362693cbd | note | ○ Maximum fines 10% passing 75micron sieve
232eb969-0447-5017-8bbb-4dcdd1d13ca4 | note | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
3ada8577-b5d6-5c26-ad0e-65347175a44b | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
44cbb730-fc71-5c17-b4da-4c8066470445 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
19e4b2d3-bbe7-5f89-8a93-293009e7e3ca | note | 0-400 - 2 tests
f528340e-b2ee-5a19-8a43-06632d2f5f9a | note | 400-1,500 - 3 tests
70608f9f-70a4-59e1-9f4c-8481e648fe77 | note | 1,500-4,000 - 4 tests
d70f4cd2-5690-5828-a2f8-a01c73728da9 | note | >4,000 - 1 test for each additional 1,000m3
99262cf8-9d51-5319-b900-3585b4ff8f9f | note | ○ Results to Engineer 2 wks before importing
8fc68b73-031f-5284-8764-8fd87cfe73d3 | note | Verification Activity: Activity - HP
4c607477-38fc-59e3-af8a-5d88ec06c368 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0eaf0498-7810-5f68-9f06-d64c7db4e49c | note | Verification Activity: By - ENG
60f9207e-2715-4c86-9446-48cc0a0d4969 | signoff | AUTHORITY HOLDPOINT
d41185f5-cb8b-4f55-8619-ad8b2d36ea3a | checkpoint | 3.15 - Weathering index: Materials (GAP65/AP65)
a1fdc9ab-d9ac-594a-bd2b-053861d139fe | note | Detail of Activity / Test - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
01a3fbc4-8f4f-5e18-80ea-014142099ee7 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
1eb891c8-9321-55cd-a40e-0be1afe973e1 | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
adcdf30c-d3c8-5b02-85a5-b5c278a53752 | note | Verifying Document - IANZ Accredited Report
74f9e36b-ce66-5246-b03e-53d274769064 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
dd39ce91-2361-580e-b576-33da8f3b2b3d | note | ○ Results to Engineer 2 wks before importing
f9180b26-3f42-56e2-92dc-fc9c80c9e561 | note | Verification Activity: Activity - HP
a1f864d5-be55-592d-b9e6-1aef67d7c136 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4b741800-f5a7-5fe3-a67b-ee4dc5c91ebc | note | Verification Activity: By - ENG
5111b628-d47f-4d01-8997-21ac46326b6a | signoff | AUTHORITY HOLDPOINT
97a39c44-6768-4b41-b6d5-91b9464e3635 | checkpoint | 3.16 - Crushing Resistance: Materials (GAP65/AP65)
9bfbefe0-2cb0-58c0-b5d1-b260754fe44f | note | Detail of Activity / Test - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
17f30846-72df-57b0-a725-0bd7c32f4e26 | note | Acceptance / Conformance Criteria - >100KN
23427afa-7d47-5cff-aab1-cc02833b9b4b | note | Standard / Specification - Appendix XVIII, Appendix V
855042ef-c049-53ad-acbf-a87161a0f150 | note | Verifying Document - IANZ Accredited Report
4fa0d14b-6989-5379-8884-b7fb3266ef93 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
2d611205-fa01-56d7-8bdb-75f96ad7f689 | note | ○ Results to Engineer 2 wks before importing
671c04bb-5ee3-5c15-9d42-4898a78db98e | note | Verification Activity: Activity - HP
54aa0d2a-b1cc-5e75-8cd2-38653113738d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
bcb37933-7a8e-513a-9a24-820f98181f29 | note | Verification Activity: By - ENG
a6502230-3ce4-4208-a4ae-1bd446b7b1fd | signoff | AUTHORITY HOLDPOINT
f4390735-8631-43b3-a91d-da9677f6225a | checkpoint | 3.17 - Maximum Dry Density and Optimum Water Content
256874eb-3a86-5c84-80b9-1c33982135a5 | note | Detail of Activity / Test - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
37231ab5-6021-5251-985e-3942b71417d8 | note | Acceptance / Conformance Criteria - Report Value Only
cddbfe11-1db5-5241-b11c-06fbc1a6df7e | note | Standard / Specification - Appendix XVIII, Appendix V
a44d47f2-18ba-5a3d-b63e-96f47d3c3644 | note | Verifying Document - IANZ Accredited Report
8f03edb6-fa3f-5910-9961-2f400572732f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
0537f98e-2abd-56e9-8701-cd893b4828f2 | note | ○ Results to Engineer 2 wks before importing
53f53d81-c297-508b-8b1a-dcf576039d32 | note | Verification Activity: Activity - HP
c25b6809-7014-5c09-810f-3e1bd018dfee | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
971e8619-6371-5005-9d49-350896f50ae5 | note | Verification Activity: By - ENG
8aeb3a61-35a2-49de-a0b7-9fad38f361d8 | signoff | AUTHORITY HOLDPOINT
1bf75f73-c467-4eb3-b430-a282a8bf34dc | checkpoint | 3.18 - Material grading: Materials (GAP20/19mm chip/Sand SAP7)
d09f3f8f-5434-5d40-875f-513b0a338ebc | note | Detail of Activity / Test - Bedding/Side Zone/ Overlay Zone/Embedment Zone
1f03ac34-daff-50ba-8c04-a3b49b13f950 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
28691f01-07b9-5b62-81cb-2b382ca27f2a | note | 19.0mm ¦¦ 85-100% passing
9e092d23-5c05-5eef-92b7-e9b6a038ec7f | note | 9.5mm ¦¦ 25-55% passing
68cab787-a6f3-5684-9629-fe2f107726cf | note | 4.75mm ¦¦ 0-10% passing
bd92e62e-f680-5cef-8166-81724e36e398 | note | 2.36mm ¦¦ 0-5% passing
4158766e-981d-5472-9697-e17c1f0e986f | note | 0.075mm ¦¦ 0-2% passing
56168df4-b448-5410-87d1-5770803e3314 | note | Sand: Sieve Size ¦¦ % Passing
1e8b39f5-19f5-5f7f-86e8-437ba1646f98 | note | 4.75mm ¦¦ 100% passing
a850cfb9-1b77-5188-9989-74cd07cceb79 | note | 2.36mm ¦¦ 90-100% passing
0171229b-9bbb-5b89-ab23-6d230046cc2e | note | 1.18mm ¦¦ 85-100% passing
8eacd96e-5c37-591c-a9e6-a65b3a556d06 | note | 0.600mm ¦¦ 70-100% passing
403c71ba-9b04-5b5d-b14f-d2e644a0d4ec | note | 0.300mm ¦¦ 50-100% passing
ac0e430b-56b7-50b3-b1b5-8f05637f4576 | note | 0.150mm ¦¦ 0-40% passing
e44de1d1-fbeb-5f5b-a8b7-c41937c2abea | note | 0.075mm ¦¦ 0-5% passing
46e0de68-1ce9-5a69-a236-10dd25b12c2c | note | Standard / Specification - AS/NZS 2566.2 (G3 - sand), PS 22.4.5
1512cf09-1ea8-586f-998e-814147005040 | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
f940a20f-d287-5276-a571-79d6d69aa10a | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
83560424-7c8f-5510-afc7-8b34b8f4b7bf | note | 400-1500m3 ¦¦ 3 Test
bb94475d-e9a7-5c5d-988f-4301ae313f82 | note | 1500-4000m3 ¦¦ 4 Test
653137fd-bc9b-5f86-a617-32eaee2abb53 | note | >4000 ¦¦ 1 Test Additional 1000m3
a3810ed3-edae-5e10-87bc-1671f6a3fb4e | note | Verification Activity: Activity - HP
05d895d6-bb13-5a82-bf3d-0244020c02d3 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f041d7b6-ee2c-5849-bc12-181781da088b | note | Verification Activity: By - ENG
cd0ef3ef-bf4e-4f7d-8c90-15da21b70514 | signoff | AUTHORITY HOLDPOINT
f08c753c-abbd-4b5f-9d62-386d50fca25f | checkpoint | 3.19 - Pipes (PE)
1b37bbdc-cb45-5a23-977a-91d222fb7718 | note | Detail of Activity / Test - Manufacturer's record and location of extrusion plants.
5ad36797-42a2-595f-aff5-e7afb64f4e41 | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
2ce733a4-4da4-50b6-ba24-e8a5bc98f72a | note | ○ Full Traceability information and certification of analysis for the resin batch.
b390e4f0-1a30-5e09-8666-c356cc8163d7 | note | Acceptance / Conformance Criteria - Full Traceability information and certification of Material and resin.
781a97fc-1405-558b-b89b-24acc379a79a | note | Standard / Specification - PS-22.4.1 (d)
0b341fa9-4fe1-5d78-973c-118a332a54e4 | note | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets.
34ced40f-ca4e-5fe7-97fa-85744b4c8d6b | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
e373babe-1dab-5e53-bebe-35c38c2309a7 | note | Verification Activity: Activity - HP
5d1b93ea-654f-5c8b-9c8c-1be1c48c778b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d4c32c1c-3012-53ae-aed2-9421077ffb0e | note | Verification Activity: By - ENG
b53ae03c-e0e3-4532-bc9d-c4dfd79c3a3a | signoff | AUTHORITY HOLDPOINT
cf754f95-d643-4c79-ba8a-96d22e0d02c6 | checkpoint | 3.20 - Valves, Adaptors, Flanges and Fittings
7b5605b8-58c9-5608-95a6-003772040209 | note | Detail of Activity / Test - Have a pressure rating no less than the designed pressure.
f10ef9a6-1f00-5643-a8a4-a08a5f956f54 | note | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
2177248c-8750-508a-be14-0cc75233c4a2 | note | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
3eb856e0-25cb-5aa2-9f73-a14a04ab5600 | note | Acceptance / Conformance Criteria - Engineer approval, AS/NZS 4129
32f79201-9e22-5db5-bd60-afc3f750fd2e | note | Standard / Specification - PS-22.4.2
a64068b4-3c3f-5744-ab60-311f1a56387d | note | Verifying Document - Delivery Dockets
149d77df-1b25-507a-9282-b1ae3cee2a11 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
16a7631b-222f-5110-8092-7963e0417cf5 | note | Verification Activity: Activity - HP
43eaa867-02f0-50fe-a117-aeadb14a468d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
bb201777-30c6-576e-b11e-12c909fa5839 | note | Verification Activity: By - ENG
48c37972-43c1-40ca-82b3-2b96f864f3e3 | signoff | AUTHORITY HOLDPOINT
08abcea0-6eb0-4145-99cf-8686b5e25cc5 | checkpoint | 3.21 - Fusion Joint Compatibility
2ef45e16-9aec-5b20-9015-d0f4b5a9936a | note | Detail of Activity / Test - Confirm pipe and fittings compatibility for fusion welding
a8e3c220-0e33-5dfb-9a53-5c609e7907ca | note | Acceptance / Conformance Criteria - No defects, compatible resin types per NZS/AS 2033
7033a665-b2e9-5ed9-8424-5c08f052f9d9 | note | Standard / Specification - NZS/AS 2033:1980, Clause 4.2
4f37a99f-8dff-5641-a2a0-b74406860012 | note | Verifying Document - Test Report
52306397-d381-5494-a757-a30bed14a642 | note | Testing Quantity Required (based from schedule qtys) - 1 per material type
9ed189c8-9ff3-5ae5-9164-9656994627e2 | note | Verification Activity: Activity - H
853284c0-2153-5aa6-a219-62119d7508c1 | note | Hold Point (Internal)
47a803e4-2e4d-5eb9-8a51-2d9aaafd0ad7 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
a3aa044e-507d-544c-9e40-9c853f0e058b | note | Verification Activity: By - ENG
eadac79b-c31f-4026-87b2-afedf032e46d | checkpoint | 3.22 - Horizonal Directional Drilling
66219400-672f-5ade-bc40-bc79f34389d4 | note | Detail of Activity / Test - Detailed methodology of directional drilling
b6f2e740-2689-516f-bdf6-1c4133b49083 | note | Acceptance / Conformance Criteria - Engineer Approval
e48c4026-f7f2-58dd-b12b-b75c5c89b9af | note | Standard / Specification - PS 21.6.6a
bddbc515-1db7-53cf-8d09-1f9f8b1816c4 | note | Verifying Document - Engineer APPROVAL
044aa6f9-056d-5119-a678-08ab8c9428b4 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
bacd48bc-0730-508b-bce5-e68def4a4b07 | note | Verification Activity: Activity - HP
e826a05e-844f-5901-b795-8a4d08c8e8bd | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1881d3b1-1988-56cc-92a6-ecef1501f040 | note | Verification Activity: By - ENG
cfd2f945-175d-46b1-b086-ae397cda5d1e | signoff | AUTHORITY HOLDPOINT
4d5387db-b0a4-4a93-9e02-752a0a127301 | checkpoint | 3.23 - Exisiting Watermain system
b3c7cb80-f463-5ef4-9dcc-62e1f4595869 | note | Detail of Activity / Test - Confirmation of existing watermain network
8e2a1856-3632-54a8-bd5d-7c56cee93c8b | note | Acceptance / Conformance Criteria - survey informations
a01a10f6-b828-5fa5-9b50-c0977eab2fa5 | note | Standard / Specification - Appendix XI
5056c2eb-9eab-501c-96b8-b6dae98bbf81 | note | Verifying Document - Survey data. PIck up existing watermain with survey
8dc58204-f52d-57f6-adac-006eb5bbe63f | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
3c715cec-96cd-5046-ab2d-dbd552a18e0d | note | Verification Activity: Activity - H
14ff4947-9131-56d6-91b4-ea82d0aad0aa | note | Hold Point (Internal)
e9d4afea-6740-5776-aa33-efc58d4bdb49 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
fc960fd8-5468-5289-b43b-934cb4adb1ae | note | Verification Activity: By - SE
23d90126-23fe-42e9-8598-3943b0b8c97c | checkpoint | 3.24 - Grouting Methodology
c715fa56-efde-518f-b41e-38e24a677ca1 | note | Detail of Activity / Test - Cement grouting the sleeve annulus
687e9e7b-55b7-563e-adbb-54a0224d61fc | note | Acceptance / Conformance Criteria - Enginner Approval
fc63f025-5d64-5241-a033-c4858a32575e | note | Standard / Specification - PS 21.6.6g
6c270a20-af0e-5af0-a2dc-70849cbc6f54 | note | Verifying Document - Engineer approval
dbf5a107-af4e-5187-8a33-deef5f1e64cc | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
94006be3-b425-5874-bc97-e204d7a78786 | note | Verification Activity: Activity - H
40319fe6-15e3-5a68-ad27-334d6f59d0f3 | note | Hold Point (Internal)
f7dbacac-b262-5411-812f-250d66907fb9 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
7c3d2021-bfc8-5eaf-8f53-1265f9402ae0 | note | Verification Activity: By - ENG
9169bc0c-ccab-4691-8b48-c784aa4338ff | checkpoint | 3.25 - Pavement reinstatement - Asphalt type to confirm
95149536-1d08-512f-8a7c-e20b143868fa | note | Detail of Activity / Test - Prior to construction, TCC will provide what asphalt to use. Testing required too
38456d78-1a6f-5f20-8710-726de520b5f3 | note | Acceptance / Conformance Criteria - TCC confirmation and approval
418a5ad5-7dde-5114-b570-974d3bc522f9 | note | Standard / Specification - TCC T460
336aa03c-da4b-5803-9c9e-4479cf817b44 | note | Verifying Document - Engineer approval
cacafba1-b84e-5cc4-b8f5-2d2c6f684eff | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
27f11118-ae00-5aa8-b032-19552349850b | note | Verification Activity: Activity - H
aeab2edd-25dd-5236-9114-fc4b64a708bc | note | Hold Point (Internal)
6c7553f8-6b4a-5cec-b475-435bb2549da4 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
3f09c30d-bec1-5225-b416-3bec0170de4e | note | Verification Activity: By - ENG
7a0ba465-894c-4ccb-a39e-ed9f5bd460c1 | section | 4.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE INSTALLATION - Excavation and Laying
3f2d42d2-616d-4618-956c-84746caac921 | checkpoint | 4.1 - Foundation Compliance
e42850fb-bb25-59d8-894b-e5c67f573eb7 | note | Detail of Activity / Test - On Granular or Cohesive Material
f8532563-d3b2-5c31-9d3d-1479f71b7b22 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
1073e5bb-e637-57d6-886e-dd0c0a25ba35 | note | (Or)
9b8a3f55-f44f-51e5-bcba-57d1f082af25 | note | Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
e606291f-d202-5918-8947-9d706522d99f | note | Standard / Specification - Appendix V, Table 21:11
85ee1fcf-e62d-5485-90a2-5d1f09be3f9c | note | Verifying Document - Scala/Shear test result
af7c6763-3c42-5133-b445-2abd09c1897b | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
fb67ca19-3c64-5448-b192-0fab57862d73 | note | Verification Activity: Activity - W
40d7098b-f250-5367-aa7e-96c4e96b19ac | note | Review of text reports/records or other evidence of compliance
c8783701-16aa-51a3-bb0f-747d0e670685 | note | Verification Activity: By - SE
7d1febcb-6952-494a-b92a-62fcce9b401a | checkpoint | 4.2 - Undercut approval
a4d88b97-73a4-5f06-9a2c-c04d624f2ad2 | note | Detail of Activity / Test - Trench Foundation
0f32e8f3-43e4-5816-9c28-5f87c42e6fcd | note | Acceptance / Conformance Criteria - 300mm Max cut
4c919c86-105d-5558-affb-f590c604ad75 | note | ○ IFC Drawing Sheet 320
46c77702-6487-50fd-8cb7-1b1bcff5e2f0 | note | (Or)
85276cb4-dafd-55f4-8263-c5f8c559f585 | note | ○ Engineers approval
a4ecdfae-2c41-5995-b2c2-613d6045d82a | note | Standard / Specification - IFC Drawing WAT. AS/NZS 2566.2/2002
e4895343-bead-5a9e-88aa-2daf96171430 | note | Verifying Document - Lab Test Report / Watermain line record
3439a3ed-ba77-5de6-9723-95492712934d | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
14193ecf-0541-5c0d-ad87-3f995c1da740 | note | Verification Activity: Activity - H
11989172-9004-510a-bf21-6f4bc7565075 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
28927c21-1ffd-52dd-b71d-b7900b2a4715 | note | Verification Activity: By - SE
abb95eba-b83a-4e22-832f-4ddf39bbe03f | checkpoint | 4.3 - Undercut Backfill Compliance
647662d6-a273-5ed7-8858-873a8c4a7052 | note | Detail of Activity / Test - On Granular Material / On each layer as per specification / on the trench foundation.
de77d3a4-b7ed-55e9-8ce0-14ac716ae801 | note | Acceptance / Conformance Criteria - Visiual Inspection
541ab577-76cf-5024-921e-d89d22807442 | note | Standard / Specification - IFC Drawing WAT
b1a72fd2-1ca8-5f70-aa27-2abcaa6b03ec | note | Verifying Document - Lab Test Report / Watermain line record
08e68330-21ea-5a28-846e-579387d46922 | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
ff2748d1-a0ae-5b0e-bbbe-17aadd8160d6 | note | Verification Activity: Activity - H
ffc9315b-3a43-5766-945c-b76740714065 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1b9f7b22-a354-542b-aab3-2dcedb5de717 | note | Verification Activity: By - SE
12e2dcdd-f9c0-494d-9522-3c9c9880e5c3 | checkpoint | 4.4 - Bedding Zone Compaction Testing
3ba2f17d-ef23-59be-b5c6-d2eddeed29ac | note | Detail of Activity / Test - On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip)
c94e7d5b-e295-522a-8b10-49e272090d43 | note | Acceptance / Conformance Criteria - Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench.
1919446d-299d-50a3-a768-42dbe2c37ae4 | note | ○ Minimum Compaction - 85%MDD
1eefde32-fbe2-551c-bc73-069d80a515a5 | note | ○ Paeangaroa Sand: clegg of ave 9 CIV and min of 7 CIV.
008899d5-fa50-5e18-b92f-feb2392c09b4 | note | ○ Wilson Sand No.2: clegg 4 CIV
0b79acfe-074c-5f20-901f-b3f983795907 | note | Standard / Specification - IFC Drawing AS/NZS 2566.2/2002
06d01fc4-bc85-5514-ae19-cc58797a6f5f | note | Verifying Document - Lab Test Report
5c9e5f2f-d937-5798-8e18-63533a92f75e | note | Testing Quantity Required (based from schedule qtys) - As per WM Specification.
a452edb2-1255-5172-9fcb-37c8c913af05 | note | ○ One test per 20m evenly spaced intervals.
03d3e85c-d1d1-596f-b434-7c012d6f65ff | note | Verification Activity: Activity - H
3ed6f419-9284-5f5e-adab-d23d72762b43 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
485716de-395d-5297-b713-c58123438090 | note | Verification Activity: By - SE
0757f5b6-ba4c-43e0-9fa5-2329aa58138e | checkpoint | 4.5 - Laying of Pipes
00ae5631-15c9-5d27-b1be-402785d218bd | note | Detail of Activity / Test - Lay in straight lines, beginning at the lower end of the line.
b81dad44-b26c-56b5-9ae6-a0742507968a | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
b053ef52-db36-552d-9c15-a8f8d7bf7e69 | note | Acceptance / Conformance Criteria - As Per Drawings. Facing upwards
91e3f690-e407-5f6b-a4cf-924381f487bf | note | Standard / Specification - PS22.7.1 C
2c31bea8-9dac-5ac3-89f5-aa745f3a6581 | note | Verifying Document - Visual Inspection / Watermain line record
aa130cb6-0632-5772-b49c-d6a4820aa629 | note | Testing Quantity Required (based from schedule qtys) - Every Line
3c263431-4efa-5aa3-a982-0eb7c393fc2d | note | Verification Activity: Activity - H
6fd50268-2644-5ac2-84f4-605a7ab01b68 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
25a81693-4cf7-5a82-aa9b-4c49502848f9 | note | Verification Activity: By - SE
4d39c3cf-e528-43ea-9125-a55e6e4d3ba8 | checkpoint | 4.6 - Pipe Installation on Curved Alignments
9b80c866-671e-5d2c-ad51-6b4ab163d6ea | note | Detail of Activity / Test - All Industry Guideline PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
4d42c364-57a9-5bf1-a840-c68bfccc7362 | note | Acceptance / Conformance Criteria - AS Per POP 202
d14e9e8d-e96d-5944-bfa4-af65fabce3ad | note | Standard / Specification - PS 22.7.1 D
99466228-0021-567e-921a-a85d2367fa11 | note | Verifying Document - Visual Inspection / Watermain line record
5c081430-7b3c-5b18-bbad-65b2e5f281d9 | note | Testing Quantity Required (based from schedule qtys) - Every Line
4edbb1ce-8dfc-5d87-88dd-dc8a20ed8646 | note | Verification Activity: Activity - M
2416c782-5171-59a5-9a4c-111c602479b1 | note | Monitor on Random Basis
b2b47585-ff27-5ae9-b5cd-8475f3860748 | note | Verification Activity: By - SE
a48cbe91-97b1-4838-8e33-58868a86ba8c | checkpoint | 4.7 - Anchor block and to extend past edge of concrete
6948b72f-071e-5f7d-9633-7e8f174bd357 | note | Detail of Activity / Test - REFER to ANCHOR BLOCK TYPE TABLE on drawings based on pipe size
dfd79a0e-52d8-504a-9fdf-26ca0716d6a5 | note | Acceptance / Conformance Criteria - IN ACCORDANCE WITH PROJECT SPECIFICATION as per sheet 0321
b7a7a4d1-bfd1-5650-84fb-8fd633afc618 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
a8343813-4539-5e75-b3e3-0901730e3f3e | note | Verifying Document - ER APPROVAL
fffec27d-5a5a-544c-a81f-8a17af7c6e7a | note | Testing Quantity Required (based from schedule qtys) - SH29/Cambridge Rd
4a1ef9bf-daa8-5fcb-9f09-6d9d6a8d3420 | note | Verification Activity: Activity - HP
cff9a8d2-9afb-5dfd-ba2e-5bc801473da2 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
51f2bbbf-4cf1-5d73-ac45-c3404d2e3dbc | note | Verification Activity: By - ENG
ea3c26d5-36de-4009-924d-fb887176f375 | signoff | AUTHORITY HOLDPOINT
73089436-0e77-4ca6-9fc6-28f236c77efa | section | 5.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE INSTALLATION - Directional Drilling
e515891e-73e2-4aac-8adf-a24f52894a8a | checkpoint | 5.1 - Check levels while drilling
00d851da-e0c3-5d24-ad75-f7aefe3028e6 | note | Detail of Activity / Test - Inspection of Pipeline Inverts
22c9488d-9db1-5901-b567-fa441c916d47 | note | Acceptance / Conformance Criteria - Vertical design Setout:
832c29b2-a5ea-598f-b329-dbdbe5116b3d | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
03eee727-c789-5ef8-8786-99b096c0b0fe | note | ○ Pipes > 1% grade: +/- 20mm variance
1f87b300-2b88-5c3f-921a-4a7569c992cd | note | ○ Horizontal design Setout: +/-30mm variance
a8af9923-8db3-5ad3-99a0-fb9f6ebb404f | note | Standard / Specification - PS- 21.7.6 Table 21.15
9b98de7f-ad04-5486-a55f-2b70fdf8fb8d | note | Verifying Document - Survey Data / As-built record
b7a52f63-a720-54b4-9dec-f44ec3be4fe6 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
ed93fdad-b268-5d04-83eb-eba17e70e532 | note | Verification Activity: Activity - HP
35c89202-10ef-592f-a2b7-ecc8879f65d1 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1a13983b-0a1a-5d61-857b-5e8ab137ec1d | note | Verification Activity: By - ENG
4c90199d-62dc-4a0e-9ae1-a001292493d1 | signoff | AUTHORITY HOLDPOINT
c9fe8457-fe4e-46e4-a08a-e1fe730abb1c | checkpoint | 5.2 - Drilling Fluid Mix
df86d471-d797-5291-8b51-a7041f7c23d8 | note | Detail of Activity / Test - Viscosity record
374ad3f8-8137-5ef5-bd3c-82a0ab30515b | note | Acceptance / Conformance Criteria - Viscosity record
c4274956-9038-5d14-9f6e-c6f8e9484ff1 | note | Standard / Specification - PS 21.6.6
ed745ed1-7be2-59c1-b5a7-d6b746f27755 | note | Verifying Document - Viscosity record /checksheet
557feb17-cf2e-5d2b-bdb9-75dc8b4b4eca | note | Testing Quantity Required (based from schedule qtys) - Every shot
8d7e82b2-7490-5b25-832f-4e9caffb2d70 | note | Verification Activity: Activity - HP
fe49ca51-12a1-539f-ae32-6bbddceed5d6 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6849753e-35a1-59ef-bcd6-456ccc824bc8 | note | Verification Activity: By - ENG
112ac3bb-a0bb-460f-a089-56b1380439d5 | signoff | AUTHORITY HOLDPOINT
d3367633-5c7d-4d43-88d9-4b81c101ae4f | checkpoint | 5.3 - Correct Reamer Used
f5fcdef4-cc2b-5d22-8a32-5c36105e7375 | note | Detail of Activity / Test - Reamer size to confirm on site
ed398f00-b7aa-5142-a669-f195ccdb5663 | note | Acceptance / Conformance Criteria - Reamer size to confirm on site
08e5360d-4ce5-5df2-8bf3-d45e3a234d3a | note | Standard / Specification - PS 21.6.6
626812b5-d3b2-5045-b82b-2649dd1f7a2f | note | Verifying Document - Checksheet
1aba0119-b3ed-50a4-95c7-2b13bba009a4 | note | Testing Quantity Required (based from schedule qtys) - 1 per drill shot
513f668a-51a3-544f-ad8f-3bfe47c8e2b5 | note | Verification Activity: Activity - HP
116f2d59-ebc2-5bbd-b69d-d4cf7e52d478 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
2cc9a542-fff9-5113-9587-3a9f70ab5f20 | note | Verification Activity: By - ENG
370e696e-b2ab-4477-9351-8af90cfaefb2 | signoff | AUTHORITY HOLDPOINT
61f7f8a1-8d35-4040-a512-af540d6180f4 | checkpoint | 5.4 - Pipe Damage
d2c9890d-5065-5438-85a7-0815060c4ba2 | note | Detail of Activity / Test - Damage <10% of wall thickness
b26866de-8c10-5277-96bc-e736ab87520e | note | Acceptance / Conformance Criteria - Damage <10% of wall thickness
82fe7b72-d825-5396-a690-f1ab0866bb2f | note | Standard / Specification - PS 21.6.6
51b19f17-fb91-5df1-9450-9278b2b06575 | note | Verifying Document - Visual inspection
35ecf8a4-2aab-5754-8bf7-b7ea027a1daa | note | Testing Quantity Required (based from schedule qtys) - Each pipe
03c2eed0-a0a0-56e0-8423-70c9e1d7436e | note | Verification Activity: Activity - HP
8f62b505-55b5-5734-9d99-63e26c70692f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a760acc6-98f5-5ae6-b705-07a6e1faaacf | note | Verification Activity: By - ENG
fa618e1f-83c8-4e94-9029-458834b28589 | signoff | AUTHORITY HOLDPOINT
78afafc4-a24a-4e23-a441-e56bc6ebc661 | checkpoint | 5.5 - Tracer Wire
c8ea77ad-2b09-5917-a4ca-e8f1d3bd93c3 | note | Detail of Activity / Test - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
3a8244c7-f06e-5427-8e75-e2930eccf887 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
6da899cd-6d02-5bc7-8d83-401d1146fa68 | note | Acceptance / Conformance Criteria - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
aa423c5d-9b02-5b7b-9734-b8ab77150202 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
eddcfcb1-1f7d-5b9e-8f5f-87a5a5d3cbc1 | note | Standard / Specification - PS 22.7.3 a
db89fee3-4c89-57c4-94db-8ce97f9b3af2 | note | Verifying Document - Visual Inspection / Wastewater line record
fb9647ca-7b7c-5942-8aa7-d4924273fdf7 | note | Testing Quantity Required (based from schedule qtys) - Every Line
3e745dd4-1102-5134-8d85-12bfb9d09f4f | note | Verification Activity: Activity - HP
4e52da63-445a-5110-87a5-cb0ed8ae7681 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ed639be5-c75f-55dc-b7af-10f71290e7fc | note | Verification Activity: By - SE/SV
8f8a6df9-9244-4080-bafa-3b93e208f2dd | signoff | AUTHORITY HOLDPOINT
22879ea4-3fe3-4d03-a793-2b24ed12270a | checkpoint | 5.6 - Drill Report
b30a13d4-e0b3-503f-8048-3c0e3ad4e3b8 | note | Detail of Activity / Test - Drill report to be submitted
2778dab2-3bab-57d9-9ad1-2b13ee69fc86 | note | Acceptance / Conformance Criteria - Drill report to be submitted
56c35107-5708-561f-996d-d9b14a4cc095 | note | Standard / Specification - PS 21.6.6
19b67f42-acf4-5ec7-ae71-ea65cc6f1ac6 | note | Verifying Document - Report
dd8f8b66-8a01-5726-bbe9-0ebf09566f62 | note | Testing Quantity Required (based from schedule qtys) - Every Line
0c13cc4f-f8f8-5053-900b-91b5ed32df7c | note | Verification Activity: Activity - HP
25ccc6a3-f763-57e8-a191-290a9f24baa1 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d7e14b0b-7205-5398-9831-984075648bd1 | note | Verification Activity: By - ENG
c34ed4e7-164f-4c3e-8448-d9432fa057e7 | signoff | AUTHORITY HOLDPOINT
752edc95-05fd-4630-931e-ab8f2d569e8f | checkpoint | 5.7 - Settlement monitoring and ground deformation (Baseline measurements)
adc49593-c6d4-5103-ba25-b014e35382c7 | note | Detail of Activity / Test - Topo survey completed before and after drill shot
d2eb818e-949d-552a-a72d-b7eb29f07d06 | note | Acceptance / Conformance Criteria - Topo survey completed before and after drill shot
0d0fda06-b352-5fdf-86eb-543e36f804fe | note | Standard / Specification - PS 21.6.6
bf3dbe32-2f12-536c-be00-b6adc56b1a3d | note | Verifying Document - Survey data
d0e9a0fd-ab64-556d-95f8-8e866bf11f3e | note | Testing Quantity Required (based from schedule qtys) - Every 6m
dda29fb7-a6b5-5edb-a716-6b7d7e23437b | note | Verification Activity: Activity - HP
d63243b2-609f-5394-a82d-79b81f5379fa | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e78f01a2-f590-5b7a-9ef1-02892d27b36d | note | Verification Activity: By - ENG
4d43b688-73c0-4b61-b55e-2ee53a8b6d9e | signoff | AUTHORITY HOLDPOINT
35b2b093-72be-4a84-abe1-5a5e180b21fa | checkpoint | 5.8 - Cement Grout - Annulus
d4196071-d31a-59e2-a860-aab386dc0584 | note | Detail of Activity / Test - The sleeve annulus are to be cement grouted after installation to prevent settlement.
e6419b23-7fff-5583-a525-5b961581da89 | note | Acceptance / Conformance Criteria - The grouting mix is to be:
4ac8251e-ea37-52a8-b063-18e161cb622e | note | 1. 1:1 Sand/cement ratio 1 : 1
2854001e-a8df-5f8e-af68-5580b9f293bf | note | 2. Water/Cement ratio 1 : 0.67 by weight
fef70480-b9cb-5947-8145-2a2886312edc | note | Standard / Specification - PS 22.5.8b
97a2b3e1-268e-5ea6-88ca-1757818ffd47 | note | Verifying Document - Visual inspection, lab report
9ee22fd2-8489-546b-b96b-4b71e920a6de | note | Testing Quantity Required (based from schedule qtys) - Every Grout
c4be9961-05db-5cf4-ba4d-cc1ab78d36a3 | note | Verification Activity: Activity - H
48f7beff-9447-558e-9522-e45d9763e692 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
fc57b03c-8d6a-5b79-a3a0-fc4c8f7110af | note | Verification Activity: By - ENG
3f459b5f-68de-4aef-96eb-a2a5d542c817 | section | 6.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Joint and Connection
36e86cd8-ba63-4971-9ade-72e1eb805d54 | checkpoint | 6.1 - Flanges
bd7d8dc9-3b0a-5195-919c-e63de51c3aa8 | note | Detail of Activity / Test - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
94789eee-2b26-58c9-9a92-62c962de43e2 | note | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
1796d7e5-3111-5503-95d6-bad5b5a8b7c1 | note | Standard / Specification - PS 22.7.5 Appendix XXII
a39b4301-0594-5585-946e-ae971f119c85 | note | Verifying Document - Visual Inspection
a500ecca-f220-516e-8794-a6538fcfa3d6 | note | Testing Quantity Required (based from schedule qtys) - First flanged joint
1c3bd9aa-9c98-5769-bacc-8013546004aa | note | Verification Activity: Activity - HP
b3895d24-a1f1-5397-99bb-044c548b815a | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
72755b6f-ae74-5112-ab92-492e05999d9f | note | Verification Activity: By - ENG
d197868f-8cda-430e-83a2-96598aa78d10 | signoff | AUTHORITY HOLDPOINT
f2a54f12-2509-489d-b2d5-8eead2c26db0 | checkpoint | 6.2 - Bends
7fe3f15d-7753-5d29-a9ef-f640e1112cf6 | note | Detail of Activity / Test - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
538d7c1a-3bb6-52c7-9132-b503aadb95d7 | note | ○ Fitting must meets the same PN rating as the adjacent PE 100.
3101cb97-276e-5c88-a172-84b385e6e94c | note | ○ Fittings must be suitable for producing the joints shown on the Drawings.3
b14ee01a-c925-5497-8edb-263310e10592 | note | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
1c0efd7b-a8ff-5bf8-bc06-22833ef85496 | note | Standard / Specification - PS 22.4.2 Appendix XXII
3434f58c-e6ee-5b31-81fa-5a07f9aae2c8 | note | Verifying Document - Visual Inspection
1814b7cd-8930-5464-9954-0711f81a7831 | note | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
f4b9e841-8bce-52ea-ad59-0aba4650744a | note | Verification Activity: Activity - H
22af44cc-1ce2-5e17-baf4-fb72c6aa0d6c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
64d4f65f-4586-5b90-8d9a-14ecdf4f3364 | note | Verification Activity: By - SE
ef888783-9aa8-46c1-88ef-56dbc6b9b95c | section | 7.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Butt-Fusion Welding
6333a1f2-b579-4e20-9b03-90ddc2af3ae6 | checkpoint | 7.1 - Butt-Fusion Construction Weld Test
d1ad2fb5-a026-59b0-8d40-9b12907ffd25 | note | Detail of Activity / Test - Test at least two welds from the first 50 welds.
25bc7bd3-24c6-500d-a898-e300f723c80f | note | ○ One of the welds to be selected by the Engineer for satisfactory result.
d006e73c-9574-5046-af14-d1a90633963b | note | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
78518362-9e32-5b47-a1ac-a9894d0ea6e8 | note | ○ 95% tensile strength; welds aligned
4e1e9aa3-8b5e-5344-b9a0-3051d4fabe67 | note | Standard / Specification - PS- 22.9.6 (a) (iv)
2454d054-c873-58a3-b191-bb7040ca9f74 | note | Verifying Document - Test report
338da675-b778-5f0f-a372-e804310cbfc4 | note | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
9f5dc18e-cc02-519e-b36e-286f1f737775 | note | Verification Activity: Activity - HP
ffe05943-4c3e-5a09-8311-e31fb74a3576 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b2e0bb97-8199-5d56-b1bf-6015400c096a | note | Verification Activity: By - ENG
0670a936-28d8-45bc-982a-b5658823a4e1 | signoff | AUTHORITY HOLDPOINT
03f1c7e6-17e8-43be-8a1e-2004517bc3a1 | checkpoint | 7.2 - Butt-Fusion Welding
2cb3b862-6112-59a4-a9c6-f455b8493939 | note | Detail of Activity / Test - Use only semi-automatic or automatic welding machines.
18661d83-6332-5039-a2b5-19ba9a087e2a | note | ○ Maintain a site record for all butt-fusion welds.
118a801d-a11d-5f8a-9be2-1b3aae2c68c9 | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
f90fe45c-15d4-5b27-a9ec-151917c64f0d | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
1a976bda-68c8-5ffe-a4ca-7faa8f67ff1d | note | ○ WMS Report
59836b63-4c63-5ba0-a417-79b83ec11279 | note | Standard / Specification - Appendix XXII PS 22.9.4 C
5f3f0cf3-c2b8-55f1-a372-f77cf449773c | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report
8b907118-cd7b-5439-9bf3-c404ef3e2302 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
a9f4b055-3a32-53a5-ab48-22c486242b6e | note | Verification Activity: Activity - HP
8fc67a66-4a28-5c02-a5d7-39552a43c888 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
18a4eb86-e6c1-5282-ac27-0b8666fdd668 | note | Verification Activity: By - ENG
843ad20b-9a3e-480a-bc0a-a1b546326670 | signoff | AUTHORITY HOLDPOINT
3c1bc9a7-d543-4ba5-82a7-fd397ab345a8 | checkpoint | 7.3 - Survey
c520b0a5-670e-5b83-92a7-2f6c20597c1e | note | Detail of Activity / Test - Inspection of Pipeline Inverts
01d5803b-7bf1-505f-bb5f-61e364bc1781 | note | Acceptance / Conformance Criteria - Vertical design Setout:
5117c711-e624-5da1-9828-f3409aedc4de | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
8d1f5370-fbe5-59b6-84df-b08fec270a67 | note | ○ Pipes > 1% grade: +/- 20mm variance
4cd4035b-2091-5f2d-8d3d-d8914c0eb89e | note | ○ Horizontal design Setout: +/-30mm variance
ad126ad1-10db-57b8-96ab-2d98b399932a | note | Standard / Specification - PS- 21.7.6 Table 21.15
1adb5aac-7150-5a3e-a4a1-e7fca88f72b5 | note | Verifying Document - Survey Data / As-built record
2ed73a18-37ad-5e06-9242-7b763bb469f4 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
2e285ce8-96ad-586e-afc1-80346172bf12 | note | Verification Activity: Activity - H
c7ac2f46-4f1f-5e84-80c9-c42aa1bb94ab | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
2ff2d74b-30ea-5705-9128-f228ebf1536b | note | Verification Activity: By - SE
342fd586-0f21-4b8a-a263-23e3b2323ea3 | checkpoint | 7.4 - Photograph of Each Weld
3844bd3a-dddd-5996-a6f8-9a6cd8a78659 | note | Detail of Activity / Test - Take sharply focused photo while clamped
8f4fe06b-244a-5c86-ad40-0b13e936a155 | note | Acceptance / Conformance Criteria - Unique weld identifier visible
80bd2ba5-8709-5ac4-b9ee-ac5f63565719 | note | Standard / Specification - N/A
b2ef570c-3dc0-5895-9801-9955ab858895 | note | Verifying Document - Weld Records; Photos
58d67ebc-48a8-59de-b07e-00c3ed2d512d | note | Testing Quantity Required (based from schedule qtys) - Each weld
9a8abe05-0769-588f-96df-e70afddfc02e | note | Verification Activity: Activity - I
a49105f6-aa21-5a12-900f-0b87dae573f3 | note | Formal inspection activity to be undertaken and recorded.
c346ef7b-2a6c-55ff-b3f9-f289534ece56 | note | Verification Activity: By - SUB
e37bb50a-0dc1-4d40-a9ff-abe50cb7f697 | section | 8.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Electrofusion Welding
de6e7e47-a3ff-4426-9b32-0f5fb64ee1b2 | checkpoint | 8.1 - EF Construction Weld Test
aa81cc6e-8652-534b-ab1c-60939ac528de | note | Detail of Activity / Test - EF weld quality to be maintained.
5ca55cb1-261b-5f7d-a291-9642f60476d4 | note | Acceptance / Conformance Criteria - EF coupler and EF saddle testing
71c33b9d-255e-535a-86ba-21fcdf87949e | note | Standard / Specification - PS- 22.9.6 (b) (iv)
3a167a92-ab12-5a4a-9f3f-9e7bfe8dd88e | note | Verifying Document - Test report
5955c4e7-745a-5dab-bc2c-2891aef3a6ac | note | Testing Quantity Required (based from schedule qtys) - 1 test per 5 welds
6df857f2-a661-55ad-a624-fcc5dff194d5 | note | Verification Activity: Activity - HP
893fdedb-b8a1-5bdc-b1e3-8c6abcc6f843 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ef27146b-7401-5314-8d21-a049738721b6 | note | Verification Activity: By - ENG
1dc79e03-7a26-44ae-b8e8-a631173d4fed | signoff | AUTHORITY HOLDPOINT
a2c967fe-134e-4cc9-9c16-08b55330c79d | checkpoint | 8.2 - EF Welding
75c7e5bb-d64d-536c-8135-d99e546d73e5 | note | Detail of Activity / Test - Required if Butt fusion welding cannot be perform.
18542a81-90dd-5fcc-b2f6-cd60368ceb99 | note | ○ EF Jointing in accordance with PIPA POP 001.
72428566-004b-5616-b2b1-11a08e1ad1e5 | note | ○ The lead welder or welding supervisor must verify on the site record form.
b3143dda-e6b2-5c72-8ba5-0cc89b70551d | note | Acceptance / Conformance Criteria - Site EF Welding record to be filled out. (Refer to CWP) and checklist. Photo of every weld.
1e611d6b-9d65-5f0d-a813-288d5ae11e68 | note | ○ WMS Report
71a9440c-c6d5-5158-8c8c-42c9ffc182c0 | note | Standard / Specification - PS 22.9.5 Appendix 22
0b7657e9-cd61-522d-b0f9-f960909ae96f | note | Verifying Document - Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report
aa2b2f91-2ef9-5b53-b7cb-7c7ef047b6a0 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
1ef1fde3-238c-5e37-89ad-c287c33df638 | note | Verification Activity: Activity - H
890aab00-6022-51ef-bcd6-bbcb3d38f028 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6c641b39-4d77-52d1-b698-6367ef0845de | note | Verification Activity: By - ENG
c84c8469-da86-4a27-ae6f-efd0435aed7f | checkpoint | 8.3 - Survey
b7a96efa-6e77-5d1d-bbd3-d8670b211e8d | note | Detail of Activity / Test - Inspection of Pipeline Inverts
98af6de4-305d-54d5-84bf-153decb49b58 | note | Acceptance / Conformance Criteria - Vertical design Setout:
ab15c7f8-23bd-556c-b75a-bb035d092c51 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
eacbb4a2-20ee-573d-99d3-056a897d5a4a | note | ○ Pipes > 1% grade: +/- 20mm variance
1211a3e3-18bc-5c98-97f9-896ab9ffd0bd | note | ○ Horizontal design Setout: +/-30mm variance
95b1cb1f-ba03-583b-b1f8-21321fde2d6c | note | Standard / Specification - PS- 21.7.6 Table 21.15
800d7e69-4c8b-5212-a2c7-c4e4174ee6b6 | note | Verifying Document - Survey Data / As-built record
3b33f10f-f7b8-5285-a264-13b74ae36363 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
9fa23c45-6854-5806-aa9c-1ba39c4d860d | note | Verification Activity: Activity - H
9f35fbed-58e5-5354-9a83-57a6b23bc05e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
dac3d92b-f212-597f-b9f3-966049383fa9 | note | Verification Activity: By - SE
8f8dfdf5-eeaa-4453-9e94-fb493375df6f | checkpoint | 8.4 - Photograph of Each Weld
f3b859ae-91b1-50b8-8be7-5c40817ae3e1 | note | Detail of Activity / Test - Take sharply focused photo while clamped
6bc5cd8e-5cf6-5c1c-955c-1229156e73ec | note | Acceptance / Conformance Criteria - Unique weld identifier visible
0412a590-db38-503e-accd-48a47403c17b | note | Standard / Specification - N/A
ee62f06a-52b4-5105-95be-8aec707c9f37 | note | Verifying Document - Weld Records; Photos
0d2702eb-9824-5316-b6a1-2c4629b55a19 | note | Testing Quantity Required (based from schedule qtys) - Each weld
adbd35e9-5132-5766-acce-6a3d6575465e | note | Verification Activity: Activity - I
599530c1-8174-5dcc-9e14-2bd5aacee449 | note | Formal inspection activity to be undertaken and recorded.
de68de9b-6654-52d8-86e7-2a7b8b7f7cfb | note | Verification Activity: By - SUB
a017c107-9072-4d99-a174-3ba30bb38553 | section | 9.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Backfill
82c54803-0b08-4d84-bda1-6822102c0fa9 | checkpoint | 9.1 - Emebment Zone - (Side Haunch Overlay)
e4c940c3-0c4f-50e2-9f60-6df3ce64caf6 | note | Detail of Activity / Test - Granular Sand backfill Compacted in 200mm Layers.
31411a75-3792-5b28-85a0-f6ba5f6d994f | note | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays.
bd187dda-066b-5271-9729-7e5fc614173d | note | ○ NDM BS to be Carried Out
78d6dcd7-4b22-5ff4-97fc-b520ad1684aa | note | Acceptance / Conformance Criteria - In 200mm layers.
6e8c4d7d-a288-5868-a433-b2f31f80330c | note | ○ More than 85% of MDD.
00369820-09d8-5c7d-8bdb-793207d39d0a | note | ○ Paeangaroa Sand: clegg of ave 9 CIV and min of 7 CIV.
bae1f2f8-5573-548a-865c-56e02fd4c6b0 | note | ○ Wilson Sand No.2: clegg 4 CIV
642e7d93-6ad8-5caa-85ba-79d6a01e2268 | note | Standard / Specification - IFC Drawing 0320-1
a5768c66-cf35-53ec-9f99-08dda0a0e223 | note | Verifying Document - Lab Report / Watermain line record
d8f66d54-b6b1-5908-8fa5-47d905e907bb | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals. 200mm lift
dd5a26dd-d029-5a70-ac5c-e6660642662e | note | Verification Activity: Activity - H
219e4f62-64b3-55ff-b4f0-dca62b0ce65e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3f108110-6d62-5f2c-b64b-72be215484d8 | note | Verification Activity: By - SE
0ee6d9b5-69f9-4475-be33-92f6fa4c0718 | checkpoint | 9.2 - Pipe Markers
42dab39e-7c1d-5e94-9c63-fdc27402d466 | note | Detail of Activity / Test - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
b5337690-0c70-5181-8c4f-e5753b1542b9 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
ffe1188c-111f-57d1-a629-d6922ea5e61e | note | Acceptance / Conformance Criteria - AS Per Drawings.
f0da361a-5a2c-52bd-9ae7-db61a51afdf3 | note | Standard / Specification - PS 22.7.3 a
b6504c12-d429-5e42-a10b-0c731442dde6 | note | Verifying Document - Visual Inspection / Watermain line record
fb1402e4-15ad-5513-bd1e-8fbd5223107b | note | Testing Quantity Required (based from schedule qtys) - Every Line
293b9951-cd02-5efb-93ca-262bb33fff21 | note | Verification Activity: Activity - H
cd957e91-6e8c-5ac5-89dc-1bf72d5e8e0c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e3e8a338-e174-5628-b2bd-75f682e25319 | note | Verification Activity: By - SE
b57f8505-00fb-435b-8c2b-42459867c46c | checkpoint | 9.3 - Backfill Compaction Testing
234e2c8f-d95c-53ab-8bb6-49668b5c275f | note | Detail of Activity / Test - GAP65/AP65 Backfill Compacted in 200mm Layers.
c48cf9df-5231-5a1e-9b34-38a4d51f0950 | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
e17317e4-bc91-58a4-a999-6b52a9539d62 | note | Acceptance / Conformance Criteria - GAP65/AP65 or site won material Backfill Compacted in 200mm layers.
688c127f-1b8e-5d4d-91e6-bbe7b9219d4d | note | ○ Testing to be completed on maximum 200mm lifts of backfill.
ed68b5bc-2f59-5941-96b7-50ea213e6f52 | note | ○ 95% NDM on Shared and Carriageway.
0b05d44e-7a6c-5b9d-b948-7799f637c55c | note | OR
a8b14f52-c294-5601-b88f-bc0537604da0 | note | ○ 28% CIV
75580e7c-c5f0-5053-ae6b-9f7a876a3e73 | note | ○ For site won: Structural fill - min 125 kPa
86d4043f-ae76-5700-86cd-c579e7f44a2a | note | ○ Landscape fill - min 80 kPa
fc953c02-201a-5042-a31b-04ac9abb81ba | note | Standard / Specification - PS- 22.13.5 NDM Standerd 25832 NZS 4402 Test 4.1.3, IFC Drawing 0320-1 PS 16.5.5
eec19f12-64ab-539e-9624-3e1222e0fc9b | note | Verifying Document - Lab Report / Watermain line record
32abd613-bc31-5929-88f5-b5a961f73864 | note | Testing Quantity Required (based from schedule qtys) - As per Specification.
88fdcdd8-cde9-5286-90b8-2df5d01e5e31 | note | ○ One test per 20m evenly spaced intervals.
e2585baa-2cc4-5db9-b2bd-7e19df7d48c3 | note | Verification Activity: Activity - H
77018f8f-7251-5627-9d8c-ba03d06469eb | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a98059f0-c87f-5857-8054-ae8e921a06bd | note | Verification Activity: By - SE
3086ad9f-4cf1-4662-8d63-937ff333b0ae | section | 10.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Inspection
f85bde1a-e75e-42c7-a29f-16443507d274 | checkpoint | 10.1 - Pipe Inspection
81006107-c8e3-51c5-b76c-696018c0ff8b | note | Detail of Activity / Test - Inspection of Drainage line
2bff6901-dde5-5da2-afef-7e86a3ed5a4e | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
90b2c9b2-6e1c-5fa0-a38a-a3471c71d582 | note | Standard / Specification - Internal
1f1a2f09-2ddc-5991-91da-d72b99965dde | note | Verifying Document - Watermain line record
33e0ff2e-de15-5dc9-83cd-40b36df7afc0 | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
b791fcc2-3a87-58cc-9303-41b96b68eb18 | note | Verification Activity: Activity - I
c35fefe9-2ed7-5a11-96da-8afe4d75ee0d | note | Formal inspection activity to be undertaken and recorded.
694e9b1d-5fa4-5df7-9310-a30ede825647 | note | Verification Activity: By - SE
99dfec7c-5d04-47c5-b01f-7b9b80fcc02b | section | 11.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE TESTING
ff3ccafd-4199-469e-9722-8ed70392d789 | checkpoint | 11.1 - Pressure Acceptance Testing
1fe704f9-6e77-553f-98de-9e08da1d9f6c | note | Detail of Activity / Test - Backfill/cover with embedment before testing
1df5c64f-1029-517e-a1ea-1c42f9871123 | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
12180a21-7924-5508-b367-e5c5699d4165 | note | Acceptance / Conformance Criteria - Potable Watermain Pipelines – 1250kPa
5f598cb9-0c68-5f33-92bb-c14c0b28a183 | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
3ada1378-8482-5998-9b16-708233f2331d | note | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
8afad52f-4be3-510f-8787-a5339c95f391 | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
12eafc93-94b4-563f-ab42-7feae5dc655a | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
c9e3e2f7-a512-5405-b4d3-085127595b70 | note | Verification Activity: Activity - HP
fcf4b900-648f-534a-a30c-d9c2181a7e9e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
92f33ac7-c955-52a6-a201-52c9a6019f56 | note | Verification Activity: By - ENG
9719ae20-5f42-4887-9887-f08eb9cba8e7 | signoff | AUTHORITY HOLDPOINT
3cd7ccfb-6a6d-4611-9889-c7027e373c3f | checkpoint | 11.2 - Swab New PE Watermain
9bb15365-d45c-5d9b-816c-18015451840e | note | Detail of Activity / Test - Swab to remove debris and air
d3529ab4-421b-5132-85e1-84f2b4692667 | note | Acceptance / Conformance Criteria - Water running clear & removed entrapped air
7560c05a-8c5e-5a6e-bb74-1fe0a7a00bf9 | note | Standard / Specification - TCC IDC TS-7
96ceef3c-fd6a-5ecd-b2e1-db422a6f89eb | note | Verifying Document - Swabbing Check Sheet
f0653a6a-4808-57a2-ac34-9e5040913119 | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed
65c35e13-a77f-52b6-97d9-3188d642bfc1 | note | Verification Activity: Activity - H
e75c4d60-df08-5c2c-b3c5-88fd4af56c58 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
470a7b89-3a7c-57d6-bb58-dcc0b266c54f | note | Verification Activity: By - SUP/SE
591370e7-6165-46ba-80c5-0be7b78794da | checkpoint | 11.3 - Pressure Test New PE Watermain
7a258f12-6540-5d54-bd25-bf9fc948b496 | note | Detail of Activity / Test - Conduct pressure test. Due to not commissioning the pipe until later in the project, CB will complete there own pressure testing upon installation of the pipe, with the full pressure testing and chlorination to be completed once the pipe is ready to be commissioned.
24b961bd-a0eb-525a-b435-1e34482af7a9 | note | Acceptance / Conformance Criteria - No leaks, no failure of any pipe, fitting or other pipeline component.
4082357d-6372-5180-b7ed-63e3de72d8b3 | note | Standard / Specification - TCC IDC TS-7.1c Pressure Rebound Test Method; TS-7.1a Constant Pressure Test Method
08420001-629b-574e-9e2a-66667a13a91a | note | Verifying Document - TS-7.1a/c Pressure Test Method (Test Report)
08fdcebe-fb58-51fc-b5bd-8ebbf22ae9c5 | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed & swabbing passed
553c9da2-c0c7-52e2-9de8-ff6232765194 | note | Verification Activity: Activity - H
f2ec6a28-9e8d-5f9e-a789-a9c792f7f378 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3099abbd-ae99-54f0-9622-324dae33cd83 | note | Verification Activity: By - SUP/SE
cefc3de7-8972-4c76-8525-425b6f84d5d5 | checkpoint | 11.4 - Chlorinate New PE Watermain
af85d48e-5347-507c-a010-0405ebb7681c | note | Detail of Activity / Test - Chlorinate watermain
316ac1fa-cba5-5610-bb28-df6da21069d2 | note | Acceptance / Conformance Criteria - 5+ pH on chlorine tester
26d304bb-44ec-5d41-b6be-0f6597ffa9df | note | Standard / Specification - TCC IDC IT-7.4.1 Disinfection Procedure
aa0ca76a-6185-5394-8f06-884bcdda0c9f | note | Verifying Document - Picture; Signed Chlorination Check Sheet
7e1dd232-a104-5472-8a84-b4ff69ff5d62 | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed & pressure test passed
0c49d854-aded-5ad7-9041-3e9892b2b668 | note | Verification Activity: Activity - H
1bd1b766-1bb8-596e-b923-9bc076e69ded | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
53db0660-5c82-599d-a2da-5c0d891ffdf5 | note | Verification Activity: By - SUP/SE
9fb7238f-2d8e-4b30-896c-6a356407c5cc | checkpoint | 11.5 - E. Coli Test New PE Watermain
36755b8a-4c65-532b-b07b-d05976acd857 | note | Detail of Activity / Test - Test for bacterial contamination
98b4a3bc-3c17-51ed-b3ad-d645444a0734 | note | Acceptance / Conformance Criteria - <1 E. coli; <1 Coliforms
edbba8f7-133d-58d1-ae6b-d0532ea1bd61 | note | Standard / Specification - TCC IDC IT-7.5 E. coli Sampling
9a287c4c-800a-51ef-a5bd-088a5485a546 | note | Verifying Document - E. coli Test Report
20cb19b7-0f60-57e2-b628-b6c4fc063720 | note | Testing Quantity Required (based from schedule qtys) - All new pipe installed & chlorine test passed
874a4922-cc19-5054-8d62-6d61dcf46259 | note | Verification Activity: Activity - H
66860fba-3bde-58cb-857e-370c0e9b7be7 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
2d55c226-4c8f-591a-8bb3-1650950a0de3 | note | Verification Activity: By - SUP/SE
955d8f6c-a1b5-44d5-8532-45888a8d6d77 | section | 12.0 - CONSTRUCTION ACTIVITY - WATERMAIN Manhole installation
946be51f-72ca-42fd-bcc8-83dd329cdb43 | checkpoint | 12.1 - Foundation Compliance
c32674ad-bd05-5b00-893e-12f1c7bf3bd4 | note | Detail of Activity / Test - On Granular or Cohesive Material
1e716aa2-12da-5d5f-bfe2-f4104f35044c | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
d7ba594c-46ef-5ee4-9af3-ee0536110565 | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
d458fb8f-97f2-5299-9515-df045167ea49 | note | Standard / Specification - Appendix V Table 21:11
be9ee7c8-2cd3-5beb-9f07-e096a70a5cbc | note | Verifying Document - Shear vane or Scala test result
ef6507b9-7c66-5c56-838d-ddbdbcf6dd99 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
6476ad1f-9449-5623-8c41-11a2c6c8f5ed | note | Verification Activity: Activity - W
b0df1a5f-5361-57c0-988e-2c46bcf1e1c1 | note | Review of text reports/records or other evidence of compliance
83fa6f29-4569-5318-9b56-e328d22abac2 | note | Verification Activity: By - SE
6077da0d-7d24-4432-aeff-5cca5df6ab25 | checkpoint | 12.2 - Undercut Approval
ea09b898-739e-53af-b1f4-e998b6270eb6 | note | Detail of Activity / Test - On Subgrade
975eb7d5-8045-5ed6-9a62-2e40d329a3e9 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
dfe626cd-dd2f-590f-b57c-8489b9e79466 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
e49e03b2-6a56-5638-9508-45e5c056c658 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
78693de5-180b-55cf-b4a5-202569416e73 | note | Standard / Specification - Table 21.5
e771fc3c-96ae-5b98-9dc5-c82707201073 | note | Verifying Document - Lab Test Report
e5ac1f36-f1d4-5988-8d08-d5f9e8ec68f4 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
88d532a7-f21a-5425-b428-4fe92b202b01 | note | Verification Activity: Activity - HP
297b66a0-d59b-58d9-8333-cc82820f8394 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ef546090-5242-5406-a5aa-a2d77840a7a5 | note | Verification Activity: By - ENG
d306428c-e1c9-4cee-9d6d-ab8a3eb69c5e | signoff | AUTHORITY HOLDPOINT
b3aec3b2-5a63-4593-99be-1edb9c4a38f9 | checkpoint | 12.3 - Undercut Backfill Compliance AP65
e288b84c-6125-53fe-8de2-6c1757bec7dd | note | Detail of Activity / Test - On Granular Material
644e711f-ff06-5976-9555-de79081ee223 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
aed81e51-8ca7-58da-8729-686563621e8f | note | OR
b1df89a5-086b-5393-bf15-e99cb55209a1 | note | ○ Clegg 25% CIV
3983b7b5-8699-543d-b7dc-f7d525b406f2 | note | Standard / Specification - PS- 16.6.4c Appendix XVIII
7cd05924-1703-512b-89ef-24dab4f9ab93 | note | Verifying Document - Lab Test Report
16d19c43-3da9-5acc-a3c3-0dbd3074da78 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
17408bea-9368-5dda-8f8f-3d8fbc4f4035 | note | Verification Activity: Activity - H
a397bee1-5ace-5966-8215-acc8688a9039 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
06bb3358-6f75-56b1-8cca-14276bd78048 | note | Verification Activity: By - SE
67810645-758b-412d-b944-8db65a13cc21 | checkpoint | 12.4 - Bedding Compaction Testing AP65
f3de33c0-5057-5f73-8c06-12e0fd449740 | note | Detail of Activity / Test - On Granular Material
ccdc9b8d-c738-5b0d-8290-255563f66cef | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
0bd67b79-a17b-5509-9727-2228e414f8f0 | note | OR
bbd3059c-01a8-5828-9753-556634703fa2 | note | ○ Clegg 25% CIV
294e6449-0676-58b0-95bd-bd9dfa15c049 | note | Standard / Specification - Appendix XVIII PS- 21.6.11
687c06fd-f447-53c1-b0e2-8db36fe5e5e7 | note | Verifying Document - Lab Test Report
5bb3b531-ac6c-503e-8d1c-0bf1f70ddd5c | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
b849c78a-4082-5fa5-96c2-7d66baf346f3 | note | Verification Activity: Activity - H
3b3c0c9f-8a82-5c78-a91c-3c4ada72c106 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d0b7b588-2176-5085-9325-c8ec94deac17 | note | Verification Activity: By - SE
c850b27a-e7ea-4d86-a0a2-356b2c0958c3 | checkpoint | 12.5 - Survey
2da45ce8-615e-508c-b056-fca0e412d597 | note | Detail of Activity / Test - Inspection of Structure
c47da2d2-d0c4-50d8-a8db-40d6cb534ec1 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
85e3cb79-9fd1-5a34-a280-37d4050dadb1 | note | Standard / Specification - PS- 21.7.6
7388f612-79dc-5ea6-bfae-2b82cdd477bb | note | Verifying Document - Survey Data
ef8868fa-b2d2-5218-8390-5cef91bae664 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
e5e347c4-c3dd-5658-be15-677d2893f649 | note | Verification Activity: Activity - H
0a586d73-e738-5634-91c7-7ea16ed723f6 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
dde3f886-a441-5d82-8fa9-9fc7dd4454f5 | note | Verification Activity: By - SV
a4e4d1af-6d84-42bd-8283-a070364c7a96 | checkpoint | 12.6 - Sidefill Compaction Testing
8bb114c6-e3cd-5a64-9878-f86d1c58fd43 | note | Detail of Activity / Test - From the bedding layer to the overlay layer of pipe.
64e7af4b-fed1-53e8-b380-6a4f8e33e706 | note | Acceptance / Conformance Criteria - AP20/GAP20
22c7d46b-0834-570c-9ae7-43022ab6eed4 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
f61147d0-44f1-5bac-8865-761cc007b5bc | note | ○ AP20/19mm chip
10ce54b9-3cf7-503b-8e48-90f6d36d4154 | note | Standard / Specification - PS- Table 21.12, DR-WAT-0320
6822c8a7-2149-5dfc-9248-926d69f9ab34 | note | Verifying Document - Lab Test Report
0ecc083d-9e0a-5a95-9ccc-3f276d1b005b | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
af54726c-e41f-5f65-a9c9-6cc79c675f7a | note | Verification Activity: Activity - H
5d0200f6-ebb3-5fa8-9cee-16fc62d91e08 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a8b10978-9a20-55ee-91a0-d9039d45bcda | note | Verification Activity: By - SE
c3df04f3-fd0e-428c-9d20-4765779adc8e | checkpoint | 12.7 - Backfill Compaction Testing
83dc66f4-6cbc-53f6-a469-3cd9033e0309 | note | Detail of Activity / Test - From Overlay layer to the subgrade layer
89d93505-4661-55ae-8714-0e6bb63c290f | note | Acceptance / Conformance Criteria - AP65
f80c3644-7b4a-500a-846c-da7ec67076d9 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
2cf356bb-424e-58da-a9b3-39621acfb537 | note | ○ AP65 - Clegg28%CIV
d2df96f2-59c9-51c4-adcb-eb8000380672 | note | Standard / Specification - PS- 22.13.5 Appendix XVIII
dfc101e0-35ad-52b7-9b52-161cbdc01bff | note | Verifying Document - Lab Test Report
9655aa22-de7e-5b7f-9b19-cd34af4e41a6 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
9cbe5ada-6434-56d3-bfc9-877bc2f3f315 | note | Verification Activity: Activity - H
cb47e9ec-2ca6-5164-8a6d-efe79a502e88 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5ade20a7-5118-56b9-aa50-806535d3d4bc | note | Verification Activity: By - SE
e74dbaf4-e88f-4c58-a63d-c0b8360bf296 | checkpoint | 12.8 - Manhole
41067be6-b450-5600-b6b8-dada81c5d9e1 | note | Detail of Activity / Test - Confirm the class and type as shown in the drawings, and fittings required for MH is same
0da55061-4242-5f6b-b8eb-d9c27f170319 | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
51bd6ff6-728c-5603-bc55-560ca79ab169 | note | Standard / Specification - Design Drawings 232735.02-WSP-DR-WAT
91b05c05-ae08-5326-aa68-a5380d214b8e | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019) Manhole checksheet
7e853f34-80a5-5be0-bc6c-fa150989f319 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site/ per manhole
0edb632e-80f0-513e-9071-b95245224247 | note | Verification Activity: Activity - H
5e3c7c28-13f6-5fd1-b7ac-8c45b0984ab9 | note | Hold Point (Internal)
c51128f0-42ce-583d-8684-ba1dc108c509 | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
bbc77d83-db99-573c-9926-04f606096a16 | note | Verification Activity: By - PE/SE
f2152634-0cbd-45e8-be78-b0beccca2bc6 | checkpoint | 12.9 - Installation of concrete chamber for Air Valves
f8612f62-c322-5d81-afa7-a0d818c2553c | note | Detail of Activity / Test - New 1200mmØ precast concrete
e53bfe1d-4e5b-5a65-bbf9-b467ccdbc343 | note | ○ Manhole concrete cut a hole in the base of the concrete chamber to a suitable size as to fit the pipelines.
3a578939-beae-54a5-8a57-cf3156e1ea52 | note | ○ Contractor to form hole in concrete chamber wall.
65bc2ae1-2ff2-5bb2-a114-ecc760cfbdd8 | note | ○ Hole to be sized just enough for fitting size; repaired with Sikadur 42 or equivalent non-shrink grout and 2 layers of Malthoid placed around pipe.
9afc02c9-1b75-54a2-b2c0-024e75094932 | note | Acceptance / Conformance Criteria - TYPICAL IN-LINE DN50/DN80 AIR VALVE INSTALLATION as per drawings
92d09d5d-67aa-51de-b955-2e284fefbe91 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
9c4b1bd8-070c-558c-81d8-5592253c186b | note | Verifying Document - MANHOLE CHECKSHEET
b1c88140-b50f-5d3a-8333-7808dfdb9794 | note | Testing Quantity Required (based from schedule qtys) - Per manhole
e252be6d-90a0-5117-9df0-ff56978b3d2c | note | Verification Activity: Activity - I
defd09ea-ab66-53ef-8bfa-316125b7d365 | note | Formal inspection activity to be undertaken and recorded.
4011a667-2a5d-5279-ad10-03cea4707763 | note | Verification Activity: By - ENG
2b8142a1-93ee-4928-86c4-57f78060576e | checkpoint | 12.10 - Installation of manhole vent offset in the berm
34177ccc-72b9-557e-9840-9bfff4acf2db | note | Detail of Activity / Test - 50mmØ galvanised steel vent - to be set back in berm. Location in berm to be determined on site.
cab68832-e1bf-504c-b55b-f14f286a3599 | note | Acceptance / Conformance Criteria - To be determined on site
e1fadd67-a532-5ede-8c59-8560d5ea2f30 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
5ffa1189-c6c6-511d-9ace-902f58a00cfc | note | Verifying Document - MANHOLE CHECKSHEET
fbf3ee7c-6c51-5d78-a6f0-2645ef05d468 | note | Testing Quantity Required (based from schedule qtys) - Per manhole
1a325a36-d17c-5b33-b22e-10c4a170eb96 | note | Verification Activity: Activity - I
fe414f47-7d23-5066-8848-cfd6e709d946 | note | Formal inspection activity to be undertaken and recorded.
316a55e3-338b-58ad-ab38-ae970f3356a7 | note | Verification Activity: By - SE
880f8ab8-dd13-41fe-b93a-cb88627d401e | checkpoint | 12.11 - Deep drainage sump installation
28380ab2-0320-525a-aeeb-ec5bff724a7a | note | Detail of Activity / Test - 150 x 150 x 100mm deep drainage sump fitted within DN80 PVC pipe piece 300mm long and cover grate.
64fb8cf2-6441-59c1-b151-3c194fc48540 | note | Acceptance / Conformance Criteria - As per drawings
69b3712d-3233-5bcf-a740-0b731bf6ae34 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
cdf21298-9e78-5ce7-be49-558f78398471 | note | Verifying Document - MANHOLE CHECKSHEET
d9b0dcf9-435b-5443-925e-3183af064fbb | note | Testing Quantity Required (based from schedule qtys) - Per manhole
66e1cc2b-b28d-5954-a1d0-9ec57a07127a | note | Verification Activity: Activity - I
94cf6bbe-c7de-5977-bb3b-5fd7c3a99a26 | note | Formal inspection activity to be undertaken and recorded.
211774dd-3b21-5272-b0c1-15492185a473 | note | Verification Activity: By - SE
05f40b75-e117-415b-b3b2-3e41c2b5be8b | checkpoint | 12.12 - 25MPa CONCRETE THICKENING, Corbels for the pipe entries/exiits
60c07273-00c2-5c67-a03f-3af1f79d207e | note | Detail of Activity / Test - YD12 reinforced starter bars drilled 50mm into mahole wall and epoxy fixed.
0e2738ab-0479-5d8e-95d0-47119bdd0d00 | note | Acceptance / Conformance Criteria - As per drawings
68d32412-32fa-5eba-9929-655dc316e569 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
19344eeb-ebe3-5cba-bb06-4c5f036ccfc7 | note | Verifying Document - MANHOLE CHECKSHEET
a1a4b219-4932-5b71-aee2-d6e0201e5b27 | note | Testing Quantity Required (based from schedule qtys) - Per manhole
a5636cb6-6111-5221-8f06-cee70a00d0f5 | note | Verification Activity: Activity - I
a915f41b-6c41-5a5a-9d39-15f06c85d52b | note | Formal inspection activity to be undertaken and recorded.
351844e6-d5c4-5f79-8ccf-47aad422cc31 | note | Verification Activity: By - ENG
182aee58-a6aa-47cc-ac1b-8011e8745d5c | checkpoint | 12.13 - Installation of heavy duty chamber lid and backfill of manhole
f04ba491-1c16-5f32-87f7-da692187ec36 | note | Detail of Activity / Test - Install the chamber lid onto the concrete chamber cover and frame as per the manufacturers specifications and backfill.
31bf6c65-d4f2-5d0c-ac36-cca98e095da8 | note | Acceptance / Conformance Criteria - As per drawings
5ba1ae41-155b-5620-8d3b-02476bba3029 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
aa6124a5-4307-5046-ac44-25326ff0f622 | note | Verifying Document - MANHOLE CHECKSHEET
17c26ad0-2df6-5531-8a00-4db69cdaee92 | note | Testing Quantity Required (based from schedule qtys) - Per manhole
1b5985e7-b20c-5c23-a3b4-3aafb6d34c5a | note | Verification Activity: Activity - I
0160e576-47f1-5006-b8b0-d4d82ae58b9f | note | Formal inspection activity to be undertaken and recorded.
b77cf50b-4735-5da3-9c5e-e7dc86995c05 | note | Verification Activity: By - SE
9011eb49-8d0d-4e91-a45d-26e51096afb2 | checkpoint | 12.14 - MH joints inspection
3065b9b5-ee5f-58cc-a36a-9aeb60f6c5e8 | note | Detail of Activity / Test - Inspection of joints
d0a6848d-065a-5ae3-8c0b-af4ee4d42b56 | note | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
d6893c24-0002-53e2-9831-e4ab4ffa49dd | note | Standard / Specification - PS 22.7.10
b8862640-10df-5186-a13f-75704c7ccccb | note | Verifying Document - Visual inspection
91774430-5b6f-5f8a-b8c9-f84388799f51 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
41535a08-968f-53a9-8521-10e5a0f690db | note | Verification Activity: Activity - HP
ec9b5a60-6be2-5d1a-912a-ed717f03f99c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
d9c3f2c0-efed-5bad-88a8-f2217dfe1b71 | note | Verification Activity: By - ENG
2950618c-340a-456d-9c09-fc62c94d661e | signoff | AUTHORITY HOLDPOINT
7888bafc-69b1-46b2-a243-eb0b99290643 | checkpoint | 12.15 - Inspection
cf3fad1e-5ae8-51d1-b979-c3d702626502 | note | Detail of Activity / Test - Inspection of Structure
487d234c-1879-5bd0-86ca-cf39f39713ad | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
1c2cd5a3-7116-5acf-98e2-a61d055d290a | note | Standard / Specification - PS- 21.6.11
19623920-e7f3-5aa7-9b26-a87f63ce8b5e | note | Verifying Document - Manhole Record
0b9c0b49-0011-58bd-8e6f-d5652de611b6 | note | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole
2b62be12-af54-53ec-bc97-3e612f07e051 | note | Verification Activity: Activity - I
b66880de-0f28-5c4f-af4a-8853909697d6 | note | Formal inspection activity to be undertaken and recorded.
0b93b744-31d5-5d4d-9284-16e538121fde | note | Verification Activity: By - SE
ecf4b729-b64a-452b-8d23-7c62e5e029c1 | checkpoint | 12.16 - Plumb
a8c2d8a1-9e63-5d7c-9cd2-ba4f15fe33fe | note | Detail of Activity / Test - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
bc1b5005-1c75-5fd4-ac47-406eb7d40e42 | note | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
c77f50e9-7e1b-5d00-9ce6-7a21fa9982a1 | note | Standard / Specification - PS-22.7.10
a2112bde-39d0-57cb-aaa5-7ff75a2b51cf | note | Verifying Document - Survey Data
093ff61b-32b8-54d4-8bf7-a7b1abe44dbd | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
a78c5d2a-6b3e-5cdc-999a-083cd0f58218 | note | Verification Activity: Activity - H
f47fbfb8-f870-50d3-a984-7758bd78f196 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
90e940fa-7f07-50de-b454-73140ef7172b | note | Verification Activity: By - SV
3a0c7095-ab37-45c3-8ba9-2444d1c7a53e | checkpoint | 12.17 - Step Rungs
8bf034fe-7ea6-57eb-9cf6-d867e72aef2c | note | Detail of Activity / Test - Step rungs evenly spaced at nominal 300mm vertical intervals
0e4932bd-e9fe-5fcf-b816-cda55df529f3 | note | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
44c73923-ec8c-551d-ae41-4cb011a98b63 | note | Standard / Specification - PS-22.7.11
213cec35-f96a-58d3-b463-32c6c881bd5a | note | Verifying Document - Visual inspection
fc66c199-4a62-5f84-bd4b-5ad2cbbddc3a | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
5f469e50-1b65-5427-a94f-6d869746bd02 | note | Verification Activity: Activity - H
bebe4458-2a3b-5092-9813-9f328017973f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
adf2212b-ef93-5743-a6e9-d5c69b3d26e6 | note | Verification Activity: By - SE
38662d55-be8e-426c-a03d-2430976667fd | section | 13.0 - CONSTRUCTION ACTIVITY - AIR VALVES
817735d1-fce9-40f8-b75e-d5bf63b39db5 | checkpoint | 13.1 - Valves/Fittings
4eb83b02-2d44-519e-bfa1-527f4a257906 | note | Detail of Activity / Test - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
ff9957eb-384a-571d-beec-07a5f5f0b370 | note | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. Air valve 10 & 11 is DN50 size.
a9cd84c9-8d97-5ce9-a33b-6d6c9e71f900 | note | Standard / Specification - PS-22.4.2, PS 22.5.10
f2da84ca-9fad-50f8-90ee-d2f80284501b | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
a7395ce9-8247-5ab3-9023-cf2e377ea5b6 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
e84914c4-22c2-5458-b736-4d9ad38af826 | note | Verification Activity: Activity - H
b8f7f47e-9d97-50d5-acf9-c0110a783e7b | note | Hold Point (Internal)
74981155-f22b-5327-b4fc-93cd1a226aae | note | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
f82b8621-6156-5d0a-b98a-94f35d3ad4cd | note | Verification Activity: By - PE/SE
ed2d1579-3c02-4fdb-8164-8b35bcb8813e | checkpoint | 13.2 - Installation of Isolation Valve
afba5764-6205-5611-9d8d-7b783eb30420 | note | Detail of Activity / Test - Verify installation per manufacturer’s instructions
9a497128-4191-532b-8209-b99fbcc14f7b | note | Acceptance / Conformance Criteria - Installed as per manufacturer’s instructions. Project Specifications
9fce447c-f9f0-55ad-84c6-b65eba2c4255 | note | Standard / Specification - PS-22.4.2, PS 22.5.10
8142e13c-946f-56c7-a96d-e1258f149fc9 | note | Verifying Document - Air Valve & Isolation Valve Check Sheet
feddf3fb-e283-5cf1-85f6-bba31acef728 | note | Testing Quantity Required (based from schedule qtys) - Each isolation valve
ca3b3512-2a9b-52de-8cec-77ac0613202c | note | Verification Activity: Activity - I
676c025f-e84e-5796-8fba-20f9fc7bbcad | note | Formal inspection activity to be undertaken and recorded.
911cc53e-59b7-5343-8336-c25729c287ad | note | Verification Activity: By - ENG
4380c543-76b2-4427-9fbd-7c110467d80e | checkpoint | 13.3 - Installation of Air Valve
6c983222-9f61-55a2-a347-9102ec29d798 | note | Detail of Activity / Test - Verify installation per manufacturer’s instructions
96a098fb-6701-556b-a051-f27212612959 | note | Acceptance / Conformance Criteria - Installed as per manufacturer’s instructions
bbbaa4d0-95e1-5ef0-98ac-194e80ec170c | note | Standard / Specification - PS-22.4.2, PS 22.5.10
b62efa21-9e0c-50f7-9b0e-c781f5a0e88e | note | Verifying Document - Air Valve & Isolation Valve Check Sheet
6745c687-9d51-55d5-a27b-fe18a0d221ee | note | Testing Quantity Required (based from schedule qtys) - Each air valve
777cfbbf-4b72-55b3-85c0-ad33f3e3e950 | note | Verification Activity: Activity - I
1af0b185-9132-50ae-b4ac-1bb2fb532079 | note | Formal inspection activity to be undertaken and recorded.
f880990c-ecc4-5b9a-8efe-62c156508ef6 | note | Verification Activity: By - ENG
e9d86403-0e16-468a-a257-bbdc8c55770e | section | 14.0 - CONSTRUCTION ACTIVITY - FIRE HYDRANTS
efd67d8c-0b8a-4e73-be89-163ff6321726 | checkpoint | 14.1 - Chamber Location
a218bafa-45b8-5f47-8a01-3cf8ae593b85 | note | Detail of Activity / Test - Location of fire hydrants and air valve chambers to be confirmed on site with the TCC engineer and offset as far back off the road surface as possible.
47fe4f66-8460-54aa-8687-a01647d96811 | note | Acceptance / Conformance Criteria - TCC Engineer approval
ea8d2155-8788-5ffc-9898-b6d5ac3a4175 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT) PS 22.4.2 i, PS 22.5.11
8ae81e90-bc07-5748-919c-4f467fa34ed6 | note | Verifying Document - TCC sign-off
e81f87b8-f7f9-5424-a5ff-9f75d3abe202 | note | Testing Quantity Required (based from schedule qtys) - CHECKSHEET
9fe1355c-8d2f-59d5-9927-451027fbb812 | note | Verification Activity: Activity - HP
d5906f25-3576-5d2e-ae56-5b0cdb126090 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3803eeb1-9263-5d5d-a485-ae75c55da3a4 | note | Verification Activity: By - ENG
ff97883f-08f3-4364-a735-2c3d4e9de9f8 | signoff | AUTHORITY HOLDPOINT
583cc2e1-b1a0-474b-9fd6-98d526760113 | checkpoint | 14.2 - Hydrant Surround Blocks, height to suit
2bcf809a-fdc3-5535-97e7-7b337ffc32bd | note | Detail of Activity / Test - Hydrant box with 150 x 150mm concrete surround to be finished flush with surrounding ground.
114591ef-b23b-5dc5-91fe-26d37bc9b6a7 | note | Acceptance / Conformance Criteria - Typical FH SHEET 0322
c24ce8bf-e8c7-5ef9-b2b8-b63b624c6404 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT) PS 22.4.2 i, PS 22.5.11
da678b6b-1d3d-54da-9fe8-a112355514b1 | note | Verifying Document - CHECKSHEET
6978ec4e-c43f-52e4-a355-027a3f5551b8 | note | Testing Quantity Required (based from schedule qtys) - CHECKSHEET
0a067811-945d-506e-98a1-4474e42aa0b3 | note | Verification Activity: Activity - I
30d67e68-c8c4-527b-9c63-7d1fd68be795 | note | Formal inspection activity to be undertaken and recorded.
b04a3054-ed04-5b8c-9c55-d3ffb2be45f6 | note | Verification Activity: By - ENG
13e9acad-7fd1-44d4-880e-b9359db5abd4 | checkpoint | 14.3 - Install ductile iron fire hydrant
e555dba3-7888-5fc4-bbf8-046606770670 | note | Detail of Activity / Test - Heavy duty valve box installed as per TCC's Code of Practice.
b6c5bca9-d1e3-5f64-a800-29789222994b | note | Acceptance / Conformance Criteria - CONTRACTOR TO ENSURE FLANGE
2e1cd9d9-0f52-57db-9c70-6ce35854759a | note | ○ DRILLING ON DN80 END OF REDUCER
f6dc4011-503f-5c9d-bac1-063e6eab6404 | note | ○ MATCHES FLANGE DRILLING ON DN80
75b70020-c52f-5c4b-9935-e14de8824afb | note | ○ HYDRANT RISER
b27b32f5-1202-589f-bcd4-311734ee0120 | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT) PS 22.4.2 i, PS 22.5.11
37e078f8-0467-5aa1-91ef-a5b77d00096d | note | Verifying Document - CHECKSHEET
8b90c9ef-9637-5f53-9a6d-883cc519d71e | note | Testing Quantity Required (based from schedule qtys) - CHECKSHEET
5f9ce90f-39ae-5bf1-8078-3f29578d7458 | note | Verification Activity: Activity - I
28c3cd13-013b-5607-a97f-531e0b7cd5de | note | Formal inspection activity to be undertaken and recorded.
42297a8b-98ad-5132-80fe-5cdeeaba5835 | note | Verification Activity: By - ENG
1e112c3e-b05d-4118-a5de-d3a394d3218a | checkpoint | 14.4 - Concrete Pedestal on offset bend
44097510-84b7-581a-9ba9-19d1cd4c47d9 | note | Detail of Activity / Test - 3mm rubber seat between bend and pedestal.
1d230772-5ef9-559f-8c65-3a9a4fcf6dbf | note | ○ 25MPa concrete pedestal.
3b5459b0-489f-5198-aacb-1b400747afab | note | Acceptance / Conformance Criteria - Typical FH SHEET 0322
b2a40337-a4a4-5569-a7b5-0f0494cf9b1b | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT) PS 22.4.2 i, PS 22.5.11
1d1e0349-be6b-5460-baf9-a88a02451e24 | note | Verifying Document - CHECKSHEET
d0490396-03e4-52db-93f5-4ebc1a53df5f | note | Testing Quantity Required (based from schedule qtys) - Per offset
3c662838-6d6a-5fa1-b014-6c33dc642c5c | note | Verification Activity: Activity - I
adeaae3d-6f88-5e30-b120-ef3fa52d6116 | note | Formal inspection activity to be undertaken and recorded.
321393b2-f54d-509d-bea3-5eb8e14e3eaa | note | Verification Activity: By - ENG
c7985fd9-fbbd-4a14-a237-7bb9859077bb | checkpoint | 14.5 - Anchor block and to extend past edge of concrete
841520cb-53ac-538f-bb3b-9a50bd521e73 | note | Detail of Activity / Test - DN315 - Type 1 Anchor 2000(L) x 600(W) x 2500mm deep concrete anchor block
f4f70111-8d78-569f-91ec-61d7b0a3d31d | note | Acceptance / Conformance Criteria - In accordance with project specification as per sheet 0307
083036a2-9968-5d97-9bb6-f44e92ed273b | note | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
22580e34-3403-5bb0-8980-e5d9c637598b | note | Verifying Document - Engineer Approval
938ed1a6-ff49-5522-9583-b5df719eb058 | note | Testing Quantity Required (based from schedule qtys) - SH29 Rd intersection
1ff87399-ca22-5f72-9c47-e68468d883fd | note | Verification Activity: Activity - H
ad471e09-2954-5fbe-844d-a5aae4d31bdd | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b6f01519-8099-560d-8646-b9cd081b0227 | note | Verification Activity: By - ENG
14db3b1d-9769-4831-921e-d82eb51bb60b | section | 15.0 - CONSTRUCTION ACTIVITY - PAVEMENT REINSTATEMENT
e7022409-3e73-413b-beae-c519a781be89 | checkpoint | 15.1 - Sub-basecourse layer
a8e30f32-b32a-5d73-8a0a-ba29ebeef19c | note | Detail of Activity / Test - AP65-1 is to match the exisiting granular pavement depth.
7daf5694-3e6e-5c62-b4b8-ceea73ab66cd | note | Acceptance / Conformance Criteria - Compacted in 200mm lifts. 95% NDM on Shared and Carriageway.
6e6b1fff-8096-56c0-9bd0-0cb428c1c070 | note | OR
2fbf7d59-4e8d-5786-b482-5f5e5d1b2d29 | note | ○ 35% CIV
906d24ac-1bcf-5738-8769-0130e9f8375c | note | Standard / Specification - PS 22.13.5, TCC T460, TNZ B/02 section7.6
86d8c9d8-8c0d-53a8-9c1c-393fad8e2b05 | note | Verifying Document - NDM/Clegg test result
f6e8def2-ce7e-5ec7-9919-936f54cf8abf | note | Testing Quantity Required (based from schedule qtys) - Every 50 metres
d6bc9da4-bcdc-5341-9bce-a5ff50a43b09 | note | Verification Activity: Activity - HP
6a5aef2b-a4c0-51bf-a649-7a33b13ef0d2 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
69958d33-d29b-5826-990d-c36557231cd1 | note | Verification Activity: By - ENG
7440a9e5-7ab9-4577-85fc-0ddd5c3e4be3 | signoff | AUTHORITY HOLDPOINT
da3c7a7c-5d3e-4a32-b4cb-2d1e476806b2 | checkpoint | 15.2 - Basecourse layer
3ece90db-f2fc-50c9-b31e-4fdcee84c9d2 | note | Detail of Activity / Test - AP40 (M/4) 150mm
55e2e96a-17cb-51da-949a-dee1688ae7be | note | Acceptance / Conformance Criteria - Compacted in 200mm lifts. 95% NDM on Shared and Carriageway.
12da3e93-2009-55f6-86c7-f25ee91f9d4e | note | OR
c0d45353-b740-5436-b46d-88ac1410e167 | note | ○ 35% CIV
b14f6238-19c2-5908-9108-884fd6408b7f | note | Standard / Specification - PS 22.13.5, TCC T460, TNZ B/02 section7.6
a366ad9a-ca47-50fa-bef1-3403192d372a | note | Verifying Document - Compacted in 200mm lifts. 95% NDM on Shared and Carriageway.
873ffdb8-a960-5aad-8242-dafb1974bfa1 | note | OR
c35b49e9-9512-5a10-9234-eed7cf856ba9 | note | ○ 35% CIV
298bac1e-9154-5020-896e-6cfbbfc7f645 | note | Testing Quantity Required (based from schedule qtys) - Every 50 metres
cd68331e-48d2-578b-b2c3-d0fb95e95b4b | note | Verification Activity: Activity - HP
f21c9d11-66e7-500b-8904-a09e930a934f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
cf8f976a-67b4-534b-972a-6728524e846c | note | Verification Activity: By - ENG
6691fcd2-a3af-4437-8695-75eaf6bf9ad2 | signoff | AUTHORITY HOLDPOINT
dfc6cae5-e75a-40a4-a938-d2001f2ef8b0 | checkpoint | 15.3 - Surfacing
49a32fd6-d33f-5af1-92a3-3467dbcbb5b7 | note | Detail of Activity / Test - Asphalt to match type, texture and thickness of existing surfacing
8055f28f-fa8d-5810-9c86-ccc10a378aa2 | note | Acceptance / Conformance Criteria - In accordance with TCC drawing T460
d4092f0c-d033-5747-8ff1-a7ea3f4749ce | note | Standard / Specification - PS 22.13.5, TCC T460
b399d345-afa4-5a1f-8352-eedb4d4c8ad7 | note | Verifying Document - Visual Inspection/Engineer Approval
96778085-9ddd-560a-8e35-da6c7c7b970a | note | Testing Quantity Required (based from schedule qtys) - Every 50 metres
714acbc9-c91b-5c2b-bfd9-f02fee589cf4 | note | Verification Activity: Activity - I
073e51a0-9c0a-5326-a1ee-a0456d6452c2 | note | Formal inspection activity to be undertaken and recorded.
9d594455-be85-5fc0-862c-d7e027d1bbdb | note | Verification Activity: By - ENG
734452ca-5097-4164-88e5-a0c1aad68bc7 | section | 16.0 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
a5e378d9-1fd4-4fbb-b972-6d8a5d02680b | checkpoint | 16.1 - Survey As-Builts
f862cedc-8bde-5aa7-be94-e488cb620d80 | note | Detail of Activity / Test - Quality Check on Nee pipeline and structure based on the tolerances in RITS
625a0a00-bebd-513f-9586-68df2d971d04 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
083ac30a-42c4-5f2d-b310-4b333599648c | note | Standard / Specification - Project Specifications
b71389ef-4fc6-59af-858d-f9d65562f6c1 | note | Verifying Document - Red pen markup only
28e58328-bdbd-5a13-be5e-5ce2007f8ba7 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
729ca649-af8f-534b-be99-2cbf58df91ad | note | Verification Activity: Activity - H
c7fce30b-1722-5291-b25a-504e54403e77 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
16bde5b8-6ea4-52ad-8750-20b6d96b6dd4 | note | Verification Activity: By - SE
0a70d10e-c43c-4f24-a08f-31a0408f09ef | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
77f4890d-2c0a-57a9-a3a3-8999446560c7 | textbox | Contractor's Rep Name:
18d1edd7-cfd5-5a4c-a530-d0fa09de383c | textbox | Engineer's Rep. Name:
a9b2022a-a925-58b3-af1c-76a6c24d649b | date | Date:
42c31502-9b1e-4f9b-abdf-9a498b41f021 | signoff | Add Signature
6dbbe6f0-c753-41b4-ab8d-9951ca291dda | checklist | DN1210-SP2-021-002 ITP Wetland 02 Stormwater Rev 1 | itp | DN1210-SP2-021-002 ITP Wetland 02 Stormwater
dbbcf9cb-73f8-4680-98dc-5031b1c13507 | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
078b3702-3fc4-4a3e-8bdf-92c6e7291334 | checkpoint | 1.1 - Extent of Line Setout
9e3522c4-9530-575c-af8a-600f68d8a94e | note | Detail / Activity - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Stormwater drawings.
ef736f62-a83e-5c86-9cbf-3923bd2e771e | note | ○ Identify any clashes before construction.
5fb9a0e2-d448-538d-9455-0cf26e4a1f45 | note | ○ Lot - Markup
dc61a665-3c75-5bab-b0b2-0c00d7c66320 | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
04fac5f6-f278-5dbe-a034-2ec310c50c70 | note | Standard / Specification - Design Drawings
65197d72-a146-5f0c-b49e-f8e667205a92 | note | Verifying Document - ITP Sign Off
daadf437-0305-53b6-a7ad-b728723d52d9 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
81091921-6687-576b-878e-54e6b235492f | note | Verification Activity: Activity - M
d73e478d-1af9-5d12-b6a1-d67bcd66c2d2 | note | Verification Activity: By - SE
d1a052a1-8865-436d-b733-1106d2948b03 | section | SECTION 2 – Material testing
be8986f0-dffc-467d-91cf-f96417ed5291 | checkpoint | 2.1 - Material grading: Materials (Gap65/AP65)
2b2a20c0-96ac-5491-b85e-081931c616dd | note | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
4ab4c641-084b-58f6-9892-c0abeee0c4bf | note | Acceptance / Conformance Criteria - No Particles >200mm
99dbe2ab-0d76-5fbf-95af-f1281f3dcd90 | note | ○ Maximum fines 10% passing 75micron sieve
1b0791c1-adcf-5571-a069-16e7b3d59883 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
2f644908-cf2b-593c-a02f-645d509f0652 | note | Verifying Document - IANZ Accredited Report
07b1e02f-779d-5cff-8f54-a64c985be5aa | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
2b44a22f-ebe3-5e1f-835f-4b883b066d82 | note | ○ 0-400 - 2 tests
8cd3001c-1888-50b7-a2a8-74bc4930053f | note | ○ 400-1,500 - 3 tests
f8bd935f-adb4-5449-8a59-1a6c63cf94ba | note | ○ 1,500-4,000 - 4 tests
849e7ea2-5793-507a-84bf-281d1492c574 | note | ○ >4,000 - 1 test for each additional 1,000m3
51a2583d-fc89-5426-8085-7675dca7e354 | note | — Results to Engineer 2 wks before importing
8eb03340-f3c6-53bd-bc8e-7485066b34b9 | note | Verification Activity: Activity - HP
d8d8c933-088e-5f21-88c8-9c7c5525904d | note | Verification Activity: By - ENG
cb7a88a0-1ce9-4fd9-8845-6d16fa033d10 | signoff | AUTHORITY HOLDPOINT
75848bbc-5ba8-434d-ba68-fa1a5fdd8ec8 | checkpoint | 2.2 - Weathering index: Materials (GAP65/AP65)
4b734fce-87ce-5af4-9f2f-2e85e8008e5f | note | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
95feb3fc-73eb-542a-ad74-5f8e0c35e3c2 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
7d98047a-c31d-523b-ba76-b0719afa423f | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
a583ce25-9fac-55c4-9cb6-2f1846e905bb | note | Verifying Document - IANZ Accredited Report
11ed218b-cb0e-5e8b-8e3b-447638ac66b0 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
2d622293-e159-5f1d-bc98-152b9883658f | note | ○ Results to Engineer 2 wks before importing
8918f60d-d3d2-5778-86cc-67db4c0f0402 | note | Verification Activity: Activity - HP
28dc6387-0868-5a7a-ae7b-ae0c3cafee46 | note | Verification Activity: By - ENG
12f510d3-8540-4327-bdc8-834943ba4903 | signoff | AUTHORITY HOLDPOINT
c27f0953-7118-443d-b18e-ff25d87d9753 | checkpoint | 2.3 - Crushing Resistance: Materials (GAP65/AP65)
7687a3e8-e6e5-5fd1-935f-f1dd3274aec1 | note | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
57b3e55c-b3a4-5242-98fe-dc11ac11999a | note | Acceptance / Conformance Criteria - >100KN
2a82026d-e346-5e44-8920-ec1ddc2f901a | note | Standard / Specification - Appendix XVIII, Appendix V
bf8165fa-a8d8-5e9d-8be9-608d46e3b276 | note | Verifying Document - IANZ Accredited Report
e44e63d2-87a5-5f94-ae72-78b46f546de4 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
4a024ef7-5c15-538c-8637-b320f2ac7d47 | note | ○ Results to Engineer 2 wks before importing
e2ad877d-4f5d-5601-9521-db5eff9f5cb2 | note | Verification Activity: Activity - HP
6118c99b-24e4-50da-b084-f6c47ed1eb8a | note | Verification Activity: By - ENG
5f61142a-6485-4ed1-b2ce-c99152b4f348 | signoff | AUTHORITY HOLDPOINT
5f5160e6-a4d6-40ec-8439-b18e506d3cba | checkpoint | 2.4 - Material grading: Materials (Sand/GAP20/AP20)
b612fe80-add0-52fb-be3d-877ca5e2575e | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
05cef0cd-d005-5016-a0d4-04b27239638c | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
5f0e87f8-e6da-545a-8206-95f8eebca9bc | note | 19.0mm ¦¦ 100% passing
af97483e-574e-5ede-883c-f3dbf79805e3 | note | 13.2mm ¦¦ 80-95% passing
cdd8b51b-ee44-555c-825c-68755fe9c6d2 | note | 9.5mm ¦¦ 64-76% passing
347116cf-0108-5b10-b73a-73cffeeaa4cd | note | 4.75mm ¦¦ 37-58% passing
43e2bfa0-7e9d-59c4-a045-75844b5770fe | note | 2.36mm ¦¦ 30-40% passing
09b52825-bd28-5745-863a-69cb62b8376e | note | 1.18mm ¦¦ 18-28% passing
240a3253-2dc6-52f6-8c16-e7892533f07c | note | 0.600mm ¦¦ 12-22% passing
7661fbeb-02b5-5f63-a08a-4b2b33f8aa72 | note | 0.300mm ¦¦ 6-14% passing
bb5a377f-3296-550d-8a37-912a17f0eeca | note | 0.150mm ¦¦ 2-7% passing
f65faf72-5982-50e4-8130-4ecd0fcbfe69 | note | 0.075mm ¦¦ 0-3% passing
6811a08f-0c50-5b43-a2fb-ed4cc92521a2 | note | Standard / Specification - PS-21.5.7, PS-21.7.2 Table 21.2
bdf259a6-0305-5fcb-a125-004e410a2799 | note | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
bc47324a-e9cd-55b0-a49a-f88f62586f16 | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
462ab603-c3ce-5de2-9328-b5372a73fdf2 | note | 400-1500m3 ¦¦ 3 Test
15f2132e-3eea-5a4a-9c12-207f473378b1 | note | 1500-4000m3 ¦¦ 4 Test
b5f5aca8-6b13-53fc-9996-6c5ed39dc090 | note | >4000 ¦¦ 1 Test Additional 1000m3
3ad5528b-89df-55a4-be03-a7a02d03cfe9 | note | Verification Activity: Activity - HP
530664ee-98bf-5a96-9a4b-06c3b9bc3d5d | note | Verification Activity: By - ENG
04e6b6b4-0ff3-4f00-ac48-28d3b486be74 | signoff | AUTHORITY HOLDPOINT
00492a0e-00a8-4535-b088-f46a226febe4 | checkpoint | 2.5 - Weathering index: Materials (AP20)
19849746-57e9-5ce1-9724-8c9cbea93f43 | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
43560f5c-8976-5bbd-a8b1-2d19caf86eae | note | Acceptance / Conformance Criteria - AA to CA
e833e6b7-b3e4-5dbe-b8dd-0c7924fae552 | note | Standard / Specification - PS-21.5.7, PS-21.7.2 Table 21.3
b1cb1016-5283-5c81-85db-89e6c6a3d955 | note | Verifying Document - Lab Test Report NZS 4407.3.11
f7e1cf41-cedc-5bb2-88fe-4209a0512480 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - 2 test per source
6a9c9d8a-f348-5e2c-a184-10ec3723fe71 | note | Verification Activity: Activity - HP
e80c25b4-8070-577b-a0eb-dbe8904ec02e | note | Verification Activity: By - ENG
e728a322-d7df-4e77-87fa-159a6f16481d | signoff | AUTHORITY HOLDPOINT
66492658-6e91-4beb-bc95-711dda5b8884 | checkpoint | 2.6 - Crushing Resistance: Materials (AP20)
e35b5c75-5704-5f5c-8f7e-0bbfaa096b56 | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
304f974a-2076-5c10-91ac-a1b09321d5de | note | Acceptance / Conformance Criteria - >100kN
83de34f1-fdc2-50ea-adf9-84827b966853 | note | Standard / Specification - PS-21.5.7, PS-21.7.2 Table 21.4
98d597ba-e66c-5084-b9ee-e9e06a473ab4 | note | Verifying Document - Lab Test Report NZS 4407:1991 Test.3.10
1ca86180-b4f0-5c4d-89b3-f030e7a968d9 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - 2 test per source
50c2da74-6472-5a20-8313-fb09ba78986d | note | Verification Activity: Activity - HP
0f1bdf35-6a24-56f9-9e12-2db9d4ff666a | note | Verification Activity: By - ENG
33691280-0e71-44cc-b725-aafce65769ad | signoff | AUTHORITY HOLDPOINT
5c4c2255-80d6-4d7d-a4f8-20a4201f682a | section | SECTION 3 – Material delivery
6c621872-b4e0-435d-8b85-c2a774c4715e | checkpoint | 3.1 - Material delivery - Pipe and fittings (Concrete pipe)
7ad58139-7fc4-5580-9203-1e422aa1a6c1 | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
04b19373-10d9-5360-8dc0-634d2c95103d | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
94f7aba9-9577-5cdd-95a5-d49e76b971fd | note | Standard / Specification - PS- 21.5.1, PS- 21.5.2
5bcaf68c-3bf3-581e-8b89-18c486e3e066 | note | Verifying Document - Delivery Dockets
c75b1567-be0a-5a4a-8ea7-d528bf4cda9a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
54662736-9c99-5084-a9e7-fdf26c27dce8 | note | Verification Activity: Activity - H
2baf0d0c-185c-536d-99d9-3201095a87da | note | Verification Activity: By - SE
8a58ada2-fc5a-4c7a-85d3-4571cc8b701b | checkpoint | 3.2 - Material delivery - Stormwater - Structure (SWMH, SDMH, GMH, CP, DCP, CPMH, MP, HW)
2966ab92-7f91-5883-81f6-efd2efa2196a | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the Structure are correct and in good condition.
efd31e26-6038-5903-a250-037c9990994b | note | Acceptance / Conformance Criteria - Confirm diameter and size as shown on the drawings, and that the Structure are correct and in good condition.
3c8f1b73-996a-5005-bed5-d5f0141c502d | note | Standard / Specification - PS- 21.5.4 NZS 3109:1997
e7027f00-c7ba-53d8-98ee-15c271b0a7bf | note | Verifying Document - Delivery Dockets
efb3e6cf-8bb4-5928-a0c6-cfcd79146b4d | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
ffe3f1a3-4039-54eb-8aa7-6b87b45bc96c | note | Verification Activity: Activity - H
3729bf4c-528e-5e3b-85d2-a9c4a5733fd5 | note | Verification Activity: By - SE
0f2ab4f0-ac50-422e-8a8f-adc29db41a63 | checkpoint | 3.3 - Material delivery - Granular Material (GAP20/AP20, GAP65/AP65)
6f03374c-7b5c-5d13-81cf-d9adca029094 | note | Detail / Activity - Confirm Specification and material in good condition.
45e54e36-fcda-5d07-b541-8c4064c68aa6 | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
4d657ff6-b70e-5c46-b00b-0b0e8eedc7de | note | Standard / Specification - PS-21.7.2
883b711c-1f00-5b97-83ea-9fb5deb085d0 | note | Verifying Document - Delivery Dockets
7cbd22c7-646c-5ab8-9bb9-a1fff922bbed | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
4a5e06f3-9905-53e7-b958-46e66dc3d7dd | note | Verification Activity: Activity - H
f088da79-81c5-50de-a712-fd1aea08dd02 | note | Verification Activity: By - SE
f4a6d2f2-b23d-4f4d-955a-9a6f9382f90c | checkpoint | 3.4 - Material delivery - Geotextile/Geogrid
f66f7cca-7200-5178-957e-6692c0c43be9 | note | Detail / Activity - TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
f382bdbf-b99a-569a-be82-95548f655cdd | note | Acceptance / Conformance Criteria - Minimum Strength Class C & Filter Class 1
36bbe172-2bd6-5c81-8f36-fec497212dd1 | note | Standard / Specification - PS-21.5.9
c0640c6e-3379-54fe-b477-fc7a21243f5d | note | Verifying Document - Delivery Dockets
ede4a2b6-da2a-5432-9cbb-d6b94b1fa577 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
627da0df-e41d-5dde-a229-29b0b218f2bb | note | Verification Activity: Activity - H
615bd032-b6ed-55ad-940d-cb51ca7585dd | note | Verification Activity: By - SE
c843b6c5-3762-42cf-93dc-21c7155e9787 | section | SECTION 4 – STORMWATER MANHOLE INSTALLATION
e3af017e-433f-4c3f-84fc-4e0a56b9f50d | checkpoint | 4.1 - Foundation Compliance
4d42dd98-f2d4-504b-9339-047cef2cc285 | note | Detail / Activity - On Granular or Cohesive Material
069c2588-d1be-5d67-bd31-07069f429184 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
e2e973e1-a3ec-56ac-8201-b4b5b8f8c7d5 | note | ○ Cohesive Material: Vane Shear Strength 70kPa
543e8c58-6b23-5537-8b14-82b0afd579e3 | note | Standard / Specification - Appendix V Table 21:11
f7ab88fa-e9a2-598b-8ec7-0bf90da344f2 | note | Verifying Document - Shear vane or Scala test result
93594ffa-0319-5f0c-9169-b372ee39616a | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
1a7f729c-d091-54e9-a788-e08574be5ecd | note | Verification Activity: Activity - W
ef74728e-c468-571c-8362-cd458b6e3bc7 | note | Verification Activity: By - SE
386ece04-d721-4bb6-ae6a-7756ab25aa8e | checkpoint | 4.2 - Undercut Approval
814789ca-7310-52ec-b231-ee18d2da3018 | note | Detail / Activity - On Subgrade
e1fe580d-57b5-5fc1-8f02-1233f72fdf3c | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
49ba0ccd-7172-54f6-a169-37b795c9674e | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
1b3c28e9-738e-5595-99c1-e0a76b672ce5 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
6f662a59-d055-5a16-875f-5e4cf488b62f | note | Standard / Specification - Table 21.5
47b94ef1-1ce4-5281-9593-f08f18e437e3 | note | Verifying Document - Lab Test Report
2c1ba65e-09e2-55f0-9737-f1eaf8ef3782 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
c58d5b87-579f-5fb1-8015-9bceddaf5e3e | note | Verification Activity: Activity - HP
6fb2b07e-e063-5afe-b055-56ac807e5010 | note | Verification Activity: By - ENG
5d4eba79-6e35-4d01-af54-6db87a2dd553 | signoff | AUTHORITY HOLDPOINT
f3f956d2-d88b-4331-9ccd-08a2b71ea45a | checkpoint | 4.3 - Undercut Backfill Compliance
a823978f-055e-5d8e-8bb2-4be2b7ca29c5 | note | Detail / Activity - On Granular Material
77013382-fb8a-5cda-a43a-d280369cda39 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
d247d2de-d399-5a53-9b77-7d33b538c3e3 | note | OR
6c1d45c8-7c29-5e8a-bf41-3ee83a983452 | note | ○ Clegg 25% CIV
fc54eecd-2cc5-50dd-9f60-d90186d1649a | note | Standard / Specification - PS- 16.5.12
8c5c1880-b109-599d-bff5-8f37131cf597 | note | Verifying Document - Lab Test Report
c9e1166f-b6a0-585c-9f44-571c977917b1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
28d741e8-fb57-57dc-a4b0-ebe4986928bb | note | Verification Activity: Activity - H
bc54c7be-61c8-52b6-9f0f-534d334bb1e1 | note | Verification Activity: By - SE
2f22d599-7ac7-47eb-bffe-73d5546c3d11 | checkpoint | 4.4 - Bedding Compaction Testing
d827e3b4-12cc-5f4d-bc22-0568352292c5 | note | Detail / Activity - On Granular Material
ddfb55c9-d8fe-5a0b-ab58-0c19ada86dfa | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
35cf59a2-007f-5f50-b4bb-baa4aa17d2e9 | note | OR
58b0093c-85ef-5901-9ab6-3fb337b3b0a0 | note | ○ Clegg 25% CIV
eb040854-e0e0-53f5-b911-8f17481ef61d | note | Standard / Specification - PS- 16.5.12, PS- 21.6.11
3cdae59b-508f-52ab-96dd-d8adf44148d6 | note | Verifying Document - Lab Test Report
12b1d5f5-7431-5538-a289-d705ee33b2c6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
b51fc6f7-a6a2-5dbf-9d48-1788c9080c3d | note | Verification Activity: Activity - H
d70c5b03-3dea-5c88-a74b-96c4ea81e2a1 | note | Verification Activity: By - SE
8e080cc5-9afb-4cdb-8be6-df774c7533b2 | checkpoint | 4.5 - Survey
f111d001-521c-5e15-a8bd-11d9c7ee7442 | note | Detail / Activity - Inspection of Structure
48495970-a5c1-5b30-8ead-9728bad7a12a | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
8000a76e-c8f4-513c-8ca2-445694279f34 | note | Standard / Specification - PS- 21.7.6
0529f656-4646-599d-9e48-ca6a13404fb4 | note | Verifying Document - Survey Data
d0dd7abb-94f5-5328-9473-c9c3d566bbf6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
6da1c556-fe83-5987-93d9-8e729b7afd0c | note | Verification Activity: Activity - H
613e017a-76cc-5008-b811-0143fc5b9929 | note | Verification Activity: By - SV
051ff30c-2946-4f54-b9a0-a37217dceafc | checkpoint | 4.6 - Sidefill Compaction Testing
47a2479b-4001-5489-9a19-1f392c2b64f9 | note | Detail / Activity - From the bedding layer to the overlay layer of pipe.
788d5489-c3cc-5096-a0cd-ac5aeddfe21c | note | Acceptance / Conformance Criteria - AP20/GAP20
8ea4d508-15fe-5833-85a3-2618ce9332f2 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
56e5f018-c6f6-5ec2-a6fb-1f2a12455439 | note | OR
d5e7f82f-74a4-5fc8-8c9b-9b169fbfa118 | note | ○ GAP20-Clegg12% CIV
b8cc20a0-bdad-52f7-bac0-19b49300dc6c | note | Standard / Specification - PS- Table 21.12
3270bd61-bb5b-5ef1-b249-b9f9b6d28323 | note | Verifying Document - Lab Test Report
7512d96b-f89a-5d4f-9116-66759bb66bf0 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
fee7b1f8-cd7c-59a5-b3e5-b1d2bcb78036 | note | Verification Activity: Activity - H
1368d8ca-80a2-5df5-8cb5-0fd8d45842b3 | note | Verification Activity: By - SE
ebb3a363-6b0c-4e3d-b512-eab70fca7069 | checkpoint | 4.7 - Backfill Compaction Testing
9f1f9fb1-6dda-52bd-bab6-3b57678b7ed9 | note | Detail / Activity - From Overlay layer to the subgrade layer
8bee0beb-fdb7-5887-8ff1-ca37bcbcedb2 | note | Acceptance / Conformance Criteria - AP65
25d73b4c-982f-58ca-9345-f94eb11f0507 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
e779616c-bb6d-5891-85fb-3b4ae4b06fd0 | note | ○ AP65-Clegg28%CIV
db8a620e-f13b-5f8e-95d8-d6fe506856d4 | note | Standard / Specification - PS- 16.5.12
57f02e86-8c36-50ad-81fc-9f95769e9aaf | note | Verifying Document - Lab Test Report
9be19ca9-87b8-5825-884c-c2e04de16c90 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
b8c08e25-b7dc-5513-9717-28e2130a5cc4 | note | Verification Activity: Activity - H
3a7a331b-5443-51e0-9299-bfec677d71fb | note | Verification Activity: By - SE
2528eb67-10ef-4daf-93ff-e6bca88d7d50 | checkpoint | 4.8 - Inspection
e085fa25-5a9c-51b5-9a0b-6fb95b420fd6 | note | Detail / Activity - Inspection of Structure
a17a1172-a885-5d67-948f-993b883e6d32 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
d912edec-7b32-5901-852f-59ed0503a946 | note | Standard / Specification - PS- 21.6.11
f34c6108-0d8a-549c-9e44-6ed359f97361 | note | Verifying Document - Manhole/Catchpit Record
564bb9e2-4b8b-5cfb-bb7f-7862eea2b212 | note | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
88b6f18d-b621-5329-bf68-3ba407f5b54c | note | Verification Activity: Activity - I
86c085dc-dc04-59e5-8106-945c703a490e | note | Verification Activity: By - SE
db6436d4-e90d-495d-9ee7-7257c5ff8043 | section | SECTION 5 - STORMATER STEEL REINFORCED CONCRETE PIPELINE CONSTRUCTION
73d81093-4b41-473c-a869-7c2ca5812385 | checkpoint | 5.1 - Foundation Compliance
17bc6aee-55b1-5be1-8c7c-73181d25f53f | note | Detail / Activity - On Granular or Cohesive Material
9ecc147f-bae6-53a4-9248-e3d2b55954b1 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
48eb4f4a-a90e-5fec-9b0a-dc2cfcf586c4 | note | ○ Cohesive Material: Vane Shear Strength 70kPa
fbf6ebc4-d52f-5b57-8314-47895213f346 | note | Standard / Specification - Appendix V Table 21:11
a1b2050f-360a-5be0-a09b-f96ce21391f6 | note | Verifying Document - Shear vane or Scala test result
56a2570d-06eb-58f8-9a79-5f79d9fa5a07 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
9688d486-2fd2-5a07-978f-af2098541e86 | note | ○ 0-5m: 1 Tests
194ba068-c0ad-54d5-a311-adb99f85e0fa | note | ○ 0m-10m: 2 Tests
162091a9-e878-5bab-992c-d552578f3566 | note | ○ 0m-20m: 3 Tests
f4f0c948-d957-551b-915d-3327ebd1bc24 | note | ○ 0m-50m: 4 Test
c04e1f5b-ba46-56d6-bf82-226b25587a27 | note | Verification Activity: Activity - W
736dce7d-97ab-5e06-b25c-8e23a2acae5f | note | Verification Activity: By - ENG
459909a1-d900-469f-9926-a576fdebd352 | checkpoint | 5.2 - Undercut Approval
e7982689-9bc6-59b8-ad2b-5b76dc5f6c3c | note | Detail / Activity - On Subgrade
c6f73eba-6e88-5a8d-9c36-42deeb6b48be | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
408f1f24-a9ce-5d7b-b22d-e1885e7185d3 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
810a1f14-612b-5ff9-b651-a0a194ba2d4c | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
bdbf7785-db78-528b-a5f5-fac01186df6b | note | Standard / Specification - Table 21.5
168c55c1-b7bb-58e9-ad26-7919db32118f | note | Verifying Document - Lab Test Report
32d8defd-1e98-5cf1-b10a-517b83efa402 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
fc156ec6-b111-599c-b0d1-e0987e7a3737 | note | Verification Activity: Activity - HP
31c49d99-2755-56c6-8769-1a183d7c9c3b | note | Verification Activity: By - ENG
b2d90f10-8600-4690-b93b-df3345bd57a0 | signoff | AUTHORITY HOLDPOINT
41f8a066-aa02-460a-a703-55cd2e4db967 | checkpoint | 5.3 - Undercut Backfill Compliance
cb69efca-16fd-579b-a904-eb5daf21647d | note | Detail / Activity - On Granular Material
c12974c4-7f04-50e1-bbbe-e883f3fde2bf | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
83bb5b47-84d9-5687-962f-4f5f4d6220bc | note | OR
18ee78c2-a076-5887-bedd-ac254f260d07 | note | ○ Clegg 25% CIV
de3b3c7c-1835-5995-b84c-42515de0c1f2 | note | Standard / Specification - PS- 16.5.12
d533984b-bb8f-59bf-b36b-8d845f7ffef3 | note | Verifying Document - Lab Test Report
f2afd4dd-477c-53dc-97e5-91d97bf96a51 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
5ed52ab2-a65c-5c55-b9ae-b90ba22cf28c | note | ○ 0-5m: 1 Tests
e096f26b-3da1-5834-9a72-1749205960a1 | note | ○ 0m-10m: 2 Tests
40e11103-8e09-515d-a99b-2452ed39f065 | note | ○ 0m-20m: 3 Tests
e07015ea-6b7a-5300-81b1-39364d04327d | note | ○ 0m-50m: 4 Test
06f8d059-e385-5b94-856a-160a6020b636 | note | Verification Activity: Activity - H
3aa65be2-15d0-5a88-bfdd-b7f01b8122a4 | note | Verification Activity: By - SE
3225f5d2-41bf-4e42-8ff2-dd0430425751 | checkpoint | 5.4 - Bedding Compaction Testing
cd975290-9726-5bb5-acdf-17d034768b26 | note | Detail / Activity - On Granular Material
3b01c70e-55f7-5fe5-8b3e-1eb288875c81 | note | Acceptance / Conformance Criteria - HS2- 100mm if D<1500 or 150mm if D>1500
e7fbcf7d-3ac0-54f1-b8bc-7d113dbe6a4e | note | ○ Minimum Compaction- Trafficable & Non-Trafficable 95% MDD on metal.
18c7aadf-7c22-5571-a4c9-6b9dff32a655 | note | Or
5a322980-3519-5e5a-a5cf-391197572dc7 | note | ○ Clegg 12% CIV
b01f45ad-eac2-5ffb-99d9-0b4443167d61 | note | Standard / Specification - PS- Table 21.6, PS- Table 21.12
64452eb0-3444-5c68-a73c-7a814b828d47 | note | Verifying Document - Lab Test Report
fb374028-712b-555b-89e8-2de9a98bd462 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
e6e4583e-fc32-529c-ac80-18cb287e1005 | note | ○ 0-5m: 1 Tests
75eb8e5e-febd-51d1-8831-07d2cca84c28 | note | ○ 0m-10m: 2 Tests
30e57c8e-0f41-5350-b3ef-2f1f9e49ab5a | note | ○ 0m-20m: 3 Tests
a0ae5850-c477-56ec-b539-89b83c454bbe | note | ○ 0m-50m: 4 Test
613879c2-b3c3-5b7e-bdcc-4f5c0855f62c | note | Verification Activity: Activity - H
f4b18ee3-1792-519f-a3d4-37f05ac83cdc | note | Verification Activity: By - SE
ca9aa94b-894e-4fd9-be67-e38f17e663ec | checkpoint | 5.5 - Survey
c2e6813c-12e7-50a6-a884-2080cc2787db | note | Detail / Activity - Surveyor to Setout
e641858b-3939-5bb8-9093-5a5bb391d2c8 | note | Acceptance / Conformance Criteria - Vertical design Setout:
a9d583f1-e94f-5b8c-994e-0dbf68f26a14 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
251ec884-a857-5583-b9b3-6dd076943b80 | note | ○ Pipes > 1% grade: +/- 20mm variance
59bcfec8-1cf2-5a43-897a-0617303f5bfb | note | Horizontal design Setout:
ba7efbc4-621d-5762-b227-8a67632929de | note | ○ +/-30mm variance
d2c801b7-63bf-5a75-a518-4ed9ed009418 | note | Standard / Specification - PS- 21.7.6 Table 21.15
13e7083b-0ca6-59c7-80ac-6ecc7680b5e8 | note | Verifying Document - Survey Data
4349907c-dd35-5cc4-92b3-61ab8118ceca | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
8f1a5fe8-c4fc-5c07-aebf-e8dcc96309f8 | note | Verification Activity: Activity - H
4397fa0d-a121-5c57-b3ca-d3298cea3d94 | note | Verification Activity: By - SV
8290f000-6346-4db1-bc33-19f728fd5d5a | checkpoint | 5.6 - Inspection
f1825702-fb59-5d56-b93e-b7ca8e876e2c | note | Detail / Activity - Inspection of Drainage line
0c3c6459-20ef-5fe7-b1df-b41b81fa0f95 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
d9fdbecc-93e3-588e-bb0a-c841f4a7e6d6 | note | Standard / Specification - PS- 21.7.6
b2259944-28cb-52cd-80b2-563496aaa090 | note | Verifying Document - Drainage line record
47438a8b-3adc-5f17-814f-f13eac1f7e28 | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
a57e76b5-083f-5358-a12b-294dbe08fdd7 | note | Verification Activity: Activity - I
15ced546-e0a6-5cc3-ade9-33a4bb3bb11c | note | Verification Activity: By - SE
e5493cb3-3170-4263-a34c-a5b674dfb264 | checkpoint | 5.7 - Haunch Zone Compaction Testing
d2549c59-cef3-5150-879c-49d66ec8018d | note | Detail / Activity - On Granular Material
7564411f-a789-5f13-bf8b-13ce33f32f25 | note | Acceptance / Conformance Criteria - HS2- 0.3xD (outer dia of the pipe)
bea71e38-2ce6-5a02-aea6-dff1e6fccb4c | note | ○ Minimum Compaction- Trafficable & Non-Trafficable 95% MDD on metal.
7fddd042-8a3c-5b5d-97f5-1f08bc8e27c8 | note | Or
ff427f6b-a02e-5cb3-9152-806ca1c5eb6e | note | ○ Clegg 12% CIV
fa638c42-64fb-5ea3-a901-dfab0d4cf9b8 | note | Standard / Specification - PS- Table 21.6, PS- Table 21.12
fb53c994-61b5-557b-bc8c-252c9f9a9829 | note | Verifying Document - Lab Test Report
9b458bcc-e969-54d0-919c-3a7c18172f6d | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
21c2ab6e-3814-5342-976b-086705bb6fef | note | ○ 0-5m: 1 Tests
d4906700-f12a-5384-b50c-8ef412c3d643 | note | ○ 0m-10m: 2 Tests
dfdfe0c8-e616-59b6-960c-1c36eb6347b1 | note | ○ 0m-20m: 3 Tests
b5177991-1700-5bf6-9f87-226cc587976d | note | ○ 0m-50m: 4 Test
57ec9231-d25d-5c72-8487-7be5f1dade98 | note | Verification Activity: Activity - H
35d62894-8b3f-5fe9-a1ca-a347b8a19402 | note | Verification Activity: By - SE
7b843ad6-fdee-4c56-bac9-84d2683c0ba2 | checkpoint | 5.8 - Side Zone Compaction Testing
91d66160-1d03-5f13-aaae-44c651802194 | note | Detail / Activity - On Granular Material
5cad0cb5-ccd9-5bba-8f91-e916d7d551c1 | note | Acceptance / Conformance Criteria - HS2- 0.3xD (outer dia of the pipe)
2c814a71-f3be-5fc8-9a3c-093f55ba62f5 | note | ○ Minimum Compaction- Trafficable & Non-Trafficable 95% MDD on metal.
660a8379-28c3-5aab-b5cf-43d7d3260e39 | note | Or
c4745dfc-60ff-546c-90ef-72f475ac659f | note | ○ Clegg 12% CIV
c9a77a92-747c-5980-ba67-812567ad968f | note | Standard / Specification - PS- Table 21.6, PS- Table 21.12
83bbe841-0219-5e2c-8ca2-6c0a25b4126e | note | Verifying Document - Lab Test Report
ddcfa0c9-f250-5da3-823e-908d343c75c8 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
75245a24-6b69-5ff4-a3aa-c725358f6efb | note | ○ 0-5m: 1 Tests
72363690-cbaf-5641-9b45-420822a05a60 | note | ○ 0m-10m: 2 Tests
38977187-735c-5ab7-b251-56cf98929396 | note | ○ 0m-20m: 3 Tests
a91eaec2-380a-5002-b660-3b74686ba4a5 | note | ○ 0m-50m: 4 Test
50adfd6e-1bcc-5735-a9cf-26a2649b81a7 | note | Verification Activity: Activity - H
28941491-0343-5f66-a4f2-d6dffad14778 | note | Verification Activity: By - SE
e1a5e463-1d29-47a5-aabc-a9d6f5ee3bf1 | checkpoint | 5.9 - Overlay Zone Compaction Testing
a3ea6850-a622-5d1f-aacd-eb4d9683f316 | note | Detail / Activity - On Granular Material
fc80f3ca-a144-55e6-9379-540d7f833699 | note | Acceptance / Conformance Criteria - Minimum Compaction- Trafficable & Non-Trafficable 95% MDD on metal.
783992d4-eb64-56ac-ac5c-89c54173c808 | note | Or
fcaf7080-ed97-5c56-a068-05c4759979d1 | note | ○ Clegg 12% CIV
9d68796b-7c12-57e3-bcc2-ed84a7a546a9 | note | Standard / Specification - PS- Table 21.12
72e454fe-d8a1-5a02-be15-19f5f3e31dc3 | note | Verifying Document - Lab Test Report
59e3b208-89e5-5e27-b8f9-83b1b9df3aa5 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
c10101ad-a6ae-5ae5-a6f2-04619132bc77 | note | ○ 0-5m: 1 Tests
c86098b6-822a-595d-92b9-ea727e52800d | note | ○ 0m-10m: 2 Tests
e17a97dd-b502-54c3-bb70-806cc2fab00b | note | ○ 0m-20m: 3 Tests
e83fc6b5-8e10-5330-ab57-34917ece1f91 | note | ○ 0m-50m: 4 Test
10d2d68d-6ca7-5daa-b475-760b8ce83370 | note | Verification Activity: Activity - H
1eef8a62-19c3-593b-b775-22df5b049050 | note | Verification Activity: By - SE
9898ca9f-fad6-4b09-8413-f75332d3ed24 | checkpoint | 5.10 - Backfill Compaction Testing
08844a6d-366e-507c-aebc-b840a5debb6c | note | Detail / Activity - On Granular or Cohesive Material
aafab661-d639-5d29-bbf3-537aa6bab601 | note | Acceptance / Conformance Criteria - AP65
86d1f609-f930-5ae4-bba8-38e688683853 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
f0136911-c2df-58e4-909e-04babfe1f55b | note | OR
75247706-91e0-5853-a29f-810725ca9d14 | note | ○ Clegg 28% CIV
22571007-e410-5191-aa06-4e7cfbef70a4 | note | Standard / Specification - PS- 16.5.12
14d856ac-b2be-50a9-8ffa-a35c0084fcf4 | note | Verifying Document - Lab Test Report
15458904-fa78-5874-a70e-9ff1f854d779 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
682eb9c7-3b20-59b2-902c-2177ff76c132 | note | ○ 0-5m: 1 Tests
68055488-9094-5026-9f6d-d6dd10d7d318 | note | ○ 0m-10m: 2 Tests
bd752870-9212-52b3-b281-8431723b51af | note | ○ 0m-20m: 3 Tests
971ee842-4d34-5b0a-aaf7-21ebcec9ca2a | note | ○ 0m-50m: 4 Test
eac833cf-0456-5803-9f8b-10a3ac338b27 | note | Verification Activity: Activity - H
7010cb51-9683-5e91-8aff-332048c3d229 | note | Verification Activity: By - SE
f47daa6d-e596-442d-94c6-c9ce1e5aa636 | checkpoint | 5.11 - Backfill Compaction Testing (Site Won Material)
321700f1-3d7a-5e37-bca1-14ebec7d3c80 | note | Detail / Activity - Site on material use as backfill
2ca42a65-0c7f-5dc0-9d7f-842c3e5a26ce | note | Acceptance / Conformance Criteria - Site won material
afd355a6-d503-59f8-af29-dbed1afe3a81 | note | ○ Testing to be completed on maximum 200mm lifts of backfill
6d6a7f8e-863a-5723-8c01-99b01c239f29 | note | ○ Shear vane:
3beb72d3-0cd2-55ce-b4d7-bef153cd7e27 | note | >60Kpa minimum
f8ca7fc7-5212-5a12-a0a4-e6b221715485 | note | >80Kpa average
5e05ef5f-687a-52cf-8a85-f3c049d5a990 | note | Standard / Specification - GCO-490
dba00ddd-1ac7-546d-8660-7c732fa69d68 | note | Verifying Document - Lab Test Report
8043548d-0af0-54d2-ba18-1a1ce7d5dddd | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
002de94f-ffa7-5fbd-86bc-e7af2c3626cd | note | ○ 0-5m: 1 Tests
b00977b5-fedd-56e1-b883-7868388cf3b3 | note | ○ 0m-10m: 2 Tests
0bf639b6-4f78-5b2a-b293-b290a8db1188 | note | ○ 0m-20m: 3 Tests
1cbf3f64-3b81-5724-846a-296f1f15b1ca | note | ○ 0m-50m: 4 Test
b3500a41-3276-5345-8060-41689cd0c135 | note | Verification Activity: Activity - HP
021dd43b-dd08-5aac-ad10-ec635bea804d | note | Verification Activity: By - ENG
bb3a4893-03f5-4398-908c-13ce4ae6d29a | signoff | AUTHORITY HOLDPOINT
47a631ac-f41a-471e-8fc4-cb955248e9c3 | section | SECTION 6 - CCTV
3acf2525-11ec-4881-88ee-b36a3327a8dc | checkpoint | 6.1 - CCTV Inspection
4b900dc6-fe71-5812-aaf6-02a36adfb8bb | note | Detail / Activity - CCTV stormwater pipes at completion of trench backfill but prior to final surfacing (pavements, etc.)
58b96f3e-93e3-59e4-87fe-7fc08a99f64b | note | Acceptance / Conformance Criteria - Every stormwater pipeline 225mm diameter or greater.
daa80066-2685-5867-9280-2afc41baaa2f | note | Standard / Specification - PS- 21.7.6, PS- 21.7.8
228efba5-4698-5c3d-b79e-ea29645a9f5f | note | Verifying Document - CCTV Report
bf8bc320-c3b9-58af-9f76-06c5a734de02 | note | Testing Quantity Required (based from schedule qtys) - 1 per line
186c3462-b9e4-56e6-8f17-1ddb485154aa | note | Verification Activity: Activity - S
beeaebae-a0d4-511f-968c-0a48d0d930a0 | note | Verification Activity: By - SE
b58f1ce0-15f7-4683-8bcd-0ab1ad6f83ba | section | SECTION 7 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
c9a74455-d725-40ca-b2b5-64f6c4a654c9 | checkpoint | 7.1 - As-Builts / Redpen markups
b7f366d4-f311-55d3-b16e-b4330ea90e3d | note | Detail / Activity - Quality Check on New Works based on the tolerances in RITS
b6a06a5f-65a6-5f0a-9ef2-b6a0385bc666 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
75a2fcc0-2373-5a2b-9c6c-75e1dac14930 | note | Standard / Specification - Project Specifications PS 21.7.7
07c58fdd-26de-51c7-916b-723b05b6a43d | note | Verifying Document - Red pen markup only
7eeaa659-c39b-51ce-bf47-ac70287a00e3 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
de52effe-0f84-583e-81ac-62aa6ddb6dda | note | Verification Activity: Activity - H
d2bcca84-967f-5b6c-97e7-3d3ecdde71c4 | note | Verification Activity: By - SE
9885d06b-7188-4670-a6b3-4dcf857e8c7b | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
285a7eb4-ac4b-5725-a43b-3ad9f31bdb4f | textbox | Contractor's Rep Name:
eebbace2-f9eb-50bc-8a1d-433c4a5519ac | textbox | Engineer's Rep. Name:
fb099eb4-ab5b-53c5-8ca7-9877ff7f4b92 | date | Date:
8d9b09cb-ec0a-41d6-b618-57222910c3e3 | signoff | Add Signature
5093aea8-96f3-4fb3-bde3-c6414263633c | checklist | DN1210-SP2-030-002 ITP Wastewater Pressure Testing Rev 1 | itp | DN1210-SP2-030-002 ITP Wastewater Pressure Testing
03ae4de7-daa1-4285-b407-1e692c38669d | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL , PERSONNEL & THIRD PARTY APPROVALS (P&G / ESTABLISHMENT)
50c5346b-6495-4a1a-9582-ccf3ef1261e1 | checkpoint | 3.1 - Work method statement
191f7eaf-d184-55ef-8d67-cf1be9802654 | note | Detail / Activity - Provide the Engineer with a detailed work method statement (WMS) with details of how the pressure testing will be carried out at least 10 Working Days prior to the test
ab8e8836-fc42-59e8-93fa-09dba318e0c1 | note | Acceptance / Conformance Criteria - WSP sign off
464abca3-887a-510b-84a2-3e10925edc26 | note | Standard / Specification - PS: 22.7.12 d)
99aa9840-fd0c-591e-97c1-6c06465e12ef | note | Verifying Document - Ineight approval
24be8c75-fe16-587a-9eca-558ee21d6de7 | note | Testing Quantity Required (based from schedule qtys) - Pre aproval
78aa505e-e852-518e-8148-849dad508444 | note | Verification Activity: Activity - HP
efe15101-99a0-5b4f-baf6-858e2494758b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
bd38e4c4-a740-5b0c-8e8b-f9d2432e7dec | note | Verification Activity: By - ENG
2524731b-b085-4ca8-9b16-89032120eb1f | signoff | AUTHORITY HOLDPOINT
1b447120-f983-4ba3-832d-75adbaa8aef9 | checkpoint | 3.2 - Witnessing of Pressure Testing
a467aec7-71dc-57ec-8044-c31bc6cf5265 | note | Detail / Activity - Pressure testing will be carried out at least 10 Working Days prior to the test
4e0d8d36-887d-5f33-aea7-0f975d68dc6c | note | Acceptance / Conformance Criteria - On site
49b5a83a-1b61-558b-aaea-9289e08ccf65 | note | Standard / Specification - PS: 22.7.12 b)
e9433ae8-bc46-56b1-b82b-aa91ab67898a | note | Verifying Document - Email
7252517c-76c7-5956-acae-f360d8527272 | note | Testing Quantity Required (based from schedule qtys) - All Testing
f3f78061-6e25-5160-b02c-52e2ea7cda53 | note | Verification Activity: Activity - HP
69fa6284-544e-5549-ad57-8a1c2f28a5ff | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
2d0f22f9-63df-5b93-a5e4-1774937bfc98 | note | Verification Activity: By - ENG
2758143a-b890-4dda-af26-e688db3c81e3 | signoff | AUTHORITY HOLDPOINT
90af0501-75b8-4b06-b813-fbea9084af64 | section | SECTION 4 – CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE TESTING
3a755ae3-2881-4065-9293-813e82436291 | checkpoint | 4.1 - Pressure Acceptance Testing
7c05669a-160e-5be6-a257-2406c42eab7b | note | Detail / Activity - Backfill/cover with embedment before testing.
979f33e0-8a45-5005-8119-a2fba80d2169 | note | ○ Complete pressure acceptance template.
b4a00837-f4ef-5fac-b252-aa0b33f87565 | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
6a661299-7105-5d4f-83e4-04b888efb136 | note | Acceptance / Conformance Criteria - Wastewater Rising Main Pipelines – 800kPa
ab7b3bb0-845b-51ab-ac6d-f0c69a927cf5 | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
f8c5f157-fa49-5f86-be55-bbd9c93491f2 | note | ○ Complete pressure acceptance template.
90097e52-9b82-5a34-a9e8-db1b428e1730 | note | Standard / Specification - PS 22.7.12 d), PS 22.7.13 b), Appendix XXI
1fced81c-b651-5fbd-a3a9-ef4f59a44fb4 | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
a2d33061-3289-5cde-83c0-d9875b3a49d7 | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
c126653e-6420-5993-810e-47cace3bd128 | note | Verification Activity: Activity - HP
e67fa501-e7f9-588a-be3d-4191caf1be00 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
037c5c40-689a-5f05-b1be-2be07877233e | note | Verification Activity: By - ENG
45d121e1-260e-469a-814f-7b61b26f9255 | signoff | AUTHORITY HOLDPOINT
40b33b51-ea60-4015-b293-748ad02b71fb | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
2cd89ce9-60d0-5b59-ac83-05b1d0565fa9 | textbox | Contractor's Rep Name:
4e365c71-5d2a-5ebe-b617-da13c88b98fb | textbox | Engineer's Rep. Name:
0e374cc4-87c6-53e7-a425-616c53a285b4 | date | Date:
0e769ee2-2789-4176-abd7-c4fd9fa73e16 | signoff | Add Signature
7e6ed34b-a1e5-462c-895f-ae84beb77d4d | checklist | DN1210-SP2-033-001 ITP Landscaping Rev 0 | itp | DN1210-SP2-033-001 ITP Landscaping
f8a493de-873d-4918-926e-65012885f520 | section | SECTION 3 – PRODUCT DATA SHEETS FOR ENGINEERS APPROVALS
c549cc9e-4352-4641-ae1d-3c2a279a43c3 | checkpoint | 3.1 - Landscape Methodology
31ce99a0-166a-5ace-a858-c04ea770ac34 | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Landscape including, testing, inspection and hold points for review and approval prior to works.
1c409c77-8355-56f2-a65a-160680148ade | note | Acceptance / Conformance Criteria - Engineers Approval
3b630366-7383-5497-ab8f-71d0008879dc | note | Standard / Specification - Appendix V
07ac4ad1-2b2a-5f26-a0f7-58cac30efc6e | note | Verifying Document - Approved Methodology
11a12535-edb4-5e4e-888e-49a7593163cd | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
3c584b29-091f-5f2e-942a-33e8cdcee9df | note | Verification Activity: Activity - HP
c1349cb4-2aeb-5fd2-8e68-287dfc7d83ca | note | Verification Activity: By - ENG
d4a8e2ba-f058-49cb-beb7-d284ec0b7cc6 | signoff | AUTHORITY HOLDPOINT
c2eb2d59-8041-4423-867d-3c4a1325aaa9 | checkpoint | 3.2 - Geotextile Fabric
f92aa35b-b09c-53b7-bde6-5aa7ad6b6672 | note | Detail - Geotextile fabric approval
1c515ec3-a26e-5ddf-9acf-74f6c98d9eef | note | Acceptance / Conformance Criteria - Class D geotextile fabric
54047d33-988a-5521-9f9b-873d2ed5a34a | note | Standard / Specification - PS 21.5.15
be73d981-fcbf-5f7c-b365-68c0986a232d | note | Verifying Document - Data sheet, Delivery Docket
bf879d56-3a0f-5102-8c45-2b28e23e9cb0 | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
d9d7e991-68a2-55b5-bdc2-91e7491ea045 | note | Verification Activity: Activity - HP
0b837387-1702-5b3a-9b0f-c8c98f83c02b | note | Verification Activity: By - ENG
f5fc7acb-29f4-44b7-a92f-2dc338cfca3d | signoff | AUTHORITY HOLDPOINT
a490a102-8935-41c0-ba9a-ce678be2e670 | checkpoint | 3.3 - Topsoil Analysis
8bdcbdff-b5c8-5634-9f8e-56fb67ff636b | note | Detail - Testing of on-site and imported topsoil for quality.
232337e2-3982-51d6-90f0-a62fca2069a3 | note | Acceptance / Conformance Criteria - Topsoil must meet the criteria specified in the project standards.
72b8bc63-eb8e-55e7-a5ed-3f23363a9846 | note | Standard / Specification - NZTA P39: 2013, Section F
90302c1b-6687-5d3f-8edb-1d1756d802a0 | note | Verifying Document - Soil Testing Report
66e6b74d-a5d9-571d-827e-1e4343c829f7 | note | Testing Quantity Required (based from schedule qtys) - Once per source
6a03ac2a-140d-5496-84c3-ecdb98824535 | note | Verification Activity: Activity - HP
ff0a838b-20dc-51ea-977e-f27b2b3bdf00 | note | Verification Activity: By - SE
0edc3188-3992-40dc-b909-b4bebf9f7744 | signoff | AUTHORITY HOLDPOINT
e841c5bd-6826-4b8a-9b11-c7741a141c43 | checkpoint | 3.4 - Mulch Material Verification
49fec409-3dc3-57b6-8cdb-eb1035a1b820 | note | Detail - Verify that the mulch used meets the specified criteria (e.g., pallet mulch, arborist mulch).
f2fe2e3c-9b04-5918-b390-09ed55b6f41d | note | Acceptance / Conformance Criteria - Mulch material should be free of contaminants, sufficiently aged, and appropriate to site and slope conditions
47d7d7e6-9c9a-530c-ad32-bc1d73a92eaf | note | Standard / Specification - NZTA P39: 2013 Section 3.9
064fffec-d5b2-54a3-bd95-3663723a0145 | note | Verifying Document - Data sheet, Delivery Docket
47bdad9c-35e4-59c3-949c-1a6998ccb684 | note | Testing Quantity Required (based from schedule qtys) - 100% of mulch used
8514693e-ab25-59f1-a2d5-f529195c0e06 | note | Verification Activity: Activity - HP
8526b86d-0863-598a-87f7-59e2057ad072 | note | Verification Activity: By - ENG
29758e09-d36e-4d0e-a7c9-36c2594ad102 | signoff | AUTHORITY HOLDPOINT
c29aa4a0-431f-4ebf-b57e-8c45926b8fff | checkpoint | 3.5 - Biodegradeable Weed Mat
b20114a2-f6c8-593f-bb22-e990b465e93f | note | Detail - Biodegradeable weed mat approval
e89778a4-f2c1-5c29-9e87-32df08c890fc | note | Acceptance / Conformance Criteria - 450 GSM, 7mm thick, biodegradeable weed mat
ec1dc88e-6983-5ef3-9e87-768f8213f3a2 | note | Standard / Specification - PS 27.3.8
7319378d-3f87-59d3-b0a3-b23030830893 | note | Verifying Document - Data sheet, Delivery Docket
0fcc8f03-2160-5abd-9afd-709df5ad3b0b | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
283c7565-8372-5e84-ad49-ad65434b8c7a | note | Verification Activity: Activity - HP
a946e28d-9fb0-5b43-a364-99e8251605af | note | Verification Activity: By - ENG
519d1932-671e-4229-abfa-0a1651cddf51 | signoff | AUTHORITY HOLDPOINT
78eecd11-bf16-46a8-a8ea-6abc90bb91fd | checkpoint | 3.6 - Hydro-seeding
6d993677-81aa-55e0-944d-00c51fb7a67a | note | Detail - Grass mix approved
911a017a-cbc7-5365-bda1-d134726d3d7a | note | Acceptance / Conformance Criteria - Send seed mix to engineer for approval
71d69700-fcec-51d4-8ec3-110431e0c056 | note | Standard / Specification - NZTA P39: 2013, Section F
1d9cc95a-9769-5200-bd0b-5754671862a9 | note | Verifying Document - Data sheet, Delivery Docket
b3b44ee1-3a51-5a57-9925-fdc5a3ad93c0 | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
46324b61-6d54-550d-b4db-e0226e96e2c1 | note | Verification Activity: Activity - HP
4f0fe548-5a1b-590e-a60d-19f2dff26275 | note | Verification Activity: By - ENG
54ddd36a-0c9e-4931-8f2a-8fc0d4fe28ff | signoff | AUTHORITY HOLDPOINT
b1895b64-3f67-4bd5-932f-2421097390a3 | section | SECTION 4 – CONSTRUCTION - CUT BATTERS
46e7c849-f5d0-4108-b20d-3b3b9f230fbc | checkpoint | 4.1 - Batters
23a03444-7f4c-5df6-b73a-26391c17a45e | note | Detail - Required slope of 2h:1v, or follow the design drawings if they differ, regular inspections of the exposed soil.
2e374cfd-d85f-580d-84da-b31b4f349562 | note | Acceptance / Conformance Criteria - 2h:1v Slope
c2d231f3-8520-520f-b9d4-319b734ba578 | note | ○ Shear vane (2.5%)
e374a128-f4f6-5399-b53b-1d8fc66a180a | note | Standard / Specification - PS:16.6.4
db1c84f3-39fc-5d95-9d86-32d066dceea1 | note | Verifying Document - Report, Photos
aa213528-09da-5ad5-9a2e-03a4fb229c27 | note | Testing Quantity Required (based from schedule qtys) - Regular inspections
998e7036-a46d-5450-b35e-cf74dc0cf77b | note | Verification Activity: Activity - I
313b88e7-5db5-57ed-b06a-c609d2c9a76c | note | Verification Activity: By - SE
95ca77b5-f64f-460b-96f5-2d0d8973bbe8 | section | SECTION 5 – CONSTRUCTION - LANDSCAPE
179fb10b-4324-4f40-b9ed-286b72af8ab1 | checkpoint | 5.1 - Setting out Notice
1a9a91e1-a174-548a-80f8-5973fb222146 | note | Detail - Confirm that the site has been marked out according to the project plans and specifications before construction begins.
330dde8e-f898-5ae2-9c7a-ef5c908dff05 | note | Acceptance / Conformance Criteria - The Contractor shall provide written notice to the Engineer, at least two days prior to Setting out.
0a3fef0e-87e3-5aa3-ae51-33a778b2139e | note | Standard / Specification - PS 27.3.2
4c46459c-994d-5081-8721-5f01ea623da1 | note | Verifying Document - Setting Out Notice Report
333aa138-331d-527a-a65b-632efd847817 | note | Testing Quantity Required (based from schedule qtys) - Before each stage
c76f524e-7e06-5cd7-9bf0-8724168a87d5 | note | Verification Activity: Activity - HP
3cb34421-351c-53a2-87cd-fc59be0794b4 | note | Verification Activity: By - ENG
78453b5a-3dd5-4b3d-ac24-212ef3a4a2bf | signoff | AUTHORITY HOLDPOINT
63647274-79a6-4c36-bf70-1749d1875eb2 | checkpoint | 5.2 - Site Grading
eb96f549-c76e-5f55-a981-2aacf5514fb8 | note | Detail - Grading for planting areas to ensure drainage.
3f475a83-1091-5bfc-984c-093ddff92b57 | note | Acceptance / Conformance Criteria - Smooth, flowing contours with proper drainage.
d8a595b4-b8d5-590a-84c0-05a7b22cfc7a | note | Standard / Specification - NZTA P39: 2013, Section G, PS 16.6.3
b162a44a-1784-568f-a25f-a3cc2be23a6f | note | Verifying Document - Visual Inspection
a34bac0e-b12b-5ed4-9259-85b1178a3e47 | note | Testing Quantity Required (based from schedule qtys) - 100% of areas
e976f11c-28c8-5239-a794-107166814bac | note | Verification Activity: Activity - I
98b1df4d-dc1f-5e33-a798-86e9f984ec02 | note | Verification Activity: By - SE
d0e83567-366f-43bf-99d1-b4eb9d4c7d29 | checkpoint | 5.3 - Tree Pit Excavation
e62ffef6-fd83-5dd6-ba86-196294559161 | note | Detail - Excavation of tree pits according to specified dimensions.
c87986ac-7157-50cd-8ca2-afcb0fd1f750 | note | Acceptance / Conformance Criteria - TABLE 1
be413bf6-3285-5c86-a587-d0cba33b5c02 | note | – – – – – – – – – – – – –
2aecc09f-2a84-519f-b6c0-05547c6eaff9 | note | PLANT SIZE (LITRE / PB) ¦¦ NO. OF STAKES ¦¦ TREE PIT SIZE
e7ad0c6a-69f1-5015-b84c-aa1811b92ab8 | note | LESS THAN 15 LT / PB28 ¦¦ 1 ¦¦ 2X SIZE OF ROOT BALL
4ee753ee-8ae9-5477-9a51-84daa6895f79 | note | 45LT / PB95 ¦¦ 3 ¦¦ 1000x1000x1000 mm
3731d8a4-7a1a-543f-8fd4-619b45d578c2 | note | – – – – – – – – – – – – –
bb8fd5e2-8b8f-5480-9eed-901d3b60721c | note | Standard / Specification - 2-32735.02-WSP-DR-UDL 0402 Rev 1
4402f9dc-e76b-577d-b894-09a901c00f3a | note | Verifying Document - Checksheet
29a89b0a-c7f5-507b-9e39-41ab8713536f | note | Testing Quantity Required (based from schedule qtys) - Per tree pit
54f11ab1-f935-570c-917d-17ae0cd94f10 | note | Verification Activity: Activity - I
307d4d58-9643-5ad5-8233-c2c3488e6f3b | note | Verification Activity: By - SE
87a2b4a1-a028-4560-b2d4-10e9adb57a25 | section | SECTION 6 – CONSTRUCTION - PLANTING
94c899f1-f465-49db-8475-1958674bcc4d | checkpoint | 6.1 - Specimen and street trees
6286e958-371a-536f-bcb4-357e183ae284 | note | Detail - Correct staking and tree placement as per plan and specifications
77c0bd69-a472-5f98-91e1-99fa7a7bf71e | note | Acceptance / Conformance Criteria - Newly planted specimen trees shall be staked with two 50 x 50 x 1.8m rough sawn Pine H4 treated or hardwood stakes with at least one third of their length (600mm) in the ground and at least 1.0m exposed minimum, or as specified on the plan with the approval of the Overseeing Organisation.
f6b7774a-cd24-5eb5-829e-c1d943d08f40 | note | Standard / Specification - NZTA P39: 2013, Section G
615225a4-5591-58c4-a435-870420ecbfe2 | note | Verifying Document - Checksheet, Photos
d2e0aec6-d521-5be2-9018-a59f910f6669 | note | Testing Quantity Required (based from schedule qtys) - Each Tree
6a45e823-177f-5446-8a49-de124cafa4f4 | note | Verification Activity: Activity - I
e4b7f969-769f-55af-a083-30c031b08bb9 | note | Verification Activity: By - SE
fa999ed7-da34-48a1-b511-1ad0b021a85c | checkpoint | 6.2 - Timber Stakes
9bd9dd41-6690-59f7-979a-b686788fa775 | note | Detail - Timber stakes used for landscaping must be of specified type, treated to prevent decay, and meet size and quality requirements. 50mmx50mmx1500mm H4 Treated Pine Stakes
6abb4ffd-2bde-5283-84f0-320854c38573 | note | Acceptance / Conformance Criteria - TABLE 1
8b17128b-02f6-5a42-90bf-3198f9b32d8f | note | – – – – – – – – – – – – –
b4e773bb-72f2-5940-88c2-265cfa13f536 | note | PLANT SIZE (LITRE / PB) ¦¦ NO. OF STAKES ¦¦ TREE PIT SIZE
32536623-7152-54a5-abb1-8b7628c5d950 | note | LESS THAN 15 LT / PB28 ¦¦ 1 ¦¦ 2X SIZE OF ROOT BALL
728fd04a-ead6-553f-b11f-b00938827410 | note | 45LT / PB95 ¦¦ 3 ¦¦ 1000x1000x1000 mm
e6433037-5661-5bd8-802b-307b03dad539 | note | – – – – – – – – – – – – –
7e74dd11-0c5a-587b-9c2e-d55f34d90e90 | note | Standard / Specification - NZTA P39: 2013, Section I
2c8edf62-c2a2-5dbc-8fa4-f576754bf5e8 | note | Verifying Document - Delivery dockets, Checksheet, Photos
69f0d287-9be2-5382-83c2-536092e969b2 | note | Testing Quantity Required (based from schedule qtys) - Per order
a36f1745-fc68-5a24-b4e5-2f1b1c5a8b36 | note | Verification Activity: Activity - I
ddf8c647-51e5-5101-bfa8-693a1f969d67 | note | Verification Activity: By - SE
d10cd3ff-c38b-4434-a788-dbfd7599501a | checkpoint | 6.3 - Fertilising
b332ea1a-4026-5785-aa89-6571882f9543 | note | Detail - All plantings shall have two-year slow-release fertilizer tablets installed at the time of planting.
0112c388-faa3-5d0c-81fb-7d202fbfc921 | note | Acceptance / Conformance Criteria - Fertiliser tablet placed in bottom of hole before planting. Fertiliser composition: 6:15:3 (N:P:K). Up to 14l is 1 tab, 45l is 4 tabs
2c090768-923a-516f-9c18-8277d92c3c73 | note | Standard / Specification - NZTA P39: 2013, 3.13
a4e17473-962d-53a8-b75d-cdb23af30edb | note | Verifying Document - Checksheet, Photos
51e5f8dd-2b1c-5d1e-aa11-2b64bf1ff51a | note | Testing Quantity Required (based from schedule qtys) - Each Area
0aabc3c8-f81e-524e-83e5-c75501d6c68a | note | Verification Activity: Activity - I
40fbd5a6-87da-5e7b-8819-ae68b0e57a06 | note | Verification Activity: By - SE
772fab60-8cb9-4d1a-890b-9d8e8b2ffcdb | section | SECTION 7 – CONSTRUCTION - MULCHING
03396163-7d06-4c89-ada8-6d2e0695d895 | checkpoint | 7.1 - Mulch Spreading
04d82b10-354c-5041-920a-65f29c7094fe | note | Detail - Correct mulch application on flat sites
44dada70-9b23-57c3-9346-dc88f3f90b0e | note | Acceptance / Conformance Criteria - On sites flatter than a 1:3 grade (1.0m high by 3.0m metres long), mulch shall be spread evenly to a depth of 80-100mm after settlement, over the planted area, creating an inverted cone hollow around each plant stem with a maximum 25mm depth around plant stems.
39808d85-6c27-54d6-b9c7-428f70db5b3e | note | Standard / Specification - NZTA P39: 2013, Section G
ddc28108-bf97-5971-8871-05785567b1d8 | note | Verifying Document - Checksheet, Photos
a5413a35-688a-5f2b-8b77-af9ef7c132a0 | note | Testing Quantity Required (based from schedule qtys) - Each Area
a72258be-f403-5eae-a715-953295299468 | note | Verification Activity: Activity - I
189aaeda-df97-5cea-8228-2052df1b4833 | note | Verification Activity: By - SE
949f3843-2018-4a04-9521-8b1a5fb7c804 | section | SECTION 8 – CONSTRUCTION - WEED MAT
0a89ac66-5967-4be7-80b0-4a8e344a547a | checkpoint | 8.1 - Weed mat laps
4cd0779c-c459-52e2-908a-2812ce1ee874 | note | Detail - Lap joints
6a5cdd83-8cab-53f0-b2c0-442a66520574 | note | Acceptance / Conformance Criteria - On slopes steeper than 1:3 biodegradeable matting shall over lap 100mm between adjacent rolls and 500mm longitudinally
d6e2f7f0-0c68-515f-9c39-4878089bbb82 | note | Standard / Specification - NZTA P39: 2013, Section G
7130bcc3-157d-5b18-b84e-86fc3eb8d073 | note | Verifying Document - Checksheet, Photos
17b622e1-11a2-5ce6-9622-ed6af6e8f7a5 | note | Testing Quantity Required (based from schedule qtys) - Each Area
3d83193d-7a02-52f4-993b-a392ba209e66 | note | Verification Activity: Activity - I
3bc6464d-2ce1-505a-8fc6-eb1fe6faeee2 | note | Verification Activity: By - SE
7568d5ad-3fa9-4ab5-b23a-e034ce147ade | checkpoint | 8.2 - Weed mat keys
d42021eb-0539-52bd-8b2c-7e9970b927f5 | note | Detail - Key in edges
c316561e-71ed-5654-a168-685c21097ff6 | note | Acceptance / Conformance Criteria - On slopes steeper than 1:3 edges shall be keyed in to topsoil 150mm x 150mm
dc6201cf-eba6-5ae9-bc31-69d66419f9e3 | note | Standard / Specification - NZTA P39: 2013, Section G
d9368bde-a546-58bf-a7f0-481e96e67a2f | note | Verifying Document - Checksheet, Photos
83d848ae-b697-56ab-975c-2a5716348cf7 | note | Testing Quantity Required (based from schedule qtys) - Each Area
1658681c-b6b3-5e8d-a6ef-904cbf746cb7 | note | Verification Activity: Activity - I
fc477b06-a765-5895-8df4-5f6ecb0e6264 | note | Verification Activity: By - SE
2681e07e-3248-49c3-a012-d4c7219432e0 | checkpoint | 8.3 - Weed mat pins
65cd5cad-e698-57dd-99e6-c7c9092a8d11 | note | Detail - Freqency of pins
e8bb8d42-9f09-5b2c-9258-207d0c688d8c | note | Acceptance / Conformance Criteria - On slopes steeper than 1:3 biodegradeable matting shall be pinned with frequency of 2 per m2 min.
afbd99b6-3cdc-5655-93b3-ddf46432b53e | note | Standard / Specification - NZTA P39: 2013, Section G
dd180b42-0f3a-5251-84fa-43615fc4b830 | note | Verifying Document - Checksheet, Photos
5390d0f7-4435-5e8c-8cf9-5ceb18690a64 | note | Testing Quantity Required (based from schedule qtys) - Each Area
2c541d2d-1527-56b9-9335-5d8493ae1de6 | note | Verification Activity: Activity - I
9175858b-abc0-57e1-8c0b-7ec5dc715a75 | note | Verification Activity: By - SE
2bdcfb0b-79b3-4e43-9ca3-ee54c41e000b | section | SECTION 9 – CONSTRUCTION - GRASSING
b0fe964f-ee32-492a-8077-c71bdb32e041 | checkpoint | 9.1 - Establishment of sown areas
267498ac-2169-5eaa-8352-baa3a8758aae | note | Detail - Apply grass seed as soon as practical after area is prepped. Protect newly established grass areas.
2ba27f45-5102-5a33-9c62-4d49fb496258 | note | Acceptance / Conformance Criteria - Newly established grass shall be protected from damage by pedestrian and vehicular traffic until grass has reached a self-sustaining state. Newly grassed areas shall be maintained with regular mowing (90mm-30mm) ensuring that all clippings are removed from adjacent hard surfaces.
e38c154b-e33d-520d-98fc-0c5e43ecee82 | note | Standard / Specification - NZTA P39: 2013, Section G
b45c3efa-abd9-5a5e-bb51-bc473ad4b2ec | note | Verifying Document - Checksheet, Photos
e84f6499-a0ab-50c3-8e45-78651e54cea1 | note | Testing Quantity Required (based from schedule qtys) - Each Area
70e49aff-d023-5dd1-8b45-18faacc818d8 | note | Verification Activity: Activity - I
5bb055d2-d83b-5bea-8978-8d8beecb5734 | note | Verification Activity: By - SE
c063a2dd-a654-44ec-a12f-6a2c9946453f | section | SECTION 10 - POST CONSTRUCTION - AS-BUILTS
e4e49ac6-f80a-47b5-97c2-dec36e627233 | checkpoint | 10.1 - As-Builts/ Red pen markup
6bbd910b-67c7-573c-bc88-b2ca6f05488d | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work.
26296988-7a52-511b-802c-b7f344def605 | note | Acceptance / Conformance Criteria - Record of work completed
7dd38882-f3b2-58df-b431-f636f40320e5 | note | Standard / Specification - PS 16.7.6
1e0181e6-a80a-580a-9df9-ca50d6260a1c | note | Verifying Document - Red pen markups
b2876d8f-14ee-5d64-a691-17f762d678fc | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
e294fd4e-d34b-5213-938e-2bf4f5baa1eb | note | Verification Activity: Activity - D
f4303a29-0c5b-599c-bffa-08e3856fed02 | note | Verification Activity: By - SV
bc36e37f-8994-45ff-acff-e5d24b43cb20 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
9a379df0-6dab-5105-a5b2-43fb0ec14c84 | textbox | Contractor's Rep Name:
800fb4d1-a486-5e58-8a6d-5af7585ad225 | textbox | Engineer's Rep. Name:
8ee52954-8ca7-5a66-af54-536f072dd12e | date | Date:
6fbbc542-d7c9-4fd8-8178-7da8976b5826 | signoff | Add Signature
55244aea-85f0-4421-ad41-fa98958bd215 | checklist | DN1210-SP2-033-002 ITP Landscape Fencing Rev 1 | itp | DN1210-SP2-033-002 ITP Landscape Fencing
b610dfb3-962f-4d8b-b152-823f541373ca | section | SECTION 3 – PRE-CONSTRUCTION - PERSONELL, MATERIAL APPROVAL AND THIRD PARTY APPROVALS
b59507bc-8721-4fd7-9e23-eff8d79298f0 | checkpoint | 3.1 - Extent of Line Setout
5d08c654-713b-57a5-bb5d-97e873e36ef5 | note | Detail - Ensure line and level of Fences has been marked out and agreed with Engineer in accordance with fence drawings.
82542a73-7f72-5556-91ce-9ff3a0be2194 | note | Acceptance / Conformance Criteria - Engineers Approval
12d4d456-e0d1-59d0-8948-da7dbf2bc81f | note | Standard / Specification - Design Drawings
48fd492a-4dd6-503c-8509-110ff53da0c6 | note | Verifying Document - ITP Sign Off
83d27a3e-ed4d-526a-95b7-1c4591172d61 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
0479ae45-b17e-5b6f-b53f-c57fdd9b2cc0 | note | Verification Activity: Activity - HP
ec9c6111-6cf3-59c5-9cf3-9040a185fc02 | note | Verification Activity: By - ENG
cc16e2d8-fa1c-4ebc-8b2c-e41bbc438571 | signoff | AUTHORITY HOLDPOINT
a316eea9-b2a5-4ec5-9d6d-3855b2f7039f | checkpoint | 3.2 - Timber (Rails/palings/battens) Posts
34250798-9280-5dea-b360-0b4cf3f810a6 | note | Detail - Treatment
4315247f-1426-5648-9757-ff72e6bc5fc2 | note | Acceptance / Conformance Criteria - H4
e0e7aa18-c06b-5b70-ab56-161607906767 | note | ○ H5 if touching ground otherwise H4
59180f2d-04e2-5d8b-ae39-95413357d15d | note | Standard / Specification - PS 27.5.5, NZS3607:1989
69323151-d7cd-5b86-93a1-da1b6b0f66f8 | note | Verifying Document - Data sheet, Delivery Docket
10abb7c4-76d8-554b-8e8c-c9d5ca94bfe2 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
2f1badbc-e369-54e9-b256-74a555b50187 | note | Verification Activity: Activity - HP
c48df7b2-895f-5e82-8251-932c536539ff | note | Verification Activity: By - SE
7db29a81-8f2f-4c5a-82f7-32559d003991 | signoff | AUTHORITY HOLDPOINT
473ca317-9d58-49ef-bbb0-92cfebca9ba7 | checkpoint | 3.3 - Steel (Post/Metal fence)
dccc0d7e-621f-53eb-9ab6-f94cd9b52e5b | note | Detail - 6063 T5 aluminium or equivalent metal
f9b1849d-a312-5c13-88bf-dd19215f80cf | note | Acceptance / Conformance Criteria - New Zealand building code clauses B1, F4. design loading is up to 0.75kN/m
bc9de633-0a4f-5c50-82d9-118a06deedf7 | note | Standard / Specification - PS 27.5.1, PS 22.5.6, PS 2-32735.02-WSP-DR-UDL-0407
9b373541-4007-5d37-9545-cf3d8a971dcf | note | Verifying Document - Data sheet, Delivery Docket
9a37d9ed-3e71-54e8-8822-77ccaa509ec6 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
566b972b-178d-55f6-ac3f-1ab81826778f | note | Verification Activity: Activity - HP
f29230bd-2c70-593d-8699-03739f65db1a | note | Verification Activity: By - SE
c9d638e9-7d3a-47b6-84d5-cb7ff62a93c5 | signoff | AUTHORITY HOLDPOINT
bac05d7c-84ba-4839-96b7-e38314511901 | checkpoint | 3.4 - Material (Fixings/fasteners/hinges)
1464ad70-cdcc-5182-89c2-6027c5769fde | note | Detail - Jointing
17830381-e2d4-5d31-b915-f6080bfddee3 | note | Acceptance / Conformance Criteria - Hot dip galvanised
8a233a3d-9be5-54c9-ba89-efef0c0286a7 | note | Standard / Specification - PS 27.5.1
42968d12-c63f-5898-8a47-7e3842e7c44f | note | Verifying Document - Data sheet, Delivery Docket
ada22dbb-503b-5bd2-bb33-c5c9fc1bbbe8 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
5d4f43f0-c4b7-5a14-a748-32726483d745 | note | Verification Activity: Activity - HP
6cfd975d-5211-5e90-9cd8-4bdefd58a459 | note | Verification Activity: By - SE
e37f9589-370c-4ab8-9d79-4307a7c4e285 | signoff | AUTHORITY HOLDPOINT
c6248f77-f793-43f5-8049-29f06872e812 | checkpoint | 3.5 - Concrete
d01e78ff-ca2f-5f21-8c07-55bedc602ec1 | note | Detail - Ground planted posts
9bc09e51-2845-5f6c-83c2-8585447bc744 | note | Acceptance / Conformance Criteria - 17.5MPa
c90b6b0c-2e19-53fe-9acc-2fd0319f7576 | note | Standard / Specification - PS 27.5.5
74fb71b4-96ec-524c-b1ed-1fbdee4dfc60 | note | Verifying Document - Data sheet, Delivery Docket
0abc99b5-fe03-578e-bc50-ba663de96949 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
530b9b2c-7a08-5497-87b0-49db4142f038 | note | Verification Activity: Activity - HP
7c54d3b3-9a8c-5803-a378-a9906af3250d | note | Verification Activity: By - SE
ea4438b5-49b4-42ca-95f9-46bb757728ea | signoff | AUTHORITY HOLDPOINT
9264b8bb-cde4-4307-bbd1-167b696bfd0f | section | SECTION 4 – CONSTRUCTION - 1.5m BALUSTRADE FENCE
56f12d67-b87a-41f4-9624-08815d6c289a | checkpoint | 4.1 - Subgrade testing
b27a1534-8f46-56d0-b3f2-e054b577d5f1 | note | Detail - Install around the Carpark
66463dc5-a826-53f4-b75d-4faf4e95dd22 | note | ○ Black powder coated finish
8af2d012-6d78-5654-b790-8ec758ae2a53 | note | ○ Shear vane testing of every 4th post
eb79038f-abe6-53d6-bf82-26c1e07e0308 | note | Acceptance / Conformance Criteria - min 100 kpA
a41d61e5-ae01-5715-8167-48158b886a4d | note | Standard / Specification - DN1210-WSP-NTC-0574
0a702783-e91f-572e-8c30-92eab451fba6 | note | Verifying Document - Testing Dockets
45c9fe76-6995-550a-ba55-0d7fad80f2b7 | note | Testing Quantity Required (based from schedule qtys) - During installation
738d8091-aaba-5ede-b43b-3f4b94e2fa7a | note | Verification Activity: Activity - H
1a3e3eb7-1d19-574f-a060-b443888b4056 | note | Verification Activity: By - SE
c7b6c114-bafa-449b-b44f-cda32064d949 | checkpoint | 4.2 - 1.5m Balustrade Fence
3de009f3-c4c0-517d-b919-e418a0d6fe34 | note | Detail - Install around the Carpark
3d40432b-557d-5dc9-83b3-978ca1946037 | note | ○ Black powder coated finish
b19cdc2d-8836-57f9-9280-6ff493a99be4 | note | Acceptance / Conformance Criteria - 1.5 metres high, hot dipped galvanised and installed as per the drawings
f8f6f83c-bd21-5e3b-bb5d-106b6962cb14 | note | Standard / Specification - PS 2-32735.02-WSP-DR-UDL-0407, PS 27.5.1, PS 27.5.3
a467de20-d1f4-5b40-8e35-75c275533764 | note | Verifying Document - Delivery docket, CKT1210-033-001
9027faeb-1314-572f-93f6-489b0bd9e6ef | note | Testing Quantity Required (based from schedule qtys) - During installation
e5995b39-cb9d-5665-a5bc-f9dd0a32f729 | note | Verification Activity: Activity - M
6c07d800-b95e-5666-9cc5-336e1f3df240 | note | Verification Activity: By - SE
cfaf0863-2800-478b-8bb4-7903b000498b | checkpoint | 4.2 - Carpark Vehicle Gate
4c9780d5-7922-593f-9c83-9381bc9be4f9 | note | Detail - Install around the Carpark
3c7c6b96-175c-5a2c-a12e-02e4492778c6 | note | ○ Black powder coated finish
25ecf2e6-0e2f-54b3-801c-4ba22f9f6f6b | note | Acceptance / Conformance Criteria - Double swing gate hinges both sides two lockable post
6fe07e75-33ed-5d1a-a719-bc1946ca37a0 | note | ○ Pad Lock supplied to school
9ffa07cd-37b9-5570-8089-3d945ae8af7c | note | Standard / Specification - PS:27.5.3
342c9ce7-5b11-52a5-ad95-67ad5b4a804b | note | Verifying Document - Delivery docket, CKT1210-033-001
6baa7b50-a7bc-576b-bd5b-e9fac0b293dd | note | Testing Quantity Required (based from schedule qtys) - During installation
1fb2f5e6-3d3b-57a5-9cf5-90e56ad2edf5 | note | Verification Activity: Activity - M
6c48ec26-c584-5010-8040-e8f0f2fae823 | note | Verification Activity: By - SE
a448dbea-51d4-49ce-8a46-edcea2b141c2 | checkpoint | 4.3 - Carpark Pedestrian Gate
489f8c60-cae9-5a45-b9b7-e91c876526c2 | note | Detail - Install around the Carpark
a4694337-e48b-55a9-a4b6-e043d4e4411f | note | ○ Black powder coated finish
b0f00708-0a9c-5198-a466-c929fc738bc2 | note | Acceptance / Conformance Criteria - To be fitted with child safety locks
5ca48a0e-1665-5152-a1a4-956fb746eebc | note | ○ Gate to be open with no obstructions
4f2daa01-a9b6-5b82-b3ae-ca50362fbe53 | note | Standard / Specification - To be fitted with child safety locks
94aff2e9-bdd2-5fb1-a327-fee14c1d3d13 | note | ○ Gate to be open with no obstructions
6bf15821-332e-5035-84ab-e30290d5d1b1 | note | Verifying Document - Delivery docket, CKT1210-033-001
250dc196-e468-577b-9935-3c4b6b792e6e | note | Testing Quantity Required (based from schedule qtys) - During installation
6ffa53c6-b32f-5a9a-80ba-d4d0ce0688bc | note | Verification Activity: Activity - M
68f0d5a8-e655-56ca-88c7-0ede9c0d8ef8 | note | Verification Activity: By - SE
72e3ef27-218c-409d-9185-dccd7839108e | section | SECTION 5 – CONSTRUCTION - 1.8m TIMBER PALING FENCE
5cbf552b-1ec2-45ec-9aa2-d84cb2e12391 | checkpoint | 5.1 - Timber fence
9938eaf7-e319-5de9-8b08-cd65ad49b4fb | note | Detail - Preserve timber exposed faces
f7a5a701-a109-59ae-a491-76dc0c09bb7a | note | ○ Post imbedded in ground
8b6e8b62-1ea4-5ecb-8d1f-721c4dfe9db1 | note | Acceptance / Conformance Criteria - 1.8m high
714f4e85-fd01-5fc4-9dce-e96186ed03d8 | note | ○ Exposed timber faces neatly protected with 2 coats of timber preservative (Metalex)
57dd88dd-1fa6-5f87-a511-53a92af12759 | note | ○ 1800mm in ground with 17.5MPa concrete
3cf9c878-c915-500e-891e-6d87c82befd6 | note | ○ Minimum 100mm extend around the post
c5eb28b4-8eb6-55f2-976f-515e6b36d1ec | note | Standard / Specification - PS 27.5.5
0b3e044e-61c6-5415-b96a-c83eb8bc9e3d | note | Verifying Document - Delivery docket, CKT1210-033-002
13535a38-4664-5d62-aa8d-be3b6ebcdde1 | note | Testing Quantity Required (based from schedule qtys) - During installation
dd26ba6f-94cc-57bc-9a0e-c90e1df9648d | note | Verification Activity: Activity - M
dffda54f-aeb1-5a6e-a5ae-b63e04b55d3c | note | Verification Activity: By - SE
b93b1007-9eff-4a99-913d-cd49e195bb38 | section | SECTION 6 – POST CONSTRUCTION - AS-BUILTS
5f7480e2-6e2a-4f64-8816-dc06f9eaa73a | checkpoint | 6.1 - As-Builts/ Red pen markup
b01df928-f891-518f-9ae9-998e3339b9e4 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work.
a2417a4f-2685-59ac-ae51-2e1bfd075d28 | note | Acceptance / Conformance Criteria - Record of work completed
edf6e5af-32f1-5deb-9977-430dfca0d0e5 | note | Standard / Specification - PS 16.7.6
ff1f5774-5be2-5124-a179-3281c46c6217 | note | Verifying Document - Red pen markups
da6ec217-bb72-521f-b635-94febfb11165 | note | Testing Quantity Required (based from schedule qtys) - After instalation
8e576754-8b7e-5db1-8351-50fa34013956 | note | Verification Activity: Activity - D
863042a8-4b95-5d8c-a1b5-5b1a5f590a3b | note | Verification Activity: By - SV
b7923d75-c9f0-4ecc-b902-0d57601e9dc4 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
d57a7cd7-5a40-5e16-b5c4-b804c27af34b | textbox | Contractor's Rep Name:
d1cce6e3-fe5b-53b2-a83a-50edb7a1eda7 | textbox | Engineer's Rep. Name:
5f842482-a8ae-54b0-85bd-fecf2dad63a6 | date | Date:
2c635bcb-9604-4e04-af43-6832e9bc0f24 | signoff | Add Signature
93d3506a-a15e-4039-8a9e-c44cf8b60cb8 | checklist | SYS - 73 |  | 73
b2dceae1-6f3c-431f-831e-6b41e00eeeff | checkpoint-no-value | Received Instruction
e4f2777a-7f04-50de-9745-2958c8a5f7c0 | textbox | Reference/SI Number
65b6d5f6-7f80-577f-bcf6-70ffa15492b8 | date | Date Instructed
9f6df03a-9879-5224-900b-760dab7f436a | textbox | Client
23c0b2aa-79e1-54c5-95fa-1603cc37dd53 | textbox | Scope of work
2bf62a9a-13fa-5a6f-9829-91da02b98aea | textbox | Agreed value
899bcdee-7434-47b3-89d9-9543876b8cb1 | signoff | Approval
05a186f2-1bb1-49b6-b698-a0075cec0e13 | checkpoint | Job Complete
ed6455d7-5e8a-52bf-8b9e-11a3372735e5 | date | Date Complete
22759515-1c8e-5c8a-bdf8-fc349711cb11 | textbox | Details of work
40537615-018e-59a6-9c8d-62638c7abeba | labour-materials | Labour and Materials
a1f6db10-ec9b-4e21-99e3-ce665914bbd2 | signoff | Attach Signature
54448d7b-622a-4c5a-9284-0dd6f6064094 | checkpoint-no-value | Values
8bc11931-2076-562b-8733-9481cc5af9c0 | number | Labour value
91d0d905-5143-55a8-b499-3bb811a6bc68 | number | Materials value
0162cfe6-2eb5-5a66-9d0b-672250d2e67a | textbox | Other items
87cc2e94-2852-5e3f-8f1b-d8b46bb36442 | number | Total value
7e3ede23-cd72-5fbc-a371-d16341a3fc56 | checklist | Ω (DEPRECATED) DN1210-0007 ITP Stormwater Rev 0 (v0) | itp | DN1210-007 ITP Stormwater Rev 0
9dbf9507-d5c1-5f76-b0e9-632a875b7d7c | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
61faafb8-e067-5299-84f0-3fd60960e68e | checkpoint | 1.1.1 - Extent of Line Setout
8c6ec2f9-39bd-56e6-af44-d2517ac396f2 | note | Detail - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Stormwater drawings. Identify any clashes before construction.
7d6a7e91-0e37-5917-8fba-1a8a1eefae57 | note | Acceptance / Conformance Criteria - Engineers Approval
e5fee9e3-7922-574d-92a5-7ffc18141aab | note | Standard / Specification - Design Drawings
44187e60-7257-5c43-8598-469a199c8f58 | note | Verifying Document - ITP Sign Off
1f14d97f-faf6-5369-b434-80379019109a | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
8b6e67aa-6aa6-5b21-9bfd-9a3eb29a45ee | note | Verification Activity: Activity - M
a97d5839-1e49-59fa-b864-a3a67cc79564 | note | Verification Activity: By - PE
58d8e667-bb88-509f-83a3-6a1f01d0e239 | checkpoint | 1.1.2 - Existing Stormwater system
49e460ff-036a-53b2-b79f-9c99f6652733 | note | Detail - Confirmation of existing stormwater network.
42c9dd57-cc47-5267-b8e0-a6a8918f72a0 | note | Acceptance / Conformance Criteria - Survey Informations
7a99dc1c-fb5a-5edd-876e-c469c1399ebf | note | Standard / Specification - Appendix V
741ac5b0-1750-5d08-89d8-999292956bf0 | note | Verifying Document - Survey data
39a0f032-457e-5f57-abda-8c2115ba5d0c | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
3651724b-6601-57d2-9532-88e9342cce24 | note | Verification Activity: Activity - HP
1684a043-6be9-57cd-a4e1-b987c3933cc0 | note | Verification Activity: By - ENG
439eb8b4-e232-503c-ae3b-29d0c5635540 | signoff | AUTHORITY HOLDPOINT
b2505ca3-943c-534d-afb7-23e310ef1e65 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
7b779b30-3202-5976-a674-5a18e46af7e0 | checkpoint | 2.1.1 - Material grading: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
1f334567-e26c-5615-a6c5-437f663ff8bd | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
24d05b84-18e6-5631-89c4-8498e20aed26 | note | Acceptance / Conformance Criteria - Stockpile size 1500 to 4000m3. PS- Table 21.2 for GAP/AP20 PS- Table 20.3 for Overlay and Embedment Zone Material NZTA F/6 for Drainage Aggregate- Grading section 2.2
5c9ddec3-cfba-5a3a-924a-5cd74196e283 | note | Standard / Specification - PS-21.7.2
a3371f70-425c-5a18-9783-f9204e2236fa | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
0cbe2752-5826-50eb-837c-fe29a51d166f | note | Testing Quantity Required (based from schedule qtys) - 4 Test 1 Test for each additional 1000m3
f33c1220-9cf8-5e0f-b2f5-9a13930a12cb | note | Verification Activity: Activity - HP
daa93a5e-c9ac-5db2-a1d1-769932c9e987 | note | Verification Activity: By - ENG
d9a47fe7-92b9-5d7e-ba3b-89916ba64f50 | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
4aeddbe8-5560-52d8-adc7-e338b59829ce | signoff | AUTHORITY HOLDPOINT
8d324d50-cc82-585e-af30-1900442f0418 | checkpoint | 2.1.2 - Weathering index: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
3e9433c2-8416-541a-9b8e-f94896d44afd | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
02556238-6038-5fd8-b6ca-daae3b6dab89 | note | Acceptance / Conformance Criteria - Engineers Approval AA to CA
aaddeb8c-95ff-56d6-9a6f-3409bffb689d | note | Standard / Specification - PS-21.7.2
189140fd-eb19-5a38-9198-6caffd786c65 | note | Verifying Document - Lab Test Report NZS 4407.3.11
da98e593-24a7-5f5a-8ce9-7c74c81324f7 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
792e2727-8b39-5b9a-b169-fd5e24df259b | note | Verification Activity: Activity - HP
cd225301-feb2-5a18-90ba-b565d40136e9 | note | Verification Activity: By - ENG
b934f0f0-a41c-5df1-9909-a98c6e8a0321 | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
a2fc101a-90b9-54e1-89a9-1383075ee775 | signoff | AUTHORITY HOLDPOINT
5c6967dd-7748-5877-a08e-26c0fca616fa | checkpoint | 2.1.3 - Crushing Resistance: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
42790e68-27b0-5257-b87e-1982f42796e2 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
984bb7bc-4f10-5043-80f2-d40e640bf675 | note | Acceptance / Conformance Criteria - Engineers Approval >100kN
e3bb4083-971b-55a2-9772-0a0a21cf7749 | note | Standard / Specification - PS-21.7.2
0a7679d5-39c2-5de1-b95d-39ec647eab43 | note | Verifying Document - Lab Test Report NZS 4407.3.10
7b856239-6bd6-5372-9166-20d22ad5dee5 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
8585d6ff-4e91-5a30-8302-655099e0e606 | note | Verification Activity: Activity - HP
2648d9d0-a0ed-5b83-8385-c18a55813457 | note | Verification Activity: By - ENG
65121ca3-b1e1-5e4a-a887-0a084d4ac8bf | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
cbd04506-6cf4-5b18-9ff7-c44dfcd7f02d | signoff | AUTHORITY HOLDPOINT
7191560b-5e9b-500b-8294-b06ed11c768b | checkpoint | 2.1.4 - Geotextile/Geogrid
6edffe58-5601-5dee-9731-a95829301d91 | note | Detail - Minimum Strength Class C & Filter Class 1 or TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
3a4e22eb-c194-507d-ad79-45831776f912 | note | Acceptance / Conformance Criteria - Engineers Site Representative to inspect trench.
ea038197-1b00-5782-8df6-03b39f7859d3 | note | Standard / Specification - PS-16.5.7
45a7f083-9498-53f2-b122-3e13010cc7d0 | note | Verifying Document - Certification
0f9de01c-864c-5a5d-9a87-6273d2f836c7 | note | Testing Quantity Required (based from schedule qtys) - 1 time
7bd65c91-8676-53ea-80aa-104dd809277c | note | Verification Activity: Activity - HP
70bcf854-abb5-5221-9218-490224e68a4a | note | Verification Activity: By - ENG
b25b3fba-56ef-5a01-97a4-28b869a99641 | signoff | AUTHORITY HOLDPOINT
d353cea1-760b-54fc-ba9d-3f6628ef5bc6 | checkpoint | 2.2.1 - Riprap test Criteria
d286ec9a-b058-5a28-8a8f-00cf21213193 | note | Detail - Weathering Index of Coarse Aggregate.
b4077272-8d75-5913-bca2-1bfc527d262e | note | Acceptance / Conformance Criteria - Engineers Approval AA to CA
4831fecc-6eb9-5f1b-81f3-d46c6f6c69d7 | note | Standard / Specification - PS-21.7.4
68a6c4d8-cf61-50c7-9b19-fe178bdd7042 | note | Verifying Document - Lab Test Report NZS4407.3.11
a816cfe2-2037-516c-975a-ca474f1f903b | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
8657b15f-6259-5bf9-ae34-67f8613f7f29 | note | Verification Activity: Activity - HP
ad7dd6dd-66e5-55cd-bffa-63ca75e31be6 | note | Verification Activity: By - ENG
c2623d1f-bd3a-5637-bac9-0bae411ac607 | signoff | AUTHORITY HOLDPOINT
37c23bd2-a3fb-5b1c-be0c-98555e939a1c | checkpoint | 2.2.2 - Riprap test Criteria
1f2b2ecb-2e9e-536c-b013-fa147e18aea2 | note | Detail - Crushing Resistance of Course Aggregate.
9f617669-633c-5613-b494-287a0eaa94a0 | note | Acceptance / Conformance Criteria - Engineers Approval > 150kN
9238c7ab-8930-54a1-9a16-5efa91586e06 | note | Standard / Specification - PS-21.7.4
c6746b54-5e95-5509-bcff-cf78f24161d7 | note | Verifying Document - Lab Test Report NZS4407.3.10
8b24e29e-64a0-5fbb-a080-7de232bfbf75 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
fc644247-06a4-507e-a5ac-029409aa04df | note | Verification Activity: Activity - HP
498ea4f1-b4e1-51d9-a137-bfa5469497d6 | note | Verification Activity: By - ENG
1ac63ecd-b84e-5578-bb6f-a120cffbdda3 | signoff | AUTHORITY HOLDPOINT
b0917513-6283-539a-acb3-a2b3aa920522 | checkpoint | 2.2.3 - Riprap test Criteria
d628b4fa-a5af-504b-a446-56451c012aa7 | note | Detail - Solid Density of Aggregate.
dfdbff3b-306e-5700-8fe9-fd39b874d80c | note | Acceptance / Conformance Criteria - Engineers Approval ≥ 2.65 tonnes per m3
a4334eca-ba29-5bde-8260-79e987fe1d3b | note | Standard / Specification - PS-21.7.4
25932fa2-7703-56ba-83e1-059a9132add0 | note | Verifying Document - Lab Test Report NZS4407.3.7.1
2187692d-ece8-5d53-8ef4-159ba70b2333 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
7bfc33aa-87c5-5816-965d-d04b52316581 | note | Verification Activity: Activity - HP
df1af21a-0031-5b1e-bf94-ec72f87e1906 | note | Verification Activity: By - ENG
a590b01d-a0ea-50ef-b3d0-57465bb74403 | signoff | AUTHORITY HOLDPOINT
5317a3a0-6700-5834-a89f-bd6ef24b9bf5 | checkpoint | 2.2.4 - Riprap test Criteria
12f0ae57-b248-5298-9aef-21cb5140cd53 | note | Detail - Grading of the material.
73ec9ed6-31a3-5759-9d8e-af6d74715b93 | note | Acceptance / Conformance Criteria - D=50 150mm Riprap Grading Aperture Size- 230mm Aperture Size- 150mm Aperture Size- 95mm
002fa807-2c30-50a7-8e68-c20a54016e80 | note | Standard / Specification - PS-21.7.4 PS-21.5.14 Table 21.3
09758b78-075b-5f15-baa0-097393ff974e | note | Verifying Document - Lab Test Report NZS4407.3.8.2
11292c02-362a-584d-a56b-3f927be37292 | note | Testing Quantity Required (based from schedule qtys) - Percentage passing- 85 Percentage passing- 50 Percentage passing- 15
d31ca261-8d16-5930-bafd-7c13e256dbb1 | note | Verification Activity: Activity - HP
588d5b23-fad5-5711-97aa-fb690e88338a | note | Verification Activity: By - ENG
947ebb05-cb3d-5cbb-9402-8ca942d558c0 | signoff | AUTHORITY HOLDPOINT
98285b74-1d71-57f6-9977-ee088beb181f | checkpoint | 2.2.5 - Riprap test Criteria
255e8990-7914-5fa5-b163-eeb7f68c9963 | note | Detail - Point Load Strength.
2d7082ac-318b-59a1-8cce-77a95e658c7d | note | Acceptance / Conformance Criteria - Engineers Approval >1.5 Mpa
15ba3521-b680-5a07-b9aa-b31840006f30 | note | Standard / Specification - PS-21.7.4
f033c320-d8d9-55fe-821c-b40d10e4aa59 | note | Verifying Document - Lab Test Report ASTM D5731
619db733-dd8a-59a0-a845-0888aa125eba | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
3d026438-f16a-5d68-af72-5e85aeb86337 | note | Verification Activity: Activity - HP
87a4d598-27dc-5715-b148-458db0082944 | note | Verification Activity: By - ENG
0063bf6f-94a0-5293-8cea-55db2d898e31 | signoff | AUTHORITY HOLDPOINT
c58e1f7b-cdec-556d-b433-f2dbfce36ed4 | checkpoint | 2.2.6 - Riprap test Criteria
e4203914-0330-590b-a5e6-017784aba336 | note | Detail - UCS Rock
bde3dda1-6f3b-5ec4-a027-5d616f175f23 | note | Acceptance / Conformance Criteria - Engineers Approval >30 Mpa
2f9f77e7-86b8-5c19-b6fd-8c5a2a960825 | note | Standard / Specification - PS-21.7.4
8ef95ebd-fef6-5403-acc8-27880f47e268 | note | Verifying Document - Lab Test Report AS4133.4.2.1
ea339cdb-416c-5b18-8a8b-d996a77051ce | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
0e0d3efd-5dd0-5a5f-ad8c-7c6c66e92c9b | note | Verification Activity: Activity - HP
351f00b1-ec78-5d7f-add6-76cb4b6e545a | note | Verification Activity: By - ENG
ebf02735-8f7e-512d-8e6c-9d466034bd52 | signoff | AUTHORITY HOLDPOINT
7685f2ef-c62e-5fb7-a70f-d353bd416788 | checkpoint | 2.3.1 - Pipe and fittings. (uPVC SN16, PVC, PP, PE and Concrete pipe).
b01a1fdd-980f-57b1-be0a-974d4f3bb258 | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
4c191b62-9e9e-5c94-be52-070246d48b7a | note | Acceptance / Conformance Criteria - Site Engineer Approval
8d5cf5a8-4e17-5231-a5b6-ca8dd8ec696a | note | Standard / Specification - PS- 21.5.1 PS- 21.5.2 PS- 21.5.3
75775828-4804-5f60-a3df-9a82d162ad6b | note | Verifying Document - Delivery Dockets
751b8bc4-6897-5063-a6d7-87d47ec7c076 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
7e8d13c8-1979-5990-aacf-08b73505fda9 | note | Verification Activity: Activity - H
4006c96a-bc64-5e43-9917-9020fd14008d | note | Verification Activity: By - SE
a5d92bcd-6b64-564d-acc9-23954f1e76ee | checkpoint | 2.3.2 - Stormwater- Structure (SWMH, SDMH, GMH, CP, DCP, CPMH, MP, HW)
950e6069-be5d-58e8-906f-75c387756cac | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the Structure are correct and in good condition.
7249efd0-13a8-5579-bfe8-c850866e2857 | note | Acceptance / Conformance Criteria - Site Engineer Approval
b50f929a-38af-527f-a81a-e53528cbf432 | note | Standard / Specification - PS- 21.5.4 NZS 3109:1997
e6a2b17a-e105-5c3c-9310-968bf24eddd4 | note | Verifying Document - Delivery Dockets
63930cae-a21d-5047-ac1e-9857f8ff5e7b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d41b08a3-eeac-54e7-8f15-e394c8e93b03 | note | Verification Activity: Activity - H
e9e75178-846a-5eef-b1b1-8521d4d46882 | note | Verification Activity: By - SE
cbed7aea-7be8-51e8-bfaa-a2df8eb77a1f | checkpoint | 2.3.3 - Granular Material (GAP20/AP20, GAP65/AP65/LRAP65/Riprap and Drainage aggregate)
407ef78e-50cd-57c8-8824-f9d8e8852c18 | note | Detail - Confirm Specification and material in good condition.
1136a1e3-699e-58c3-9d0c-aa15898cd5f4 | note | Acceptance / Conformance Criteria - Site Engineer Approval
b8087df2-d012-5974-9df1-eba90d28bbbf | note | Standard / Specification - PS-21.7.2
cdc5971a-6269-5354-b5c8-8f9475803eae | note | Verifying Document - Delivery Dockets
9d088f1f-9f2a-5ca3-bb59-e6e1b2142f5a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5a3f4e82-12f6-5d82-8f50-0afdd218756f | note | Verification Activity: Activity - H
077a5639-66fb-5771-88cc-8c3b6cf276b6 | note | Verification Activity: By - SE
c71f9062-d24e-5bf6-a7c7-105d5eef56fd | checkpoint | 2.3.4 - Geotextile/Geogrid
7bcf08b7-ff3d-545e-84c3-04e1e82f1589 | note | Detail - Minimum Strength Class C, Filtration Class 1.
e1ab34a5-a3f2-5e9c-927f-ff3d58e9cc8b | note | Acceptance / Conformance Criteria - Site Engineer Approval
ae9fbf32-cb1a-5c09-97d0-ef9c77c01924 | note | Standard / Specification - PS-21.7.3
3c978ce7-deea-5c28-a3fb-87c317f1a200 | note | Verifying Document - Delivery Dockets
2666c2e2-715b-5082-910b-8fbf5a733244 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
95b961d6-569a-5cba-9d93-b4a540fa1ba6 | note | Verification Activity: Activity - H
e11c4279-6af9-5f37-8469-0635e4d97c4f | note | Verification Activity: By - SE
9cc06a11-17ee-5f49-ac50-31c36fc22fcb | section | SECTION 3 – CONSTRUCTION ACTIVITY
6060b861-66f7-50a6-931b-1a3e09522cab | checkpoint | 3.1.1 - Foundation Compliance
7536601b-5795-54c4-9390-a7bed0019a30 | note | Detail - On Granular or Cohesive Material
724edf15-3e3a-5915-9121-84578bd157f8 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
f830645a-2aab-58bb-906c-27c71c18a48c | note | Standard / Specification - PS- 21.7.2 Appendix V
8c31040c-a189-533b-825a-9de443fb9ff9 | note | Verifying Document - Scala test result
8740789d-55d4-5feb-971a-45877bdd7d1a | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
c84c9e22-44a5-5f1d-affd-04e3960ef8b3 | note | Verification Activity: Activity - W
6ecf1e8f-3477-5567-837f-fa8625d3e6b8 | note | Verification Activity: By - SE
c1c96344-d442-58de-82ed-d9085e766b87 | checkpoint | 3.1.2 - Undercut approval
00595da2-b0ec-5ba3-b6df-33932dcee49a | note | Detail - On Subgrade
7af00c8c-0774-501e-ba30-da67c0745a5c | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
25a1d52f-7fda-5426-b137-dd447b2e82ad | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
baaf7fca-54a1-5394-b84d-d1811e3fb804 | note | Verifying Document - Lab Test Report
8ea61e8d-88b8-50d8-acc4-310275e23e59 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
1d831097-2f81-5314-aeb1-6393177b78c0 | note | Verification Activity: Activity - H
92fe9a12-d005-54bf-bb3d-bfeeeb2adab5 | note | Verification Activity: By - SE
1a41ffdc-e630-5238-b3c6-b7ddb238f1d2 | checkpoint | 3.1.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
6479ab9c-b45b-5e98-ace7-2a2eb58883e8 | note | Detail - On Granular Material
6aa210aa-94f1-5f44-9779-2cb46f254d92 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
1da33ee3-ae6d-5b44-beeb-d48a29e36b20 | note | Standard / Specification - PS- 16.5.12
55ff37d4-947c-5ac3-a0dc-9a1ac4e5af92 | note | Verifying Document - Lab Test Report
b9c7f2b9-a88f-5b50-9010-a5d3751a4a1a | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
3195e80f-8f03-5d16-af20-4cc0d10e4085 | note | Verification Activity: Activity - H
bea0a486-f7a1-590a-9672-73554f189ccd | note | Verification Activity: By - SE
122c791d-c0bb-5292-b890-be01180cb1f8 | checkpoint | 3.1.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
eb402eea-cbce-5dd1-a273-ee269f7ccd3d | note | Detail - On Granular Material
83dc2d43-8184-51d7-94cd-24ed704f194a | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
d64474e8-d06b-51eb-b3e4-359d201a1552 | note | Standard / Specification - PS- 16.5.12
830684fd-21d1-565f-bd8f-b354a2dfb8f4 | note | Verifying Document - Lab Test Report
5ef9c053-d06b-5ce9-ac02-98995c5ebb54 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
1bc17671-cf1c-5423-ba88-09bfa3f56f0b | note | Verification Activity: Activity - H
454bf4fe-bd23-55ed-b3e8-9e1c8817b574 | note | Verification Activity: By - SE
6f02a627-0efa-5c52-bfc6-1db0fde3e838 | checkpoint | 3.1.5 - Pre-Backfill Inspection
e77f1704-9e25-5c33-82d2-09c9dbcbaf60 | note | Detail - Inspection of Structure
f951ec8b-dc9a-5405-91b7-0b06259a0bc3 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
f66efe11-8c35-5953-92b4-943ab3b55648 | note | Standard / Specification - PS- 21.6.11
64af34f4-5cfc-5680-ac8c-58a6c7f63728 | note | Verifying Document - Manhole/Catchpit Record
b27ddea0-6078-5c28-9201-42a353cbad85 | note | Testing Quantity Required (based from schedule qtys) - Continuous
bb2164bf-e8e5-5586-aea5-061af184642d | note | Verification Activity: Activity - I
e5f99403-c158-536d-bfe9-6880cebf1bf7 | note | Verification Activity: By - SE
c35a65d5-6eb2-5191-8c79-ec76f3f7c3b4 | checkpoint | 3.1.6 - Survey
1bf06fba-025e-505c-a887-754d08cdaa1d | note | Detail - Inspection of Structure
eef5d195-346e-560a-9c18-f7ae502040d2 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
3d297368-0aa2-5564-8d83-e1bfe2975029 | note | Standard / Specification - PS- 21.7.6
585535f5-494f-5bcf-901d-dbd9dc20572d | note | Verifying Document - Survey Data
ac82bd90-691d-5db6-a45e-46fcee96c120 | note | Testing Quantity Required (based from schedule qtys) - Continuous
623c6f9c-4701-599d-8589-c1f0211284ec | note | Verification Activity: Activity - H
57afac1e-90f7-56b1-bd39-70911dccf45b | note | Verification Activity: By - SV
e681d924-eb9d-5908-874f-e2a9cfead256 | checkpoint | 3.1.7 - Backfill Compaction Testing
2e8ec344-8cd3-50fa-ab02-e7785f1be849 | note | Detail - On Granular or Cohesive Material
c5251a47-746a-55b5-8328-90325b509eff | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
84724f52-fc63-5dd7-94a8-ed5a9141e72c | note | Standard / Specification - PS- 21.6.12 Appendix V
f06b0520-7e15-5235-8046-70af6152b0c3 | note | Verifying Document - Lab Test Report
001d7a06-1d2a-51f9-a625-fecf948e3e76 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
09b3371e-2d21-5aeb-8089-bc2b2d8f5770 | note | Verification Activity: Activity - H
00e72377-0f35-5af7-9afa-474c27318faf | note | Verification Activity: By - SE
8a67bad2-49a0-5b3e-9e07-3e95e06d76d3 | checkpoint | 3.2.1 - Foundation Compliance
6693aa39-d64e-5264-bf3b-3d30c6fa7822 | note | Detail - On Granular or Cohesive Material
e31f585c-fea8-5cfb-b089-a19c2db76d02 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
b276eb1f-1549-534b-a017-94d90077d154 | note | Standard / Specification - PS- 21.7.2 Appendix V
13cd0b61-a024-5d4e-98e4-6077201c68d9 | note | Verifying Document - Scala test result
ceef2f8c-5d86-5446-963d-a823469e910f | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
433d211f-33cc-5b63-8ae2-b545b77c9e46 | note | Verification Activity: Activity - W
81d04145-5426-5dea-860a-998a8a1ec3b7 | note | Verification Activity: By - SE
5c32e1a0-52b7-5c2e-8003-fdd7656ac09f | checkpoint | 3.2.2 - Undercut approval
ea278464-af9f-5fde-bd25-54d1ce0d139a | note | Detail - On Subgrade
80be3fd5-ac77-51c8-8656-679b043104cb | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
d035fdd2-0e37-5bf8-a24e-00f64ab6f4bd | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
b9dfc0b1-f7d0-5327-9c11-2df9f61ecda5 | note | Verifying Document - Lab Test Report
35c74bc4-0996-5b4f-b771-e9bfaeb3cf92 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
1c526564-e335-52bc-8daa-cd0f240e6fa8 | note | Verification Activity: Activity - H
4bd8b7ba-ea6f-5198-bb35-0097bea43aa0 | note | Verification Activity: By - SE
811e271f-f2a2-52ee-9167-0e158033e720 | checkpoint | 3.2.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
dcadc4d9-96fd-55ca-b0bd-89a8fff7a309 | note | Detail - On Granular Material
175eb5c8-e07a-5b6d-a58f-6695e40e86a8 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
def5d9ef-5cce-5477-9b47-c8546a5d1cb4 | note | Standard / Specification - PS- 16.5.12
7b3b0c16-3de9-53d5-8208-072297668bb8 | note | Verifying Document - Lab Test Report
10fb19b6-58bb-5b0c-ae29-e85d8d061777 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
30199c4e-14ec-592f-8548-0c6d5aded7b3 | note | Verification Activity: Activity - H
e9693bdf-97b2-570b-876d-3ccaed5e26a4 | note | Verification Activity: By - SE
77568fee-af21-5f9b-9f96-160b1a618b0b | checkpoint | 3.2.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
d3385acd-9e7e-55ff-ac08-aa28120b1ea3 | note | Detail - On Granular Material
6d9d584d-97c3-55a6-8e69-b1b64b687153 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
0adbe8b4-10a5-50d1-8637-12fd7870f94b | note | Standard / Specification - PS- 16.5.12
3d74ac21-d6ba-5b18-b993-94bb528d9d7c | note | Verifying Document - Lab Test Report
b1bb2dab-d898-5cd2-aad6-1e93c56ee60d | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
13a9894c-3b43-555f-8001-726e44a83bec | note | Verification Activity: Activity - H
54b0181f-8c7e-5a98-9b96-e51954539c7c | note | Verification Activity: By - SE
ff95eca0-5856-535c-b653-c34444e1d4db | checkpoint | 3.2.5 - Pre-Backfill Inspection
d610233e-42ab-5f87-a8d7-fca5762d01e1 | note | Detail - Inspection of Structure
4f3c5e54-c54a-5214-ac39-374f38f41675 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
02c38837-cfa7-5130-8f2c-4bfe01c5e835 | note | Standard / Specification - PS- 21.6.11
7ce2509c-5fbe-54f8-88f6-a2b46450e743 | note | Verifying Document - Manhole/Catchpit Record
cd972a7b-69e6-5e5f-8399-85ca4a4f4fd5 | note | Testing Quantity Required (based from schedule qtys) - Continuous
fced3349-4f6d-5430-82c9-db793cb555bd | note | Verification Activity: Activity - I
d4e5c9b9-6be9-5d50-8c4f-59798657d98c | note | Verification Activity: By - SE
8438b253-2cbd-5d5d-b5cf-63795fbb55c6 | checkpoint | 3.2.6 - Survey
7bdafb6a-9389-579e-b973-43343bcdadf2 | note | Detail - Inspection of Structure
e865e0af-739a-5375-b99d-123f9ad5c315 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
0e860317-0ff9-5357-afc2-06540e5ba10a | note | Standard / Specification - PS- 21.7.6
66f21632-48c8-54e7-b7ac-9151bd796787 | note | Verifying Document - Survey Data
a0dbbb05-8b70-547b-ba31-519ac1630378 | note | Testing Quantity Required (based from schedule qtys) - Continuous
8f5ce6b7-123f-53d3-9130-bb110ec1b3a1 | note | Verification Activity: Activity - H
c41e2a53-7736-569c-b991-9bd9148cb4be | note | Verification Activity: By - SV
b695541f-0861-5c72-a422-a5c37de96d6a | checkpoint | 3.2.7 - Backfill Compaction Testing
06f3bd12-4223-53d9-b29e-7d06a8343e5e | note | Detail - On Granular or Cohesive Material
8ef45800-36a7-57f2-91cf-a08f6e68c701 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
c253d9db-85d6-5395-99e5-ea5597604fdd | note | Standard / Specification - PS- 21.6.12 Appendix V
d72d5baa-fcce-5be2-833e-294e3bb480d5 | note | Verifying Document - Lab Test Report
f122f1b7-fa5f-58a5-b9ad-f7ca22b1bbea | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
46ee0a82-6c95-556e-8e14-55b3fe15e3f6 | note | Verification Activity: Activity - H
b4c34036-c8c4-53ac-99aa-ab67401f7bc3 | note | Verification Activity: By - SE
300b8fa1-28bb-53b2-8f55-761644c8d091 | checkpoint | 3.3.1 - Foundation Compliance
72b25472-d766-501a-831b-55c9f74ccb4f | note | Detail - On Granular or Cohesive Material
930b3a55-fefd-5113-b05d-16fd1c509667 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
d0feac88-eb37-517f-a9b7-520293a67e61 | note | Standard / Specification - PS- 21.7.2 Appendix V
a2b06bbd-6854-5815-880c-d7cf839fef59 | note | Verifying Document - Scala test result
6e33f9c1-30e4-5561-b3cf-a235a3921534 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
f1767cdd-3d25-53fc-a759-9694a9376d59 | note | Verification Activity: Activity - W
eb8d5159-f0aa-5677-8701-777298379968 | note | Verification Activity: By - SE
dff5ee8a-9019-5036-bebf-6f91dc5f062c | checkpoint | 3.3.2 - Undercut approval
62f7f656-3915-5fe1-999b-b1c784c58bb2 | note | Detail - On Subgrade
18aad1f8-a05d-569e-bd6f-f312c8237b7a | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
94915bbc-9276-53e4-ae92-1debd9c4e928 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
835a9559-1b67-550a-b55f-8e55eb2dfd68 | note | Verifying Document - Lab Test Report
79397d05-e464-55ed-adaa-ed48e7df704b | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
a845de8f-a05a-5d34-b04f-b007ea7876b8 | note | Verification Activity: Activity - H
b437dfd3-46d2-5a26-9ad5-98ccea8c7a11 | note | Verification Activity: By - SE
19146973-bab4-5555-ab24-77b09a0bbffe | checkpoint | 3.3.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
bf7449a2-e26c-52e5-a4e1-4804e01160c8 | note | Detail - On Granular Material
422260c0-3c73-5bec-9a50-24b474648e95 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
c4f86e78-aa99-59f3-96c8-0b5c9589c87b | note | Standard / Specification - PS- 16.5.12
0933885b-432e-5287-869b-39cee23cc6ce | note | Verifying Document - Lab Test Report
e9a47674-39d2-583b-8646-550672af1e8a | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
7f9eb0b6-750c-5889-a74a-664d89746c81 | note | Verification Activity: Activity - H
78779cd2-0f31-5357-b747-116add696165 | note | Verification Activity: By - SE
94a0623a-421b-55f6-bfcc-21a724ec9dfb | checkpoint | 3.3.4 - Bedding and Embedment Zone Compaction Testing (Polypropylene(civil boss)/Polyethylene Pipe).
5d6416a8-6629-59b5-8972-8054db23e34f | note | Detail - On Granular Material
b56a5fbf-25c2-5138-ae4c-a3a9acc94f41 | note | Acceptance / Conformance Criteria - Bedding Zone: 100mm(for DN300 & DN375) 150mm (for pipes greater than DN375) Embedment Zone: Pipe Dia ≤450 - 150mm GAP20/AP20 - Overlay Pipe Dia 450< D ≤900 - 150mm GAP20/AP20 - Overlay Pipe Dia 900< D ≤4000 - 150mm GAP20/AP20 - Overlay Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
b6dc7386-bcd0-5a96-b0db-e9b815586e18 | note | Standard / Specification - PS- Table 21.7 PS- Table 21.12 AS/NZS 2566.2/2002
98cbd37d-a6ae-5726-b7a6-b8c811e85d8e | note | Verifying Document - Lab Test Report
c9022001-0066-5752-9f30-29dec6664249 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
eb703980-b343-5b35-b4e9-ae266e81c5a2 | note | Verification Activity: Activity - H
08b1c655-664d-5fad-ba55-b191d3419185 | note | Verification Activity: By - SE
d2e13628-b927-50fd-ad8e-db3f761f1f7d | checkpoint | 3.3.5 - Survey
4f14edc7-e9a4-52f1-86c5-798205a9be33 | note | Detail - Surveyor to Setout
9aaf4ffb-8a34-55c0-9b8f-534553d3a398 | note | Acceptance / Conformance Criteria - Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance
5f46781b-fac3-5535-b0f7-4236485214f6 | note | Standard / Specification - PS- 21.7.6 Table 21.15
29691daf-2cec-5dbc-9554-fd4dd5340e7a | note | Verifying Document - Survey Data
aa9af37a-13a7-5b98-8ca2-93763c070541 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
7ca755d6-9e4e-5c08-b7bf-60dfcec72b9b | note | Verification Activity: Activity - H
bb14b4d7-ca9b-55e5-93d4-c48df3421efe | note | Verification Activity: By - SV
652c96e1-768e-5161-abb8-33857043d37c | checkpoint | 3.3.6 - Backfill Compaction Testing
47ca7528-0d20-5fce-992c-8c0031ca4e99 | note | Detail - On Granular or Cohesive Material
32176970-0811-5c42-91cb-991b95a0281d | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
9842a3cd-5db2-54d5-865d-b6f862a0a05c | note | Standard / Specification - PS- 21.6.12 Appendix V
a5d78d5b-202b-5f3c-a550-fd62b25bd144 | note | Verifying Document - Lab Test Report
e7439544-899e-5b79-8ee2-d2bb641a8f06 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
1aae88bf-61ef-5403-97bf-80a113807d94 | note | Verification Activity: Activity - H
43b502f6-f5ba-5206-a0fc-688b56775d8c | note | Verification Activity: By - SE
276798c2-34e6-5e87-bb66-a7f7df9fa38c | checkpoint | 3.3.7 - Pipe Inspection
a06df628-6013-57d7-a7ac-1babe6b7f651 | note | Detail - Inspection of Drainage line
ec6eb0af-4baf-5fab-9b74-5626aa4d40db | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
19d27f5f-351b-5aeb-9ea9-d95200a9b1fc | note | Standard / Specification - PS- 21.7.6
e1c1c3c9-58ca-56b4-85d0-e418d334d0b5 | note | Verifying Document - Drainage line record
5aa69d23-1991-58b1-9a59-332e16116508 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
c091935b-68ff-51ce-98cb-936e9c5d13fa | note | Verification Activity: Activity - I
73b2bb90-7fd3-5df0-b0d5-4a0cbfb04bb8 | note | Verification Activity: By - SE
23e48d28-c984-5a1a-adf0-687888856fce | checkpoint | 3.4.1 - Foundation Compliance
b1f82680-2f23-507d-87ef-07e955ead30f | note | Detail - On Granular or Cohesive Material
1b93c683-9a16-58d4-ac1b-397eeb6713a0 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
294224ec-429c-56f6-b1f4-926c48f6aedf | note | Standard / Specification - PS- 21.7.2 Appendix V
d9e02b9a-d672-52e5-a7bf-b568f7a18e0a | note | Verifying Document - Scala test result
5e9520af-5a32-5a5c-9585-f45b773a33cd | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
2499b3ea-793c-5c4b-8fa9-3064a06065b4 | note | Verification Activity: Activity - W
2a5383b3-1ae7-58cb-9ef3-97ba0f35a866 | note | Verification Activity: By - SE
2e297fed-b0b9-5c9a-82c6-da43f519fdc6 | checkpoint | 3.4.2 - Undercut approval
545f6878-eea1-53de-b124-115e4bea2d50 | note | Detail - On Subgrade
10340e4e-6257-5290-b88f-6e40d6a7a12f | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
edb7d806-2d41-5542-98c4-eb52582f365d | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
093f5f9a-3816-5de1-ac1c-6e9fcd02705d | note | Verifying Document - Lab Test Report
80a49d8c-ebb7-5b16-9ca8-d1dcf9e87a49 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
bd67af40-cd47-5271-84e1-b2da193705be | note | Verification Activity: Activity - H
f625d731-0e13-5d69-948e-c653bdc205df | note | Verification Activity: By - SE
34f0d9ca-7f76-56e1-a2e3-84ec7ac51186 | checkpoint | 3.4.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
1cde9d5b-6e5b-51b0-96b1-89b50215cdf0 | note | Detail - On Granular Material
ecfefb9b-e1e0-5eab-90d9-373d1bcda7be | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
53de2b2f-1021-5d68-a804-5faae55e6841 | note | Standard / Specification - PS- 16.5.12
7e978c77-060f-54fb-ae26-91a16b8ef59b | note | Verifying Document - Lab Test Report
2cdd3332-b236-51b5-8327-796aa39199f1 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
6162c2a1-63a8-57fb-bb0b-7622e1405e38 | note | Verification Activity: Activity - H
173f5d3c-1b2b-5dcc-a2ac-58c7bfbe497c | note | Verification Activity: By - SE
5d768dd2-9cd0-5756-bb3c-505106479de8 | checkpoint | 3.4.4 - Bedding Compaction Testing
e0d9eb16-66df-5645-8e1f-d4e3c38dda8b | note | Detail - On Granular Material
99b11551-54e4-54cd-a53d-cad405368fc6 | note | Acceptance / Conformance Criteria - HS2- 0.3xD (outer dia of the pipe) Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
b2a1e921-a6a9-5310-bcf0-49ace4543ca2 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
98f34698-29eb-5684-b946-231b0b1fdad6 | note | Verifying Document - Lab Test Report
1a08ef5d-a3eb-55f8-a583-415abebb5504 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
9aa15384-64ca-56a3-a1a5-704acaf63829 | note | Verification Activity: Activity - H
19ee0ce2-d1ad-586f-81ea-517090fdf8fa | note | Verification Activity: By - SE
4bfe46f7-744f-55e6-8523-2ea18484410b | checkpoint | 3.4.5 - Haunch Zone Compaction Testing
224e6c9d-bdd6-531f-9a04-548031bde3a1 | note | Detail - On Granular Material
75f3cb6e-0698-5a92-8841-e0e9a35055a8 | note | Acceptance / Conformance Criteria - HS2- 100mm if D≤1500 (or) 150mm if D≥1500 Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
ed49a71e-fcd5-53e6-9ca9-d990f1cff0d2 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
cf4d2da9-bd55-5f3f-9c41-662eaa888790 | note | Verifying Document - Lab Test Report
f0be1216-6c9e-51d9-9af2-b2e776e44c86 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
9efd0274-a60a-57ba-b9ef-ccb4abbf1e5c | note | Verification Activity: Activity - H
e36eb1a9-5762-5ddc-ab87-3a11d36356ff | note | Verification Activity: By - SE
4844df56-a700-5e51-ab74-6839a6589fc8 | checkpoint | 3.4.6 - Side Zone Compaction Testing
045cfc2d-e067-5c0d-b7ee-3de5ee0a51c0 | note | Detail - On Granular Material
902bb784-8f80-55d7-a628-ba068f696b5a | note | Acceptance / Conformance Criteria - HS2- 100mm if D≤1500 (or) 150mm if D≥1500 Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
197bfed8-4df7-5d6b-896c-bc9e643a3fe5 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
22a9f67b-954c-5a70-a4be-1ea07b3eec27 | note | Verifying Document - Lab Test Report
bd0aa8a8-2d6a-56f4-9da3-955b0d0bec8e | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
02a51015-539b-5496-a1d6-cca46e19783f | note | Verification Activity: Activity - H
c0f448f2-ef13-57ec-b25e-67d5360e370b | note | Verification Activity: By - SE
43578e81-672f-5d7a-9d20-9ac1e812a489 | checkpoint | 3.4.7 - Survey
f110438e-dbb1-5f27-b476-ad22c584065f | note | Detail - Surveyor to Setout
d13b1de4-0a4a-55fc-ba7f-1bcf383fe023 | note | Acceptance / Conformance Criteria - Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance
a7bf3aa8-13db-5519-a403-e2e43b483e2f | note | Standard / Specification - PS- 21.7.6 Table 21.15
551d7c42-81f9-5cef-aaec-1839171717f6 | note | Verifying Document - Survey Data
6c9ae2f8-ce02-5e92-82d0-2782494c2f06 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
02243be4-0538-547e-8fa3-672b12b7beb2 | note | Verification Activity: Activity - H
3a82526b-f26f-58bf-8e47-1f813a1487b8 | note | Verification Activity: By - SV
b1c5561f-735f-5ab9-80a5-52eccf1118e5 | checkpoint | 3.4.8 - Overlay Zone Compaction Testing
21620ddf-4f86-5dfe-932a-8b6316603fe3 | note | Detail - On Granular Material
dfcd6cd6-66e2-538b-8a8c-67d72e089686 | note | Acceptance / Conformance Criteria - Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
33243dda-43bd-581c-8039-3e52aeb08f27 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
f8e50a62-3f10-5546-a417-21c635152588 | note | Verifying Document - Lab Test Report
431e22ce-c629-529b-b9ad-fb11b917760c | note | Testing Quantity Required (based from schedule qtys) - One test per 30m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 1 Tests 0m-50m: 3 Tests 0m-100m: 5 Test
d6b81813-19b0-5eb9-ab7d-2e630aa5a232 | note | Verification Activity: Activity - H
fa87cd6f-f03c-5fd2-866d-130718e89598 | note | Verification Activity: By - SE
1b1ebc88-e4b8-502f-a958-3dcc4a007de4 | checkpoint | 3.4.9 - Backfill Compaction Testing
6a094b79-1e76-5958-8703-4e9310286b05 | note | Detail - On Granular or Cohesive Material
11097803-d3b1-5322-8840-d9c50d0ca5dc | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
cc1b8541-1fae-502d-a986-042fb92fef01 | note | Standard / Specification - PS- 21.6.12 Appendix V
7398fa83-6c42-5e52-9853-413853c200c4 | note | Verifying Document - Lab Test Report
8e68f238-4b88-503f-a35e-a4968b197090 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
1fe264f1-fced-5c9e-92b3-e784ab8ea9c3 | note | Verification Activity: Activity - H
4616e0ce-8c25-596f-a21b-a6bea2533fe2 | note | Verification Activity: By - SE
b758dbb4-248e-55bb-94cc-12a4cac84109 | checkpoint | 3.4.10 - Pipe Inspection
8d62a9ca-2cb4-51ee-8612-9cfdecb7cd6d | note | Detail - Inspection of Drainage line
7390c541-2715-5937-a0fc-79281c4f4290 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
c70214f0-30f1-5268-ad19-c6148d2aae66 | note | Standard / Specification - PS- 21.7.6
ae3d6d27-9844-5c17-ba83-d851b62db0a8 | note | Verifying Document - Drainage line record
cc65bc02-bfd1-54ff-a5a1-a937d0a7af29 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
85044673-0283-5e56-bae4-211e54ff9e8a | note | Verification Activity: Activity - I
5d0e0b52-3d6f-54c9-b7b1-24e898dd5b39 | note | Verification Activity: By - SE
a76d1aac-996b-561a-bc2b-69470a3fa996 | checkpoint | 3.5.1 - Headwall and Wingwall Foundation Compliance
f78edb06-81df-5055-a7c6-22d019d7c9d4 | note | Detail - On Granular or Cohesive Material
97596680-55f9-5a46-8ce9-b8b1984f656d | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
161eaefd-8b47-59b9-b777-387959290641 | note | Standard / Specification - PS- 21.7.2 Appendix V
7b8e1d0e-bdaf-5c20-8b28-cafdadd6986c | note | Verifying Document - Scala test result
e03bdc2e-8294-534f-a613-5a33f65f7bd0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Structure
2040fe92-1fb9-507d-b744-8496efceebd4 | note | Verification Activity: Activity - HP
b7f8addb-ca48-546f-a551-113c91e28417 | note | Verification Activity: By - ENG
70cd1be4-24ef-5063-abbf-f9dd93200e27 | signoff | AUTHORITY HOLDPOINT
f0688442-75bc-5d76-8177-3a9f6ee2134e | checkpoint | 3.5.2 - Undercut approval
ef0cd571-aeb0-54e9-9e9e-19dd57cc235e | note | Detail - On Subgrade
bb14ca25-4957-5fc9-8545-89ff1c784f8a | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
655ae977-f498-5805-a035-bc4288e7a720 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
05a01e9c-c880-52f5-94aa-0b63f931fedb | note | Verifying Document - Lab Test Report
a9411a00-5910-5970-aa31-7e3d6790cf9c | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
b06f7107-af61-5bfb-bf17-3763ded23ba6 | note | Verification Activity: Activity - H
95be9e29-2675-5975-90ba-ec47a2d96f0e | note | Verification Activity: By - SE
2478973b-6f47-5310-9ffd-14c721927804 | checkpoint | 3.5.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
5042d307-9abd-5707-9605-d866128daf16 | note | Detail - On Granular Material
fa542ca6-6552-5098-94cd-791e525997ec | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
b9cbfc1c-82d8-5684-822f-dad934367fa1 | note | Standard / Specification - PS- 16.5.12
23883edc-8bb5-5cf2-ba08-227d467d0ee7 | note | Verifying Document - Lab Test Report
bdb4fb1d-8f73-5155-b396-f6c9d5bfd867 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
94f59778-160b-5167-ab93-15cf962ff3fd | note | Verification Activity: Activity - H
24812b13-38e5-58c8-91de-caf926e6101b | note | Verification Activity: By - SE
4ba0a161-7530-58d1-afea-40100c2ddf2a | checkpoint | 3.5.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
aa4eae94-8e84-57e9-bc40-c0b6b8009d56 | note | Detail - On Granular Material
eba0b638-dba3-5c2a-ab67-2e5b677eedea | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
c6897a67-2e80-5b1d-8f91-4aed91d56933 | note | Standard / Specification - PS- 16.5.12
bb90d2cb-a8b6-530d-b551-b981361468b1 | note | Verifying Document - Lab Test Report
71ae2f59-a3e0-51c5-a2e9-f2c0861accbe | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Structure
c0bf7afb-a77e-5085-943d-ab34d9e6b8ef | note | Verification Activity: Activity - H
16e83c92-8258-53c7-be6e-bd8f2bc5bf7b | note | Verification Activity: By - SE
67a6cf71-f8c4-51e4-a8e6-ca7a915ab61e | checkpoint | 3.5.5 - Pre-Backfill Inspection
c9139488-9c15-5b76-a7ac-fe17a6e366e7 | note | Detail - Inspection of Structure
83687d12-36a9-5e3d-92c8-897dcf39c5fc | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
734c6fe9-b6e4-52ea-8756-b95c074ba38f | note | Standard / Specification - PS- 21.6.11
8180e4c1-c5b4-5603-94e3-0a2f84fec26b | note | Verifying Document - Manhole/Catchpit Record
9e476b44-9580-5f7d-8534-13388d2f8daa | note | Testing Quantity Required (based from schedule qtys) - Continuous
8e9a0637-842a-5346-80d7-c99da18b9f0a | note | Verification Activity: Activity - I
4b91cc23-a269-5d77-b7ac-8accd37f2e43 | note | Verification Activity: By - SE
d18baf16-8975-5e0c-8261-32049d9f49aa | checkpoint | 3.5.6 - Survey
84f9a34c-796e-57ed-b114-985940468f9f | note | Detail - Inspection of Structure
5711b32e-0f22-5f39-a7c7-b4e77ea77a32 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
a48f22c0-7cdb-59b4-afec-1a8992a98a71 | note | Standard / Specification - PS- 21.7.6
e95723be-0632-52be-9f6d-f854b5b07e04 | note | Verifying Document - Survey Data
ff404fa2-d32e-5ed9-8635-b5305ae93854 | note | Testing Quantity Required (based from schedule qtys) - Continuous
29a1340b-6e42-5360-b910-b3b22a11e517 | note | Verification Activity: Activity - H
ce76f530-653d-59ae-8e7a-47f935139969 | note | Verification Activity: By - SV
dc025cac-6aca-58ae-b492-06adb07f8de3 | checkpoint | 3.5.7 - Backfill Compaction Testing
1346e21b-2fef-5562-85ac-4cea3a579f77 | note | Detail - On Granular or Cohesive Material
71051c6d-4c93-52d4-b996-5076b9fb16d6 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
3195505d-e3f2-5348-baf9-25ab49003165 | note | Standard / Specification - PS- 21.6.12 Appendix V
14bcfe6b-29c5-53b7-9ba1-74dbebc17739 | note | Verifying Document - Lab Test Report
3b096be4-1256-5002-a55a-71e8231fb4d7 | note | Testing Quantity Required (based from schedule qtys) - 1 test per layer at Quarter Points around the Structure.
4039098c-fb29-5e32-91ac-91c844648db6 | note | Verification Activity: Activity - H
81f698d1-a27d-5d65-bc46-6da8159ee841 | note | Verification Activity: By - SE
909aaa35-1436-5b32-b06b-9bd5efa45dfb | checkpoint | 3.6.1 - Riprap Foundation Compliance
8c982575-8f2c-59c1-977e-c25c39d64f25 | note | Detail - On Granular or Cohesive Material
2bb8285c-229b-54fb-97ec-f833ba6be8f1 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
dc955bbc-9a3d-593e-9962-9c82ee33751b | note | Standard / Specification - PS- 21.7.2 Appendix V
9add7a5a-96f2-581e-bc0c-7dcc547c8131 | note | Verifying Document - Scala test result
458d268d-c5ce-58a1-acdd-6a0e85e5b93b | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
4265f2e4-0470-5cd6-99c9-d0fbed85396e | note | Verification Activity: Activity - W
8e3ec2d6-cb8b-5d7a-82ad-f27f70273460 | note | Verification Activity: By - SE
c318d5a2-491c-50a3-a033-e6f98e6800b5 | checkpoint | 3.6.2 - Undercut approval
0e8c63a4-8c7b-5557-b780-b6bd4f412b40 | note | Detail - On Subgrade
d618f982-fedd-5c90-b8c8-6f337bd942df | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
f89839c8-0e55-5a32-849f-7799c50c9639 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
e53943a5-601a-5adb-aca0-5d36125067c9 | note | Verifying Document - Lab Test Report
7b1e4c0b-e56c-5662-88b8-11aaf8368b70 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
67d32ada-8318-541d-aff5-31b1a35b74fa | note | Verification Activity: Activity - H
5445342b-5422-5140-9aec-4eed0f9bebf4 | note | Verification Activity: By - SE
6a55d5f9-a096-5d22-bb1c-56e2e00cb6d1 | checkpoint | 3.6.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
4d27efe5-19d0-50e1-8ef6-50037e431090 | note | Detail - On Granular Material
1cc127d0-0a40-512c-8ee3-73acb8f02810 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
27b92731-ded7-54d5-9e34-9ba001b42097 | note | Standard / Specification - PS- 16.5.12
a2064463-78e9-5070-a08b-0d3b645233d1 | note | Verifying Document - Lab Test Report
930351f6-ec88-51bc-8c2d-be40d14ef1cb | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
673ded28-b7af-5da6-9048-05f86cacdd96 | note | Verification Activity: Activity - H
92b90047-732d-5e91-8a1b-0c821b01b370 | note | Verification Activity: By - SE
70aa118b-5499-55a2-88d1-6a112d0eb702 | checkpoint | 3.7.1 - CCTV Inspection
46c6bdc6-2aae-5108-affc-809fef37f6fd | note | Detail - CCTV stormwater pipes at completion of trench backfill but prior to final surfacing (pavements, etc.)
ccd8b0cc-b65c-5d2e-a6da-a6fe7b42fda4 | note | Acceptance / Conformance Criteria - Every stormwater pipeline 225mm diameter or greater.
162700d6-751b-549a-96a9-86215702274a | note | Standard / Specification - PS- 21.7.6 PS- 21.7.8
d89f7f1c-f83f-5c38-982b-be558f2eb986 | note | Verifying Document - CCTV Report
5bfeab30-8546-5182-ad77-d2a8f0024b72 | note | Testing Quantity Required (based from schedule qtys) - 1 per line
5a19d298-49c6-5d79-ab44-c505a060d77c | note | Verification Activity: Activity - S
3af3faf7-912c-5633-8f2a-a41081eb6280 | note | Verification Activity: By - PE
84c3283d-24bd-504e-b593-7adb2a662256 | section | SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
13049da8-dc5f-50e6-9653-61f13f53ec94 | checkpoint | 4.1.1 - Survey As-Builts
43405ff8-93a4-578f-8245-80b6a0ba30db | note | Detail - Quality Check on New Works based on the tolerances in RITS
75fa7eec-e69c-5510-a9fd-4d65f0dc461d | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
7e5788d2-50c9-52f4-bf02-4a7eda67d156 | note | Standard / Specification - PS-21.7.7
5fe67f93-427a-59b5-ae3e-31e8cfcf0324 | note | Verifying Document - Red pen markup only
91e56975-23b2-52d3-a796-4e4e6b9d9e16 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
7b449813-211a-5938-b86c-3592cb4fb49a | note | Verification Activity: Activity - H
84f4cb19-b321-5af5-81b4-05813f1cc00d | note | Verification Activity: By - SE
cb6ba0b2-0793-4a89-a8bd-eb5bb3818a9f | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
23a52ea0-c0a3-58f6-a912-c89c733a0219 | textbox | Contractor's Rep Name:
e566d123-07cf-5568-93a5-76ca2c9dd9fc | textbox | Engineer's Rep. Name:
95981a3f-70e7-52bc-bd38-a2aa23047133 | date | Date:
d6eef712-edbd-4cd5-8ca8-0e8534f86864 | signoff | Add Signature
453dec8d-3ba2-448a-b765-0fee0b726515 | checklist | Ω (DEPRECATED) DN1210-0007 ITP Stormwater Rev 0 (v1) | itp | DN1210-007 ITP Stormwater Rev 0
9dbf9507-d5c1-5f76-b0e9-632a875b7d7c | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
61faafb8-e067-5299-84f0-3fd60960e68e | checkpoint | 1.1.1 - Extent of Line Setout
8c6ec2f9-39bd-56e6-af44-d2517ac396f2 | note | Detail - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Stormwater drawings. Identify any clashes before construction.
7d6a7e91-0e37-5917-8fba-1a8a1eefae57 | note | Acceptance / Conformance Criteria - Engineers Approval
e5fee9e3-7922-574d-92a5-7ffc18141aab | note | Standard / Specification - Design Drawings
44187e60-7257-5c43-8598-469a199c8f58 | note | Verifying Document - ITP Sign Off
1f14d97f-faf6-5369-b434-80379019109a | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
8b6e67aa-6aa6-5b21-9bfd-9a3eb29a45ee | note | Verification Activity: Activity - M
a97d5839-1e49-59fa-b864-a3a67cc79564 | note | Verification Activity: By - PE
58d8e667-bb88-509f-83a3-6a1f01d0e239 | checkpoint | 1.1.2 - Existing Stormwater system
49e460ff-036a-53b2-b79f-9c99f6652733 | note | Detail - Confirmation of existing stormwater network.
42c9dd57-cc47-5267-b8e0-a6a8918f72a0 | note | Acceptance / Conformance Criteria - Survey Informations
7a99dc1c-fb5a-5edd-876e-c469c1399ebf | note | Standard / Specification - Appendix V
741ac5b0-1750-5d08-89d8-999292956bf0 | note | Verifying Document - Survey data
39a0f032-457e-5f57-abda-8c2115ba5d0c | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
3651724b-6601-57d2-9532-88e9342cce24 | note | Verification Activity: Activity - HP
1684a043-6be9-57cd-a4e1-b987c3933cc0 | note | Verification Activity: By - ENG
439eb8b4-e232-503c-ae3b-29d0c5635540 | signoff | AUTHORITY HOLDPOINT
b2505ca3-943c-534d-afb7-23e310ef1e65 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
7b779b30-3202-5976-a674-5a18e46af7e0 | checkpoint | 2.1.1 - Material grading: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
1f334567-e26c-5615-a6c5-437f663ff8bd | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
24d05b84-18e6-5631-89c4-8498e20aed26 | note | Acceptance / Conformance Criteria - Stockpile size 1500 to 4000m3. PS- Table 21.2 for GAP/AP20 PS- Table 20.3 for Overlay and Embedment Zone Material NZTA F/6 for Drainage Aggregate- Grading section 2.2
5c9ddec3-cfba-5a3a-924a-5cd74196e283 | note | Standard / Specification - PS-21.7.2
a3371f70-425c-5a18-9783-f9204e2236fa | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
0cbe2752-5826-50eb-837c-fe29a51d166f | note | Testing Quantity Required (based from schedule qtys) - 4 Test 1 Test for each additional 1000m3
f33c1220-9cf8-5e0f-b2f5-9a13930a12cb | note | Verification Activity: Activity - HP
daa93a5e-c9ac-5db2-a1d1-769932c9e987 | note | Verification Activity: By - ENG
d9a47fe7-92b9-5d7e-ba3b-89916ba64f50 | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
4aeddbe8-5560-52d8-adc7-e338b59829ce | signoff | AUTHORITY HOLDPOINT
8d324d50-cc82-585e-af30-1900442f0418 | checkpoint | 2.1.2 - Weathering index: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
3e9433c2-8416-541a-9b8e-f94896d44afd | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
02556238-6038-5fd8-b6ca-daae3b6dab89 | note | Acceptance / Conformance Criteria - Engineers Approval AA to CA
aaddeb8c-95ff-56d6-9a6f-3409bffb689d | note | Standard / Specification - PS-21.7.2
189140fd-eb19-5a38-9198-6caffd786c65 | note | Verifying Document - Lab Test Report NZS 4407.3.11
da98e593-24a7-5f5a-8ce9-7c74c81324f7 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
792e2727-8b39-5b9a-b169-fd5e24df259b | note | Verification Activity: Activity - HP
cd225301-feb2-5a18-90ba-b565d40136e9 | note | Verification Activity: By - ENG
b934f0f0-a41c-5df1-9909-a98c6e8a0321 | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
a2fc101a-90b9-54e1-89a9-1383075ee775 | signoff | AUTHORITY HOLDPOINT
5c6967dd-7748-5877-a08e-26c0fca616fa | checkpoint | 2.1.3 - Crushing Resistance: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
42790e68-27b0-5257-b87e-1982f42796e2 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
984bb7bc-4f10-5043-80f2-d40e640bf675 | note | Acceptance / Conformance Criteria - Engineers Approval >100kN
e3bb4083-971b-55a2-9772-0a0a21cf7749 | note | Standard / Specification - PS-21.7.2
0a7679d5-39c2-5de1-b95d-39ec647eab43 | note | Verifying Document - Lab Test Report NZS 4407.3.10
7b856239-6bd6-5372-9166-20d22ad5dee5 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
8585d6ff-4e91-5a30-8302-655099e0e606 | note | Verification Activity: Activity - HP
2648d9d0-a0ed-5b83-8385-c18a55813457 | note | Verification Activity: By - ENG
65121ca3-b1e1-5e4a-a887-0a084d4ac8bf | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
cbd04506-6cf4-5b18-9ff7-c44dfcd7f02d | signoff | AUTHORITY HOLDPOINT
7191560b-5e9b-500b-8294-b06ed11c768b | checkpoint | 2.1.4 - Geotextile/Geogrid
6edffe58-5601-5dee-9731-a95829301d91 | note | Detail - Minimum Strength Class C & Filter Class 1 or TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
3a4e22eb-c194-507d-ad79-45831776f912 | note | Acceptance / Conformance Criteria - Engineers Site Representative to inspect trench.
ea038197-1b00-5782-8df6-03b39f7859d3 | note | Standard / Specification - PS-16.5.7
45a7f083-9498-53f2-b122-3e13010cc7d0 | note | Verifying Document - Certification
0f9de01c-864c-5a5d-9a87-6273d2f836c7 | note | Testing Quantity Required (based from schedule qtys) - 1 time
7bd65c91-8676-53ea-80aa-104dd809277c | note | Verification Activity: Activity - HP
70bcf854-abb5-5221-9218-490224e68a4a | note | Verification Activity: By - ENG
b25b3fba-56ef-5a01-97a4-28b869a99641 | signoff | AUTHORITY HOLDPOINT
d353cea1-760b-54fc-ba9d-3f6628ef5bc6 | checkpoint | 2.2.1 - Riprap test Criteria
d286ec9a-b058-5a28-8a8f-00cf21213193 | note | Detail - Weathering Index of Coarse Aggregate.
b4077272-8d75-5913-bca2-1bfc527d262e | note | Acceptance / Conformance Criteria - Engineers Approval AA to CA
4831fecc-6eb9-5f1b-81f3-d46c6f6c69d7 | note | Standard / Specification - PS-21.7.4
68a6c4d8-cf61-50c7-9b19-fe178bdd7042 | note | Verifying Document - Lab Test Report NZS4407.3.11
a816cfe2-2037-516c-975a-ca474f1f903b | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
8657b15f-6259-5bf9-ae34-67f8613f7f29 | note | Verification Activity: Activity - HP
ad7dd6dd-66e5-55cd-bffa-63ca75e31be6 | note | Verification Activity: By - ENG
c2623d1f-bd3a-5637-bac9-0bae411ac607 | signoff | AUTHORITY HOLDPOINT
37c23bd2-a3fb-5b1c-be0c-98555e939a1c | checkpoint | 2.2.2 - Riprap test Criteria
1f2b2ecb-2e9e-536c-b013-fa147e18aea2 | note | Detail - Crushing Resistance of Course Aggregate.
9f617669-633c-5613-b494-287a0eaa94a0 | note | Acceptance / Conformance Criteria - Engineers Approval > 150kN
9238c7ab-8930-54a1-9a16-5efa91586e06 | note | Standard / Specification - PS-21.7.4
c6746b54-5e95-5509-bcff-cf78f24161d7 | note | Verifying Document - Lab Test Report NZS4407.3.10
8b24e29e-64a0-5fbb-a080-7de232bfbf75 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
fc644247-06a4-507e-a5ac-029409aa04df | note | Verification Activity: Activity - HP
498ea4f1-b4e1-51d9-a137-bfa5469497d6 | note | Verification Activity: By - ENG
1ac63ecd-b84e-5578-bb6f-a120cffbdda3 | signoff | AUTHORITY HOLDPOINT
b0917513-6283-539a-acb3-a2b3aa920522 | checkpoint | 2.2.3 - Riprap test Criteria
d628b4fa-a5af-504b-a446-56451c012aa7 | note | Detail - Solid Density of Aggregate.
dfdbff3b-306e-5700-8fe9-fd39b874d80c | note | Acceptance / Conformance Criteria - Engineers Approval ≥ 2.65 tonnes per m3
a4334eca-ba29-5bde-8260-79e987fe1d3b | note | Standard / Specification - PS-21.7.4
25932fa2-7703-56ba-83e1-059a9132add0 | note | Verifying Document - Lab Test Report NZS4407.3.7.1
2187692d-ece8-5d53-8ef4-159ba70b2333 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
7bfc33aa-87c5-5816-965d-d04b52316581 | note | Verification Activity: Activity - HP
df1af21a-0031-5b1e-bf94-ec72f87e1906 | note | Verification Activity: By - ENG
a590b01d-a0ea-50ef-b3d0-57465bb74403 | signoff | AUTHORITY HOLDPOINT
5317a3a0-6700-5834-a89f-bd6ef24b9bf5 | checkpoint | 2.2.4 - Riprap test Criteria
12f0ae57-b248-5298-9aef-21cb5140cd53 | note | Detail - Grading of the material.
73ec9ed6-31a3-5759-9d8e-af6d74715b93 | note | Acceptance / Conformance Criteria - D=50 150mm Riprap Grading Aperture Size- 230mm Aperture Size- 150mm Aperture Size- 95mm
002fa807-2c30-50a7-8e68-c20a54016e80 | note | Standard / Specification - PS-21.7.4 PS-21.5.14 Table 21.3
09758b78-075b-5f15-baa0-097393ff974e | note | Verifying Document - Lab Test Report NZS4407.3.8.2
11292c02-362a-584d-a56b-3f927be37292 | note | Testing Quantity Required (based from schedule qtys) - Percentage passing- 85 Percentage passing- 50 Percentage passing- 15
d31ca261-8d16-5930-bafd-7c13e256dbb1 | note | Verification Activity: Activity - HP
588d5b23-fad5-5711-97aa-fb690e88338a | note | Verification Activity: By - ENG
947ebb05-cb3d-5cbb-9402-8ca942d558c0 | signoff | AUTHORITY HOLDPOINT
98285b74-1d71-57f6-9977-ee088beb181f | checkpoint | 2.2.5 - Riprap test Criteria
255e8990-7914-5fa5-b163-eeb7f68c9963 | note | Detail - Point Load Strength.
2d7082ac-318b-59a1-8cce-77a95e658c7d | note | Acceptance / Conformance Criteria - Engineers Approval >1.5 Mpa
15ba3521-b680-5a07-b9aa-b31840006f30 | note | Standard / Specification - PS-21.7.4
f033c320-d8d9-55fe-821c-b40d10e4aa59 | note | Verifying Document - Lab Test Report ASTM D5731
619db733-dd8a-59a0-a845-0888aa125eba | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
3d026438-f16a-5d68-af72-5e85aeb86337 | note | Verification Activity: Activity - HP
87a4d598-27dc-5715-b148-458db0082944 | note | Verification Activity: By - ENG
0063bf6f-94a0-5293-8cea-55db2d898e31 | signoff | AUTHORITY HOLDPOINT
c58e1f7b-cdec-556d-b433-f2dbfce36ed4 | checkpoint | 2.2.6 - Riprap test Criteria
e4203914-0330-590b-a5e6-017784aba336 | note | Detail - UCS Rock
bde3dda1-6f3b-5ec4-a027-5d616f175f23 | note | Acceptance / Conformance Criteria - Engineers Approval >30 Mpa
2f9f77e7-86b8-5c19-b6fd-8c5a2a960825 | note | Standard / Specification - PS-21.7.4
8ef95ebd-fef6-5403-acc8-27880f47e268 | note | Verifying Document - Lab Test Report AS4133.4.2.1
ea339cdb-416c-5b18-8a8b-d996a77051ce | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
0e0d3efd-5dd0-5a5f-ad8c-7c6c66e92c9b | note | Verification Activity: Activity - HP
351f00b1-ec78-5d7f-add6-76cb4b6e545a | note | Verification Activity: By - ENG
ebf02735-8f7e-512d-8e6c-9d466034bd52 | signoff | AUTHORITY HOLDPOINT
7685f2ef-c62e-5fb7-a70f-d353bd416788 | checkpoint | 2.3.1 - Pipe and fittings. (uPVC SN16, PVC, PP, PE and Concrete pipe).
b01a1fdd-980f-57b1-be0a-974d4f3bb258 | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
4c191b62-9e9e-5c94-be52-070246d48b7a | note | Acceptance / Conformance Criteria - Site Engineer Approval
8d5cf5a8-4e17-5231-a5b6-ca8dd8ec696a | note | Standard / Specification - PS- 21.5.1 PS- 21.5.2 PS- 21.5.3
75775828-4804-5f60-a3df-9a82d162ad6b | note | Verifying Document - Delivery Dockets
751b8bc4-6897-5063-a6d7-87d47ec7c076 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
7e8d13c8-1979-5990-aacf-08b73505fda9 | note | Verification Activity: Activity - H
4006c96a-bc64-5e43-9917-9020fd14008d | note | Verification Activity: By - SE
a5d92bcd-6b64-564d-acc9-23954f1e76ee | checkpoint | 2.3.2 - Stormwater- Structure (SWMH, SDMH, GMH, CP, DCP, CPMH, MP, HW)
950e6069-be5d-58e8-906f-75c387756cac | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the Structure are correct and in good condition.
7249efd0-13a8-5579-bfe8-c850866e2857 | note | Acceptance / Conformance Criteria - Site Engineer Approval
b50f929a-38af-527f-a81a-e53528cbf432 | note | Standard / Specification - PS- 21.5.4 NZS 3109:1997
e6a2b17a-e105-5c3c-9310-968bf24eddd4 | note | Verifying Document - Delivery Dockets
63930cae-a21d-5047-ac1e-9857f8ff5e7b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d41b08a3-eeac-54e7-8f15-e394c8e93b03 | note | Verification Activity: Activity - H
e9e75178-846a-5eef-b1b1-8521d4d46882 | note | Verification Activity: By - SE
cbed7aea-7be8-51e8-bfaa-a2df8eb77a1f | checkpoint | 2.3.3 - Granular Material (GAP20/AP20, GAP65/AP65/LRAP65/Riprap and Drainage aggregate)
407ef78e-50cd-57c8-8824-f9d8e8852c18 | note | Detail - Confirm Specification and material in good condition.
1136a1e3-699e-58c3-9d0c-aa15898cd5f4 | note | Acceptance / Conformance Criteria - Site Engineer Approval
b8087df2-d012-5974-9df1-eba90d28bbbf | note | Standard / Specification - PS-21.7.2
cdc5971a-6269-5354-b5c8-8f9475803eae | note | Verifying Document - Delivery Dockets
9d088f1f-9f2a-5ca3-bb59-e6e1b2142f5a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5a3f4e82-12f6-5d82-8f50-0afdd218756f | note | Verification Activity: Activity - H
077a5639-66fb-5771-88cc-8c3b6cf276b6 | note | Verification Activity: By - SE
c71f9062-d24e-5bf6-a7c7-105d5eef56fd | checkpoint | 2.3.4 - Geotextile/Geogrid
7bcf08b7-ff3d-545e-84c3-04e1e82f1589 | note | Detail - Minimum Strength Class C, Filtration Class 1.
e1ab34a5-a3f2-5e9c-927f-ff3d58e9cc8b | note | Acceptance / Conformance Criteria - Site Engineer Approval
ae9fbf32-cb1a-5c09-97d0-ef9c77c01924 | note | Standard / Specification - PS-21.7.3
3c978ce7-deea-5c28-a3fb-87c317f1a200 | note | Verifying Document - Delivery Dockets
2666c2e2-715b-5082-910b-8fbf5a733244 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
95b961d6-569a-5cba-9d93-b4a540fa1ba6 | note | Verification Activity: Activity - H
e11c4279-6af9-5f37-8469-0635e4d97c4f | note | Verification Activity: By - SE
9cc06a11-17ee-5f49-ac50-31c36fc22fcb | section | SECTION 3 – CONSTRUCTION ACTIVITY
6060b861-66f7-50a6-931b-1a3e09522cab | checkpoint | 3.1.1 - Foundation Compliance
7536601b-5795-54c4-9390-a7bed0019a30 | note | Detail - On Granular or Cohesive Material
724edf15-3e3a-5915-9121-84578bd157f8 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
f830645a-2aab-58bb-906c-27c71c18a48c | note | Standard / Specification - PS- 21.7.2 Appendix V
8c31040c-a189-533b-825a-9de443fb9ff9 | note | Verifying Document - Scala test result
8740789d-55d4-5feb-971a-45877bdd7d1a | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
c84c9e22-44a5-5f1d-affd-04e3960ef8b3 | note | Verification Activity: Activity - W
6ecf1e8f-3477-5567-837f-fa8625d3e6b8 | note | Verification Activity: By - SE
c1c96344-d442-58de-82ed-d9085e766b87 | checkpoint | 3.1.2 - Undercut approval
00595da2-b0ec-5ba3-b6df-33932dcee49a | note | Detail - On Subgrade
7af00c8c-0774-501e-ba30-da67c0745a5c | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
25a1d52f-7fda-5426-b137-dd447b2e82ad | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
baaf7fca-54a1-5394-b84d-d1811e3fb804 | note | Verifying Document - Lab Test Report
8ea61e8d-88b8-50d8-acc4-310275e23e59 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
1d831097-2f81-5314-aeb1-6393177b78c0 | note | Verification Activity: Activity - H
92fe9a12-d005-54bf-bb3d-bfeeeb2adab5 | note | Verification Activity: By - SE
1a41ffdc-e630-5238-b3c6-b7ddb238f1d2 | checkpoint | 3.1.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
6479ab9c-b45b-5e98-ace7-2a2eb58883e8 | note | Detail - On Granular Material
6aa210aa-94f1-5f44-9779-2cb46f254d92 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
1da33ee3-ae6d-5b44-beeb-d48a29e36b20 | note | Standard / Specification - PS- 16.5.12
55ff37d4-947c-5ac3-a0dc-9a1ac4e5af92 | note | Verifying Document - Lab Test Report
b9c7f2b9-a88f-5b50-9010-a5d3751a4a1a | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
3195e80f-8f03-5d16-af20-4cc0d10e4085 | note | Verification Activity: Activity - H
bea0a486-f7a1-590a-9672-73554f189ccd | note | Verification Activity: By - SE
122c791d-c0bb-5292-b890-be01180cb1f8 | checkpoint | 3.1.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
eb402eea-cbce-5dd1-a273-ee269f7ccd3d | note | Detail - On Granular Material
83dc2d43-8184-51d7-94cd-24ed704f194a | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
d64474e8-d06b-51eb-b3e4-359d201a1552 | note | Standard / Specification - PS- 16.5.12
830684fd-21d1-565f-bd8f-b354a2dfb8f4 | note | Verifying Document - Lab Test Report
5ef9c053-d06b-5ce9-ac02-98995c5ebb54 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
1bc17671-cf1c-5423-ba88-09bfa3f56f0b | note | Verification Activity: Activity - H
454bf4fe-bd23-55ed-b3e8-9e1c8817b574 | note | Verification Activity: By - SE
6f02a627-0efa-5c52-bfc6-1db0fde3e838 | checkpoint | 3.1.5 - Pre-Backfill Inspection
e77f1704-9e25-5c33-82d2-09c9dbcbaf60 | note | Detail - Inspection of Structure
f951ec8b-dc9a-5405-91b7-0b06259a0bc3 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
f66efe11-8c35-5953-92b4-943ab3b55648 | note | Standard / Specification - PS- 21.6.11
64af34f4-5cfc-5680-ac8c-58a6c7f63728 | note | Verifying Document - Manhole/Catchpit Record
b27ddea0-6078-5c28-9201-42a353cbad85 | note | Testing Quantity Required (based from schedule qtys) - Continuous
bb2164bf-e8e5-5586-aea5-061af184642d | note | Verification Activity: Activity - I
e5f99403-c158-536d-bfe9-6880cebf1bf7 | note | Verification Activity: By - SE
c35a65d5-6eb2-5191-8c79-ec76f3f7c3b4 | checkpoint | 3.1.6 - Survey
1bf06fba-025e-505c-a887-754d08cdaa1d | note | Detail - Inspection of Structure
eef5d195-346e-560a-9c18-f7ae502040d2 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
3d297368-0aa2-5564-8d83-e1bfe2975029 | note | Standard / Specification - PS- 21.7.6
585535f5-494f-5bcf-901d-dbd9dc20572d | note | Verifying Document - Survey Data
ac82bd90-691d-5db6-a45e-46fcee96c120 | note | Testing Quantity Required (based from schedule qtys) - Continuous
623c6f9c-4701-599d-8589-c1f0211284ec | note | Verification Activity: Activity - H
57afac1e-90f7-56b1-bd39-70911dccf45b | note | Verification Activity: By - SV
e681d924-eb9d-5908-874f-e2a9cfead256 | checkpoint | 3.1.7 - Backfill Compaction Testing
2e8ec344-8cd3-50fa-ab02-e7785f1be849 | note | Detail - On Granular or Cohesive Material
c5251a47-746a-55b5-8328-90325b509eff | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
84724f52-fc63-5dd7-94a8-ed5a9141e72c | note | Standard / Specification - PS- 21.6.12 Appendix V
f06b0520-7e15-5235-8046-70af6152b0c3 | note | Verifying Document - Lab Test Report
001d7a06-1d2a-51f9-a625-fecf948e3e76 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
09b3371e-2d21-5aeb-8089-bc2b2d8f5770 | note | Verification Activity: Activity - H
00e72377-0f35-5af7-9afa-474c27318faf | note | Verification Activity: By - SE
8a67bad2-49a0-5b3e-9e07-3e95e06d76d3 | checkpoint | 3.2.1 - Foundation Compliance
6693aa39-d64e-5264-bf3b-3d30c6fa7822 | note | Detail - On Granular or Cohesive Material
e31f585c-fea8-5cfb-b089-a19c2db76d02 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
b276eb1f-1549-534b-a017-94d90077d154 | note | Standard / Specification - PS- 21.7.2 Appendix V
13cd0b61-a024-5d4e-98e4-6077201c68d9 | note | Verifying Document - Scala test result
ceef2f8c-5d86-5446-963d-a823469e910f | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
433d211f-33cc-5b63-8ae2-b545b77c9e46 | note | Verification Activity: Activity - W
81d04145-5426-5dea-860a-998a8a1ec3b7 | note | Verification Activity: By - SE
5c32e1a0-52b7-5c2e-8003-fdd7656ac09f | checkpoint | 3.2.2 - Undercut approval
ea278464-af9f-5fde-bd25-54d1ce0d139a | note | Detail - On Subgrade
80be3fd5-ac77-51c8-8656-679b043104cb | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
d035fdd2-0e37-5bf8-a24e-00f64ab6f4bd | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
b9dfc0b1-f7d0-5327-9c11-2df9f61ecda5 | note | Verifying Document - Lab Test Report
35c74bc4-0996-5b4f-b771-e9bfaeb3cf92 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
1c526564-e335-52bc-8daa-cd0f240e6fa8 | note | Verification Activity: Activity - H
4bd8b7ba-ea6f-5198-bb35-0097bea43aa0 | note | Verification Activity: By - SE
811e271f-f2a2-52ee-9167-0e158033e720 | checkpoint | 3.2.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
dcadc4d9-96fd-55ca-b0bd-89a8fff7a309 | note | Detail - On Granular Material
175eb5c8-e07a-5b6d-a58f-6695e40e86a8 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
def5d9ef-5cce-5477-9b47-c8546a5d1cb4 | note | Standard / Specification - PS- 16.5.12
7b3b0c16-3de9-53d5-8208-072297668bb8 | note | Verifying Document - Lab Test Report
10fb19b6-58bb-5b0c-ae29-e85d8d061777 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
30199c4e-14ec-592f-8548-0c6d5aded7b3 | note | Verification Activity: Activity - H
e9693bdf-97b2-570b-876d-3ccaed5e26a4 | note | Verification Activity: By - SE
77568fee-af21-5f9b-9f96-160b1a618b0b | checkpoint | 3.2.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
d3385acd-9e7e-55ff-ac08-aa28120b1ea3 | note | Detail - On Granular Material
6d9d584d-97c3-55a6-8e69-b1b64b687153 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
0adbe8b4-10a5-50d1-8637-12fd7870f94b | note | Standard / Specification - PS- 16.5.12
3d74ac21-d6ba-5b18-b993-94bb528d9d7c | note | Verifying Document - Lab Test Report
b1bb2dab-d898-5cd2-aad6-1e93c56ee60d | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
13a9894c-3b43-555f-8001-726e44a83bec | note | Verification Activity: Activity - H
54b0181f-8c7e-5a98-9b96-e51954539c7c | note | Verification Activity: By - SE
ff95eca0-5856-535c-b653-c34444e1d4db | checkpoint | 3.2.5 - Pre-Backfill Inspection
d610233e-42ab-5f87-a8d7-fca5762d01e1 | note | Detail - Inspection of Structure
4f3c5e54-c54a-5214-ac39-374f38f41675 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
02c38837-cfa7-5130-8f2c-4bfe01c5e835 | note | Standard / Specification - PS- 21.6.11
7ce2509c-5fbe-54f8-88f6-a2b46450e743 | note | Verifying Document - Manhole/Catchpit Record
cd972a7b-69e6-5e5f-8399-85ca4a4f4fd5 | note | Testing Quantity Required (based from schedule qtys) - Continuous
fced3349-4f6d-5430-82c9-db793cb555bd | note | Verification Activity: Activity - I
d4e5c9b9-6be9-5d50-8c4f-59798657d98c | note | Verification Activity: By - SE
8438b253-2cbd-5d5d-b5cf-63795fbb55c6 | checkpoint | 3.2.6 - Survey
7bdafb6a-9389-579e-b973-43343bcdadf2 | note | Detail - Inspection of Structure
e865e0af-739a-5375-b99d-123f9ad5c315 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
0e860317-0ff9-5357-afc2-06540e5ba10a | note | Standard / Specification - PS- 21.7.6
66f21632-48c8-54e7-b7ac-9151bd796787 | note | Verifying Document - Survey Data
a0dbbb05-8b70-547b-ba31-519ac1630378 | note | Testing Quantity Required (based from schedule qtys) - Continuous
8f5ce6b7-123f-53d3-9130-bb110ec1b3a1 | note | Verification Activity: Activity - H
c41e2a53-7736-569c-b991-9bd9148cb4be | note | Verification Activity: By - SV
b695541f-0861-5c72-a422-a5c37de96d6a | checkpoint | 3.2.7 - Backfill Compaction Testing
06f3bd12-4223-53d9-b29e-7d06a8343e5e | note | Detail - On Granular or Cohesive Material
8ef45800-36a7-57f2-91cf-a08f6e68c701 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
c253d9db-85d6-5395-99e5-ea5597604fdd | note | Standard / Specification - PS- 21.6.12 Appendix V
d72d5baa-fcce-5be2-833e-294e3bb480d5 | note | Verifying Document - Lab Test Report
f122f1b7-fa5f-58a5-b9ad-f7ca22b1bbea | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
46ee0a82-6c95-556e-8e14-55b3fe15e3f6 | note | Verification Activity: Activity - H
b4c34036-c8c4-53ac-99aa-ab67401f7bc3 | note | Verification Activity: By - SE
300b8fa1-28bb-53b2-8f55-761644c8d091 | checkpoint | 3.3.1 - Foundation Compliance
72b25472-d766-501a-831b-55c9f74ccb4f | note | Detail - On Granular or Cohesive Material
930b3a55-fefd-5113-b05d-16fd1c509667 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
d0feac88-eb37-517f-a9b7-520293a67e61 | note | Standard / Specification - PS- 21.7.2 Appendix V
a2b06bbd-6854-5815-880c-d7cf839fef59 | note | Verifying Document - Scala test result
6e33f9c1-30e4-5561-b3cf-a235a3921534 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
f1767cdd-3d25-53fc-a759-9694a9376d59 | note | Verification Activity: Activity - W
eb8d5159-f0aa-5677-8701-777298379968 | note | Verification Activity: By - SE
dff5ee8a-9019-5036-bebf-6f91dc5f062c | checkpoint | 3.3.2 - Undercut approval
62f7f656-3915-5fe1-999b-b1c784c58bb2 | note | Detail - On Subgrade
18aad1f8-a05d-569e-bd6f-f312c8237b7a | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
94915bbc-9276-53e4-ae92-1debd9c4e928 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
835a9559-1b67-550a-b55f-8e55eb2dfd68 | note | Verifying Document - Lab Test Report
79397d05-e464-55ed-adaa-ed48e7df704b | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
a845de8f-a05a-5d34-b04f-b007ea7876b8 | note | Verification Activity: Activity - H
b437dfd3-46d2-5a26-9ad5-98ccea8c7a11 | note | Verification Activity: By - SE
19146973-bab4-5555-ab24-77b09a0bbffe | checkpoint | 3.3.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
bf7449a2-e26c-52e5-a4e1-4804e01160c8 | note | Detail - On Granular Material
422260c0-3c73-5bec-9a50-24b474648e95 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
c4f86e78-aa99-59f3-96c8-0b5c9589c87b | note | Standard / Specification - PS- 16.5.12
0933885b-432e-5287-869b-39cee23cc6ce | note | Verifying Document - Lab Test Report
e9a47674-39d2-583b-8646-550672af1e8a | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
7f9eb0b6-750c-5889-a74a-664d89746c81 | note | Verification Activity: Activity - H
78779cd2-0f31-5357-b747-116add696165 | note | Verification Activity: By - SE
94a0623a-421b-55f6-bfcc-21a724ec9dfb | checkpoint | 3.3.4 - Bedding and Embedment Zone Compaction Testing (Polypropylene(civil boss)/Polyethylene Pipe).
5d6416a8-6629-59b5-8972-8054db23e34f | note | Detail - On Granular Material
b56a5fbf-25c2-5138-ae4c-a3a9acc94f41 | note | Acceptance / Conformance Criteria - Bedding Zone: 100mm(for DN300 & DN375) 150mm (for pipes greater than DN375) Embedment Zone: Pipe Dia ≤450 - 150mm GAP20/AP20 - Overlay Pipe Dia 450< D ≤900 - 150mm GAP20/AP20 - Overlay Pipe Dia 900< D ≤4000 - 150mm GAP20/AP20 - Overlay Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
b6dc7386-bcd0-5a96-b0db-e9b815586e18 | note | Standard / Specification - PS- Table 21.7 PS- Table 21.12 AS/NZS 2566.2/2002
98cbd37d-a6ae-5726-b7a6-b8c811e85d8e | note | Verifying Document - Lab Test Report
c9022001-0066-5752-9f30-29dec6664249 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
eb703980-b343-5b35-b4e9-ae266e81c5a2 | note | Verification Activity: Activity - H
08b1c655-664d-5fad-ba55-b191d3419185 | note | Verification Activity: By - SE
d2e13628-b927-50fd-ad8e-db3f761f1f7d | checkpoint | 3.3.5 - Survey
4f14edc7-e9a4-52f1-86c5-798205a9be33 | note | Detail - Surveyor to Setout
9aaf4ffb-8a34-55c0-9b8f-534553d3a398 | note | Acceptance / Conformance Criteria - Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance
5f46781b-fac3-5535-b0f7-4236485214f6 | note | Standard / Specification - PS- 21.7.6 Table 21.15
29691daf-2cec-5dbc-9554-fd4dd5340e7a | note | Verifying Document - Survey Data
aa9af37a-13a7-5b98-8ca2-93763c070541 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
7ca755d6-9e4e-5c08-b7bf-60dfcec72b9b | note | Verification Activity: Activity - H
bb14b4d7-ca9b-55e5-93d4-c48df3421efe | note | Verification Activity: By - SV
652c96e1-768e-5161-abb8-33857043d37c | checkpoint | 3.3.6 - Backfill Compaction Testing
47ca7528-0d20-5fce-992c-8c0031ca4e99 | note | Detail - On Granular or Cohesive Material
32176970-0811-5c42-91cb-991b95a0281d | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
9842a3cd-5db2-54d5-865d-b6f862a0a05c | note | Standard / Specification - PS- 21.6.12 Appendix V
a5d78d5b-202b-5f3c-a550-fd62b25bd144 | note | Verifying Document - Lab Test Report
e7439544-899e-5b79-8ee2-d2bb641a8f06 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
1aae88bf-61ef-5403-97bf-80a113807d94 | note | Verification Activity: Activity - H
43b502f6-f5ba-5206-a0fc-688b56775d8c | note | Verification Activity: By - SE
276798c2-34e6-5e87-bb66-a7f7df9fa38c | checkpoint | 3.3.7 - Pipe Inspection
a06df628-6013-57d7-a7ac-1babe6b7f651 | note | Detail - Inspection of Drainage line
ec6eb0af-4baf-5fab-9b74-5626aa4d40db | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
19d27f5f-351b-5aeb-9ea9-d95200a9b1fc | note | Standard / Specification - PS- 21.7.6
e1c1c3c9-58ca-56b4-85d0-e418d334d0b5 | note | Verifying Document - Drainage line record
5aa69d23-1991-58b1-9a59-332e16116508 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
c091935b-68ff-51ce-98cb-936e9c5d13fa | note | Verification Activity: Activity - I
73b2bb90-7fd3-5df0-b0d5-4a0cbfb04bb8 | note | Verification Activity: By - SE
23e48d28-c984-5a1a-adf0-687888856fce | checkpoint | 3.4.1 - Foundation Compliance
b1f82680-2f23-507d-87ef-07e955ead30f | note | Detail - On Granular or Cohesive Material
1b93c683-9a16-58d4-ac1b-397eeb6713a0 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
294224ec-429c-56f6-b1f4-926c48f6aedf | note | Standard / Specification - PS- 21.7.2 Appendix V
d9e02b9a-d672-52e5-a7bf-b568f7a18e0a | note | Verifying Document - Scala test result
5e9520af-5a32-5a5c-9585-f45b773a33cd | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
2499b3ea-793c-5c4b-8fa9-3064a06065b4 | note | Verification Activity: Activity - W
2a5383b3-1ae7-58cb-9ef3-97ba0f35a866 | note | Verification Activity: By - SE
2e297fed-b0b9-5c9a-82c6-da43f519fdc6 | checkpoint | 3.4.2 - Undercut approval
545f6878-eea1-53de-b124-115e4bea2d50 | note | Detail - On Subgrade
10340e4e-6257-5290-b88f-6e40d6a7a12f | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
edb7d806-2d41-5542-98c4-eb52582f365d | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
093f5f9a-3816-5de1-ac1c-6e9fcd02705d | note | Verifying Document - Lab Test Report
80a49d8c-ebb7-5b16-9ca8-d1dcf9e87a49 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
bd67af40-cd47-5271-84e1-b2da193705be | note | Verification Activity: Activity - H
f625d731-0e13-5d69-948e-c653bdc205df | note | Verification Activity: By - SE
34f0d9ca-7f76-56e1-a2e3-84ec7ac51186 | checkpoint | 3.4.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
1cde9d5b-6e5b-51b0-96b1-89b50215cdf0 | note | Detail - On Granular Material
ecfefb9b-e1e0-5eab-90d9-373d1bcda7be | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
53de2b2f-1021-5d68-a804-5faae55e6841 | note | Standard / Specification - PS- 16.5.12
7e978c77-060f-54fb-ae26-91a16b8ef59b | note | Verifying Document - Lab Test Report
2cdd3332-b236-51b5-8327-796aa39199f1 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
6162c2a1-63a8-57fb-bb0b-7622e1405e38 | note | Verification Activity: Activity - H
173f5d3c-1b2b-5dcc-a2ac-58c7bfbe497c | note | Verification Activity: By - SE
5d768dd2-9cd0-5756-bb3c-505106479de8 | checkpoint | 3.4.4 - Bedding Compaction Testing
e0d9eb16-66df-5645-8e1f-d4e3c38dda8b | note | Detail - On Granular Material
99b11551-54e4-54cd-a53d-cad405368fc6 | note | Acceptance / Conformance Criteria - HS2- 0.3xD (outer dia of the pipe) Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
b2a1e921-a6a9-5310-bcf0-49ace4543ca2 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
98f34698-29eb-5684-b946-231b0b1fdad6 | note | Verifying Document - Lab Test Report
1a08ef5d-a3eb-55f8-a583-415abebb5504 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
9aa15384-64ca-56a3-a1a5-704acaf63829 | note | Verification Activity: Activity - H
19ee0ce2-d1ad-586f-81ea-517090fdf8fa | note | Verification Activity: By - SE
4bfe46f7-744f-55e6-8523-2ea18484410b | checkpoint | 3.4.5 - Haunch Zone Compaction Testing
224e6c9d-bdd6-531f-9a04-548031bde3a1 | note | Detail - On Granular Material
75f3cb6e-0698-5a92-8841-e0e9a35055a8 | note | Acceptance / Conformance Criteria - HS2- 100mm if D≤1500 (or) 150mm if D≥1500 Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
ed49a71e-fcd5-53e6-9ca9-d990f1cff0d2 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
cf4d2da9-bd55-5f3f-9c41-662eaa888790 | note | Verifying Document - Lab Test Report
f0be1216-6c9e-51d9-9af2-b2e776e44c86 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
9efd0274-a60a-57ba-b9ef-ccb4abbf1e5c | note | Verification Activity: Activity - H
e36eb1a9-5762-5ddc-ab87-3a11d36356ff | note | Verification Activity: By - SE
4844df56-a700-5e51-ab74-6839a6589fc8 | checkpoint | 3.4.6 - Side Zone Compaction Testing
045cfc2d-e067-5c0d-b7ee-3de5ee0a51c0 | note | Detail - On Granular Material
902bb784-8f80-55d7-a628-ba068f696b5a | note | Acceptance / Conformance Criteria - HS2- 100mm if D≤1500 (or) 150mm if D≥1500 Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
197bfed8-4df7-5d6b-896c-bc9e643a3fe5 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
22a9f67b-954c-5a70-a4be-1ea07b3eec27 | note | Verifying Document - Lab Test Report
bd0aa8a8-2d6a-56f4-9da3-955b0d0bec8e | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
02a51015-539b-5496-a1d6-cca46e19783f | note | Verification Activity: Activity - H
c0f448f2-ef13-57ec-b25e-67d5360e370b | note | Verification Activity: By - SE
43578e81-672f-5d7a-9d20-9ac1e812a489 | checkpoint | 3.4.7 - Survey
f110438e-dbb1-5f27-b476-ad22c584065f | note | Detail - Surveyor to Setout
d13b1de4-0a4a-55fc-ba7f-1bcf383fe023 | note | Acceptance / Conformance Criteria - Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance
a7bf3aa8-13db-5519-a403-e2e43b483e2f | note | Standard / Specification - PS- 21.7.6 Table 21.15
551d7c42-81f9-5cef-aaec-1839171717f6 | note | Verifying Document - Survey Data
6c9ae2f8-ce02-5e92-82d0-2782494c2f06 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
02243be4-0538-547e-8fa3-672b12b7beb2 | note | Verification Activity: Activity - H
3a82526b-f26f-58bf-8e47-1f813a1487b8 | note | Verification Activity: By - SV
b1c5561f-735f-5ab9-80a5-52eccf1118e5 | checkpoint | 3.4.8 - Overlay Zone Compaction Testing
21620ddf-4f86-5dfe-932a-8b6316603fe3 | note | Detail - On Granular Material
dfcd6cd6-66e2-538b-8a8c-67d72e089686 | note | Acceptance / Conformance Criteria - Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
33243dda-43bd-581c-8039-3e52aeb08f27 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
f8e50a62-3f10-5546-a417-21c635152588 | note | Verifying Document - Lab Test Report
431e22ce-c629-529b-b9ad-fb11b917760c | note | Testing Quantity Required (based from schedule qtys) - One test per 30m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 1 Tests 0m-50m: 3 Tests 0m-100m: 5 Test
d6b81813-19b0-5eb9-ab7d-2e630aa5a232 | note | Verification Activity: Activity - H
fa87cd6f-f03c-5fd2-866d-130718e89598 | note | Verification Activity: By - SE
1b1ebc88-e4b8-502f-a958-3dcc4a007de4 | checkpoint | 3.4.9 - Backfill Compaction Testing
6a094b79-1e76-5958-8703-4e9310286b05 | note | Detail - On Granular or Cohesive Material
11097803-d3b1-5322-8840-d9c50d0ca5dc | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
cc1b8541-1fae-502d-a986-042fb92fef01 | note | Standard / Specification - PS- 21.6.12 Appendix V
7398fa83-6c42-5e52-9853-413853c200c4 | note | Verifying Document - Lab Test Report
8e68f238-4b88-503f-a35e-a4968b197090 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
1fe264f1-fced-5c9e-92b3-e784ab8ea9c3 | note | Verification Activity: Activity - H
4616e0ce-8c25-596f-a21b-a6bea2533fe2 | note | Verification Activity: By - SE
b758dbb4-248e-55bb-94cc-12a4cac84109 | checkpoint | 3.4.10 - Pipe Inspection
8d62a9ca-2cb4-51ee-8612-9cfdecb7cd6d | note | Detail - Inspection of Drainage line
7390c541-2715-5937-a0fc-79281c4f4290 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
c70214f0-30f1-5268-ad19-c6148d2aae66 | note | Standard / Specification - PS- 21.7.6
ae3d6d27-9844-5c17-ba83-d851b62db0a8 | note | Verifying Document - Drainage line record
cc65bc02-bfd1-54ff-a5a1-a937d0a7af29 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
85044673-0283-5e56-bae4-211e54ff9e8a | note | Verification Activity: Activity - I
5d0e0b52-3d6f-54c9-b7b1-24e898dd5b39 | note | Verification Activity: By - SE
a76d1aac-996b-561a-bc2b-69470a3fa996 | checkpoint | 3.5.1 - Headwall and Wingwall Foundation Compliance
f78edb06-81df-5055-a7c6-22d019d7c9d4 | note | Detail - On Granular or Cohesive Material
97596680-55f9-5a46-8ce9-b8b1984f656d | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
161eaefd-8b47-59b9-b777-387959290641 | note | Standard / Specification - PS- 21.7.2 Appendix V
7b8e1d0e-bdaf-5c20-8b28-cafdadd6986c | note | Verifying Document - Scala test result
e03bdc2e-8294-534f-a613-5a33f65f7bd0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Structure
2040fe92-1fb9-507d-b744-8496efceebd4 | note | Verification Activity: Activity - HP
b7f8addb-ca48-546f-a551-113c91e28417 | note | Verification Activity: By - ENG
70cd1be4-24ef-5063-abbf-f9dd93200e27 | signoff | AUTHORITY HOLDPOINT
f0688442-75bc-5d76-8177-3a9f6ee2134e | checkpoint | 3.5.2 - Undercut approval
ef0cd571-aeb0-54e9-9e9e-19dd57cc235e | note | Detail - On Subgrade
bb14ca25-4957-5fc9-8545-89ff1c784f8a | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
655ae977-f498-5805-a035-bc4288e7a720 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
05a01e9c-c880-52f5-94aa-0b63f931fedb | note | Verifying Document - Lab Test Report
a9411a00-5910-5970-aa31-7e3d6790cf9c | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
b06f7107-af61-5bfb-bf17-3763ded23ba6 | note | Verification Activity: Activity - H
95be9e29-2675-5975-90ba-ec47a2d96f0e | note | Verification Activity: By - SE
2478973b-6f47-5310-9ffd-14c721927804 | checkpoint | 3.5.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
5042d307-9abd-5707-9605-d866128daf16 | note | Detail - On Granular Material
fa542ca6-6552-5098-94cd-791e525997ec | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
b9cbfc1c-82d8-5684-822f-dad934367fa1 | note | Standard / Specification - PS- 16.5.12
23883edc-8bb5-5cf2-ba08-227d467d0ee7 | note | Verifying Document - Lab Test Report
bdb4fb1d-8f73-5155-b396-f6c9d5bfd867 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
94f59778-160b-5167-ab93-15cf962ff3fd | note | Verification Activity: Activity - H
24812b13-38e5-58c8-91de-caf926e6101b | note | Verification Activity: By - SE
4ba0a161-7530-58d1-afea-40100c2ddf2a | checkpoint | 3.5.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
aa4eae94-8e84-57e9-bc40-c0b6b8009d56 | note | Detail - On Granular Material
eba0b638-dba3-5c2a-ab67-2e5b677eedea | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
c6897a67-2e80-5b1d-8f91-4aed91d56933 | note | Standard / Specification - PS- 16.5.12
bb90d2cb-a8b6-530d-b551-b981361468b1 | note | Verifying Document - Lab Test Report
71ae2f59-a3e0-51c5-a2e9-f2c0861accbe | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Structure
c0bf7afb-a77e-5085-943d-ab34d9e6b8ef | note | Verification Activity: Activity - H
16e83c92-8258-53c7-be6e-bd8f2bc5bf7b | note | Verification Activity: By - SE
67a6cf71-f8c4-51e4-a8e6-ca7a915ab61e | checkpoint | 3.5.5 - Pre-Backfill Inspection
c9139488-9c15-5b76-a7ac-fe17a6e366e7 | note | Detail - Inspection of Structure
83687d12-36a9-5e3d-92c8-897dcf39c5fc | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
734c6fe9-b6e4-52ea-8756-b95c074ba38f | note | Standard / Specification - PS- 21.6.11
8180e4c1-c5b4-5603-94e3-0a2f84fec26b | note | Verifying Document - Manhole/Catchpit Record
9e476b44-9580-5f7d-8534-13388d2f8daa | note | Testing Quantity Required (based from schedule qtys) - Continuous
8e9a0637-842a-5346-80d7-c99da18b9f0a | note | Verification Activity: Activity - I
4b91cc23-a269-5d77-b7ac-8accd37f2e43 | note | Verification Activity: By - SE
d18baf16-8975-5e0c-8261-32049d9f49aa | checkpoint | 3.5.6 - Survey
84f9a34c-796e-57ed-b114-985940468f9f | note | Detail - Inspection of Structure
5711b32e-0f22-5f39-a7c7-b4e77ea77a32 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
a48f22c0-7cdb-59b4-afec-1a8992a98a71 | note | Standard / Specification - PS- 21.7.6
e95723be-0632-52be-9f6d-f854b5b07e04 | note | Verifying Document - Survey Data
ff404fa2-d32e-5ed9-8635-b5305ae93854 | note | Testing Quantity Required (based from schedule qtys) - Continuous
29a1340b-6e42-5360-b910-b3b22a11e517 | note | Verification Activity: Activity - H
ce76f530-653d-59ae-8e7a-47f935139969 | note | Verification Activity: By - SV
dc025cac-6aca-58ae-b492-06adb07f8de3 | checkpoint | 3.5.7 - Backfill Compaction Testing
1346e21b-2fef-5562-85ac-4cea3a579f77 | note | Detail - On Granular or Cohesive Material
71051c6d-4c93-52d4-b996-5076b9fb16d6 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
3195505d-e3f2-5348-baf9-25ab49003165 | note | Standard / Specification - PS- 21.6.12 Appendix V
14bcfe6b-29c5-53b7-9ba1-74dbebc17739 | note | Verifying Document - Lab Test Report
3b096be4-1256-5002-a55a-71e8231fb4d7 | note | Testing Quantity Required (based from schedule qtys) - 1 test per layer at Quarter Points around the Structure.
4039098c-fb29-5e32-91ac-91c844648db6 | note | Verification Activity: Activity - H
81f698d1-a27d-5d65-bc46-6da8159ee841 | note | Verification Activity: By - SE
909aaa35-1436-5b32-b06b-9bd5efa45dfb | checkpoint | 3.6.1 - Riprap Foundation Compliance
8c982575-8f2c-59c1-977e-c25c39d64f25 | note | Detail - On Granular or Cohesive Material
2bb8285c-229b-54fb-97ec-f833ba6be8f1 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
dc955bbc-9a3d-593e-9962-9c82ee33751b | note | Standard / Specification - PS- 21.7.2 Appendix V
9add7a5a-96f2-581e-bc0c-7dcc547c8131 | note | Verifying Document - Scala test result
458d268d-c5ce-58a1-acdd-6a0e85e5b93b | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
4265f2e4-0470-5cd6-99c9-d0fbed85396e | note | Verification Activity: Activity - W
8e3ec2d6-cb8b-5d7a-82ad-f27f70273460 | note | Verification Activity: By - SE
c318d5a2-491c-50a3-a033-e6f98e6800b5 | checkpoint | 3.6.2 - Undercut approval
0e8c63a4-8c7b-5557-b780-b6bd4f412b40 | note | Detail - On Subgrade
d618f982-fedd-5c90-b8c8-6f337bd942df | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
f89839c8-0e55-5a32-849f-7799c50c9639 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
e53943a5-601a-5adb-aca0-5d36125067c9 | note | Verifying Document - Lab Test Report
7b1e4c0b-e56c-5662-88b8-11aaf8368b70 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
67d32ada-8318-541d-aff5-31b1a35b74fa | note | Verification Activity: Activity - H
5445342b-5422-5140-9aec-4eed0f9bebf4 | note | Verification Activity: By - SE
6a55d5f9-a096-5d22-bb1c-56e2e00cb6d1 | checkpoint | 3.6.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
4d27efe5-19d0-50e1-8ef6-50037e431090 | note | Detail - On Granular Material
1cc127d0-0a40-512c-8ee3-73acb8f02810 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
27b92731-ded7-54d5-9e34-9ba001b42097 | note | Standard / Specification - PS- 16.5.12
a2064463-78e9-5070-a08b-0d3b645233d1 | note | Verifying Document - Lab Test Report
930351f6-ec88-51bc-8c2d-be40d14ef1cb | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
673ded28-b7af-5da6-9048-05f86cacdd96 | note | Verification Activity: Activity - H
92b90047-732d-5e91-8a1b-0c821b01b370 | note | Verification Activity: By - SE
70aa118b-5499-55a2-88d1-6a112d0eb702 | checkpoint | 3.7.1 - CCTV Inspection
46c6bdc6-2aae-5108-affc-809fef37f6fd | note | Detail - CCTV stormwater pipes at completion of trench backfill but prior to final surfacing (pavements, etc.)
ccd8b0cc-b65c-5d2e-a6da-a6fe7b42fda4 | note | Acceptance / Conformance Criteria - Every stormwater pipeline 225mm diameter or greater.
162700d6-751b-549a-96a9-86215702274a | note | Standard / Specification - PS- 21.7.6 PS- 21.7.8
d89f7f1c-f83f-5c38-982b-be558f2eb986 | note | Verifying Document - CCTV Report
5bfeab30-8546-5182-ad77-d2a8f0024b72 | note | Testing Quantity Required (based from schedule qtys) - 1 per line
5a19d298-49c6-5d79-ab44-c505a060d77c | note | Verification Activity: Activity - S
3af3faf7-912c-5633-8f2a-a41081eb6280 | note | Verification Activity: By - PE
84c3283d-24bd-504e-b593-7adb2a662256 | section | SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
13049da8-dc5f-50e6-9653-61f13f53ec94 | checkpoint | 4.1.1 - Survey As-Builts
43405ff8-93a4-578f-8245-80b6a0ba30db | note | Detail - Quality Check on New Works based on the tolerances in RITS
75fa7eec-e69c-5510-a9fd-4d65f0dc461d | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
7e5788d2-50c9-52f4-bf02-4a7eda67d156 | note | Standard / Specification - PS-21.7.7
5fe67f93-427a-59b5-ae3e-31e8cfcf0324 | note | Verifying Document - Red pen markup only
91e56975-23b2-52d3-a796-4e4e6b9d9e16 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
7b449813-211a-5938-b86c-3592cb4fb49a | note | Verification Activity: Activity - H
84f4cb19-b321-5af5-81b4-05813f1cc00d | note | Verification Activity: By - SE
963d04ed-09a1-5cc8-8265-74053e53279a | checklist | Ω (DEPRECATED) DN1210-0008 ITP Noisewall 1 Rev 1 | itp | DN1210-008 ITP Noisewall 1 Rev 1
dc439d04-ad5e-5573-818f-c5c286b26df4 | section | SECTION 1 – PRE-CONSTRUCTION - MATERIAL, PERSONNEL & THIRD PARTY APPROVALS
5ba25caa-7a71-5139-8d6d-82357c289e49 | checkpoint | 1.1.1 - All metalwork to be approved by the engineer after fabrication
87bdd074-adec-58fd-a63c-e6d5e028f17e | note | Detail - Hot dip galvanised to standard hdg 900
98c69e01-29f3-53f2-8d6f-dd8f1cafe8dc | note | Acceptance / Conformance Criteria - Engineers Approval
b0b5c028-b263-5d86-8468-bed9858bf891 | note | Standard / Specification - PS 18.6.3
c6975e6d-cf42-58a9-96dc-90bbede7ad84 | note | Verifying Document - Visual inspection
071be570-ee9f-5a57-8e93-4b073c8c9c16 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
9bee1edf-40d8-5d3f-9a5d-4906f515415f | note | Verification Activity: Activity - HP
79f83faf-d5c7-5db3-9443-d9741f98c18e | note | Verification Activity: By - ENG
068dedb1-7fbd-5e00-a102-f41752de9010 | signoff | AUTHORITY HOLDPOINT
5b77c275-c7aa-5684-bd40-ba54d126d5bf | checkpoint | 1.1.2 - Hot rolled steel plates
2c47a6e9-a08e-5739-8f29-c7e8d3d02837 | note | Detail - All hot rolled steel sections shall be grade 300 complying with AS/NZS 3679: part 1
0dabdb54-74a7-54dd-ae40-de3ad20818e8 | note | Acceptance / Conformance Criteria - Grade 300 - AS/NZS 3679 Part 1
c76b6bca-e6f4-56fa-b7bb-d1453d9508b2 | note | Standard / Specification - PS 18.6.3
a46f0673-50f2-5848-9a66-351ee8402005 | note | Verifying Document - Supplier data sheet/ Mill certs
f71ae4d5-a759-5b64-b484-b80fad78b13a | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
80d4a903-5755-56af-b710-67b364d9d378 | note | Verification Activity: Activity - WP
b76c6864-d65d-5d6e-ba9b-54b00ad6a871 | note | Verification Activity: By - SE
993a2c97-80d3-5c56-8bb5-3a0cd3e51097 | checkpoint | 1.1.3 - Cold formed steel plates
d229f0f2-364a-5210-8086-72c1ce3bc2bc | note | Detail - All cold formed steel sections shall be grade 350lo complying with AS/NZS 1163
ba4d8304-9bcc-5de9-bb60-487d32752774 | note | Acceptance / Conformance Criteria - Grade 350 lo - AS/NZS 1163
c8b7045d-4e65-5004-b178-2faf397810e7 | note | Standard / Specification - PS 18.6.3
d30d11e5-c982-50e0-8b24-1c3de7152c7d | note | Verifying Document - Supplier data sheet / Mill certs
88a15989-7ae8-53ff-bf84-0175e84754d0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
7c299bb9-c2f8-54d8-a453-63e52980a80f | note | Verification Activity: Activity - WP
27df037d-7969-5882-879b-edce791de7c5 | note | Verification Activity: By - SE
db79d8f7-33e2-5c0e-862f-cefa1df6e8e5 | checkpoint | 1.1.4 - Mild Steel plates
a32c4834-9a78-539c-a5d5-7389c11d1b7d | note | Detail - All mild steel plate shall be hot rolled grade 350 complying with AS/NZS3678 (AS/NZS 3678-350)
7cd9c1c7-b21f-5d70-88cb-fbbfeaa4afd6 | note | Acceptance / Conformance Criteria - Grade 350 - AS/NZS 3678 (AS/NZS 3678-350)
d88a1b24-e1db-52f5-8aaa-7b85b0ae3e0f | note | Standard / Specification - PS 18.6.3
46e7120f-018f-5703-8219-bb5e63b2883d | note | Verifying Document - Supplier data sheet / Mill certs
a914bf70-1c36-5e5c-897c-04a8c79f8ab1 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
5f2399dc-817f-55ed-a292-855b1c106f85 | note | Verification Activity: Activity - WP
c77476e6-0463-533c-a9c8-eac096afef73 | note | Verification Activity: By - SE
4efd7e12-8765-507c-8da0-599a589078b5 | checkpoint | 1.1.5 - Round bar/rod
d5ef4756-3498-5ae0-9a8b-684db7d96f7f | note | Detail - To be grade 300 to AS/NZS 4671
fbc5f7fb-ae65-5167-953f-1701743687a8 | note | Acceptance / Conformance Criteria - Grade 300 - AS/NZS 4671
b4cd69d2-a6ba-5f3c-9b24-fa0050b144d7 | note | Standard / Specification - PS 18.6.3
c4b46c52-20a5-5af5-ac60-51251bebc3eb | note | Verifying Document - Supplier data sheet / Mill certs
e6e6c9c9-4a44-573d-9963-66dcef45d4e0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
4d58bc98-af07-5c06-b891-53233ccb29c2 | note | Verification Activity: Activity - WP
56ab8d87-e873-54cf-a6c1-e57300c7fd8d | note | Verification Activity: By - SE
1e999714-ded7-5714-ab23-b5f574a633d9 | checkpoint | 1.1.6 - Bolts and treaded rods
1e50e369-0191-5760-bd17-89eba5bce932 | note | Detail - All bolts and threaded rods shall be category 4.6/s to AS 1252
2d982ca6-dcd0-5c16-b12e-41a1e5c8cdf4 | note | Acceptance / Conformance Criteria - Category 4.6/s to AS 1252
844e284f-14e5-5b7f-be6d-cb835df0005b | note | Standard / Specification - PS 18.6.3
29b0a3f2-dd61-5e2b-97cc-688a22af3ac7 | note | Verifying Document - Supplier data sheet / Mill certs
791a825e-9754-565d-9548-7fc700f2c145 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
d3c70cf8-f765-5516-bc1b-8e0a2780853b | note | Verification Activity: Activity - WP
bfc76215-8b62-5cc8-8738-8c55a68ce26c | note | Verification Activity: By - SE
d47b70c7-d4f7-50b0-a088-bbd13a0577a5 | checkpoint | 1.1.7 - Rough or sharp edges
8239cc44-df77-5242-9d2a-53a51beb9e26 | note | Detail - All rough or sharp edges or protrusions to be buffed smooth
17f0a785-ff6a-5f0f-9d31-ed21bf94dabd | note | Acceptance / Conformance Criteria - All rough or sharp edges or protrusions to be buffed smooth
b5b71663-219b-5d9f-b957-16d39207e4cc | note | Standard / Specification - PS 18.6.3
cc58fa48-e238-53d1-85fc-bf562f0e3f01 | note | Verifying Document - Visual inspection
59159e4c-59a9-5256-99c1-d369a80f0b82 | note | Testing Quantity Required (based from schedule qtys) - During construction
14acb6ad-ba1b-5e05-8b3c-2c7e58085328 | note | Verification Activity: Activity - WP
730fa375-2c73-551a-be83-c3d2fc2ee5c9 | note | Verification Activity: By - SE
704a29d7-c4e9-5cfa-84e8-252fd7bf2eb1 | checkpoint | 1.1.8 - Epoxy Coating to the Steel column
da36ea66-3e4c-5373-8400-500b2eeccdc8 | note | Detail - High build epoxy paint all round the UC column concrete interface
4f50d82f-af3a-5dee-a5b8-897551e5b9f3 | note | Acceptance / Conformance Criteria - all columns must be coted with epoxy at steel and concrete interface
3831f71a-b15d-5fee-a9a9-57072adab45d | note | Standard / Specification - WSP-DR-STR-0306
3b331bb3-c95a-5cb7-93b2-40083c5e8e22 | note | Verifying Document - Visual inspection
c71ecc60-3158-574f-b678-6bc87e3f42be | note | Testing Quantity Required (based from schedule qtys) - During construction
e57e7e2d-40fe-5f23-b707-093f89a44736 | note | Verification Activity: Activity - WP
7b63766e-38d0-5caa-954f-4697e765b776 | note | Verification Activity: By - ENG
95a62a2d-dc41-5729-8c34-772c79c3554e | checkpoint | 1.1.9 - Butynol sheeting - membrane
5a887d98-a2d4-54ae-a390-0257dd636dcd | note | Detail - Butynol or any similar approved shall be used between timber and steel
2ca757a4-cbc8-566c-a551-e5db903dcfc1 | note | Acceptance / Conformance Criteria - Membrane seal
b6b16dcb-822a-55ae-88cc-938242b76771 | note | Standard / Specification - PS18.6.3
ef5fb293-1a54-57d4-96f0-4323475e14ee | note | Verifying Document - Supplier data sheet and Engineers approval
82673ede-b43f-50e3-bcde-fc08d9726de8 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
2a6cfa88-e388-5cd9-ac3a-21a9ef606b81 | note | Verification Activity: Activity - HP
345840de-24e7-571d-b77f-bf487038ee5b | note | Verification Activity: By - ENG
ba2ef6ed-92a6-53c7-bfe9-b134dba90eb7 | signoff | AUTHORITY HOLDPOINT
e6bb1c37-103d-54be-bbb4-bf36c50c5f77 | checkpoint | 1.2.1 - Timber
54251110-fb04-5634-804a-92c22b624288 | note | Detail - Timber shall be VS8 grade radiate pine complyng with NZS 3603 and graded to NZS 3631
fcd03198-8f9c-5850-84d0-b493cd0ba8d4 | note | Acceptance / Conformance Criteria - VS8 Grade radiate pine with a Timber strength - 11.7MPa
5e992fc1-b3d7-5182-9932-816b8f7679e4 | note | Standard / Specification - PS 18.6.3
c4f87a52-0519-5ae8-b336-5759aea2f92c | note | Verifying Document - Supplier data sheet
fa6a83af-5c9d-580d-a86b-e5a78110f7e3 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
a50d4d7b-7c36-5752-a447-950f2b4e1fb5 | note | Verification Activity: Activity - I
e1de97ba-ae1c-5ab1-918a-6404fe0c2bb2 | note | Verification Activity: By - SE
30369b36-252b-59e5-8453-1ef6cc725793 | checkpoint | 1.2.2 - Timber - in contact with the ground
5152ee6b-48c1-5452-b7f7-665c012b4671 | note | Detail - Round or rough sawn piles in contact with the ground to be H5
c3eeb317-ac30-5f95-9d7e-3101991d8efb | note | Acceptance / Conformance Criteria - H5
75f7dbe8-72b9-5f1a-b8f7-15826c932b2d | note | Standard / Specification - PS 18.6.3
bf956d8b-9861-5579-80f7-03b4bee0420a | note | Verifying Document - Supplier data sheet
23055f9c-ecab-5a59-a7fb-780233919e42 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6e964ee1-46bb-52ad-b717-a5218a6e0fdd | note | Verification Activity: Activity - I
f380da60-80b7-5056-9f3a-2277ffcf4687 | note | Verification Activity: By - SE
94a81899-257a-5ffe-8a11-73f210325de7 | checkpoint | 1.2.3 - Timber - not in contact wth the ground
43baedb1-f8dd-5799-ac13-68a41cd4a8ae | note | Detail - Rough sawn timber not in contact with the ground to be H3.2
cc284ec9-df83-5816-ad1e-e548ef3fd65a | note | Acceptance / Conformance Criteria - H3.2
8995acd9-333c-570a-aec6-e20765ea8fac | note | Standard / Specification - PS 18.6.3
7cc07edd-fd8c-54ae-9d41-96ce81f43ac9 | note | Verifying Document - Supplier data sheet
7544f38c-33b7-522c-846e-628837afbd0f | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
91921caa-8caf-5c2e-9d1c-53429a51783a | note | Verification Activity: Activity - I
51024bff-9929-505d-af6d-acbf42b96537 | note | Verification Activity: By - SE
ee29378b-32d7-5f42-aa47-1090de8ff24e | checkpoint | 1.2.4 - All timber components of noise wall
c2944171-e8da-5bd4-8444-bbb67bfefd09 | note | Detail - Timber treatment shall comply with requirements of the NZ Timber Preservation Council incorporating - MP 3640. All timber shall be branded to NZS3640:2003 and must be treated not less than 2 months prior to use.
6448cf6e-b977-5414-adad-2b8f783fe839 | note | Acceptance / Conformance Criteria - MP 3640 NZS3640:2003
00a5bf57-9093-5222-a8de-7d7dded3457f | note | Standard / Specification - PS 18.6.3
1e318461-45a4-58c1-8ed2-c2bcf92458f5 | note | Verifying Document - Supplier data sheet
8c1efafa-2b61-531e-8f1f-39397d4d62b1 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
a0d72391-9573-5058-a0eb-84b413e05e9b | note | Verification Activity: Activity - I
3f823901-11f9-5b7a-981a-3f0f4aac3691 | note | Verification Activity: By - SE
f9d62092-ddd4-595b-9974-ca2ed9af18d3 | checkpoint | 1.2.5 - All timber components of noise wall
0efa02f3-da79-5b77-bdd5-a4d5f22e1971 | note | Detail - Timber shall have a moisture content less than 18% at time of installation to avoid excessive shrinkage effects.
20c0394f-4abc-5d3b-8f4d-edef79533980 | note | Acceptance / Conformance Criteria - Timber shall have a moisture content less than 18% at time of installation to avoid excessive shrinkage effects.
2d87e160-dae4-5e64-b3a7-76c6a9977cb4 | note | Standard / Specification - PS 18.6.3
94f6326b-2489-5eb6-be61-4aa3bd13487b | note | Verifying Document - Supplier data sheet
307a1a62-bac2-522c-a99c-4cf8b742b1ba | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6a315b29-999f-5814-ba87-a57841b3c4c0 | note | Verification Activity: Activity - I
bc525129-b4b8-5d43-885b-04861ce2640c | note | Verification Activity: By - SE
3272a837-e1fc-58a0-bc7d-7379bc60c516 | checkpoint | 1.2.6 - All timber components of noise wall
544ad440-b824-5da8-aee9-8bd16b5721e5 | note | Detail - Treat all cut surfaces with clear zinc naphthenate preservative and in accordance with NZ 3602.
f76dc74f-24e1-549f-88e4-1abf6be9aa7f | note | Acceptance / Conformance Criteria - Treat all cut surfaces with clear zinc naphthenate preservative and in accordance with NZ 3602.
37588d10-c423-59ed-961c-c956f7444c29 | note | Standard / Specification - PS 18.6.3
64c3846b-da7a-5d28-afc5-0c21935d4daf | note | Verifying Document - Supplier data sheet
d518a1e3-9870-5cfd-a733-66bea55e6cfc | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
eaf54b00-742e-551f-b9ec-5f73e8687585 | note | Verification Activity: Activity - I
911327c4-79d1-5baa-bb99-d9fb85bf6469 | note | Verification Activity: By - SE
f9dfbf52-7921-564c-a925-33cba059da58 | checkpoint | 1.2.7 - Galvanised bolts
2440ec0a-26dc-5d22-924a-c6e698d6f007 | note | Detail - All galvanised bolts in contact with H5 treated timber shall be protected using CP grease in pre-greased holes
855e0003-4cf5-5e72-8e20-f8b1614cf3e2 | note | Acceptance / Conformance Criteria - All galvanised bolts in contact with H5 treated timber shall be protected using CP grease in pre-greased holes
42f7b2c3-d6c9-51a6-8261-8b52eb60acaa | note | Standard / Specification - PS 18.6.3
e0a8034f-f8a9-5a0b-b2ba-c642ba4a4544 | note | Verifying Document - Supplier data sheet
3c2a2849-e465-5a3c-9b68-b756239e59e9 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
f4e95223-4a6a-5b04-8f80-6bfc0009a868 | note | Verification Activity: Activity - I
d4334259-f555-5639-a09f-63f567035a45 | note | Verification Activity: By - SE
e1936029-7894-51a0-a7be-3a1a2e755a8a | checkpoint | 1.3.1 - FH Nails
28d68371-a3d5-511d-b574-81b8c7782309 | note | Detail - General structural use 75mm x 3.15mm FH nails . All nails shall be flat headed, unless otherwise shown, hot dip galvanised and fully driven
db628c59-bf96-53a3-807a-f39fd18dcc9b | note | Acceptance / Conformance Criteria - 75mm x 3.15mm FH Nails
4a24bfb7-c4b1-5ca4-98da-eb87499c26ca | note | Standard / Specification - PS 18.6.3
05837ee9-a67a-5272-9bcb-f7894e309c17 | note | Verifying Document - Delivery dockets and supplier data sheet
fa89e629-1bca-55aa-aec2-dbd87af7df2f | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
82240e18-b2c3-525e-a2bd-727bb0d0d38b | note | Verification Activity: Activity - I
d179c9ba-17a7-5947-bae0-079338a7cc4e | note | Verification Activity: By - SE
92dc6277-2665-5d70-9e48-177822abec7e | checkpoint | 1.3.2 - Bolts
6fd1fc27-2e0a-5602-b948-507ecdba4eab | note | Detail - Bolts shall be M12 hot dip galvanised engineers bolts fitted with 50x50x5 galvanised square washers both ends. Washers for coach screws shall be provided in accordance with NZS 3604
672ea647-fc9d-597d-a6f1-13f399bfe296 | note | Acceptance / Conformance Criteria - M12 hot dipped, 50x50x5 galvanised square washers
f0c14c3d-8f7f-5a83-bc6c-760c84878fa1 | note | Standard / Specification - PS 18.6.3
aa565e89-d839-522b-9d92-689160284664 | note | Verifying Document - Delivery dockets and supplier data sheet
9ecbbaa8-0958-51a5-9143-d165d1ec9f6c | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
42240d1d-3fb6-54ad-979c-dcceb7e9c33c | note | Verification Activity: Activity - I
d49b33e6-b909-5d28-a95a-0e9dd644da3e | note | Verification Activity: By - SE
f6166390-0424-550a-b578-335017e863af | checkpoint | 1.3.3 - Bolts within 100mm of ground
ef0a452e-c447-559d-b720-ec3894f29512 | note | Detail - Bolts within 100mm of ground to be stainless steel.
910e16b5-6385-5c14-b82a-1a3eddeba3a0 | note | Acceptance / Conformance Criteria - Stainless steel bolts
aad17169-f7e8-5347-b07f-98395edf6661 | note | Standard / Specification - PS 18.6.3
126723f5-ecf6-5a58-a83c-f5b39d7d2534 | note | Verifying Document - Delivery dockets and supplier data sheet
4c1ffdfc-2a94-538b-909e-c3a8044cabe0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
413b49f0-dcc7-5238-8eab-d5a8b84ec194 | note | Verification Activity: Activity - I
3581952e-8803-5645-a554-6a585406dae6 | note | Verification Activity: By - SE
52dad3df-5c5f-542a-9707-5e4361323e21 | checkpoint | 1.3.4 - Coach screws
057507f2-4ca3-53ed-b8f0-f91c2e0da906 | note | Detail - All screws shall be hot dip galvanised and screw fixings shall be pre-bored.
1172649a-ca70-5d69-8e0d-9831d8152c9f | note | Acceptance / Conformance Criteria - Hot dip galvanised
43aeca2a-3829-5bf7-9322-fe2d86805984 | note | Standard / Specification - PS 18.6.3
a00ac75c-241f-517d-b981-d91e3044bfad | note | Verifying Document - Delivery dockets and supplier data sheet
7d2e118d-6fb3-5f8f-a6c3-dfbb5789eab7 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
df201f03-523a-5c04-b873-1de4e77e82bc | note | Verification Activity: Activity - I
96482dff-afec-5c12-b89f-0f524336fc05 | note | Verification Activity: By - SE
868e15d2-a829-5664-9f4e-1c730798c2ea | section | SECTION 2 – CONSTRUCTION ACTIVITY
8abc6212-3111-540b-9738-78a20e86ed40 | checkpoint | 2.1.1 - Setting out of Noise wall 1 all Posts
db9796ec-3de3-5f3e-a2b1-b371b55d636e | note | Detail - Setting out to follow design coordinates and levels within tolerance as specified in PS 18.5.7 section (e).
53c8d121-406a-5754-9665-84e5ce60fddc | note | Acceptance / Conformance Criteria - Engineers Approval
1ac7c545-fb56-5f43-9e9d-71200baa4099 | note | Standard / Specification - PS 18.6.1
49eefdea-60f2-5a7e-9485-4e81f54dee3d | note | Verifying Document - Visual inspection
9b22254b-b8c5-5fe2-abd2-fa7d667abe0e | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
d1b4e7ef-1486-5850-8c93-780e3ff27f28 | note | Verification Activity: Activity - WP
d5b62a0e-ab48-51a2-a5ca-bac0bff62f81 | note | Verification Activity: By - ENG
ac86be99-18f9-57a8-bf7c-14f69d596955 | checkpoint | 2.1.2 - Geo Technical investigation on each post holes
45032e44-c37a-598f-82f4-efe6d77a54e1 | note | Detail - Holes are to be 400mm dia and 2.8m deep. Shear vane testing to be completed to a strength of 60kpa
89cde49d-cbed-5656-8b76-5995c7d79101 | note | Acceptance / Conformance Criteria - Shear vane strength of 60kpa
815a6b13-4eda-5a1c-a9bb-3617264cd253 | note | Standard / Specification - PS 18.6.2
754362a4-9655-5c9c-92cb-f40197172609 | note | Verifying Document - Shear vane test report/Visual inspection
f9620d0c-b2c0-56cb-bd18-a6a4a167c6e9 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
c233521d-d38f-54bc-a9e0-72be1d3f9899 | note | Verification Activity: Activity - HP
4209a781-2ab3-588f-8d78-e9fa3287449d | note | Verification Activity: By - ENG
9e47e5c7-cb75-541e-a14f-4afa4b5d7a68 | signoff | AUTHORITY HOLDPOINT
2cdf9c15-2c63-5aac-9f2e-a940d4990caf | checkpoint | 2.1.3 - Noise wall footing concrete
139e9071-f02a-51c5-872c-60346393be5c | note | Detail - 17.5 MPA Concrete
9a2ac467-7a99-507c-88f3-8c9200f75b7b | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 17.5MPA
01f3b2d3-71df-5c0e-a557-cebe048096f7 | note | Standard / Specification - PS 18.6.2
a31d14e4-0d82-51e2-8601-61322fbf976b | note | Verifying Document - Concrete Delivery Docket
324e5e6c-bff7-5126-a664-7c0f7209f2b4 | note | Testing Quantity Required (based from schedule qtys) - During Construction
3216a620-a366-5d1a-8ff3-dfedb315054d | note | Verification Activity: Activity - I
2d5f18ab-85ce-56a2-b39b-83bbed73787d | note | Verification Activity: By - SE
b0af36a8-2e1e-5d8c-8d3d-b3d850c71730 | checkpoint | 2.1.4 - Installing Wooden Railings
207f27c0-a0e6-587f-8899-c5cad0ebc6df | note | Detail - with sufficient embeddment of nails and connecting details as per drawings
b8c45349-31a7-5ed8-9b83-67be91a22764 | note | Acceptance / Conformance Criteria - Skew nails shall be installed as shown:
6543a4e4-ab92-5a54-b0b3-4b3930c38246 | note | Standard / Specification - PS 18.6.3
6487da79-9484-5263-a42b-99a80c9b5613 | note | Verifying Document - Noise wall Checksheet
5ef90dfc-9ed5-55fb-8406-0f069a808cc3 | note | Testing Quantity Required (based from schedule qtys) - During Construction
89875b75-8f03-53ee-8339-893c9791911f | note | Verification Activity: Activity - I
a98fea2e-6479-5811-8272-80c2c4a34be4 | note | Verification Activity: By - SE
47886ec3-63d6-5e34-814f-8a266d50043d | section | SECTION 3 – POST CONSTRUCTION (HANDOVER)
49e56452-d262-55bb-8e2e-45db3938f81d | checkpoint | 3.1 - As-builts
790edb2b-229c-5e7c-980d-fe019c0d306d | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
4915cc5a-a225-518b-a3da-ffe8886dca97 | note | Acceptance / Conformance Criteria - All changes to design need to be captured on the noise wall drawing set
71b63e81-f275-5591-812b-c0601b22bae6 | note | Standard / Specification -
f046623b-db5a-53f8-bd6b-d4e4b89d9e10 | note | Verifying Document - Redpen Markup
9cd59d86-5195-5dd3-a4f3-42f6def3fa28 | note | Testing Quantity Required (based from schedule qtys) - During construction and after finishing
ffc5e08f-200b-5cd0-ab09-336f592f225b | note | Verification Activity: Activity - WP
a1abcf24-c909-5eb5-a2d0-6730301d1972 | note | Verification Activity: By - SE
9106ce5b-bafd-42ff-96c7-72ce71857c54 | checklist | Ω (DEPRECATED) DN1210-0010 ITP Landscaping & Urban Design Rev 1 | itp | DN1210-010 ITP Landscaping & Urban design
0d3a019b-e651-4e29-b70b-e1622c5589ea | section | SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
bcd03629-5ffc-461a-9fc5-5de2eaf54a4c | checkpoint | 1.1.1 - Wetland & Landscaping Methodology
56b71d30-7c42-593d-a5e2-4dbbde720a8e | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Wetland & Landscaping including, testing, inspection and hold points for review and approval prior to works.
3b04df75-a96b-57d4-b854-7f0729ee0305 | note | Acceptance / Conformance Criteria - Engineers Approval
6ce8d178-6d90-50e1-8786-f5299c4edfcb | note | Standard / Specification - Appendix V
b1c55a44-5288-5950-b61e-5167d0361184 | note | Verifying Document - Approved Methodology
adb39d7f-f4f7-553e-9ca7-70fab82bac5d | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
8801275c-659b-57fe-b181-46a82e836a04 | note | Verification Activity: Activity - HP
624ffdd5-2cbd-53ca-83ae-16bbf20740bd | note | Verification Activity: By - ENG
6c3f322b-b901-4f81-99fb-7b3710f431af | signoff | AUTHORITY HOLDPOINT
dca57886-5e7e-45d6-ad0f-af47e9586807 | checkpoint | 1.1.3 - Bentosure geosynthetic Clay liner
bf85234d-620e-547b-8b64-39d09872658c | note | Detail - Permeability value of bentosure liner
246f2bb1-43cb-5469-96d6-ad782e295edf | note | ○ Liner Approved for use
d82ac261-8f7f-5b0d-91af-c9206967edd8 | note | Acceptance / Conformance Criteria - permeability value of 1 × 10⁻⁹ m/s
5d3309e7-7e3b-5000-b2ea-a7f64f375775 | note | Standard / Specification - Refer to installation guide
35e11882-5cd0-5adc-84d4-e27aeb6c209d | note | Verifying Document - Delivery dockets
28e5e77f-d4a4-5e8d-bf16-c9e177598a9d | note | Testing Quantity Required (based from schedule qtys) - Once per source - prior to commencement of works
5c230c41-df8c-5ded-9b1f-3196e70e52c8 | note | Verification Activity: Activity - HP
469c15e6-4ddb-58b7-8af8-61ed3fa4a5e7 | note | Verification Activity: By - ENG
d2109ebd-2352-4405-8d98-b26d989ccd78 | signoff | AUTHORITY HOLDPOINT
4870f329-3339-4285-adec-77a34e867db6 | checkpoint | 1.1.4 - Geotextile Fabric
da56f042-b66f-5662-9e81-a5727a6b2184 | note | Detail - Geotextile fabric approval
8d9591c1-abc5-5b37-b0f7-e1ebbef535a6 | note | Acceptance / Conformance Criteria - Class D geotextile fabric
6d848204-f984-5638-a2c5-83a03bc7bf99 | note | Standard / Specification - PS 21.5.15
a7fbb07c-81d8-5290-85d9-2123c4fc3e7e | note | Verifying Document - Engineers Approval
7ad1e53a-731d-5c6b-8a72-694d0ec97ce5 | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
cb6cb8dc-9f80-57d6-b500-9424123619d0 | note | Verification Activity: Activity - HP
2d9225dc-afa7-545a-8ea1-84d810b473db | note | Verification Activity: By - ENG
7a1486d3-20a4-4e13-8f5a-1e763253b088 | signoff | AUTHORITY HOLDPOINT
84ed47bd-cf25-4d8a-b92b-989332b3f02d | checkpoint | 1.1.5 - Topsoil Analysis
c7a93da4-bb39-535a-bd83-8c22b378cb3f | note | Detail - Testing of on-site and imported topsoil for quality.
ce588929-3fd8-5ffa-bc9c-470a0aebe9b6 | note | Acceptance / Conformance Criteria - Topsoil must meet the criteria specified in the project standards.
fc9c7fd2-3d34-5957-88e4-78c0c1e00eaf | note | Standard / Specification - NZTA P39: 2013, Section F
e552f529-0218-532c-aa0e-f8d12be28907 | note | Verifying Document - Soil Testing Report
8877648e-2e01-56d7-a862-0209df9fbc02 | note | Testing Quantity Required (based from schedule qtys) - Once per source
6f8ffb52-0629-5afc-b3b3-b89239007ab5 | note | Verification Activity: Activity - HP
cb86aad0-ca01-5e66-aa30-035ae99fbc4f | note | Verification Activity: By - SE
bebbec83-656c-439d-8f89-1744d9d1c2f8 | signoff | AUTHORITY HOLDPOINT
67f450d3-ae8d-42c4-bb5e-18fd7c38d0a4 | checkpoint | 1.1.6 - Mulch Material Verification
714553b6-d775-52cb-8e13-9ded7f31c0c4 | note | Detail - Verify that the mulch used meets the specified criteria (e.g., pallet mulch, arborist mulch).
009c8aba-2f41-561f-8650-4659515d0c28 | note | Acceptance / Conformance Criteria - Mulch material should be free of contaminants, sufficiently aged, and appropriate to site and slope conditions
110c186e-9d1f-5907-951b-a9b8a9403d3d | note | Standard / Specification - NZTA P39: 2013 Section 3.9
f712d9c4-677c-5c8d-91e4-30d83d7cb79f | note | Verifying Document - Mulch Material Certification
96c4f8c0-1bbe-51e9-98dd-f2365a7f35ef | note | Testing Quantity Required (based from schedule qtys) - 100% of mulch used
9213ee67-bc16-58ad-8020-c3bc8c4fe731 | note | Verification Activity: Activity - HP
d942a541-7967-5112-b510-9f7040ea73e0 | note | Verification Activity: By - ENG
6b1a9963-01d5-4f8a-93cd-fda497ba055b | signoff | AUTHORITY HOLDPOINT
4f13c2a7-a274-4472-9539-5e6b1d1bd8b7 | checkpoint | 1.1.7 - Biodegradeable Weed Mat
6761f342-fab1-5ef3-bf36-7a3cfa9c2b6c | note | Detail - Biodegradeable weed mat approval
277df228-bd83-5e91-a310-3e0d0e4f8efe | note | Acceptance / Conformance Criteria - 450 GSM, 7mm thick, biodegradeable weed mat
fbd4d623-e186-5117-9c6f-b50b9c0b03bb | note | Standard / Specification - PS 27.3.8
8f66b2c3-a806-5d39-97b5-2c5dda911648 | note | Verifying Document - Weed Mat Approval
9bc52eab-36e5-54a5-a7c6-3639c421ebd1 | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
eb254917-d5e3-5933-836e-dfd152158b6d | note | Verification Activity: Activity - HP
f44e3569-c396-56f9-b2c4-182b052148a9 | note | Verification Activity: By - ENG
c9795f8a-debe-4fb0-a119-7d2ec1dd9c0e | signoff | AUTHORITY HOLDPOINT
9d2e255a-2bb6-45fd-b597-7fc1d259c81f | checkpoint | 1.1.8 - Rock Rip Rap Approval - Grading
8f2b6351-48a0-5546-baa3-5104eb2a84a9 | note | Detail - D50=150mm Grading Approval D50=250mm Grading Approval
27bbce31-e479-53db-8397-692ae13801b7 | note | Acceptance / Conformance Criteria -
42de9532-4c84-5727-b26c-2569879a6bd2 | note | – – – – – – – – – – – – –
374d287b-9823-5620-b293-93e419d8c1dd | note | Table 21.3: D50 = 150mm Riprap Grading
56e55a0b-80aa-5042-ae74-2d93dc71c93c | note | Aperture Size (mm) ¦¦ Percentage Passing
3040e424-06cb-5dbd-9b06-e82870ee3337 | note | – – – – – – – – – – – – –
9718b3d6-0e93-5c3f-a6d7-943122f6122d | note | 230 ¦¦ 85
f74cdace-379c-51a3-998c-c6d2f447ec46 | note | 150 ¦¦ 50
dd811a63-84e0-5af3-ae5c-a8677618392f | note | 95 ¦¦ 15
cc1fbff5-2825-5bc3-84fd-465cf3daed3b | note | – – – – – – – – – – – – –
371d40e7-26aa-5634-842b-65fb946da877 | note | – – – – – – – – – – – – –
a1303275-e24f-5b1a-821d-74761a861ffd | note | Table 21.4: D50 = 250mm Riprap Grading
a7c980b4-2d29-5ccd-ad5c-974a74de27d5 | note | Aperture Size (mm) ¦¦ Percentage Passing
f4f169ab-84ea-5a3a-8164-59089c1f0408 | note | – – – – – – – – – – – – –
17e4f0ec-14a8-5525-a2c7-4147d850ffb7 | note | 380 ¦¦ 85
bbaef4cc-75ee-55f1-8c33-c9cd1bdc14c7 | note | 250 ¦¦ 50
f65fe505-3b3f-5d12-855e-40420b4a2499 | note | 160 ¦¦ 15
c6734d32-7bc1-5eed-b255-9c15418a48c1 | note | – – – – – – – – – – – – –
edf1af65-54c9-5b22-968a-b9ca07b54811 | note | Standard / Specification - PS 21.5.14
90dfadc2-dd0d-583d-b340-e0e934a7c5a8 | note | Verifying Document - Engineers Approval
33b8f7fc-33b7-5738-8535-30179c5a660d | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
e469e256-e7da-58cf-bff2-482f0f6fb4ab | note | Verification Activity: Activity - HP
cb0b78ea-7f80-521f-a2cf-052d7e436984 | note | Verification Activity: By - ENG
7bb87710-9aed-4f0c-9f7e-9c27dd9342a1 | signoff | AUTHORITY HOLDPOINT
dccd58d1-ea75-42c9-89ab-fbaa00d63fc7 | checkpoint | 1.1.9 - Rock Rip Rap Approval-Weathering
af29bd83-ab80-521e-acb9-3dbdd0c8b49e | note | Detail - Weathering Index of Coarse Aggregate
9bd1eb3a-94ef-5b0f-8097-9de939cdc92d | note | Acceptance / Conformance Criteria - AA to CA
f32ab109-3eb5-5587-8f00-a7e45f1799d9 | note | Standard / Specification - PS 21.7.4
e14ac5b2-1381-5daa-a6cf-1c4cfd27ed3f | note | Verifying Document - Engineers Approval
cfed4a66-2907-579b-a598-a3e1b44bf821 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
5e9599f1-f3a7-5b2c-94c1-e5ce23f6513d | note | Verification Activity: Activity - HP
a99bbddd-8bf9-58a5-8acd-5493923a0162 | note | Verification Activity: By - ENG
d336685d-eb6d-4e42-bddd-8d9710c7265a | signoff | AUTHORITY HOLDPOINT
a9338eaa-6c09-4dea-abe3-be5fb73cbc35 | checkpoint | 1.2.0 - Rock Rip Rap Approval-Crushing resistance
60aedaf9-2813-512a-af0a-9d9363b8ad3c | note | Detail - Crushing Resistance of Course Aggregate
70c61dfa-b9c3-5db7-8b78-46b122c37de8 | note | Acceptance / Conformance Criteria - >150kN
ecad224c-dbbf-54ce-a893-8098dfb495e4 | note | Standard / Specification - PS 21.7.4
feffc4f3-0182-5e6c-a771-a94f75dedb8e | note | Verifying Document - Engineers Approval
c99bec14-e9e1-5e2e-bc11-77dbbb166893 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
e4e91005-11c7-5482-a02b-a663b7861646 | note | Verification Activity: Activity - HP
3c3ba6b9-debf-540c-a31f-74826e5f3cf5 | note | Verification Activity: By - ENG
650283da-7545-42fe-8051-d1698125a3a5 | signoff | AUTHORITY HOLDPOINT
d67d6864-155a-4fc3-9a5d-de0dea9dff05 | checkpoint | 1.2.1 - Rock Rip Rap Approval-Solid density
78ea7c4d-f1bb-5ca7-9e03-18e3b6110f9a | note | Detail - Solid Density of Aggregate
b724af75-39e6-5d4a-8cff-35939b7c63e4 | note | Acceptance / Conformance Criteria - >2.65 tonnes per m3
1edf199d-d831-56d6-b9ec-7ba30ea6910c | note | Standard / Specification - PS 21.7.4
90f90673-c295-5f45-a381-7b93b4f4d873 | note | Verifying Document - Engineers Approval
8c132e5d-5488-59aa-b731-d81524e9d93a | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
e366a693-651a-5d08-b2b4-e4dac3ac1664 | note | Verification Activity: Activity - HP
ce38e7d6-70e4-5b4e-bc56-3ef57bfea88e | note | Verification Activity: By - ENG
7cfb5060-0a40-4bbd-a82f-b5f446667552 | signoff | AUTHORITY HOLDPOINT
04392113-3afe-4e96-bbda-b6d6ad602628 | checkpoint | 1.2.2 - Rock Rip Rap Approval - UCS
899ca3f7-2d68-5bd3-b50e-f4bc9cfab8ac | note | Detail - 1 per 1000m3 AS4133.4.2.1 >30 MPa
86fce1ff-f91c-50ca-9337-cbb63a95cade | note | Acceptance / Conformance Criteria - >30 MPa
ac08dd48-81e0-5575-9349-3802d434f320 | note | Standard / Specification - PS 21.7.4
aa85086e-003a-51be-a07b-beb115b6850c | note | Verifying Document - Engineers Approval
ae1242a5-88d6-5c67-808d-764f62230373 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
3071d9f5-f95d-5775-b8cf-510734e36b20 | note | Verification Activity: Activity - HP
dafc41c1-e51f-5f04-9570-463b072b33e2 | note | Verification Activity: By - ENG
c1b97413-76cf-4fe4-bb46-44267ce94c4e | signoff | AUTHORITY HOLDPOINT
805cd343-8fd0-4be3-9b31-56e2d282a009 | checkpoint | 1.2.3 - Rock Rip Rap Approval-Point load
9676bc1d-e81d-511c-813b-f07b1592cedb | note | Detail - Point Load Strength
2eab9405-c62d-569d-89a9-d31887a85ebd | note | Acceptance / Conformance Criteria - > 1.5 Mpa
33274b88-18ab-5ffe-8b94-d3644202aa44 | note | Standard / Specification - PS 21.7.4
7cc5e091-c987-5a2e-8b82-eb2b57089706 | note | Verifying Document - Engineers Approval
ab50067f-2f93-56c7-b584-9069803122e5 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
910f7e81-a294-54f3-8cf2-245e60607819 | note | Verification Activity: Activity - HP
c8ec072f-890b-5463-aeab-9bf79bca14c2 | note | Verification Activity: By - ENG
258c9f51-62c1-4b7c-9e8b-5f4920a52f03 | signoff | AUTHORITY HOLDPOINT
0f0791ec-f106-49c2-ab7e-6cd5bbb7b78a | checkpoint | 1.2.4 - Hydro-seeding
e3a80902-014d-51c5-85e8-1ec95369ce24 | note | Detail - Grass mix approved
e5411b10-42c8-50e9-b079-553cbed4ccb8 | note | Acceptance / Conformance Criteria - Send seed mix to engineer for approval
cd344696-ed74-589e-8093-f570578c8e45 | note | Standard / Specification - NZTA P39: 2013, Section F
8070805d-e4a6-5db1-b30e-6e4f9645d885 | note | Verifying Document - Seed Mix
b962694d-af9f-5a9f-9ffb-ccc27b9e1ba1 | note | Testing Quantity Required (based from schedule qtys) - Once prior to commencement of works
7299fff5-a57c-5e62-9610-453a52278b6f | note | Verification Activity: Activity - HP
a9e750b8-87ad-5118-9744-caaaefca8757 | note | Verification Activity: By - ENG
7b9a839f-c99d-42c7-8d28-8905ba834ed4 | signoff | AUTHORITY HOLDPOINT
a1c29397-c852-4967-9ad9-bb1eb5770e8d | section | SECTION 2 – CONSTRUCTION ACTIVITY - LANDSCAPING
6a0bef51-4bf7-49e9-9877-8ee16047276f | checkpoint | 2.1.3 - Setting out Notice
a0bd0d5e-d125-5567-abae-18f9ae0156de | note | Detail - Confirm that the site has been marked out according to the project plans and specifications before construction begins.
7a9dd47e-d0cd-589e-a2d4-dac672933e4a | note | Acceptance / Conformance Criteria - The Contractor shall provide written notice to the Engineer, at least two days prior to Setting out.
fe8ba159-8343-5507-84c0-85dfa35d8e99 | note | Standard / Specification - PS 27.3.2
248fd696-1b0c-528e-aad8-79a183755ef6 | note | Verifying Document - Setting Out Notice Report
c8fc382a-09ef-57fd-b273-550378252125 | note | Testing Quantity Required (based from schedule qtys) - Before each stage
03cd54a9-0c50-5b42-b5fb-5ed0007ae4b6 | note | Verification Activity: Activity - HP
bbda9a7f-18e9-528e-a604-511a5344b9b7 | note | Verification Activity: By - ENG
276f7080-3dfd-4769-b7f9-d2e0c09ca5c0 | signoff | AUTHORITY HOLDPOINT
2b6d53a9-77fb-457c-aba2-b6ebb5d5320c | checkpoint | 2.1.4 - Site Grading
1534b553-291c-5357-9ae9-e8e08e9f0eb1 | note | Detail - Grading for planting areas to ensure drainage.
54022a08-c9e8-5e37-a156-1be4996e1c62 | note | Acceptance / Conformance Criteria - Smooth, flowing contours with proper drainage.
5a619942-37b7-5cd6-8ab5-f6f6bccccb60 | note | Standard / Specification - NZTA P39: 2013, Section G PS 16.6.3
05a245ba-7e4b-5026-ac81-49e0f8115fa3 | note | Verifying Document - Visual Inspection
8b953883-ae67-505e-8e40-edb6b20a0c85 | note | Testing Quantity Required (based from schedule qtys) - 100% of areas
a2fdcc07-d2f6-5ea1-9862-24f5e6691ac9 | note | Verification Activity: Activity - I
e08cdf6a-ce20-5bfa-a063-951faa0ce6ea | note | Verification Activity: By - SE
001d3783-37e4-470f-bb45-f29e1288ea7c | checkpoint | 2.1.5 - Tree Pit Excavation
bf1ec804-b0d8-5e08-8d33-de23869d60eb | note | Detail - Excavation of tree pits according to specified dimensions.
5f114f22-139a-5019-a254-3c0b7a67f0d6 | note | Acceptance / Conformance Criteria -
80bd512d-818a-5e0c-84c3-76b4feb72ad1 | note | – – – – – – – – – – – – –
488ac0fd-05e7-5c15-be92-3011fe29a6c2 | note | TABLE 1
97a451e3-d896-52e2-9b25-fe0be5611f0a | note | PLANT SIZE (LITRE / PB) ¦¦ NO. OF STAKES ¦¦ TREE PIT SIZE
a7c4c734-0d21-5a06-a409-745521bf8949 | note | – – – – – – – – – – – – –
8a7e3725-bb71-548c-87a8-0f842592e96a | note | LESS THAN 15LT/ PB28 ¦¦ 1 ¦¦ 2X SIZE OF ROOT BALL
40895d7f-9990-5108-8db3-218456ce28a7 | note | 45LT / PB95 ¦¦ 3 ¦¦ 1000x1000x1000 mm
ba3db31b-2424-5e0c-8e2c-79ae85aad8fa | note | – – – – – – – – – – – – –
136314ff-406b-5070-8844-3b3b44c03429 | note | Standard / Specification - 2-32735.02-WSP-DR-UDL 0402 Rev 1
f6d93763-fbb4-5ef2-be7e-118e0e755958 | note | Verifying Document - inspection report
1edf570f-699b-5bf3-a816-d891ed917be6 | note | Testing Quantity Required (based from schedule qtys) - Per tree pit
fcf49fc6-6969-52bc-b898-632de13630f7 | note | Verification Activity: Activity - I
b5fe3f1b-54d0-598f-b277-8e3ef09771bb | note | Verification Activity: By - SE
0ea9b508-0a7e-4808-af32-c24e8b929905 | checkpoint | 2.2.1 - Specimen and street trees
7bc8a06a-0c01-5a23-aee2-a2485e1d36cd | note | Detail - Correct staking and tree placement as per plan and specifications
0dad2ae7-633a-5282-b35a-ac26bcda995d | note | Acceptance / Conformance Criteria - Newly planted specimen trees shall be staked with two 50 x 50 x 1.8m rough sawn Pine H4 treated or hardwood stakes with at least one third of their length (600mm) in the ground and at least 1.0m exposed minimum, or as specified on the plan with the approval of the Overseeing Organisation.
2c84aebb-1c0c-545f-bf89-3f9c90f96dba | note | Standard / Specification - NZTA P39: 2013, Section G
e1aaaf4e-49dd-5842-be20-ed0470b5fec0 | note | Verifying Document - site records
d49ff711-a3d4-581c-a6ac-9b6faa0abdd8 | note | Testing Quantity Required (based from schedule qtys) - Each Tree
c5f101d2-f27a-50b0-abd9-074c935e4026 | note | Verification Activity: Activity - I
9fe1e1c6-e752-56e1-bfc3-b75468eb964c | note | Verification Activity: By - SE
5720d50a-be2f-49f8-a155-31d770530c6b | checkpoint | 2.2.2 - Timber Stakes
94b7523d-bb5f-5308-ac2e-64d7a6d2b445 | note | Detail - Timber stakes used for landscaping must be of specified type, treated to prevent decay, and meet size and quality requirements.
a1db5968-dd14-5298-9dfc-019c2596d043 | note | ○ 50mmx50mmx1500mm H4 Treated Pine Stakes
5a74a1ed-593a-5c80-b254-2a82ad44020b | note | Acceptance / Conformance Criteria -
27e83e73-eec3-5cab-9458-68397a1d9a04 | note | – – – – – – – – – – – – –
e7b75959-d02e-5360-aefb-25535750a95c | note | TABLE 1
0dbc8580-f108-5917-8e5b-2b24f43b7eb5 | note | PLANT SIZE (LITRE / PB) ¦¦ NO. OF STAKES ¦¦ TREE PIT SIZE
95cfa976-42e8-5a32-9557-695ff20f95e3 | note | – – – – – – – – – – – – –
ab5d2d08-6717-54ad-993a-071494cf0444 | note | LESS THAN 15LT / PB28 ¦¦ 1 ¦¦ 2X SIZE OF ROOT BALL
03bd7699-b3c8-5b6c-8175-dd14b29256bb | note | 45LT / PB95 ¦¦ 3 ¦¦ 1000x1000x1000 mm
b528fc24-0664-5e74-967b-a891e02b6287 | note | – – – – – – – – – – – – –
9315b44a-66a6-56fc-93ce-85d2fcbb5bc4 | note | Standard / Specification - NZTA P39: 2013, Section I
84402c16-63f3-5800-87cb-cff9d2ab269e | note | Verifying Document - Material Dockets
b3ce527e-2a9c-5a3a-a327-1d92df8fafbb | note | Testing Quantity Required (based from schedule qtys) - Per order
e0a9e1b6-6d12-5372-b311-b16ba3e64106 | note | Verification Activity: Activity - I
f5a61a72-81a7-5c16-bbe5-16f5e93c631a | note | Verification Activity: By - SE
11d7d946-9b9b-4eb2-9c67-97bc677d206b | checkpoint | 2.2.3 - Fertilising
25069235-6098-516e-8e6f-bcf6e6b30c03 | note | Detail - All plantings shall have two-year slow-release fertilizer tablets installed at the time of planting.
713083f9-9bb3-5abf-8909-5a8ec5b0897b | note | Acceptance / Conformance Criteria - Fertiliser tablet placed in bottom of hole before planting. Fertiliser composition: 6:15:3 (N:P:K). Up to 14l is 1 tab, 45l is 4 tabs
b4b1e0b7-24b9-5e49-9e6f-d49fbe5b90ad | note | Standard / Specification - NZTA P39: 2013, 3.13
1d01de68-2490-5812-83d9-34afd2ac278b | note | Verifying Document - Site Records/photos
7c894c7f-871f-5366-96e1-fd5b726bb26c | note | Testing Quantity Required (based from schedule qtys) - Each Area
0a68f4a8-a3c7-525c-a30a-c4cf997d9cc4 | note | Verification Activity: Activity - I
2cc353cc-fc99-5331-bbfe-bc604aef95b7 | note | Verification Activity: By - SE
9ac29aaf-3b99-4977-9c34-3534ff88eea5 | checkpoint | 2.3.1 - Mulch Spreading
f94af4ce-6a01-5a29-8829-2a0b9d011b5b | note | Detail - Correct mulch application on flat sites
8470ed06-bd72-5ff9-8e0f-4d26a7e11448 | note | Acceptance / Conformance Criteria - On sites flatter than a 1:3 grade (1.0m high by 3.0m metres long), mulch shall be spread evenly to a depth of 80-100mm after settlement, over the planted area, creating an inverted cone hollow around each plant stem with a maximum 25mm depth around plant stems.
ace61c5d-d7b9-592b-840b-00043ceb87b3 | note | Standard / Specification - NZTA P39: 2013, Section G
29d71e80-6343-5193-b607-75c75b33f54a | note | Verifying Document - Site Records / As Built Survey
7f0a07ba-5e9d-5174-b351-1b53b8b95813 | note | Testing Quantity Required (based from schedule qtys) - Each Area
1160e196-d417-5943-b4d5-7cede0bb29fa | note | Verification Activity: Activity - I
328d6a62-9dcc-52c0-aed1-67f70a6ac5da | note | Verification Activity: By - SE
b3010409-0d74-4ba4-8e6c-51a80284768f | checkpoint | 2.4.1 - Pre Bentosure liner inspection
3c06b0fe-b62f-5411-8c3b-cd8b339022f5 | note | Detail - inspect before installing bentosure liner
2ac62687-196a-523a-825d-a7d4169e80db | note | Acceptance / Conformance Criteria - Ensure subgrade is smooth, compacted, and free of sharp objects, debris. Confirm BentoSure rolls are delivered intact, labeled, and stored properly (off the ground, covered). Confirm panel layout plan and anchor trench dimensions are per specifications.
32548aa7-9260-5f17-a80c-66b6bdecc603 | note | Standard / Specification - Refer to installation guide
443348fd-b421-5539-9362-d50290b371c5 | note | Verifying Document - Visual Inspection/Check list
9164ebb6-73a0-55ab-89d9-b285f014ef4c | note | Testing Quantity Required (based from schedule qtys) - For all liner areas
3cf329f1-d1de-53a1-bcc2-b5b920d98bad | note | Verification Activity: Activity - HP
5e86d20e-0b17-58a1-b822-042faccfdbdc | note | Verification Activity: By - SE
9ef59706-3acf-43e7-8d21-787d2abb0123 | signoff | AUTHORITY HOLDPOINT
6f6612c1-0639-4f9a-af14-1c4a93e01b55 | checkpoint | 2.4.2 - Bentosure Liner key Footing
dc083f0e-c1cc-52d1-80dc-0c4430615909 | note | Detail - Anchorage for Bentosure
990e8785-80fb-5925-8348-880c848e9c0a | note | Acceptance / Conformance Criteria - 600mm Deep/400mm wide Anchorage key in footing
7ad2a050-437e-511f-b32b-92e36e16f98a | note | Standard / Specification - Refer to installation guide
387678e6-7fc4-5a03-80d6-f60e34386cee | note | Verifying Document - Site Records/photos
ffabb86a-57b2-548a-8770-d18069a2f0cd | note | Testing Quantity Required (based from schedule qtys) - For all liner
b1ad5a4d-5af9-5d5c-a146-d4784d40bcf4 | note | Verification Activity: Activity - I
61f1ab96-e4de-5cc0-911f-1ee66b0d6877 | note | Verification Activity: By - SE
1402f364-d629-44e2-a421-4b89c5828399 | checkpoint | 2.4.3 - Bentosure liner laps
069d828b-a6f3-561f-b55c-03e0fb7d56bb | note | Detail - longitude and latitude overlaps
db704575-8db5-5e90-a8a4-2deb36a9b2bb | note | Acceptance / Conformance Criteria - Longitude 300mm/Latitude 500mm overlaps minimum
9cc808fa-8093-54a6-bb2f-721ab6ce7805 | note | Standard / Specification - Refer to installation guide
b950f459-887a-5363-b6e8-945d76203212 | note | Verifying Document - Site Records/photos
669f1fb5-c54c-5334-bd2f-ec3d1cd58529 | note | Testing Quantity Required (based from schedule qtys) - Each Area
d08fa80a-e26b-59a0-9821-de74b48ac85c | note | Verification Activity: Activity - I
9d8e2d3f-4b60-5e66-bf24-b5dba7b45954 | note | Verification Activity: By - SE
65639e8e-fb22-416d-9a76-0ea281749b3a | checkpoint | 2.4.4 - Post Bentosure liner inspection
4bac33aa-2c3e-53eb-8c5d-8f0e5a3e9e62 | note | Detail - Post inspection - after bentosure has been laid and before any topsoil is placed on top
78ba6c22-5e88-5fea-87cc-e4b0304418e5 | note | Acceptance / Conformance Criteria - Verify panels lie flat without wrinkles or folds.Check seam overlaps Inspect anchor trench dimensions and proper backfilling.Confirm cover soil is free of sharp objects and is at least 300mm thick.Inspect for tears, punctures, or wrinkles; repair as needed with 300mm overlap and bentonite application.
16d1a822-77a7-5dff-a0b8-3942be05a00f | note | Standard / Specification - Refer to installation guide
588b4940-789e-51f7-b358-d78c65ffe569 | note | Verifying Document - Visual Inspection/Check list
6ccb7c7b-0bb6-5d0a-b879-64945910f549 | note | Testing Quantity Required (based from schedule qtys) - For all liner areas
67553ee5-9db1-5ef7-820a-4b9544bb4f1f | note | Verification Activity: Activity - HP
eaf0b6b6-23a0-5e0e-a41c-bdc646bdd65b | note | Verification Activity: By - SE
87e85fb0-4995-44b5-825d-ee2be163835b | signoff | AUTHORITY HOLDPOINT
9201d617-1499-4f4e-b806-7c21cf702767 | checkpoint | 2.4.5 - Bentosure Liner key Footing
8c0549f9-ee18-5e5d-b559-f0ef7bf4ac3d | note | Detail - Anchorage for Bentosure
48214b96-3fc4-5cb3-8cbc-18362e35e333 | note | Acceptance / Conformance Criteria - 600mm Deep/400mm wide Anchorage key in footing
d978735c-f5a5-5d01-9bc6-9b2e0f6b6beb | note | Standard / Specification - Refer to installation guide
9a9f2efd-f3fe-52c9-8a07-8ead3b028d66 | note | Verifying Document - Site Records/photos
3415d750-d37e-5948-92f1-5f45cdd1ffd5 | note | Testing Quantity Required (based from schedule qtys) - For all liner
37184ad5-c424-5a0a-9456-a97b17289ead | note | Verification Activity: Activity - I
71b7c02c-5789-5ee9-bd21-54cfe91b9f5b | note | Verification Activity: By - SE
12a96591-cc46-446b-9d7f-201cc1df6761 | checkpoint | 2.5.1 - Weed mat laps
2261928e-3f46-55c8-bd6b-4137d5abba63 | note | Detail - Lap joints
94716cc4-6947-58ec-af31-447d04fe445e | note | Acceptance / Conformance Criteria - On slopes steeper than 1:3 biodegradeable matting shall over lap 100mm between adjacent rolls and 500mm longitudinally
a664162d-e3c6-5ccd-bded-4fbd4288724e | note | Standard / Specification - NZTA P39: 2013, Section G
53501d55-da89-59b3-9575-2decaf641177 | note | Verifying Document - Site Records/photos
f047a24f-98d4-598e-9502-bf2a22745c02 | note | Testing Quantity Required (based from schedule qtys) - Each Area
6951e738-7859-5217-8ddf-6546c5ff42df | note | Verification Activity: Activity - I
7c430260-5ab5-54aa-a56c-604ab1aa84af | note | Verification Activity: By - SE
147005f2-9eff-49e4-be41-2151dfe45e5d | checkpoint | 2.5.2 - Weed mat keys
925af4e3-09be-5c6b-bd44-c9d4b51100f8 | note | Detail - Key in edges
bf9559a8-5756-5242-a5c2-e01d2fe833b6 | note | Acceptance / Conformance Criteria - On slopes steeper than 1:3 edges shall be keyed in to topsoil 150mm x 150mm
35f1e4ef-f0c4-52c6-bc73-74b6c47afd41 | note | Standard / Specification - NZTA P39: 2013, Section G
dd8a8632-e220-5cdd-8f53-36a6cd316e56 | note | Verifying Document - Site Records/photos
f67c7ff7-6c19-57ad-9e6d-626c8e76fad8 | note | Testing Quantity Required (based from schedule qtys) - Each Area
347f00ea-c822-5a8d-bd7d-f50cca3b047e | note | Verification Activity: Activity - I
49c27206-214f-50e0-a796-2bd95f93135a | note | Verification Activity: By - SE
6b0b328f-e670-4a76-98ad-8c6b1048eade | checkpoint | 2.5.3 - Weed mat pins
3362ef25-b61f-5202-b580-ff171477cfea | note | Detail - Freqency of pins
4a373fe5-bb3e-5cb8-9f8d-fdce52fdaa51 | note | Acceptance / Conformance Criteria - On slopes steeper than 1:3 biodegradeable matting shall be pinned with frequency of 2 per m2 min.
33504857-0a14-56ce-9476-508d89bedfe8 | note | Standard / Specification - NZTA P39: 2013, Section G
9cbb257f-9faa-517c-b328-44dab6c4f5ad | note | Verifying Document - Site Records/photos
2fb70ab4-638d-5e07-af64-e65eb23c9a9a | note | Testing Quantity Required (based from schedule qtys) - Each Area
9a4d8cbb-424a-5885-87b6-71294c577430 | note | Verification Activity: Activity - I
c70b6e2f-903c-5faf-9b26-070243a86054 | note | Verification Activity: By - SE
07c0802d-bbe7-4090-ab26-368c5c77d72e | checkpoint | 2.6.1 - Establishment of sown areas
c6336517-3f59-5a55-a6b2-3dfb04ac8b84 | note | Detail - Apply grass seed as soon as practical after area is prepped. Protect newly established grass areas.
00d3ac77-8f68-5e4e-a840-2d68746c1151 | note | Acceptance / Conformance Criteria - Newly established grass shall be protected from damage by pedestrian and vehicular traffic until grass has reached a self-sustaining state. Newly grassed areas shall be maintained with regular mowing (90mm-30mm) ensuring that all clippings are removed from adjacent hard surfaces.
27e5be12-0e47-593d-9057-2aed20a7d59f | note | Standard / Specification - NZTA P39: 2013, Section G
4e13670e-8d31-5398-8286-d531868cf830 | note | Verifying Document - Site Records/Photos
d971fc40-ff6d-51c1-b07c-2197e30fe879 | note | Testing Quantity Required (based from schedule qtys) - Each Area
6fba636e-7a17-5fb5-9d60-c2917e7ae2fa | note | Verification Activity: Activity - I
c8026af4-70b4-5fcc-b635-7f52a3b7873a | note | Verification Activity: By - SE
3c54b40f-dacd-45a3-9ee6-21ba9fc821ea | section | SECTION 3 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
dd49df47-a36d-48da-9efb-00305a1de61c | checkpoint | 3.1.1 - As-Builts/ Red pen markup
3f3a0b6b-25ce-5ba4-9783-23b0fcbd7897 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work.
a8ffd6cd-1670-5db2-aece-b92b9b615ab9 | note | Acceptance / Conformance Criteria - Record of work completed
fd948e28-50ab-5da7-b9f5-e9d216a9c46a | note | Standard / Specification - PS 16.7.6
492759ff-1fc7-5913-97d3-ba0320926fa7 | note | Verifying Document - Red pen markups
3a64a441-03d3-51e3-b0cc-a3be9371d4ae | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
39d90cbd-14ae-5d48-a00d-a24674f1b110 | note | Verification Activity: Activity - D
146b113b-adf5-5e34-90dd-624e4899dd46 | note | Verification Activity: By - SV
842392d6-021e-41d4-ab9a-253188f27336 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
912e97a5-73bc-5fb4-9707-9e8c9202ff19 | textbox | Contractor's Rep Name:
91d6d672-9a0e-5291-87e5-66fd31ded53f | textbox | Engineer's Rep. Name:
894d3f38-6ba6-5412-a828-dd6ff60cbab1 | date | Date:
93450def-a627-401a-9ede-e691bc43012e | signoff | Add Signature
df22f407-2ccb-4a33-8ce5-c7f06a5f2987 | checklist | Ω (DEPRECATED) DN1210-0012 ITP Utilities Rev 1 |  | DN1210-012 ITP Utilities Rev 1
8e916c0c-5850-4ca0-aad3-d295c9619403 | section | 1. PRE-CONSTRUCTION (P&G / ESTABLISHMENT) - 1.1 GENERAL
4a66bb89-4063-48d7-ba64-2c8f3122a315 | checkpoint | 1.1.1 - Trench Profile
0bcb6d66-7e1e-522d-ba87-be9b0db6f981 | note | Detail - Tolerance of +/- 100 mm of the planned horizontal alignment and the maximum deviation shall be 1 in 20 in both the horizontal and vertical planes.
67dc9f3e-9171-50cf-b1b6-87fec1d0c3a6 | note | Acceptance / Conformance Criteria - Survey Set out
dd78f3e2-e03d-5227-a645-a1acee11c522 | note | Standard / Specification - PS 25.13.2 a (1)
40ba78fc-9e73-52b2-a54a-f9029e66caf3 | note | Verifying Document - Survey Data
20d912dd-83fb-52e2-b2fc-f85bf0271bb6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
9abec1dd-c417-52ff-a7dd-f5c2e029111e | note | Verification Activity - H
f2dfcbc7-c870-5849-aeca-006cd2d2d0c7 | note | By - ENG
d7f561a4-3e32-4b1a-9982-23753a93830f | signoff | AUTHORITY HOLDPOINT
25425128-8231-4e6d-aa60-7136a71593a6 | checkpoint | 1.1.2 - Underground Services
283dd870-0601-52e4-855c-ca1a319e14fe | note | Detail - Pothole all services within traffic management prior to commencement of trenching. Accurately record the location and reduced level of each service and forward Engineer.
e9093ccf-6692-5b86-aa60-478a2d8764e6 | note | Acceptance / Conformance Criteria - Survey Data/Existing utilities Drawings
c178e828-e156-5366-98fb-7c2b3ee5879b | note | Standard / Specification - Appendix V
afa0302e-7ad5-5f89-980f-717933ab154f | note | Verifying Document - Survey Data
999d0726-1342-5992-bf08-3221e0b8ecb8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
5195c12a-66bf-5ab3-be01-01228c27e530 | note | Verification Activity - H
917c7757-35c5-53a4-b610-1d5f602e77cd | note | By - PE/SE
af7a8933-9e5a-48a0-a05a-129fd15c5cc9 | signoff | AUTHORITY HOLDPOINT
39a6b05e-30a2-4740-ac86-41f6215e698b | section | 2. MATERIAL, PERSONNEL & THIRD PARTY APPROVAL - 2.1 MATERIAL TESTING
486cc648-29a7-46e8-87c0-82a4976fb1ca | checkpoint | 2.1.1 - Bedding and Overlay Material: Clean Imported Sand or SAP 7
4c6a5b85-12dc-57af-9f84-eb844b1a72b4 | note | Detail - Material grading:PSD
81d99318-3953-50b0-87a3-553626258b67 | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
842b2c18-b12a-55f1-ac5d-21652cdca29f | note | Standard / Specification - PS 25.13.2 g) & h)
110948ae-0e2c-51af-a67d-1197efab1263 | note | Verifying Document - Delivery Dockets/Material Certification
6d35a092-9e71-53f3-8366-f69dd71548b1 | note | Testing Quantity Required (based from schedule qtys) - NA
5b73eeea-f3c1-562c-addc-9e13da30056b | note | Verification Activity - HP
9a700353-5f28-57db-a746-62af3930586e | note | By - ENG
b1e0dc8e-de0b-4e74-a9aa-38a5ebc23b8a | signoff | AUTHORITY HOLDPOINT
44d83bac-76f3-42c4-8c5e-39b2257c0cec | checkpoint | 2.1.2 - Materials: GAP65-Backfill Material
23b3c69e-61c3-5c8d-b7c9-27e3a083e564 | note | Detail - Material grading:PSD
69982c10-640a-5c1d-b2c2-6349b69f27c9 | note | Acceptance / Conformance Criteria - Stockpile size over 4000m3 PS- 16.5.11 for GAP65
0d2e1224-6bdf-544e-8baa-647e3abc8c29 | note | Standard / Specification - PS-21.7.2 Table 21.9
89926f4d-431c-5a36-a4e7-5be287cc0f9a | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
538f58d9-8e96-5832-bd96-e69312922f9f | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 1000m3
582b6634-6b50-520c-8e89-1d5f35c4e7b7 | note | Verification Activity - HP
9569ed76-8c8e-598b-ac62-26995c7de055 | note | By - ENG
63d81330-269f-4298-9075-db67765b857e | signoff | AUTHORITY HOLDPOINT
0b6e92e6-b517-4dab-b57d-d9abacf69d0b | checkpoint | 2.1.3 - Materials: GAP65-Backfill Material
dead2c3d-8425-5ced-9f1d-c49fef0cedf6 | note | Detail - Weathering index:
10ac7968-b8ea-5b19-8b95-0f9febb656a2 | note | Acceptance / Conformance Criteria - AA to CA
f554ac44-d467-5ccc-847c-8f1390459f01 | note | Standard / Specification - PS-21.7.2 Table 21.9
987d8f4e-3f75-5e58-83e8-8420be2644fd | note | Verifying Document - Lab Test Report NZS 4407.3.11
8b7fa9c2-a910-5cc0-bdd6-f7af3e21259d | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
89b237ec-4d43-5544-857e-dccdc5cffbda | note | Verification Activity - HP
5eaf02df-d9ca-5f5a-8fa5-c343b8ec9cfc | note | By - ENG
464c66bc-6468-4260-b978-70b3310b1037 | signoff | AUTHORITY HOLDPOINT
09ef89c4-2afa-4d83-9697-447334c2113f | checkpoint | 2.1.4 - Materials: GAP65-Backfill Material
67aaf769-fcec-552c-9ed7-bf1a39112466 | note | Detail - Crushing Resistance
ffc49956-2e6a-5dd3-a304-40ece59ef931 | note | Acceptance / Conformance Criteria - >100KN
f76a0622-fd6e-5455-847e-d508fcacedbc | note | Standard / Specification - PS-21.7.2 Table 21.9
1a5aa289-6eaf-59a0-9437-a111b759d478 | note | Verifying Document - Lab Test Report NZS 4407.3.10
92ed5aba-43ea-56b8-a774-1a2293235f5c | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
b14c597e-8b01-5272-8ddb-301b10feb6bb | note | Verification Activity - HP
b5d26f2d-714e-521b-9a61-469d0abb98d8 | note | By - ENG
006c000e-da74-49b5-97af-9a1160001773 | signoff | AUTHORITY HOLDPOINT
0e80def9-0026-4998-a4ca-cde2b81a47e9 | checkpoint | 2.1.5 - Materials Approvals
a56af989-ca4e-5c53-a433-cd450e47f5e5 | note | Detail - All works and materials are to comply with the National Code of Practice for Utilities Operators' Access to Transport Corridors, and Individual Utility Providers Requirements
8895bb7e-c427-5901-a5aa-07751a808d3a | note | Acceptance / Conformance Criteria - Prior to Commencement and throughout construction
fdbe7567-dbbc-519b-80f5-59a9d0d58c39 | note | Standard / Specification - Project Specifications
5c389606-b39f-5d8e-8d26-163bf0f5146f | note | Verifying Document - Utilities Providers Approval/Material Certification /Delivery Dockets
3ddf2253-d8cc-5de2-81a4-28ced242fc94 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
ef51aec0-3acf-5b8c-814d-5627875e5648 | note | Verification Activity - H
1af29b68-624c-5b9b-b62a-c702c9fce0fe | note | By - SE
4ece6099-0f01-4b16-bde4-65c5945709fa | signoff | AUTHORITY HOLDPOINT
83f97cbe-b43e-4cbc-bc3b-729ae9f6c33e | section | 2.2 MATERIAL DELIVERY
ee48925a-b035-46ef-97b4-087f4ef5eabb | checkpoint | 2.2.1 - Pipe and fittings. Ducts
7db8345a-ba3e-58a1-ae6b-4d5f1a4d4028 | note | Detail - Duct Pipes shall be of the size, material and class nominated in Drawings. Ducts shall be high impact uPVC or High-Density Polyethylene (HDPE). Duct colours shall be to local authorities requirements. Duct colours for the different Utility Structures must be in accordance with the guidelines.
333fbb3f-f90e-5faa-ae0e-3ca9b54ed4ef | note | Acceptance / Conformance Criteria - Comply with Project Specifications
625baae0-854c-5ffd-9828-2611affb4ecb | note | Standard / Specification - PS 25.13.6 b)
51f875eb-7058-5199-9123-ccc9ee657e66 | note | Verifying Document - Delivery Dockets/Material Certification
497e2f66-3f6d-5599-b0d5-be28065d2a77 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5aa16fdc-5187-5a70-a7e8-62d24fd18fa9 | note | Verification Activity - H
78bc25dd-85bf-5421-be72-73f158f43e7c | note | By - SE
f97a8dfd-6853-5b80-b674-22bd03bdd93b | note | Comments / Closeout Details - Duct details will be instructed by service providers.
30b72118-4b36-4dd5-91c9-00414bc65ae7 | signoff | AUTHORITY HOLDPOINT
95fc4281-439d-4b9a-bfa7-e0f188d3b25a | checkpoint | 2.2.2 - Bedding material
349f055c-40d5-51ac-b330-812b78a35726 | note | Detail - Clean Imported Sand or SAP 7
52d5971e-85d0-5bd6-a4bf-6ae513e08feb | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
ac7553e4-090f-598d-93fd-a88a790432ad | note | Standard / Specification - PS 25.13.2 g) & h) & 25.13.7 b) ii
c7246019-cc11-595a-a5c5-ed534863d820 | note | Verifying Document - Delivery Dockets/Material Certification
da3558cd-d367-5395-806d-f6d08fba0c9f | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
13520fea-8f9a-58bd-94f0-b9d17b4cee98 | note | Verification Activity - H
bd332cbf-5d6b-5170-a45e-98515475dc80 | note | By - SE
e29ceea3-5f67-41be-9f64-7ba1ea194895 | signoff | AUTHORITY HOLDPOINT
d5398cc0-f040-422b-8e23-1339dfa1e2a1 | checkpoint | 2.2.3 - Backfill Material
775a8ca9-30b0-5457-92f9-21908aa5712d | note | Detail - Under roads, driveways and footpath - refer to pavement section for appropriate materials and layer thickness. Under berm or grass areas - site Won materials to be approved by Engineer or GAP65 to be used if site material does not meet Specs
b2e368c6-bc23-5da4-a48d-978978955761 | note | Acceptance / Conformance Criteria - Comply with Project Specifications
dc270cb9-cd17-59bd-803a-59e13c5cd7f6 | note | Standard / Specification - PS 25.13.2 h) i to iii & 25.13.4 a)
05583998-e4ea-505c-906c-b3681ae0bfd5 | note | Verifying Document - Delivery Dockets/Lab Test reports
b3465e16-1c11-5103-b922-723dc70f41a1 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
1524ee9f-d13e-5e50-87c6-a5e81f8459d0 | note | Verification Activity - H
9ba41559-439e-5d84-8fd8-cd22bd752862 | note | By - SE
7245ad1a-3400-43c7-aa67-5b628124c14c | signoff | AUTHORITY HOLDPOINT
a4d7cdb7-b059-4497-a17f-f892ba5d8756 | checkpoint | 2.2.4 - Pits Covers
b54dfeb9-8272-5c6a-9c91-dbe596f03cfd | note | Detail - Jointing and pulling pits shall have slip resistant surfaces.
6e129f47-6b34-5471-a0c8-52ff04f7831c | note | Acceptance / Conformance Criteria - Class A-10Kn. Class B- 80Kn. Class C- 150Kn. Class D-120KN.
f10b6ad6-3c89-5058-ba2a-5ab374cde17a | note | Standard / Specification - PS 25.13.6 c) AS/NZS 3661-1- 1993.
febba2d3-986d-5831-b1b0-a89896aa2976 | note | Verifying Document - Material Certifications. Delivery Dockets
8632adbf-8bac-5027-840e-de9d33e4f89b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
b523dd59-d9ee-5824-bcb7-d9730aa34ecf | note | Verification Activity - H
3c22d34c-297b-55df-9dc8-1e84a24caef9 | note | By - SE
12320b3f-a7f1-48e9-acfe-43a50c1746ea | signoff | AUTHORITY HOLDPOINT
2e80cf9e-cce2-4de5-a526-19b5f0b1c990 | section | 3. CONSTRUCTION ACTIVITY - 3.1
4473bcd7-a7bd-4e0a-b8c6-5007ed250edc | checkpoint | 3.1.1 - Trench Excavation
881014cb-a527-53b7-bee5-f8672fe67d26 | note | Detail - To be excavated to within a tolerance. Not more than 100 metres of trench associated with each site shall remain open at one time.
3e77300b-24e3-57d9-8d0c-54d09709df76 | note | Acceptance / Conformance Criteria - #ERROR!
12365ca8-56e6-5f1a-acee-ef8499fd5229 | note | Standard / Specification - PS 25.13.2 a) i
e5d1fb7e-67ac-59a5-9234-fe1d48f36ff3 | note | Verifying Document - Survey
39daa345-e591-50a6-9823-ea6a4c1e5c31 | note | Testing Quantity Required (based from schedule qtys) - Every time
6b035129-a403-50e6-a124-eafc4b6f86b9 | note | Verification Activity - M
b8e83467-db66-5745-9ff7-de536dd190a8 | note | By - SE
c560f64e-3631-49b4-b19d-a3becd6f68a3 | checkpoint | 3.1.2 - Unsuitable Materials
788da501-45e1-5204-b133-312faf493b0b | note | Detail - All confirmed unsuitable material shall be excavated down to suitable materials.
3b5a9fdc-7571-5cb9-8c38-a2295f4015fa | note | Acceptance / Conformance Criteria - Dig Down to Get Suitable Materials or get Engineers Approval.
8d8e26ee-a00d-5e92-ad99-5ebf580c87e6 | note | Standard / Specification - PS 25.13.2 b) ii
a32f42d3-0de8-5a1a-a4e0-0f297dd3fd71 | note | Verifying Document - Visual
eacc48f2-a624-5251-8847-87e6cddcb3cb | note | Testing Quantity Required (based from schedule qtys) - Every time
9d2893a1-8ed0-54ea-a3ad-ea1451cc7677 | note | Verification Activity - M
50c89cc8-28e1-5b9a-8865-40337e15e174 | note | By - SE
4a681e24-b46a-4441-9bd6-7e42252ebb01 | checkpoint | 3.1.3 - Foundation Compliance
9f3f9957-5265-56a7-8e28-baf2e6f1f334 | note | Detail - It shall be de-watered prior to installation of bedding material. If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
b4f5bf4b-5651-5370-9694-0525360b32f1 | note | Acceptance / Conformance Criteria - 50mm granular layer shall be laid and compacted before the bedding layer is laid.
70967d19-82ff-5029-93ac-e78b1e927194 | note | Standard / Specification - PS 25.13.2 c) and g)
bb29f6e5-6443-5910-892c-ab0fdd680881 | note | Verifying Document - Visual Inspection
d7b30555-ed23-54f5-971d-8f7663e42d70 | note | Testing Quantity Required (based from schedule qtys) - Every time
7f197952-ec14-51dd-a602-b43e97854998 | note | Verification Activity - M
f2e6e66d-882f-50c4-8a0e-428f0e065146 | note | By - SE
49179d62-20cd-451d-9cc5-4bdc9f49dc68 | checkpoint | 3.1.4 - Bedding
8614c5cc-5665-5fa3-ab79-3f8940785aa5 | note | Detail - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
0736aece-5d03-503d-8bd2-dc15e71dfe33 | note | Acceptance / Conformance Criteria - Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
119d2e5e-a84d-5440-9563-82cc8c9de3ac | note | Standard / Specification - PS 25.13.2 g)
f566dbf0-0c84-5db8-aa23-db97f0e0357e | note | Verifying Document - Visual Inspection
95c8247d-bef3-517d-afe5-71c62c023bcb | note | Testing Quantity Required (based from schedule qtys) - Every time
cf88f922-c00b-5c77-94ae-58ea7117c49b | note | Verification Activity - M
7af9af8b-6269-5b6b-9749-5e37f31ca339 | note | By - SE
78830cf9-10a2-4c5e-8550-200be233c777 | checkpoint | 3.1.5 - Bedding (Encased in concrete)
e2a882fc-91f0-5b73-ac67-4727ea84b5b1 | note | Detail - Concrete Bedding to be placed. Compressive strength of concrete used no less than 20MPa
e92735c5-112e-5f6a-ab41-56137c2c3ed8 | note | Acceptance / Conformance Criteria - 50mm
c925fb4c-df71-59d9-8612-f84c6aee1fad | note | Standard / Specification - PS 25.13.7 c)
aa502856-7f55-501a-8b7a-1cc391135779 | note | Verifying Document - Visual Inspection
15aa5f42-8a9c-5efd-8d93-0ae20c77a890 | note | Testing Quantity Required (based from schedule qtys) - Every time
99a33773-5ba8-5074-9c2e-001402773f08 | note | Verification Activity - M
b3c964ab-9694-5169-83b2-96437b72a933 | note | By - SE
dfc31b15-66cf-447e-b61f-2a1b0891b1c2 | checkpoint | 3.1.6 - Installation of Ducts
5b79e591-f8e5-5827-adaa-be34a18a3b89 | note | Detail - If more than 2 ducts are being placed.
a223bcd1-0b1c-5e32-beba-bb2d6eb87ff5 | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
deeb4f1c-8275-5660-ad84-a68effb8da42 | note | Standard / Specification - PS 25.13.7 b) iii
d86431aa-c70a-50be-a1cf-a63445223e1f | note | Verifying Document - Visual Inspection
24b5f92a-0d49-5a68-85cd-e4c7a023a435 | note | Testing Quantity Required (based from schedule qtys) - Everytime
4d7275e2-defa-5308-9cdc-0c13ffff8e33 | note | Verification Activity - M
4c27abcb-e832-5ed4-8489-e71afe910f15 | note | By - SE
a05dd518-a7e7-4a26-9f83-a8f2a44879cd | checkpoint | 3.1.7 - Draw Wires
5edb7e75-29a5-5246-b153-3b8dadcbedb7 | note | Detail - A draw wire shall be installed in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting.
9d659fb7-8cb7-5a1b-be14-7d781f814ada | note | Acceptance / Conformance Criteria - Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load. ≥20 years design life. The ends of draw wires shall be made fast within the pits and be secured to the duct plugs.
5c218fd5-e8d2-540a-9a00-2af658da7a07 | note | Standard / Specification - PS 25.13.7 e) ii to iv
f066a145-aaea-5c8d-a3ab-5f5869ec9dda | note | Verifying Document - Visual Inspection
8f57c5b6-de05-5c56-a867-4cffa95efeb7 | note | Testing Quantity Required (based from schedule qtys) - Every time
752d02da-2b6f-5438-b36b-7effcef8df65 | note | Verification Activity - M
d77a631e-2c4a-503f-aae3-306c4c26277e | note | By - SE
9d07cbba-54d9-488f-aaaa-b8959d513f76 | checkpoint | 3.1.8 - Caps
1bfdfd82-7fe6-5e68-9de7-b048819822ff | note | Detail - All duct ends shall be capped
ae5add1e-5d83-53f5-8d27-724134035025 | note | Acceptance / Conformance Criteria - Capped ducts
a3d7f628-012e-5ea4-b7c4-6f7f0f8c09e4 | note | Standard / Specification - PS 25.13.7 e) v
1b0dc8a4-1927-5f71-b1f5-72771fe7de73 | note | Verifying Document - Visual Inspection
387d27f1-087e-5ca4-aeaf-1624f5a7c315 | note | Testing Quantity Required (based from schedule qtys) - Every time
393cf3ed-7340-5bb4-9068-e6e079e4f5c2 | note | Verification Activity - M
57c7c6ec-efd8-5ea6-bda5-8e472b70ed9f | note | By - SE
b17ea8f5-9cdb-4403-a4d8-4c5f65d3300c | checkpoint | 3.1.9 - Warning Tape
fffcaef5-8628-5f0b-974b-849c726c921d | note | Detail - Warning tape to be placed above services.
51439d3b-16f0-5217-8a6f-2a24ba22fa89 | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the duct
e9c43411-659c-5c77-b569-388644d1a8ed | note | Standard / Specification - PS 25.13.7 b) iii & f)
fe08ade8-e822-5587-8394-f5dcc7688f8f | note | Verifying Document - Visual Inspection
00f192cc-e9dd-52d7-a66c-f6a410d5c154 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
66839ed7-44f6-50fe-a63f-4fcd43402bea | note | Verification Activity - M
5924d14b-7652-5653-ab92-1041568205ed | note | By - SE
e306fc1c-d395-46d7-a477-4d04ef77d232 | checkpoint | 3.1.10 - Overlay
c96c786d-a3ac-538f-bd2f-f7a7a9396209 | note | Detail - Clean Imported Sand or SAP 7 to be placed and compacted
bc7ad0de-793b-56a0-b539-d517e3b9bc52 | note | Acceptance / Conformance Criteria - 100mm thick Clean Imported Sand or SAP 7
a891bdad-70a0-52b3-aacc-ffe42aceab7b | note | Standard / Specification - PS 25.13.7 b) ii
1dd21f08-8d27-5bfb-b9e8-6a9f25e00417 | note | Verifying Document - Visual Inspection
127845bd-db3a-5def-b2b7-0a3acf4b4686 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
d556104c-2e88-5f64-9ae2-9701f3e1b8a3 | note | Verification Activity - M
b9d5c2fd-2a2a-5863-8989-b22e6624b3e7 | note | By - SE
3f3429b5-7132-4adb-b746-c9a7683a7539 | checkpoint | 3.1.11 - Overlay (Concrete Encased Ducts)
1f4429d8-f8a2-5bac-a86d-0813b9fde853 | note | Detail - Overlay and surroundings to be placed with concrete.
0b70a8f8-2690-5c27-8c4c-3c4c4fd010c2 | note | Acceptance / Conformance Criteria - 100mm thick on top of Ducts 50mm thick side of the Ducts
f9675d8c-79e1-56da-a27d-b43646e236b3 | note | Standard / Specification - PS 25.13.7 c)
010b256a-1588-58ba-9c39-62df9f4f7179 | note | Verifying Document - Visual Inspection
b34dbc84-d497-5c86-b2ce-8799a8d0f168 | note | Testing Quantity Required (based from schedule qtys) - Every time
d597156a-ed6b-5674-85c6-119be7aa2d64 | note | Verification Activity - M
236de8df-23be-5469-b74e-c361c55f82d8 | note | By - SE
0bae926a-9ce6-4858-9d51-9b2f9caa194c | checkpoint | 3.1.12 - Overlay Testing (Concrete Encased)
35e54c37-e0b1-598a-be0e-b1e2bb10136f | note | Detail - Placed Concrete needs to meet the strength Criteria
b074a358-5034-527a-bf77-2f7fbd297b7a | note | Acceptance / Conformance Criteria - >20 MPA
fa29de66-7375-50c6-8352-5c130ce9b7b3 | note | Standard / Specification - PS 25.13.7 c)
b0012925-f4cc-5a23-b915-ab5034f37dbe | note | Verifying Document - Concrete Dockets
91ed986f-a827-54fe-9a6b-7600723d8aa7 | note | Testing Quantity Required (based from schedule qtys) - Every time
9aacd20f-1f0f-508c-b1b7-468d26f1adbc | note | Verification Activity - H
90a5508c-f605-5494-9626-9395b1c0b5a6 | note | By - SE
0491c173-2aab-4592-86c2-67fcbec243f9 | signoff | AUTHORITY HOLDPOINT
5b6c2158-a99a-4448-ab3e-92552e8438d9 | checkpoint | 3.1.13 - Backfill
5bf88ea3-a40c-5c85-9bc5-bd9bc4a1e4e6 | note | Detail - GAP65 to be used if site material is not approved. NDM Testing to be carried out.
d007f31b-e980-5f51-b330-b26ba3ad43ae | note | Acceptance / Conformance Criteria - NDM Test every 250mm compacted layer Min 92% compaction rate and Average of 95%.
d72fe4f3-f5d8-5c87-ba13-19390696dae7 | note | Standard / Specification - PS 25.13.10 a) modified
b5333357-30a1-5679-9e39-f6a426589629 | note | Verifying Document - Lab report.
053515aa-9b3b-50c0-bfb4-56f808ca9c52 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
682f58e3-a6cd-56d3-ae35-8208fb6bbe45 | note | Verification Activity - H
3e64b478-e791-5aab-9131-020ba8bddd83 | note | By - SE
f4cf8649-25a9-4847-814e-28f6d264bf5b | signoff | AUTHORITY HOLDPOINT
aee89273-de10-42e4-89e7-889fa4ef10d3 | checkpoint | 3.1.14 - Pit Installation Location
78c4648b-49e0-5f28-8583-31e1f07bcca5 | note | Detail - Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid .
bfb37dbb-602a-54ce-865a-5f9bc9a9edc0 | note | Acceptance / Conformance Criteria - Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas. When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side. When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side.
1835a7c4-faa8-5498-b21a-52a635aa2845 | note | Standard / Specification - PS 25.13.8 a)
0708013d-51a8-535c-bd10-3d6f229329d2 | note | Verifying Document - Visual Inspection
950eab39-7f6f-598c-b4bc-b438a93cd9a9 | note | Testing Quantity Required (based from schedule qtys) - Every time
7c294134-4f12-5c05-a658-a9c7c627ad90 | note | Verification Activity - H
3f51bcd6-f532-5373-99ff-edace48712db | note | By - SE
b17ed789-fce9-5f0b-af6a-f65804704759 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
b30154a2-27cf-4399-9ebd-8961bb518b47 | signoff | AUTHORITY HOLDPOINT
4fede5a1-b426-4107-93fe-fbd3a4824ffd | checkpoint | 3.1.15 - Pit Installation Bedding
4ba50b52-7982-5304-a05b-b5ece97d1dda | note | Detail - Bedding with 150mm compacted GAP20 covered with 20mm compacted sand
f714ef28-6d1a-5fe8-b6e0-c8594a9f683b | note | Acceptance / Conformance Criteria - 150mm GAP20 covered with 20mm Sand
88a7d06c-e1cd-5f91-b95c-78a49a4d9b81 | note | Standard / Specification - PS 25.13.8 d)
f3588442-3583-5377-886f-1334bf1a0099 | note | Verifying Document - Visual Inspection
4a69ed86-2acf-5fb1-ba3b-a28f9a65b3be | note | Testing Quantity Required (based from schedule qtys) - Every time
9f492a93-7b7f-5b2c-bb98-924386c86df8 | note | Verification Activity - H
a4bd4db7-0e1e-51c1-b511-0cf4fb01e48f | note | By - SE
cdd9bd87-4c5e-595c-bae4-1b37f5494cab | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
0bd6e6a0-05f2-41ed-8cf5-802339320a6a | signoff | AUTHORITY HOLDPOINT
fe4a52eb-50ec-46b2-829a-261874d7888e | checkpoint | 3.1.16 - Pit Installation Backfilling
7d489dc7-5bbc-5fb4-9b31-a0f8163f708e | note | Detail - Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts.
500e8173-6802-5b17-a562-f5da50056f90 | note | Acceptance / Conformance Criteria - Min 92% compaction rate and Average of 95%.
ef7d94e5-4ee1-5d47-89e9-4f90d2138b3b | note | Standard / Specification - PS 25.13.10 a) modified
3e39b019-1e19-5ace-9f61-521efd6d31db | note | Verifying Document - Visual Inspection
72261735-3e57-5fe8-98e5-1f9fe9c01b44 | note | Testing Quantity Required (based from schedule qtys) - Every time
b747e77b-8f12-5546-96fd-5bdbf812d01f | note | Verification Activity - H
301bcfe1-402b-5b92-bc23-86c8a3fb4796 | note | By - SE
effe1658-db19-571c-b1eb-3597f1a6ecb6 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
81bc6170-8c9c-45f0-b620-12e1089e96ca | signoff | AUTHORITY HOLDPOINT
a1333581-120a-45d8-9b00-bb9c191658e9 | checkpoint | 3.1.17 - Pit Installation Clean up
cea66dc3-485e-5822-8e9f-c030703f0300 | note | Detail - Clean out all pit after completion of the work
ba3186df-c924-5b82-ac04-b2f5eae40ea4 | note | Acceptance / Conformance Criteria - Pit are free of dirty, mud,water and foreign materials
4a67d1d0-2cf3-5de9-aca4-16a4e0882ed1 | note | Standard / Specification - PS 25.13.8 e)
42dd3885-0376-5ec5-9b6d-c0db556cf49d | note | Verifying Document - Visual Inspection
bcdb6a29-93e7-5635-ac42-4cf1cfdf82ef | note | Testing Quantity Required (based from schedule qtys) - Every time
01606bd5-cb4b-5683-ba2d-65dbe816a496 | note | Verification Activity - M
c7db4af7-46f8-560c-8b92-e1d42d0b4448 | note | By - SE
4b3f379c-f817-5f86-b89e-9105a8b52a80 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator will clean the pit.
c508a466-171c-4f79-875c-c23e6a410c2f | checkpoint | 3.1.18 - Survey As Built
f986c5ac-7748-5e6b-b32b-c2a181dade03 | note | Detail - As Built every ducts joint before backfill
f9fbcc29-98d5-562e-84e9-57d1f7357dcf | note | Acceptance / Conformance Criteria - Completed as per drawings
108777ac-97dd-5670-b2fd-aa1ebb5ff775 | note | Standard / Specification - Standard Practise
c091fbf0-ef67-52e4-a28d-f14313c9f7ef | note | Verifying Document - Survey
449f69b7-8db5-5180-9127-5cd276569e69 | note | Testing Quantity Required (based from schedule qtys) - on going
0542d6c1-82c9-55fd-9307-73923cbeb027 | note | By - PE
8684bf06-73a7-4869-a78a-feab8acbd2f0 | section | 4. POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - 4.1 AS-BUILTS
2af294bc-bf87-484b-989f-db926cf70510 | checkpoint | 4.1.1 - Survey As-Builts
53cf4a25-16e2-5051-b5db-eb5ec3759817 | note | Detail - Quality Check on New Works based on the tolerances in RITS
83de8240-0fb0-5adb-8cdb-1750f0103661 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
b9ffad88-9cb4-57f8-b1b9-5dedfdde3f02 | note | Standard / Specification - PS-21.7.7
bbed9c01-fa35-530b-ab40-200efdd164d8 | note | Verifying Document - Red pen markup only
313a5680-5efb-513d-9f2e-dcdbdfe71f03 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
e4c858d1-5129-5530-baed-d20d31d20be2 | note | Verification Activity - H
9394f156-0b56-5a84-8b84-7ffc7787352e | note | By - SE
a072cf05-9802-47ac-9772-7070c5ba6526 | signoff | AUTHORITY HOLDPOINT
2e511a95-c3d3-59b6-a074-0c7fb5c1986b | checklist | Ω (DEPRECATED) DN1210-0016 ITP Fencing Rev 1 | itp | DN1210-016 ITP Fencing Rev 1
9dbf9507-d5c1-5f76-b0e9-632a875b7d7c | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
61faafb8-e067-5299-84f0-3fd60960e68e | checkpoint | 1.1.1 - Extent of Line Setout
2d49439a-3db5-5e85-9b0b-ca24f4b79ac2 | note | Detail - Ensure line and level of Fences has been marked out and agreed with Engineer in accordance with fence drawings.
29900d8c-108b-5bcb-ba90-3d2400fb1787 | note | Acceptance / Conformance Criteria - Engineers Approval
06e46e56-df76-5bec-90a5-c8ab5053aedd | note | Standard / Specification - Design Drawings
6e8489e2-fb2d-58f0-bf97-b57361fa463e | note | Verifying Document - ITP Sign Off
c1e300dc-eedd-5142-9f9a-1031ebfcf3b6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
9867705c-34a8-5fa4-ac89-8b325319a281 | note | Verification Activity: Activity - M
2597987d-ecc6-5af2-a423-671d0723a0f9 | note | Verification Activity: By - ENG
e9e8c2cd-2e34-5f02-8879-699288a9aa24 | checkpoint | 1.1.2 - Existing Fences system
f32c2d60-9006-5930-9f6b-c2059a7b2aec | note | Detail - Confirmation of existing Fence network.
8e482f4a-68fc-5545-8c52-941d9c8393af | note | Acceptance / Conformance Criteria - Survey Information's
15423d91-33c1-5772-b194-ca935acfe13d | note | Standard / Specification - Appendix V
a22b1324-349d-5388-b8f2-7cd6deed0be7 | note | Verifying Document - Survey data
06f131f8-2b9c-517c-8bf1-a86163db0679 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
2c553a08-9c29-57a0-b028-7b823682dc6c | note | Verification Activity: Activity - HP
455af034-9038-5f48-af09-f4980792f812 | note | Verification Activity: By - ENG
a071cef9-3b84-5a44-b239-8ada30897af8 | signoff | AUTHORITY HOLDPOINT
b2505ca3-943c-534d-afb7-23e310ef1e65 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
5032c6c8-1674-507b-9e9e-9ec0d09378eb | checkpoint | 2.1.1 - Timber (Rails/palings/battens) Posts
a81013da-d335-5038-9c3a-bf1ada791a78 | note | Detail - Treatment
c29adedd-6d0a-5c3c-af84-2548b36de425 | note | Acceptance / Conformance Criteria - H4
641c8d13-92c6-5734-a9f9-7a827bc2e863 | note | ○ H5 if touching ground otherwise H4
a8116ba3-05fb-5a11-a829-3fc17a982a24 | note | Standard / Specification - PS 27.5.5, NZS3607:1989
dc71efa7-cd41-5d29-a76d-db43d735b4d7 | note | Verifying Document - Delivery docket
d54ebcd7-a415-52f4-bb63-b53fb1780186 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
6dea0fbd-834c-5396-b585-29f6c8f5d8ef | note | Verification Activity: Activity - M
2cadf66d-84f1-567f-8b9d-b6ad000b32e5 | note | Verification Activity: By - SE
ff5686ac-35c4-536d-8305-ab342ed5957e | checkpoint | 2.1.2 - Steel (Wire/Metal fence)
471c13c3-334c-56e2-8a0b-e96c7e97c797 | note | Detail - Standard galvanised high tensile steel wire
75e50762-15d6-5b4a-9e79-d2ada755fd73 | note | Acceptance / Conformance Criteria - 2.4mm 12 gauge
6106274f-2944-5117-b75f-6a67e37f4337 | note | Standard / Specification - PS 27.5.1, PS 22.5.6
18e4522f-9002-5550-a9f3-e815c15dabdf | note | Verifying Document - Delivery Docket
55eefcb1-cdb8-56ea-b5ca-83b50390d83a | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
6da8dfdd-3e94-51cf-aa9a-d50d3657a29f | note | Verification Activity: Activity - M
1e6d896a-d77b-50fe-b701-9fa92a840bfc | note | Verification Activity: By - SE
489029af-ef0a-5f3a-b8fe-c98f2f8d59cc | checkpoint | 2.1.3 - Chain Link Net
fb315c75-5831-5ae8-838a-9490cc84d931 | note | Detail - Standard galvanised high tensile steel wire
75edb50b-7a66-5053-b343-dd5aaa97a314 | note | Acceptance / Conformance Criteria - 50*50 Max grid size
cb612150-a942-5284-9355-afa86e7fd150 | note | ○ Powder coated black finish
05b033fb-a4e9-593a-972f-af3ab8aeda25 | note | Standard / Specification - PS 14.6.1
b4ef8562-d5f3-5c66-94d7-614093dae351 | note | Verifying Document - Delivery Docket
dc0041d3-2301-51ce-bc4f-c9f15e7f8fb2 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
4e760af3-a526-5d2c-80d1-e5eb00863b05 | note | Verification Activity: Activity - M
8d4e7b06-7ee1-5d0f-95b9-b572a860eb13 | note | Verification Activity: By - SE
591f8625-e14e-5db2-9fa4-b5d19a067cc5 | checkpoint | 2.1.4 - Material (Fixings/fasteners/hinges/chains)
28e911e2-5198-5b13-a9be-af191a00da8e | note | Detail - Jointing
822cc2ce-04e1-5a67-b3e5-2148ab5ae88d | note | Acceptance / Conformance Criteria - Hot dip galvanised
01f9a961-8407-559f-a4b0-288c00dca841 | note | Standard / Specification - PS 27.5.1
f639d918-6f43-5577-84ff-6b2799ba0d07 | note | Verifying Document - Delivery Docket
3d59af60-6986-50ea-811a-cda0111e73f6 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
7806c0f5-e56b-58dc-93cc-ac50fd55c2ed | note | Verification Activity: Activity - M
e2935100-6616-5c08-9fbe-19fcfe7e7cca | note | Verification Activity: By - SE
9cc06a11-17ee-5f49-ac50-31c36fc22fcb | section | SECTION 3 – CONSTRUCTION ACTIVITY
4f3a473f-e466-5291-a795-4d0c92b1a2b3 | checkpoint | 3.1.1 - Wetlands Fence
f866857b-ce13-59f6-8fca-ccf773564bd7 | note | Detail - Install around the wetland
16be6173-c6ec-598a-80a0-bc506f5d4028 | note | ○ Black powder coated finish
02f97957-1b4c-5ba0-913e-2c6a46c4d6a9 | note | Acceptance / Conformance Criteria - 1.5M high
7878d232-a1da-53e7-8b56-551687b16305 | note | ○ Hot dip Galvanised
49455d3b-ce8d-5a0b-bb1d-4ee2f0059392 | note | Standard / Specification - PS 2-32735.02-WSP-DR-UDL-0407, PS 27.5.1, PS 27.5.2
b3e15b83-25bd-53c8-8724-0afc06f86748 | note | Verifying Document - Delivery docket
db100ae5-c88c-5953-bdac-afd6169ee08f | note | Testing Quantity Required (based from schedule qtys) - During installation
b54fff12-3021-50a1-a528-9d5e4e6811d0 | note | Verification Activity: Activity - M
8b1cfc15-3b30-5ee6-a294-a4d0f16103c9 | note | Verification Activity: By - SE
42ecb55c-639f-5bdc-a60c-8778e8f586be | checkpoint | 3.2.1 - Timber fence
d4316e81-867b-58ab-9596-b44287b1f3cf | note | Detail - Preserve timber exposed faces
5d5e9a2d-6a4d-58bc-9093-8643504d18fd | note | ○ Post imbedded in ground
8e9338f9-e7a9-5b7d-9ca3-3aa80ff61f31 | note | Acceptance / Conformance Criteria - 1.8m high
9508edf4-88d7-55ba-9ac8-e6968cf7b96b | note | ○ Exposed timber faces neatly protected with 2 coats of timber preservative (Metalex)
9623e987-c6f2-5d55-81fc-5622cb550839 | note | ○ 1800mm in ground with 17.5MPa concrete
4e0aa3d2-8b75-5ddd-8631-9598808c35b4 | note | ○ Minimum 100mm extend around the post
a685488e-d7f7-514d-942c-d745412a8f69 | note | Standard / Specification - PS 27.5.5
f6d7f996-c09b-5457-82a7-f73078527bb4 | note | Verifying Document - Delivery docket
7faebad8-8d34-5361-b428-2cbb50372b40 | note | Testing Quantity Required (based from schedule qtys) - During installation
4cc86542-9a5b-5660-882a-2b059e971f0b | note | Verification Activity: Activity - M
26b50076-ae91-5c35-8a91-c9991469d4f5 | note | Verification Activity: By - SE
0925a98a-cb05-53ed-bbcf-af284fac16fe | checkpoint | 3.3.1 - Post and Wire Farm Fence
a99eecce-1bd6-5757-ab09-4a0d680142a2 | note | Detail - 8 Steel wire
7db0eb80-7ddd-573a-9253-9f0367c508c9 | note | ○ Timber post located at max 5m centre and securely rammed
94b5ab92-09fd-549a-bbef-470b80a3ded6 | note | ○ Battens affixed to wire and timber evenly spaces
468bcdd9-c010-5727-bb03-23297570b593 | note | Acceptance / Conformance Criteria - Wire and ground distance < 125mm
a81f057d-2c0a-5b49-913d-da98849be607 | note | ○ Top wire to > 1m from ground
a6e655e0-1d7a-5e59-bdce-49e96ca95c86 | note | ○ Top of post > 50mm top wire
4fe274a8-f56a-5649-9772-9f3c0ea9eca6 | note | ○ Wires not attached on road side
79fcb05f-b14c-593e-9310-936c029d8ec0 | note | ○ First 3 wire separation 125mm
3819f83b-c1d0-5a7b-93fa-b09ec9bce062 | note | ○ Min 3 battens between posts
042662cf-7c8a-5cba-9f10-e32e166877c2 | note | Standard / Specification - PS- 27.5.6, NZS 2566
3418000d-3d38-57bb-9402-e322950b9a0a | note | Verifying Document - Visual inspection
ef05d5b9-bd63-5ba9-97f5-67cb63132ce0 | note | Testing Quantity Required (based from schedule qtys) - During Construction
cb8ceb04-16f5-57d6-9011-32b47bb8254a | note | Verification Activity: Activity - M
750bf047-2bb0-5ba5-b919-f85ad174c439 | note | Verification Activity: By - SE
94bb45d6-7c4a-5d34-9c38-ef50db464e25 | checkpoint | 3.3.2 - Strainer Posts
5eaa510d-3abf-564d-91e0-0687d7761430 | note | Detail - At new and existing fence terminations
51b392b8-abab-5567-87a5-77726bb2042c | note | ○ At each corner distance between corner and/or termination strainer exceeds 200m
d6c56c89-dfe6-5340-8dba-2e813b7fd5f7 | note | Acceptance / Conformance Criteria - Double footing and tight wire secured to the post using 4mm wire
b0a26b89-41ad-5167-af76-f10b58d3241c | note | Standard / Specification - PS 22.5.6.b
6ddd964e-1636-56b0-96f6-13d333cc1fd6 | note | Verifying Document - Visual inspection
5bf4e9fe-de84-5ef6-b6e3-19665fa1c039 | note | Testing Quantity Required (based from schedule qtys) - During Construction
9fd2937e-3755-58d7-ac9e-22f0494e473d | note | Verification Activity: Activity - M
d0bf2e5e-cac4-54d8-a3ed-5919040b7a75 | note | Verification Activity: By - SE
4067999f-5728-5587-8d89-7544a2a9c8b2 | checkpoint | 3.4.1 - Chain Link fence
49ccd8f6-152c-5be0-86c8-0816a13e7e1b | note | Detail - As per drawings
cf7d3ade-8d42-5a14-a50f-070e5a74f692 | note | ○ Headwall and Wingwall fencing
bb2211d5-3200-58fd-ab7a-1eb31f32ef4a | note | ○ Secured with posts and top rails
08ca82e7-f3c2-5580-985a-2e7f1364c65b | note | ○ Spacing between two post must be equal
66f2a5bf-d6be-5cb9-9bbd-d73b88e04d37 | note | Acceptance / Conformance Criteria - Tie wire on every second diamond
742f6d38-b923-5d12-b795-864bced588b5 | note | ○ Spacing < 2400mm
eb901cff-cee9-5f5c-97bd-5755a3be111b | note | Standard / Specification - PS 2-32735.02-WSP-DR-UDL-0407
cfbb4d20-0a62-51e2-83f7-f7e6f4f19055 | note | Verifying Document - Visual inspection
016b0d32-bd62-5a8b-8694-80f46c88f8c5 | note | Testing Quantity Required (based from schedule qtys) - During Construction
929a7432-3580-52b6-949b-87077a10bcf3 | note | Verification Activity: Activity - M
359818d8-98d8-5a2b-8d59-d3bb6f1a10b4 | note | Verification Activity: By - SE
801f7ada-618c-5ced-9ef5-1d9f7eae2d38 | section | SECTION 4 – HANDOVER
13049da8-dc5f-50e6-9653-61f13f53ec94 | checkpoint | 4.1.1 - Survey As-Builts
80835152-ec3b-5e5a-b659-35b7e243d274 | note | Detail - Quality Check on New Works based on the tolerances in RITS
6137f7ba-ad1a-5fce-8331-3e570fa5c5e8 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
5afaec36-5ff3-5d6c-8432-40d0ad8dea64 | note | Standard / Specification - PS-21.7.7
a9994d3c-d6bb-548a-a6b8-094cae2a1a95 | note | Verifying Document - Red pen markup only
02da7ac2-5c09-551f-b3e2-139dc087d778 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
44d84a42-1183-5ed1-aa30-431c32e958db | note | Verification Activity: Activity - H
9dd801c2-36c1-54bb-89d4-b13fc7e94d3a | note | Verification Activity: By - ENG/PE
27026435-63b7-4de6-a5e0-1515761c6dfe | checklist | Ω (DEPRECATED) DN1210-SP2-0006-0006 ITP Vehicle Crossings Rev 1 | itp | DN1210-SP2-006-006 ITP Vehicle Crossings
21d0a90c-635b-4647-9c7d-7508c04f5a04 | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL, PERSONNEL & THIRD PARTY APPROVALS
be5e3ae2-26f0-4e71-ae98-808822583d54 | checkpoint | 3.1.1 - Crushing Resistance
fb01caa0-e1af-5bff-8c4a-c55e88e8b2e5 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
8007206b-c4b5-584a-ab99-29d6becfac83 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
9d0d1281-c3d4-56c4-a6cf-2a0884d0e00b | note | Standard / Specification - Project Specifications 20.9, TCC-IDC IT-4.8 table 4.6
4875482a-fb5a-53cb-8d01-11a24cb716c6 | note | Verifying Document - IANZ Accredited Report
931c4f75-20aa-5b26-89a5-21fbf7719851 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
710c509c-bcd8-58e9-87a0-6a3826e7db87 | note | ○ Results to Engineer 2 wks before importing
8e2acf5d-fdc1-50f9-b672-70a105bb14a8 | note | Verification Activity: Activity - HP
841f1e19-2695-58d0-affd-48ffef682f2d | note | Verification Activity: By - ENG
81e6294a-aa5d-493d-81b4-936ba9ad3e62 | signoff | AUTHORITY HOLDPOINT
b8c2b0d6-ffec-40bc-88a3-f13adcaa83ee | checkpoint | 3.1.2 - Soaked CBR
fa72c847-22ec-56bd-9391-7f83fe1b6b34 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
bbc52872-69d5-5c3f-a7a7-87b0addb58c4 | note | Acceptance / Conformance Criteria - >80%
b3167cf1-8cb0-53bb-8422-ac47cbcc3fab | note | Standard / Specification - Project Specifications 20.9, TCC-IDC IT-4.8 table 4.6
e41e9767-404f-514e-b116-877d16535b58 | note | Verifying Document - IANZ Accredited Report
d899066e-8d3d-57ef-8bb6-31f078a8ce8d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
3b0d302a-0ab6-5ab4-a8ea-f2b68e45f76c | note | ○ Results to Engineer 2 wks before importing
efec1bf0-f301-5290-b6c0-0c02d5331042 | note | Verification Activity: Activity - HP
3e42d750-5d05-5dd5-840c-bd70552fece9 | note | Verification Activity: By - ENG
4d77b517-4059-4a16-9e0f-6321520bdfb5 | signoff | AUTHORITY HOLDPOINT
e95d4515-aa17-4a3f-a5cb-e4fc10b6aff3 | checkpoint | 3.1.3 - Accelerated Weathering
31bf0118-c0b6-5048-90fb-1ec07948d183 | note | Detail - NZTAT/20 Ethylene Glycol Accelerated Weathering Test
816a4f69-7b99-5ce1-83f1-11ab65ada2a7 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
5a3df4b5-1d4b-5e9b-81b2-c3fcd5d33a73 | note | Standard / Specification - Project Specifications 20.9, TCC-IDC IT-4.8 table 4.6
80b667de-27b9-5912-b351-47c03dfefbf2 | note | Verifying Document - IANZ Accredited Report
328b72bf-bf0e-55ab-b956-0146d891bb52 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
8771fd04-6281-5bba-9d38-671a4f8ed0a3 | note | ○ Results to Engineer 2 wks before importing
db758d29-0364-5dc7-b701-d3b0ce3fd8b6 | note | Verification Activity: Activity - HP
9962557f-abdb-53e8-a36f-dfbb999ac70e | note | Verification Activity: By - ENG
beb67fc3-ebbe-495e-a992-4275f0b75214 | signoff | AUTHORITY HOLDPOINT
c0989cf6-7820-4723-bb9f-0a9af357b15e | checkpoint | 3.1.4 - Weathering Resistance
d29be925-1d80-5a93-ac58-72e43a6c00d8 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
c3aee4a7-61e3-5592-8906-0976ef9fb54f | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB or CA
20f7c0e4-ad1e-5ad5-9b02-d4265c1ef6e1 | note | Standard / Specification - Project Specifications 20.9, TCC-IDC IT-4.8 table 4.6
10b4e86d-b34d-5cd9-93cf-034aa2766075 | note | Verifying Document - IANZ Accredited Report
07d8329f-1d09-57dc-ad36-e7764646dcd3 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
a085c989-3d8f-5c32-b9e8-315b958f0679 | note | ○ Results to Engineer 2 wks before importing
62547bf3-6821-525c-a0c4-eed584b17e2d | note | Verification Activity: Activity - HP
287ad739-ead8-59ad-9b0e-0b526aeb33b5 | note | Verification Activity: By - ENG
2e90d0a6-973c-4650-a964-617ee7aca72b | signoff | AUTHORITY HOLDPOINT
83eb187f-659d-4668-84a1-aab92920e7e0 | checkpoint | 3.2.1 - Particle Size Distribution
3be07129-a86c-5533-8f39-a425889b5228 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
6a11f0d4-5416-50f9-ad87-890767bce598 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
4d70c8f5-1806-5b19-998d-18c2a49de41a | note | 37.5mm ¦¦ 100% passing
3c5cb16f-9bdb-5033-9a73-adca501bf440 | note | 19.0mm ¦¦ 60-75% passing
61bfa52b-2f03-521d-b4ad-acf9544dc9f9 | note | 9.5mm ¦¦ 37-50% passing
fdc769a0-61ab-5425-b78e-aae34c7792d3 | note | 4.75mm ¦¦ 20-35% passing
06bd031e-8332-5385-a341-5411a7ae60f4 | note | 2.36mm ¦¦ 12-28% passing
a6a596d6-b8b9-5697-9817-da1ca366d4f0 | note | 1.18mm ¦¦ 9-20% passing
df2afdf2-7bce-5b4a-9521-1fe9d4fd12f1 | note | 0.600mm ¦¦ 7-12% Passing
dbb7a48a-0996-5cbc-9afe-99cb38cd861d | note | 0.300mm ¦¦ 3-10% Passing
c8e13e92-c946-56d0-8fba-00bd32198a86 | note | 0.150mm ¦¦ 0-5% passing
aca3362b-fefd-508d-ad96-86b0d51f2f6e | note | 0.075mm ¦¦ 0-5% passing
5c3c3323-c191-5955-940c-b9f1312221c7 | note | Standard / Specification - Project Specifications 20.9, TCC-IDC IT-4.8 table 4.7
7d28d4f6-4ba3-5b7a-8f03-5e0578f09f21 | note | Verifying Document - IANZ Accredited Report
566ce60e-9ef6-5d7a-9bc4-31b8e8ab2e70 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
ea9b3cac-7725-573d-a314-b1555f721ce1 | note | ○ 0-400 - 2 tests
82ec5efa-26ed-55c7-ac99-8b47c9d5e300 | note | ○ 400-1,500 - 3 tests
77c3dda5-7661-5760-90c4-5f403e7b0e5d | note | ○ 1,500-4,000 - 4 tests
d0427e2e-ac25-5f76-af83-4f8c3b7820ca | note | ○ >4,000 - 1 test for each additional 1,000m3
9a867c66-2b2e-5757-833b-45f8ec0d10e9 | note | — Results to Engineer 2 wks before importing
fdc0b0d3-bcb3-5cd8-8f7c-9c31b8beead1 | note | Verification Activity: Activity - HP
d0ebbf02-a21a-5487-aad0-949659c1dcd5 | note | Verification Activity: By - ENG
eb21856e-84a0-43cd-882c-5f69b67f13a1 | signoff | AUTHORITY HOLDPOINT
cff054b6-f2c3-4791-b67b-b5ccfc28b0bb | checkpoint | 3.2.2 - Shape Control
9324852f-27f8-5d4e-83e6-4c8fe13962d5 | note | Detail - Tolerance allowed from approved grading curve (%)
85502cd5-e6ec-57e1-b1eb-30c80dfb5e23 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
b519e2fd-e389-5db8-b31a-85ddb2d47b83 | note | 37.5 – 9.5 ¦¦ 28-48%
dd25e1ff-7918-502c-a29d-5e6c34ead5a6 | note | 19.0 – 4.75 ¦¦ 14-34%
d82f0467-b707-5948-a6c1-02336aa98de7 | note | 9.5 – 2.36 ¦¦ 7-27%
9fc0dd9c-370b-5cee-91e1-c34be5182687 | note | 4.75 – 1.18 ¦¦ 6-22%
57ceb7bb-7cea-59a9-a8c7-2a56f6b835db | note | 2.36 – 0.6 ¦¦ 2-20%
bc574505-4785-5559-bffb-ce1b516afee6 | note | 1.18 – 0.3 ¦¦ 5-19%
14afa95c-9ce5-5005-be1e-50eb7c9db576 | note | 0.6 – 0.15 ¦¦ 2-14%
7a5d5751-2374-554c-b084-867e1232f15e | note | Standard / Specification - Project Specifications 20.9, TCC-IDC IT-4..8 table 4.7
c6e16b98-1ca6-57d4-92ef-9b84037b6f43 | note | Verifying Document - IANZ Accredited Report
639f6e31-535e-52e3-ac5e-6f20f0353f59 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
05c92fe9-b713-5433-ba85-8b1d10a4e6fc | note | ○ 0-400 - 2 tests
9e44cdde-2f70-5f1e-9753-866b4eb08b96 | note | ○ 400-1,500 - 3 tests
cb543149-e60b-52cd-86c2-ff377a23053f | note | ○ 1,500-4,000 - 4 tests
30b11133-65de-56f5-9d7d-ef2f81489a7b | note | ○ >4,000 - 1 test for each additional 1,000m3
4543e343-9dff-5712-aab4-4ca33394196f | note | — Results to Engineer 2 wks before importing
d9cc5f17-03c3-53d8-97ae-20dc59f67cb6 | note | Verification Activity: Activity - HP
537f00bd-808f-5107-9f43-d04e91c3651a | note | Verification Activity: By - ENG
38aff92c-b485-42e0-9be9-b7cf450cffcc | signoff | AUTHORITY HOLDPOINT
ddf8bdd7-f256-4ca3-b781-0ee9ca01f980 | checkpoint | 3.2.3 - Sand Equivalent
40e38dd3-6d20-5727-9e6e-f20c15fd903a | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
1aca796d-d0ab-54ed-8a0b-62b2497460a8 | note | Acceptance / Conformance Criteria - ≥ 40
7e7c701f-a735-5e5a-8718-28200c50ef12 | note | Standard / Specification - Project Specifications 20.9, TCC-IDC IT-4.8 table 4.7
73435c64-02fd-5211-af3d-4492314928e7 | note | Verifying Document - IANZ Accredited Report
b55d1823-3f0c-5296-a0d2-ebb78bcc2157 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
15802d11-d087-57a1-9eea-ec626749087b | note | ○ Results to Engineer 2 wks before importing
48db1826-1d09-57f8-a03b-631d872c2251 | note | Verification Activity: Activity - HP
bd398f26-11e7-5480-abdf-f460583b6566 | note | Verification Activity: By - ENG
4410e992-23e1-474f-8011-e05dcc61ddcd | signoff | AUTHORITY HOLDPOINT
7327deab-017a-4d16-aea0-c86937e76105 | checkpoint | 3.2.4 - Plasticity Index
6de581b8-881c-5365-a5db-7a258accb25d | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
6db03cbe-0fc5-5497-941a-7df1b644392d | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
24d788ef-cc24-5568-951d-48464f395839 | note | Standard / Specification - Project Specifications 20.9, TCC-IDC IT-4.8 table 4.7
47253b1d-b84a-5d13-a734-41fbda8c8e71 | note | Verifying Document - IANZ Accredited Report
c2d7acc9-c85e-5ed5-b5a9-d7cabd98380f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
ef561b2e-1083-51dd-8253-46c6e1fdb68a | note | ○ Results to Engineer 2 wks before importing
bd1e3ac6-8fb8-5852-965d-a66ff4be67c8 | note | Verification Activity: Activity - HP
da3e7d3b-5681-5f7f-b481-8c4fecda8c32 | note | Verification Activity: By - ENG
7abcaa94-6b08-4667-9e75-8c97907241bf | signoff | AUTHORITY HOLDPOINT
80f65c5e-63e3-41e9-88c6-6ffd10508548 | checkpoint | 3.2.5 - Cone Penetrometer Limit
485bf190-dfd8-5558-ab26-a67794f4d539 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
e0a36da5-99f5-5004-a3fc-a99b832537f5 | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 30
d1a2e61f-f5ec-5263-b0a4-323ee41a4866 | note | Standard / Specification - PS 20.9, TCC-IDC IT-4.8 table 4.7
0fcaa1cd-bf85-5b52-8feb-49afc1041611 | note | Verifying Document - IANZ Accredited Report
0e925867-c640-58a2-af79-cf55a034f0c6 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
ee1e1104-93d3-5d7a-8381-764358312213 | note | ○ Results to Engineer 2 wks before importing
cf5e4294-4be6-58ca-a81d-b3bfd0d749dc | note | Verification Activity: Activity - HP
76f552f7-0a55-5149-9ff0-bd5040e0ffef | note | Verification Activity: By - ENG
8d11851f-fec6-4ef1-a041-cd3b7ebe58fd | signoff | AUTHORITY HOLDPOINT
8fe7eab4-95bb-4314-be34-5d900d364c0a | checkpoint | 3.2.6 - Clay Index
7f40b5de-17b4-5ab7-90e2-47656423a22e | note | Detail - NZS4407:2015, Test 3.5 - Clay Index Test Report
9e5b7652-17a7-5408-956e-a8861ce7fd6f | note | Acceptance / Conformance Criteria - ≤ 5
ddd4a1d0-ad30-5eae-9e39-7f52c8688e60 | note | Standard / Specification - Project Specifications 20.9, TCC-IDC IT-4.8 table 4.7
714f41e9-e6d4-54e2-a8a3-de4ff2af97fe | note | Verifying Document - IANZ Accredited Report
6811506b-a023-5edd-878a-7fa805f1db34 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
b21c219e-c931-5b17-9afb-694b2ba261c3 | note | ○ Results to Engineer 2 wks before importing
46950442-863d-5790-a61c-405264c81964 | note | Verification Activity: Activity - HP
8f73e62c-19db-5271-a32a-6dfbc6b88b04 | note | Verification Activity: By - ENG
6b891fe5-a5d3-4f1e-a4f6-1867ed2f69e4 | signoff | AUTHORITY HOLDPOINT
5c85dcac-0b0f-4b72-ba3d-536a1069b44b | checkpoint | 3.2.8 - Maximum Dry Density and Optimum Water Content
ac1b86e6-fa58-5956-8e2d-2af0d9b172fe | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
ec1190b3-67a1-5ed7-833c-34574744b994 | note | Acceptance / Conformance Criteria - Report Value Only
9504bb9b-a070-56b4-bb98-18b9df93f31f | note | Standard / Specification - NZS4402:1986 Test 4.1.2
b9b426ac-1b42-5bff-a720-6c50f502f052 | note | Verifying Document - IANZ Accredited Report
5e72ce0e-39fc-523d-8841-c1cac8fe411f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
7c57c901-e480-5ef1-b64e-a42776bf043e | note | Verification Activity: Activity - HP
493240f3-5295-599f-a8df-41c1ce688a73 | note | Verification Activity: By - ENG
9b58abb9-9f3d-454d-9610-3dd3981ce6db | signoff | AUTHORITY HOLDPOINT
3af16d2c-a2a4-42c8-b8a0-7d7b66545688 | checkpoint | 3.3.1 - Reinforcing Mesh
09be6faf-da4c-5a51-aa52-a3427ec10c56 | note | Detail - 661 Reinforcing mesh (Commerical Vehicle Crossing)
1676eff7-385d-513e-9239-77399a7f8f08 | note | Acceptance / Conformance Criteria - 661 Reinforcing mesh (Commerical Vehicle Crossing)
407cdd4a-3956-5f3f-af4d-f90b512f2e3d | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
8e556146-4d6b-5291-86fe-936a7406d2e8 | note | Verifying Document - Material Data Sheet, Engineer's Approval
46b2c1c4-f6a4-52bf-96ed-16ec3d8fd01b | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
012e2e61-2c89-5417-941a-aae1fa5229fe | note | Verification Activity: Activity - W
01bab8d5-0df7-55f9-855f-5917a2a59113 | note | Verification Activity: By - SE
c4e52aec-5cce-448a-9e0c-0cf3f4f2cc6c | checkpoint | 3.3.2 - Reinforcing Ties
f6af33bf-eec5-517d-89db-3287867f61c7 | note | Detail - R6 Ties (For commercial crossing only)
aedd3cc5-e4dc-5f7b-801c-185b1298e2dc | note | Acceptance / Conformance Criteria - R6 Ties at 600 centres with 60 mm (For commercial crossing only)
cd5b1f70-0f16-5187-817a-9df24bd31e3c | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
ba6a9496-84d2-5e98-a614-8dc18fe08815 | note | Verifying Document - Material Data Sheet, Engineer's Approval
1fc12d0b-d4b3-5e78-9bd8-b810f6818b6d | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
174e8a95-9903-5696-b858-d06d21d5f762 | note | Verification Activity: Activity - W
0350df67-ff66-50c3-8924-4a090cbfb8a7 | note | Verification Activity: By - SE
817bde90-1faf-4d1f-b1fc-19f7b42a627c | checkpoint | 3.3.3 - Reinforcing Bars
09808d58-1692-5ab3-b4a8-04e1821d8099 | note | Detail - 4-D12 Bars (For commerical crossing only)
3fcdb810-6b8f-576e-99c6-9d215eb53b21 | note | Acceptance / Conformance Criteria - 4-D12 Bars with 50 mm Cover (For commerical crossing only)
a2771221-96fe-535d-9e56-1c8b5548327e | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
45e438a3-84c6-5fcf-8f57-51c55434f957 | note | Verifying Document - Material Data Sheet, Engineer's Approval
ff4cf850-4d0f-5eb9-9d24-9e0073c6eb4f | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
c7bbd17a-87a1-51d6-aed5-13be266b68b7 | note | Verification Activity: Activity - W
ec009e6e-3645-52ff-bfce-ee21735a8529 | note | Verification Activity: By - SE
8d9b106a-047b-4773-aeb4-c793c250f699 | checkpoint | 3.4.1 - Concrete Mix Design
79e0bf42-9970-5ddb-8b9f-c6b7eef9f5ef | note | Detail - 20.0 MPA concrete. 4kg/m3 black oxide (2.5%)
efaa34f0-cb37-5df7-9fed-606f89106879 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 20MPA
c8a7dbf7-db09-53d1-ab6c-65d48edc81af | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405
1db4c3e4-0add-5ce1-b4c1-71fabd43a351 | note | Verifying Document - Material Data Sheet, Engineer's Approval
a55824c6-3813-5841-a537-be9d1fd8c7ed | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
e5a367cf-385d-590e-b2c2-99a8b7acdb78 | note | Verification Activity: Activity - HP
5ba8e87f-a8ff-5a9a-8492-5f41e789d600 | note | Verification Activity: By - ENG
86c59c7c-d048-4a4e-b315-208161338ab5 | signoff | AUTHORITY HOLDPOINT
57b0927a-3e15-484a-9888-20bedc4f101b | section | SECTION 4 - CONSTRUCTION
ca90406c-cb93-415a-a30d-32da9af0af0a | checkpoint | 4.1.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
fd4b2250-43b2-579c-970d-c844588edbc3 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
6b4a9a74-8610-5f94-b0aa-f034ed3537b8 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
4817528e-df90-577d-bad4-962541391d97 | note | Acceptance / Conformance Criteria - Average Minimum SU:
e38e4d05-ab70-55a1-845a-4e31a460456f | note | — > 60kPa
c4929259-bbff-5dec-b067-bd5b89f8d77d | note | — CBR: >3
e2e65f42-b5e5-5f2a-aa77-148188d51c54 | note | ○ Single Test Minimum SU:
b22eb6e6-bbac-5778-9768-12ba4e84fe5e | note | — >50kPa
365f1ed3-0795-56ce-b289-501b4dac8675 | note | Standard / Specification - Project Specifications Appendix XVIII
04c40126-3853-562e-abec-1d8dd595d435 | note | Verifying Document - Shear Vane Report
55241dd8-2e2e-52e0-98bf-f5d09e92cde6 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100m2
85aef746-1a81-56bc-943f-bf3ecc3bf54d | note | Verification Activity: Activity - I
da6b9da8-5569-5ad2-bce8-dd1f6f9b9808 | note | Verification Activity: By - SE
94c51d23-53ae-48ce-b8cc-f837cbf0c5e5 | checkpoint | 4.1.2 - Cut Subgrade Testing - Granular Scala Penetrometer
dc556c1d-6f60-5e39-bf76-f019cbb76d25 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
9558bd7b-813f-5f3f-bc96-b7cd79c02b40 | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
0bdad1ae-6c57-5a67-a89b-77a7ab681d42 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
c81130f7-3bb5-53eb-b54f-af1016aa0a10 | note | Standard / Specification - Project Specifications Appendix XVIII
21f4d813-9773-587d-bc75-910b8e74b4a3 | note | Verifying Document - Scala Report
884269cd-4ceb-575e-97af-74ef9d2beee0 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400m2
a70b7850-661c-512c-9417-5f6da4ee22dc | note | Verification Activity: Activity - I
32de67e0-29ee-500b-a35f-2960befa26a9 | note | Verification Activity: By - SE
cb0c7dce-64ca-466b-9de9-e1320ee12f77 | checkpoint | 4.1.3 - Proof Roll Subgrade
9bf6367c-6653-5ca6-81d2-6ae11990dc08 | note | Detail - Visual Inspection of Proof Roll
c41e1ab5-a261-5a39-9ab1-ac36ba6a5219 | note | Acceptance / Conformance Criteria - Visual Inspection
cf00438c-92f2-5a84-9026-9543b75b8490 | note | Standard / Specification - Project Specifications Appendix XVIII
5703d7c8-92d6-5fc8-baeb-3e7ee08564e0 | note | Verifying Document - Visual Inspection/Photos
56d89d0f-630c-53d5-be46-d486851b14db | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
7626018b-5cf1-5348-882b-e3a433dbde34 | note | Verification Activity: Activity - I
5057cfd8-342d-5fb6-beba-c3a03cd8e460 | note | Verification Activity: By - SE
5f8cab21-2609-4b9d-978e-ca12fbb0b5a5 | checkpoint | 4.1.4 - Hold point
7aa1bec9-8172-506e-bafe-1816c6cd47ba | note | Detail - Subgrade signoff
cd380824-0fc0-5554-bb63-e794c4e0a256 | note | Acceptance / Conformance Criteria - Conqa signoff
be3d59ea-f8fa-5261-b321-c9fe26db05c0 | note | Standard / Specification -
7652917f-2aef-53b1-b087-e6cf807a0965 | note | Verifying Document - Conqa signoff
340590ea-1648-5a39-9929-6bd50e011b02 | note | Testing Quantity Required (based from schedule qtys) - Each area
b3d41d93-891f-558b-a659-b55ea892f4ee | note | Verification Activity: Activity - HP
af131512-3724-597c-b943-b98eb29839c2 | note | Verification Activity: By - ENG
6ece917a-3847-45dd-bbf2-fa537a8b884a | signoff | AUTHORITY HOLDPOINT
36664998-978c-40a7-85b1-a4f76f35740b | section | SECTION 5 - CONSTRUCTION - RESIDENTIAL AND COMMERICAL VEHICLE CROSSINGS
f266db7b-88da-41cd-b4b8-1f55a615f56d | checkpoint | 5.1.1 - Stringlines or equivalent
e7146593-0f4b-508c-86f5-9be2899f0b58 | note | Detail - Stringlines or equivalent to check finished height of surface
9c065cc8-775a-5b96-945e-dda4348e641b | note | Acceptance / Conformance Criteria - Height '+15mm/0mm
1f9a1325-ac26-5038-a8c2-dfa14fe5066c | note | ○ Width –20 mm +100 mm
a43a9a40-5f87-5439-a030-163849f29940 | note | Standard / Specification - NZTA B/06 8.2.2 - Table 3
d5fa5f9c-9066-5d13-b8af-2e3a1f6a7983 | note | Verifying Document - Surveyor Records
c66f0e1c-8a94-5740-b0a1-8b43aac8a90c | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
4f299b41-3d15-5f5c-ba7c-89df18eab4f9 | note | ○ 1 set = 5 tests
dad07ab8-1741-547d-a0d3-5143e98deec4 | note | Verification Activity: Activity - I
455c08c8-0855-5804-b375-9457046ac5da | note | Verification Activity: By - SE
172d5da9-f3c5-4231-a40b-71d86aa2dab9 | checkpoint | 4.2.2 - Compaction - Clegg Hammer
e7d94db2-6707-537f-b0ae-1655acfd9ad1 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
19aa116b-2cad-5d77-867f-f040b86068e7 | note | Acceptance / Conformance Criteria - Min CIV 18
b4291f8c-00bc-5f1d-9fbc-a0192135110c | note | ○ Ave CIV 20
8500998e-d625-593f-87d4-42f0c4de417a | note | Standard / Specification - Appendix XVIII
a3ef3384-a8a3-5e69-a100-aa966fe45c8d | note | Verifying Document - Clegg Hammer Report
75745885-8b1c-5efc-a583-01280b05d774 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
727bc7f0-0988-5f01-8d05-21621271be69 | note | Verification Activity: Activity - H
fb318684-e493-5c82-9122-d605eb5d76f0 | note | Verification Activity: By - SE
0872d87d-9fe1-41e8-87f7-f1f5d3d9375e | checkpoint | 5.1.2 - Compaction - NDM
99572d3e-7435-5d13-8473-453ba35acc8b | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
a1bbe3d9-844e-546a-ae92-dea86ece6b42 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
7dd1b9e2-d51e-57a3-b0be-fa4d49b5a2aa | note | ○ Min >92% of MDD
c69e5943-f2d6-518f-9f6f-02db48d5bec5 | note | Standard / Specification - NZTA B/02 7.6
572dbca2-d36d-5b3c-b3c1-f9eeb32a78dd | note | Verifying Document - IANZ Accredited Report
d4b992de-443f-5230-b947-48b585238cb6 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
7a0365e2-4c6e-5559-81f7-9ef9a02b3401 | note | Verification Activity: Activity - I
b808c0fb-4317-52ae-a019-eda541a8d681 | note | Verification Activity: By - SE
f2c8b08f-fea3-46f4-bd76-2a642de9a835 | checkpoint | 5.1.3 - Hold point
c1c3a90b-fac3-591b-98f5-29403ea6db0a | note | Detail - Basecourse signoff
bad066dd-693e-532e-8d9d-7ea031472eaf | note | Acceptance / Conformance Criteria - Conqa signoff
b85021e0-e9c7-551d-852d-40db6492d8ee | note | Standard / Specification -
aa668013-b31f-518d-96a6-f2f0b614edc3 | note | Verifying Document - Conqa signoff
1a624c9c-569f-57b2-bc41-87ce84c0d274 | note | Testing Quantity Required (based from schedule qtys) - Each area
1598f0d2-2980-55f6-8041-c8d21911864f | note | Verification Activity: Activity - HP
977acd5a-1086-5226-80e8-261fa54a8a04 | note | Verification Activity: By - ENG
1ea49bf1-c01a-43de-bba0-052a0c231bbb | signoff | AUTHORITY HOLDPOINT
6f379e1d-601b-4af2-bd39-13a9695f1598 | checkpoint | 5.3.1 - Surveyor check
2713017f-1f13-51fb-91ea-fc3d99ba243d | note | Detail - Equivalent to check the position of the formwork
8729a4b1-9598-5314-9b76-19ef9881a1eb | note | Acceptance / Conformance Criteria - +\- 100mm of design
c3e8896d-2e34-5434-a620-a67815bf4db7 | note | Standard / Specification - Project Specifications 27.4.5 (b)
b13e8c2a-dd8f-5af6-9266-c9d1d6c254c4 | note | Verifying Document - Surveyor Records
0efdc6db-667f-59d0-9ee4-073a9de213c0 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
2cc7ccd1-9900-5796-bd2e-aeb740dc79db | note | ○ 1 set = 5 tests
fc3cadfc-dd66-5452-b9c9-54bdb7f420f6 | note | Verification Activity: Activity - HP
e6cef7ac-ad0d-5318-96b2-4b618a46421c | note | Verification Activity: By - ENG
b5bb68e3-ecc9-4a57-8b9f-87c814e5f1cb | signoff | AUTHORITY HOLDPOINT
e97bfe8b-49b9-4fb6-9a99-a6a831e48c69 | checkpoint | 5.3.2 - Surveyor check
12c36cab-dfc2-5968-9b08-dc9fc19bbf7c | note | Detail - Equivalent to check finished height of framework
3b820106-803f-5538-8e76-5643f3020924 | note | Acceptance / Conformance Criteria - +\- 10mm of design
87859a7d-7583-5854-bc73-b5833e1f3270 | note | Standard / Specification - Project Specifications 27.4.5 (b)
68c8b11f-a43e-5881-96fd-aa4ec60fd9ce | note | Verifying Document - Surveyor Records
585cd140-4ae2-5622-9d60-705bd4a7c14d | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
9861e834-fc34-5cd1-a2a3-503ba9cee95e | note | ○ 1 set = 5 tests
89854bfc-95c2-5dcf-8c3e-baaf5803c2a5 | note | Verification Activity: Activity - H
5db80d52-7683-5894-928b-e689b7f5f0f1 | note | Verification Activity: By - SE
a8c3366b-9ebf-43af-86f5-5d91f62ceec6 | checkpoint | 5.4.1 - Reinforcing Mesh Check
dbeac556-b5fd-566b-b5dc-a6ee2487b2be | note | Detail - 661 Reinforcing mesh (Commerical Vehicle Crossing)
3a80d719-3f7e-5a3a-a982-5bdfb1f1815a | note | Acceptance / Conformance Criteria - 661 Reinforcing mesh (Commerical Vehicle Crossing)
3f42bac1-bac2-524b-a998-12ea4578c689 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
b02cd7d7-43e9-5178-81b9-96ca4ae112ba | note | Verifying Document - Delivery Dockets, Visual Inspection/Photos
200ded1c-c185-5dcf-8080-b5526cb0f0e4 | note | Testing Quantity Required (based from schedule qtys) - Before Pour, During Construction
8a59f231-acc7-5340-9b78-47162c87e2c0 | note | Verification Activity: Activity - H
8ff86538-1947-549e-9d7e-6edfdec99ed0 | note | Verification Activity: By - SE
2f6a993b-32d1-42fd-ae18-b6ab01d69c1c | checkpoint | 5.4.2 - Reinforcing Mesh
bdd1a77c-c221-5005-891d-f6bbf071f00c | note | Detail - Ensure that overlap and cover above and beneath mesh
14efeda6-d1e7-5dbc-9236-711b87b77a3a | note | Acceptance / Conformance Criteria - Reinforcing mesh to be placed centrally in the concrete layer
2b375017-b1ae-59fc-9ece-be496fd7402b | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
08d6103a-3509-55ed-97eb-c3e115d6c4fc | note | Verifying Document - Visual Inspection/Photos
202df981-952e-517e-bc80-cb514b20a220 | note | Testing Quantity Required (based from schedule qtys) - Before Pour, During Construction
14821953-2e47-59db-824a-56509e4061e4 | note | Verification Activity: Activity - H
60360293-5cb0-5660-9f14-86f243c7e4b0 | note | Verification Activity: By - SE
a8f2ccf5-5b3b-4fb4-866f-a3ea098cf203 | checkpoint | 5.5.1 - Reinforcing Ties
44cf46f6-8374-5448-8dae-1392c7491839 | note | Detail - R6 Ties at 600 centres with 60 mm (For commercial crossing only)
ed692563-8fbd-588e-a12b-fc796a3510b3 | note | Acceptance / Conformance Criteria - R6 Ties at 600 centres with 60 mm (For commercial crossing only)
24080c86-31b7-5ee0-b93b-52ced079c6fa | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
3f8e2931-11f4-598c-ab29-db0ceaa517c0 | note | Verifying Document - Delivery Dockets, Visual Inspection/Photos
600c985d-d516-5064-b18a-48919dc1b35d | note | Testing Quantity Required (based from schedule qtys) - Before Pour, During Construction
fe10bc0c-27be-57be-a487-1a1e9ba31af7 | note | Verification Activity: Activity - H
8b268173-13ad-5223-9f36-ac2eccbe2031 | note | Verification Activity: By - SE
08681b0d-09be-4f0c-88b6-c3aab5855c22 | checkpoint | 5.5.2 - Reinforcing Bars
ca4d8799-f850-59ff-ae71-747118b18ed0 | note | Detail - 4-D12 Bars with 50 mm Cover (For commerical crossing only)
3a4013d5-6782-5868-966a-e8e24ce52769 | note | Acceptance / Conformance Criteria - 4-D12 Bars with 50 mm Cover (For commerical crossing only)
668c9928-9adc-5a83-9309-d694571a782c | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
d5ccd590-2f60-5130-bedb-ec31419a7c61 | note | Verifying Document - Delivery Dockets, Visual Inspection/Photos
f1b5bb33-0530-5b02-9938-e82911a3003e | note | Testing Quantity Required (based from schedule qtys) - Before Pour, During Construction
3f7ee954-8e33-5e22-b9c7-d8af92031c74 | note | Verification Activity: Activity - H
0fd35f1c-98d3-5c9a-94d5-cc8afa2adcc0 | note | Verification Activity: By - SE
ae6712bd-a07f-4052-8c79-9fbe06db69f5 | checkpoint | 5.6.1 - Concrete
e3753cc6-fcb8-563b-a7c0-a84b400b0fd1 | note | Detail - 20.0 MPA concrete. 4kg/m3 black oxide (2.5%)
072023a1-2300-56f6-a956-ae12111534f8 | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 20MPA
6140bb8f-3797-53d0-849e-5213b5cd79b0 | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405
04ae2dc1-ca32-54f3-b001-c47fb7bc0b23 | note | Verifying Document - Concrete Delivery Dockets, Test Results
7e58c2b7-a27f-5b44-b697-c314cc8ba7bf | note | Testing Quantity Required (based from schedule qtys) - Before Pour, During Construction
675700d1-1f13-56c5-b368-ce4fbc5814b6 | note | Verification Activity: Activity - H
eb6b11f9-353e-5499-9ef8-40cd0fce0d93 | note | Verification Activity: By - SE
c9f282fc-621d-4795-a648-0f2b3b176559 | checkpoint | 5.6.2 - Concrete Layer Thickness
aebaaf11-62f1-5d2b-b387-1e61b98acd12 | note | Detail - Concrete layer thickness to be 150 mm for Residential Vehicle Crossings
c8fe6de0-e05d-55da-81c2-7e36274e2926 | note | ○ Concrete layer thickness to be 200 mm for Commerical Vehicle Crossings
afa8ab20-3035-5b69-9061-ed6a5f15ba87 | note | Acceptance / Conformance Criteria - Concrete layer thickness to be 150 mm for Residential Vehicle Crossings
aa46fd5f-47f8-5b95-b6db-478c0f41e386 | note | ○ Concrete layer thickness to be 200 mm for Commerical Vehicle Crossings
bed76428-cc94-5e7a-989b-adb8e9ac6e52 | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
c12cad25-53a0-5084-aa6f-2ebcb3da1bcc | note | Verifying Document - Pre-Pour CheckSheet
69b678b0-cec4-5d3c-b095-8bd72ded2d31 | note | Testing Quantity Required (based from schedule qtys) - Before Pour
2c690edc-afc7-549b-a31d-b97422dece42 | note | Verification Activity: Activity - H
a4d41280-1cdc-594f-ab45-724ca75115c7 | note | Verification Activity: By - SE
3f694dc4-5908-4d5b-86a3-59fac2e0346e | checkpoint | 5.6.3 - Final Finish
3abc0269-9572-5e18-aaed-61bd757a6fde | note | Detail - Rough broom finish
b55ea4bf-7d2c-54ef-9a85-4558cb48ba67 | note | Acceptance / Conformance Criteria - U5
ec93497c-f04c-51e0-9a26-01073710a39b | note | Standard / Specification - 232735.02-WSP-DR-UDL 0405
ad155bac-a4a1-565b-ac2a-5867ecf59556 | note | Verifying Document - Post-Pour CheckSheet
a2be6b71-0f2f-53ef-a592-108375766fc6 | note | Testing Quantity Required (based from schedule qtys) - After Pour
ac6871a8-a02d-5297-b570-73db41b1f243 | note | Verification Activity: Activity - H
5bb66e28-f719-5cd6-9168-9438e5468610 | note | Verification Activity: By - SE
88b0ab10-bb4c-4bf0-914a-513b4ef4f01f | checkpoint | 5.6.4 - Saw Cuts
ca0a4799-b193-5817-84b0-73e7cdae12f5 | note | Detail - Saw cut expansion joints at 4m centres maximum each way
65eeff37-8207-520e-9181-4fe3630e1fb2 | note | Acceptance / Conformance Criteria - Saw cut expansion joints at 4m centres maximum each way
46377514-2b54-5ea6-af26-1b67dad7b15a | note | Standard / Specification - 232735.02-WSP-DR-RSA-0305
5bb69918-f539-5af3-924d-9fe1be7d722a | note | Verifying Document - Post-Pour CheckSheet
6243bede-9f77-51ae-93b9-cc5f849222a6 | note | Testing Quantity Required (based from schedule qtys) - After Pour
be827b78-d05d-50a7-8a2a-643ea995c221 | note | Verification Activity: Activity - D
e6acb78d-23c2-5f0d-873c-c583e846aeab | note | Verification Activity: By - SE
f61bb8a0-b339-4f65-b898-4f9b505b39b5 | section | SECTION 6 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
fe03c0fe-2e5b-4569-a9bc-267ef1090837 | checkpoint | 6.1 - As-Builts
af8bd243-ba2e-5300-ab6e-1aa95381a2f8 | note | Detail - Final inspection of all concrete work.
c5b8361f-240f-53e1-bd15-e4e42495aa10 | note | ○ Red Pen Mark up
3631f16b-5e3c-55d9-b1d1-a5d49effd4fe | note | Acceptance / Conformance Criteria - All works meet project specifications and standards. any changes to be noted on redpen markuProject Specifications
583d3ff5-1d6d-54c1-ae2a-9662525aac52 | note | Standard / Specification - Project Specifications 16.7.6
d6fc0235-5d13-5e2d-9e6d-80ad198a1257 | note | Verifying Document - Red Pen Markup
93cc6fca-198d-5373-886b-207404ca787b | note | Testing Quantity Required (based from schedule qtys) - 100% Completion of works
8ec40ee0-49a7-58e4-ab04-7a29c30aaeec | note | Verification Activity: Activity - D
b8c3ba06-f541-54b3-b82f-bfafb0601d0f | note | Verification Activity: By - SV
7b9534f7-db0c-4943-ad1d-a9eeb6db60e1 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
0d001949-ddfa-517a-ad85-8143779311ad | textbox | Contractor's Rep Name:
49fbaff9-bf96-5743-9674-0577696bf3f6 | textbox | Engineer's Rep. Name:
3ea99e20-0f80-5965-ac3b-64497797293c | date | Date:
644cb770-e421-4e65-9c41-9085837550ce | signoff | Add Signature
52ff326d-121f-48d7-aa4e-3315044c2cb9 | checklist | Ω (DEPRECATED) DN1210-SP2-0010.001 ITP Retaining Wall 04 Enabling works Rev 1 | itp | DN1210-SP2-010.001 ITP Retaining Wall 04 Enabling works
948dbe0b-dbbf-4f79-9475-6aa3ca2ef671 | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS - MATERIAL, PERSONELL & THIRD PARTY APPROVALS
3f8f3008-516d-44cd-b724-05fa98c17d12 | checkpoint | 1.1 - IFC Drawings and Specification
0a9bf23e-60bd-5cc8-896d-81e2bb46ea75 | note | Standard/Specification/Detail - Drawings to be issued by DNZ Temporary Works team - IFC stamped
bce98b6e-5a8c-5445-8bf6-e275e116cfdc | note | Acceptance / Conformance Criteria - A minimum of two weeks prior to construction: document review. DWG’s are for construction or as per instruction
9f819b66-cd2f-57ac-92df-cb309a561de9 | note | Test Frequency - Once
ec8dc528-80a0-5790-a6bd-2e13b0515ec8 | note | Verifying Document/QA Record - N/A
f8849103-413a-5eb1-8e33-98dfa3ae0bd4 | note | Verification Activity: Activity - HP
1c4c4caf-8d09-586a-acd6-af0abafa5143 | note | Verification Activity: By - SE
7a063b0d-10b1-41bf-97a6-f190ab17e4a9 | signoff | AUTHORITY HOLDPOINT
7bf262ce-68b5-4fbc-816b-b8270fd2ebb3 | checkpoint | 1.2 - Method Statement & JSEA Development
bb509f48-bc3f-5e82-b2f2-e27b53715ccd | note | Standard/Specification/Detail - The Downer Standards (TDS)
c46ee69b-6c78-530a-b697-c55d2ee61e39 | note | Acceptance / Conformance Criteria - Prior to construction: document review.
d2dd3fe4-42ad-5bf8-a7e0-8dde8e55dcb7 | note | Test Frequency - Once
52b75a63-56e3-53c8-91d9-7f670b50db1e | note | Verifying Document/QA Record - Method Statement & JSEA Completed & signed by site crew
8e81fea7-c6ed-5280-951c-9d83cdde079c | note | Verification Activity: Activity - HP
621e694e-7428-5c51-9d9a-54d0f1b7670d | note | Verification Activity: By - SE
ec960d71-15d5-4880-8771-179c05ab0427 | signoff | AUTHORITY HOLDPOINT
353af4b3-54fe-4a3d-a114-51d3e53ded8a | checkpoint | 1.3 - Slope Stability
cc566219-2074-598b-8b7a-da678a21164b | note | Standard/Specification/Detail - N/A
a05e3488-ae9d-5ac4-a1b9-1d2fbc4e3a17 | note | Acceptance / Conformance Criteria - Geotechnical check on slope stability for a 35t excavator tracking along sheet pile wall alignment.
b5142529-1ca9-592b-a5bd-9bcffe17027c | note | ○ Completed a minimum 2 weeks before commencement of works
b30ae43e-f4b1-5f31-94f4-e6329f04c6fe | note | Test Frequency - Once
094cd109-ec30-5085-b2e2-588036ec5ba7 | note | Verifying Document/QA Record - Temporary works signoff
7d6b2071-6283-5881-a4bf-59c805e8837a | note | Verification Activity: Activity - HP
af5fd706-5c8e-5328-88f6-8e3d2b89135c | note | Verification Activity: By - SE
85c1b81e-51c5-456c-ace9-737ceb39a70f | signoff | AUTHORITY HOLDPOINT
719df702-878d-4a7f-85b2-8d8f4e33332a | checkpoint | 1.4 - Permit to Dig
e605ad37-f283-5cf2-a220-ca3e793e641d | note | Standard/Specification/Detail - DN-ZH-ST043 Ground Disturbance SP03-ST-3150
cb2ab505-9729-55cc-9140-5744952a3414 | note | Acceptance / Conformance Criteria - Prior to construction, all services shall be located ahead of construction.
1be3af8f-b682-5336-973c-bffdf456e65e | note | ○ Permit in the work package.
4d385181-9cac-5c07-979a-ee897164aa9b | note | Test Frequency - Permit issued each week
5e00045a-f724-57ca-a464-b7517bbf18db | textbox | Verifying Document/QA Record - Permit number
812e8e33-953f-540b-925e-f9563da3d75f | note | Verification Activity: Activity - HP
a7930d4f-281e-5894-9929-ddf30b22e331 | note | Verification Activity: By - SE
ebee0e36-0c60-4365-8010-9446d7adc09a | signoff | AUTHORITY HOLDPOINT
638a6e9a-75c0-45ec-8f45-3a0fe183980d | checkpoint | 1.5 - Survey Model
e755fb18-8f9b-5cbb-a650-8c155785ee7b | note | Standard/Specification/Detail - N/A
5ef70c96-7adc-5a69-b7fe-c727b05c2b43 | note | Acceptance / Conformance Criteria - Model Review.
729e4be9-836f-5310-9d65-7b85319bf2b1 | note | Test Frequency - Once
7e75184b-3392-587e-934e-e004afdd9114 | note | Verifying Document/QA Record - Visual Inspection & measurement Survey Check set out as per design
fcf81cb1-9d56-5cbd-a69e-5562d76c0a45 | note | Verification Activity: Activity - HP
8bf7cda7-1c4c-5011-8631-98294c330e16 | note | Verification Activity: By - SE
46f9f8c8-e823-4319-8ee9-302325759b84 | signoff | AUTHORITY HOLDPOINT
a824dec3-aa48-40a6-b234-e0f8ce762f33 | checkpoint | 1.6 - Lift Plan
0a9a1471-2d26-51c8-baa2-a720abb2003c | note | Standard/Specification/Detail - DG-ZH-ST047 Cranes and Lifting Equipment Standard
33d8b9d0-6f2b-5ea0-a9f7-6e2273058dc3 | note | Acceptance / Conformance Criteria - Prior to construction. For lifting of sheet piles with Excavators.
18ac40f8-86af-5240-9fbb-52746fa3f4f9 | note | Test Frequency - Prior to Construction when required
9fb1084e-3e92-5aad-8816-cd66f4aef9c8 | textbox | Verifying Document/QA Record - Permit number
79966b86-23ac-55c5-8e78-120e29e6b7ce | note | Verification Activity: Activity - HP
baaa2abd-d1e0-5dd9-9e8b-9ec40643a345 | note | Verification Activity: By - SE
7a282575-a4cd-4977-8635-d0a6b64ee875 | signoff | AUTHORITY HOLDPOINT
a9682670-0562-453e-a1b0-1b00314bf9af | checkpoint | 1.7 - Hot Works
7089131c-8ad2-5a3d-ae78-3166d09e06dd | note | Standard/Specification/Detail - DG-ZH-ST041 Hot Work Standard
03cccc97-6469-5ba7-b8b6-419872fb6851 | note | Acceptance / Conformance Criteria - Prior to construction,for welding, gas cutting, grinding etc a Hot work permit shall be in place ahead of construction.
0650c868-bc89-581d-ad4e-8f6a66e67d9f | note | ○ Permit in the work package..
9f3e9201-100b-5aca-8268-a3f0c865cdc3 | note | Test Frequency - Prior to Construction when required
747318c5-eb7f-5728-b55a-231d503476fd | textbox | Verifying Document/QA Record - Permit number
a7dd9ede-7891-5bd9-8897-4497612b202c | note | Verification Activity: Activity - HP
de048365-2f20-520c-8239-7745d55e7cd7 | note | Verification Activity: By - SE
47590ca2-d766-4239-b80e-7008676a1551 | signoff | AUTHORITY HOLDPOINT
b9696645-1554-4072-8c3e-f2523c937b00 | checkpoint | 1.8 - Working at Heights
726b56df-4230-5095-bd00-8c00864954b3 | note | Standard/Specification/Detail - DG-ZH-ST042 Working at Heights Standard
f9af7f83-f483-59fc-831e-6455d8b85249 | note | Acceptance / Conformance Criteria - Prior to construction, permit in work package.
155685df-5585-57e7-8a3c-59c4b2eb3272 | note | Test Frequency - Prior to Construction when required
e0ca109a-251c-5480-8d48-a3801d6a0920 | textbox | Verifying Document/QA Record - Permit number
f9256be9-ff57-5615-a7bb-5c9881758bb3 | note | Verification Activity: Activity - HP
00adb36c-2fe4-5dfb-8b10-6cafe8d99109 | note | Verification Activity: By - SE
3a24d20d-52ea-483f-a011-faa9f70ba9c7 | signoff | AUTHORITY HOLDPOINT
7dadba04-d940-4d5b-b4da-8d7d6e64989d | checkpoint | 1.9 - Assess geotech reports and confirm driveability for sheet piling
252c813e-4b8c-5232-a516-167fa76f9c5c | note | Standard/Specification/Detail - WSP Geotech Report
c1ec6f5a-ade8-5431-9e5d-ba67e422a237 | note | Acceptance / Conformance Criteria - Prior to construction: document review.
e27ef86e-daa0-50b8-a244-51b4bf5b9c8b | note | Test Frequency - Prior to Construction when required
cf922852-3514-5734-aabb-01ada8add838 | note | Verifying Document/QA Record - Visual Inspection & discussion with operator on ground resistance profile
fff7a403-8563-5b43-bdfc-d5ae16241e41 | note | Verification Activity: Activity - HP
c6d04c2f-2da0-5904-9d6d-ba9fb02ffa6e | note | Verification Activity: By - SE
cc9e8f95-4a72-4b9b-8052-2cde3e54eaed | signoff | AUTHORITY HOLDPOINT
50dbae2c-bd77-4414-a083-4189befafee9 | checkpoint | 2 - Underground utilities
cbc02a71-c651-54fd-9cfb-6a7468a08ca5 | note | Standard/Specification/Detail - Diversion of underground utilities
1c91a503-3bf5-538f-b77b-147f53a6d8ec | note | Acceptance / Conformance Criteria - Confirm underground utilities have been diverted from the alighment of the sheet piles
68ec508d-8384-5022-a090-0e375c6a7581 | note | Test Frequency - Prior to installation
9846df8c-abd5-57eb-85b7-2c30f2edbd23 | note | Verifying Document/QA Record - Visual inspection of diverted known services
088da235-ba82-52ef-906c-64142f8fdc4a | note | Verification Activity: Activity - HP
7283e609-4d6d-55df-9050-519a86be30e7 | note | Verification Activity: By - SE
4d42c0d9-98af-41c6-a7ca-960e55baf171 | signoff | AUTHORITY HOLDPOINT
b638862c-ba0a-4842-8e06-90645e6ae818 | checkpoint | 2.1 - Sheet Piles
daaf76e2-d918-5cec-8abe-1450eb9b1d87 | note | Standard/Specification/Detail - NZGS Spec SPERW
b05ab69e-528b-5396-a59d-d8dcb1803fff | note | Acceptance / Conformance Criteria - Sheet Piles are in good condition, free from rust and debris.
3887891b-f01d-5282-a177-437904b60e76 | note | ○ Leading edges cut to assist driving
e74eb3fd-b2b2-5951-a09d-91ee3695940e | note | ○ 40mm lifting eyes cut in side wall of sheets, lengths as per IFC drawings
3f1dedec-7be1-5761-af0a-a4daed7e42e9 | note | Test Frequency - Prior to installation
cb46cd64-8bff-53f1-a47b-67f1b1d7f7a7 | note | Verifying Document/QA Record - Visual Inspection
270d2d88-e860-5401-9d49-ca66577606be | note | Verification Activity: Activity - I
aa0a5e07-de2f-5535-a89b-187cce5c4a43 | note | Verification Activity: By - SE
b5fac70f-1e22-426a-89db-81e80ed6b7fb | checkpoint | 2.2 - Driving Gates
7b0aaf0b-abaf-5629-93a0-28aa6a0cf0f4 | note | Standard/Specification/Detail - N/A
678b6b7e-ed5e-5cc5-b733-d2cdda4f326c | note | Acceptance / Conformance Criteria - Position gates to wall alignment
8d234a68-4b5b-5abd-9c35-13e88303d09b | note | Test Frequency - Prior to installation
fa1c7e45-fafc-5a43-a2a6-4e890ca45f6a | note | Verifying Document/QA Record - Visual Inspection
5d7f9b00-88ac-5241-ba7f-2ecf70f6b4b0 | note | Verification Activity: Activity - I
e76daaf7-1ac6-5211-8b26-48be7f808c6a | note | Verification Activity: By - SE
4b6a5074-23a1-456a-8469-77d43613114d | section | SECTION 2 – CONSTRUCTION ACTIVITIES
283a069b-f24a-40cc-b61d-1263acf9529f | checkpoint | 2.2 - Pile set out
37cb37fd-fba0-5579-8006-fe5e21264dce | note | Standard/Specification/Detail - DWG details to be provided
2d4bafd8-426d-5848-b6a0-7bdff9e1f56c | note | Acceptance / Conformance Criteria - Before commencing sheet piling operations, survey set out wall alignment based on model. Set out to include offset.
f9f765ad-3740-5b75-844f-4ae9152aca5e | note | Test Frequency - 10m chainage
f0c56c67-11e1-5242-9009-0be73f8952fe | note | Verifying Document/QA Record - As-Built
e8456a57-b213-5f93-9160-fb5f4a0a1855 | note | Verification Activity: Activity - HP
cdc2432b-f5e9-50db-9e28-1d943a020693 | note | Verification Activity: By - SE
e200ce67-83e1-43cc-ae1b-f8ca64393062 | signoff | AUTHORITY HOLDPOINT
bfcbfddd-2337-4c9b-9feb-c9edc749179b | checkpoint | 2.3 - Driving Gates
0704693f-ef02-5553-9e71-4879c2d66ddb | note | Standard/Specification/Detail - N/A
a4d9d544-4f65-5876-8b4f-22d84009fa15 | note | Acceptance / Conformance Criteria - Position gates to wall alignment
4879b365-c388-561a-a1fe-b6bcfdbaae0d | note | Test Frequency - 10m chainage
780d23c4-2cdb-5bbb-98f2-c666431167b5 | note | Verifying Document/QA Record - As-Built
1aa493e8-945a-5aa6-bfb0-ce5baccb93b6 | note | Verification Activity: Activity - I
18ca03e4-2bd5-5d18-bb46-5c48ba4a75d0 | note | Verification Activity: By - SE
5cf650ac-1eed-4062-9223-eba0781aa206 | checkpoint | 2.4 - Install sheet piles
fca54c8d-1cb5-5645-8556-98b9968385e7 | note | Standard/Specification/Detail - Proposed Access Ramp General Notes: 3235599-SP03-ST-3001-1RW4 Sheetpile Geometry - Elevation - DN1210-05-DRW-001 REV A.4
cc33cc85-1dbf-5ec7-a676-b95c158789de | note | ○ Proposed Access Ramp General Notes: 3235599-SP03-ST-3001-1RW4 Sheetpile Geometry - Elevation - DN1210-05-DRW-035 REV A.4
b26259fe-e017-5d09-817f-acf433574f32 | note | Acceptance / Conformance Criteria - Sheet piles driven to the required depths / embedment
6d6cf27a-82c5-52e7-9abe-6857f7a7e27a | note | Test Frequency - As required
936da4c6-7bd1-5527-bd57-e1aec4b56649 | note | Verifying Document/QA Record - Written record, sheet length and embedment depth
7e9bde7d-520f-59c5-bd05-6398dc661f27 | note | Verification Activity: Activity - I
a4ee4c44-1364-5b06-807f-5edae33b86c9 | note | Verification Activity: By - SE
2d672f2a-795a-46a9-9313-2797ffdda90b | section | SECTION 3 – AS-BUILTS/REDPEN MARKUP
ae94b6ad-674b-4009-bc13-da0bba5df247 | checkpoint | 3.1 - As-Builts
662a4484-e833-5c83-95fb-ee4d2c317237 | note | Standard/Specification/Detail - As-Built records and drawings shall accurately record the layout and extent of all the work and locations of sthe installed sheet piles
37b96d52-9fd6-59f2-b18d-476dd111162b | note | Acceptance / Conformance Criteria - As-Built records and drawings shall accurately record the layout and extent of all the work and locations of sthe installed sheet piles
3a5bb778-1920-57d6-9978-8b7e2dd8d60e | note | Test Frequency - PS 16.7.6
6df94e91-4fe7-5e91-979a-7979edc8935c | note | Verifying Document/QA Record - Survey Records/ Redpen markups
58a9e7a1-1c54-5889-b4ad-a213404d4223 | note | Verification Activity: Activity - HP
32620c35-70ae-509e-be7f-498ad91ca12f | note | Verification Activity: By - SV
8f4a91c2-8735-4011-abb2-30945d6ab897 | signoff | AUTHORITY HOLDPOINT
80f40747-fd28-42c9-93e3-536e8ce31eb8 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
186ec40b-5224-5a00-bfce-ca51a5c1178d | textbox | Contractor's Rep Name:
345b9f3c-7ef8-57e7-aa51-78af64f13f34 | textbox | Engineer's Rep. Name:
d53d34f6-d363-56d2-b4be-3af616375eea | date | Date:
a85783bb-8d02-47b9-aeba-735e08c186da | signoff | Add Signature
2aed0dfa-0317-444d-a3d7-7be818dfb17e | checklist | Ω (DEPRECATED) DN1210-SP2-0011-002 ITP Northern Access Road WW Rev 1 | itp | DN1210-SP2-011-002 ITP Northern Access Road WW
7150bf16-ebe0-41f0-be61-c7096fac6d65 | section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL , PERSONNEL & THIRD PARTY APPROVLS (P&G / ESTABLISHMENT)
8f9dd735-218b-46d5-a893-b1cf1bfe29c6 | checkpoint | 3.1.1 - Pipe Laying
5af889d7-a1c2-5077-bb97-3d690acaadc1 | note | Detail - Method statement
de1ad7f9-42fc-5228-b4ae-4a6928217973 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
ce619e7d-57f3-5470-a221-f30c17d2e197 | note | Standard / Specification - PS- 22.3 Appendix V
526ab13c-ec77-514d-a285-1c9e6cdba3e8 | note | Verifying Document - Wastewater Construction Work Pack Sign off
fb9f1d27-aad3-56ae-b040-b767dcb021bf | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
7e1c01b9-71ab-59d5-b808-6ca1374ed8f5 | note | Verification Activity: Activity - HP
22390c3f-9555-5beb-90f9-5503bdd645a5 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c31ec1d4-d1cd-5ee4-9e1b-72b51d264bf8 | note | Verification Activity: By - ENG
4c3ce1a6-61bb-4fbc-ba3c-ec6472800bb7 | signoff | AUTHORITY HOLDPOINT
d6b08391-ff88-4f80-a774-bc8aabd3a9bc | checkpoint | 3.1.2 - Pipeline Pressure Testing
08c48d06-2db3-5307-a50a-7a1dde994778 | note | Detail - Method statement
da0c002f-3e39-593d-b645-42f0e490e991 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
4b0417d0-ca08-5843-90b0-980c520d4014 | note | Standard / Specification - PS- 22.3 Appendix V
67f3e354-4539-5aff-8bd3-ddb32c817a02 | note | Verifying Document - Wastewater Pipeline Pressure Testing Work Pack Sign off
4c5745e3-3dd3-57ff-93c6-db5c3d26183f | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
f3cd29b0-95c1-59e4-9cd9-a43bb9ea950d | note | Verification Activity: Activity - HP
1fd90b91-3eb4-5d2a-ab3d-f5a193436686 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
cf09c9a6-13f7-577e-bd0a-c6f63246490b | note | Verification Activity: By - ENG
58e66b74-d0d9-4f09-a07c-5d8488231d86 | signoff | AUTHORITY HOLDPOINT
3d104f6e-28bd-4ad7-ba3f-80e6fd214b35 | checkpoint | 3.1.3 - Extent of Line Setout
d2dda2d7-1c7c-5894-8537-8eb0f1fff92f | note | Detail - Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings.
88335e6d-90b1-54b1-b7bd-b7ae00d1d3eb | note | ○ Identify any clashes before construction.
f726474c-a1ba-5d06-b26b-8cca4ff68081 | note | ○ LOT - markup
058a9b15-fbf6-5035-aed1-8fff809da5db | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
13bed892-01b0-5107-b5ec-94356ca012d9 | note | Standard / Specification - Design Drawings
4c7d2f9c-c08d-5c44-83ed-f27549252dcc | note | Verifying Document - ITP Sign Off / Mark-up
7dedf5b5-e45e-5d6d-8a6b-64a9994d90c4 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
53369a46-3d90-5946-8c2d-c205e2e29830 | note | Verification Activity: Activity - HP
952a9f17-2e66-544f-be55-f696b55f1450 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5d202b9f-f755-5628-b55b-e83f4083cfa7 | note | Verification Activity: By - ENG
9f5d7b07-a3b7-4d5c-920e-2e94845355aa | signoff | AUTHORITY HOLDPOINT
300a1f89-7361-4fd4-8048-aa601f1457d1 | checkpoint | 3.2.1 - Material grading: Materials (Gap65/AP65)
e3d7f0de-da93-59ac-a72f-dbebe670b26c | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
e1da3289-28d3-57ff-8540-c468026c0b7f | note | Acceptance / Conformance Criteria - No Particles >200mm
001110fd-0f37-534b-a821-c003023a16d3 | note | ○ Maximum fines 10% passing 75micron sieve
f7bd3d56-49b5-5891-aaa1-a3e9bde4d62b | note | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
3e2c7da2-a5ef-5e1f-b0f3-668cfabe4127 | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
0662f7d7-72fa-52c4-8762-e9fe5c61290a | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
0d057512-bac5-5e17-8b73-74046864f46d | note | ○ 0-400 - 2 tests
b3f0e20c-2ab5-5945-b237-a47ab2ced05c | note | ○ 400-1,500 - 3 tests
831bdfab-d52a-58de-956d-45d128214968 | note | ○ 1,500-4,000 - 4 tests
8ed6bb2b-350c-5123-83d3-3cae1b37b33f | note | ○ >4,000 - 1 test for each additional 1,000m3
62f4fe79-c8e4-5cb7-b076-001b496d1cd6 | note | — Results to Engineer 2 wks before importing
bb8b2b75-58bd-53b4-b1cb-92be57debb7b | note | Verification Activity: Activity - HP
4093301b-8362-5ae4-ba7c-e627500a1e15 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
77d6e926-09b6-5c9a-bb31-0276be9d5482 | note | Verification Activity: By - ENG
e50d760e-3c8d-46f0-b9e3-bdf46664c876 | signoff | AUTHORITY HOLDPOINT
5b64475f-d9eb-4db5-bb60-3b8b470b45f9 | checkpoint | 3.2.2 - Weathering index: Materials (Gap65/AP65)
1f8f9192-92e5-5c53-801d-c80b9b20b46e | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
efb7ba06-c7a1-53dc-a97f-90a633928da9 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
03273d0b-c551-5948-b371-c588cfe6fc08 | note | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
5ad9f21a-f2d6-549d-894d-c47fcfb9cfbc | note | Verifying Document - IANZ Accredited Report
589cc134-d21a-52c4-84a8-6da368e10ff5 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
c6cd9ea5-bcd5-5d6f-8e29-c8ad6655f1ff | note | ○ Results to Engineer 2 wks before importing
6a7bc3fe-23e0-52ec-99d7-ace6a977ceb9 | note | Verification Activity: Activity - HP
b16c4e25-4ba2-54a8-be6e-1aa88c78ddcd | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e1e71556-ce64-594a-beb9-9f86998b8f37 | note | Verification Activity: By - ENG
58712b44-db16-468c-90e2-e899e6c4869e | signoff | AUTHORITY HOLDPOINT
ed9d4939-83f8-4a99-9c3b-edbc0b3120fb | checkpoint | 3.2.3 - Crushing Resistance: Materials (Gap65/AP65)
77820080-8cca-5efb-94b3-98fb372639b5 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
35ec8b1d-eef4-5839-aea4-1ca9b28cbc5c | note | Acceptance / Conformance Criteria - >100KN
482871f9-1311-5a7f-8dce-67e2613dbe43 | note | Standard / Specification - Appendix XVIII, Appendix V
686705dd-6a92-536d-955d-eaaa453b476f | note | Verifying Document - IANZ Accredited Report
f2451790-e3af-5dd2-9794-2ae999a57195 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
cf782e7d-fdd9-5f43-8b5c-db5e3d49e176 | note | ○ Results to Engineer 2 wks before importing
9707dde0-2727-52c3-a09e-d6f73c39b8ee | note | Verification Activity: Activity - HP
b63f0948-e5ae-52a5-beea-4385ca3036c7 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
567238c3-4aa6-5fd1-b8a2-0d6f5cfcca15 | note | Verification Activity: By - ENG
1f13573b-7d6d-431b-95b3-0ec7a6e20e56 | signoff | AUTHORITY HOLDPOINT
6da5e4ab-bb9f-4c28-967e-287ab3dce718 | checkpoint | 3.2.4 - Maximum Dry Density and Optimum Water Content
c5b29d01-f995-5355-be44-2be967d5f47e | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
fb2e7b6c-2c77-54e9-9650-53ec647aa60e | note | Acceptance / Conformance Criteria - Report Value Only
fd531d9e-076a-5888-b560-46f19deae1b8 | note | Standard / Specification - Appendix XVIII, Appendix V
5d706bf4-186c-5406-99c5-67b841105466 | note | Verifying Document - IANZ Accredited Report
a2da786c-b0e2-5f51-a430-bb54b9cba970 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
93c224ca-90b6-50de-86e2-e265fee60b1c | note | ○ Results to Engineer 2 wks before importing
9b285a22-e5c5-5dd7-a5e6-d10f295fb982 | note | Verification Activity: Activity - HP
bd0080f6-2c05-5d84-8a61-8c7c40bee3c3 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
40d6ab80-840e-5335-bc3e-fdeec18284ea | note | Verification Activity: By - ENG
9d9c6bbb-3a91-4305-b39d-785fae360026 | signoff | AUTHORITY HOLDPOINT
8a979a4f-dea4-404e-af14-cee1f02a87c8 | checkpoint | 3.3.1 - Material grading: Materials (GAP20/AP20)
aeb808df-cfbe-5043-b713-e537ebcac54d | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone
560996c5-2860-5017-bd25-483012b871c3 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
3aa1471c-b031-5c89-8923-9ad0eee852f9 | note | 19.0mm ¦¦ 100% passing
f55689ea-1c2b-5b47-b9f2-e8b3cddfa9c6 | note | 13.2mm ¦¦ 80-95% passing
2ca5db01-48f3-5c67-a39f-e1067ad618fd | note | 9.5mm ¦¦ 64-76% passing
63391414-fae5-54ca-a8c3-beca9894220b | note | 4.75mm ¦¦ 37-58% passing
e80806ba-63fc-5690-9c67-fee63b21a308 | note | 2.36mm ¦¦ 30-40% passing
51060382-c2da-507f-a868-c316aa4587c9 | note | 1.18mm ¦¦ 18-28% passing
dab1eb45-2d66-5a0e-a7a7-f9952179135c | note | 0.600mm ¦¦ 12-22% passing
fd507e25-cbc2-5481-b427-9aec7fda615f | note | 0.300mm ¦¦ 6-14% passing
33978732-79ec-5378-a203-888e26472727 | note | 0.150mm ¦¦ 2-7% passing
447621e2-f6e2-511d-a08e-0ebb9f6511c0 | note | 0.075mm ¦¦ 0-3% passing
6f4f6c46-f261-57ca-a93a-9552d29ae764 | note | Standard / Specification - PS-22.4.5, PS-21.5.7, PS-21.7.2 Table 21.2
b4e7c912-2f42-538b-8230-9be193f22966 | note | Verifying Document - Lab Test Report NZS 4407.2015 Test 3.8.1
11f12125-0513-5a10-b609-3c6b4e65b2ed | note | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
dd0dd799-18ca-5a69-8b21-b5493eb5b338 | note | 400-1500m3 ¦¦ 3 Test
743fd880-6470-55dc-bfcc-c6c4d7266988 | note | 1500-4000m3 ¦¦ 4 Test
c48a9a57-ce7c-5aa1-894d-1d09af8cb49c | note | >4000 ¦¦ 1 Test Additional 1000m3
f9d3771a-dd81-52ac-b9df-574e7bc730f5 | note | Verification Activity: Activity - HP
7e27149a-3998-5b05-8300-1b622b3b4d56 | note | Verification Activity: By - ENG
4d42c975-368b-4759-9b50-e632ae810912 | signoff | AUTHORITY HOLDPOINT
19392546-383e-4e49-b4cb-2f2897a62f70 | checkpoint | 3.3.2 - Weathering index: Materials (AP20)
c936a28c-b92a-5f4d-a3a4-ec51f01fc7fb | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone
57db6a94-2728-503c-b990-a4812b47f013 | note | Acceptance / Conformance Criteria - AA to CA
c08ba18b-c51e-5f1c-9207-6e2c0fe143b4 | note | Standard / Specification - PS-21.5.7, PS-21.7.2 Table 21.3
48340521-4fd3-5196-a9b2-cf0fd618f1bd | note | Verifying Document - Lab Test Report NZS 4407.3.11
322fb831-85ff-549d-a642-1b15f46c6a83 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - 2 test per source
2c1e515d-ad4b-5274-9b1d-23b1ed7513b3 | note | Verification Activity: Activity - HP
372b85cf-d614-5d44-9c90-58159ac1deec | note | Verification Activity: By - ENG
5c9b3227-1dec-4ec4-89ca-fdf671500be9 | signoff | AUTHORITY HOLDPOINT
320f995c-cc0a-4ff9-aaae-81de2aad5e1e | checkpoint | 3.3.3 - Crushing Resistance: Materials (AP20)
84cd888e-f2f8-5b6b-b7a4-175ebbc8077e | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone
2acc42aa-6019-5ccd-9bd8-75a45a49adc7 | note | Acceptance / Conformance Criteria - >100kN
c747f4d7-e081-56fb-94c8-09a0c37b055e | note | Standard / Specification - PS-21.5.7, PS-21.7.2 Table 21.4
cf32f9d6-5815-5b40-85a3-1d3f23611947 | note | Verifying Document - Lab Test Report NZS 4407:1991 Test.3.10
0698957e-2dad-520a-ab87-2d2067f13e9b | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - 2 test per source
e159285d-116d-5e4c-b492-aaa2f3015535 | note | Verification Activity: Activity - HP
e2637162-7fa6-5750-a9bb-7130908d95f7 | note | Verification Activity: By - ENG
a795e95d-9073-4aa5-8c21-e3de3ec68910 | signoff | AUTHORITY HOLDPOINT
1ee757a4-ef1d-4633-b981-060269844cd9 | checkpoint | 3.4.1 - Particle Size Distribution
55f1b99f-f274-5380-957a-e71c2befce96 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
ef269ba4-91d5-57ec-aa10-5128d4420fa1 | note | Acceptance / Conformance Criteria - Report Value Only
a2ac0bd9-e756-5a68-8336-5a37085a8456 | note | Standard / Specification - PS 21.7.2, PS16.5.12, IFC Drawing WST-0320
e297b0ac-3959-5626-9df7-bc0168c0d950 | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
053f1217-5684-5ff8-b832-3b04de928f64 | note | Testing Quantity Required (based from schedule qtys) - 1 Test for each additional 1000m3
7bbee64b-a22f-570b-b496-5e00adbd5272 | note | Verification Activity: Activity - HP
30f1520a-f175-5107-980a-277c62b4a924 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
bad3ad27-c802-5ef5-855b-66ff73b72e6a | note | Verification Activity: By - ENG
0e873776-2d4d-4440-982d-ba82bea1517a | signoff | AUTHORITY HOLDPOINT
e8ea7e40-1e74-4318-abbf-fe3bb60cd6c6 | checkpoint | 3.4.2 - Maximum Dry Density and Optimum Water Content
383d295c-e834-5d70-a227-3f437b4668a8 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
3e945c3b-0854-5a69-a3c6-0ea53ac18e4a | note | Acceptance / Conformance Criteria - Report Value Only
b0938388-097c-569d-938a-4c18b125c5cd | note | Standard / Specification - PS 21.7.2, PS16.5.12, IFC Drawing WST-0321
c3661d78-4728-5c41-80b3-0745d8f10f67 | note | Verifying Document - Lab Test Report
712676c3-cfba-53bf-beab-fcdde1ed8cdd | note | Testing Quantity Required (based from schedule qtys) - 1 Test for each additional 1000m3
3afeb946-c897-5be2-b3dc-18ca1448dbee | note | Verification Activity: Activity - HP
7470e1b1-3a9e-56bc-9d71-d11bc76d175f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7e4e9908-2e6e-538c-9d25-edaa9126721b | note | Verification Activity: By - ENG
366461a6-e296-493f-a95f-af0fefe76ff1 | signoff | AUTHORITY HOLDPOINT
55374e12-1b77-4256-8fc5-28414bd2d72d | checkpoint | 3.5.1 - Pipes (PE/ PVC)
0a08cf91-c87f-5b36-92f1-6167a448bee8 | note | Detail - Manufacturer's record and location of extrusion plants.
19e9fb36-8eda-5f76-bc01-00a3b2a1235c | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
5f54b17c-780a-5bff-8597-4eb561f7d230 | note | ○ Full Traceability information and certification of analysis for the resin batch.
a55eed77-11c0-59ea-adc2-08bc2c0396ae | note | Acceptance / Conformance Criteria - Full Traceability information and certification of Material and resin.
25a72ed6-4de2-56a4-914d-af946e0fe134 | note | Standard / Specification - PS-22.4.1 (d)
1d3ece15-b98d-5b7b-a45d-9108085f95cc | note | Verifying Document - Full Traceability information and certification of Material and resin, Delivery Dockets
514f8cfc-605c-5092-b1d2-1cdea0aa1815 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
57ec42b4-9b74-57e4-8f0e-e2b41d841c6c | note | Verification Activity: Activity - HP
a8c8b7fa-558b-575f-bcaf-7de432c8c417 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e8e5f78b-7a74-5707-894a-fa22198f211a | note | Verification Activity: By - ENG
6d14cdcd-f331-4c06-9397-e0a5c7e5ba95 | signoff | AUTHORITY HOLDPOINT
a0b123d5-ff19-40ed-b840-fa0628d97a35 | checkpoint | 3.5.2 - Green Dome Odour Filter
daddccf4-c90f-5ebf-bd11-848709f05e7c | note | Detail - A Green Dome Odour Filter (Model GDOF36) complete with DN150 ducting.
2ebb774a-bc4c-5d4e-9e51-bef2ff064a77 | note | Acceptance / Conformance Criteria - IFC Drawing 0324-1
caf7645a-0638-5a57-ab56-60299c3b42bf | note | Standard / Specification - Model GDOF30
82c33052-8871-5ef1-9655-ce538a38fb1e | note | Verifying Document - Delivery Dockets
54d72347-80ef-5583-a394-a370350d0070 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
220e1c64-d98e-5174-a8f8-62ee8bd8a695 | note | Verification Activity: Activity - HP
322db013-5891-5004-a3e7-f8dd393351fd | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8396576b-3714-5235-ae8b-96a0056674cb | note | Verification Activity: By - ENG
9c47accb-cf27-4c81-b988-509c005d9a93 | signoff | AUTHORITY HOLDPOINT
9cc17863-096e-4f2b-a5f4-05e1e055ac41 | checkpoint | 3.5.3 - Valves, Adaptors, Flanges and Fittings
18a44f1c-97ff-5963-a23e-2f53358101e1 | note | Detail - Have a pressure rating no less than the designed pressure.
2372dc05-c35b-5d00-b5c0-cb5c5c37fb81 | note | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
41e5b97a-898d-5b6e-959a-bf0ff381d6a3 | note | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
e0ebbae6-c447-5d76-b371-8bef064466a9 | note | Acceptance / Conformance Criteria - Engineer approval, AS/NZS 4129
3db1997e-18e9-5658-a13d-02b8a9ad8cc3 | note | Standard / Specification - PS-22.4.2
eca0f2d6-4aa4-5f23-b325-9bb9cf569530 | note | Verifying Document - Delivery Dockets
4c1284cb-7bde-5bd9-8ecd-8b944a45889a | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
97029d4c-6d58-5301-bbd0-bb6449e04ff0 | note | Verification Activity: Activity - HP
e406c016-069a-5707-af58-1e58f0b9bdbe | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
944f733a-9616-5305-8ebc-83946c1ef176 | note | Verification Activity: By - ENG
350db4aa-03c5-4e29-bcc5-f564cd5163bf | signoff | AUTHORITY HOLDPOINT
c831eac3-6c3f-42dd-b2f6-f0d2579e3b42 | checkpoint | 3.6.1 - Pipe and fittings. (PE100- DN250 PN10 RM, DN300 PVC SN16)
6995ea16-8322-5409-a429-5628df314b9b | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
2cb75fe1-31ee-5de6-8d1a-92ce0071969d | note | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
2308d8b7-e73b-5feb-9ef1-49b47563b329 | note | Standard / Specification - Design Drawings
a6ce75ed-bfe3-5e47-ae05-85137929a1a0 | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
b296defb-02aa-5421-b89f-5f7103a0c64e | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
8d959cea-3068-5c91-9b0a-fe58fb6c619e | note | Verification Activity: Activity - HP
15ce2863-bf92-543e-9020-2c52af743393 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
67c1ad55-1cc9-582d-90fb-29dda0c046b4 | note | Verification Activity: By - ENG
6079bcb5-31cb-4e22-bcbe-4545530b3b09 | signoff | AUTHORITY HOLDPOINT
b6f50d32-708a-45a6-9583-8a85e7601464 | checkpoint | 3.6.2 - Valves, Adaptors, Flanges and Fittings
46d9a69a-96b5-5691-b0df-1c2d48f0790c | note | Detail - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
a0190226-ca63-5975-a68f-93e11c6d610b | note | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
e938e072-6d9b-5881-a6c2-6fb00c9e6570 | note | Standard / Specification - PS-22.4.2
1cdeee6b-6597-5b9a-8858-d0f58c64a744 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
c9d9a673-ade7-5e60-94db-b13085b0a308 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
f7b54ce0-dcc2-5211-860b-3b98301bd6f8 | note | Verification Activity: Activity - HP
fc106f48-be0e-5350-b382-268747246a6f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c5de1ebc-ee0d-5a64-b382-c0ab57017467 | note | Verification Activity: By - ENG
663eeebc-1265-475b-b7e7-03672b713ece | signoff | AUTHORITY HOLDPOINT
91b99453-59bb-4cab-92f8-70689ce8a912 | checkpoint | 3.6.3 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65)
4e49f30d-f25b-5cdf-a665-c0c18299a887 | note | Detail - Confirm Specification and material in good condition.
354b8046-6746-524b-80d3-47de2f0137a8 | note | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
730455da-c7f2-55dd-bc96-5364fbea6bf2 | note | Standard / Specification - PS-22.4.1
69bfd282-5e97-5056-82b1-ff1329c32ae4 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
9173c41f-8c95-510a-9ce5-79f116509087 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
026c743f-972c-5a7c-9f70-438a91b9cb24 | note | Verification Activity: Activity - HP
5b48a699-f9da-515d-8480-db93b8423f3e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6a11b7cf-a479-516e-b166-14a1a4fffcfe | note | Verification Activity: By - ENG
ea26603c-a4dd-4e3d-a9f5-99ad682ebb75 | signoff | AUTHORITY HOLDPOINT
525c5248-fb9e-47e9-bb49-959a22f060b8 | checkpoint | 3.6.4 - Bidim/Geogrid
a78109f4-d635-52a8-8fae-0c830966e0b9 | note | Detail - BIDIM A29, Durogrid 30/30 or similar.
9e09c002-b521-5f80-a0b3-c9cc5457051d | note | Acceptance / Conformance Criteria - Site Engineer Approval
4404ecea-92c6-5912-b108-57d72f124712 | note | Standard / Specification - PS-22.4.1
888a41d6-8acd-5bf6-8b9a-438fb379467f | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
8a472c50-8b93-5243-9480-85be0a011c8f | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
56d929d6-2aa8-5027-b974-5ec6fa0c8c69 | note | Verification Activity: Activity - HP
a090d1cd-8728-5619-a5ca-20dea4d68ce1 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
44973e41-0faf-5ddd-bae6-d72019c0dbc2 | note | Verification Activity: By - ENG
74c48c65-a046-4ad0-80ca-95331b3dcc50 | signoff | AUTHORITY HOLDPOINT
db33fa38-50e8-490b-aeab-2e0d32acc0b6 | checkpoint | 3.6.5 - Manhole WWMH 01
6c238812-bcdb-5010-b027-60cbbb740bf2 | note | Detail - Confirm the class and type as shown in the drawings, and fittings required for MH is same
5d964f17-e4df-53e9-ae6a-14d3a5b57b02 | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
94d5e0cd-6ee8-5a86-b9c9-80bbe1c300cc | note | Standard / Specification - Design Drawings
0d7cecd2-4ad9-5540-bcc2-29d256b08862 | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
1e050862-796e-56da-b7a6-bdca4b1fa943 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d94a8952-3408-562a-b61d-62d158bf1186 | note | Verification Activity: Activity - HP
5313634a-ad00-59bd-91a6-29c2a3f99fbb | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a4a9890c-c551-5a9b-b9ec-43e4ff7a4b33 | note | Verification Activity: By - ENG
7e8deccc-4364-4896-8e71-d352c23e153c | signoff | AUTHORITY HOLDPOINT
1a33e64c-72c7-4c2c-a942-ae5d254c5629 | checkpoint | 3.6.6 - Manhole WWMH 02
525c30ac-7842-500e-8603-1b3a7e2e8bdd | note | Detail - Confirm the class and type as shown in the drawings, and fittings required for MH is same
6acf6bba-b7c4-51bc-b5d0-4228e2d06334 | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
0da39875-c6e9-526c-b942-8fc2e80490f6 | note | Standard / Specification - Design Drawings
1324671f-1e2f-53d8-a361-ddb60d4c4b2d | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
ea899930-ceee-5d82-9cec-a87ca797703e | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
467094cf-5c47-59d4-90a5-43d3b280be0c | note | Verification Activity: Activity - HP
a1f6b5dc-cee1-56de-9ad0-8a21555952ba | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
346ed2b5-7cd2-54af-bcda-d4ff4e9d9d4b | note | Verification Activity: By - ENG
06adb6eb-40c3-44bd-9aa8-f4a2bfb431b7 | signoff | AUTHORITY HOLDPOINT
d3da51f9-3387-4d86-afa9-0ebec257dd52 | checkpoint | 3.6.7 - Manhole WWMH 03
c93036d6-10dd-598f-8647-42d5d7f66e5c | note | Detail - Confirm the class and type as shown in the drawings, and fittings required for MH is same
a03950bf-263c-5ca8-9624-fd3265e9100f | note | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
c1b7a0ea-e1fb-512d-b47a-ecf702f04b3a | note | Standard / Specification - Design Drawings
4611fd9e-a4b0-530c-89b2-f34919c193aa | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
6f6d34bf-a6d4-5d76-a816-85a5c32e3fcd | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
2dff5165-9b5b-599b-872e-4d5ad608e2ef | note | Verification Activity: Activity - HP
7811ef03-9000-5393-ab03-6d584c10b95e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f04da556-6c9c-58d8-893f-63279e377c78 | note | Verification Activity: By - ENG
136e769b-ee13-4a88-86c9-cacb17ef4f56 | signoff | AUTHORITY HOLDPOINT
9bc8354c-537e-45d3-a354-172229e93404 | section | SECTION 4 – CONSTRUCTION ACTIVITY
bbd862bd-f6f4-40f3-ba92-bb859385bfc5 | checkpoint | 4.1.1 - Foundation Compliance
0ef28f47-6ded-58a9-8786-57cc598a034e | note | Detail - On Granular or Cohesive Material
069bc6d2-7bc5-566d-9554-b94b8354aa8c | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
b1286d05-19f8-5e17-9ec6-eb285b5d0dc9 | note | (Or)
a090efcd-ccc2-510e-8fb4-e421e7e6d94e | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
13ee66bc-5542-5090-b795-cc8a0fa8eeda | note | Standard / Specification - Appendix V Table 21:11
f144ef58-19b3-50b7-a769-39eeb7d7541b | note | Verifying Document - Scala/Shear test result
43a970d8-8e5c-5bd9-b6b8-9a5a2876df9b | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
599e6969-ce57-5f11-84af-7a992b86bdf8 | note | Verification Activity: Activity - W
7f0ee014-919d-553e-ba24-1424eb3dda44 | note | Review of text reports/records or other evidence of compliance
98fef9d1-2ac7-52f6-9382-d2a473b0a780 | note | Verification Activity: By - SE
3cf6b41a-14e6-488b-bb14-e67421e5c9c6 | checkpoint | 4.1.2 - Undercut approval
0619ba75-6be6-5116-9f59-2344f6621db5 | note | Detail - Trench Foundation
e5d22ec0-b74b-5b40-9a8c-739b18bbaf26 | note | Acceptance / Conformance Criteria - 300mm Max cut
8b727667-b695-5abd-9502-4392427f8bf3 | note | ○ IFC Drawing Sheet 320
24c69562-d1e9-5145-8f46-27992afdf6f4 | note | (Or)
c04f9c84-043f-5d10-8839-9db93024df77 | note | ○ Engineers approval
edc221d7-46cc-5c56-b5ff-5089a4dffb6b | note | Standard / Specification - IFC Drawing WST 0320. AS/NZS 2566.2/2002
cb5d3bae-2ed6-5c4f-9e5c-b9bf1abe26b4 | note | Verifying Document - Lab Test Report / Wastewater line record
59471c22-94a1-5955-b586-4f5ed94d7af6 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
b0de72c7-2cb4-5144-a647-c10eba87c34d | note | Verification Activity: Activity - H
86a81fae-105e-5c9a-9991-36e6aad69811 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e1642d21-244a-5cd4-b88f-6d8c72be427b | note | Verification Activity: By - SE
fc204548-3e26-4977-9cd7-769a20a53a8c | checkpoint | 4.1.3 - Undercut Backfill Compliance (PAP5)
16b846b8-0162-53e3-90de-3c5d1de4647a | note | Detail - On Granular Material / On each layer as per specification / on the trench foundation.
77f57f17-a269-5a2b-a47a-127b573e6b5b | note | Acceptance / Conformance Criteria - Visiual Inspection
5439a77d-f0b8-5de4-a6d8-b9a466e248ea | note | Standard / Specification - IFC Drawing WST 0320
00b45317-9c98-51dc-be78-ec9bc9adfe4c | note | Verifying Document - Lab Test Report / Wastewater line record
03cbdf0d-4514-5d9d-8fd1-eaa3dfa740c7 | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
daf00c35-b9b0-584d-9662-8d8a8de5835e | note | Verification Activity: Activity - H
98dbd770-d3b5-5d0a-aaa1-84c59ef9e77b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
84b1dbbb-7a28-55fd-ba9c-c114bb8f379a | note | Verification Activity: By - SE
45be29f2-8a27-441c-8169-324db3f873d7 | checkpoint | 4.1.4 - Bedding Zone Compaction Testing
5337087b-0b36-5a60-82ec-dc71f380a8d7 | note | Detail - On Granular Material / On each layer as per specification (Imported Sand or GAP20)
03755e9c-ffcb-5ae0-a4a9-a584c1e2b8ba | note | Acceptance / Conformance Criteria - Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench.
bb72073f-283f-54ea-8639-8983992a1ca1 | note | ○ Minimum Compaction- 85%MDD
65abc27f-d981-547d-b459-83ebc963e597 | note | OR
f78937ed-a1f1-54e0-9c88-5d2aed74d961 | note | ○ 12% CIV
5ed75f6f-d62f-53a8-b9ac-df0f6d24769a | note | Standard / Specification - IFC Drawing 0320-1, AS/NZS 2566.2/2002
209665b0-0196-5208-9494-2c01a83d605d | note | Verifying Document - Lab Test Report
87548edc-a05a-57a4-a7e8-9eeec589a21b | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification.
bc53fa88-8bdd-5791-998d-abe807cb3597 | note | ○ One test per 10m evenly spaced intervals.
74eb54c7-6014-5279-aec8-c619db82059a | note | Verification Activity: Activity - H
507dc35d-e143-5518-8a67-6e21812a55b5 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a3c81ce4-64d6-5176-8b1a-9568d5b7015c | note | Verification Activity: By - SE
c9eda5b3-fde9-49dd-a9e6-302d280b7d46 | checkpoint | 4.1.5 - Laying of Pipes
a9069dce-e99f-5a93-b3fb-5de592834d79 | note | Detail - Lay in straight lines, beginning at the lower end of the line.
8b0711a8-1e82-5220-9cdb-f56d7597da80 | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
9450752b-fb24-5e7a-82e1-4ab67ea0cdf9 | note | Acceptance / Conformance Criteria - As Per Drawings, Facing upwards
889c542b-3a84-5fec-85ae-1fe3659d7cde | note | Standard / Specification - PS22.7.1 C
d150cdaa-995b-5cc7-99a3-b63f4ad5517e | note | Verifying Document - Visual Inspection / Wastewater line record
890c0549-4305-568f-a281-6292ad2c9237 | note | Testing Quantity Required (based from schedule qtys) - Every Line
f447e4a8-eebc-5ea8-bae4-221543b2c73d | note | Verification Activity: Activity - H
5f4cf889-d163-5150-b644-bb3e64ec0987 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
fe71eae2-6f08-5639-a2f3-48d9425ac579 | note | Verification Activity: By - SE
14e6eb93-e1bd-4a8f-948c-e6082419ed3c | checkpoint | 4.1.6 - Pipe Installation on Curved Alignments
189b271c-bfe9-5cfc-98b3-482855c518f1 | note | Detail - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
ca9fe41c-c5ee-58ef-b7da-87dc2baf4118 | note | Acceptance / Conformance Criteria - AS Per POP 202
64195c3e-6d2b-582b-ab31-b6a8677eefa1 | note | Standard / Specification - PS 22.7.1 D
cb24f712-701e-52a9-86b2-81f343a8bca4 | note | Verifying Document - Visual Inspection / Wastewater line record
cf8456f5-c8a0-53c0-950c-d991d4ca1760 | note | Testing Quantity Required (based from schedule qtys) - Every Line
67eb5dac-be71-5e82-b478-9755dfaf71c0 | note | Verification Activity: Activity - M
51d43ac0-82f7-516a-8ea9-e17d89843ea9 | note | Monitor on Random Basis
30208d5d-f6dc-5f61-b470-452655b0f42c | note | Verification Activity: By - SE
645e8238-a0d9-4906-8486-bbea02059775 | checkpoint | 4.2.1 - Flanges
dfc62811-1521-5cec-aa95-a39f212f59a3 | note | Detail - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
ece8c7c4-b2fd-5254-a519-8f78bdb7defb | note | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
0954290f-b616-5d9a-94e4-6a3450b06c73 | note | Standard / Specification - PS 22.7.5
7f9c01b0-f597-59d8-8b24-8cf089d70c0a | note | Verifying Document - Visual Inspection
9dcf4b03-28af-5b08-b366-1f918ccb8963 | note | Testing Quantity Required (based from schedule qtys) - First flanged joint
3f32953f-246a-5e8e-b93d-f6a7eabc41dc | note | Verification Activity: Activity - HP
0510e4f1-4920-514c-ab38-09eaa9496cac | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c2e08c07-c421-53eb-882c-4b400e9a3122 | note | Verification Activity: By - ENG
726be62b-f3d8-494b-bd15-a9ab5435d3ac | signoff | AUTHORITY HOLDPOINT
9629f571-727d-4ff7-9415-4dc4f326f8c4 | checkpoint | 4.2.2 - Bends
dddd5b06-1d1f-5dd4-ab21-182a5e987bda | note | Detail - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
b37170a3-dcde-5a5e-a039-677fae9696d8 | note | ○ Fitting must meets the same PN rating as the adjacent PE 100.
9f366528-9213-5886-a01b-fa42476b3caf | note | ○ Fittings must be suitable for producing the joints shown on the Drawings.
b486a3f0-2983-54da-aae0-1aa61340ee90 | note | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
4d2f1e56-ea90-529b-bdcf-c8ff6ac2dc86 | note | Standard / Specification - PS 22.4.2
92af560f-e06c-5679-a495-adec4194785e | note | Verifying Document - Visual Inspection
b9ebe231-a65c-5c12-9bf4-f38282bd1874 | note | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
6e1cc68b-e533-5f62-b305-c2b545c6b692 | note | Verification Activity: Activity - H
be8ee5ec-56ed-5bf2-9287-34aae36826f6 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
86cbd32d-edb8-5831-9ee5-1b90b3472a53 | note | Verification Activity: By - SE
a7e7abe0-cb03-4b0c-91c5-4927fb13219d | checkpoint | 4.3.1 - Butt-Fusion pre construction weld test
6cb0c543-9c39-56fa-a2d3-78b0ccacea9f | note | Detail - One weld on the most common size of pipes used for the project.
9a07cef6-f272-5d72-8ac2-f1422d760ed0 | note | ○ One weld on the thickest wall (highest PN) pipe
7c305deb-1116-5280-91c1-d2f2bf0f9fcf | note | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode, WMS Report
e5dbc0a9-1f7f-5b05-a26d-44dbd4c46291 | note | Standard / Specification - PS 22.9.6 (a)
ec8c4e72-d262-5c1a-a7f5-62ac6ae554a1 | note | Verifying Document - Visual Inspection
d1c9b87e-1468-5c25-b201-ec82e021f82a | note | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
d5ffff05-95c0-5464-8d67-a2e1dd246aa5 | note | Verification Activity: Activity - HP
831eff2a-dd47-5939-81c3-8b6330ee25f6 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a8e15394-152c-5cca-8b61-5af874fc1997 | note | Verification Activity: By - ENG
9815b126-dc05-45a1-9417-c8095550eec2 | signoff | AUTHORITY HOLDPOINT
07c1d5e5-ca53-4a8e-bf0a-849ac6304f6b | checkpoint | 4.3.2 - Butt-Fusion Welding
c85d3e2d-8102-559e-afd2-9d055d8cad21 | note | Detail - Use only semi-automatic or automatic welding machines.
030a3a3a-0ebb-5714-8515-5eb9ea87454a | note | ○ Maintain a site record for all butt-fusion welds.
03048752-d466-51d6-8da7-5056b778c974 | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
63350778-9e75-54f8-9e95-c70f181cfc09 | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP), WMS Report
0ad257ec-faee-5f91-a420-ac108a8ace90 | note | Standard / Specification - Appendix 22. PS 22.9.4 C
eb82f74f-952b-5e64-8fed-cacf490d79e4 | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist, WMS Report
ec5ec1bc-5b9a-5d72-a930-ce45b3ec680b | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
aa6d881b-e0e5-5291-9514-672aba43e4d1 | note | Verification Activity: Activity - HP
bdbbee35-dfd1-5dd2-abde-1caef2a8b377 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0bdbd3d1-370e-5787-a69d-a8d4b3ca0b2c | note | Verification Activity: By - ENG
dad54491-4cc5-4c9b-afa1-cbab000a1131 | signoff | AUTHORITY HOLDPOINT
74d196d9-0d00-4b65-9afe-a4fa85942d82 | checkpoint | 4.3.3 - Butt-Fusion Construction weld test
36ad04c4-849f-5710-8f3e-400b5d3d9daf | note | Detail - Test at least two welds from the first 50 welds.
0ecdeafb-569a-5cf2-b22d-cdc627372002 | note | ○ One of the welds to be selected by the Engineer for satisfactory result.
08bac351-6a77-5154-9fb2-6fd26c7c0ba3 | note | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
4aba504a-c943-5120-8412-3b013bfe42d3 | note | Standard / Specification - PS- 22.9.6 (a) (iv)
d4f15978-7b66-5139-b863-b3a40cf5c85c | note | Verifying Document - Test report
541cbe77-a72f-5fc7-aa2c-9c6f2d0283fd | note | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
02c888cb-431f-552e-89e8-0005cb7a9aaf | note | Verification Activity: Activity - HP
6bb2d425-d9f3-50a9-b662-9c0e920be829 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4213728a-c870-5ef6-b8e5-a8a6a5f8b895 | note | Verification Activity: By - ENG
daf399b0-1756-439e-93eb-137a9356ee8e | signoff | AUTHORITY HOLDPOINT
42bcaaed-b247-48bc-8138-f51adca3a629 | checkpoint | 4.3.4 - Survey
ba6f6b1f-9b9a-598f-bd3e-4cb5f85bb417 | note | Detail - Inspection of Pipeline Inverts
621b7521-5c87-5b41-b310-25c087821e06 | note | Acceptance / Conformance Criteria - Vertical design Setout:
949a72ae-1675-52ef-9c2e-ca0906db5c32 | note | — Pipes ≤ 1% grade: +/- 10mm variance
f0ddb397-7942-5fb4-a620-a9341602f20c | note | — Pipes > 1% grade: +/- 20mm variance
748a9b3a-0bf7-5507-9b56-82c16889cf34 | note | ○ Horizontal design Setout:
9ff23ebf-aee1-5b57-8593-09ce4a6f06b5 | note | — +/-30mm variance
3e4420f1-b1b2-5b94-9b7a-83ab5df7448a | note | Standard / Specification - PS- 21.7.6 Table 21.15
90ab9a9c-6248-54c6-94de-4ce111d483e4 | note | Verifying Document - Survey Data / As-built record
5ee31629-64eb-5c58-86c4-e0cce4dab450 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
edd9a12f-486a-5560-b51b-6fa02c144af5 | note | Verification Activity: Activity - H
7d1c5849-ba6f-51b6-8f9a-95910c2ec87d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
416322b7-f384-5737-90ec-610fba988e1e | note | Verification Activity: By - SE
7d19b88d-bc16-48f5-9b29-c240a1193aaf | checkpoint | 4.4.1 - Electrofusion (EF) pre construction weld test
9be829d4-2bbc-5374-b8eb-81c29f8b576c | note | Detail - Use the designated welding equipment and the approved WMS.
521f26db-c7fb-5e6e-bb0d-4803db5d79bc | note | ○ On the largest size of PE pipe used in this Contract
fd611304-2987-5b0e-8c17-c834277c6521 | note | Acceptance / Conformance Criteria - ISO 21751 (strip-Bend test) or ISO 13954 (Peel-decohesion test), WMS Report
ca8a06a0-55b3-5ff5-800e-a8f2eab61130 | note | Standard / Specification - PS 22.9.6 (b)
f451cb37-5b81-5bf3-9f75-2afe8da176bd | note | Verifying Document - Visual Inspection
1daf66e4-0cdb-5210-a2f8-79cf44c8748f | note | Testing Quantity Required (based from schedule qtys) - One test welds per operative(Welder)
e0d82315-4a01-5d03-bfc0-c7bc0d7e4651 | note | Verification Activity: Activity - HP
4bc16773-ca90-5419-a82d-ebfec361d67c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
28baed59-650a-5654-8b3c-3fa269a96663 | note | Verification Activity: By - ENG
9b97fd33-7d32-4631-a4b5-b38cfeeab671 | signoff | AUTHORITY HOLDPOINT
c6728d3c-f343-4446-92c4-b1f6abfe2ed2 | checkpoint | 4.4.2 - Electrofusion (EF) Welding
beff309d-dbf0-5c9e-b4a6-02736a54b9a3 | note | Detail - Required if Butt fusion welding cannot be perform.
40c1bd22-94e5-51e1-b7e7-ef36928fcc85 | note | ○ EF Jointing in accordance with PIPA POP 001.
28008dfa-ac9a-5412-824b-5cef3b43ce0c | note | ○ The lead welder or welding supervisor must verify on the site record form.
e28ecfff-dc1c-5ca3-bfe6-ca0f20852988 | note | Acceptance / Conformance Criteria - WMS Report, Checklist (refer to CWP).
36e0919f-5f6d-52f8-b8c7-44e69e517304 | note | Standard / Specification - PS 22.9.5 Appendix 22
31263690-0dc0-576f-8e30-cd1a38508bad | note | Verifying Document - Visual Inspection / Electrofusion (EF) welding record checklist, WMS Report
c121815b-3103-59ad-81d6-6e6c90ae9150 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
5f420bcd-c9de-5f67-8bef-d1725589f9b9 | note | Verification Activity: Activity - H
1eb8d2ee-9d03-544e-8fba-918745ee39b2 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5c119be7-b62e-524d-8981-d41c164d41ab | note | Verification Activity: By - SE
0db6c956-c9d1-4821-a171-dfa1357fe2ec | checkpoint | 4.4.3 - Electrofusion (EF) construction weld test
05d40db0-bb4f-5298-84f1-741ec3b353f6 | note | Detail - EF weld quality to be maintained.
8c3350a5-293d-570b-ae5d-f7e2e2fc2969 | note | Acceptance / Conformance Criteria - EF coupler and EF saddle testing
f94779b7-2937-5f92-90be-b642179bf7cb | note | Standard / Specification - PS- 22.9.6 (b) (iv)
5b791374-d113-5254-865d-f8aa9ca297f3 | note | Verifying Document - Test report
99118322-8293-5fee-9252-b8842048d041 | note | Testing Quantity Required (based from schedule qtys) - 1 in 10 test
e0f04f0a-ef96-5450-8152-4b36b0ad59cc | note | Verification Activity: Activity - HP
8eac8ab8-86a0-5445-bba1-40686bdedd7c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8d7938cd-ed7f-57d5-a189-a64276a3ecdf | note | Verification Activity: By - ENG
c33e5a5d-1664-4adc-8d4c-f17cb887ff57 | signoff | AUTHORITY HOLDPOINT
3062b65e-dac1-4aa0-9317-0a82fd7e8a71 | checkpoint | 4.4.4 - Survey
abd87c4c-c4c1-5a6f-987e-282f90b38121 | note | Detail - Inspection of Pipeline Inverts
a360a6eb-aa01-56d8-acb7-0a2763c936ad | note | Acceptance / Conformance Criteria - Vertical design Setout:
fe7bf984-2e20-5125-817b-76d97b64cb89 | note | — Pipes ≤ 1% grade: +/- 10mm variance
dc193e4b-3583-5f21-bce4-14ceb9dde922 | note | — Pipes > 1% grade: +/- 20mm variance
b28b20e0-84de-5d5b-b7da-46c19792bbdc | note | ○ Horizontal design Setout:
08ef1fc0-e06f-535a-9107-fdae758c7fae | note | — +/-30mm variance
aa1f7afc-f4e5-5b34-a70f-4e9c21adc4e1 | note | Standard / Specification - PS- 21.7.6 Table 21.15
3126b8d9-41bf-51ef-a5ca-c4c76d3828bb | note | Verifying Document - Survey Data / As-built record
a63a5057-4e30-51f5-9da6-989935f6ded5 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
f46bf93c-c5a7-5735-ad50-a5710f58916c | note | Verification Activity: Activity - H
d3abdca8-05c6-538e-bbcf-622726d7ac6f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4075d428-b677-5bd0-aee2-d9047899dd3a | note | Verification Activity: By - SE
53eda6b7-261b-4d7e-9e69-e7aa43037a05 | checkpoint | 4.5.1 - Emebment Zone - (Side Haunch Overlay)
c728d2d8-cee5-5362-a413-a09cf1f142b6 | note | Detail - Granular Sand backfill Compacted in 200mm Layers.
a4322bde-ada3-515b-86e3-44f1dc37a703 | note | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays.
958b80b3-9279-5981-bbf0-fc39912f737c | note | ○ NDM BS to be Carried Out
3a025aee-a51d-5cc1-8c10-861d47753cac | note | Acceptance / Conformance Criteria - in 200mm layers.
be96f679-1661-5320-a97c-a3503ea16a18 | note | ○ More than 85% of MDD.
8bcec44c-9caf-5b9f-881d-9a8ded42aefc | note | OR
f4ebb6c8-8d18-50ca-af52-f14e40343f95 | note | ○ 12% CIV
8481a2e9-27c1-5ddf-9a1d-24b91d9b9edc | note | Standard / Specification - IFC Drawing 0320-1
7a52a811-ecbf-52d0-98fe-336e657937ab | note | Verifying Document - Lab Report / Wastewater line record
a65d9c2e-9574-57c2-8533-b3ae586a41f2 | note | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals. 200mm lift
a300bc3c-0a96-5d1b-99b6-82a30bf2738c | note | Verification Activity: Activity - H
a22a6ef7-6e3e-5e27-9798-8ca32618c9d4 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1b7b41c2-2681-50ae-9132-164fa4eabd8d | note | Verification Activity: By - SE
588609ff-82d9-4aa2-a2e6-05a38d6839e1 | checkpoint | 4.5.2 - Pipe Markers
ece606ad-7c12-56a0-8826-c7a4427388d1 | note | Detail - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
c7631c1e-a51c-5805-a5d8-2dfa0099a004 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
5a84dce2-9960-51e6-b921-484da73bed77 | note | Acceptance / Conformance Criteria - AS Per Drawings.
1aaecf52-9a54-5209-a969-c1d1653c34de | note | Standard / Specification - PS 22.7.3 a
565f177c-7c0b-5e6c-9efe-1375aff0cafe | note | Verifying Document - Visual Inspection / Wastewater line record
817ef3b5-f072-55aa-b3b5-cc81268bbbc0 | note | Testing Quantity Required (based from schedule qtys) - Every Line
350205e9-e124-559e-a4cd-e62608f06bb7 | note | Verification Activity: Activity - H
2e9e0435-abff-5680-a653-29ad1d27a799 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a40eea72-0950-5580-b416-b72ab5ca5dee | note | Verification Activity: By - SE
73cb9d1f-756c-42de-b44b-bee070fc3e51 | checkpoint | 4.5.3 - Backfill Compaction Testing
18647010-e2d3-5de4-bcb6-5e2b9c70b443 | note | Detail - GAP65/AP65 Backfill Compacted in 200mm Layers.
32a8bd72-4348-57c1-bb46-ea96352fc538 | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
ee249497-4ab7-5b62-b992-90041451ad71 | note | Acceptance / Conformance Criteria - GAP65/AP65 Backfill Compacted in 200mm layers.
cae26816-e01a-5b6d-9f09-9deb9233c095 | note | ○ Testing to be completed on maximum 200mm lifts of backfill.
3e6ce016-1660-570c-a1f3-6fefe961a014 | note | ○ 95% NDM on Shared and Carriageway.
232a8a6a-92ad-5a4c-b84c-92f700aa657c | note | OR
48fe8f93-3fd3-551a-8e2d-868684ddb1ac | note | ○ 28% CIV
0a6e7f33-f84d-51fe-a490-c86dbba34439 | note | Standard / Specification - PS- 22.13.5, NDM Standerd 25832 NZS 4402 Test 4.1.3, IFC Drawing 0320-1
a28a6b70-2a4a-54a3-9fb0-941601b3f8aa | note | Verifying Document - Lab Report / Wastewater line record
7780d977-aee0-5a46-b53e-a666dff553d4 | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 10m evenly spaced intervals.
44543915-e326-5372-8b0c-f488b12a9205 | note | Verification Activity: Activity - H
20ef93ce-bfed-5dbf-b4c8-c93cf7e5680e | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ff5ed0f2-ca5f-5ecc-84d7-452c12238437 | note | Verification Activity: By - SE
b056a7b2-a39a-458b-a71a-2b31f8e13f96 | checkpoint | 4.6.1 - Pipe Inspection
4daaeb3f-cc46-595c-abcb-b5a068cd8c89 | note | Detail - Inspection of Drainage line
d29afb06-ede5-59dc-a49e-8ed2def31d29 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
3db623fb-7fdc-5c66-8405-e45542355fbb | note | Standard / Specification - Internal
3df33a84-f141-5560-a873-00b510234ea0 | note | Verifying Document - Wastewater line record
6c451521-0553-57ee-9c55-4266f486f78c | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
11721787-adee-5ebd-83fa-f76285e17fc8 | note | Verification Activity: Activity - I
e1a3faf0-c539-571c-9e38-d628e85845c1 | note | Formal inspection activity to be undertaken and recorded.
482aa422-e380-5139-9a5f-f4c0b40a4208 | note | Verification Activity: By - SE
c102a678-5676-46c8-ba11-b1eefbdd4a7d | checkpoint | 4.7.1 - Pressure Acceptance Testing
6183ee52-370e-5cc7-9dc8-668d6cb822bd | note | Detail - Backfill/cover with embedment before testing
9b598e10-1a20-5f68-990f-ece36bc4af1a | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
3bcd23fb-2809-57b6-9a17-7ae4e2f4ca79 | note | Acceptance / Conformance Criteria - Wastewater Rising Main Pipelines – 800kPa
7e4af3ef-c690-540e-9b45-b808b82bdb6c | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
fbbcb32e-c0e8-5248-b5dd-bc3232397fe7 | note | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
2c7a39b0-65c7-54d1-b174-a228cdaab32c | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
dba33869-db50-5e09-ada8-7bfc9c40bbb6 | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
4c16ff39-b86c-51a0-b809-5e09b1f42673 | note | Verification Activity: Activity - HP
98c2f385-3ffc-5a2f-95aa-ed5a0017632c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
37e5d4b3-961b-5be4-9a35-3a79b71bd4f3 | note | Verification Activity: By - ENG
7a10f3e0-cd9a-4128-aaa3-7c2bfa1286dd | signoff | AUTHORITY HOLDPOINT
18871f3d-a86f-4254-a5d9-050d7ab59335 | checkpoint | 4.8.1 - Foundation Compliance
dc9aefa9-1eb8-5e29-9341-8c5ab30061dd | note | Detail - On Granular or Cohesive Material
a134f4a4-0e33-5b71-a516-4b5acfb0836b | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
7cc38307-44ec-51f4-b6ee-73fd830d09a5 | note | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
1cf15b41-3899-5c2c-979e-8f02e947ebc3 | note | Standard / Specification - Appendix V Table 21:11
a500e111-c4ee-57db-97a1-c369822f96df | note | Verifying Document - Shear vane or Scala test result
68270394-462d-5faf-ad3e-42e7940fed1b | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
8a945828-71b7-52b8-a05b-20339be56ee9 | note | Verification Activity: Activity - W
b3e7c1c8-f85d-56f2-a4fd-168294cbd2fa | note | Verification Activity: By - SE
156b36f3-ad17-4052-8b6e-99e51b957674 | checkpoint | 4.8.2 - Undercut approval
f5e5870e-79cc-58bd-a289-3b9925c51f5b | note | Detail - On Subgrade
91eff6c1-de9f-52ff-ae8e-03f1673685e9 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
7e0bafc1-dad1-51a6-bfe2-143ec3515769 | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
62789d44-88d6-5f5c-99eb-90a2787dd74f | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
2982344f-27bb-55cd-9410-3d9b153b7b1a | note | Standard / Specification - Table 21.5
9bdc52e4-af14-536c-b315-5f3356129961 | note | Verifying Document - Lab Test Report
a650d3ba-6618-512f-8420-742e9ae3d272 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
626739b5-2197-5ade-8104-f5c333064b01 | note | Verification Activity: Activity - HP
de7659c8-1dd0-533d-8dcf-200b24518ddb | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
576ac35c-29c1-5a09-952b-c2c47836ea8c | note | Verification Activity: By - ENG
03630248-dc5f-4443-85f5-cf894214096b | signoff | AUTHORITY HOLDPOINT
8d19f917-bc15-43f5-ac2a-f13e8aa2c948 | checkpoint | 4.8.3 - Undercut Backfill Compliance AP65
fc556f61-66c9-5d50-a156-e9c966a05d77 | note | Detail - On Granular Material
20dcac8b-225f-5966-93c2-f82c46437a14 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
8056dcde-e6a7-5dbb-b7ad-5feee038916f | note | OR
f8ea05d8-eccf-50dd-8545-0443c36a8c65 | note | ○ Clegg 25% CIV
f12ca0c8-94e4-5c42-8116-c097728bcafb | note | Standard / Specification - PS- 16.5.12
4d2b2170-e47a-5f42-a8d4-47a9ab56d82c | note | Verifying Document - Lab Test Report
08242902-6b24-52c3-ad81-ad4d16981157 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
7f0788ab-e300-5458-a240-5031b157cfab | note | Verification Activity: Activity - H
b6223878-563b-56d5-a807-2787a716cfdb | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f4011cc6-9170-54f8-8e1f-bded2b7b9ffc | note | Verification Activity: By - SE
65c07cc0-1063-4dac-83be-0ccd94c64b52 | checkpoint | 4.8.4 - Bedding Compaction Testing AP65
4f38b4c4-531e-5d9c-81ff-3ca05745600f | note | Detail - On Granular Material
e85a60c7-9d2b-5998-8c73-8a047eddc2d0 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
c06592f4-8829-557a-aeea-4648f894c5d2 | note | OR
d6309dbb-362e-5ad4-a4be-d2d6766dbdbe | note | ○ Clegg 25% CIV
4b757957-eee9-5ddf-be65-6d2a3cee3ded | note | Standard / Specification - PS- 16.5.12, PS- 21.6.11
f0f2b799-6cab-574e-9825-7a3296b81fd9 | note | Verifying Document - Lab Test Report
a15afe5b-b5dd-583f-8cb6-10ce2f79b882 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
cadc09da-4978-5732-aab5-d9b9ba3ff0c1 | note | Verification Activity: Activity - H
88473642-6627-57d2-96bf-b5939f7a4621 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
60d979e5-b209-5c79-b610-a657e8707e6a | note | Verification Activity: By - SE
db92887b-d3a5-4213-b5f3-fe5a6b870f63 | checkpoint | 4.8.5 - Survey
5069fd7c-bcc2-5d86-b38d-1034a4eab832 | note | Detail - Inspection of Structure
9734ca2c-97d5-5b7b-a24c-3d4ed8e8abc8 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
80e75c5d-6b36-54cf-bd9c-abdc873beb89 | note | Standard / Specification - PS- 21.7.6
38114e1d-36dd-5463-9926-71edc229abdf | note | Verifying Document - Survey Data
8b3b7d32-0db7-514c-8301-3a04157875bc | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
927123b7-c717-5e75-aaa2-bdd8221ae11c | note | Verification Activity: Activity - H
39d438e2-e898-52cc-889a-1752e518531f | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
aeba93cd-d011-5bae-a103-e0c0d9387234 | note | Verification Activity: By - SV
9fb17e29-871d-45ef-9424-aa2839800df2 | checkpoint | 4.8.6 - Sidefill Compaction Testing
51e0afab-4e1d-5bbc-8434-938ac9433c4a | note | Detail - From the bedding layer to the overlay layer of pipe.
02428bf9-3903-5a57-955e-f5a687a56a5f | note | Acceptance / Conformance Criteria - AP20/GAP20
64477c3e-e81d-5c1e-8062-d2fc124ab0c1 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
ccd7d191-4b5b-5cfb-84f5-1bd6254a03ab | note | OR
0ea019d4-e76b-55c2-aed8-fc4abb3b1818 | note | ○ GAP20-Clegg12% CIV
459d854b-4c38-516f-bbd1-b8247f9bb5d3 | note | Standard / Specification - PS- Table 21.12
ad9d7251-1e0a-5587-ace7-da530d3ca7f4 | note | Verifying Document - Lab Test Report
0ea0d7a1-949f-52c6-a17a-db11878b943c | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
c3e338ba-8870-5629-8fcb-42caead43506 | note | Verification Activity: Activity - H
13689995-735c-5079-8dbd-732bf806412d | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4daa0a6c-02bc-539f-aeb1-f6b79c8a83f3 | note | Verification Activity: By - SE
b510b435-f60b-4107-98fe-f501eaa25f23 | checkpoint | 4.8.7 - Backfill Compaction Testing
a1a2921c-cdcb-5336-aa6f-7622172878d1 | note | Detail - From Overlay layer to the subgrade layer
fdc849b0-dff5-53c5-87fc-4c7223ecec90 | note | Acceptance / Conformance Criteria - AP65
5f3eaf52-93ef-5cff-b788-f23e66f0b8f5 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
e08f2078-5c6c-589b-a4c9-ca2454e61139 | note | ○ AP65-Clegg28%CIV
d96e1baf-19ef-5c2d-acd3-25837b1f44d4 | note | Standard / Specification - PS- 16.5.12
9ccc9ca0-52f8-5e36-a282-fa0dd71ef832 | note | Verifying Document - Lab Test Report
fccd4771-356d-5573-b5db-05e6e0a4c105 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
69af996a-3703-58f7-8b3e-8509497bfc3b | note | Verification Activity: Activity - H
7d32e757-afbd-5660-b230-aad422ffe1d2 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f4d79319-3b6f-5391-acd2-3e6f6499686b | note | Verification Activity: By - SE
6672cd6d-33cb-4229-b543-f8129415c1d5 | checkpoint | 4.8.8 - MH joints inspection
7e2547ac-0854-54ce-b22b-b83b85a658fa | note | Detail - Inspection of joints
c102217a-0d67-5736-b0b2-0ba72b325378 | note | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
3002e7eb-fe45-585a-9186-57d32da21df9 | note | Standard / Specification - PS 22.7.10
1e9c0c98-43e9-5c19-b81c-d5626713b439 | note | Verifying Document - Visual inspection
eed89abd-d284-5325-aa0f-7cf77a4afdf7 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
d1d29faf-c4c3-586f-a6a2-8bb488b3f8a0 | note | Verification Activity: Activity - HP
47aeabc1-8c1e-531c-bb86-cc01df64f8f1 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
eded15e2-fd30-521b-a8da-8a365dbe3356 | note | Verification Activity: By - ENG
87d7c251-5816-4dab-adac-5dace36f477b | signoff | AUTHORITY HOLDPOINT
a5dadab6-325d-4b39-be80-be9e732f89a6 | checkpoint | 4.8.9 - Inspection
55e58d77-e5a6-5beb-9089-30c92fd3d9e8 | note | Detail - Inspection of Structure
778fb0c0-a2a0-5e46-9390-e1715a0e554f | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
0fb8d969-0135-56a2-b206-389a7a5884b8 | note | Standard / Specification - PS- 21.6.11
281ac817-1b73-5fb8-8214-fe25d6b0a2a4 | note | Verifying Document - Manhole/Catchpit Record
3514efe0-2652-547a-9dc1-7e316e7e83d6 | note | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
bb25d5ff-1c16-58b1-8fd8-8730fce5186c | note | Verification Activity: Activity - I
044989f5-a97e-5901-adef-50ae75717175 | note | Verification Activity: By - SE
e1bf7b83-b0cf-485e-9567-428950ab178e | checkpoint | 4.8.10 - Plumb
fc66554f-1642-5d7a-8d11-580ef0ad96cf | note | Detail - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
a38cb9cd-3ead-55ff-99c1-ca919ca8ce50 | note | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
c416f675-e681-5265-b4c5-37abc77b1d19 | note | Standard / Specification - PS-22.7.10
49c7a5dc-abe3-5621-aed5-ed4eb2747233 | note | Verifying Document - Survey Data
5628ffc6-d45e-541a-954e-435963e6ce2b | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
0ed951ec-7a51-5994-8e63-2b1064fc3592 | note | Verification Activity: Activity - H
ada977bc-8cf2-57e8-b570-f0a198d498aa | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
dae8d4ac-2a6e-5593-bfd3-d2815a89a651 | note | Verification Activity: By - SV
19d728e4-9f40-488d-96a3-75a07d4ceda3 | checkpoint | 4.8.11 - Step Rungs
3ec9fe03-0716-5bcc-8e05-a3ef26a0d0fa | note | Detail - Step rungs evenly spaced at nominal 300mm vertical intervals
c2a647dd-0c8e-5f32-b91b-e55485078985 | note | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
517ca68b-5183-5339-a8bf-f7575af6c3b1 | note | Standard / Specification - PS-22.7.11
fd107d03-1d4a-599f-9578-eee4aaa483b4 | note | Verifying Document - Visual inspection
85f1128b-592b-5b15-9b62-562f3423ec46 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
ee0d5be2-a518-5930-9a7b-77ad8dd4799a | note | Verification Activity: Activity - H
d379cfaa-ee66-5011-ad56-2789aebb2f6b | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
486acb19-3a85-512f-93be-88dff7dc76d2 | note | Verification Activity: By - SE
ff79ce08-9224-453c-99ab-a7899302a0b8 | checkpoint | 4.8.12 - Manhole frame and covers
b403af37-34c5-5027-825b-7fb0e96bcae1 | note | Detail - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
9ad0a3f0-6ab2-503d-89bf-258fb2138e55 | note | Acceptance / Conformance Criteria - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
c619b603-8204-5950-adbc-5b28700fb6d8 | note | Standard / Specification - PS-22.7.12
070a18bb-02f7-598a-84a8-f30299887e8b | note | Verifying Document - Visual inspection
22ac60f3-4322-5757-bf2e-9b8c62e2761d | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
9d78da68-dcbb-5276-be92-70f8e978cb9e | note | Verification Activity: Activity - H
d58af695-581d-550f-9626-75f7c0a5b30a | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e7930c54-2fba-5265-81cb-241d0ed2dbaa | note | Verification Activity: By - SE
20c00b90-15dc-41cb-8376-43513d044345 | checkpoint | 4.8.13 - Manhole lateral connection
2d0249ff-bf92-5703-a77d-b224f4e9681a | note | Detail - DN150 PVCu connection for future lateral.
201336b5-987f-5567-b0d7-8c2025126d40 | note | ○ 800mm above manhole outlet invert
d2e8d470-c65e-57e7-9438-abef3812f552 | note | ○ DN150PVCu end cap
9bf818aa-4512-5765-8422-f0a062defc6d | note | Acceptance / Conformance Criteria - DN150 PVCu connection for future lateral.
7483f1be-890c-5ff4-b1be-7e90595fdad7 | note | ○ 800mm above manhole outlet invert
79a3d96c-3fc9-58be-8749-e2db41ba37d8 | note | ○ DN150PVCu end cap
07a02c47-20e4-5b41-b8ae-1df24bd973fb | note | Standard / Specification - IFC Drawing 0320-Rev 03
91721558-4968-506c-a1bc-0682c48b6894 | note | Verifying Document - Visual inspection
bf8712cb-d7b6-5ffd-bada-e0c6b9320f86 | note | Testing Quantity Required (based from schedule qtys) - Per connection
fe5b7519-8488-5105-a49f-8011b0e2addb | note | Verification Activity: Activity - H
219fb0b6-839d-5d81-a93a-3ccb20817b11 | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
86c328b8-768c-5654-b63d-47e799cbc6d5 | note | Verification Activity: By - SE
646bde79-b546-4051-98da-cca5c5db5945 | section | SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
5c1ad72f-b7bc-482b-86dd-cbd0a7d21336 | checkpoint | 5.1 - Survey As-Builts
a0925c66-ea95-5aee-b16a-cf861ed0dea7 | note | Detail - Quality Check on Nee pipeline and structure based on the tolerances in RITS
2f78870b-2a88-5413-b384-94b3d3761d82 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
c913c823-d4ef-513f-a898-7c6819ebc144 | note | Standard / Specification - Project Specifications
f9106083-75bb-5530-883e-10adadd41423 | note | Verifying Document - Red pen markup only
a81746db-be10-598e-872a-d4577bac3609 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
e258dec3-f7c6-5819-9506-077b78dd3f33 | note | Verification Activity: Activity - H
71b5d5b6-9d3b-524c-95ae-40531c3e9c7c | note | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
7648297d-ed3a-565c-9b83-77180bf61137 | note | Verification Activity: By - SE
03c49c92-5450-4726-9491-1330ab69aa25 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
e4a12413-6e35-5eb6-a3bb-10682154a57f | textbox | Contractor's Rep Name:
162b90b8-4336-52a6-af19-aa804c44a216 | textbox | Engineer's Rep. Name:
a1a2b569-1e92-576b-894d-12df60e2e493 | date | Date:
a3384633-35da-4cc9-9a61-a3d8ad5f1c66 | signoff | Add Signature