## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
32a7b644-6617-4047-af3a-f82f0994c8b1 | checklist | CL031A - Pre-Pour Checklist Rev A |  | CL031A - Pre-Pour Checklist - Location:
476e545d-5a01-4d0b-a7c9-e21db544452f | section | 1 - Preliminary Checks
4c394843-c544-4df5-ad15-059ecc9bf5aa | checkpoint | 1.1 - Confirm current drawings being used (Drawings to be listed)
3a928982-6eda-459e-80e0-abee0df624eb | checkpoint | 1.2 - Surveyor set out slab/concrete area and locations of cast in items etc. Pre-pour survey conformance completed and provided to Fulton Hogan.
03a52bd2-89fc-4dae-b11c-6fd276231048 | checkpoint | 1.3 - Existing slab faces checked:
4860f883-88ae-5e03-8203-a92d31b812fd | note | — Must be cleaned of any loose material
b6696cd9-f0a0-50f1-b6ab-f2cb9e9638fd | note | — If required, patched & smooth
003fc971-63e0-4c94-a215-eb3958a000cc | section | 2 - Check formwork secured & constructed correctly
90cfe3ba-f322-4acc-baec-92e8e2fcee1d | checkpoint | 2.1 - Check no debris/rubbish in formwork. All cleaned.
c05b4e8f-5349-4f70-882b-fcc12d72737d | checkpoint | 2.2 - No movement in forms. Top end of form does not vary 3mm in 3m.
6f53f656-34d2-412b-b822-ce2e7df5bdde | section | 3 - Check reinforcement placed as shown on the drawings
f80e5052-430e-45cb-89e1-6a79cb8cd3e8 | checkpoint | 3.1 - Check bar spacing
d2958c14-1445-4105-9391-66ac99f5d781 | checkpoint | 3.2 - Check cover – Refer to Drawing Spec
d1e5866a-1211-4d98-80ae-65e7c44b72d3 | checkpoint | 3.3 - Check no debris/dirt on reinforcement or in pour area. All cleaned.
1a7a43a7-306a-44b1-bd32-4db1aa474ab0 | checkpoint | 3.4 - Lap lengths as per specifications.
1d7a86d2-01de-488b-b996-87a6b33117cc | checkpoint | 3.5 - Check Block Outs are installed (if required)
eb9e2e9f-8324-4178-b731-042dbb3d93b2 | section | 4 - Cast in items
c9707bc0-511a-4519-8a61-d74c755b4439 | checkpoint | 4.1 - Dowels installed as per drawings.
59e94f51-c060-480f-b2f1-64b33ab212f6 | checkpoint | 4.2 - Conduits and other cast in items in place
d397485a-1b57-4464-adcc-d7d1236f68e8 | checkpoint | 4.3 - Confirm starter bars are in correct locations (if required)
939c8257-51d2-48ee-a580-ae69840b1ed7 | section | 5 - Joints (if applicable)
036665ca-9f4b-4751-abae-2d9cfbc4474b | checkpoint | 5.1 - Expansion joints in correct position, 20mm compressible material in place
d5fdfc59-12bc-493d-973c-f93d35060c11 | checkpoint | 5.2 - Dowel Cradles set out and secured.
0221fa6f-c8e8-475c-97ae-7e38c19838fc | section | 6 - Check Pour Area
f7c568fb-8d5e-4c43-a343-bfeceeca88b6 | checkpoint | 6.1 - Check base of bond breaking layer is not damaged, any areas missing to be rectified. Check area is clean from debris.
5da69942-0f6c-4876-bdf3-84cea56cf4d3 | checkpoint | 6.2 - Ensure broom condition is sufficient for use i.e. bristles are free from deleterious material and not clumped together.
e7f7d905-6b43-4f2b-85a7-4273be7d8ce6 | section | Checklist completed
9a658f11-a040-4b31-886b-b4324d7897dc | checkpoint | Checklist completed:
56800c6c-8e00-5a02-989a-0adc34fcf854 | date | Date:
648ac47d-ef6b-43b4-bc0c-2054e31b4ca1 | signoff | Signed:
c144afde-555c-5528-9daf-3e37c758849c | checklist | FH-ZU2-QU-ITP001 - Demolition of Existing Pavements - Rev 0 | itp | ITP001 - Demolition of Existing Pavements
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
de6ba418-2f03-5955-aff5-5e2c470d39b5 | note | Frequency - Prior to works
bb451165-5268-54e3-b4b3-8cbe6e9d37fa | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
6ed2bb77-45d4-5333-a0a1-cce4e1527cc8 | note | ○ Using the correct and complete set of drawings.
cff6e110-a38b-51b6-a6e5-0e28d19fe499 | note | ○ All drawings are the latest revision
33fc753a-477a-5f83-a6b1-be5cbddefd25 | note | Reference Documents - Aconex
869252e6-5f03-5a03-a27c-06d6aa13de5b | note | Inspection/Test Method - Visual inspection
e10801c6-67d0-59d2-a960-52a5b2a6237d | note | Record of conformity - This ITP signed
98e00363-1acd-579f-aa9e-b465cfc1d60d | note | IP
2e60b1e9-7e3d-5aca-850f-c29ad54093ee | note | Responsibility - Project/Site Engineer
a181c36b-ae14-5c86-a20a-ba915d3c521c | date | Date Completed:
652fe225-451a-5ff1-9c3e-5cb20fa77399 | checkpoint | 1.2 - Demolition Work Plan
bb0d47e1-b70f-5be4-86bc-6d0d37693a4d | note | Frequency - 2-weeks prior to start of works
e1c9a3bf-226c-5123-9338-2edf778f750e | note | Acceptance Criteria - Prepared and submit Demolition Work Plan in accordance with AS 2601 to Contract Administrator two weeks prior to start of works.
c758a3bb-d8ed-5e95-a947-289dfedf1fac | note | Reference Documents - Spec cl. 8.4 AS2601 WMS-001
4ca45db9-8b0c-593f-854a-70f9c91cca6c | note | Inspection/Test Method - Verify
c8cd80e1-5dc0-5e39-a4bd-8395ab627af1 | note | Record of conformity - This ITP signed
e2077523-4d37-50e2-a1f7-236a89c4a6fb | note | HP
7d84c665-a967-530f-8433-c484bfb0d278 | note | Responsibility - Project/Site Engineer, Principal’s Representative
5db4d83c-29fd-5cdf-960c-ed9c12482e50 | date | Date Completed:
43ecc5c0-58a0-53a5-aafc-38fb21ddebd8 | signoff | AUTHORITY HOLDPOINT
af19260b-7d35-5f5b-8ddb-fb72e51d7659 | checkpoint | 1.3 - Dilapidation Report
7bd5b0c6-ba17-5187-adc3-e6a326a32eb2 | note | Frequency - Prior to works
35695348-166d-5426-94a1-37f22be6a12e | note | Acceptance Criteria - A dilapidation report is to be completed and submitted prior to works on site. Dilapidation report to include photos and recordings of the condition of the pavement prior to demolition works.
218d6988-09da-5982-a2e4-909d172da817 | note | Reference Documents - Dilapidation Report
0b41a501-7016-5af3-988e-a6311d817726 | note | Inspection/Test Method - Visual inspection & Verify
405be92c-0e43-50e6-8944-d5e211f5759f | note | Record of conformity - Aconex & This ITP signed
74a7bfa7-7423-5826-abb8-adebfeae7f9a | note | HP*
023533ff-1616-5d33-a2b8-30bef7b7486b | note | Responsibility - Project/Site Engineer
c2e3814f-1ccd-534b-a013-4d4f743f21dd | date | Date Completed:
56a333f6-6275-5ad8-a545-852b0bef9497 | checkpoint | 1.4 - Existing Service Identification & Protection
45f1702d-5b43-575b-9667-75048355810b | note | Frequency - Prior to works
4522f48d-9bdf-5866-8d04-f661277673a2 | note | Acceptance Criteria - Existing services information gathered from APAM prior to works. Area to be demolished has current BYD plans, service scanned, and existing services has been proved. Services have been identified and protected prior to demolition.
58dd54e3-03e1-5fb7-849e-d8f22fa07fbe | note | Reference Documents - Spec cl. 8.5.1 Drawings, BYDA, Survey Maps
97297616-c88e-5eb6-99ed-b539126ae022 | note | Inspection/Test Method - Verify
e5c985f5-f458-58aa-a10f-f5e7346a67d4 | note | Record of conformity - This ITP signed
f276c259-8c21-5cca-a78f-49100e7c9402 | note | IP
5907faef-fe05-5530-81d6-24ed30a1b715 | note | Responsibility - Surveyor, Project/Site Engineer
4f9c2daa-fa7b-5ede-9e45-eefa43fd675d | date | Date Completed:
3d5540f9-8951-5202-993d-61e164319ff8 | checkpoint | 1.5 - Execution of Demolition works
b9f49108-0177-5ea0-a0db-0e2301b5389a | note | Frequency - 2-weeks prior to start of works
e6729bde-b9d0-5217-9282-8cc785387ff1 | note | Acceptance Criteria - If working within the existing vicinity of AGL services, Fulton Hogan to give APAM a two-week written notice to work in the vicinity of existing AGL cables and transformers, to provide notice for APAM to assist in isolating services.
8c4ca2a2-bc2a-51a5-89eb-197856cb2a8e | note | Reference Documents - Spec cl. 8.5.1
2705b2d5-423f-5299-9b17-ff18479d6236 | note | Inspection/Test Method - Verify
f6a5a2d9-aa00-55c5-af5b-02517ffb42e5 | note | Record of conformity - This ITP signed
9b05a6b9-21b7-5a6d-94f2-aac152dfdcfe | note | IP
6769e4c8-2210-5634-bd56-691fabf8e714 | note | Responsibility - Project/Site Engineer
2ec735ad-f8dd-51ad-a7d0-bdab91a4efac | date | Date Completed:
d5e7c061-a358-5f3c-acdf-8cdcdba2ba43 | checkpoint | 1.6 - Implementation of all measures and controls
0288d473-5da7-580d-bb77-dd34ac13a7f6 | note | Frequency - Prior to works
5b133118-4d35-573b-806b-23778d780fd9 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, ECP, TMP, SWMS and WP. Existing areas that are not part of the demolition will be delineated with bollards or similar to ensure that it is not disturbed during demolition.
34224c36-7f04-5aef-8886-f22b446426a1 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
f22f7a72-5027-5553-b48d-c50f459710fb | note | Inspection/Test Method - Visual Inspection
00819a04-f5a1-5f8f-a38e-4a4f6fa7092b | note | Record of conformity - This ITP signed
a3cd1da0-3c74-5829-81b8-79d9cb39a0f3 | note | IP
b88747a5-0950-5069-8d91-33c9885de087 | note | Responsibility - Project/Site Engineer
05a68ad6-76b3-58df-93c1-dd9252a94a11 | date | Date Completed:
b92327ca-5de2-55c0-95cf-bd10482bf603 | checkpoint | 1.7 - Testing of Demolition Materials
d7fd890f-720a-5d4d-9d5e-fff65772b3c3 | note | Frequency - Prior to works
eb55cd7b-dcfa-5434-8639-c55e87603b0a | note | Acceptance Criteria - Ensure PFAS testing has been completed. The results of the testing will be used to determine the appropriate disposal or re-use of the demolished materials. Offsite disposal of material has been approved by APAM and comply with regulatory requirements.
e07c9c66-19b8-53e8-ae70-ef8968bfec0a | note | Reference Documents - Spec cl. 8.5.5
50f7461a-2b7e-5d7d-9c84-ffedd2400d90 | note | Inspection/Test Method - Verify
8bdecf34-d91f-5805-b803-d4e50f3f66b2 | note | Record of conformity - This ITP signed
de5775e5-cd56-550e-8333-79a2f2215f3f | note | HP*
c9bfbcd4-75a8-59e6-8fe8-974782b93305 | note | Responsibility - Project/Site Engineer
9f4b5e74-2c21-5070-a5c6-40e28d21b6bd | date | Date Completed:
661b1258-317b-55df-91af-3bd2da089919 | checkpoint | 1.8 - Excavation Permits
be982e0d-451d-5990-b371-14bd6a185547 | note | Frequency - Prior to works
31b23bba-6ec6-56fd-a149-0b62d29a0b33 | note | Acceptance Criteria - Prior to works, check that excavation permit has been gathered from APAM prior to any demolition works. Internal Fulton Hogan permit has been issues to excavation works and plant operators.
b7c27170-a1ca-5d0d-b0b8-cb64a43d841e | note | Reference Documents - APAM Excavation permit, FH Permit, Go- Cards
10f5a5af-1690-5b5a-9bda-dee7d4bdb2d8 | note | Inspection/Test Method - Verify
1b9c1d85-945d-5cd5-87df-b56aa0eeb97e | note | Record of conformity - Excavation Permit
2e86c833-d897-5663-8392-742befa2a4f6 | note | HP*
08f2e4dd-49c9-5a1d-b705-b46fe3ed0ad2 | note | Responsibility - Project/Site Engineer
f80a5894-3af3-507f-a3c4-605e3111fde8 | date | Date Completed:
a5e70c95-ebf5-5449-920c-b3ca49bac0f8 | section | 2.0 - Demolition of Existing Pavement Works
53302c01-4ad4-5657-937a-dc89dcc79ddc | checkpoint | 2.1 - Definition of a works area (survey)
aae52969-45d2-503e-adc2-d30ba1dd9d2d | note | Frequency - Each Lot
b4adfc7f-599d-5b8d-8cd3-e661d18ab14f | note | Acceptance Criteria - Work area has been cleaned and surveyed (marked on site). Limits of demolition are clearly marked.
ef12fdfe-1564-5ea2-b5f6-2d7d56fe5e0c | note | Reference Documents - Drawings
e867c56c-9d76-5a56-bb23-b85897312423 | note | Inspection/Test Method - Verify
17d31cd7-172a-5a27-b550-5cef99ad77ce | note | Record of conformity - This ITP signed
4d590bf8-5081-5894-a2b4-5b161ed967fb | note | IP
53d97e94-87e1-5ed2-b6ab-66f519b380ae | note | Responsibility - Project/Site Engineer, Surveyor
9dfd43f7-e8ef-503e-bd0b-4685d0cc6190 | date | Date Completed:
51012452-a66f-5350-9652-8079c72d73f7 | checkpoint | 2.2 - Temporary Supports
284bf415-c66d-52fc-87f8-f1d3317cd3e5 | note | Frequency - Each Lot
c5a0bfd9-acef-5e79-9960-d1bba05f5585 | note | Acceptance Criteria - Check demolition will not affect any structural or service supports, if so, temporary supports will be provided until it is no longer required.
25fd1501-6624-532a-8618-4460e259eb3a | note | Reference Documents - Spec cl. 8.5.3
4527299f-b244-5799-ba2a-31ec22a6e6f8 | note | Inspection/Test Method - Verify
bff6d09d-e026-51bf-8796-48ecd81b755d | note | Record of conformity - This ITP signed
26408a23-98a8-529a-8c69-e60a9c256fc1 | note | IP
9cb94ee1-978c-577c-a441-c9a96ac698b7 | note | Responsibility - Project/Site Engineer, Superintendent, Foreman
c6fd8ad7-c9a7-519e-bb7f-7215c1ca0594 | date | Date Completed:
cb2d8e84-991f-5559-a72a-59370f524404 | checkpoint | 2.3 - Disposal of Material
edeeb9de-8f1d-5408-948d-f170556aefb9 | note | Frequency - Each Lot
62348367-a089-5ff2-965a-d5b97f1490d5 | note | Acceptance Criteria - Demolished clean concrete material will be taken to Vic Civils at Gate 8, for concrete recycling. Contaminated or PFAS material are to be taken to Gate 11 to be stockpiled into their dedicated category and contaminant. Any discovered contaminated material found on site, that are not already known, will be notified to the client immediately.
d51bfb7b-fb2b-5e85-bb31-102f96a844ab | note | Reference Documents - Spec cl. 8.5.5
628bdfa2-776a-56b3-ad7f-2c6f15db31a7 | note | Inspection/Test Method - Verify
34eb3d96-c6e2-5c48-a27e-e66ecd8623f7 | note | Record of conformity - This ITP signed
eab19740-24a5-5057-b0a7-4656c968481d | note | IP
6ef59242-739d-584c-9780-6332e3011149 | note | Responsibility - Project/Site Engineer, Foreman
4d348c96-f5be-5a9b-a86f-4c97db7f50b6 | date | Date Completed:
7c53d2ae-eb69-5762-99e4-f9eb16eb80bc | checkpoint | 2.4 - Asbestos Materials
4973ee8e-e824-5621-8769-1660434f041c | note | Frequency - Each Lot
50401d4f-5850-55fc-867d-33e4e17c44a6 | note | Acceptance Criteria - If asbestos material is identified, works are to be stopped until test is conducted to verify the asbestos. If asbestos is confirmed, licensed subcontractors are to remove and dispose the asbestos out of site.
c8338bbf-c5cd-5c6d-8560-17ec9a11dcf2 | note | Reference Documents - Spec cl. 8.5.6
63eac01c-1285-511f-9009-807a05066da4 | note | Inspection/Test Method - Verify
deb03700-7275-57e9-8b52-ec1baaf14c47 | note | Record of conformity - This ITP signed
1919a9ee-a3fc-5a1d-a43f-206f21f2ed84 | note | HP*
2660f46f-ffde-5d8d-ba2b-1fe0c70f3c7f | note | Responsibility - Project/Site Engineer, Foreman
f9a21230-85e8-5c8a-8766-654ec65b288f | date | Date Completed:
8656f687-014e-5488-a5ea-5ac5f08f4f8a | checkpoint | 2.5 - Made Good
2e649beb-1249-56e7-bdf6-b2a3358aed94 | note | Frequency - Each Lot
72cb9da6-7592-566c-a0c5-7bad14187df7 | note | Acceptance Criteria - Removed and demolished pits and/or cavities are backfilled and compacted. Backfilled areas match adjacent existing surfaces.
a122d8df-a5a6-5039-abe3-45ddf042b566 | note | Reference Documents - Spec Cl. 8.5.7
032378c0-9e5f-5fe6-9c7c-a7a25c0cc35f | note | Inspection/Test Method - Verify
de1d9087-ec08-57fa-9c3b-a8e2f082dd8a | note | Record of conformity - This ITP signed
753bd93d-d588-5243-bb18-80ffc50e8cb1 | note | HP*
95172b46-6943-5d2b-b5b9-60aef6f9cecb | note | Responsibility - Project/Site Engineer, Foreman
0d69e2a8-438f-5fbd-be52-ebd47e1cc6e7 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
2e649beb-1249-56e7-bdf6-b2a3358aed94 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
72cb9da6-7592-566c-a0c5-7bad14187df7 | textbox | Print Name:
a122d8df-a5a6-5039-abe3-45ddf042b566 | textbox | Position:
032378c0-9e5f-5fe6-9c7c-a7a25c0cc35f | date | Work Completed On:
de1d9087-ec08-57fa-9c3b-a8e2f082dd8a | date | Date:
c16a7dd0-c687-5cd6-887d-70efd49b6468 | checklist | FH-ZU2-QU-ITP002 - Site Establishment - Rev 0 | itp | ITP002 - Site Establishment
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
3cfc1515-1fe7-5182-8110-095e2a556c32 | note | Frequency - Prior to works
5f979054-727e-54aa-8645-fb79302086c9 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
7a7b835a-87b9-5819-b24a-054c8dcd3994 | note | – Using the correct and complete set of drawings.
f8079544-3881-5620-98b8-59beb27370c3 | note | – All drawings are the latest revision
a8475448-f144-5495-b5fc-6993900571fa | note | Reference Documents - Work Pack
bf8a3dd4-0e62-571f-98da-683c260cb359 | note | Inspection/Test Method - Verify
958ce004-234e-5e71-88fd-6fa4b18a21bd | note | Record of conformity - This ITP signed
90469bb2-d27a-536c-acea-5544ec8976bb | note | IP
8ce14f19-a51e-55f3-81ea-0f8a06940dd7 | note | Responsibility - Project/Site Engineer
0f7b1605-06d9-53a7-9a06-c33e112dd6ee | date | Date Completed:
4bd1d280-8d7f-5dfb-abc2-9c57770ba8c2 | checkpoint | 1.2 - Dilapidation Report
c2bcdd88-d14e-5d6b-a936-b84cdcbd0466 | note | Frequency - Prior to works
c26ff740-c231-52ba-b06c-8c6efda807a6 | note | Acceptance Criteria - A dilapidation report is to be completed and submitted prior to works on site. Dilapidation report to include photos and recordings of the condition of the site compounds areas prior to start.
e5b19e94-a206-5ae9-b7b5-3bebbc124d70 | note | Reference Documents - Dilapidation Report
abf9fb6f-e6bd-5b84-9c6c-bbb1fc04293c | note | Inspection/Test Method - Verify
61cbd3d1-e908-5933-b041-d38e71e0f6e0 | note | Record of conformity - Aconex & This ITP signed
ec2200f5-4a02-51e7-88e8-2ba60278d73c | note | HP*
87eb43cf-d3bc-5448-a56b-f2b3d9588de5 | note | Responsibility - Project/Site Engineer
8170464f-1e89-5ae7-a7f9-ea5bf1cb95d9 | date | Date Completed:
1345e494-308d-59f2-9734-1b56d70c486c | checkpoint | 1.3 - Existing Service Identification & Protection
c91f897a-bbb9-557f-b0d6-b68cad614832 | note | Frequency - Prior to works
a5f8e5b3-8e44-5306-a72b-ed5465d53ee9 | note | Acceptance Criteria - Hardstand area has current BYD plans, service scanned, and existing services has been proved. Services have been identified and protected prior to demolition.
dabcbcc8-a24c-5a75-8c79-37a520ffe796 | note | Reference Documents - BYDA, Survey Maps
db005276-8c78-56db-84ad-8194afcea8e2 | note | Inspection/Test Method - Verify
1f97c349-d1c4-5349-ab1c-9fbb364f8e06 | note | Record of conformity - This ITP signed
761d0319-0a04-56dc-82fc-3e7a37a2af9a | note | IP
4d9a8f6a-9164-5dfa-9de7-9b1576639340 | note | Responsibility - Surveyor, Project/Site Engineer
3a1c9c80-0467-5605-9459-fd9cf9a7a741 | date | Date Completed:
2b2d509f-644c-513b-8429-dc08b6bd0803 | checkpoint | 1.4 - Implementation of control measures
2102382c-98b4-55ec-b64f-c362f5d93de1 | note | Frequency - Prior to works
82f3d642-92cf-5365-a9d8-ac7a7ad9079a | note | Acceptance Criteria - All necessary control measures are being implemented, which include PSP, ECP, TMP, SWMS and WP
1106c405-6435-545f-8e0c-fbce99609408 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
c8f203b8-de9d-538c-9fa8-de265c221722 | note | Inspection/Test Method - Verify
2e4e799e-1a58-58cc-8183-e0c31531b986 | note | Record of conformity - This ITP signed
ad65f495-a215-5c46-b32d-c93fd03a6710 | note | IP
9624af7e-36c8-5a93-8425-4efbc949557c | note | Responsibility - Project/Site Engineer
b6171726-97ec-5f08-9180-4fb7cb54bb40 | date | Date Completed:
940df89a-8186-56ea-b5c3-4645a58a692b | checkpoint | 1.5 - Testing
56b0609c-3136-5adb-99e7-6dcebb30eb90 | note | Frequency - Prior to works
0fa57451-1e5c-5b06-ab1c-28c81e6b2bc7 | note | Acceptance Criteria - Ensure PFAS testing has been completed. The results of the testing will be used to determine the appropriate disposal or re-use of the demolished materials.
1ccf6cf2-b3af-5025-8e17-a48c645c1d2a | note | Reference Documents - Aconex
efded1df-a4f6-5702-8cfc-40a516be814f | note | Inspection/Test Method - Verify
875c58e8-5650-55dd-98e5-667a9fad9d8d | note | Record of conformity - This ITP signed and test report
88f43a90-dbaa-55a4-813d-f7e661c27c40 | note | HP*
121c1f21-fd9f-58f7-bf2a-77c8dcf0392c | note | Responsibility - Project/Site Engineer
ede39bc6-21e6-5577-89e6-4f486939a620 | date | Date Completed:
b7e81dec-e470-5248-a10c-e95e95f63636 | checkpoint | 1.6 - Excavation Permits
438f0943-5177-502b-8329-f1c93846ee19 | note | Frequency - Prior to works
626de8fa-07e5-5ee3-8890-a365da489a19 | note | Acceptance Criteria - Prior to works, check that excavation permit has been obtained from APAM prior to any ground penetrating works. Internal Fulton Hogan permit has been issued for excavation works and plant operators have a Go-Card.
a54e3c31-8e56-52bd-bb6a-6e561a515ea8 | note | Reference Documents - APAM Excavation permit, FH Permit, Go-Cards
acb02066-1e9f-5d4e-a02b-3524ecf65518 | note | Inspection/Test Method - Verify
8e9c8bd5-f7ac-5969-a618-e51bcce70ad7 | note | Record of conformity - Excavation Permit
3f36bc56-a1ae-5524-a1b5-203eb3437f1b | note | HP*
2ea25830-60bd-5a21-9281-8bb933f3dddb | note | Responsibility - Project/Site Engineer
53bb5044-b0c6-587d-96c6-ef4f3c40ef13 | date | Date Completed:
e66747cf-dea2-51eb-b3ec-1b89f3bf0b5d | checkpoint | 1.7 - Geotechnical Testing
a4717674-a002-501b-becd-3542952ad92d | note | Frequency - Prior to works
1a27f139-cfa4-5855-b846-c7ceca0c45fc | note | Acceptance Criteria - Ensure testing is carried out to obtain a Hardstand design that meets the requirements and suitable for use.
aa6eaba6-6550-5320-bc28-5704f826047b | note | Reference Documents - APAM Excavation permit, FH Permit, Go-Cards, FH spec
d1e480aa-8ca8-59b1-b0d9-8911b71b7fb2 | note | Inspection/Test Method - Verify
7a3e9e1d-e818-5582-a74a-5742912a6702 | note | Record of conformity - Excavation Permit
55237742-d7d0-5ba3-aae7-197b754af9e0 | note | HP*
f6691999-63d4-5007-a230-0e782e5acee6 | note | Responsibility - Project/Site Engineer
7bea0aba-af66-5129-8dfa-567546d0a78d | date | Date Completed:
68d4b750-18d0-5bb8-97d3-fe4e562f8dc0 | section | 2.0 - Building Hardstands
53302c01-4ad4-5657-937a-dc89dcc79ddc | checkpoint | 2.1 - Definition of a works area (survey)
1495f105-79ac-5ae6-958c-b8af2f0917fd | note | Frequency - Each Hardstand
01e59542-55ff-56a7-aa8c-3bd66f93bf12 | note | Acceptance Criteria - Work area has been cleaned and surveyed (marked on site). Limits of hardstands are clearly marked.
d24c548c-733b-5b2f-abf7-fb8acbda0a0a | note | Reference Documents - Site Markups, Survey layouts
b3aeb841-330e-5fb0-bc8f-0c972c71cd39 | note | Inspection/Test Method - Verify
6a1d4755-e820-59c7-877f-a8267b2a731b | note | Record of conformity - This ITP signed
8b048cc1-d142-5981-852a-346e271051c3 | note | IP
263c11bc-6929-5a56-9e2b-d67036efd2c1 | note | Responsibility - Project/Site Engineer, Surveyor
f2fb3fe2-53a4-5a0c-a34d-21a5c29f3c5d | date | Date Completed:
25acb849-3109-53dc-b0ef-d853cbf5237d | checkpoint | 2.2 - Preparing subgrade
0500d3f1-331d-53cf-92e7-71e3c5882841 | note | Frequency - Each Hardstand
2056ded0-8e4b-5e8a-97af-bb9d5e1849f8 | note | Acceptance Criteria - Ensure topsoil stripped as per hardstand temp design and subgrade compacted to meet design requirements from Geotechnical Engineer.
b9d6dd20-7633-5fc9-934b-2e738cabf5b7 | note | Reference Documents - Geotechnical temp design
cff19e40-fcb9-544a-94e4-101c985beb63 | note | Inspection/Test Method - Verify
4ef23d7c-8ee6-5f4f-93d3-276683bfb7d0 | note | Record of conformity - This ITP signed
7ca16b4b-c013-5661-866b-649b18a4799c | note | IP
adf3bda5-8f3a-5328-aa10-88d2359ad0e5 | note | Responsibility - Project/Site Engineer, Foreman
2ed9a8c6-51e9-55d1-ab26-0b8d28996d2a | date | Date Completed:
cb2d8e84-991f-5559-a72a-59370f524404 | checkpoint | 2.3 - Disposal of Material
5a4695fc-fed9-5d39-993b-510f73c26ba4 | note | Frequency - As Required
3647b628-1080-5ac0-b783-d8115721a752 | note | Acceptance Criteria - Contaminated or PFAS materials are to be taken to Gate 11 to be stockpiled into their dedicated category and contaminant.
663f3cad-596d-5600-ac40-ce55a7eb5859 | note | Reference Documents - Negri PFAS Permit
21926fa3-6a6b-5ba1-b5a7-04ec5295ffab | note | Inspection/Test Method - Verify
1051b69c-784e-5baa-821a-685cf463f56f | note | Record of conformity - This ITP signed and Negri Permit
14b22d9f-12b9-54c5-baf2-d886cd44341f | note | IP
8c75014e-8b2e-599f-8b71-9df089d86128 | note | Responsibility - Project/Site Engineer, Foreman
a38167de-9652-580c-b90b-bc2a92606021 | date | Date Completed:
e7e79b9b-f0bc-58a2-9b2b-3a96a8c6c442 | checkpoint | 2.4 - Building Hardstand
00812335-82b0-5f82-a978-d66410fe7bbb | note | Frequency - Each Hardstand
948565d6-733a-5129-949a-6d6626132e7b | note | Acceptance Criteria - Make sure hardstand is built according to the geotechnical temp design, no soft spots existing after proof rolling.
13626329-6635-5e4f-ab0d-9320cbea65c8 | note | Reference Documents - Geotechnical temp design
3ba010e5-4f98-50ab-9f06-1e842ade4b3a | note | Inspection/Test Method - Verify
e55312eb-1212-5945-b08d-29d1795a93f1 | note | Record of conformity - This ITP signed
fac0995c-3df7-564b-88ba-c6ef256d86c6 | note | HP*
07acc568-4d34-5e61-80ba-8d566d18a14a | note | Responsibility - Project/Site Engineer, Foreman, Geotechnical Engineer
033a81d7-b825-5c67-807e-e2a45faea285 | date | Date Completed:
196b06ac-ca40-5029-82a1-25b9e85b4c1a | checkpoint | 2.5 - Building Crossways
24afd2cf-7314-5d7d-8524-bb6e52f39473 | note | Frequency - As Required
6951fa49-1dc5-561e-a19a-05594f2f1e53 | note | Acceptance Criteria - Construct culvert crossing/driveway access where required as per the temporary design.
7af45202-667f-5d7d-844b-376be1ae9dce | note | Reference Documents - Temporary Design
9993275a-e295-5c89-8fea-488eed4ed7d0 | note | Inspection/Test Method - Verify
555f84ed-9ffb-5bac-94b6-eed048703976 | note | Record of conformity - This ITP signed
09403b2b-f310-53d7-9b6d-107cf6c40f3e | note | HP*
bc825d6d-54af-53f1-896d-cdcd4437350a | note | Responsibility - Project/Site Engineer, Foreman
4fae311f-986e-5084-9887-13b447c20d07 | date | Date Completed:
b7bf38dd-40ca-503b-9c6c-3c2f944e444c | checkpoint | 2.6 - Installing Fencing
2d642617-6f94-57c4-a8cb-79d6413ad8e3 | note | Frequency - As Required
6a4b3d31-c75a-5a35-ab95-c6707a983f3f | note | Acceptance Criteria - Fencing installation is done as per the temp design or Australian standards AS4687
cee0728a-ca97-52b3-9931-596a16407ea8 | note | Reference Documents - Temporary Design
70d40084-dc8c-5ebd-859a-3361fde9f881 | note | Inspection/Test Method - Visual inspection & verify
ad67a3d9-bcff-53d7-b960-693d887c30a7 | note | Record of conformity - This ITP signed
ae9c735d-ac9d-533c-9799-f4cd5f930588 | note | HP*
e81d5045-3b97-50c8-a580-ffe7680ddca9 | note | Responsibility - Project/Site Engineer, Foreman
613c1904-3c34-59be-aff9-6aabec9d5697 | date | Date Completed:
584e46b0-8c84-5cbc-8fcf-927a08f8bafa | section | 3.0 - Mobilization and Set Up
9b8789bb-08fc-5e44-933d-a6c1af9aa666 | checkpoint | 3.1 - Landing and Levelling Sheds
7df20ce7-1bce-5bad-b012-07f31c438756 | note | Frequency - Each Hardstand
16d6c691-10b3-547e-bf53-e42c8b13e516 | note | Acceptance Criteria - Sheds are level and as per the site management plan.
e01217b5-9153-58bc-bbdc-18783838db10 | note | Reference Documents - Manufacturers specification
797168ac-a472-531f-9cd6-fe49616e8dd9 | note | Inspection/Test Method - Visual Inspection
1c18e28a-aeb6-56af-8b04-09385f08da47 | note | Record of conformity - This ITP signed
6b27caa2-19ff-5478-9a42-982c2b053420 | note | HP*
ed054c00-a465-57f1-9e8d-e2841ca4ef42 | note | Responsibility - Project/Site Engineer, Foreman
8bae08db-8d08-599d-add9-df806f7f6e72 | date | Date Completed:
8f737ad7-8dbb-5065-8ec0-f419c46b67a2 | checkpoint | 3.2 - Erecting Hayshed
57049837-e6ce-58e4-848a-828da521ef1f | note | Frequency - Each Hardstand
bd1ac969-30a5-59cf-948e-d25e80e4213c | note | Acceptance Criteria - Hayshed has been constructed as per the verified temporary design provided by OPT
d818c8d1-37c4-5d90-9795-51b1448746f6 | note | Reference Documents - Temporary Design
c2c6e331-eebf-5ab1-b63d-5dae1c5edf6e | note | Inspection/Test Method - Verify
a79d71dd-7cce-52a7-a077-d8d34fef6462 | note | Record of conformity - This ITP signed
07272eac-048d-54b3-a9a7-324c54f19912 | note | HP*
475e6078-bd4f-58d3-9584-8dfbbf0e0133 | note | Responsibility - Project/Site Engineer, Foreman
791c8721-250c-51ba-9c7a-873b0d6eb072 | date | Date Completed:
07aa1c9b-d315-5fdf-9465-365031099f34 | checkpoint | 3.3 - Connecting electrical and plumbing services and appliances
52c6b1ec-caa5-507b-b7ee-81561729edb9 | note | Frequency - Each Hardstand
74ee067a-3644-5bd6-bc78-7023ae184444 | note | Acceptance Criteria - All appliances and connections are functional and tested and tagged
37ddfe63-6932-5aa1-be1b-260df3edf73c | note | Inspection/Test Method - Verify
f9f078d4-88a9-532e-9806-4bd6abf31f24 | note | Record of conformity - This ITP signed
f4e10d7d-947f-5f4c-80e2-bcf1d06ffc36 | note | HP*
d84d564b-45d2-566a-bd7f-4d5be6c4422a | note | Responsibility - Project/Site Engineer, Foreman
2bee9357-f1c3-5394-87f1-7515da434d13 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
26cc0429-e587-5450-b454-1ebe89d0daf6 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
383b649f-0c48-5212-8c94-fd8b492b7fc4 | textbox | Print Name:
0cf105b1-a508-5f4b-aa82-8acee5a17fd9 | textbox | Position:
2e5731f2-7afe-535e-97ba-f3610e5d15c5 | date | Work Completed On:
2c9bcd1c-9204-524f-9d2e-3f7b651761c8 | date | Date:
c7f2a25d-63b1-576a-877c-1278810f36d3 | checklist | FH-ZU2-QU-ITP003 - Stripping Topsoil and Bulk Excavation - Rev 0 | itp | ITP003 - Stripping Top Soil and Bulk Excavation
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
b0bf35cf-bf6c-5dcc-bc41-0235c9052364 | note | Frequency - Prior to works
e04509c7-936f-53e0-8fb6-f7bcc1a327ea | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
fdc5d8e3-669e-5553-b761-b07e1a397496 | note | ○ Using the correct and complete set of drawings.
48eb929d-4aad-5b25-ae8d-1d7116fe3a1a | note | ○ All drawings are the latest revision
6ca6d629-4784-5861-a79c-4c0ba3d6f4eb | note | Reference Documents - Aconex
dd16b1cc-ab12-505c-a2b7-7bb53fe3bd1d | note | Inspection/Test Method - Visual inspection
2d9a6b90-f30a-5624-8211-191e8989370d | note | Record of conformity - This ITP signed
cc09c387-0c2f-5dda-adea-a8ef80176672 | note | IP
ea4975d0-50ea-5d69-bb76-c1968543b9ce | note | Responsibility - Project/Site Engineer
cf4ecca4-eaeb-5bec-9d03-95e47a4cca08 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
a1c6b7af-0051-5b47-adee-2ba83b1e11a9 | note | Frequency - Prior to works
0fbcefe2-64ad-51a3-9613-d315fef28308 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS and WP.
e4c9d16e-a953-5b9b-9a45-8877156edfba | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
7d8cb712-2e8a-5a0d-a8b0-c44a5c45ec04 | note | Inspection/Test Method - Visual inspection
d25d94ff-7601-53b0-919b-c613f70f2323 | note | Record of conformity - This ITP signed
b7a0ec80-5f8e-587f-834b-1d098369588f | note | IP
0a63dfdf-bbf5-580e-a8d0-ae9bf172ca29 | note | Responsibility - Project/Site Engineer
72eda7e5-1afb-5c67-acd8-196c3e10781d | date | Date Completed:
e7a6e343-1080-52f9-bd48-1f0f6f5a115d | checkpoint | 1.3 - Survey
b28ddb15-dca5-55f8-87fa-e72f19e92a7a | note | Frequency - Prior to works
8f6fc471-c5ab-56c6-92c3-cdc17da61ba1 | note | Acceptance Criteria - Area has been surveyed, highlighting any areas where excavations should not occur (e.g. exclusion zone).
895ea11a-326a-5b69-9652-f24fcd91fd48 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
d8337aa2-37fe-515d-b4f3-1bacfc84dc3c | note | Inspection/Test Method - Visual inspection
7717e169-d754-5552-bb9d-d4f6f8d10b45 | note | Record of conformity - This ITP signed
eb0c37fb-eed5-5944-85a7-b335db33ccc5 | note | IP
fd3a1bf8-2181-59f0-ac7e-d79f06a26e54 | note | Responsibility - Project/Site Engineer Surveyor
bf4564b4-0f61-503c-bcf3-02eccb92fc4f | date | Date Completed:
bd6fccff-030c-5e03-b297-aee09316b255 | checkpoint | 1.4 - APAM permits
f25c9f2a-2ac1-560f-9017-7b5a7084fae8 | note | Frequency - Prior to works
24dd5cb6-1f04-5f82-a4dd-46e652983d3d | note | Acceptance Criteria - Excavation permit issued. If working near HV electrical, an Electricity supply Isolation form and cabling permit has been issued from Melbourne Airport.
9212205d-6ac3-54ab-8fc9-fee1a896df2e | note | Reference Documents - Excavation permit
c8d42d6b-eab7-5cb6-8755-e20453f295ab | note | Inspection/Test Method - Approved permits
cd6b0421-3dd9-5c4c-b73a-de6b1c4ef85c | note | Record of conformity - This ITP signed
8c0fd384-a553-5a21-86d2-9c2ae1ecfe59 | note | HP*
d444af54-ebc2-5cb7-8451-2ffc6d07021f | note | Responsibility - Project/Site Engineer
8be9d07d-a5ae-5841-b757-795c9b56f251 | date | Date Completed:
2e351d7f-b3b9-5262-b49f-9acd784e8df1 | checkpoint | 1.5 - Fulton Hogan Permits
46947f88-5c71-5c7e-b717-22cd2b1a7fc2 | note | Frequency - Prior to works
71e0ef47-8be4-5ac0-962e-604e87161e84 | note | Acceptance Criteria - Fulton Hogan Excavation permit issued to plant operators prior to excavation works. Native Grass heatmap issued and boundary of working area has been set out.
6f1796c9-4d05-53e0-bdde-821c5592e2a9 | note | Reference Documents - Excavation permit
d8325656-3f12-56e1-b210-0d4b6ceac6e5 | note | Inspection/Test Method - Approved permits
4967b778-ff83-52d9-ba59-8cdfef0f275f | note | Record of conformity - This ITP signed
286d6d2b-0311-53eb-ab23-9f4d05737f61 | note | HP*
e52bf27e-db56-57ab-bf83-dafe2c698d6d | note | Responsibility - Project/Site Engineer
eee46c57-60e0-571e-a3f7-97999f76db52 | date | Date Completed:
4bc40f29-44b7-5162-af9f-0698ea5dc38f | checkpoint | 1.8 - Plant and Equipment
725e528d-8b52-5ff5-85fb-0ada1e94e3c8 | note | Frequency - Prior to works
85884f2f-55a6-5be8-9305-0ab219e520c7 | note | Acceptance Criteria - Plant and Equipment used in the works are appropriate to achieve specifications requirements. All plant inducted and inspected as per Fulton Hogan’s plant safety guidelines.
0c019c51-0614-53a0-a154-a2497f8f1c0a | note | Reference Documents - WMS - 003
49aa4a47-fa8b-5fc8-9e34-53bd8059363b | note | Inspection/Test Method - Visual Inspection
6f0ef1fb-f190-53d8-bb13-c894ce09a267 | note | Record of conformity - This ITP signed
1200834b-44a9-5646-b802-8fb932cef07a | note | HP*
acb14978-a615-5ab1-b64f-c6ca52037d13 | note | Responsibility - Project/Site Engineer
d2181fa4-4cd9-5c12-8779-31f6d7c56cc6 | date | Date Completed:
ea5dc8b5-493b-5278-aaf7-f712b642d5b6 | section | 2.0 - Stripping / Bulk Excavation
4e2902bd-6fa2-5de7-a9a2-a7d948c2aa61 | checkpoint | 2.1 - Site Preparation
e27a247b-1e88-5f51-a280-e8299a920aef | note | Frequency - Each lot
0a25fe0f-b005-5d68-9994-e63d04d72117 | note | Acceptance Criteria - All excavation and filling will be free draining to low points clear of the Works. Sufficient pumps, well-points or other equipment for work area de-watered during the works shall be provided where required. Existing drainage lines and water mains found to be traversing the site must be removed as shown on drawings. Contractor must provide temporary pollution control devices or ponds in existing drainage systems and receiving waters.
fb794ab0-50c9-5a06-9d65-96021ddcebff | note | Reference Documents - ZULU- BECA-001- DWG-00001 to ZULU- BECA-005- DWG-01119
57f65844-de94-507d-8927-bfcd2dc9e32f | note | Inspection/Test Method - Visual Inspection
de7135f9-ef45-53c4-a19f-d3aee6734303 | note | Record of conformity - This signed ITP
1e268370-06e4-51b0-93f7-5fe806d0e603 | note | IP
fdf1cd7f-ee62-5ff2-92da-3766f85b1d48 | note | Responsibility - Project/Site Engineer
a585c59e-e787-55aa-92e0-4d29ff87e6d7 | date | Date Completed:
6b0d4de9-7bdf-5139-bfb9-9bbf4e32fa40 | checkpoint | 2.2 - Dust & FOD control
4d67a5f8-2cd4-5cd9-9125-ce8a13c6a8e4 | note | Frequency - Each Lot
9d8de3bf-fc2b-5dc9-a674-f8c8cc422829 | note | Acceptance Criteria - Prevention of dust during earthworks and subgrade preparation. Sweeper onsite at all times to manage dust / FOD.
4ad3cfa1-c539-5aed-8a56-1a9ecdfb9de9 | note | Reference Documents - Site ECP
c801db41-4373-5367-9606-050abb383544 | note | Inspection/Test Method - Visual Inspection
ffd00528-9efe-5abc-885c-e0a0693ef0cd | note | Record of conformity - This signed ITP
191ac37f-fb65-59aa-9cf7-0486937f3484 | note | IP
8e80ef2a-479d-5ee0-bfd4-90df9d4824b1 | note | Responsibility - Project/Site Engineer
58934db1-aab0-59e1-af23-b9571dc42add | date | Date Completed:
a9be7178-4948-5336-bda8-c7104a9e9d10 | checkpoint | 2.3 - Stripping Top Soil
a2cb99da-1e4a-5761-888c-818826c7f6f0 | note | Frequency - Each Lot
795111e8-641b-57d4-817c-253a3653277c | note | Acceptance Criteria - Prior to bulk excavation, site shall be stripped of all topsoil and organic matter as shown on the drawings. Spoil to be taken to Gate 11.
e90c0149-9f06-5f8a-befe-fb458a02b66b | note | Reference Documents - WMS - 003
58244c20-c81e-55b3-810d-ca191ccd8952 | note | Inspection/Test Method - Inspection Point
544ed1e8-6d34-59ab-93b7-0c67e29edcbe | note | Record of conformity - This signed ITP
b8aec92e-8e8a-5dac-95b4-9a205065a43a | note | IP
b77161e9-7ad9-5ed9-bb01-df12fda98a3b | note | Responsibility - Project/Site Engineer
f8d6de4d-e30d-5464-bfc8-fdf096736fcf | date | Date Completed:
9b151195-b645-57b8-8894-c358f2e97edb | checkpoint | 2.4 - Excavation
655ef21e-d583-540b-b0e8-1ae4f87f9ef6 | note | Frequency - Each Lot
fd71f423-e2b8-53ba-bbee-19f9db30e125 | note | Acceptance Criteria - Bulk out subgrade to 100mm of subgrade. If rain is imminent, ensure subgrade is left 100mm high prior to trimming.
c7cc11d3-553d-5d81-b8f0-0f6f1407a670 | note | ○ Rocks Under <800mm can be taken as mixed fill to Gate 11
623c6037-b637-5187-982a-aec791a42130 | note | ○ Rocks >800mm to be sorted and taken to Vic Civil
00c8d2f8-9d2e-5735-9cec-8d01d06b07aa | note | Reference Documents - WMS – 003 Spec 001 - Cl8.5.3
14dccc02-a646-50f9-8f6d-32f24959c516 | note | Inspection/Test Method - Inspection Point
5d396ef6-eb80-5b2a-b64b-d36b8ef0cd6f | note | Record of conformity - This signed ITP
f0aa852a-6306-543b-81bf-7bb4fe5f8563 | note | IP
5d0cec04-02dc-5c0f-8bfd-6084f48216a9 | note | Responsibility - Project/Site Engineer
55143d0a-4292-5671-8588-0096dd2b279b | date | Date Completed:
ee92312b-90a8-534a-a85f-46726ca60607 | checkpoint | 2.5 - Batters & Temporary Support
0078066f-7ff2-5a7e-8bd0-f096e2d634ee | note | Frequency - Each Lot
a9d660c2-8e06-58b0-819c-137e62261509 | note | Acceptance Criteria - All batters to be kept at 1:1. If not, temporary support will need to be designed, engineer and approved for use. Temporary support will remain in place until it is no longer required.
29b426b8-1462-5593-8f23-9614a99f34eb | note | Reference Documents - WMS – 003 Spec 001 - Cl8.5.3
126bb257-8287-5830-aac8-804f9eb9a3ce | note | Inspection/Test Method - Inspection Point
2c813702-c8eb-5da1-a4cc-6123c2135816 | note | Record of conformity - This signed ITP
087bd442-d3ce-5bd3-a28d-e96e359893d3 | note | IP / HP* (if required)
391bd648-17fe-558b-a9e4-f3742978176b | note | Responsibility - Project/Site Engineer
5b4b410e-8682-530d-bb89-ffc8cee3cc2a | date | Date Completed:
1f461390-d201-5a9a-9dc1-82fc60ff9cfd | checkpoint | 2.6 - Excavation – Detailed Trim
409c906c-8df3-5ce5-baed-d2848aa53b27 | note | Frequency - Each Lot
6c4e7036-00b5-55de-ae66-e0e7d66c0a00 | note | Acceptance Criteria - Detail trim Subgrade with excavator / dozer
261f738f-711f-58c1-9b34-cd5f799091d7 | note | Reference Documents - WMS - 003
c48ff060-151e-56f8-8dbd-337de1a3b9d6 | note | Inspection/Test Method - Inspection Point
857f60cb-c4f5-52c7-a914-3d2c5f25ef5e | note | Record of conformity - This signed ITP
d00655ce-58a8-571d-a4f0-17a5c069092c | note | IP
2e518698-e4ba-51be-a036-130fbe55bbbe | note | Responsibility - Project/Site Engineer
b7c1f4d5-948f-56cc-8b7f-1d61781f5e30 | date | Date Completed:
3bf76795-3e73-576b-94f4-19c2ecefa43f | checkpoint | 2.6 - Contaminated Materials (if found)
67d60ac1-c767-5cea-b33a-9c957fe6607c | note | Frequency - Each Lot
7449cf1a-8fdd-5cbe-ae73-f35efccbcd1c | note | Acceptance Criteria - If contaminated or hazardous materials are found, immediate notice is to be given to the Principal’s Representative. These include the following;
18a1b02f-fa5f-5c4b-b29e-8f690d0c20a9 | note | ○ Asbestos or material containing asbestos;
0e601b8e-85e3-5a48-a95a-ce16b3c42b43 | note | ○ Flammable or explosive liquids or gases;
2ffaae20-313d-56b8-af17-0013db1ffe64 | note | ○ Toxic, infective or contaminated materials;
62627aff-bf7a-5503-aaa0-559e22ae8235 | note | ○ Radiation or radioactive materials;
07a861b9-fcc3-52fa-867a-fdd1a56a7642 | note | ○ Noxious or explosive chemicals; and
ea990217-0df6-564d-b132-aaf6c7ce482c | note | ○ Tanks or other containers which have been used for storage of explosive, toxic, infective or contaminated substances.
37992f1d-ea50-5adf-8ffe-baa1ff457dd3 | note | ○ High levels of PFAS
2b53e1b2-cddd-5f0b-ad08-820e0dc38a18 | note | – Agreed removal location to be confirmed with Principles Representative.
9480a3e7-6a36-5ce4-ae96-c773283c46a8 | note | Reference Documents - WMS - 003
c114f601-e3b3-5150-891f-fd79140ee62f | note | Inspection/Test Method - Inspection Point
544d69e3-e333-556a-a981-ea4bfb155186 | note | Record of conformity - This signed ITP
a5480ed3-09c5-55d5-9668-ff3b1e52ce26 | note | HP*
1ec73940-2fe9-55e5-ae19-877a013ce1a4 | note | Responsibility - Project/Site Engineer
cae0531d-97c9-55cc-8a76-caf2995f702c | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
b663b21c-3dfa-536b-b178-91b4f1c37e18 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
ee31d79b-0f59-5a23-82d1-8fe5dd6ec31c | textbox | Print Name:
664f83e7-742d-544a-9d95-9b5f459e4f81 | textbox | Position:
b8ae34f3-9bd9-5e79-9bd4-5cef927f9b58 | date | Work Completed On:
3fe6fc4e-f7a1-5d0e-aa19-8fd21eac62dd | date | Date:
741da932-01e5-5ed2-b7bf-7bd6c0ccbab0 | checklist | FH-ZU2-QU-ITP004 - Select Fill Placement - Rev 0 | itp | ITP004 - Select Fill Placement
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
08c4b17e-a29e-56a5-be50-2ab69afd4d71 | note | Frequency - Prior to works
ec07a3cb-c1f0-5188-bcf9-00a8a0a7c914 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
0afb9d20-3984-59f9-afad-cbce551ff055 | note | ○ Using the correct and complete set of drawings.
9934483f-2306-58cc-9494-554d12355379 | note | ○ All drawings are the latest revision
ffc9abf8-4d0f-5d97-bd9f-25c82ca3379e | note | Reference Documents - Aconex
ab0c1193-80ea-588b-943d-7498f0b43bae | note | Inspection/Test Method - Verify
9190310b-61ff-55e1-b585-7c6deddfd16d | note | Record of conformity - This ITP signed
d5d4dd88-73b5-5173-aa38-2d4c061b361e | note | IP
f1a09c02-c144-573f-9bf1-fc6e921e59dc | note | Responsibility - Project/Site Engineer
5582b486-373d-5a50-a97b-1b17f5be5c85 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
b26f041a-9e1a-53f5-a2a7-ae357fb1b158 | note | Frequency - Prior to works
5f736424-2c68-5813-9f3e-9938bc60e9e0 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS and WP.
f2c2258a-099b-5a2d-bbb8-405e99612b87 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
2a982293-b48a-53b5-9ab5-3e0ad4ffa560 | note | Inspection/Test Method - Visual inspection
4651ff39-7b00-5362-9150-e2db58cfff0d | note | Record of conformity - This ITP signed
2f29ce51-e199-555a-98f0-058275729f9f | note | IP
2f332fd5-58f8-54ee-b8b4-6bcfbdb45e3b | note | Responsibility - Project/Site Engineer
847d413e-f5a2-5801-bdce-d489bf57302a | date | Date Completed:
e7a6e343-1080-52f9-bd48-1f0f6f5a115d | checkpoint | 1.3 - Survey
b94c6f79-9487-5050-adc7-6028f0f7816c | note | Frequency - Prior to works
bb4e26e8-aa42-5610-aa37-25d1a70889db | note | Acceptance Criteria - Area has been surveyed, highlighting any areas where excavations should not occur (e.g. exclusion zone).
d71e8c39-5636-59d4-aeb9-34f2bc826c1b | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
a5158671-8dd3-51d0-8cea-a932a5e0b6ce | note | Inspection/Test Method - Visual inspection
5e36ac1e-3494-5b2b-8bbe-78c39bdf135f | note | Record of conformity - This ITP signed
09f23b99-26a6-52f7-a317-f1e4add963d3 | note | IP
2bb97587-0580-57bc-8c47-320a24478bc9 | note | Responsibility - Project/Site Engineer Surveyor
43a2c40b-d1a0-5c47-a992-6064ca6125ff | date | Date Completed:
42f3e87a-e178-51d2-a080-8cf107eecf0a | checkpoint | 1.4 - Select Fill Material Source (Under Pavements, Imported)
daaba572-1025-5653-afd5-9bf625b59ef9 | note | Frequency - Prior to works
cbb4fed3-7ecd-5ef1-9d34-d585415b842c | note | Acceptance Criteria - Material to meet the following the properties:
be36a13f-2979-5221-b8a4-81124970ae9a | note | – – – – – – – – –
00897eec-50ef-56f5-b303-a4a67d250bfb | note | Wet strength ¦¦ Not less than 125 kN wet/dry strength variation less than 40%
49dcfc3f-2abb-5459-8068-e575a930b0fe | note | – – – – – – – – –
2c356531-e24e-5bfe-a5ed-558c7e48cfbf | note | Linear Shrinkage ¦¦ < 6%
1e1a2f50-b31b-599f-b1b8-b6cedf70dba4 | note | Organic Matter Content ¦¦ < 0.2%
4dec1663-fb29-55bd-95db-83504927c099 | note | Maximum Particle Size ¦¦ 75 mm
28ecf767-cd52-5370-a3ff-72d6443e29f1 | note | % Passing 0.075 mm sieve ¦¦ 0-12%
476e4531-4980-5b57-a950-4372438293d5 | note | Soaked CBR ¦¦ > 20%
b265c9d2-38af-59c4-8e30-d0393ed05e4d | note | CBR swell % ¦¦ ≤ 1.5%
c9074b6f-1d34-594b-b824-102bd68533e0 | note | Permeability ¦¦ < 5 x 10-9 m/s
d8ecc50e-bce7-5f79-8a5c-a4b2dc1bfc3f | note | – – – – – – – – –
d8e6513b-c0b9-52ee-bf6c-8f331b0195b6 | note | Material Property:
814c752b-bb60-50f1-96f9-edf0e7c737d7 | note | – – – – – – – – –
c0a6959d-2e3d-5fb8-ac12-ff1d57863ae2 | note | Material Property ¦¦ Requirement
f2a02c5d-7e16-43b5-bb11-24639f86353b | note | Liquid limit ¦¦ < 35%
6023c1d1-dc64-42b9-b566-66672555818b | note | Plasticity Index ¦¦ < 12%
cf82e18b-2dd1-4b6c-af80-f76a73ba9eb2 | note | Wet Strength ¦¦ Not less than 125 kN Wet/dry strength variation of less than 40%
a6256b04-31e1-4c46-bb8b-be1963b43002 | note | Linear Shrinkage ¦¦ < 6%
c25f9859-1f75-4146-8214-12162e402f21 | note | Organic Matter Content ¦¦ < 0.2%
28a6fc05-a96f-400f-9a83-f665e36487fe | note | Maximum Particle Size ¦¦ 75 mm
18e70ce3-cd41-4e80-b2e7-cdecd621e86f | note | % Passing 0.075 mm sieve ¦¦ 0-12%
426ddf19-4a19-428c-81d9-a0976b6ba863 | note | Soaked CBR ¦¦ > 20%
56b31f61-ec77-4a26-9c02-193aec6fd96f | note | CBR Swell % ¦¦ ≤ 1.5%
3c76cdd8-3729-43ea-9684-809f18ec2000 | note | Permeability ¦¦ < 5 x 10^-9 m/s
279ea369-5031-4f1b-91e8-626b863153c5 | note | – – – – – – – – –
d5283e63-ac96-4ffb-8466-b3b6a9038e9a | note | Gradings:
c2e5e53a-5d01-4f32-a8cb-c9d3eec343f1 | note | – – – – – – – – –
e962e5c9-1583-517a-8479-ab3ac3cd2746 | note | AS1152 Sieve Size (mm) ¦¦ Percentage of mass passing sieve size
cfe1cd19-1284-5aa2-9cf8-91fea8545b4f | note | – – – – – – – – –
bed041fd-d001-5108-af09-ef0e9711b9e0 | note | 75.0 ¦¦ 100 to 100
f320a33c-f6e6-5e94-99ea-c648d595de8b | note | 37.5 ¦¦ 67 to 100
2f304236-d42e-550f-bb74-14664bc6880a | note | 26.5 ¦¦ 54 to 100
1c1acd2b-5d4c-5220-9478-f62ad2876162 | note | 19.0 ¦¦ 44 to 85
6d8636bc-a42b-5f14-9b5f-c72cb8ab9d44 | note | 9.5 ¦¦ 31 to 65
31e3bec9-ba20-56cd-8c5a-6f576fda8073 | note | 4.75 ¦¦ 21 to 50
0faee927-3dcf-5944-91aa-5c5917c5dccd | note | 2.36 ¦¦ 13 to 38
c568518d-b7e3-533f-a9a7-bc6383d1fb15 | note | 1.18 ¦¦ 9 to 30
b3f56a11-f6f1-5983-937f-1d114c23c723 | note | 0.425 ¦¦ 4 to 23
0d6d1251-8dbd-5410-b46f-a3b6e67d4b61 | note | 0.075 ¦¦ 0 to 12
d6ae7631-afe6-5798-9b1a-d28144e937a3 | note | – – – – – – – – –
040eeceb-01be-5cb7-acbf-c3f57fee68c1 | note | ○ Production testing if supplied select fill will be: 1 per 1,000t for first 5,000t, increase to 1 per 2,000t following conforming 5,000t of conforming results. If material source changes, testing to be re-conducted from start.
04ffc556-268c-52b6-b721-d92339b742b2 | note | Reference Documents - Spec 002 – CL2.5 Cl2.7.5
3ca23b7d-514d-5470-97a3-39d41093fa60 | note | Inspection/Test Method - Test Report
9c5f393c-f175-51db-9434-fda4147480d2 | note | Record of conformity - This ITP signed
8a63c909-49de-5436-b4b5-575aefd813ac | note | HP
02927e97-19f7-5fbe-a3b4-eee1b7c62d58 | note | Responsibility - Project/Site Engineer Principles Rep
da34b4ca-7a9f-578d-9c02-d4fabb27fd31 | textbox | Checked by: Principles Representative - Aconex:
071c1a9c-2607-5e67-a29d-6a65f01f5cb8 | date | Date Completed:
2851e022-b0d9-56e3-9a4e-6c082b32a0d6 | signoff | AUTHORITY HOLDPOINT
f232dced-33bb-568f-a2fa-a747fd009e10 | checkpoint | 1.5 - Select Fill Material Source (Other Locations, Site Won)
063b6ae1-0810-55a7-b6a7-6b5db22bfcbb | note | Frequency - Prior to works
258f4ebc-f34d-5d30-bd3f-22d86510d714 | note | Acceptance Criteria - Each source of select fill shall be approved by the Principles Representative.
ac6389cc-17e2-595b-b34b-dd88ffe8864e | note | Reference Documents - Spec Cl 2.6.2
719895c5-7f3e-5091-ba15-8a37bcc0b054 | note | Inspection/Test Method - Test Report
b178ae95-a6a8-5f30-a71e-77c3180b179a | note | Record of conformity - This ITP signed
5fea5191-b455-5379-a562-341e47f23a5c | note | HP
1b1175c9-563b-5f66-9a51-8150698498ab | note | Responsibility - Project/Site Engineer Principles Rep
e3e36edf-af24-4dfa-9403-05f346394d44 | textbox | Checked by: Principles Representative - Aconex:
51923049-c02d-5ec6-b16f-c5aea6323641 | date | Date Completed:
4f1faf1f-32cf-5c03-ada3-e9a28be51c49 | signoff | AUTHORITY HOLDPOINT
78804ac0-3e61-566e-8208-64cfe762ca7d | checkpoint | 1.6 - Submission of Select Fill Methodology Plan
d005a128-0585-5c5f-a4ed-dc6cd7fed680 | note | Frequency - 14-days Prior to works
7f0a4f4d-b378-5a12-b0e4-f56352981a2f | note | Acceptance Criteria - Principal Contractor to submit a Select Fill Methodology addressing the criteria listed in Spec cl. 2.3.1. Hold Point to be released by Principal’s Representative after acceptance of Select Fill Methodology.
9669e478-dd97-5343-81cd-5199ba8b11fb | note | Reference Documents - Spec cl. 2.3.2
9a4f811b-2c81-59e0-bc06-90aeeca2bea8 | note | Inspection/Test Method - Select Fill methodology & verify
7ee34b39-a2d3-5e3b-b6b4-d71bab0d7184 | note | Record of conformity - Select Fill methodolog y & this ITP signed
ab118804-4cfd-581c-a8b2-4173b3f62ba2 | note | HP
c427744c-00ec-5244-95ee-1968a0a0506d | note | Responsibility - Project/Site Engineer Principal’s Rep
3ff59667-9db9-5e0f-af41-a6422fa1c607 | date | Date Completed:
603923c1-5792-516e-9695-7b16fe07e83f | signoff | AUTHORITY HOLDPOINT
93a0280e-652b-5cbf-b020-d3fa7b051fb8 | checkpoint | 1.7 - Starting Works
191a663e-328f-5ce5-a946-a8d013cca794 | note | Frequency - Prior to works
6988de33-b3cc-59d5-ab8d-79735df2e94a | note | Acceptance Criteria - Principles Representative to approve works starting in each Separable Portion
d953518c-4665-5be5-9df4-3b5706752e35 | note | Reference Documents - Spec cl. 2.3.1
8da07ef4-0244-55ed-84cb-82af9c176d0f | note | Inspection/Test Method - Verify
9c0d8931-832c-56ec-b854-27402cac329e | note | Record of conformity - This ITP signed
01cc9dd3-f181-5d4e-b595-c5bddced1061 | note | HP
1c0dfe50-17e6-5aec-a644-70f7bd58cd85 | note | Responsibility - Project/Site Engineer, Principal’s Rep
f8c8d075-b3c2-428c-b172-8159d39d679b | textbox | Checked by: Principles Representative - SP8 Aconex:
b154fc99-0a6d-550d-b606-cf95d0f9bece | textbox | Checked by: Principles Representative - SP9 Aconex:
5e843dd3-b3d2-5eb4-9338-9d3baeddc93d | textbox | Checked by: Principles Representative - SP10 Aconex:
ed099b5c-abd0-5fc3-bf77-6287326c1569 | date | Date Completed:
59b60230-39ed-59c3-b78a-fb4e61c6129e | signoff | AUTHORITY HOLDPOINT
c558d9a3-521a-5d48-b5a0-ab318534cad4 | checkpoint | 1.8 - Preparation of Underlying Surface Layer
3fd33117-7eb2-586f-aa85-c38c3a5e3e4e | note | Frequency - Each lot
d49700fe-80cf-52d1-b05b-5a9dd1b1a079 | note | Acceptance Criteria - All excavation and filling are free draining to low points clear of the working area. Sufficient pumps, well-points, or other equipment for work area are de-watered as required.
29337356-89d0-56e5-9ce6-bb65769f6fa6 | note | Reference Documents - Spec cl. 2.8.2 ITP003
be289948-f406-5e5d-aa09-44a86a08572d | note | Inspection/Test Method - Verify
6554c8ee-bac9-53ad-8ac4-0c6a0f9b9336 | note | Record of conformity - This ITP signed
509f5b45-e354-5884-871e-a14c5219f88e | note | IP
a8de60f0-59c1-5c31-8c97-7ab7c45d6531 | note | Responsibility - Project/Site Engineer Foreman
843759f7-5dbd-5c16-aced-bd975265065d | date | Date Completed:
fe92d223-db1f-56f0-9a40-9bee7d494c9e | checkpoint | 1.9 - Cut Floor Level
6c8d8f56-6505-5557-a082-4e1a61cb67ac | note | Frequency - Prior to works
e41bf1b5-9786-5635-8da4-452b93549516 | note | Acceptance Criteria - Cut floor to be inspected for suitability - compacted, firm and dry
b5ec83c9-941c-5393-a618-6317d028adb3 | note | Reference Documents - WMS003 cl 3.3.3
4d0e6c39-2d95-58d1-8054-9ff4a0c20dc4 | note | Inspection/Test Method - Verify
1357443b-4fe8-50f2-bc24-5754a41f44d2 | note | Record of conformity - This ITP signed
8ca3c972-2063-5790-8b54-d410a0ba7407 | note | HP*
47799b55-8c62-5420-b582-d3bfe6e9728d | note | Responsibility - Project/Site Engineer Foreman
a61bf0fe-c74c-5468-8b07-734f781a523f | date | Date Completed:
956d87eb-1ea3-5a3b-b0ad-217a98aa1992 | section | 2.0 - Select Fill Works – Imported Material - Under Pavements
49f2c445-65d8-595e-a8e7-1a7107a4605f | checkpoint | 2.1 - Select Fill Placement
a285683c-8b89-5d00-8ee5-7dd4aed4cce1 | note | Frequency - Each Lot
1088eff9-1f90-59a7-b41b-14d0f0ad1908 | note | Acceptance Criteria - Each Lot of fill must:
76abb573-0b41-5839-8ab6-8f3a78d19147 | note | ○ Not be greater than 200mm in thickness
c7e45ad8-2f77-5838-8b90-c5dfcf3d6e79 | note | ○ Material is to maintain within 1% of the optimum moisture content during all steps of placement, compaction, and finishing
678a7288-b1b6-53dc-b1f4-3c67e7ce5832 | note | ○ Placement of material to commence at the crown or the highest side of the pavement, with each lane spread adjacent to the previously placed lane
6db7de3f-3c47-57c9-8429-27b32fabba9d | note | ○ The first layer of placed material is dropped and spread using a dozer, grader, or similar plant to prevent trafficking 7mm seal
af09624f-e3c1-5797-9314-8274a1c59ed7 | note | ○ Material to not be contaminated by foreign materials and other contaminants
dea3f41c-156d-5b00-bb00-1ff047c6fc4b | note | ○ Plant and equipment does not traffic 7mm Aggregate Seal
3dbc7cb7-6509-580f-91f9-e9a368e88d35 | note | Reference Documents - Spec cl. 2.8.4
f4e6e6d0-2488-542e-a580-ab6ff313a746 | note | Inspection/Test Method - Verify
255c8a3e-d31e-5112-864d-8f0b1a95a4c9 | note | Record of conformity - This ITP signed
cbb35942-afe0-5989-8175-5db882b1f056 | note | HP*
5f20e431-67c6-5049-94d6-bf6ddc20f219 | note | Responsibility - Project/Site Engineer Foreman
d8351717-5829-52da-9630-21fa92547fd8 | date | Date Completed:
cd06c634-3b25-54fe-9f17-72e175164dd2 | checkpoint | 2.2 - Proof Rolling & Compaction
f6bcdc13-2b29-5e73-a520-feffb5a5ff4c | note | Frequency - Each Lot
e256642d-13d3-5932-b4a9-3a0ded3bfdae | note | Acceptance Criteria - Each layer of select fill under pavements is to be inspected with the Principles Representative.
d7d39b8c-6eb2-537e-8c6f-760b58edb6fe | note | ○ A medium size vibrating roller (or larger) is to be used for all proof rolls.
ba9f68a4-a645-56b1-abbe-2ce5f7244fd2 | note | ○ At least 5m of longitudinal Select Fill and 500mm of lateral overlap of proof rolling between adjacent areas is needed.
4f3eb4f4-7107-5840-9dee-53fc6614bbc9 | note | ○ At least one working days’ notice is to be provided to schedule the presence of the Principles Representative.
24ebd48e-de5b-5a02-b3d8-bd75dd473447 | note | ○ Maximum allowable rutting of 25mm.
8400133a-8770-5d5c-aa61-6afb25a99e31 | note | ○ No heaving to be observed.
d47c6d07-a0d7-4b4c-a959-37094aa81598 | note | ○ Proof rolling of the select fill will be approval to place Sub-basecourse or Basecourse. If rain falls on select fill prior to placing next layer, a further inspection will be required.
aa8ce4a4-dfad-50ae-9679-f4a320171abc | note | Reference Documents - Spec cl. 2.10, Spec Cl 4.6
43d9517b-b833-59e1-a928-f0e9191db911 | note | Inspection/Test Method - Visual Inspection & Verify
007a5866-30c6-5e94-9f7b-eda3d6be2915 | note | Record of conformity - This ITP signed
75d45070-7e38-5e90-be33-a40b6c4d25f9 | note | WP, HP, HP
1035b6bc-5313-55a3-89f8-247dc8516c36 | note | Responsibility - Project/Site Engineer Principal's Rep
e74b8669-4382-5781-a35f-13ab9e7a638b | date | Date Completed:
f9d3f337-d7df-5819-a509-9fab63543ffa | signoff | AUTHORITY HOLDPOINT
c2466015-5915-51a9-8eca-423a20554634 | checkpoint | 2.3 - Final Trimming and Surface Finishing
b969e5f6-98cc-5976-a1db-96e747fccfd0 | note | Frequency - Per lot (final layer only)
c5073318-1d2b-5d22-8b0a-7bfc85218377 | note | Acceptance Criteria - Final layer of Select Fill surface to the required level, grade, and shape with a tolerance of +0mm and -25mm. Intermediate layers of select fill do not require a Survey Conformance Report
bbcd9e54-00b8-5001-8b05-4da4db95e2bb | note | Reference Documents - Spec cl 2.11 WMS003 – cl3.4.5
cb48011c-a1e9-5dfd-ae7d-68851eeacc67 | note | Inspection/Test Method - SCP
61bdba24-af61-5bcf-8e88-65004e5e2603 | note | Record of conformity - This ITP signed
cbc322f2-a319-54e9-95bd-9652bfb5dd3d | note | HP
d843fe42-ddf3-58e3-b760-959cd61a1cff | note | Responsibility - Surveyor, Project/Site Engineer
5f10bc1c-6362-5c7f-b1df-be0007331eb8 | date | Date Completed:
c0aade32-64a8-5f42-87c3-c0ceb97e85c1 | signoff | AUTHORITY HOLDPOINT
480a09e0-ea92-5938-b3d2-6cc734b0994e | section | 3.0 - Select Fill Works – Site Won Material – Other Areas (Not Under Pavements)
611c3468-2940-5641-8ce8-27310ad03598 | checkpoint | 3.1 - Select Fill Placement
dd600633-1855-5efb-aa7a-b22b1a16b9ad | note | Frequency - Each Lot
6cf86ae2-1ebf-5597-a601-ce96a64e12c9 | note | Acceptance Criteria - Each Lot of fill must:
5c46b0da-a8eb-525b-805d-7a15fe1ddb17 | note | ○ Not be greater than 200mm in thickness.
ff7b2559-af03-547a-9188-aff61a7ed3ad | note | ○ If required, material to be lightly watered to aid in compaction.
164428fd-9f41-5a84-989b-371e5ef907e5 | note | ○ Placement to start on the high side.
606c0f40-6a0a-5a36-a25b-d94b5802f1b9 | note | ○ Material to not be contaminated by foreign materials and other contaminants.
595e330f-84d7-5d07-bdd1-f36f30d40394 | note | Reference Documents - Spec cl. 2.8.4
261751eb-649e-54fc-858d-2c38f03f9163 | note | Inspection/Test Method - Verify
6a4957a0-b9ab-5808-9006-ec62b9ccf935 | note | Record of conformity - This ITP signed
84c8b8d1-03dd-59e6-9d99-6c4ff276b04f | note | IP
2a1f2666-ba88-513c-b479-bda9af6ebe9e | note | Responsibility - Project/Site Engineer Foreman
3cd2359e-478d-5a7c-937b-723ea792aa09 | date | Date Completed:
1bfe831d-057d-54d6-9332-9df26d5d643a | checkpoint | 3.2 - Proof Rolling & Compaction
61716091-7ff1-53da-be97-6525d3ab0d02 | note | Frequency - Each Lot – intermediate layers
0e621325-bc78-538e-9d1c-ad5c898e2500 | note | Acceptance Criteria - Intermediate Layers
7eb80e75-eeda-5830-bbf2-877aa402d695 | note | ○ Each intermediate layer will be visually inspected for conformance to the specification following compaction.
16d757da-361e-5a78-a738-deaa432d1861 | note | ○ No rutting greater than 25mm observed
de4e646d-a05c-5dcd-bdaf-e12065b7296b | note | Reference Documents - WMS003 – cl3.4.4.1
1121916d-79fd-5972-b23d-a650ab4d24a8 | note | Inspection/Test Method - Verify
1c5f4405-0f62-5fb5-8c5f-310627cbe0fb | note | Record of conformity - This ITP signed
554a3ed7-20f7-5e35-83f7-6728a552da00 | note | HP*
e63bbe64-3698-541a-9ae4-d8da7237141a | note | Responsibility - Project/Site Engineer Foreman
ccaaa446-44ab-5a1a-af6f-eff82876dee0 | date | Date Completed:
59b6de6f-36db-4e4d-808a-997b73e3906b | checkpoint | 3.2 - Proof Rolling & Compaction
c08bae98-5572-5c0f-bc54-6c2e4e967af5 | note | Frequency - Each Lot (final layer only)
c5d002ec-66be-5b68-8f97-eae95a2aed15 | note | Acceptance Criteria - Final layer
546f7143-3279-5d94-9daf-380e3a1eaf5c | note | ○ Principles Representative to be invited to visually inspect final layer of Select Fill not under pavements.
333ff332-9e8b-5a29-a97a-d2e1c8e1531e | note | ○ At least 5m of longitudinal Select Fill and 500mm of lateral overlap of proof rolling between adjacent areas is needed.
5d380afc-eb96-5670-9bfd-668848f80509 | note | ○ If requested, Proof rolling is carried out in the presence of the Principles Representative
d960ea35-51db-573f-89d1-ce44c75a5cac | note | ○ If requested, at least one working days’ notice is to be provided to schedule the presence of the Contract Administrator.
b49298b2-d1ef-5f42-8be4-cf51205e8922 | note | ○ Maximum allowable rutting is 25mm.
af69c2c0-630e-5064-96fa-814131dd5fee | note | ○ No heaving to be observed.
b59bcabf-c714-52e2-92ff-fa9244039adc | note | Reference Documents - Spec cl. 2.10 WMS003 – cl3.4.4.1
381fbbab-cc3c-5605-9803-bee173c2d21b | note | Inspection/Test Method - Visual Inspection & Verify
716b97f9-32ec-58ce-8d4f-8e536b454e40 | note | Record of conformity - This ITP signed
93ca3368-b935-5713-9776-0469b8471dbd | note | WP, HP, HP
5c34c3a5-4097-5295-a686-eb8106c9fb84 | note | Responsibility - Project/Site Engineer Principal's Rep
40dbf905-4676-5e94-ae72-655a8ae24718 | date | Date Completed:
4059a6fb-81ea-5f9c-a1ce-717bd26edeb7 | signoff | AUTHORITY HOLDPOINT
f7b45ac7-7370-5e15-b918-9d991e274492 | section | 4.0 - Testing & Acceptance
670307a5-96f5-566b-91dc-2ebfaa94544c | checkpoint | 4.1 - Classification and Testing (imported material, under pavements only)
497bfaa0-6206-5775-81af-233539a11d92 | note | Frequency - Each Lot
271fc17f-30a4-59e8-bbca-65edc4f02acc | note | Acceptance Criteria - Imported Material Under Pavements
27355161-24bb-5967-93e9-dda843f4ba98 | note | – Dry Density as per AS1289.5.3.1
3179e986-b82b-5056-98ff-4aabbe83c0dc | note | ○ 4 test per lot to achieve average
e64042f7-dd1c-50be-926d-7c64a5cbf840 | note | ○ Minimum average standard dry density ratio of no less than 98.0%.
fdb3a14a-9a9e-55d1-ab92-eb781d5eda6f | note | ○ No single standard dry density ratio test result being less than 97.0%.
4dfaf25b-ec5f-5a98-b76f-018000e525bb | note | Reference Documents - Spec cl. 2.9 AS1289 5.3.1, AS1289 5.4.1, AS1289 5.8.1, Spec tab. 2-3
cde87d4d-e124-5808-9805-530b6d47ec39 | note | Inspection/Test Method - Verify
20e31860-c7e0-59f1-bbe5-e62b5343e90b | note | Record of conformity - Test results & This ITP signed
fec63964-1ec3-5c2e-b894-f48a5a9eee1d | note | HP
befcf3c6-d0dd-5b27-b626-a9a33bf6131f | note | Responsibility - Project/Site Engineer, Principles Rep Foreman
57cd6c31-ace6-54db-9b2e-2802c5fd7311 | date | Date Completed:
23824eb6-508d-5398-b1e5-f8ed54d7b2ad | signoff | AUTHORITY HOLDPOINT
ecd1a6b2-d49b-594c-8bb7-55abdcbc9c40 | checkpoint | 4.2 - Lot Acceptance
fd6d64c3-6ffb-527d-8b4b-bcb152ea8af2 | note | Frequency - Each Lot
6094e51b-56c8-55be-81e7-ccc9388928af | note | Acceptance Criteria - Principles Representative to review acceptance of lot according to table 2-3. Acceptance of lot will not hold up placing succeeding layer of subbase.
2da0f362-8c08-58fe-9a83-451b169eb89d | note | Reference Documents - Spec Table 2-3 Cl2.12
5cadbf22-2e7d-5c0b-8f81-bb24150c0f16 | note | Inspection/Test Method - Verify
5317b649-84e5-5a25-8ad7-23504448e577 | note | Record of conformity - Test results & This ITP signed
565abba3-17d0-5afd-9e87-56fb95d8fbf4 | note | HP
c23be552-5ce0-5137-bd63-cde77864010b | note | Responsibility - Project/Site Engineer, Principles Rep
f8286b5b-50b2-5dec-af24-fffc837e80cd | date | Date Completed:
39d52e64-abdd-5af5-bc89-31082ce50170 | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
c99016f3-cb40-5a62-aebc-b4d7bb465048 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
f2bc87cb-c91c-5291-95da-3deaa91d47f1 | textbox | Print Name:
997fdfdb-a196-5436-9205-97836b076b0c | textbox | Position:
68dcca9c-d28c-529d-b4b1-3ceac23b94e3 | date | Work Completed On:
2181d0aa-ae54-5dfc-8386-981fe6cd1902 | date | Date:
eacdf556-7493-5d31-8b67-b3ac4559ccfa | checklist | FH-ZU2-QU-ITP005 - Stormwater Drainage - Rev 1 | itp | ITP005 - Stormwater Drainage
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
54e098fd-2875-533c-ae63-868a90e30081 | note | Frequency - Prior to commencing activity
3a9488af-ceef-526d-a9e6-e8a30e966b9f | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
471f36d6-b4b4-5388-a9d2-5ae7ece93b5f | note | ○ using the correct and complete set of drawings
8f7a1599-66cb-573c-9016-a55fbc589bc8 | note | ○ all drawings are the latest revision.
c2e5a589-5901-5b02-9701-76e4ce132a9a | note | Reference Documents - Drawings and Aconex Register
a2ee1067-eb31-532d-8b47-6005b527fbc3 | note | Inspection/Test Method - Visual Inspection
bfafb1b0-e9c1-591c-b5de-dc2927d5d9b0 | note | Record of conformity - Up to date drawing sets & ITP
839ea919-c7d7-547f-a4c5-a127348d8a0e | note | HP*
95bf2957-8d71-57ca-98d9-f701505fe279 | note | Responsibility - Project/Site Engineer
16f17a8f-429d-5221-b86f-2a3ff34b50bc | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
2b1c2541-a2e3-53ee-acdf-59d7d816963e | note | Frequency - Prior to commencing activity
56e020d7-7c16-5716-9b87-daa768345924 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: CEMP, TMP, SWMS & WP.
bc2543d4-aa2d-54cf-a7b6-1c651c7eef89 | note | Reference Documents - CEMP, TMP, SWMS & WP
b2945d35-791b-5282-9eab-f1096aae2e5c | note | Inspection/Test Method - Verify
6743976f-a864-5448-8b47-d3bd43ab57a1 | note | Record of conformity - Site and Office Inspection
f3bde6b2-9eeb-5f16-a6fd-7ab73df5c502 | note | HP*
7247c46e-49a4-5101-afd6-c19f89422b74 | note | Responsibility - Project/Site Engineer/Supervisor
a959ad58-ba7b-515e-934e-cfe533042728 | date | Date Completed:
ddc68377-ad92-57e5-8ab0-c671f713640c | checkpoint | 1.3 - Excavation Permit
67c58622-d040-5817-8e40-c14ba3c81201 | note | Frequency - Prior to commencing activity
858c6e33-5f6d-5f36-b9be-131e6512679b | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
d89748f0-3fe4-5f6e-bd16-db487ca14c10 | note | Reference Documents - Excavation Permit
5ac316e1-5683-5604-bf46-2f6aa45e1fe3 | note | Inspection/Test Method - Verify
2a3b06da-8a9d-55ae-a1b3-00d7413308e1 | note | Record of conformity - Proof of signed permit
62992194-6156-50b2-81f9-ef93471b5596 | note | HP*
11702d77-2c52-5332-81a8-f6e2b636d283 | note | Responsibility - Project/Site Engineer
5da7027f-4163-53a4-8cf3-0db8251e49d5 | date | Date Completed:
8a938930-5b81-5c2a-981f-3429c2180500 | section | 2.0 - Stormwater Products and Materials
5f7ce117-da10-5b8f-8bce-12ebc1eaf9df | checkpoint | 2.1 - Drainage Pipes (RCPs)
41d9fad8-a375-534c-a828-f397d7515358 | note | Frequency - Prior to commencem ent of works
6f00cc3b-c4a0-5f15-b5f6-bf98b9efe43f | note | Acceptance Criteria - Drainage pipes supplied in accordance with AS4058.
bb56e26e-19e7-566c-ba5d-74cdce66240b | note | ○ Material submission approval.
b162d0c8-25a1-5911-b3f4-0422cfa98d99 | note | Reference Documents - CL16.6.1
8228597f-c73b-526f-af9d-351be9066490 | note | Aconex ref: DCWC Mgt-GCOR-009281
25943020-9f4e-5ca1-bb79-37472b1edede | note | Inspection/Test Method - Document Review
ad6d63b5-fe57-5348-bd57-1d841f377ee4 | note | Record of conformity - Aconex
d8eba816-e46c-541d-aec8-fefd40c15961 | note | HP
57487e94-4c41-5a5e-8e96-638ad350df34 | note | Responsibility - Project/Site Engineer, Beca
179683db-9a8d-5462-955f-c7ee24fced30 | date | Date Completed:
e3753df8-916f-5363-bbda-b521a4126ecb | signoff | AUTHORITY HOLDPOINT
1b2eb359-4c69-5a42-8120-5367c623b1bb | checkpoint | 2.2 - Pipe Support Cradles
8d618c69-5b5e-5645-817f-836c8e834b02 | note | Frequency - Prior to commencem ent of works
9c03adc9-e7de-52a6-993c-ccf61071cfe7 | note | Acceptance Criteria - Pipe to sit on firm foundation with pipe support cradles.
cea46deb-31cf-5803-af12-5fe92b2db20f | note | ○ Material submission/ Shop drawing submission.
b213bf5e-eb9c-5753-b606-7d40d87cd7e4 | note | Reference Documents - Cl16.5.6.1
a40cf2e5-0db3-51ea-b1c4-75fbd7cbc6d1 | note | Aconex ref: DCWC Mgt-GCOR-009496
076afd1f-35a5-5927-a7fc-edd5de7cec1e | note | Inspection/Test Method - Document Review
3a0220cb-cceb-5803-a539-4a7b71938cac | note | Record of conformity - Aconex
5acb6203-0f4b-5ceb-886a-84cdc070e164 | note | HP*
ec6daf90-e504-55df-a72d-5737e28ea03c | note | Responsibility - Project/Site Engineer
ee87f83a-c632-507e-9a14-1ea8ce2dcacd | date | Date Completed:
71c61f1f-7bf6-51f7-9473-621c8a53ddd0 | checkpoint | 2.3 - Encasement Material
046121b9-b4f0-54f0-8a63-31d5a43a9243 | note | Frequency - Prior to commencem ent of works
cfed6de3-a0e4-56e6-a0f6-bd5a01012fcb | note | Acceptance Criteria - Encasement Material to be 5Mpa lean mix concrete for all RCP’s.
75304e44-4159-53f3-9435-58d198c06a7b | note | ○ Material submission approval.
549db1d7-fd4a-5eab-b6d1-07156f91fe49 | note | Reference Documents - Cl16.5.6.1 & 16.6.2.2 & Tender Clarifications #36
eb1080aa-021d-5be6-b979-d353ecb13764 | note | Aconex ref: BecaCPL-RTRFI-000089
1ed1078f-fff6-57f8-b1e1-0cf5460b2dd8 | note | Inspection/Test Method - Document Review
42d9471f-bd13-5359-b02c-cf38eb141023 | note | Record of conformity - Aconex
be559595-6804-5b57-ac83-af45fe1f80c8 | note | HP
2e927600-b0f8-50f9-b5ef-90d1180e4339 | note | Responsibility - Project/Site Engineer, Beca
378e34be-3bd9-5bee-b76f-f57c9a9a2a99 | date | Date Completed:
d52c4130-ee00-55e4-80f9-ae18f97deb84 | signoff | AUTHORITY HOLDPOINT
ea30ceb6-447f-5f06-879d-cf20a33d83c1 | checkpoint | 2.4 - Backfill Material
fa1e2509-551b-53e2-b3e4-40cc2b17a126 | note | Frequency - Prior to commencem ent of works
00ce685d-1629-5606-af60-85e42324d169 | note | Acceptance Criteria - Backfill material to be 6% cement stabilised sand to pavement formation level or approved otherwise.
b7edf96b-f4dc-56ba-a385-62c46425914d | note | ○ Material submission approval.
1269190a-dcff-5390-9084-4e405c70093c | note | Reference Documents - Cl16.5.6, 16.5.6.3 (a)(i) & 16.6.2.2.
f4389ac0-ef80-594f-bf52-856b6d8aa05b | note | Aconex ref: BecaCPL-GCOR-000802
62c05dc6-f5a7-5245-b8ba-0b49ce5d172c | note | Inspection/Test Method - Document Review
1449f01c-c4aa-5c77-aa84-5af40b4e64e8 | note | Record of conformity - Aconex Ref
affd4a93-a921-5aa2-8cd0-44c441e6648d | note | HP
fd9f3fa5-4bfc-54a0-8e72-7bffd8a90810 | note | Responsibility - Project/Site Engineer, Beca
c7981258-9841-5a6b-88cc-4a9f38a7f6e3 | date | Date Completed:
f9b66524-c85f-5e85-aa46-2367e78ebd6e | signoff | AUTHORITY HOLDPOINT
b45f932a-0d12-5d1d-ac10-211cdf6d5105 | section | 3.0 - Stormwater Delivery
6d60dbb5-efe8-5503-9c41-8894fa297110 | checkpoint | 3.1 - RCP Delivery
88e5903e-8133-58e3-8e64-8e8887c3b17a | note | Frequency - Each Delivery
9ab65ed4-0c52-5684-b951-353241be59b1 | note | Acceptance Criteria - Drainage pipes supplied and delivered as per approved Material submission.
041fa456-d7d6-5468-88a3-8afbf07b794a | note | ○ Manufacturer’s conformance report.
325517ec-3131-5c6c-8485-ad1ddfe7f2ff | note | Reference Documents - CL16.6.1 & AS4058
4f86dc35-1ead-595a-963f-52d63f59fb27 | note | Inspection/Test Method - Verify
6c5cabb9-9f3b-5c37-b5c0-8304d309bcb3 | note | Record of conformity - Order Acceptance Form
5f4e3bae-bc6b-59ba-969b-1387a4915c0c | note | IP
fdf5360e-5800-577c-ad9f-ffc483d77ba0 | note | Responsibility - Project/Site Engineer
67bc3511-85af-51e9-a897-ae6d65695009 | date | Date Completed:
f12fff67-318b-5116-a2de-09fa37e1377f | section | 4.0 - Construction Activities
5c6df739-5258-5ade-9921-36b1301c399e | checkpoint | 4.1 - Survey Setout
184b7804-94df-5c10-9503-064b7e236985 | note | Frequency - Prior to construction and each lot
74e80b21-7b41-5c14-8fd1-0aaea06ed169 | note | Acceptance Criteria - Set out the stormwater drainage as shown on the Drawings to identify the locations, lengths and levels at outlets and inlets of pipes.
c997444a-d4ec-5293-9985-137593984628 | note | ○ This constitutes a Hold Point.
45c2e80c-419c-5521-b8b4-d3401d87004b | note | Reference Documents - Cl16.7.1
f12f3715-d50d-5ab2-ae65-f56d39c25ae4 | note | Inspection/Test Method - Survey
572ef53e-e8d6-50be-be91-ee3ee56e43f0 | note | Record of conformity - ITP Signed
39a0f67d-1725-5c40-9a71-dcb48f857a75 | note | HP
54ba654f-6272-5c0d-b9e1-ea03ebe60ed6 | note | Responsibility - Project/Site Engineer, Beca
fa4a235e-3294-560d-8789-a3d08c871e5a | date | Date Completed:
ff9f951f-7476-5d3f-ba8e-80db7c677589 | signoff | AUTHORITY HOLDPOINT
e4eb01cf-d31f-52a8-b825-5b5a10cd54a0 | checkpoint | 4.2 - Excavation
ae9b32ec-7fff-5d0a-9424-24163091f7a9 | note | Frequency - Each Lot
4d6accd7-8604-53a9-ba80-22e6de486899 | note | Acceptance Criteria - All excavation to be performed to the minimum depths, widths and batter slopes as shown on the Drawings, regardless of the type of material.
923600d7-e22b-5c6b-b9b3-98e96bec5038 | note | ○ Trench excavation is to commence at the downstream end, where practical.
c06bac9c-d541-57f4-9632-d0d3b38d1659 | note | ○ The width of trench to be such that the horizontal clearance from the outside of the pipe to wall of the trench to be minimum 300mm when under the runway and taxiway graded strip. Trench width outside of the runway and taxiway graded strip to be the greater of 150mm and D/6.
f20b6792-e317-56ec-9aab-88b5226f314c | note | ○ Subgrade Inspection to constitute a Hold Point.
107547f8-aa65-500c-ae0e-13c46097e260 | note | Reference Documents - Cl16.8.1 & Cl16.6.2.2
b4c9308b-6d7f-54c9-bb86-94b073803c26 | note | Inspection/Test Method - Verify
e4767b4c-5011-58e6-aed5-79760c673c48 | note | Record of conformity - ITP Signed
2ed83b9e-e250-51d5-9d5f-c97d45d2ec14 | note | HP
68cabd5c-0e9e-5d91-acd3-bdee66617bbb | note | Responsibility - Project/Site Engineer, Beca
a9d66231-9287-5067-8242-cbb0f31407c8 | date | Date Completed:
ff5e91b7-5a2a-57f8-87eb-01651d3a2682 | signoff | AUTHORITY HOLDPOINT
af37bbcb-ba49-5b6e-8c2b-a91b2ba28f0b | checkpoint | 4.3 - Site Dewatering
e99776f6-6cf4-5503-9c98-dd1a53bdacac | note | Frequency - Each Lot
389dad6e-d921-5c6e-84c1-f0e86313a748 | note | Acceptance Criteria - Excavations are to be kept free from water during construction and backfilling and provide pumps, well-points or other equipment as necessary.
b278c28b-7740-546c-9834-724a125c10a8 | note | ○ Any temporary works to be designed such that flooding upstream of the diversion does not occur. This constitutes a Hold Point.
c55d97ae-880c-5161-913e-dea6114660c2 | note | Reference Documents - Cl16.8.4
da00b571-a482-5590-8ee3-bbb311c60c04 | note | Inspection/Test Method - Site Inspection
93d02277-da10-5973-8a27-3ffba730c5a5 | note | Record of conformity - Aconex Ref BecaCPL-GCOR-000891
a7d77778-30f4-570c-a3f4-92e9ce0195a3 | note | HP
c829d6c5-3da0-555f-99f8-f98c7d2adf74 | note | Responsibility - Project/Site Engineer, Beca
8e733820-540c-5f3f-ba59-1d720e847f55 | date | Date Completed:
158e35e2-fa25-5a50-831f-0658256d25c8 | signoff | AUTHORITY HOLDPOINT
7ede9ad6-dd5b-5212-896e-f145ac8b730f | checkpoint | 4.4 - Confirm Ground Conditions
c24d7f4c-211d-512c-8f62-fb8c74c5f909 | note | Frequency - Each Drainage Line
1f1e2149-09a6-5a8a-bf8e-05bcf9343e0e | note | Acceptance Criteria - Min. 1 x DCP test to be undertaken per drainage line / structure to confirm ground conditions. If the first DCP is inconclusive or fails, additional DCP to be taken as needed based on on-site assessment of the ground.
03f1408a-fcfa-59d9-9794-c463a54760c7 | note | ○ Contractor to notify the Contract Administrator of any area of the foundation which contains material that is inadequate to support the proposed drainage structure.
21488094-6570-5bb8-b7d2-27530887acab | note | ○ Inadequate material is deemed to have a bearing pressure less than 130kPa, equivalent to 4 DCP blows per 100mm, per note 4 on drawing ZULU-BECA-012-DWG-07102.
242cba19-a3d8-5f42-88f9-69b17170d46f | note | ○ Inadequate foundation material is to be replaced with a layer of coarse crushed aggregate compacted to 95% relative standard compaction to AS1289 Section 5.5.1 over a geotextile Bidim A29 or approved equivalent.
a504a46e-b0eb-5c9d-97d2-012af669a2a0 | note | Reference Documents - Cl16.8.2 & Tender Clarification 179
b45513b3-79a1-56a5-ad23-95b269d572e3 | note | Inspection/Test Method - Site Inspection
920754ad-5496-5649-ac23-cc159d334d41 | note | Record of conformity - DCP, Test Results
19a4ccca-6f42-515d-a026-65b358677d48 | note | TP
e0837cd8-3bb2-5877-86de-a5278106923e | note | Responsibility - Project/Site Engineer/ Beca
a252e786-e6c8-54d0-8b34-75422fb024b4 | date | Date Completed:
323efbc6-a12c-5e89-ae8a-d285ad22322a | checkpoint | 4.5 - Bedding
61b37c59-fb70-5d0e-a698-20adcac2ec80 | note | Frequency - Each Lot
af9fe81b-be0f-51af-9fc1-0aa0674506f3 | note | Acceptance Criteria - Bedding material/subgrade to be prepared for laying the pipes. Pipe support cradles to be placed on firm bedding. This constitutes a Witness Point.
a494ec9f-64b2-5c1a-adbb-3d56b1681edc | note | Reference Documents - Cl.16.6.2.1
3dbef3ef-2cbd-5041-8907-f8b8307af3a2 | note | Inspection/Test Method - Visual Inspection
1956b3b1-4e04-5e3e-9732-44247b2e39cf | note | Record of conformity - ITP Signed
b97739b7-6d89-55a2-b679-4865132d3009 | note | WP
092f1bf4-ab52-5aea-8233-0f976053f229 | note | Responsibility - Project/Site Engineer, Beca
d2238a42-f78c-584c-9962-043e884ad5b2 | date | Date Completed:
f4714e5d-4d40-5cef-833b-c6bd246f4dd3 | checkpoint | 4.6 - Laying of Pipes (Sample)
b0f015fc-6552-5b29-bc8d-4109aaefe0fa | note | Frequency - First Lot
fdcea21a-b0f1-5a9e-9488-f4881b37681d | note | Acceptance Criteria - Initial sample 20m length of concrete pipeline to be laid and approved by the Contract Administrator for line and level before continuing construction of pipe network, Hold Point.
8154e474-aae9-522a-bb86-a36adaf49a47 | note | Reference Documents - Cl.16.9.1.6
ff430c75-267d-5dc4-9bb9-27ba336032d5 | note | Inspection/Test Method - Verify & Visual Inspection
c912703c-040e-512b-9f93-f947c2067b52 | note | Record of conformity - ITP Signed
0a819ca1-a073-554e-b852-5981530c427d | note | HP
45418fb0-ad6f-55e9-bb76-4c331754f30c | note | Responsibility - Project/Site Engineer, Beca
364dcce2-0e59-5280-b67b-e0c39dfd3bbe | date | Date Completed:
f6289789-09b6-5389-8687-34863a6d111e | signoff | AUTHORITY HOLDPOINT
afa0a0c6-8f35-51b7-8ae2-75ecdc349b39 | checkpoint | 4.7 - Laying and Jointing of Pipes
55ab6429-192d-55db-90d1-e22d55d14f86 | note | Frequency - Each Lot
7ff6eaa5-759b-58da-bcda-b470e99c9620 | note | Acceptance Criteria - Concrete Pipes to be rigidly supported by approved steel pipe cradle during laying.
1ab0c57c-d867-51c9-805d-1cfba53d82cb | note | ○ Pipes to be placed with spigot end facing downstream.
6fe829fb-2d02-5890-ba73-92b42ff58f96 | note | ○ Pipes to be laid with the word ‘TOP’ and or lifting holes uppermost. Lifting holes to be plugged after installation.
3f96e12c-a485-5858-aabe-f2cf56590f05 | note | ○ All Concrete Pipes to be checked and subject to the approval of the Contract Administrator prior to commencement of backfilling, Hold Point.
2fcb497d-7650-53d4-a543-98138cafc299 | note | Reference Documents - Cl.16.9.1.6
eaf88d90-0d84-5b9d-9e63-fcd1e3dd790c | note | Inspection/Test Method - Verify & Visual Inspection
4ad99015-63ff-5ef0-baa5-e0c2fe2c7d66 | note | Record of conformity - ITP Signed
6a597174-ca65-5552-882a-99ff143fd83e | note | HP
c92309d5-ae3a-50f4-9998-027105030665 | note | Responsibility - Project/Site Engineer, Beca
e2eaa18f-509d-5079-a636-1319ae775611 | date | Date Completed:
d20dc25a-fc90-5eff-8bc2-8dcc4456488e | signoff | AUTHORITY HOLDPOINT
5ad7c8ca-97a0-5547-8ef2-3f3b02311170 | checkpoint | 4.8 - Survey
19ba0200-7d70-5c1c-9869-0b767944f1c9 | note | Frequency - Each Lot
ba84b8bd-9cfc-5c75-8319-359bfbd60ead | note | Acceptance Criteria - The alignment, level and grade to be checked on the obvert of every third concrete pipe unit.
051e0e72-b396-5bac-8001-2c429bd84e51 | note | ○ Pipes shall be laid to the lines, grades and invert levels shown on the Drawings. No deviation shall be made without the prior approval of the Contract Administrator.
3bcbb87d-38bc-50b8-854c-b22cd0532cd9 | note | Deviation from Invert Level
9cfa4cdb-4a32-599c-897b-a0be107b8529 | note | ○ Maximum deviation from design invert level to not exceed 20mm and not result in zero grade or reversal of grade in any length of concrete pipe.
b404e9c4-7ff7-5ee3-9781-a07bfd70a889 | note | ○ Where the design pipe grade is less than 1%, maximum deviation from pipe socket to pipe socket does not exceed 20 mm.
bf35ce05-4c92-599f-848f-79c69bdded2a | note | ○ Maximum deviation from design invert level between upstream and downstream structures to not exceed 20mm and not result in zero grade or reversal of grade in any length of concrete pipe.
8ab47876-2624-553a-a091-f979dbe03713 | note | Deviation from Alignment
8746020d-7933-5d0a-94d6-715b8f5b708e | note | ○ Maximum deviation of the concrete pipe from the alignment shown on the Drawings to not exceed 25mm.
00bf8704-8b53-5f6d-90eb-dbeac1b3f060 | note | Reference Documents - Cl.16.7 & 16.9.1.6
98e36215-0999-5d5f-b355-ee54b245c97c | note | Inspection/Test Method - Survey
45d4783a-a78e-5de2-a1e9-a5aaae115305 | note | Record of conformity - Survey Report
e8c5c51b-7c73-5362-bbab-5bc699b81f75 | note | SCP
ec49249a-59ed-5f71-bd09-36378a6def97 | note | Responsibility - Project/Site Engineer
29281e2a-c5e9-596e-a91c-3ba3578fbc68 | date | Date Completed:
a21a4ac7-d74f-52f9-80a8-ed14b5804858 | checkpoint | 4.9 - Backfill Materials
d330036d-185e-5e46-8366-c2c7f4b375fe | note | Frequency - Each Lot
c465880e-2673-5fe3-a924-adb7d7121a49 | note | Acceptance Criteria - RCP’s under Runway and Taxiway Graded Strip
0ff8ca7d-6a9b-587d-82b3-ae0b80d2a9c6 | note | ○ 5MPa wet lean mix to 200mm above pipe obvert.
b7a47116-f844-5054-8ea5-77a8929a72a8 | note | ○ 6% Cement Stabilised Sand to pavement formation level or approved otherwise.
2b325fbd-334e-55c4-a31c-ad9693321040 | note | RCP’s outside Runway and Taxiway Graded Strip
8e1d4e99-575a-5cb3-a0db-2ff00c22e48e | note | ○ 5MPa wet lean mix 150mm above pipe overt completed in stages
a2be7076-28f2-5a0b-989c-7dd7e1330b73 | note | ○ Site won material completed in 200mm loose layer thickness (maximum) or 6% stabilised sand to pavement formation level or approved otherwise.
be32f9d6-757b-5617-af9f-340f9192925c | note | Reference Documents - Cl.16.5.6 & IFC Drawings & Tender Clarification #164
599b4af8-1dfc-5861-8e5c-a43813aff579 | note | Inspection/Test Method - Verify and Site Inspection
c8ab4ca6-dd7b-503d-a5d1-861f531aca8e | note | Record of conformity - Delivery Docket and ITP Signed
0d893b32-e969-5749-b54c-411d59d73362 | note | IP
ada9dd1b-ddca-5e6e-b385-6d121df1925c | note | Responsibility - Project/Site Engineer
5b8512f3-b805-5670-9e2b-46b008eb4aa1 | date | Date Completed:
8f5ad56b-ccbc-5351-8e29-07e076d4b2bc | section | 5.0 - Testing and Inspection
5269f1ff-a783-5266-b983-4f37188b54be | checkpoint | 5.1 - Compaction Requirements (RCPs)
20cf176f-a6b7-5c20-a15f-3a00128219f6 | note | Frequency - 1 test per lot.
130a3c59-641f-510a-aa7a-32754c96dced | note | Acceptance Criteria - Concrete Backfill Under Runway and Taxiway Graded Strip
d7323c0b-d2a3-52ba-b3c3-bdbbc0c3869a | note | ○ 1 compressive strength test for each 50m3 of backfill
b81c3dbe-96d4-5cad-8aaa-3c074b3ed218 | note | Concrete Backfill Outside Runway and Taxiway Graded Strip
13116915-82ef-58ce-a250-2e687f1b84fa | note | ○ 1 compressive strength test for each 100m3 of backfill
5b0edd3d-8dc9-5638-81b6-d2af923ddc36 | note | Backfill Zone - Outside the Runway and Taxiway Graded Strip (for site won material)
28818352-ac85-59f9-9890-d6dc2ad38044 | note | ○ Minimum RD of 95% SMDD (1 lot consists of every 50m3 for concrete backfill and every 2nd layer of backfill zone material every 40m.)
50268ddf-4832-5a04-b762-7344556c95dc | note | Reference Documents - Cl.16.5.6.3 (c), Cl.16.9.6 & AS3798.1 Table 8.1
e4e7c828-7985-5b35-9867-0ed080422016 | note | Inspection/Test Method - Site Inspection
7c2f5a42-9f8d-5f65-b4c2-8ab18d53ae71 | note | Record of conformity - Test Records
c98f2819-da3f-5a3b-9606-d21d1a15883d | note | TP
f5adbcf0-2707-52f6-844c-97e15c83e568 | note | Responsibility - Project/Site Engineer
49e3653e-dbb4-598c-928a-a15de17bcc47 | date | Date Completed:
425ea013-7e49-55f0-b058-434e57d240b7 | checkpoint | 5.2 - Inspection of drainage lines
dc0e3d4b-5cd4-5d5d-a0ed-7e2dd2a289ab | note | Frequency - Prior to constructing pavement
6dd1734b-9742-579c-9bb6-cb16e9c5a269 | note | Acceptance Criteria - CCTV inspection of RCPs required at the completion of the works.
65d7ac9b-b970-5c02-bb61-569d311577b3 | note | ○ Submission of CCTV footage to the Contract Administrator for review is a Hold Point.
21589f61-502d-5693-b289-8a8c5369d97a | note | Reference Documents - Cl.16.10.1
bd1cb358-993c-50bd-b162-888a5e2fe05e | note | Inspection/Test Method - Verify
5bfc6948-2c78-54c6-8b42-5e86765dbe38 | note | Record of conformity - Aconex Ref
5125a29a-784c-58df-bca6-136d172fd69d | note | HP
0a750240-ecff-52c8-9832-f0ad5e348793 | note | Responsibility - Project/Site Engineer, Beca
84fa9f99-d2e5-53e8-991a-df278960a6a1 | date | Date Completed:
cf83799e-b148-56c3-9496-619f3a2b924e | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
07843a40-ad75-597b-8d27-a2d33627f1bb | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
74bea63c-2144-54cf-8d9c-2c5d0a5c32bb | textbox | Print Name:
ceef9121-eb7a-57ad-9b81-0ff6d16629d8 | textbox | Position:
93d9e161-3a8c-5069-bbc8-466eab8fc03c | date | Work Completed On:
4ad221ca-63b8-5fac-8d71-1d492ee82fa6 | date | Date:
723ead20-e652-509e-a1ee-bdda34e5a4b3 | checklist | FH-ZU2-QU-ITP006 - Subsoil Drainage - Rev 2 | itp | ITP006 - Subsoil Drainage
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
b203efa7-9a22-5926-bd73-8de13b415a22 | note | Frequency - Prior to commencing activity
bbc090e4-5691-53ff-8630-4771d69f82b0 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
0bd51d55-9b65-50b8-b133-094970bffa42 | note | ○ using the correct and complete set of drawings.
2796cb7c-8938-5ce3-864e-aed637875e7b | note | ○ all drawings are the latest revision.
46916086-2b53-5d88-ad5d-4ec4e0b35143 | note | Reference Documents - IFC Drawings
2331c893-c1ca-5edd-a5bc-32cd368b8062 | note | Inspection/Test Method - Document Review
0c7059cd-7c8d-5927-b2a6-53aeda36e7f6 | note | Record of conformity - This ITP Signed
2a4ea12c-0fc8-5bf2-8321-e0e60a39e82b | note | HP*
62a43976-e7ef-5bb6-b3c4-d0f251e5ed9b | note | Responsibility - Project/Site Engineer
babe2d24-e642-593a-b977-cfdd507e634e | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
941dc993-a111-5574-9200-06146195396a | note | Frequency - Prior to commencing activity
40f86d52-0a66-57a8-890a-0408cd16eb95 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: CEMP, TMP, SWMS & WP.
2e4953e3-5ca0-5ad7-8b53-475ec0eb0254 | note | Reference Documents - CEMP, TMP, SWMS & WP
c9883755-8c08-5007-a533-cc805d703693 | note | Inspection/Test Method - Verify
9f40c57f-8d81-5fbc-97cc-5cc438a222b3 | note | Record of conformity - Site and Office Inspection
d456838d-d521-5f5e-9814-6ebab7e168ba | note | HP*
13a3a736-2da8-5338-9439-c66cf07d0f9e | note | Responsibility - Project/Site Engineer/Supervisor
8d3617a0-ff7a-589c-97a6-7746d94759b0 | date | Date Completed:
ddc68377-ad92-57e5-8ab0-c671f713640c | checkpoint | 1.3 - Excavation Permit
4621e442-d233-5395-83bc-ce811358abeb | note | Frequency - Prior to commencing activity
c10cec44-4414-5d8f-adad-794206ee4cef | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
6a9c7f96-9941-5267-b05e-e17eaf8ad66d | note | Reference Documents - Approved Permits
b7759b67-f929-5676-a29c-9f2d90988101 | note | Inspection/Test Method - Verify
f39f1bfc-9cd3-5716-a541-b40dbc723cf1 | note | Record of conformity - Proof of permit & ITP signed
7a6a615a-ed94-53da-aa6d-817b63f120c6 | note | HP*
178bd2a1-3ba0-50c6-afce-5996683f0817 | note | Responsibility - Project/Site Engineer
99112c83-d7a5-59d9-aef3-fc94599fd70f | date | Date Completed:
640c5bd1-aac8-5fb6-adc2-66cc46a99347 | section | 2.0 - Subsoil Materials
ff30ac65-459e-5113-9d3a-ab4a10f8d53e | checkpoint | 2.1 - Subsoil Drainage Pipes
5b646d98-aa7a-5836-ae73-381d8ebf1b62 | note | Frequency - Prior to commencing work
bcaec0c9-9031-5295-9942-dbf72084364d | note | Acceptance Criteria - Pavement Subsoils:
b7359a8d-0550-508d-8b02-ed66b1b36fc1 | note | ○ 100mm Dia slotted with filter fabric (sock) CL1000 SN20.
d5a93f8c-7cf5-5dd9-ac9b-3357d03174ae | note | Subsoil Collector Pipes:
b092e40d-b547-5be0-99d7-08a0a40cc028 | note | ○ AGL Carrier Pipe: 80mm Dia PN12 uPVC Non-Perforated Pipe.
c71454fc-b17e-5349-9e45-7aa67f16c22d | note | ○ SSD Carrier Pipe: 150mm Dia PN12 uPVC Non-Perforated Pipe.
0fe68566-15e7-5f87-ac33-ea7c86b3cb4d | note | Reference Documents - Cl.16.5.3, Cl.16.5.4 & IFC Drawings
7db0c490-ad5b-577f-af6c-8253694d2b26 | note | Inspection/Test Method - Verify
7b19fdb1-45b4-5c3e-8438-1738fb265c3e | note | Record of conformity - Order Inspection Checklist
5a52b1f3-475b-5840-a3fe-5ad3d836fb4e | note | IP
6a41afaf-d4b0-56ae-9cde-29297e7b2dbc | note | Responsibility - Project/Site Engineer
7e10c348-b168-547c-b344-2948e99a3363 | date | Date Completed:
e858c774-7201-5034-909b-d12807265395 | checkpoint | 2.2 - Bedding and Backfill
0a65b798-f2a0-50d4-8a54-048370d7f9e6 | note | Frequency - Prior to commencing work
65490841-89f8-52b9-a6c8-0e6ade8c75c5 | note | Acceptance Criteria - Subsoil Drain Pipes Under Pavement
8d673ba2-f482-50d9-8e8d-01e35ea81db5 | note | ○ Holcim’s 5mm Moriac Sand or approved equivalent.
ea074592-f6e0-5276-8ecf-09e2aa464e5e | note | Subsoil Collector Pipes – Under Pavement
90d57a37-66c0-5a63-9a00-37a0d5ea31cb | note | ○ Approved 5MPa lean mix.
0a750720-2d3c-5829-b0b1-43f7a714381f | note | Subsoil Collector Pipes In Grass
f6feccc3-2a5b-5c58-8c91-7bc66bc2ac4e | note | ○ Holcim’s 5mm Moriac Sand or approved equivalent.
a375508d-7a04-5b79-a062-dd33308b9ec0 | note | ○ Excavated Soil
0be3036b-e5c3-5cd3-94d1-82069d58357c | note | Reference Documents - IFC Drawings & VicRoads Section 702
192a4443-013d-5350-bee7-1ced123affd2 | note | Inspection/Test Method - Verify
04805040-cf54-5fbd-ab74-74d27943c596 | note | Record of conformity - Visual Inspection & Delivery Docket
12a91005-a1ce-5115-9639-3ff57f494a39 | note | IP
75b3b35e-138d-55f3-86be-0386538781c7 | note | Responsibility - Project/Site Engineer
977a00fc-306d-59b1-9a0a-2ac71d410998 | date | Date Completed:
32c59ad7-af87-5ed9-bdb5-404bdab7319f | checkpoint | 2.3 - Geotextile Fabric
1f00f2b1-23ff-5d29-ad30-843835eca1db | note | Frequency - Prior to commencing work
3654a3b6-f2a4-5ef2-a001-4d0b5aca6d9b | note | Acceptance Criteria - Non-woven type complying with the requirements of VicRoads for first stage filter or approved otherwise.
e7938520-5e9f-54bc-91a5-5d8faeca7148 | note | Reference Documents - Cl.16.5.8 & VicRoads Section 702
cbdc78d0-0722-54da-8205-b90cc9af3622 | note | Inspection/Test Method - Verify
447ec906-7210-5a3a-a5f3-6f908f3d604c | note | Record of conformity - Visual Inspection & Delivery Docket
0c6a5fea-3afd-512c-8368-a5417aef9492 | note | IP
f8fe6ab3-b47f-56cd-a396-18119f9ec08b | note | Responsibility - Project/Site Engineer
d3362b11-23dc-5195-9144-10052d55416a | date | Date Completed:
b8e682d2-d993-5fb5-9467-4b54608abadc | section | 3.0 - Excavation and Installation
7d370922-7733-519c-b084-007467ea59e9 | checkpoint | 3.1 - Trench Excavation
93bdb9fc-556e-5244-9d83-f6783c956641 | note | Frequency - Each Lot
8c640fb9-21ba-520b-a95f-471abad2330d | note | Acceptance Criteria - Trenches shall be excavated to the minimum depths, widths and batter slopes as shown on the drawings.
56f6e280-b7f1-5fd9-a677-7c644276b746 | note | Minimum Trench Widths:
43759727-e5da-57a1-af50-b01cf3d394bb | note | ○ Subsoil Drain Pipes
43e28dc1-5a6a-5792-b73e-e85f01e8c46f | note | – 300mm total width for the subsoil drain pipe (DN100).
af2bffd1-df6b-5b82-83e6-861c7441d94c | note | ○ Subsoil Collector Pipes
02934fcd-64ef-573a-95a1-a5782919ad2c | note | – Horizontal clearance from the outside of the pipe to the wall of the trench to be minimum of 150mm for all collector pipes (DN80 & DN150 both under pavement and in grassed areas).
c83e1bc1-a23f-50ea-a791-ee6fee052881 | note | ○ Excavated material disposed per approved CEMP.
d35269e0-0384-5008-8156-7ca76583fce3 | note | ○ Completed excavation works shall constitute a Hold Point.
30c8a41b-bf2d-5399-81fb-af8d6620b1df | note | Reference Documents - Cl.16.8.1 & IFC Drawings
84ef1c63-e86c-5e80-8a4a-3617827e4c3e | note | Inspection/Test Method - Verify
20ae350c-40fc-5b50-9d8f-19f392727a14 | note | Record of conformity - This ITP Signed
2579ceae-223e-5bc5-813e-452564241e37 | note | HP
bc954475-f8de-599e-8749-faa5b05ffb8a | note | Responsibility - Project/Site Engineer Beca
6efe9634-1020-5184-b917-5d6940c41288 | date | Date Completed:
f3ac8999-e404-5e36-bf08-9da493dca846 | signoff | AUTHORITY HOLDPOINT
7c207bae-6922-56c2-bc1c-fd1a1380798c | checkpoint | 3.2 - Geotextile Placement
ef9802b5-3e5f-5715-a88b-5cb5dc0ff26f | note | Frequency - Each Lot
deb9c76e-c3ed-54e6-b14d-4668eeb6639b | note | Acceptance Criteria - Geotextiles in trench drains shall be placed to conform loosely to the shape of the trenches.
21d2eb47-3873-541e-b2c9-79d7673f0a3e | note | ○ Site trial to be undertaken to evaluate the proposed construction process and compaction method, Hold Point.
dab879b0-1f17-5774-8e0f-6117afa132ea | note | Reference Documents - Cl.16.9.4.2, Cl.16.9.4.5 & IFC Drawings
82e70949-388e-58e4-a299-eb94ab7b8933 | note | Inspection/Test Method - Visual Inspection
71db4eed-f250-532a-bb94-bd3a828c4158 | note | Record of conformity - This ITP Signed
e5f82998-cc61-5ce3-93b0-24d850879a9b | note | HP
705d94a8-4029-58fe-a8b9-780793c31bca | note | Responsibility - Project/Site Engineer Beca
860b8d14-7b9e-506a-a000-6954dab63e0c | date | Date Completed:
19246d8a-6502-5423-8f48-410f20468d0c | signoff | AUTHORITY HOLDPOINT
c65e052b-cb68-5319-8e1b-8bfead12d177 | checkpoint | 3.3 - Bedding
edf8c917-c28c-5c70-b565-3e2d432fd2dd | note | Frequency - Each Lot
62421231-2c6d-5eca-9810-3473afb30050 | note | Acceptance Criteria - Bedding for Subsoil Drain Pipes Under Pavement and Subsoil Collector Pipes in Grass
bc12892a-da80-540e-8469-0dfa293e3156 | note | ○ Bedding of granular filter material or approved equivalent:
9ef781b3-6406-5d7a-b1e3-c4c4d0ffd4bb | note | – 100mm for subsoil drain pipes.
8739fd5d-84f9-595e-bd56-eb792fcc829d | note | – 75mm for subsoil collector pipes
4a1d56be-0e72-559e-8a13-4adfe3968569 | note | ○ Filter material shall be placed and compacted with minimum disturbance to pipes and in layers no greater than 200mm uncompacted or as approved otherwise.
f7bbff52-7368-5ad4-ac3a-16b9fd15f9eb | note | Reference Documents - Cl.16.9.2 & IFC Drawings
a1ff3c14-5b58-56dd-9b30-9a770d99dedc | note | Inspection/Test Method - Visual Inspection
edbf6be4-9c0b-5c1e-8e98-001ed939039e | note | Record of conformity - This ITP Signed
11b14a64-c51f-50ef-a675-66ea99711356 | note | IP
60facb07-3d1a-5dc6-9896-76c918e4279c | note | Responsibility - Project/Site Engineer
b6e19c2b-861b-5e35-aa57-f3dfa61fcc93 | date | Date Completed:
bf93a28a-5e59-52ec-b619-d5e40854365f | checkpoint | 3.4 - Laying and Jointing of Pipes
acc63919-1859-5956-accd-4338e7a69607 | note | Frequency - Each Lot
982dab69-d0d8-5ee3-9b07-5a9200f9ad52 | note | Acceptance Criteria - Pipes laid at the depths and lines indicated on the drawings. Where grades are not specified, the bottom of the trenches shall be trimmed to provide no less than 0.5% longitudinal fall.
43ca6168-124c-5106-916f-7f05a8f1181f | note | Reference Documents - Cl.16.9.2 & VicRoads Section 702.03, 702.09
f30b24eb-069d-52f8-9c80-00edf093fa0c | note | Inspection/Test Method - Visual Inspection
8d17080c-d48d-5c25-8294-368a7b2b11f5 | note | Record of conformity - This ITP Signed
12ccdfeb-6447-5b5f-9c90-89d12c8e5783 | note | IP
5af6caf2-1f5c-55ba-9bda-dd7a686406ea | note | Responsibility - Project/Site Engineer
5fed5454-4550-5138-823f-625274cf1e2e | date | Date Completed:
929f05a2-5222-5ae8-8d37-53da19f97499 | checkpoint | 3.5 - Backfill
82e0d72f-b673-55f3-a373-a8ea5a346c9c | note | Frequency - Each Lot
782fda5e-a891-560b-a090-0d895cc5246e | note | Acceptance Criteria - Backfill for Subsoil Drain Pipe (⌀100mm pipe)
16f6de95-850c-54e9-9cda-8db3e3234d8a | note | – Granular filter material or approved equivalent backfill is to be placed to the underside of the CTB layer.
c65b7a80-90b6-58d2-b607-783ba0e61707 | note | ○ Backfill for Subsoil Collector pipe ⌀150mm Under Pavement
db90f132-f0d7-53d9-8eae-ea8a81b12ea0 | note | – 5MPa lean mix backfill is to be placed to a minimum of 150mm above the pipe crown to underside of pavement formation.
7815479a-a64b-514a-a8ac-c710635bff3e | note | – Backfill to be completed in two stages to avoid pipe floatation.
52e3cb2e-51b0-5ed2-a80d-117db9ebcc0a | note | ○ Backfill for Subsoil Collector pipe ⌀150mm In Grassed Areas
e01eaf9d-2a64-523d-b88e-eaba57882e10 | note | – Granular filter material or approved equivalent is to be placed to a minimum of 150mm above the pipe crown.
04f9a45d-67aa-5f3a-9cf6-d80049db9353 | note | – Excavated soil recompacted in layers not exceeding 200mm loose thickness to underside of topsoil.
7a5f02a3-76eb-5822-a496-80137de680ef | note | ○ Backfill for Subsoil Collector pipe ⌀80mm
3d708b91-b862-571a-bd20-879a1ca722a2 | note | – 5MPa lean mix backfill to be placed to top of 150mm FCR subbase layer
d63fb179-d759-5832-859e-dff393f317ce | note | – Backfill to be completed in two stages to avoid pipe floatation.
e2f44423-fabd-5fc4-a2bd-d2019986ed13 | note | Reference Documents - Cl.16.9.2, IFC Drawings & Tender Clarification #38
2c3a2b19-1ecf-55da-b4cc-23359d952d5d | note | Inspection/Test Method - Visual Inspection
c359ccd0-b0bf-56ed-9d34-2103b9b83abc | note | Record of conformity - This ITP Signed
89d9dfb0-fe82-54a4-b618-7d17b9f3ecf1 | note | Project/Site Engineer
5a6ddc48-3b75-5b34-a0cc-51ff2e6bbcdb | date | Date Completed:
aa113495-ff71-5ee9-af22-889d3a144bc7 | checkpoint | 3.6 - Geotextile Protection
2729af9d-76e7-5b4f-b482-22072c7b5378 | note | Frequency - Each Lot
93d4d9f0-a715-5621-902f-6b616213da84 | note | Acceptance Criteria - Geotextile must fully envelope the backfill material in the trench with a minimum 150mm lap.
9cac07ab-e16d-4284-bfb7-7686791e9c0d | note | ○ Prior to placement of next layer of pavement material, inspection to be undertaken to check if the geotextile is correctly overlapped and free from punctures or tears and ensure it is pinned down to prevent movement and the filter material becoming contaminated. Should these issues occur, they must be rectified prior to placing the next fill material. This shall constitute a Hold Point.
43351c17-7eda-5104-ba99-610b06d2a88b | note | Reference Documents - Cl.16.9.4.2, Cl.16.9.4.3 & Aconex FHPL- GCOR- 006263 & IFC Drawings
f54cbdc1-b074-5ceb-b237-b304e63b3eca | note | Inspection/Test Method - Visual Inspection
118f5f81-1efc-52a1-88c9-a445cb2c84c2 | note | Record of conformity - This ITP Signed
dc0e6d00-83df-50ea-81de-bb9fbdfead91 | note | HP
02300ae5-d391-51c9-a516-b20c5ddd137f | note | Responsibility - Project/Site Engineer, Beca
cc3b74dc-e10e-501a-a4f7-2f5006fa8096 | date | Date Completed:
3bc895d2-9865-5f8e-b872-b810f8cc5d91 | signoff | AUTHORITY HOLDPOINT
0d640a99-ec2e-5652-9486-4672ee480699 | checkpoint | 3.7 - Subsoil Drain Outlet
4ce793d0-4b56-55ae-bbda-0be872c461e9 | note | Frequency - Each Lot
160fda7a-f329-55cf-b8ba-fdf84ab370a6 | note | Acceptance Criteria - Subsoil outlet point to be located at a drainage pit, pipe end wall or outlet in a fill batter or drain. All subsoil drain outlets shall be fitted with Vermin Guards.
59bd5fb0-e432-5242-b273-7bf5b9e311ed | note | Reference Documents - IFC Drawings
7b40b719-15b4-5402-93d8-59527c560432 | note | Inspection/Test Method - Verify
f3ef272f-cdec-523a-903c-f3f96bd94df1 | note | Record of conformity - This ITP Signed
4717fb7b-5e44-5540-b72d-1c7a289ab715 | note | IP
c6899f67-80fc-5df1-80cf-fe23901deb0d | note | Responsibility - Project/Site Engineer
47d5459c-6674-578c-9823-3add99fab108 | date | Date Completed:
b16f032e-a06c-51da-bedd-4bf211c93ec3 | checkpoint | 3.8 - Flush out Risers
4ca51bc6-a49b-5cdc-90f8-be1ffe24b462 | note | Frequency - As applicable
3e406be0-0322-543b-a8ef-6daa7ba05a9f | note | Acceptance Criteria - Cleanouts shall be located at the heads of all subsoil drains and as specified on the Drawings.
4a800173-7989-52ab-8d58-a3d54e3636fa | note | Reference Documents - Cl.16.9.2 & IFC Drawings
6cd03d77-7d8a-54ad-9359-c814cb1e0d82 | note | Inspection/Test Method - Visual Inspection
5494ab28-0f52-5649-b76a-f86b564fb504 | note | Record of conformity - This ITP Signed
7d927a6d-e401-5733-aaf5-fff9868ebd5e | note | IP
3d8ea8a8-f64e-597f-b966-ffb378018b49 | note | Responsibility - Project/ Site Engineer
89424513-edb2-57cc-b080-fa44a44fceac | date | Date Completed:
d0dd6e34-86d2-5297-913f-37b8b638172d | section | 4.0 - Post Construction
29e6a9a6-c10a-5416-a835-e9aa5e568085 | checkpoint | 4.1 - Flushing Test
ac2cde80-3d01-529a-812e-aef469bf814a | note | Frequency - Each Lot
33817df8-516a-506f-bf30-2f709891d88f | note | Acceptance Criteria - Flushing test to be carried out for subsoil pipes to remove material that has entered the pipes during construction and to ensure that the drainage line is free from obstruction. This constitutes a Witness Point.
9b875275-a4ca-5915-bdf5-2499e12fbd6d | note | Reference Documents - Tender Clarificati on #33
eee59dc7-f9c7-5a81-8506-01615d50d95b | note | Inspection/Test Method - Visual Inspection
02293552-747a-5fd4-866a-94f45d6e5a3e | note | Record of conformity - This ITP Signed
62c6cda1-4101-52c8-9adf-97edc1fddbc1 | note | WP
67f67238-bbbc-5e97-b0ec-911c93b51479 | note | Responsibility - Project/Site Engineer
c6604951-a6da-5fa5-a47e-d47d5f6087bd | date | Date Completed:
f28c1d32-46be-5ee4-a0e8-31aecf23fb4d | checkpoint | 4.2 - Records
265d3813-d435-55c9-8a25-0b3901c43330 | note | Frequency - Each Lot
a5ebcd79-d827-530b-81ad-26bce792df85 | note | Acceptance Criteria - Levels and alignment recorded in as built documentation.
5a5215f2-64c1-573e-ae61-0cbce602f745 | note | Reference Documents - As built Data
4c686766-1525-5f55-bbeb-013432f0beb7 | note | Inspection/Test Method - Verify
0d197c67-89f3-5a1e-b1ae-c8ebc5c7e02f | note | Record of conformity - Aconex Correspondence / Asbuilts
287c6857-e310-5e63-8b19-69f7316bccd1 | note | SCP
5b6a66e7-a082-5f5d-b2a2-fea9a80aa612 | note | Responsibility - Project/Site Engineer
5ebdc4ef-343c-5375-8a19-e6b25236d540 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
61331d75-b3c7-5352-8079-414b603e3db6 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
5572ef30-e932-5a08-a991-e4f08674c94b | textbox | Print Name:
f6667217-4fcf-50bd-b2bf-6f44ca637a42 | textbox | Position:
f259472e-32a8-5470-b3b9-9487c05a4eb7 | date | Work Completed On:
933ef43f-f06a-5888-ba35-78c4fb61c965 | date | Date:
beb379db-a922-5180-82d2-2d45e5dc0c76 | checklist | FH-ZU2-QU-ITP007 - Precast Drainage Structures - Rev 1 | itp | ITP007 - Precast Drainage Structures
d7d6e24a-41e3-57a2-9551-08a3da3fcd83 | section | 1.0 - Preliminaries
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
5db1b43a-1481-53e1-8de3-6d2f2dc31855 | note | Frequency - Prior to commencing activity
1a76d17f-abc3-50a3-b63a-504f13b3a613 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
0d8d158f-73f0-5a63-b5b1-81123ed6bfe9 | note | ○ using the correct and complete set of drawings.
bbdc7d62-c614-531d-9e87-93061dcfdf4b | note | ○ all drawings are the latest revision.
2cceb0a1-7ceb-5f46-90ba-44ce40a286b7 | note | Reference Documents - IFC Drawings
57e73c5b-8753-5f96-9e6b-7503760b523e | note | Inspection/Test Method - Document Review
3453148d-86f9-55d1-9874-e84456f23411 | note | Record of conformity - This ITP Signed
f2aebf2b-e43a-5cb6-b55f-8253f262294f | note | HP*
31f3edd6-0a74-5ffd-994f-63f47528d216 | note | Responsibility - Project/Site Engineer
9b90ffe2-5c62-5bad-b57d-2238a6456e16 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
7db392a2-fa21-5236-8c16-e9900da3e150 | note | Frequency - Prior to commencing activity
f4083910-855f-57c0-9147-6a80de365aa0 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: CEMP, TMP, SWMS & WP.
06f95c10-fae3-5fe3-ab27-fe120bb891db | note | Reference Documents - CEMP, TMP, SWMS & WP
8a3feeb6-5bce-57be-b8e7-c3078292fad6 | note | Inspection/Test Method - Visual Inspection
016a468e-f575-5630-a16d-5dfbd4f4075a | note | Record of conformity - Site and Office Inspection
a0e8ae7d-3b8c-58c4-9d58-ac3382dc190e | note | HP*
bb752f86-d03a-511d-84ff-723e46cdeb21 | note | Responsibility - Project/Site Engineer/Supervisor
dba43527-ddff-57f6-bb82-05b51bf52559 | date | Date Completed:
ddc68377-ad92-57e5-8ab0-c671f713640c | checkpoint | 1.3 - Excavation Permit
b22648d9-7d02-580d-85cd-cdbdcad4c8ac | note | Frequency - Prior to commencing activity
191cd235-416b-56c4-ae45-ba847c9b457a | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
3fd46ef3-909e-574d-bc0a-517872f8ebd0 | note | Reference Documents - Approved Permits
aed208a1-ac7a-596e-9042-0a061c81d802 | note | Inspection/Test Method - Verify
83a18917-fc0f-5b77-80ab-116c9821c0b8 | note | Record of conformity - Proof of permit & ITP signed
5d722d91-8a36-5933-b731-3c1675a16b46 | note | HP*
2368bad9-cb75-5cf3-a8ba-657e6c725e1b | note | Responsibility - Project/Site Engineer
70234546-ef16-5344-83b2-265b140986d3 | date | Date Completed:
12d91755-f6b0-5418-b819-f73d40c1e0c5 | section | 2.0 - Material Approvals
f7951c56-de28-5258-8451-17b4166c3f84 | checkpoint | 2.1 - Precast Structures
ab58fa24-f116-51e1-bb56-2a5a9c8ec0a2 | note | Frequency - Prior to commencing activity
cf5ed991-6585-57b3-b911-3d0f86fa22e2 | note | Acceptance Criteria - Details of the proposed precast drainage pits, headwalls, and culverts to be as specified on the IFC Drawings.
bdd411b2-4986-53fb-b73b-7e7c7000d1e2 | note | ○ Approval of the shop drawings constitutes a Hold Point.
dc249841-c08f-5a5f-af73-76dbf53cd354 | note | – Outline of sampling and test program
fed5492d-1da5-53b7-a7cf-795b5d8a04cc | note | Reference Documents - Cl16.6.1 & Manufacturer's documents
1301e68d-a0a5-5b05-bcea-f42d62c4a43f | note | Inspection/Test Method - Document Review
727e61f8-7fd4-50b5-a15d-86daf5052d56 | note | Record of conformity - Aconex Correspond ence
0599f0ff-d4c6-5ff8-8896-4d09cc6f8ea3 | note | HP
60e01000-b791-57e5-bb2f-4f7d4d1ff2ac | note | Responsibility - Project/Site Engineer
2794c579-9153-5731-8224-ae2a4141554f | date | Date Completed:
b4c31f0b-0aa9-590b-a901-d453e8a0654a | signoff | AUTHORITY HOLDPOINT
64f2e985-6054-5a03-b410-dc6ff9bee5d3 | checkpoint | 2.2 - Access Cover and Grates
ee79c773-1a56-5fe8-899f-c58377ade254 | note | Frequency - Prior to commencing activity
738d9405-acdd-56c8-ba83-7a8e734ab43c | note | Acceptance Criteria - All Pit covers to conform to AS 3996 and the applicable load class to be as noted on the Drawings.
fa10de75-6a4c-5fb4-a5fb-5874320a4794 | note | ○ For all drainage pits, pit lids are to be Class D.
e579fe7a-accd-5bed-91df-d69f754eb26c | note | Reference Documents - Cl16.5.7.1 & IFC Drawings
ec5278a1-6e0e-5f5b-b066-f574f2cc1a35 | note | Inspection/Test Method - Verify
26f47815-84b6-555e-8d46-79bb5eaf571e | note | Record of conformity - This ITP Signed
01dc8e7e-e7f0-55ad-8db3-4ececbf30b27 | note | HP*
bd40906a-f0ca-51cc-ad66-83ab99c6018f | note | Responsibility - Project/Site Engineer
bb342a11-5224-5e4d-95e4-d782fb070f5c | date | Date Completed:
e6b7e050-8df8-5309-8d57-3ace2e422035 | checkpoint | 2.3 - Box Culverts Bedding, Side, Overlay and Backfill Zone Materials.
688061a6-81b0-559a-8250-397751cc1678 | note | Frequency - Prior to commencing activity
f4a418bf-6ffb-5a9d-aba5-c09c320a74ba | note | Acceptance Criteria - Materials are to be compliant with the requirements detailed in Cl.16.5.6 or as approved otherwise.
38053ff1-cd39-5fdf-8ce8-f5930d7b639e | note | ○ Material submission approval.
16451f44-84f4-5e7c-9a14-7a0da0f8e1d3 | note | Reference Documents - Cl16.5.6 & 16.6.2.2
8b226639-1b33-5015-b62c-a5ab6e527522 | note | Aconex ref: BecaCPL-GCOR-000960 (Box culvert installation methodology with approval of materials for use)
30b99241-d916-525a-bfc3-2d08052484b7 | note | Inspection/Test Method - Document Review
2eb85dda-ae6a-50fa-bbfb-e924fb5d65de | note | Record of conformity - Aconex Correspondence
bb4d22c6-594e-5e4e-a331-0681ccdd570c | note | HP
7fcdd18b-5de0-57e4-9b71-aaa4a4660761 | note | Responsibility - Project/Site Engineer, Beca
08680424-9ec9-592b-8546-d45754dd8cba | date | Date Completed:
1d22fc60-66a1-5916-ade2-7806e4ace807 | signoff | AUTHORITY HOLDPOINT
7a40bb56-ecee-5114-bbd7-28b82b977398 | checkpoint | 2.4 - Blinding for Drainage Pits and Headwalls
2cdc4b40-de5a-5ded-8076-77119d0265f3 | note | Frequency - Prior to commencing activity
a24482b1-7c81-59d4-a748-46579e1d29c8 | note | Acceptance Criteria - Approved bedding material as per IFC Drawings or as approved otherwise.
783bb8e2-be87-5037-9220-8c38c2c4dd3c | note | Reference Documents - IFC Drawings
7ab25307-343e-5eb3-bcf9-7a0d3eeb0fd4 | note | Aconex ref: BecaCPL-RTRFI-000089 (Blinding mix) & DCWC Mgt-GCOR-009582 (Crushed rock bedding for pits)
f44ffccd-5943-5302-aed5-53db29ae97ce | note | Inspection/Test Method - Document Review
63f4a899-fbd9-5678-a97e-10b5d6ed1165 | note | Record of conformity - Aconex Correspondence
e90d6749-9565-5df0-b4c1-b94133094ae9 | note | HP*
930504cd-e750-5cfb-b16e-1becd7073c2d | note | Responsibility - Project/Site Engineer
11bca55f-d813-5454-a26b-d1954d7f4432 | date | Date Completed:
b4208e7e-9703-5497-9cf6-a7359c21d079 | checkpoint | 2.5 - Geotextile Fabric
0951a30d-bcd5-5f82-bef2-ba9a2aad8644 | note | Frequency - Prior to commencing work
f891fcef-102e-5a05-8555-ad08670e8ccb | note | Acceptance Criteria - Non-woven type complying with the requirements of VicRoads for first stage filter or as approved otherwise.
24b2885c-192f-549e-802c-228765e85054 | note | Reference Documents - Cl.16.5.8 & VicRoads Section 702
e5e4b048-774b-50c9-ba9a-7182b3bd8257 | note | Aconex ref: BecaCPL-RTRFI-000144
c630faca-13d4-560f-830e-3f4aa85bed97 | note | Inspection/Test Method - Verify
1294c6fe-f4d9-590b-9f86-0f6f852ba88a | note | Record of conformity - Visual Inspection & Delivery Docket
c0d53522-9130-5af2-a8d7-de0dc81e3b98 | note | IP
4dba0165-a49b-5344-86bc-0d5dd9ac3264 | note | Responsibility - Project/Site Engineer
b2b17873-ad3d-59da-a630-c012a3d50118 | date | Date Completed:
66be0a60-ccaa-5da5-82e3-47322e7bc7ce | section | 3.0 - Material Receival
4e595278-c063-523d-9160-3efd6b8df4d5 | checkpoint | 3.1 - Precast Structure Delivery
510d066f-aaad-521c-acd0-6ab33d93d77d | note | Frequency - Each Lot
dd9eb527-123d-5ff3-8a1d-3dc9615eb7ee | note | Acceptance Criteria - Ensure each precast component is inspected upon arrival ensuring:
07b2c205-7888-5b47-92a6-db01e80e6c1d | note | ○ Dimensions are as shown on manufacturer drawings.
7cc21e09-88cc-50a3-9e6f-0ca3fb4973b0 | note | ○ All blockouts in correct positions and to dimensions.
135c1ef7-713d-5cc5-ba69-8ad6e14a1ce1 | note | ○ No damage to any precast structure component to the satisfaction of FH Engineer
8d9ffef1-ea02-531e-8f73-963f781550bf | note | ○ No modifications to the pits are to be made without written approval from manufacturer.
5074dbb4-fe4f-5a86-8c38-d55d527c200c | note | ○ Manufacturer’s conformance report
6d2e38b7-5e7a-579b-98aa-27efa490fb76 | note | Reference Documents - Cl16.6.1 & IFC Drawings
16726ebd-142c-5e2d-94c3-c144f08e5ef2 | note | Inspection/Test Method - Visual Inspection
315da72d-1ceb-58aa-8eff-c1fd0d60823b | note | Record of conformity - Order Acceptance Form
59a9abc0-badd-59c7-8e34-ca95cacf72b3 | note | HP*
0f267815-5dc3-5586-9e6c-2588f0be04e8 | note | Responsibility - Project/Site Engineer
9b599835-4289-5d69-b59b-6d98ad2786ab | date | Date Completed:
8411b870-30d9-58f8-9930-1bfc13a433c0 | section | 4.0 - Drainage Pit, Headwall and Culvert Installation
5c6df739-5258-5ade-9921-36b1301c399e | checkpoint | 4.1 - Survey Setout
96f73f4c-1ddb-5ecf-8655-9ec86c40c259 | note | Frequency - Prior to construction and each lot
80120edb-cad5-57b6-b432-a9dfba621b6a | note | Acceptance Criteria - Set out the drainage structures as shown on the Drawings to identify the locations, lengths and levels:
eaaa0d90-e5de-575a-bd91-aeb0a7373072 | note | – All pits, and inlet and outlet structures.
c40a009b-6410-5c62-97aa-7dbe26d35a79 | note | – Ends of wing walls and headwalls.
15456013-b6fe-5a16-8b34-9444a9a3f601 | note | – At outlets and inlets of box culvert structures.
739131ea-764e-5029-b752-a70fa5c75714 | note | ○ Setout of each drainage system to constitute a Hold Point.
6c41b77b-65df-5b8e-9a67-f535ee05e9e9 | note | Reference Documents - Cl16.7.1
1f07cdb5-abfd-522c-b9e8-564f84f66c66 | note | Inspection/Test Method - Survey
16a01d25-681e-5993-bc13-59adf1d5e086 | note | Record of conformity - This ITP Signed
219b5388-f45e-56f4-a1df-a87748de4426 | note | HP
14944d7e-92c0-52a4-bacf-e90676402f30 | note | Responsibility - Project/Site Engineer, Beca
fa7a906f-cd3c-519d-84f4-67963423f62e | date | Date Completed:
ff9f951f-7476-5d3f-ba8e-80db7c677589 | signoff | AUTHORITY HOLDPOINT
e4eb01cf-d31f-52a8-b825-5b5a10cd54a0 | checkpoint | 4.2 - Excavation
1176e267-a531-5cdd-b74e-306ee86a5a72 | note | Frequency - Each Lot
e374136f-55f7-5a35-86e5-f75d59b8c3a4 | note | Acceptance Criteria - Excavation to be performed to the minimum depths, widths and batter slopes as shown on the Drawings, regardless of the type of material.
1a9ec8b6-abbe-5c22-9433-db8811c2a6dd | note | ○ Inspection of completed excavation works to constitute a Hold Point.
d8d48fdc-af48-5f58-80f8-c3a8dd8d7a41 | note | ○ Pits: The shape of the excavation to be as required and the size sufficient to enable construction of the structure.
dde9fb29-d00c-5e0f-80d9-470fd164b600 | note | ○ Box Culverts: The width of trench to be not less than the exterior width of the culvert plus 400mm, and not greater than that required for satisfactory backfilling.
ccdb8dbb-6936-568e-baa8-372a04b9834d | note | Reference Documents - Cl16.8 & Cl 16.6.2.2
c5d4529e-db4c-5d84-959d-20a5f2f5efb7 | note | Inspection/Test Method - Verify
d9f522df-c5ed-5ac9-9d83-0fa5b613c708 | note | Record of conformity - This ITP Signed
571c1da6-a91a-5fa3-a70c-66ec3ae68a74 | note | HP
c6c80ad7-00a7-5073-908c-c069c67ae74c | note | Responsibility - Project/Site Engineer, Beca
94484256-bf2c-5fd8-b6dc-a6317e71bd2a | date | Date Completed:
ff5e91b7-5a2a-57f8-87eb-01651d3a2682 | signoff | AUTHORITY HOLDPOINT
f916e68d-a2b3-5b1e-b050-5226d6cd6b04 | checkpoint | 4.3 - Confirm Ground Conditions
b8d350c1-8ff5-5b96-973a-67f22efdb856 | note | Frequency - Each Structure
20e25821-d580-5c2e-b669-b1ad3bb75e5f | note | Acceptance Criteria - Min. 1 x DCP test to be undertaken per drainage line / structure to confirm ground conditions. If the first DCP is inconclusive or fails, additional DCP to be taken as needed based on on-site assessment of the ground.
36164437-c5cf-56ae-9d48-c40a20b3ed9a | note | ○ Contractor to notify the Contract Administrator of any area of the foundation with inadequate material to support the proposed drainage structure. Inadequate material is deemed to have a bearing pressure less than 130kPa, equivalent to 4 DCP blows per 100mm, as per note 4 on drawing ZULU-BECA-012- DWG-07102.
2f1f7b49-708c-5f8c-a252-fe31b08cae2d | note | ○ Inadequate foundation material is to be replaced with a layer of coarse crushed aggregate compacted to 95% relative standard compaction to AS1289 Section 5.5.1 over a geotextile Bidim A29 or approved equivalent.
2350b2d8-7113-5a27-a640-aeecc9cfcaee | note | Reference Documents - Cl16.8.2 & Tender Clarification #38
ea4ce89e-4f55-53c5-bd51-7609dc2a8f82 | note | Inspection/Test Method - Site Inspection
2423809a-6b01-53b2-8e5b-8dd890b86fdd | note | Record of conformity - DCP, Test Results
06e8b35d-cbaa-523b-9400-83dc0bda6785 | note | TP
6c53e3f2-cb75-566e-aa85-9477e2f68835 | note | Responsibility - Project/Site Engineer
0414f3d0-9444-5ffb-b0fa-d989cc17b6be | date | Date Completed:
e8bd3d80-c970-5ff2-b8d8-884efdcd9bc0 | checkpoint | 4.4 - Blinding for Drainage Pits and Headwalls
bcad1afe-016b-5246-927e-c5f03a90f683 | note | Frequency - Each Lot
b55575d8-14b3-5e3f-8751-50467135ca28 | note | Acceptance Criteria - Blinding to be installed as per the depths and widths shown on the Drawings.
45ac2b98-d9a1-5003-b229-0a8f31ab2df2 | note | ○ Pits: 50mm Crushed Rock bedding
89a61e11-443b-50b1-8d5a-9700e1abaa68 | note | ○ Headwalls: 100mm 15MPa Concrete blinding or as approved otherwise.
ebd7362e-49bf-5a7b-9ffb-9e0d8661adbc | note | Reference Documents - IFC Drawings & VicRoads SD
0e10937e-f79f-5a21-a6a5-a510f354efb2 | note | Inspection/Test Method - Verify and Visual Inspection
7f27ad83-67f0-59e9-b805-d75ab259c9b1 | note | Record of conformity - Delivery Docket & This ITP Signed
dc4048a4-91fe-5f55-ada0-70be55bd2a52 | note | HP*
d9ac6299-f974-558c-b572-02ef9cc116d3 | note | Responsibility - Project/Site Engineer
f8ec5fdd-ff5b-5701-9419-f7ff43c7b7ef | date | Date Completed:
360c7d9d-bbd2-53e4-8559-df3b0d350a25 | checkpoint | 4.5 - Bedding for Box Culverts
f6104982-9dea-5959-98f6-70237c3d3dd8 | note | Frequency - Each Lot
4fa34d6c-f014-5a38-beb1-1c3e335ffd31 | note | Acceptance Criteria - Bedding material to comprise of approved select fill or as approved otherwise and to be placed for the full width of the trench.
42c26375-9a6c-569e-9359-fb0c5cfd5717 | note | ○ Upon completion, the bedding is to provide a uniform firm foundation with the top surface of the bedding shaped to the details shown on the drawings. This to constitute a Witness Point.
14025ba8-9afd-54e8-be08-4d2e8e8a27af | note | Reference Documents - CL16.5.6. 1
20d97cde-028a-5067-846d-c4bcc652d396 | note | Inspection/Test Method - Verify and Visual Inspection
18606999-4387-52e4-a1c1-37ccd808471b | note | Record of conformity - Delivery Docket & This ITP Signed
f52e261e-1bef-5aa7-8741-0bb3dabc2c2b | note | WP
61c2e6db-e12f-5367-ad8e-43d826fcc22d | note | Responsibility - Project/Site Engineer Beca
34b4a718-4ed3-563b-bec5-2a949aab05dd | date | Date Completed:
8e65e6b4-af39-5ca6-a9c5-8b0ace278aea | checkpoint | 4.6 - Positioning of Precast Structures
11f1ce0f-933d-5c66-b10d-8ca75e1a0230 | note | Frequency - Each Lot
cc95c182-f51a-5dd3-8794-6c3a70be63aa | note | Acceptance Criteria - Precast structures installed as per survey set out points marked on blinding / bedding layer
df1710e5-23d8-5ac6-b0a9-32a51a5dfb01 | note | Reference Documents - Cl.16.8.1 & IFC Drawings
52618993-76b4-5fe0-b5ec-760dd3780ed4 | note | Inspection/Test Method - Verify
d0e4ca64-9106-55b0-a47a-48a846c16bf7 | note | Record of conformity - This ITP Signed
62ffd668-108d-5f05-a822-06fac03094e8 | note | IP
5ef51f22-b49d-5375-87c3-b02487c59eac | note | Responsibility - Project/Site Engineer
ac26066b-3fa6-50e3-bf9c-b1f302782640 | date | Date Completed:
159501bb-b6bb-53ea-9a80-faa22dafd3d2 | checkpoint | 4.7 - Backfill Materials for Box Culverts
f797f376-3caa-58b0-bd53-dfce5ebb7902 | note | Frequency - Each Lot
4fa89b10-99b2-50e1-818a-1cb940c0473e | note | Acceptance Criteria - Side Zone, Overlay Zone and Backfill Zone Subject to Vehicle Loads
d2e1e579-fd48-5bdc-aee0-64eb6b1073a6 | note | ○ Approved 6% Stabilised Sand.
29ef28c6-caad-5e95-a851-4720cb916273 | note | Overlay and Backfill Zone – Not Subject to Vehicle Loads
39bc908f-7787-552e-9edc-bcd4afe87479 | note | ○ Approved 6% Stabilised Sand.
5f59707d-fbdf-5d92-aa4c-011a03990d19 | note | Reference Documents - Cl.16.5.6 & IFC Drawings
04391806-868e-55c2-967c-a5a34dd0621a | note | Inspection/Test Method - Verify and Site Inspection
f87b33fe-04c5-5d60-8d00-8d73cafd1cb8 | note | Record of conformity - This ITP Signed
32827412-ef03-5eae-97ff-c2b0e931a375 | note | IP
23df4aec-6efa-5a2b-bcf0-63d5419c08b5 | note | Responsibility - Project/Site Engineer
3d43666e-c673-5375-aaad-1c98ed6901b8 | date | Date Completed:
c83fdcaf-9e5c-50db-9b66-3cf10748adc8 | checkpoint | 4.8 - Compaction Requirements (Box Culvert)
98400f66-d4ff-57da-81dd-2aa44bd1cdbf | note | Frequency - 1 test per lot.
e82ad8bb-5d63-55ba-b493-617779f660fa | note | ○ "1 test per layer of bedding for bedding materials."
6505258c-50fe-5498-909a-6ec23215c323 | note | Acceptance Criteria - Bed Zone – Minimum 90% SMDD
cdbf78aa-742b-5d44-acd4-73ad8c9d8c0a | note | ○ Side Zone Not Subject to Vehicle Loads – Minimum RD of 95% SMDD
224642d9-8551-5dfa-9f37-38db447150ec | note | ○ Side Zone Subject to Vehicle Loads – Minimum of 95% SMDD
7185abd0-f6b6-5e6d-9992-fe193d868633 | note | ○ Overlay Not Subject to Vehicle Loads – Minimum RD of 90% SMDD
20b777a5-0948-5cab-a93d-a92f0a9be3d4 | note | ○ Backfill Zone Not Subject to Vehicle Loads – Minimum RD of 90% SMDD
a6406e74-85d9-50e7-bb1f-e5c15ddfa32d | note | ○ Overlay and Backfill Zone Subject to Vehicle Loads – Minimum 95% SMDD. Top 300mm under pavement to a minimum of 98% SMDD.
c3136cf7-8b38-5165-872c-2c5d937abe76 | note | Reference Documents - Cl.16.5.6. 1 (b) (iv)
db9b4411-efa6-5856-af78-2ea2b9335782 | note | Inspection/Test Method - Site Inspection
f82995cc-38b0-5b15-a358-a96ca9566be0 | note | Record of conformity - Test Records
473aac9c-b16d-5edb-bb4d-33375d1f8a79 | note | TP
d5d91f95-4800-5240-bfec-fc3ad1f31973 | note | Responsibility - Project/Site Engineer
af50add4-63eb-5738-b5a5-38eb32e83ab0 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
4bfba408-c2c7-5b13-a5b6-2aac8afb6c80 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
bd8aa650-6082-5eb0-9fb1-0784fb190a53 | textbox | Print Name:
07933e25-3d1e-5871-b20e-a61376c04a4e | textbox | Position:
94923ded-cd73-539a-81ee-c1c46804e037 | date | Work Completed On:
9c06ea5a-c74f-5bfa-9993-ce5fe6ee7f38 | date | Date:
83dcff00-7f03-54c5-96ff-8dfbf2083bb1 | checklist | FH-ZU2-QU-ITP008 - Lime Stabilisation / Subgrade Improvement - Rev 0 | itp | ITP008 - Lime Stabilisation Works
ff951edb-ead3-5ac5-97d7-0fdf5903d931 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Materials and Trials
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
f80ad63e-e054-58a6-a576-5a5156f8f8f3 | note | Frequency - Prior to commencing works
34372137-72c1-5b78-8857-0f4f56117113 | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex.
580de26a-94ed-5a77-9d34-68c0de8454b4 | note | Reference Documents - Aconex
5884289d-b391-508f-8f26-6eb97aee0dc9 | note | Inspection/Test Method - Visual Inspection
2221d813-5b0e-555c-b17a-b06903a82588 | note | Record of conformity - This signed ITP
1641ee97-6204-5c83-9048-3a8b6c09dcc5 | note | HP*
0916181f-7bd9-570f-ba06-450763029d6b | note | Responsibility - Project/Site Engineer
3a82f130-c2e3-5900-9703-54d723e73696 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
2c1d7258-8000-5b31-8f79-226a154efb79 | note | Frequency - Prior to commencing works
417cbc72-d3c4-5e70-9d6b-6d7fd9543fa3 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
f58b910f-8b97-58b0-9ec4-8d835fad21a5 | note | Reference Documents - PSP, EMP, TMP, WP SWMS
16c2ed29-62a0-56d2-a6bd-dcc04d5066c9 | note | Inspection/Test Method - Visual Inspection
c098280e-eab5-5450-82a7-3064d0f70f3f | note | Record of conformity - This signed ITP
4a2d40a3-38c1-5039-a5f4-dd646da1fe9c | note | HP*
cc8e0828-610c-5047-af96-86a758dd60ef | note | Responsibility - Project/Site Supervisor
17c04995-8757-5c6f-82eb-4b3d59be076c | date | Date Completed:
65eca0b2-e9e2-5d31-b703-45bbc204d847 | checkpoint | 1.3 - Current excavation permit
48755452-95f8-5c14-a233-f2e1cf26d6fc | note | Frequency - Prior to commencing works
b01f95de-178b-54ed-aeb7-b45562fdd472 | note | Acceptance Criteria - An Excavation Permit and an Isolation permit issued by Melbourne Airport. Fulton Hogan Excavation permit issued to plant operators.
fbbb0ee7-a34f-5610-bf1a-f5a488b2f235 | note | Reference Documents - Excavation Permit
d7fb0750-fc55-58dc-9eed-a9c56f8dc487 | note | Inspection/Test Method - Visual Inspection
4d53328b-f3e0-5e07-9229-c4368426e0b3 | note | Record of conformity - Permits
a28cb457-3300-5049-a9dc-6df79138d9f1 | note | HP*
16159f6c-a4d3-5c8a-9ff3-26033da1286f | note | Responsibility - Project/Site Foreman
b1e6b55d-eb1d-59ed-94ef-517a38151dd1 | date | Date Completed:
14c56455-f0de-5f93-9717-18fd02274123 | checkpoint | 1.4 - Preceding Lots Satisfactory
7b4d2be7-586c-5c08-92ec-a97afa14a7d4 | note | Frequency - Prior to commencing works
5a0cab34-2cd9-5151-83c4-bffc7a581e96 | note | Acceptance Criteria - Review ITP004 (Select Fill placement) and ITP003 (Stripping and bulk out) has been completed to a satisfactory level
d8e0fc77-3146-5441-a683-eca1b40121a0 | note | Reference Documents - ITP004, ITP003
11225a67-461e-574a-a52e-67f98e2149e9 | note | Inspection/Test Method - Visual Inspection
a50494c7-dc42-5d61-9716-1ad5c838a926 | note | Record of conformity - This signed ITP
c01588dc-e681-5eb9-ac50-cf96b17b44ea | note | HP*
947156b6-065d-5acf-b73c-792903b506a4 | note | Responsibility - Project/Site Engineer
2a7c5747-5127-549f-967b-707955a736f5 | date | Date Completed:
76b2ed20-883d-56e1-9e50-63150676e11e | checkpoint | 1.5 - Test Pits
7c8519cf-ff0c-5c02-aa96-9b158f5e6e29 | note | Frequency - Prior to commencing works
41a79849-3252-57fd-b30f-d4a68214ffbb | note | Acceptance Criteria - Test Pits have taken for the works area and suitable lime content parameters have been established. Test Pits should be taken at least one month prior to works beginning.
71daa2cc-6103-565b-b46c-98841bbca874 | note | Reference Documents - WMS003 – cl3.1.9
57acbe24-3046-54bd-bb53-a17a9127cecb | note | Inspection/Test Method - Visual Inspection
64134581-a21c-506b-99a9-d0d1c880f2a9 | note | Record of conformity - This signed ITP
ea9433d0-78af-51f7-94a0-b0b613798d59 | note | HP*
f22378cc-3fca-5bf0-b859-26e4d26a13d4 | note | Responsibility - Project/Site Engineer
545db90f-ab5b-53d7-bea8-b422883bd1d6 | date | Date Completed:
b3dd08dd-11b6-5f39-8645-239ea003b322 | checkpoint | 1.6 - Stabilised Lime Content
f2f31c7f-52ce-57ee-9395-40c354934c6f | note | Frequency - Prior to commencing
0e307209-0378-5981-9057-c4b66b6e204d | note | Acceptance Criteria - Stabilised Lime subgrade material shall have a minimum of lime content of 4% and a specified minimum strength of 20% CBR after 7 days of curing.
0ad1c593-f993-5554-b867-61a4f26394a8 | note | Reference Documents - Spec cl. 3.3
dfe53d81-bbca-5d9e-8f62-4e024c45e26c | note | Inspection/Test Method - Testing
21a7fda0-7769-5e6f-9181-6b849c545dfd | note | Record of conformity - Test results & This ITP signed
083f471c-d4f2-5af5-aaf9-70e82188470f | note | HP
cea4568a-f969-58c2-b43b-f9e846f19f75 | note | Responsibility - Project/Site Engineer, Principal’s Representative
d0ac1f16-ef5b-5c04-b294-6e28176e1e57 | date | Date Completed:
a36502c5-adb9-560d-a70d-678505437c86 | textbox | Principles Rep - Aconex Ref:
83aa5d6c-d189-5195-a97a-4c1a535c3e2e | signoff | AUTHORITY HOLDPOINT
1e3af235-d8a6-52b7-8154-473184406420 | checkpoint | 1.7 - Stabilised Soil Trial
e3d0b6f7-6262-5ae7-a116-cdf8203cc42b | note | Frequency - Prior to commencing
2e2fcecc-d65e-5881-8a0f-c4e3d62082c6 | note | Acceptance Criteria - Trial of the Lime Stabilised Subgrade is greater than 500m2 to demonstrate that the Subgrade is able to meet the required specification.
d9320f77-f9cf-5415-aeee-ad3e50d4eeb0 | note | ○ If trial is approved and accepted by Principal’s Representative. Trial of Lime Stabilised Subgrade will form the completed Works.
764a3254-a6cd-5bb3-8d96-1553077c9681 | note | ○ Principal’s Representative to approve trial before commencing Lime Stabilised Subgrade placing.
c74c4ef1-a31a-5983-b31f-08be016efe25 | note | Reference Documents - Spec cl. 3.6
ee59310b-da9b-5b45-944b-c2caf07af9ba | note | Inspection/Test Method - Verify
97a2130d-f4a2-5239-b27e-9e5f00e946b7 | note | Record of conformity - This ITP signed
f0486ae8-36d6-593f-af18-abc1300c6ef1 | note | HP
f78d5313-a3c9-5c16-9805-4ae05ace1554 | note | Responsibility - Project/Site Engineer Principal’s Representative
8f783d79-6766-59c1-bb70-a94fb669fd07 | date | Date Completed:
c36a71d2-164f-57c8-9dfa-96c797a967ac | signoff | AUTHORITY HOLDPOINT
92110380-56da-5e6c-8b29-049697713c30 | section | 2.0 - Subgrade Preparation & Replacement
639e9b05-062e-503a-92c8-f9b52bb2162b | checkpoint | 2.0 - Pre-treatment of earthworks
62101956-cfd2-56c5-a143-4fcaba515afd | note | Frequency - Each Lot
ca2ab39e-38b8-5645-8e8e-460eeec59cf4 | note | Acceptance Criteria - Inspect subgrade that will require lime stabilisation.
f7698896-93d5-5474-af2c-25a6768a2d96 | note | ○ Subgrade that is excessively wet and/or contains rocks greater than 60mm to 100mm, subgrade will need to be removed and replaced with site won material.
449ef220-c86c-57a5-9b93-86589310e7a8 | note | ○ No testing or proof rolls required on replaced subgrade
e925ddb6-f95f-555d-bd8a-84e3a6919e3e | note | ○ Survey to for any excessive high and/or low spots. Fill / excavate spots as required.
6574d0fc-589f-501c-b9e6-d4e591f900c9 | note | Reference Documents - WMS008 – cl 3.2.1
d934765e-d9f6-599e-85ab-b2db351f6738 | note | Inspection/Test Method - Verify
2d74c1c7-55a6-5095-a646-e3a7e197179d | note | Record of conformity - This signed ITP
9c64b3e9-bc04-5d0a-b882-244b2a0eb039 | note | IP
6198c2fc-43cc-59eb-be6f-1ed67fefda31 | note | Responsibility - Project/Site Engineer
fc7a943e-af06-5ce0-ad19-febd7032786d | date | Date Completed:
c293051d-8e81-5993-be55-a414c1752978 | checkpoint | 2.1 - Rip Subgrade
0ed5f65f-3dd4-572f-b3f2-fc4a6da3a75f | note | Frequency - Each Lot
289ff85d-0e0f-52af-a6c4-b533252d1c95 | note | Acceptance Criteria - Prior to spreading lime, the subgrade is to be ripped and pulverised to at least 400mm
78a69a18-ef9f-5a5f-b19f-44f9a9e27cfa | note | Reference Documents - Cl3.7
07a86b6f-2f5c-53df-9cd7-e2343a34de4f | note | Inspection/Test Method - Verify
8ebee48c-0faa-5a95-8e7a-c814d37c73e5 | note | Record of conformity - This signed ITP
8987659c-3dd4-56df-8cee-3eafa73c79e0 | note | IP
0978e5f5-b066-569d-8337-01eadd85b626 | note | Responsibility - Project/Site Engineer
e412f8a9-a9a1-5572-a8f5-fca294ade8de | date | Date Completed:
1a1bf616-437d-580e-b174-4d67646e5283 | section | 3.0 - Layer Placement
0d246930-b701-58d1-9f0f-0403386ba8dc | checkpoint | 3.1 - Layer Parameters
99e44411-a4ad-5fcb-830f-e0d514ee55f7 | note | Frequency - Each Lot
9668753c-07fd-5ae3-9a2d-500b9dad8b2d | note | Acceptance Criteria - Summary of Layer Parameters:
e7987681-aecf-5adf-9e89-02b191d8bde4 | note | ○ A Lot is defined as one days production
fddf2ea4-53ad-52e6-9b97-31c9a6cd1f6a | note | ○ Min depth of 300mm for PT01, PT03, PT08
0b2f3865-99cd-5ea6-a77a-5b4f53aada8e | note | ○ Min Depth of 400mm PT02
a12d4f6f-4b99-52bd-a159-699b10b67c91 | note | ○ Shape: <12mm over a 3.5m straight edge
042cf666-81dc-5ef0-a900-b9ebf2205b1a | note | ○ Surface Level: -25mm to +0mm
d55ac57e-4ef5-53a8-a429-8559b87327f8 | note | Reference Documents - Cl 3.16, Cl. 3.14.3
f37964be-4804-592f-8472-6ac8abb7c365 | note | Inspection/Test Method - Verify
b6018f76-a667-5ba2-857f-b65ce20ea6e5 | note | Record of conformity - This signed ITP
4244dc42-aa65-5ad0-b98b-0e643ce23f76 | note | IP
ee8912da-58a6-5c54-a045-2dcd5397f24e | note | Responsibility - Project/Site Engineer
70f4e856-2faf-59ca-9345-bdf1a240d1f2 | date | Date Completed:
e188e23f-7387-546a-be1a-ef1b527e3391 | checkpoint | 3.2 - Prior to Works Starting
f09b7eeb-84a5-5d2c-a892-80da7ab3a55c | note | Frequency - Each Lot
8c0af34f-fa40-554b-af73-418ad7d50957 | note | Acceptance Criteria - Check weather forecast for rain and wind. Works to not beginning if rain is imminent. Works must not start or cease if wind increase over 15 knots.
e886f363-b2b7-5d65-a0d3-74b740221ef7 | note | Reference Documents - Cl3.7
428c7c0b-bcd8-5ef4-b124-ab659e25d26b | note | Inspection/Test Method - Verify
edea983b-1021-5459-87af-07fad8ad33ea | note | Record of conformity - This signed ITP
40298fdd-eece-5a4d-bf52-24aa79d1721d | note | IP
840a110e-9bae-54b5-b7b6-7aa8312005d7 | note | Responsibility - Project/Site Engineer
2097ba3d-a9c1-5756-a462-013f70a97ea0 | date | Date Completed:
7cff3135-aaaa-5a07-be57-d8a647bc4b01 | checkpoint | 3.3 - Spreading of Lime
78e2769e-331f-565f-ac61-b2172501c3a3 | note | Frequency - Each Lot
ee78259e-b187-553c-a8f8-a39f8b65891d | note | Acceptance Criteria - Lime to be spread uniformly over the prepared surface at the Lime spreading rate calculated.
33187a45-846e-52b6-ab6a-5d438b34c101 | note | Reference Documents - Cl3.7
ca0f43a1-fc2a-5041-9c08-4906d7047af9 | note | Inspection/Test Method - Verify
d8bc3daf-9fff-5d39-a2f3-3270cfd3f663 | note | Record of conformity - This signed ITP
0976379c-eeb2-55c7-91f8-d74f1929eb49 | note | IP
4ee44097-ec15-5b67-b8c6-59ed3780f975 | note | Responsibility - Project/Site Engineer
420033b4-467d-50e9-a35e-c3d53789f22b | date | Date Completed:
66449636-bf24-5bb3-86e0-ea99af02cfa4 | checkpoint | 3.4 - Spreading of Lime
a75badb0-eb77-5a41-8fd7-57d54ba88ce7 | note | Frequency - Once Per Hour
b74e3e83-f0f3-54a3-affc-686b1d414fcc | note | Acceptance Criteria - Lime spread to be checked every hour and shall be with +/- 5% of the specified amount. An area to be checked is required to be not less than 1x1m2.
3390d410-7f7c-5242-8e9f-d6a14c96a9d9 | note | Reference Documents - Cl3.7
94907931-d99d-5f4a-9ed1-72a7bd40a53c | note | Inspection/Test Method - Verify
1d6bc099-7de6-521e-a53b-c1dc33af1031 | note | Record of conformity - TP
6bce729d-7697-5a49-bed7-d09bba0b0fdb | note | IP
ad236bae-a6ed-5aed-89d2-cbd80ce624e7 | note | Responsibility - Project/Site Engineer
704bcd53-dd10-5f8e-abf6-1d85f6e1e264 | date | Date Completed:
933cace5-29ee-5793-b62c-7744cf4d97ac | checkpoint | 3.5 - Mixing
342dc891-c403-5f90-b824-bbf8f7a88c87 | note | Frequency - Each Lot
390ce6f2-6e8b-5b9c-af40-e7318e0b4f9e | note | Acceptance Criteria - All lime to be mixed to the specified depth within 8 hours of spreading. Mixing passes to overlap to ensure subgrade is mixed twice as a minimum.
cc5e43e5-aeea-5ebe-89e0-150f5c893321 | note | ○ Where possible, adjacent material will be placed within 1.5 hours of initial placement to avoid joints from forming.
1dffa4ef-977c-5200-9704-d4057650e30f | note | Reference Documents - Cl3.8
6bfe17ce-16bc-52bb-a1c0-3e907940d531 | note | Inspection/Test Method - Verify
e0aabdf2-0f0c-51bd-855e-f54daab64e09 | note | Record of conformity - This signed ITP
d0540783-c182-5522-b955-56420d6d484a | note | IP
994e21c9-ca3a-5509-a5a3-0cf0d1059d7e | note | Responsibility - Project/Site Engineer
9a5228ee-ec2b-5d18-8311-95a576bf01a8 | date | Date Completed:
ff71ab95-b7a7-5d0b-b295-91823ce88429 | checkpoint | 3.6 - Mixing
c562766c-54bc-512f-8f72-d70eadefc4f0 | note | Frequency - Once Per Hour
c1f928cf-02bb-562e-8be8-3b04caaf0ac3 | note | Acceptance Criteria - Approximately every hour, mixing plant will record the depth of application to check compliance with the specification (300mm or 400mm).
ce08e854-5a2e-5f75-a0ce-ee62a04c30b8 | note | Reference Documents - Cl3.8
fddc46ec-5c36-548c-9341-af9ba77c9e32 | note | Inspection/Test Method - Verify
3718af78-1a8b-57a9-a532-0dea2ad1f0fc | note | Record of conformity - TP
6e7b5fd0-bb87-52f0-8aa3-de05d6a89a6a | note | IP
604b6d97-13ba-5a6c-a11c-15e0afee918b | note | Responsibility - Project/Site Engineer
9911afd3-d0e0-521b-bea9-867e1aa90967 | date | Date Completed:
3697a363-4bf7-5a6e-9fc5-ad0f8c7a4397 | checkpoint | 3.7 - Joints
d260d097-aab9-5437-a478-470276285dfb | note | Frequency - Each Lot
87275da8-6c25-52f9-a6f7-98b66d093217 | note | Acceptance Criteria - Construction Joints when required, will be placed to ensure no single plane of weakness. Construction joints of adjacent lots will:
56b137d2-41f8-5edb-9b14-5cb2bf5b70bf | note | ○ Longitudinal Joints – Will be avoided by overlapping adjacent lime stabilisation mixing runs.
3ff60da7-8cef-5b45-aac3-88eb76284fb9 | note | ○ Traverse Joints – Will be staggered to avoid forming a single joint.
09fc5b76-e89a-55e9-91a1-304745c6f012 | note | Reference Documents - Cl3.13
4f5cf043-d1a6-5402-9422-ec3286759824 | note | Inspection/Test Method - Verify
0f8796f9-0f68-5d9d-911c-4dd0df554f39 | note | Record of conformity - This signed ITP
91fc4eb7-572e-5e1d-b5bb-73b2d8d06491 | note | IP
59a162e2-9def-5e63-800f-f58f1cd41a8f | note | Responsibility - Project/Site Engineer Foreman
71be9b34-2f3f-51e8-96e1-c87052da0403 | date | Date Completed:
413572a0-25bc-542a-acdf-8a670d1944f6 | checkpoint | 3.8 - Compaction
98edc022-ce50-597f-a49e-fd5f9cd8f64f | note | Frequency - Each Lot
a802c0d7-976b-507a-82ab-78328487457b | note | Acceptance Criteria - After satisfactory mixing, compaction shall commence within two hours and be finished within eight hours of mixing completion. Additional moisture may be added if required.
4c8d3682-ad1a-5729-9c6f-2e04e34da9f8 | note | Reference Documents - Cl3.11
e5693786-39f2-5aae-81e9-a3617205b081 | note | Inspection/Test Method - Verify
e15bc505-3a49-52dd-9b7c-9ed1054f2c30 | note | Record of conformity - This signed ITP
43fc5fae-6188-59b1-82a8-c5d0d4f56eeb | note | IP
a7256504-2d31-5e6a-bb32-f6b1487cad93 | note | Responsibility - Project/Site Engineer
813850de-8025-5607-84f0-7cdf4c1621ec | date | Date Completed:
2d7fbba9-dc8c-5587-8a0f-e95b8eb31515 | checkpoint | 3.9 - Trimming
b2c11689-93f9-520e-b751-4b92349a7772 | note | Frequency - Each Lot
70ccdfdc-aa8b-545f-9f9d-36c5789170e9 | note | Acceptance Criteria - Surface to be trimmed to +0mm, -25mm
a4867d15-b3ab-57ac-b389-76f5f082326a | note | Reference Documents - Cl3.11
2c8e1993-e02f-5023-82c6-ff4971f7b99f | note | Inspection/Test Method - Verify
21f15f9a-1bae-52d8-9b6c-b7f6cf06e552 | note | Record of conformity - This signed ITP
e4704b06-5569-5e33-a586-8cc50ab7f1c9 | note | IP
1357d1c2-2430-5df4-85a6-b9c7d2652ddd | note | Responsibility - Project/Site Engineer
e44933a5-f7c7-5f2c-a310-b86a294811e4 | date | Date Completed:
c0af1ea1-39d6-5efa-83e4-1636172927dc | checkpoint | 3.10 - Protection
3a917592-6749-5df9-b2e0-1e85c23e2f6f | note | Frequency - Each Lot
e2b99457-d65b-54d8-8fef-e7c361627566 | note | Acceptance Criteria - As soon as lime stabilisation activities start, no construction plant to travel across works zone (other than those involved in the operation for 48 hours minimum.
2dd506ec-22c9-5e37-a1bf-fc4acf1eedc7 | note | Reference Documents - Cl3.15
17f9f7c3-91cc-5b6c-8462-621aa1bfd5a8 | note | Inspection/Test Method - Verify
a3d5d5de-4b52-5924-9d24-2c0b71b05c48 | note | Record of conformity - This signed ITP
e7639432-5a5f-5ccc-88ff-b79580bbf1c5 | note | IP
7e023d29-6b28-5d62-b994-407b63ef41fd | note | Responsibility - Project/Site Engineer
eb4df604-5d71-5666-8157-65e62f99e767 | date | Date Completed:
f84bb287-d950-50cb-8abc-00e5cc9832d7 | checkpoint | 3.11 - Curing
f5d664e1-3302-5239-b31b-bb3d32877dae | note | Frequency - Each Lot
3634ecf6-60c9-5eb9-9428-1f7e010dcc54 | note | Acceptance Criteria - Curing shall commence as soon as practical. The curing period is 48 hours or until the succeeding layer is placed.
61592bc7-ee26-52a2-a062-6e051423a52d | note | Reference Documents - Cl3.15
7180bd48-55d1-52eb-bc1a-3e79860497ec | note | Inspection/Test Method - Verify
17d9e9eb-a333-5f92-a309-9d214f33daa2 | note | Record of conformity - This signed ITP
2ec1438f-9013-52d1-822b-308c154d145f | note | IP
02640a26-aa0f-5092-8fb2-64afa27ad078 | note | Responsibility - Project/Site Engineer
77d43f30-4dbf-58d2-86f2-a8ea53be2978 | date | Date Completed:
6ca566ab-1509-5601-bcce-96cd27b957db | section | 4.0 - Acceptance – Lime Stabilisation
347223d9-59ca-5890-96d1-49b7315b1ce5 | checkpoint | 4.1 - Proof Roll
2f9353b6-e54c-554e-8c1b-d099c954ad0a | note | Frequency - Each Lot
36368a93-d957-5fdf-89b4-f9e013b6bb09 | note | Acceptance Criteria - Following completion of the curing period, detailed trim and survey conformance, the Principle’s Representative will be invited to a proof roll (24 hours notice). Proof roll will be accepted if no rutting greater than 25mm is observed. Proof roll will involve using a heavy vibrating roller (in static mode)
c68d0f35-ea92-50b2-a8f9-67e617c28a42 | note | ○ Proof rolling of the subgrade will be approval to place Sub-basecourse or Basecourse. If rain falls on subgrade prior to placing next layer, a further inspection will be required.
01c1e634-186b-5a82-a4b8-b45d73df62b1 | note | Reference Documents - Cl3.12 Cl4.6
87be2623-dfbd-595f-891c-8be21e24dbf4 | note | Inspection/Test Method - Verify
18dcd2dc-0dc5-50c3-9665-7cd0923ebd3a | note | Record of conformity - This signed ITP
6fc411fb-3ae7-5906-8a89-562298867e11 | note | HP WP HP HP
d1fa4d52-e8b4-590a-968e-cf95e9142cce | note | Responsibility - Project/Site Engineer Principle’s Representative
66401dcd-82fa-5286-aead-1904100de9e2 | date | Date Completed:
9d6eb9f1-cb88-5972-8c60-c08da8aff17f | signoff | AUTHORITY HOLDPOINT
62d9d645-c8d9-5c1e-8705-8289f13a5ebb | checkpoint | 4.2 - Surface Smoothness
837b0e22-2d8b-5699-84c5-515f36d75e55 | note | Frequency - Each Lot every 10m
de08aee8-f886-5796-a501-5eabd7247879 | note | Acceptance Criteria - Long straight edge surface not to deviate by more than 12mm over a 3.5m long straight edge, following subgrade treatment
55319a9f-9797-5e69-859e-50134128725b | note | Reference Documents - Cl3.16
16184e99-8bbd-5666-ad3a-1593c7749c5b | note | Inspection/Test Method - Verify
b9fa94eb-211f-52da-8503-97c347b9b63e | note | Record of conformity - This signed ITP, Results Attached
badb7c5b-c62c-5b51-9f76-70912fae58ac | note | TP
0789e41b-dcac-5f88-996d-89e182908747 | note | Responsibility - Project/Site Engineer
b79112a3-6ced-57fa-b89d-fddd9e664d09 | date | Date Completed:
574d05bf-851b-5876-a180-0a560a77c85d | checkpoint | 4.3 - Strength Testing (CBR)
d85a453c-5089-51ed-954f-8e86db541710 | note | Frequency - Each Lot – Once per 1500m2
f5a104ee-3f30-5158-8fbb-ace6a4d16cbf | note | Acceptance Criteria - To exceed 20% CBR after 7 days.
dcfc4b1e-0919-542f-b37d-11d9d298b83c | note | Reference Documents - Cl3.16
9aafccc7-b587-5e41-9e41-508f824c8f8e | note | Inspection/Test Method - Verify
7d77674a-c72a-53e8-8a83-e1b6063b07ef | note | Record of conformity - This signed ITP, Results Attached
da13dbcc-c9e4-57d0-8957-1788082fb56b | note | TP
d639452d-ccd1-5669-8883-d3a580538630 | note | Responsibility - Project/Site Engineer
a45fc774-3ef6-57c2-b1f7-690c9bddcf71 | date | Date Completed:
77efabb3-9ddf-5f45-b887-19ac7988e251 | checkpoint | 4.4 - Field Dry Density
5b50c56a-2fb2-56de-a1a9-589bcd9b2868 | note | Frequency - Each Lot – Once per 500m2
13f56cac-10c3-5539-9859-e527e2da735f | note | Acceptance Criteria - Maximum Dry Density used is lime stabilised subgrade 100% using standard compaction.
f62b5305-d129-5dbc-bf9c-8ff4bafc6a11 | note | Reference Documents - Cl3.11 Cl3.16
92188a49-9e45-5703-b6e1-72394050c8e9 | note | Inspection/Test Method - Verify
458eb129-b3d5-54be-9309-1a51f9e67403 | note | Record of conformity - This signed ITP, Results Attached
f5b3e371-e308-5ab0-b6ae-b1becb453e47 | note | TP
a6ee8b2b-41ec-5e59-a54f-86f1f31451df | note | Responsibility - Project/Site Engineer
7fb847a3-e1dd-5c9b-871a-e52592ada559 | date | Date Completed:
3b380c3c-68d2-570c-840f-61931a66179b | checkpoint | 4.5 - Surface Level
f264f4f4-7d4f-54d0-8b2f-52a809c0980a | note | Frequency - Each Lot
a9239d3b-556d-58a1-9f60-bb446b8a5ee5 | note | Acceptance Criteria - Stabilised and compacted subgrade surface layer to comply within -25mm to +0mm from specified levels.
dd91c709-302e-59a4-9b57-787abfb44091 | note | Reference Documents - Cl3.16
5c788dd4-2a4d-591d-bc3d-cf3bd5319e8d | note | Inspection/Test Method - Verify, Report
03035fda-fbdf-5aca-9ea7-6a19bf79a240 | note | Record of conformity - This signed ITP, Results Attached
a3606e88-472f-5d9d-8a9b-d3aa27803cec | note | SCP
22446a72-33e9-53a1-a9d8-daa4db972c79 | note | Responsibility - Project/Site Engineer
8536f0c4-4dcf-5494-a569-c3e75eed94ca | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
77834e6f-6574-54f0-b03c-6bcabe6cb4dc | note | On behalf of Fulton Hogan, it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
e9b4af31-26aa-5a17-b1c7-baaf6919ffd1 | textbox | Print Name:
a304cf96-b429-5255-a2df-662eb05d02a4 | textbox | Position:
7de9a745-74e3-5528-8e04-9e99c94961b2 | date | Work Completed On:
fb9de0d3-dd9f-5aff-9a96-ab452a1610b2 | date | Date:
fc56461e-5b2b-4a2b-92c7-0b8442422da2 | checklist | FH-ZU2-QU-ITP009 - Unbound Pavements (FCR & RCC) - Rev 1 | itp | ITP009 - Unbound Pavements (FCR & RCC)
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
22b60133-d07e-5778-afbb-3104cb451e98 | note | Frequency - Prior to commencing works
90628709-661f-5c1d-808d-3f9633505536 | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex
bc77cecb-25db-54e2-a46f-f50316ce64bd | note | Reference Documents - Aconex
248e7c02-a029-5336-9878-3422c829cf56 | note | Inspection/Test Method - Visual inspecti on
505c13d3-3958-55d4-b28a-dbe56fcb6509 | note | Record of conformity - This signed ITP
d9b9a31e-4fc1-55c9-8cf1-e24191b8f35b | note | HP*
577c368a-5703-5a58-b59c-18e92dbc9be8 | note | Responsibility - Project/Site Engineer
0ca55223-b839-58b1-9ea2-63b876b41d8e | date | Date Completed:
0ee48894-54ec-5653-949e-3aecb94d8a6f | checkpoint | 1.2 - Implementation of all measures and controls, weather, and material properties.
d49a7852-f9a9-5121-afd2-663081afa613 | note | Frequency - Prior to commencing works
1e3e4950-6df5-54d8-b002-d4b18ac8c1d9 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
46aa07a5-24fd-5c8d-8bf3-189213104141 | note | ○ Check weather prior to starting any works.
4274f253-54a3-50bd-9ec8-7b1601fe3d02 | note | ○ FCR material used for the works in accordance to VicRoads Class 2 Crushed Rock.
9351f45c-6020-5acc-acdf-0786a7e52f32 | note | ○ RCC material to be used for the Works in accordance with VicRoads Class 3 Crushed Rock.
67de20a2-0256-57b6-850f-aadb800e0d07 | note | ○ Checking underlying layer ITP’s (subgrade ITP008 and select fill ITP004 has been completed)
337e8923-b57f-5282-856b-d3a6b8d18b41 | note | Reference Documents - PSP, EMP, TMP, WP SWMS, Spec Cl 4.19, Spec cl. 4.1, VicRoads Technical Note 107 Spec cl. 4.6
b918f1ef-0da1-5bc1-8bb8-6c02335de461 | note | Inspection/Test Method - Visual inspection
6f531f46-a05a-5c16-b04e-195d1c3f4a93 | note | Record of conformity - This signed ITP
3b7b3517-c997-5002-97c8-f1aa5f1e7cae | note | HP*
2de72f79-4994-57b6-a35f-9b3e18858774 | note | Responsibility - Project/Site Engineer, Foreman
baa8b9fa-f889-5d30-8dea-a71cc722d564 | date | Date Completed:
b55c3da7-c29e-50dc-b5c6-6c3d6d4c85da | checkpoint | 1.3 - Material Report - Fine Crushed Rock (FCR) Material & Recycle Crushed Concrete (RCC)
08f8e815-db8e-5c04-a20e-779ea9c698a3 | note | Frequency - 7 Days - Prior to works
f23fc5f1-f6fb-5435-ad79-c5ecdcd035c6 | note | Acceptance Criteria - Material Report to be submitted 7 days prior to works to include;
1344dbf9-3674-54ba-b047-2f9a512d67de | note | ○ Source and Quarry location
dc8222db-ef8f-5c16-b274-2905dc7a31d3 | note | ○ Quarry material is sourced from.
a8449f49-f55e-5365-8100-695b2068f934 | note | ○ Material rock type and petrographic description
8b784087-184c-59ef-b6b6-040c79a2a485 | note | ○ Historical test results
836aacce-c6f4-5341-b85b-04b293e861dc | note | ○ Method of processing and transportation
52202e1b-799b-57e1-bfb2-b5a8c390d48f | note | ○ Material summary of the results of recent test on samples of the material from the source
e2e34f1e-e0b2-5faa-bb77-6746fc484680 | note | Reference Documents - Spec cl 4.20.1
c4580524-9128-5583-a7bf-4fa86d4a90ec | note | Inspection/Test Method - Verify
6f6417f1-69f8-5ad5-984c-fd198378675f | note | Record of conformity - This ITP signed
c8da58f1-5852-54c6-b606-35386ce293d9 | note | HP
27f7bd55-d87c-5dde-b69a-8a690d4a1c5c | note | Responsibility - Project/Site Engineer, Principles Rep
98351715-983d-55b6-b5e4-29818398c2fb | date | Date Completed:
f90cc78c-5577-584a-bf6f-2baea0a79d8a | note | Principal’s Representative - Aconex Ref: Holcim RCC Class 3 - DCWC Mgt-GCOR-009582
6ed4e75b-7d7c-59d4-860f-84f44b2920d0 | note | ○ Holcim FRC Class 2 - DCWC Mgt-GCOR-009581
f1140fed-3d65-5000-a675-33f0cf450936 | note | ○ Stirling Class 3 - DCWC Mgt-GCOR-009565
8b2d5395-ceb8-53cb-8eb1-c7add6510501 | signoff | AUTHORITY HOLDPOINT
ec34d278-5586-5c2a-99c8-01e2abad83a0 | checkpoint | 1.4 - Reference Samples
525ba691-af22-5b05-b06f-d97f2febed12 | note | Frequency - 5 Days prior to works
d6fbd216-8984-5446-82cf-f06bf7078519 | note | Acceptance Criteria - Reference samples to be submitted 5 days prior to works commencing. Two bags to be taken each weighing 25kg. One bag submitted to Client, one retained by Contractor
393a62fb-dc1a-51af-820d-43d92dcf2ed5 | note | Reference Documents - Spec cl. 4.20.2
81cb4669-886b-5347-b152-1895c2aef53c | note | Inspection/Test Method - Verify
3df23d20-62cf-5417-b4eb-60cb6864ab05 | note | Record of conformity - This ITP signed
afaad2f4-dbb5-5fd8-87e6-401b5bf4febd | note | HP
54753b28-df32-5121-a510-4e413fb619cc | note | Responsibility - Project/Site Engineer, Principles Rep
ee76c1dc-3531-5a2f-8c1f-475d8f250b39 | date | Date Completed:
9ddd2561-c351-5c44-858a-2e4143344a3b | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000825
d95e7d5e-6bf0-5924-b391-1cfea39c7d6c | signoff | AUTHORITY HOLDPOINT
86350ec1-aec3-5802-aaf3-a14a45b6d2ff | checkpoint | 1.5 - Trial Section
65684dbf-f369-509e-a5e8-b314c3fd8819 | note | Frequency - Prior to works
bafdae1c-25bf-5ae2-9cd0-6608d8ef0a98 | note | Acceptance Criteria - Trial section to be completed with Principles Representative approving the use of the spreading machine.
6c6faa28-2c6a-59b8-bc47-3393a4e05f95 | note | Reference Documents - Spec cl. 4.7
af7d6c18-3dcc-50bf-b3f8-53ce25ab318e | note | Inspection/Test Method - Verify
17a066a2-c53c-51e9-a713-f8604f6dba5c | note | Record of conformity - This ITP signed
eeb60278-237d-56da-890e-daecf0bb1cf4 | note | HP
b8253941-a061-5b59-a6f1-8d269d6fe801 | note | Responsibility - Project/Site Engineer, Principles Rep
a035e09f-3c92-5f13-973b-02f96ca5b1ac | date | Date Completed:
50b5aab5-7a04-53ea-a4dd-31d851a2dce3 | signoff | AUTHORITY HOLDPOINT
690716ed-b540-5814-804e-da1a18d341a5 | checkpoint | 1.6 - Compaction Equipment
b945be75-e6e9-57a1-8123-6e8633aab849 | note | Frequency - Prior to works
e74b505a-9f5c-54a0-aeea-6de10bb335eb | note | Acceptance Criteria - Pneumatic tyred rollers having a weight of 27t (min roller weight can be 7t spread across 7 wheels). Tyre inflation pressure to be checked. A 15t to 20t smooth drum roller to be used.
2801421f-e441-58d5-bb6a-16a4d3e6997a | note | Reference Documents - Spec Cl 2.4.3 Item 84 Tender Clarifications
7714caf1-b8f8-5140-a270-f11a742d03c8 | note | Inspection/Test Method - Verify
c68e6fd7-3cf1-58cb-b9e5-ef98680eb80c | note | Record of conformity - This ITP signed
1ca6e76d-4a10-59f8-9af4-a8cfd70ad21c | note | WP
de947921-e38e-5dbb-98de-20d29f6f2cf3 | note | Responsibility - Project/Site Engineer, Principles Rep
780ed8c5-c16d-5d7d-a120-b2874bf1d159 | date | Date Completed:
f1bd1704-9d65-5504-9073-a58e0fb450e7 | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000893
1d9506f5-f6c7-5206-bffc-81f4f4f90212 | signoff | AUTHORITY HOLDPOINT
282695af-0cd0-5fe3-8b64-3dcbc3207e5e | checkpoint | 1.7 - Testing Determinations
435afed8-b133-50ef-9159-3038e4e9ce4f | note | Frequency - Prior to works
36ad8297-35ac-522d-abb9-b2825c174034 | note | Acceptance Criteria - 1. Basecourse and Sub-Basecourse thickness test points selected randomly.
23450c8f-eb32-5958-a1f6-4c1070f0aa49 | note | 2. Field dry density test locations selected in accordance with AS1289.1.4.1.
b46d1e09-9f04-5e91-94c9-e815bb795a73 | note | Reference Documents - Cl 4.21.1
523cd7eb-bebb-5653-b8f3-ced01627075f | note | Inspection/Test Method - Verify
a6984f74-007e-5d32-81f4-43d2d0ae7149 | note | Record of conformity - This ITP signed
9d271944-3ad5-5014-8b38-573d1b5c08db | note | HP
c4dc7eef-31c3-51c3-8336-cd5de23a3ab5 | note | Responsibility - Project/Site Engineer, Principles Rep
4e0c42ad-439e-5855-9604-6d597d69fa7b | date | Date Completed:
466d62da-b64c-5642-9815-ed935f373305 | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000890
83a1d299-f349-508e-bab0-117c246c15aa | signoff | AUTHORITY HOLDPOINT
31f3573f-3cd4-53a2-bab5-d81150ad14d3 | section | 2.0 - Placement of Sub-basecourse and Basecourse
520af3e6-6af9-53b6-9cab-e0a37d5ddeeb | checkpoint | 2.1 - Layer Placement Parameters
aaa3edf8-61eb-55f2-97a1-d0fb08386030 | note | Frequency - Every Lot
16c77b6b-81f0-5b20-ad8d-8506d7ec2d02 | note | Acceptance Criteria - Summary of Parameters for each Lot;
3f87eaec-bfd5-5113-a5dd-c989fed0fec5 | note | ○ A lot is defined as one layer placed in a single days production of uniform material
ba7c17ca-eae9-5ba4-a3ff-214dac3491bc | note | ○ Max Layer is 200mm
322cb297-e6e8-5565-b3fe-48d519767cce | note | ○ Min Layer is 75mm
ce182ba1-c8fb-5c79-9cb4-9e7811cce7b1 | note | ○ Final Surface Level +0mm, -10mm (excluding intermediate layers)
3fcf686c-043f-5d65-9648-ea4b780b560f | note | ○ Shape: every 10m intervals, <7mm deviation over 3.5m straight edge (excluding intermediate layers)
2a7aa885-9c4f-5381-8ece-bb1b9ccba295 | note | ○ Material to be batched within 1% of OMC
2585bc1f-f9ba-51cb-839f-4f8d9b4863dc | note | Reference Documents - Spec Cl4.8, cl 4.21.2, cl 4.13
cced5364-2910-5d18-aa42-577b9981563e | note | Inspection/Test Method - Verify
8100ba46-80fe-5560-aca3-286dd0f42292 | note | Record of conformity - This ITP signed
be2c8188-b893-5606-951c-1d3052e63cd4 | note | IP
6d1c799a-1c5e-5479-95f5-52693cfb267f | note | Responsibility - Project/Site Engineer
c035320a-65e6-5da3-8edd-85233f228189 | date | Date Completed:
ab12b78d-7983-5acd-aa07-c177c46370e6 | checkpoint | 2.2 - Placement Checks
35f1d8ab-6103-59c1-8b59-7dbfdfd5a318 | note | Frequency - Every Lot
d330c613-67e4-5ca5-a41d-034019e87353 | note | Acceptance Criteria - During placement of the material check;
a0897ee6-0317-5245-b2d4-b7319354e90a | note | ○ Deliveries do not disturb underlying layer
c52be776-0b87-5bb4-9639-97923473720f | note | ○ Spreading starts from crown / high side where practical.
6558ad17-534d-5102-861d-33bdf6acdef4 | note | ○ Material does not get contaminated during placement / delivery
da1053c0-3a2a-5ac3-86fd-b3ecc6fd4402 | note | ○ Watercart is present to condition material as required
23130571-9585-5f82-a1bd-667592304329 | note | ○ Edges are cut / removed if dry of not compacted with abutting lots
25bb25f1-45b3-507e-b660-1bdfb628c3bb | note | Reference Documents - Spec Cl 4.8
35f5add3-e162-53d8-9bcf-6f098b9c662c | note | Inspection/Test Method - Verify
b7644ee8-0ce7-5f78-90af-aafeca592397 | note | Record of conformity - This ITP signed
5a905e00-c1e4-512f-9a17-ade2ccd58b44 | note | IP
19652dec-189a-5f21-8896-0766c8cb7a88 | note | Responsibility - Project/Site Engineer
2a0baffe-e984-564d-9c01-dab08964c6d6 | date | Date Completed:
03b653d0-0f2f-5bbe-ba99-60916a24386a | checkpoint | 2.3 - Compaction Check
58e6a7da-0a23-579e-adb3-07ffa5af4807 | note | Frequency - Every Lot
09efdcc0-9ad5-589b-9f7a-29a04ff56202 | note | Acceptance Criteria - During Compaction check;
112f68b3-7620-566d-bcbd-453cf4539fcb | note | ○ Heavy smooth drum roller of 15t to 20t is used for initial compaction
156bec7b-d118-5098-80a4-9f9811800889 | note | ○ Pneumatic roller of 27t will compact material for final consolidation.
63744c10-259a-59ff-aa84-ed5a2ec11330 | note | ○ A heavy smooth drum roller (in static mode) may also be used for final consolidation
1dcab749-3f6d-5dc0-8b70-8e6ccc60521a | note | ○ Watercart Present onsite for conditioning
55bdb2c8-4342-5857-baae-a10bdc7ecac0 | note | ○ Materials are trimmed to required shape and level
d22c4f0e-7900-552c-8a73-ef0db6e4ae0e | note | Reference Documents - Cl 4.10
1993e4bb-389f-5674-aac7-b01ba95c1fb1 | note | Inspection/Test Method - Verify
669b9d6b-f3ad-50de-bde3-67155680d007 | note | Record of conformity - This ITP signed
14eaa2db-1f06-5432-8e0c-27042f49ab02 | note | IP
6cd03551-ea7e-545c-bfad-d40f0419bc20 | note | Responsibility - Project/Site Engineer
045eb3cb-4193-5ec9-b4b2-f7ded14ec478 | date | Date Completed:
56c1eb5a-a610-51e7-86f1-f05ba8e1b5bd | checkpoint | 2.4 - Services & Culverts
cad1544e-6b90-53e9-b346-5cdaec13789b | note | Frequency - Every Lot
6ade1825-13f6-521f-80f3-e6df0e156981 | note | Acceptance Criteria - Check if any culverts or services are with the influence zone for compaction.
f01b9dd3-612c-5a17-a57d-010ef1513183 | note | ○ A general rule, FH will seek advice from the Principles Representative if any culverts, duct banks or RCP pipe are identified closer than 1m from pavement layer surface. If identified, Fulton Hogan will maintain a 1m exclusion zone either side from centre of service for vibrating compaction activities. Hand held DPU’s/whacker plate to be used in lieu of rollers in restricted areas.
67c452e0-d6b9-5f8e-a3da-b3d574687983 | note | Reference Documents - CL4.10
fa8211c9-abd1-57da-b54f-de0c6e5dbe35 | note | Inspection/Test Method - Verify
ffa561c5-3a1c-5b2a-8fdc-90801c716515 | note | Record of conformity - This ITP signed
33423efd-62ae-5c89-b304-dd78ede7b634 | note | IP
54f78c92-1f94-54e5-9290-23165c7f8f9b | note | Responsibility - Project/Site Engineer
d6d1b5b8-e9d7-5583-8a85-3068b4699540 | date | Date Completed:
af9dc4f1-7e43-5752-b5a1-15b8f94cf295 | checkpoint | 2.5 - Protection of Layer
b5def97a-8a82-52be-9c54-498ac337f247 | note | Frequency - Every Lot
f5abe81d-8f4d-510d-8885-fa3cc5fca33b | note | Acceptance Criteria - Protect area from undue deterioration by;
f417fc95-2acf-5b5c-8b72-7fc970c8db29 | note | ○ Section off area for at least 12 to 48 hours to allow material to dry back.
59af82c2-ee2b-55ae-9f1a-84ba3d796d2f | note | ○ If unable to do so, keep traffic to a minimum
7b0a10bc-80ce-5720-b786-07441ed72b4e | note | ○ Or ensure any traffic that has to cross pavement layers, do not follow the same driving line.
98124425-bbe9-54b3-9173-c49ea88147ad | note | Reference Documents - Cl4.17
941d9051-473f-561a-bb5b-246c9d4cf08f | note | Inspection/Test Method - Verify
4ca87943-c62f-5a1b-b82a-fc898998e077 | note | Record of conformity - This ITP signed
fbcb7b46-d64b-5e69-8d4c-558089c333e1 | note | IP
86dbe21d-b474-525d-b7cc-73d45852ecfe | note | Responsibility - Project/Site Engineer
c1acb8c3-0d37-5859-88bb-9dc12a60a61b | date | Date Completed:
ed4dca39-7158-53f5-b80c-2934cf975618 | checkpoint | 2.6 - Proof Rolling
44460523-6468-5e7d-8f76-60c382cfa5cc | note | Frequency - Every Lot
b7f9cddf-e0d6-57dc-b450-1557ea5a71de | note | Acceptance Criteria - Proof rolling will be undertaken at the top layer surface of the imported select fill material for under pavements using a 16T smooth drum roller (minimum), or a 15kL watercart (minimum).
1d13e8cc-aca0-5c16-ade1-a98bb49c050a | note | ○ Principles Representative to be invited to proof roll 24 hours prior to inspection.
2bc6ddb4-edfd-5f91-8fd6-de65508b146e | note | ○ Principles Representative must witness the proof roll.
ebf5a59e-8e44-5291-8371-0f476cc2fda0 | note | ○ Following completion of the successful Proof Roll, Principles Representative will approve Fulton Hogan to place the next layer.
6134a0b9-74fd-5991-9fe4-7f7c835cb261 | note | ○ Placement of next layer can occur once lot is accepted following proof roll. Proof roll inspection will satisfy pre-placement CTB inspection
ed8f929c-5f3c-5d99-9d6c-e9ec5ff8a2c2 | note | Reference Documents - CL 4.11, CL 4.8, CL 4.16, CL 5.9
8853b58d-aa9e-5f04-8604-ca7be2a1e182 | note | Inspection/Test Method - Verify
9166191e-1d47-50c9-a1c2-aa87106416fb | note | Record of conformity - This ITP signed
8d54efd3-12ea-58c5-9db4-1ee9e840e530 | note | IP, HP, WP, HP, HP
b82ae293-b330-51f3-a3dd-5b0af50e15d0 | note | Responsibility - Project/Site Engineer
baa750f2-e49b-504c-a61d-2e359d14fe2f | date | Date Completed:
40f59b4f-71be-5a37-8b06-48355023e0f7 | signoff | AUTHORITY HOLDPOINT
18355098-3bb1-5292-9129-5d9c49ee19cd | checkpoint | 2.7 - Completion of Remedial Works (if required)
a6eea7f7-f90d-5f24-ba42-3cee0d13807c | note | Frequency - As required
10860f22-bd45-5045-b42a-51938225a3eb | note | Acceptance Criteria - Completion of remedial works or nonconforming Sub-Basecourse and/or Basecourse to be approved by Principal’s Representative before proceeding with the next layer of pavement Works.
b60361f7-65c4-5619-aaf9-fb1de60ca685 | note | Reference Documents - Spec cl. 4.21.3
a5be587b-5a31-5d92-87c4-2cf51d5227dc | note | Inspection/Test Method - Verify
ba4d1c10-00f9-5670-bb2c-33ef0baf1f43 | note | Record of conformity - This ITP signed
99acb4ef-c1fe-5a03-89cc-dff4993bedc2 | note | HP
a0e4e81b-9909-57d4-ba10-bc175a31943f | note | Responsibility - Project Engineer, Principal’s Representative
8a219366-a68a-5b60-8cff-5a38571304ec | date | Date Completed:
90a2a886-571d-56de-9a6a-670b0a14580e | note | Principal’s Representative - (if required)
c3655578-698a-581e-b5a5-f09c022177f4 | signoff | AUTHORITY HOLDPOINT
9b0000de-0289-50d5-8923-c7478a283c5e | section | 3.0 - Testing, Lot Size and Compliance
8ba74c27-2d49-528e-b53a-453ab30f277b | checkpoint | 3.1 - Survey Conformance
ce5c29e5-5140-5189-9eb7-e50ab50e5199 | note | Frequency - Every Lot
f272f98a-afa0-55a2-99ab-2926a15cf644 | note | Acceptance Criteria - Final survey level to be checked in a 5mx5m grid to conform with -10mm to +0mm.
df4c2108-63ab-5b10-b7f3-2e9c90d8b439 | note | ○ Survey report not provided for intermediate layers of the same material type (i.e. for PT2 where multiple layers of same material type placed).
12872338-4862-5c8b-9333-33b95e486659 | note | Reference Documents - Cl 4.13
53f1e0a9-3cd8-5987-afac-9955739ce2e2 | note | Inspection/Test Method - Survey Report
cfaa3583-94cb-5b87-a96f-4b0626c0b7ea | note | Record of conformity - This ITP signed
115ef3cc-0237-5ccb-b90f-4e1d03a9a55a | note | SCP
929cefd4-f1a7-5699-a3e6-84e1cfe5d6df | note | Responsibility - Project/Site Engineer
9d93fb88-69f1-59e3-929a-d5c9541b8328 | date | Date Completed:
80ed8158-99a3-513d-9e12-09880383a921 | checkpoint | 3.2 - Surface Smoothness
c0ec5a15-a8a0-51ca-90fd-d266a977ae28 | note | Frequency - Every Lot
d3bb6e9d-cacf-567a-bb05-bb6f85f87f76 | note | Acceptance Criteria - Surface smoothness to be checked every 10m by placing a 3.5m long straight edged on the ground a checking any deviations over 7mm. Complete within 7 days of completion of each section. Document results.
c0794366-a9f1-513e-a322-e27e793bf4c7 | note | ○ Intermediate layers and shoulder pavements are not required to be checked.
428ff593-cbc8-5486-9adf-190d324ee211 | note | Reference Documents - Cl 4.14
916d282e-b4f1-5915-a1c9-84918bf87ad0 | note | Inspection/Test Method - Verify
f13e2c07-1d50-5bc0-b7a8-ec257e7c1c05 | note | Record of conformity - Report
0a56ea0b-1e1d-575f-aaaa-8362bd7334a7 | note | TP, HP
7c42df32-edf4-5349-9cac-0db15597dd49 | note | Responsibility - Project/Site Engineer, Principles Rep
7afe6ac4-7764-512e-b7a2-c8fe830be0cc | date | Date Completed:
ab521b67-11c2-59d8-a3c0-98ec86671180 | signoff | AUTHORITY HOLDPOINT
12ef7ba2-4a80-5164-a247-feedc5d67ff8 | checkpoint | 3.3 - Layer Thickness
c7d134cc-94cd-5822-9a24-cf05412661f1 | note | Frequency - Every Lot
dfdd1cec-5b69-565b-969b-13bfc3125815 | note | Acceptance Criteria - Check thickness of layer using survey at the frequency of field dry density determinations. Thickness shall not be less than what is shown on the design documentation other than allowable construction tolerances.
39ceb27a-a277-5db6-8968-85e5c122043f | note | ○ Total pavement thickness is to be checked. Intermediate layers, no check is required.
02cf8440-e7ce-5019-8d6d-f32d5fb3afbd | note | Reference Documents - CL 4.12, CL4.21.1
018a61a9-d71a-5691-a975-97cdb35c1e0b | note | Inspection/Test Method - Survey
7625b794-097f-518f-90e0-c3cf230ed64d | note | Record of conformity - Survey Report
381236eb-aca7-59e3-a405-b6edd1e665c5 | note | SCP
53f8aeac-1b5e-5448-811f-f523a49ae4ee | note | Responsibility - Project/Site Engineer
f8c2b687-9f81-5752-bade-f7897cef9e9b | note | Aconex Ref: DCWC Mgt-RTRFI-001329
8bc84e71-cdd6-5f5b-afd0-1b535d392c96 | date | Date Completed:
9fdc7f62-f611-5a1d-a6d5-ee615e4ec42e | checkpoint | 3.4 - Degree of Saturation - Sub-Basecourse or Basecourse
88ac18ee-32b3-5465-8cd7-55615a26e84c | note | Frequency - Every Lot
9c74aee7-54c4-5afa-91e6-17f8b6c54a58 | note | Acceptance Criteria -  Degree of Saturation to be tested for information.
7d6d8edb-471d-59a3-84c9-22efe19673c4 | note | ○ Target less than 70% Mean Moisture Ratio.
5267ce29-e9dc-5467-8683-1ff409d3ea82 | note | ○ Test to be taken the shift prior
9ceab416-7620-5e4c-90dd-667de55b8550 | note | ○ If lot gets impacted by significant wet weather, tests to be re-taken
8589b525-694e-5da5-b255-316e9b32bc6b | note | Reference Documents - Cl 4.9
5fc35d50-782c-58c0-a03c-3e2d8632bc41 | note | Inspection/Test Method - Test
36e1d3a5-9404-5501-a43d-8d4439103d9f | note | Record of conformity - Test Report
5b334ed9-a6bc-5b9f-a9a5-188554ebf8fe | note | TP
57654c0f-8304-5154-aabe-6a53ae12880c | note | Responsibility - Project/Site Engineer
2fb7e3e4-a500-5dab-971f-da16c64f635a | date | Date Completed:
93d9ed7b-13bd-571c-b28a-b3e62bf41308 | checkpoint | 3.5 - Field Dry Density
ab290cab-8857-5299-aa93-394c9f7fa1cd | note | Frequency - Every Lot
44b41968-019b-5980-9048-f4b4803f2fa7 | note | Acceptance Criteria - Dry density for basecourse layer has the following acceptance criteria:
14d36e20-9b4e-51c7-b303-4820d35263fe | note | ○ Average of 5 consecutive tests exceeding 100% MMDD.
58de0ee5-78b1-54c6-8224-caf072eeab7c | note | ○ No individual test result less than 98% MMDD.
5d48328e-ac3a-5ad6-b3d1-2406a288f5b8 | note | ○ Principal’s Representative approval based on the results of proof rolling.
f93e1ad9-5cf4-5128-a858-cd7b9bd4cdbb | note | Dry density for sub-basecourse layer has the following acceptance criteria:
e55b6308-f7dc-5856-a542-efcc3c4daea4 | note | ○ Average of 5 consecutive tests exceeding 98% MMDD.
9bf576a0-bf13-5841-ab9a-3afc1935f1b8 | note | ○ No individual test result less than 95% of MMDD.
87da770e-45a7-5e52-8aa1-dda76aa5f24a | note | Principal’s Representative approval based on the results of proof rolling.
44ea133f-24b6-54a9-a30f-f261e13a62f9 | note | Reference Documents - CL4.10 Cl4.21.1
f280a436-de2a-53ef-93ab-b1e3225eeeeb | note | Inspection/Test Method - Test
52cdd929-b842-55ad-8145-5e9812049d33 | note | Record of conformity - Report
407dbe1a-efa0-5213-9bb6-8e6f36cbc3c5 | note | TP
ab5827b3-767d-5dbc-a203-d030deba9967 | note | Responsibility - Project/Site Engineer
e7b37db0-a68e-5a1c-bb23-556cc134f8ee | date | Date Completed:
78953ecd-84e7-5c05-ab3e-4b8357499fea | checkpoint | 3.6 - Quality Assurance Records
6006ffa3-1aa2-59bd-83dc-d6b805ff55b4 | note | Frequency - Each Lot
b2f55ca2-6a14-5a7e-82ba-84de49be30a1 | note | Acceptance Criteria - Submit test results on Aconex for every lot of Sub Base and Basecourse. Results to summarise each test (Moisture content, field dry density and layer thickness).
7bd5a9d8-f1f0-515c-9bd2-db15c58c3a89 | note | ○ Aconex ref to be submitted as Hold Point sign off.
37e3ac2e-1f70-5db3-af28-32a669466602 | note | Reference Documents - Cl4.21.2
c4470a88-b0fb-56dc-9525-ae5913364874 | note | Inspection/Test Method - Verify
e77eb85f-0ce5-5a4d-8372-d2a926cf0d3b | note | Record of conformity - Summary of results
425f643f-a056-5010-9038-22100d4cf06c | note | HP
199e0e4e-ff37-594a-a3d2-8836730d58da | note | Responsibility - Project/Site Engineer
76c8b366-beb3-55a7-bfb4-5516b9aae5c1 | date | Date Completed:
9cafd654-8c3b-5d53-b27f-4fd2723098a3 | note | Principal’s Representative - Aconex Ref: FHPL- TRANSMIT- 001750
172816b0-0bf5-52f3-80f0-01074156ae49 | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
ed6b8455-38dd-51af-bd54-3125b5c47d2a | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
df9f428d-9eb7-515a-8ac0-5b3ec3fd6875 | textbox | Print Name:
f06a7fa1-f701-5396-b827-73e4dfa88863 | textbox | Position:
e17ead71-e36c-5c5b-8116-ea40ac9b8e17 | date | Work Completed On:
4f3c133c-1503-54e8-8324-f5dd13700c4c | date | Date:
844a0099-8d6f-5795-a9d0-14824a95b1d6 | checklist | FH-ZU2-QU-ITP010 - Cement Treated Base - Rev 1 | itp | ITP010 - Cement Treated Base
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
8aa88d4b-ee91-5ba0-8457-6ddccc0d3aa5 | note | Frequency - Prior to works
f596a299-9f58-53ca-9c69-525ee7c3cc5c | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex.
e63a70e3-79b5-5073-95c3-410eeed9d6ef | note | Reference Documents - Aconex
66c5096d-0ffa-51b0-b947-f747cf16c41e | note | Inspection/Test Method - Visual inspection
5576b08f-da41-5fb2-928c-3099cdaa6f44 | note | Record of conformity - This signed ITP
bd555431-cb25-5b36-b645-bdbb62cd6733 | note | HP*
3b038d3a-33f6-557b-82bd-e7cd92c4d207 | note | Responsibility - Project/Site Engineer, Superintendent, Foreman
2f246865-c5bc-5edc-9639-3718d72b4815 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
b0b243f7-51c3-55b3-a663-0dc1b1e0b83a | note | Frequency - Prior to works
f696c199-a47f-5990-bd66-7861ff848da2 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
94fa6461-840a-5ed1-8c42-e091c2be9c8f | note | Reference Documents - PSP, EMP, TMP, SWMS & WP
77b7ee44-7821-5616-bd18-d2ce2cac25ba | note | Inspection/Test Method - Visual inspection
63a96ffb-32b4-5e4b-8a97-562a0fa2a122 | note | Record of conformity - This signed ITP
af9cf847-45a8-50a3-a06c-f3aa247d5f84 | note | HP*
1bb9c244-d14a-5e0b-ad9d-5e50f2486391 | note | Responsibility - Project/Site Engineer
20fe73d9-f13f-5d4b-9540-7726d2227e41 | date | Date Completed:
b9437d57-cad2-5d07-86bd-bc4cd9694fa4 | section | 2.0 - Cement Treated Base Documentation & Trial
f713fe9a-9690-5e10-a912-023f37ca0459 | checkpoint | 2.1 - Submission of Mix Design
f84701ba-8df7-56a7-bbf7-fd0108956189 | note | Frequency - 21 days prior to works
4c9630b9-e2f4-5db5-896f-1a0e63df22cf | note | Acceptance Criteria - CTB material and test results to be submitted to the Principal’s Representative for review to ensure that specifications are met and are compliant, prior to the initial placement of the material.
e094d516-039e-569f-9119-c1c7926abfa5 | note | Mix design results will include:
6e374311-1c48-581e-bddc-512318494010 | note | ○ Cement sample should include a CTB material within +/-0.5% of the specified cement content.
7554aa82-ddbf-5f1b-bdd1-acb07d6ad61f | note | ○ Aggregates comply with either Section 4.4 or VicRoads Class 2 or 3 material.
74caf24d-bc49-56b5-a014-a303fa78a0dc | note | ○ Cement shall be Portland Cement Type GP or Type GB complying with AS 3972.
4bd42f13-d34e-5934-acc8-df754cb1cd35 | note | ○ 3% minimum Portland cement content by weight of the dry un-stabilised material.
0998a3e8-f98a-5b9a-be32-e00b897df493 | note | ○ Mean seven-day unconfined compressive strength of CTB to be a minimum of 5MPa and a maximum of 15MPa. No single samples are to be below 5MPa.
42cad487-7e07-5ecf-9580-c34b1c0004d7 | note | ○ Water to be pot
1b7669d0-aaac-57b0-96ea-a1fcdf6df9ca | note | Reference Documents - Spec cl. 5.4, Spec cl. 5.5 AS 3972 VicRoads Class 2, VicRoads Class 3
873572a1-d8cc-565f-94c0-b94eb417573b | note | Inspection/Test Method - Verify
a66909ef-0334-52a2-bb86-0d40152f53e9 | note | Record of conformity - Approved Mix Design Report
2a6c4f49-8b5a-554f-8666-bcb24bd3eb89 | note | HP
5f8594b4-a8be-5f85-bfc9-24cd96c89d3a | note | Responsibility - Project/Site Engineer, Principal’s Representative
6f53238e-be9b-5995-8685-fd629656dbea | note | Principles Rep - Aconex: BecaCPL-GCOR-000790
66263921-7ec1-5447-8330-44ed2cae7d71 | date | Date Completed:
5b68e915-fa91-5491-8e7f-3cf5fa1c57e8 | signoff | AUTHORITY HOLDPOINT
b08682c6-b8e3-5977-9b10-3b486b29efa1 | checkpoint | 2.2 - Supply of Information on Materials Source
72c22c59-df34-5e6a-8aae-a691c8b99d03 | note | Frequency - Prior to works
f06bcd80-cb39-5f6c-b7ee-acc980e2837c | note | Acceptance Criteria - Principle Contractor to supply the Principal’s Representative with supply information regarding the source of the CTB material via Aconex.
8162544f-1551-5f20-8f89-31e412124556 | note | ○ Material information will include the material brand, material type, material supply source, and a supporting test certificate from a laboratory registered by NATA to prove material suitability for the Works.
0fa3973c-f303-515a-83ef-710cdaa6e7b0 | note | Reference Documents - Spec cl. 5.21.1, Spec cl. 5.21.1.1 AS3972
f426f090-b259-5e95-9fe5-efd9491e0e42 | note | Inspection/Test Method - Verify
f4fd7777-24a4-5e24-8f03-2efc20b3adda | note | Record of conformity - Approved Supply of Information Material Source
2c108637-99ea-5b69-8af2-367b81ad171b | note | HP
77f8cbba-a50c-5b3b-980b-bc14c923226d | note | Responsibility - Project/Site Engineer, Principal’s Representative
737f78ca-d449-5e8e-9300-55c08726cd26 | note | Principles Rep - Aconex: BecaCPL-GCOR-000790
2deff7dd-cb7b-5ccf-9592-103910360dfc | date | Date Completed:
2be119e5-29ff-5f1c-b5de-c6aec4a7e549 | signoff | AUTHORITY HOLDPOINT
a3b266d6-20d2-577d-8bcc-cd0d95185e7c | checkpoint | 2.3 - Production and Construction Trial
2237b766-5dba-5d29-821a-e23e772d006b | note | Frequency - Prior to works
3851ad88-0336-50bc-9701-1a660bba0fbb | note | Acceptance Criteria - Construction Trial for CTB mix to be undertaken by Contractor and reviewed by the Principal’s Representative.
a16ae413-4a25-567f-a41e-e6d4836ce8bd | note | ○ Trial of CTB will be based on the first day of placement. Construction procedure to be reviewed and updated if there are any non-conformances associated with the initial trial.
b2ee570e-0077-5e08-a6d7-b9ab0e54b482 | note | ○ The size of the trial area shall be a minimum of 3.5m wide and 50m in length.
92a07a74-804e-50e3-927c-8e7863345b9a | note | ○ The CTB trial area may form part of the completed works.
9c4ed211-657f-57d9-81c5-2446d3c19ac0 | note | Reference Documents - Spec cl. 132, Spec cl. 5.6
717ed14e-d0fa-59c1-bb81-5da36d688f29 | note | Inspection/Test Method - Verify
2dee421f-a4d7-599a-92f8-3f4f57c30792 | note | Record of conformity - Approved Construction trial report
aae278da-12eb-5ac9-aa6e-efefd64eccb1 | note | HP
22a01488-e3ea-50b4-87f1-af2f3639ea98 | note | Responsibility - Project/Site Engineer, Principal’s Representative
05718d70-ae85-54e4-8dac-399b72b5185c | date | Date Completed:
b511eb0c-9811-5b67-89e8-b06a8ab74610 | signoff | AUTHORITY HOLDPOINT
36dd2170-94f3-5210-af3d-9abe62a51461 | checkpoint | 2.4 - Placement of CTB Methodology
8f31af96-a04d-519f-825d-c89d24070a0f | note | Frequency - Prior to works
22af0bf6-e6a7-533b-8b84-023de9149711 | note | Acceptance Criteria - Prior to placement of CTB the Principles Representative shall review this Work Method Statement for proposed methods of placement, compaction and curing
668d3fd8-fac2-52af-8caf-cb2488203135 | note | Reference Documents - Spec cl 5.9
9de3b2f3-7747-5f3c-baa3-785a2747e99a | note | Inspection/Test Method - Verify
c9bf8592-c08d-5316-bb18-160a3df6be87 | note | Record of conformity - Aconex Sign off
86c48c51-5b11-53ec-8c30-3f290786b3b5 | note | HP
da4ae08c-fac7-5e47-93e1-6f347419f540 | note | Responsibility - Project/Site Engineer, Principal’s Representative
7786b41c-8d21-537b-9856-adcc3eb88695 | note | Principles Rep - Aconex: BecaCPL-GCOR-000810
58f6c910-c461-5b65-a59d-decf015fc5c0 | date | Date Completed:
d887b5c3-5f02-5d22-ace4-5123e7694541 | signoff | AUTHORITY HOLDPOINT
ce085ba5-14a6-5251-aa31-3e4c7b381a10 | checkpoint | 2.5 - Provision of Material Samples
f34ea86e-e126-502d-b7d8-799a4d4501b1 | note | Frequency - At Least 5 Days Prior to works
dd7bb70d-a2b5-55c9-94b4-8dfc76fad08d | note | Acceptance Criteria - Principal Contractor to physically handover reference samples to Principal’s Representative of the approved CTB material. To be truly representative, the reference samples will be taken straight from the supplier of the material.
0c874d56-cf4b-5428-a181-0fb5c3e72280 | note | ○ The reference samples shall be divided into two representative portions, with one being held by the Contractor and the second portion by the principal until completion of the Works.
a7eaa790-89eb-560b-bb6a-42b034b9f4b6 | note | Reference Documents - Spec cl. 5.21.1.2
4123a350-addc-57f1-bedd-545a3336c7ad | note | Inspection/Test Method - Verify
e3479ff3-9d0e-5684-8e1e-0bf3b53ff2f0 | note | Record of conformity - Handover of Reference Samples and Aconex sign off
da9049f6-a774-5ab7-b2b1-03431ba9fadc | note | HP
92c0e4db-5ee2-5bbb-a183-8fea440ae72a | note | Responsibility - Project/Site Engineer, Principal’s Representative
ba3782a7-3abb-5d95-b86c-c78ef690149a | date | Date Completed:
dfd5e478-bd8f-595e-9f3f-8d4fc3db5035 | note | Principles Rep - Aconex: BecaCPL- GCOR- 000825
ce0e26d2-cdbc-5212-b7b6-711abae7313d | signoff | AUTHORITY HOLDPOINT
3a93befc-813a-54fa-93e6-ed544f594f7e | section | 3.0 - Placement of Cement Treated Base
e6432367-fc0d-5d29-92fc-3e7e2637f723 | checkpoint | 3.1 - Subgrade, Basecourse Preparation
1d26deef-fe2e-5fdb-a424-a3909955245a | note | Frequency - Each lot
90173b31-4a14-50e9-93e3-3fed40bb5797 | note | Acceptance Criteria - Existing surface of subbase is maintained in compliance with tolerances on surface smoothness and level. The subbase is clean and clear of any foreign matter before the placing of the CTB.
c310d359-b226-5439-8830-9bf651637b3d | note | ○ Principal’s Representative will be notified 24 hours prior to the placement of CTB to allow the subbase to be inspected prior to the placement of the CTB. This will be recorded in ITP009 – Unbound Pavements.
65fd1623-8231-5854-aa9f-5cda3e8b9715 | note | ○ Principles Representative to be notified of the intention to place CTB.
b1ae7aca-a8e4-5915-b171-70d23878625f | note | Reference Documents - Spec cl. 5.7, Spec cl 5.9
35910732-4634-5050-a1f3-a7e82e567390 | note | Inspection/Test Method - Visual Inspection
a9a3fb03-d34e-5643-aeab-c7f7c06b097d | note | Record of conformity - This signed ITP
0061e970-f3a6-5f64-861d-4a3562876699 | note | HP*
b5dc517c-d7f8-5f6b-b8b0-6a317bdab769 | note | Responsibility - Foreman, Site Engineer, Principal’s Representative
de55df49-5ade-5de7-908d-27572a37eefb | date | Date Completed:
d5f5265f-9acd-5150-85f4-b8e0fd5c4c1b | checkpoint | 3.2 - Layer Placement Parameters
15d20a59-abb9-5a63-bbbb-ae10c247e7e7 | note | Frequency - Every Lot
a7549654-01da-5468-98c6-45fd6149d6b2 | note | Acceptance Criteria - Summary of Parameters for each Lot;
9b307856-48e1-5148-b00c-36535f9c5285 | note | ○ A lot is defined as one layer placed in a single days production of uniform material
443263a8-e71e-5b88-afb4-8b92e59bb419 | note | ○ Max Layer is 200mm
bed1a5bc-d098-5239-b2e4-030a8525d7c3 | note | ○ Min Layer is 100mm
187f4fc7-665d-5338-8487-8e92b1d07d02 | note | ○ Final Surface Level +0mm, -10mm (excluding intermediate layers)
7171547a-ee6b-53d6-b20f-7d3ad0a0d8c9 | note | ○ Shape: every 10m intervals, <7mm deviation over 3.5m straight edge (excluding intermediate layers)
01ea9862-06c3-54c0-8365-67d7ef6c4f5d | note | ○ Material is batched within 1% of OMC
154ea760-0093-5671-9a15-c4fb065e211a | note | Reference Documents - Spec Clause 5.9
23e30d10-91f9-5caf-bf9a-50c0b7a25197 | note | Inspection/Test Method - Visual Inspection
e3db2985-1629-55b1-86de-615aa90f8bca | note | Record of conformity - This signed ITP
92da49e6-752c-58e5-a3a5-368767d9eadc | note | IP
131f5628-0346-5a4c-830c-ee5d14e15223 | note | Responsibility - Foreman, Site Engineer, Principal’s
cc2418e7-c804-5128-ace2-e40bde4c6554 | date | Date Completed:
a791ad98-de04-56f3-baea-854bfe3fec6e | checkpoint | 3.3 - CTB Placement – Weather
a8945776-a6f4-5b36-b3fe-925c329ce3df | note | Frequency - Each lot
527d722b-c5b1-574b-81b0-1a2b37349e23 | note | Acceptance Criteria - Weather to be check prior to placement, CTB shall not proceed when;
8b6f23cb-bdd6-52db-9b80-19f7c3a85136 | note | ○ Ambient temperature is below 5°C
b5a25fd6-d1a7-555c-a444-784f86bdf94d | note | ○ Temperature is over 35°C
abb0ce29-4364-5f04-86af-c2c1030115d2 | note | ○ Heavy Rain fall is forecasted
e8bd97b5-51ed-58e4-b56f-93694ea86fc5 | note | Reference Documents - Spec cl 5.18
17631fb5-c95b-50f9-96d9-c8cb7cd5a4ae | note | Inspection/Test Method - Visual Inspection
d44b3070-6831-5703-af8f-496e3889538e | note | Record of conformity - This signed ITP
77032644-9c84-5d86-8fa0-8438ebe70d20 | note | HP*
19904e0d-6cd6-551f-af45-e992a7ccbd14 | note | Responsibility - Foreman, Project/Site Engineer
ccba4635-1cdd-5b1f-84fb-6f07cec24b9c | date | Date Completed:
a990dc3f-4e0f-51d5-8138-9ebb78589eff | checkpoint | 3.4 - CTB Placement – Checks
1bb2aa2a-c4ff-561d-a13d-7afbe13bc904 | note | Frequency - Each lot
32f8ef17-8490-50c9-9251-810682a3751a | note | Acceptance Criteria - During CTB placement Activities check;
40f02693-c8d1-535f-a199-ece05f6f73b8 | note | ○ Placement starts on the high side or crown of the layer where practical
048bd7c5-c004-55da-9bc4-93e115f79601 | note | ○ Material is spread in the direction of Taxiway across full width
4f433ccd-ee6c-524f-b818-eae38e7377da | note | ○ Underlying layer is not disturbed during deliveries
d08de34c-ea7f-583a-b415-47e596003fb9 | note | ○ Inspect Material for any contamination through placement activities
a61ff818-105d-5a4e-8680-ff9d042ce44a | note | ○ Adjoining layers are a clean face / vertical
8df5403a-2649-51c2-a3ad-c7303e4bb19d | note | ○ Segregation does not occur
b355b70a-b0ac-5a92-b3ac-1b8a400fe4a1 | note | ○ Placement to be completed within 120 minutes from time of batching and before concrete has obtained its initial set
f4942690-8cd5-558c-9f3a-44274fe159c5 | note | Reference Documents - Spec cl. 5.9 AS1289.5.2.1
b574633f-2bb1-5d4e-950e-ff2484b56389 | note | Inspection/Test Method - Visual Inspection
60226c75-b0de-5c5b-96e9-8673327b422c | note | Record of conformity - This signed ITP
b828ff37-ec7f-50be-94b1-ee32fc7cc07b | note | IP
d1b766ef-1c08-5b21-b039-7f9ab4683bf1 | note | Responsibility - Site Engineer, Foreman
2654885b-329c-5964-89f4-e465307a4a9b | date | Date Completed:
7401f6c4-9bed-5d6f-b4ec-db03b8a866c1 | checkpoint | 3.5 - CTB Compaction – Checks
d318849b-5618-597c-91b3-814e52d4f0e1 | note | Frequency - Each Lot
ae30e580-e65b-59b1-93b6-ceb7450cd2f2 | note | Acceptance Criteria - During Compaction check;
b10036b6-d4c3-53e6-a7dd-623f106280d5 | note | ○ Heavy smooth drum roller of 15t to 20t is used for initial compaction
d1f1c126-533a-5e6a-8dc4-2e235688e671 | note | ○ Pneumatic roller of 27t will compact material for final consolidation.
05876ce7-e80b-5055-948b-92633bd9b857 | note | ○ A heavy smooth drum roller (in static mode) may also be used for final consolidation
8a9f03d1-75fb-512e-bbdb-7318c1488415 | note | ○ Watercart present onsite for conditioning
65490f31-31f1-55fa-ba27-62cb0064acd3 | note | ○ Materials are trimmed to required shape and level
18e147eb-3edb-5867-bda3-b7734942fa05 | note | Reference Documents - Cl 4.10
a5cc52f2-9ea2-51e1-9d76-86f779782816 | note | Inspection/Test Method - Verify
4ed1fdbe-a813-5556-8b34-fa80b91e4a55 | note | Record of conformity - This ITP signed
d2cb62fd-45c5-53ba-a041-c81c964b747c | note | IP
8ca58966-39f3-51c1-9bf7-7cfb7924a9f8 | note | Responsibility - Project/Site Engineer
7d2e2bd3-99ca-5153-891e-45c4cf8e6ee3 | date | Date Completed:
2bddfd15-ae28-5cbe-bfb1-25a7421f7b98 | checkpoint | 3.6 - Curing & Protection
d9202bed-4ccb-5e6c-8eae-441e32bd0d2a | note | Frequency - Each Lot
3d18e78a-fbc1-525b-822e-0dad77056df3 | note | Acceptance Criteria - Curing to commence as soon as CTB has been placed, compacted and trimmed. No plant (other than curing) to track across CTB for minimum 24 hours.
3ff88ce5-7c4d-55c3-8a20-b2077108bb2f | note | Curing to follow one of the below methods;
426e9ca7-487a-5f20-a6ae-ffdc3fd8f5d4 | note | 1. Wet Method: This will involve a watercart lightly spraying the CTB surface for minimum 7 days.
ac0408e5-01eb-511d-bec8-72574746a26a | note | 2. Debonding Coat: The CTB will be covered with a bitumen curing compound. In locations of PCC, will be the C170 seal with 7mm aggregate.
dcc282aa-d774-5d32-a21a-2340833e3a7f | note | Reference Documents - Spec cl. 5.15
c185cb39-41db-5b74-bf4b-58039a1d2486 | note | Inspection/Test Method - Verify
5ed27476-046b-5d4c-91f4-9d6dc280e91b | note | Record of conformity - This ITP signed
4127c5e4-b820-5275-befd-3ba282773570 | note | HP*
90a1f255-e2f6-5258-82f4-a6608d585ead | note | Responsibility - Foreman, Project Engineer, Site Engineer
b29214e6-d20d-57e7-b892-48164a53e9e0 | date | Date Completed:
6e009c69-70d7-514c-b44e-f3bb3867a1e3 | checkpoint | 3.7 - Post Placement CTB Inspection
c133101a-b607-579c-b4f9-2cf71ca93f9b | note | Frequency - Every Lot
a7f09b74-8c7e-5e9c-8c19-390ba5710f6c | note | Acceptance Criteria - Prior to the application of the succeeding layer or installation of the de-bonding coat, CTB final surface is to be inspected with the Principle Representative
3dd631f2-a2a1-571d-a620-d5d946c8b5bb | note | Reference Documents - Spec cl. 5.9
84554310-d991-5d29-82f6-a3c07c5d5599 | note | Inspection/Test Method - Verify
09e8586b-eca6-5d3a-a226-2bcb388209a4 | note | Record of conformity - ITP signed
5ccaaf5a-f383-5dcb-9802-a10733a58443 | note | HP
905e8200-14cf-53ec-a676-f2ddc9f34212 | note | Responsibility - Project/Site Engineer, Principal’s Representative
d7a8daed-5a8c-5363-9fc5-cd375d53fabb | date | Date Completed:
1fbbaaa5-dcbd-58a7-a340-05841913c755 | signoff | AUTHORITY HOLDPOINT
131e830c-80ee-5bfa-ae6d-3cee6331c53a | section | 4.0 - Acceptance, Compliance, Controls and Quality Assurance
99e681f2-8a6c-56a0-be58-12603b6f7477 | checkpoint | 4.1 - Field Dry Density
f03186bd-59c9-5281-b6ef-20321711d5ed | note | Frequency - Each Lot One test every 500m2 (or 250T) or part thereof
102f1ebf-e51b-5ed9-ad43-a0896478ebdd | note | ○ Minimum 4 tests for Lots under 800m2 (or 400t)
f5ceefec-34de-5727-916e-0b288c1aabd4 | note | ○ Minimum 6 tests for Lots over 800m2 (or 400t)
803c9230-1f43-5b08-9bac-c416ef40d10d | note | Acceptance Criteria - Average of Specified Minimum Dry Density Ratio (SMDDR) of 97% of the Maximum Modified Dry Density
0f72bb26-c4ac-5f47-9353-d47361c2c94d | note | – Average Equals or Exceeds 96% with no individual result be less than 93%. The lot will be accepted.
54e288c2-afc9-5831-bdd3-c814dbafdac1 | note | – Average Equals or exceeds 96% with a result being less than 93% - an additional 4 tests will be taken
7422857c-dbf4-5cde-8fcd-7a9eebb01ddf | note | – Average is less than 94%, the lot will be rejected
58937cc4-12d9-5cda-a665-45ab2a8da7e5 | note | – Average is in between 94% and 96% - an additional 4 tests will be taken
a9f58864-2561-54a2-bfa0-dab77c1e7259 | note | Reference Documents - Spec cl. 5.10, Spec cl 5.21.2.5
28029483-eb30-5e34-b3a9-ed80ee976a2f | note | Inspection/Test Method - Verify
71a6959e-311c-5755-aa07-77880c544a37 | note | Record of conformity - This ITP signed, Test Report Attached
16a6d560-db93-5e93-aac4-1ef0e3b58824 | note | TP
4d63e4ce-61af-549e-93cd-88e90439f6fe | note | Responsibility - Foreman, Project Engineer, Site Engineer
d729f33b-569d-5d94-bf25-bde0399b776e | date | Date Completed:
c083058b-dae6-5e3d-a513-cc68f715ae5a | checkpoint | 4.2 - Moisture Tests
48e1392d-43e6-58f5-af5e-7dedfde8269c | note | Frequency - Each Lot One test every 500m2 (or 250T) or part thereof
06c7fffd-057a-5683-a5f7-8a8c381a276e | note | ○ Minimum 4 tests for Lots under 800m2 (or 400t)
2b0ffe7c-a0d8-59f6-bebc-62ca95b1f694 | note | ○ Minimum 6 tests for Lots over 800m2 (or 400t)
ebec3e40-e3e6-5a4b-9711-f0369aaf6a53 | note | Acceptance Criteria - Target Moisture content of +/-1% for information only. Production of CTB to be within 1% of OMC.
b5ab453a-a9ac-5e01-bf8f-b88b1b412688 | note | Reference Documents - Spec cl 5.21.2.5
31eba2f8-121a-5f0a-9bbd-1df0d0fcd5d6 | note | Inspection/Test Method - Verify
1d86b1f4-11bd-5c0c-9580-e4d32aaf98f6 | note | Record of conformity - This ITP signed, Test Report Attached
6a896df5-fbe0-5c11-9572-3ea136c6b665 | note | TP
dd17bd53-ffd2-53b4-ac3a-23be9eb1f240 | note | Responsibility - Foreman, Project Engineer, Site Engineer
da840038-f33d-5214-8629-cc69fb864320 | date | Date Completed:
435a97a0-8348-5acf-b9b1-f34f54f87f6c | checkpoint | 4.3 - Strength Testing
27bc8c7e-95d1-5dcf-88ae-82823e1085d9 | note | Frequency - Each Lot, divided into four approx. equal sub-lots
2fddab20-aeb3-51af-80f7-3033426b797b | note | Acceptance Criteria - A total of 4 sub-lots will be taken as samples, with 2 being used for the 7-day strength testing, and the remaining being used for the 28-day strength testing. 28 day results are for information only.
53e841bf-eed4-57b9-9fbd-fd88b73d2b2a | note | ○ The mean 7-day unconfined compressive strength of the CTB shall be a minimum of 5.0MPa and a maximum of 15.0MPa. No single sample shall be below 5.0 MPa.
2750053b-5e5b-527a-927e-8e87f4aab69a | note | Reference Documents - Spec cl 5.11, Spec cl. 5.21.2.6, AS1012.9, AS5101.4
520a4d5f-8343-5414-af26-941844343fab | note | Inspection/Test Method - Testing
51ba2912-8e23-5929-9c94-7c2fc5b9173a | note | Record of conformity - This ITP signed, Test results
102a9d58-c7cf-58d9-a254-e2b57c059a11 | note | TP
62c9a368-385e-5f8a-a5fd-3173b78cbeb5 | note | Responsibility - Project/Site Engineer
cd63fc81-2748-5204-8c71-1ecdc8d7094d | date | Date Completed:
a63f0532-32bb-5725-9bef-0a20b43e1e13 | checkpoint | 4.4 - Process Control
c610b4ae-a285-5c6e-8fcd-207cb4c478c1 | note | Frequency - Each Lot
139d6cc6-0860-5d37-84ea-5eec2d18cc61 | note | Acceptance Criteria - CTB production and process control test results to be supplied to the Principles Representative
4cf57679-b162-55ad-abc5-71060624730a | note | Reference Documents - Spec cl. 5.21.2.1
a2362452-e6b9-50cc-8ab0-15193aa438e1 | note | Inspection/Test Method - Verify
6b11e16c-b89c-532c-8d84-0dde9b1f6e07 | note | Record of conformity - This ITP signed
f14b3625-4f6b-54d3-86cd-83ac17befadb | note | IP
cbabd8ff-86fb-5ea7-adaf-3d9bcd3a5cc2 | note | Responsibility - Project/Site Engineer
81b3934b-4a7c-5973-9a83-ac3ddb5484e9 | date | Date Completed:
2bcbf63d-6c13-5d63-acf0-f62700f979cb | checkpoint | 4.5 - CTB Layer Thickness
1799115e-1fc2-519a-85de-f01907f95ab3 | note | Frequency - Once Every 30m2
fb01f919-1253-50b5-bafd-444151f02c79 | note | Acceptance Criteria - CTB layer thickness to be measured, recorded, and included in the Quality Assurance records. No CTB layer thickness to be less than that shown on the drawings other than allowable construction tolerances
86aed6fe-a7e1-5bbe-b54d-a6febb6dcee1 | note | Reference Documents - Spec cl. 5.21.5, Spec cl. 5.21.7
1751b0ea-39bf-557f-a987-76db1c978ff5 | note | Inspection/Test Method - Testing & verify
8f655c65-eeac-573b-a41b-ff7a4763d512 | note | Record of conformity - Test results & this ITP signed
1edaa5b4-7fe2-53f7-904d-ef6ccb84713b | note | IP, SCP
440d35fd-e0b5-5913-b784-e8a1609522a6 | note | Responsibility - Project/Site Engineer, Site Engineer
4d29f0b7-fd7d-5f66-8910-65653e2fc014 | note | Aconex Ref: DCWC Mgt-RTRFI-001329
8486d6a6-edbe-5b6f-ad1b-e3320c99b948 | date | Date Completed:
a65f8491-197d-5f8d-98e9-df0607f9802b | checkpoint | 4.6 - Quality Assurance Records
e28ad406-42b3-54df-bd45-1d533d8a6992 | note | Frequency - Each Lot
6bff1fb8-fc6a-5245-be5d-b0d34882f2da | note | Acceptance Criteria - Provision of ITP test reports must be submitted within 60 days after the completion of the Works. Principal contractor to supply electronic copy of reports detailing the results of the quality control and testing undertaken.
ff73a1e8-da4b-56d3-b9ad-dd3e0a5b5867 | note | ○ Reports to be transmitted on Aconex and Aconex Reference to be quoted as Hold Point Sign off.
901e3f69-22d4-5dff-a8fb-4777b97224e0 | note | Reference Documents - Spec cl. 5.21.3
dbe748d1-13fc-59a6-b11a-3fde2f3eafe5 | note | Inspection/Test Method - Submission of ITP reports
d186873f-c9c4-57e7-a8a6-10ef7c2b1f91 | note | Record of conformity - This signed ITP
ddbf53ba-4ba6-5162-a876-1db4a0b8cda0 | note | HP
6a8940a0-674a-51b8-a949-c153ebc3521f | note | Responsibility - Project/Site Engineer, Principal’s Representative
a6b55153-f7f0-5005-ad8c-0083e0fd459c | date | Date Completed:
d26e1c20-cd8c-5956-8617-743c63ff978f | note | Principles Rep - Aconex Ref: FHPL- TRANSMIT- 001750
ad2de4d9-5721-5145-9475-1d1edaefaba1 | signoff | AUTHORITY HOLDPOINT
39c190b7-b116-57f8-a2a7-da1cc234c6f0 | checkpoint | 4.7 - Survey As-Built Report
2275ba0b-0e87-5dba-a66e-9441454b85ae | note | Frequency - Each Lot
dbb59df4-c843-56b6-8c73-5f8a99b22177 | note | Acceptance Criteria - The surface level at the top of the final CTB layer shall not deviate from design level at the specified points by -10mm or +0mm. Contractor to provide Survey Conformance report of completed CTB surface layers per Lot.
61d1d193-4712-5f16-853e-4cf7e99a2d55 | note | Reference Documents - Spec cl. 5.17, Spec cl. 3.14.2
c5212fbd-57c5-5049-9e22-15468fa5c769 | note | Inspection/Test Method - Verify
b30b9298-b275-527f-83c5-0965084bdb9c | note | Record of conformity - Completed drawings, survey report, & this ITP signed
a9cbc0bd-f47a-5f26-81e9-5f5cb769aaf6 | note | IP, SCP
3d2bd58c-980e-593c-8704-511a08c99272 | note | Responsibility - Surveyor, Project Engineer
c5056a76-945c-5f08-b874-d76e1d320dbe | date | Date Completed:
0f7f576e-520a-5643-9fc4-f169fffc004d | checkpoint | 4.8 - Surface Smoothness
5d4acac4-2875-5596-93f5-1a785ba3e054 | note | Frequency - Every Lot
93786c44-4ebd-54d3-aca1-951acc07afb5 | note | Acceptance Criteria - Surface smoothness to be checked every 10m by placing a 3.5m long straight edged on the ground a checking any deviations over 7mm. Complete within 7 days of completion of each section. Document results.
91fb8cd2-d46e-5227-b807-708f1a461489 | note | ○ Intermediate layers and shoulder pavements are not required to be checked.
c01c18c5-37ba-58b4-a6a2-642d82ab94c0 | note | Reference Documents - Cl 5.17
58c12aac-2d98-5ac4-b686-7c9e9cfaa8e0 | note | Inspection/Test Method - Verify
ed18d16e-eb2c-55be-9c34-5b2c4fd34347 | note | Record of conformity - Report
3b7bb992-09a4-5bdd-9c10-fcc45ede27d4 | note | TP
f9ae33fc-2416-5f39-a778-8195e2fb3791 | note | Responsibility - Project/Site Engineer
effa941f-c08e-5def-b3a5-5ecdab676233 | date | Date Completed:
c801c62f-58a1-5837-8f7c-89512b249fce | checkpoint | 4.9 - Correction of Nonconforming Work
9ec784eb-353e-506d-9619-b27d85a09297 | note | Frequency - Each Lot (if required)
369bd2a4-9673-5e6f-b9a7-c89bb20602c2 | note | Acceptance Criteria - All CTB that do not meet all the specified requirements will be rejected by Contract Administrator. Materials to be removed full depth of the layer and reinstated, unless otherwise approved through the NCR process.
ac35cc23-2d07-57ea-aa08-9d3098856e40 | note | Reference Documents - Spec cl. 5.21.4
99ba277c-f48e-501e-89c3-e4675b0c7544 | note | Inspection/Test Method - Verify
55f90695-7572-5a0e-8395-fe465a26db9f | note | Record of conformity - This Signed ITP
db96ea5a-921e-5ed5-8c15-2a19c2d9a5bd | note | HP
6a3f2218-7f09-5a57-b7a7-c49b0d52d177 | note | Responsibility - Project/Site Engineer, Principal’s Representative
dba5f565-ca20-52ba-aca1-c9ea7c152251 | note | Principles Rep - (if required)
e18f55d4-6a0b-5027-bffa-6021233c4d87 | date | Date Completed:
a1f73c0c-47cf-52f8-abb9-28b1f1690f2e | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
f9a7189c-b860-50c9-ac40-38214720411f | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
2ed5916a-4453-538c-a5f9-3dc1b4870a03 | textbox | Print Name:
3b7bd65a-2e57-5fdf-babf-8993d668d7c2 | textbox | Position:
90d84dfb-f506-5b4b-b2a3-b1f9ce2894e4 | date | Work Completed On:
bbf80422-452e-53b5-8e68-f944166304fe | date | Date:
34dab725-d24e-5abc-bb57-788fb4f92dc1 | checklist | FH-ZU2-QU-ITP011 - Concrete Production - Rev 0 | itp | ITP011 - Concrete Production
d1d7c36c-2cf6-5a58-97fc-e2b1a4a2ed68 | section | 1 - Plant
bb149d3d-8aaf-5a14-bfd7-edfc4cdccea4 | checkpoint | 1.1 - AS1379 4.2.1
ec167bae-073e-5196-ab41-92473e890fab | note | Inspection Description - Batch tolerances
d0878c4c-a23d-5965-97d4-579044b8b2ec | note | Acceptance Criteria - AS1379 Table 4.1
5ed08f6d-628d-5eb0-b0dd-4434f6270e6b | note | Frequency - Each Batch
52121fff-1c4b-5854-991b-b198f71b2ce7 | note | Initiated by - PS
965b0cfd-d216-5c8e-8809-cdc0de6a7f41 | note | Approved by - PS
b962d637-e9aa-5562-b71e-79c077fc3e90 | note | Verification/Witness: HOL - W
a3db39d9-32c1-5a00-a7fb-28d48db0b6fc | note | Verifying Document - Electronic
5b528f62-34e2-58e6-815e-fb5414fc749b | note | Record Location - Batch computer
fd112218-a86d-56fe-8602-0f9007ca5737 | checkpoint | 1.2 - HOL QMS PN6.1
3b609834-fa06-55d4-8cd0-cacfb868e819 | note | Inspection Description - Record Plant Malfunctions
04c07292-181e-5bdb-8111-9ba04a90011e | note | Acceptance Criteria - All plant mulfunctions are to be documented
aea9e1ab-4f16-5471-9ea9-a4277a345348 | note | Frequency - Each Time
4bcdff02-027f-59e7-840c-0bc0962d7292 | note | Initiated by - PS
98280ffd-c0ec-5356-a8a1-de6b660b82ff | note | Approved by - AOM
f1c6d24b-5b40-564c-8bc2-e7806562b04f | note | Verification/Witness: HOL - W
8f124b17-a4c4-5dde-b618-227f1e40b0de | note | Verifying Document - Register
ec962c2b-72a0-5c25-a96b-4a2f098b53c0 | note | Record Location - AOM office
342318df-c5b1-57cc-98d2-56502aa5f8e7 | checkpoint | 1.3 - AS1379.3.3.2
2261224e-cd10-571d-a0ab-59ac2b4ce738 | note | Inspection Description - Weigh Hopper (Cem & Agg)
82ae748d-8021-51a3-b248-8c4a5e3f3eb3 | note | Test/Inspection method - AS1379
e06efce3-0121-5f53-b67c-d923f3c0475b | note | Acceptance Criteria - ± 0.4% of the Max. Scale Value
aa6ab432-ab8c-59e1-bff1-aba5445484e6 | note | Frequency - VicRoads Min. 3 Monthly
399fa8fe-81d5-511d-a735-cea7efe141c1 | note | Initiated by - PS
7ecef803-c0f1-5522-8ebc-e64f9073ccd1 | note | Approved by - AOM
6d6ed851-6c70-51cc-bf36-5f2cc76086c9 | note | Verification/Witness: HOL - W
85870595-d124-5eb1-8088-caf5f6adaefd | note | Verifying Document - Calibration Report
192385be-8cc9-511f-bf2f-ab939170b91a | note | Record Location - Google
8f189730-16dc-562c-8244-e99fc03abffc | checkpoint | 1.4 - AS1379.3.4.2
5b532b14-badf-53ea-aad8-13610672b158 | note | Inspection Description - Water Meters (Plant, Slump Stands & Trucks)
edb974ae-b9d0-55fe-9dc7-1ed8bcd5cec6 | note | Test/Inspection method - TRBE652973
4216efc3-7727-5fc9-bda8-331453c5d15d | note | Acceptance Criteria - ± 2%
45b897df-835c-5acf-9bcd-a87106d50105 | note | Frequency - VicRoads Min. 3 Monthly
cb184bc8-a986-5d31-b1a6-b22904df3ac9 | note | Initiated by - PS
a837287c-f051-5cef-97be-83ee664dc989 | note | Approved by - AOM
c3808748-d2f7-5f44-b833-3fb41b8c94f5 | note | Verification/Witness: HOL - W
ec824824-a32b-52e1-83fc-8c6c044e48aa | note | Verifying Document - Calibration Report
d6a1db43-9664-50d0-ae91-1d1e8c2216a9 | note | Record Location - Google
a2c93459-c8fe-5526-9725-ce55b11e23f9 | checkpoint | 1.5 - AS1379.3.4.2
f7e763de-1cf7-5be6-b977-0b3ec21f707c | note | Inspection Description - Admixtures
7257f113-7b5e-5517-9197-6fa4eabbadf7 | note | Test/Inspection method - BASF TM033
107b6b82-a1b3-5d9e-a90a-4a53e8fb73b1 | note | Acceptance Criteria - ± 5%
74cd3856-d407-58c5-9652-009768bffd21 | note | Frequency - VicRoads Min. 3 Monthly
33a9b1e5-0d1c-5fad-84fc-d1a08459a347 | note | Initiated by - PS
6a65c703-aa0e-59be-99b5-7400c71691aa | note | Approved by - AOM
9344f309-a5b0-5b1c-9480-d95b503bc764 | note | Verification/Witness: HOL - W
bc22657a-b306-5e6f-bf36-a6fd8b56b345 | note | Verifying Document - Calibration Report
056ca247-dce2-51f6-9c77-ec15673b6387 | note | Record Location - Google
b2b49c19-fb17-5e3e-bd41-38bd1fde4a01 | section | 2 - Cementitous materials
60b4bf12-aca3-51d3-b8a9-ab48b3f52f0e | checkpoint | 2.1 - AS1379.2.2
89275da6-0465-5e62-8e36-d04ca4b76f58 | note | Inspection Description - Type GP cement
23282475-8466-5ae3-97a1-6111eefaaa61 | note | Test/Inspection method - AS2350
588d428e-e1f3-543c-928d-cf8a461146df | note | Acceptance Criteria - AS3972 Table 2
942c42a1-c57d-5baf-a541-665ef510490a | note | Frequency - Cement Australia Supplied (as per AS3972 Clause 5.2)
af1a8ef4-fc18-5a0e-b703-de2e2ced3c1e | note | Initiated by - Supplier
da2d45a0-5f7a-5873-8267-ef844bfbb62d | note | Approved by - Tech Mgr
e6844906-2f9c-5bda-b9b2-26180e80a17f | note | Verification/Witness: Supplier - W, R
81c65be7-13f9-5e95-b447-d1c14d5cbad7 | note | Verification/Witness: HOL - W
500a7175-b576-59cc-abef-ff2ec7862a7c | note | Verification/Witness: Company - H
f707f541-a427-54af-8984-141816080ed1 | note | Verifying Document - Supplier test report
1643a055-3b71-5e4c-bfc0-d338cb7b8daf | note | Record Location - Tech Mgr office
e44c08d5-33f4-5f97-912d-d286e23f0854 | signoff | AUTHORITY HOLDPOINT
8f9a460e-8448-59e5-b2df-be1e037dc6b8 | checkpoint | 2.1 - BECA Cl 11.4.7, 11.24.5
7e3f15cc-e9fb-5a65-893a-375ff27a6784 | note | Inspection Description - Reference Sample
b8295b62-42c9-512c-b895-f7e14165375d | note | Acceptance Criteria - -
6247c27b-afe9-5fb0-8e02-5a424feb764b | note | Frequency - Plant Sample : 10kg / 1000 tonnes
d3e6c3a4-b367-51c5-93ae-608aa856ffb3 | note | Initiated by - Supplier
254de3e8-8a66-56e4-bf57-ac7601a18a8e | note | Approved by - Tech Mgr
fe4125e2-18ba-591f-a7d0-ee9716a69681 | note | Verification/Witness: Company - W
bc8a5893-2226-53f5-a6b1-2008a422b372 | note | Verifying Document - Record only
f1323379-b76a-52b3-8e14-25fea0d7d4d4 | note | Record Location - Tech Mgr office
bb025ecb-aea6-52c2-b32d-71450f87a789 | checkpoint | 2.2 - AS1379.2.2
33439117-724e-5950-bc43-2fcfdb604d6e | note | Inspection Description - Flyash
29bad1a1-3892-5f1d-9dd4-1272b961bdb5 | note | Test/Inspection method - AS3583
38e649b9-cf2d-51e2-95e2-fc590323a903 | note | Acceptance Criteria - AS/NZS3582.1 Table 1 - Grade 1
66331346-9de3-57b4-a751-8826155f5c58 | note | Frequency - Cement Australia Supplied (as per AS/NZS3582.1 Table 2)
0450bcf7-b261-5937-805b-686e17ffd645 | note | Initiated by - Supplier
e2ef16de-5fcf-5d9f-a3c7-4952b23bd1af | note | Approved by - Tech Mgr
65e036aa-fd80-5942-aab9-359a60786982 | note | Verification/Witness: Supplier - W, R
e2b3da04-acf3-500d-946f-d78e125a0670 | note | Verification/Witness: HOL - W
931cdb5e-47fc-5dc9-b82b-a0e970a68758 | note | Verification/Witness: Company - H
ff7bad1c-7fc0-55db-aace-c8e9fd136e86 | note | Verifying Document - Supplier test report
4219d34d-10f4-547d-a930-d564fa09a2ff | note | Record Location - Tech Mgr office
ed4e4f7c-28b8-57c8-b86f-66b1ce71146e | signoff | AUTHORITY HOLDPOINT
f1c81b6f-1209-55f3-a019-1e541e392a1f | checkpoint | 2.3 - AS1379.2.2
2ad2fa49-64a7-5261-8406-0e7c0529f8a7 | note | Inspection Description - Slag
947265eb-f55f-51c6-841c-514b73d001d6 | note | Test/Inspection method - AS3583
cfde5cd4-276f-5832-8548-f26348b73ca7 | note | Acceptance Criteria - AS3582.2 Table 1
e6847eac-f3fb-509c-8cc7-47a06fcda99e | note | Frequency - Cement Australia Supplied (as per AS3582.2 Table 2)
8b0adaca-df8b-5ed1-8abd-196615ee0253 | note | Initiated by - Supplier
d559e9ec-beac-5801-a9b6-41fdcac89f0e | note | Approved by - Tech Mgr
e47aa184-ce01-5c0a-bf64-8f5d9a6cd291 | note | Verification/Witness: Supplier - W, R
90c23712-674d-5a2c-be11-736bb7e41d01 | note | Verification/Witness: HOL - W
306c3c62-b3b0-5288-ba56-c8a29b6ae623 | note | Verification/Witness: Company - H
b6673083-e377-5b92-b7a2-34cdd6198fbe | note | Verifying Document - Supplier test report
cb2b4f39-2550-5973-b9b3-538f2b4670f7 | note | Record Location - Tech Mgr office
2090be1b-7fd9-5116-9b30-36decf7a68c8 | signoff | AUTHORITY HOLDPOINT
d96a8d82-973e-5a54-9fd9-6912feb16437 | section | 3 - Coarse Aggregate
0b71bfd6-f444-5ed2-9c2a-0f5ea47e3f4c | checkpoint | 3.1 - AS1379.2.3
1a8c117b-a752-5916-a5ce-b426f631942e | note | Inspection Description - Particle Size Distribution
2badb670-17ef-56b3-8338-5da843f9ad33 | note | Test/Inspection method - AS1141.11.1
6004f56a-7e7e-5568-9d4d-0fda6d9e5ea5 | note | Acceptance Criteria - AS1379.2.3
7e15badb-46b7-56c6-bfab-8778656a6726 | note | Frequency - 1/1000 tonnes
9e041410-b66c-512b-92c6-8d27e7411f06 | note | Initiated by - Supplier
eba55a77-0ab0-5436-82b1-00becd49158e | note | Approved by - Tech Mgr
bff9d7fe-05e0-52e1-a259-b4809bd5fb13 | note | Verification/Witness: Supplier - W, R
e017140e-90d9-565f-8492-9cf259be669f | note | Verification/Witness: HOL - W
b2484355-173d-5e84-bdda-ae87b4eda37e | note | Verifying Document - Supplier test report
8e9c8ee7-3404-5901-9c28-ed084c30ba93 | note | Record Location - Tech Mgr office
bf87235f-4852-55dd-ac36-e73b389d5f0d | checkpoint | 3.2 - AS1379.2.3
90a89ed1-074b-54da-ab43-9d31e898ef46 | note | Inspection Description - Flakiness Index
59996869-f8ca-55c7-afb3-73c55d972e17 | note | Test/Inspection method - AS1141.15
0cdc2a4a-072e-568b-b20d-6f6a70218d86 | note | Acceptance Criteria - AS1379.2.3
ed276801-9212-5213-82f0-c1aea7cf3664 | note | Frequency - 1 per month
6f42b9d2-01e2-50d7-a771-869c4f68d883 | note | Initiated by - Supplier
99df91ef-1b47-5dff-b241-e63b7f464041 | note | Approved by - Tech Mgr
fabd7f73-e5a9-5470-8fc2-5e12121fcc07 | note | Verification/Witness: Supplier - W, R
cf8188bd-ffa9-5ec8-b024-ced7c8850502 | note | Verification/Witness: HOL - W
6071c129-e1dc-5bf1-b8ec-a741604e226c | note | Verifying Document - Supplier test report
7649344e-9b58-569d-80a2-c53e7c5994d3 | note | Record Location - Tech Mgr office
75293781-92f8-597a-a5f2-9a7d61ce4029 | checkpoint | 3.3 - AS1379.2.3
d77a03fe-5c7a-5da5-b26d-3c76e1a5decf | note | Inspection Description - Particle Density & Water Absorbtion
f1b5c3de-5aa8-5b98-a644-9e9a31559c3c | note | Test/Inspection method - AS1141.6.1, AS1141.5
706cb644-832c-5f18-b582-7cd29201dc3f | note | Acceptance Criteria - AS1379.2.3
ef6aeaf7-56b6-5f3a-bd46-04e9c9ae5bdf | note | Frequency - 1 per 3 months
6761046f-11ff-5253-8296-d8ac3da12157 | note | Initiated by - Supplier
4e2bf9ee-b702-55a1-8d5d-ccb6295d1480 | note | Approved by - Tech Mgr
0bdbf743-cfd2-56e5-9d99-73dab69d6293 | note | Verification/Witness: Supplier - W, R
756f561a-06c6-5164-9409-b592af2cd80d | note | Verification/Witness: HOL - W
4194c6c4-f8da-5e91-b302-889ce7143aa3 | note | Verifying Document - Supplier test report
9a156953-26e1-5f0f-80f4-b112f16a4c01 | note | Record Location - Tech Mgr office
78181c15-11bc-5013-84d2-a4ec9c501a1f | checkpoint | 3.4 - AS1379.2.3
a9b42171-555e-5b35-8efc-210030104666 | note | Inspection Description - Los Angeles Abrasion Index Value
cf64a4f4-e5dd-5234-abc9-c66a9fa3bb4f | note | Test/Inspection method - AS1141.23
9497de55-dd23-5f18-9839-d735c6b2080c | note | Acceptance Criteria - AS1379.2.3
cfe06d4a-d1e4-5877-95bb-5b367cbeb78e | note | Frequency - 1 per year
6f484f8b-6bee-5a36-9c0f-49c7f4dab7ef | note | Initiated by - Supplier
4cf457ca-da7f-573c-98cd-729f2902a2a9 | note | Approved by - Tech Mgr
350a2201-473e-52de-88f7-b9aaf3194dcc | note | Verification/Witness: Supplier - W, R
294af989-6cb8-56ad-8b9e-ff5b570c110d | note | Verification/Witness: HOL - W
2601cee5-17e1-5a6a-bd3f-8eb17e890fe3 | note | Verifying Document - Supplier test report
7729f1aa-6f76-5ca4-9ccf-ac910409cbd3 | note | Record Location - Tech Mgr office
6a3a7aaf-efa9-5717-ab38-7f9e218de83e | checkpoint | 3.5 - AS1379.2.3
2ea03519-dbac-5426-b342-9ebef12327a9 | note | Inspection Description - Weak Particles
e2063494-f159-5047-a0b3-afe487d93b7c | note | Test/Inspection method - AS1141.32
bd320f79-0581-5dca-902d-0a2802a08cae | note | Acceptance Criteria - AS1379.2.3
6feebfc9-a096-581b-8e64-badcf4995ae8 | note | Frequency - 1 per year
2d40c2a2-eb46-51c7-b127-ba06ecad9a97 | note | Initiated by - Supplier
047280db-e63e-5a63-be4f-5a9689e53ef6 | note | Approved by - Tech Mgr
81194b8b-3b42-5a7b-bb15-296507742150 | note | Verification/Witness: Supplier - W, R
8f467c84-4c4a-5687-90b6-fcd919d0d606 | note | Verification/Witness: HOL - W
bb8ae132-1108-503a-beb7-5abad5420d28 | note | Verifying Document - Supplier test report
5d257d22-b264-5441-874c-873169d1241a | note | Record Location - Tech Mgr office
f53c62bd-04a5-533e-b171-a7352348ff69 | checkpoint | 3.6 - AS1379.2.3
7862026e-5234-5cd4-babe-170741560dea | note | Inspection Description - Wet/Dry Strength Variation
02910be3-8956-5aee-a905-345a02900d2b | note | Test/Inspection method - AS1141.22, AS2758.7
2453eec4-72dc-5d90-a914-ec7392d23a1f | note | Acceptance Criteria - AS1379.2.3
07e5a24f-1d0a-54db-8e4d-a58329faa5b2 | note | Frequency - 1 per year
71f61974-3f03-5854-b05f-2f35a6b613d6 | note | Initiated by - Supplier
58b77205-a3f5-529c-8fc5-b019f730aeba | note | Approved by - Tech Mgr
7d200daa-e924-5fcc-96ba-45d2427c4dec | note | Verification/Witness: Supplier - W, R
94bcc53f-5c91-5e26-8edd-0761081ac44f | note | Verification/Witness: HOL - W
70cf9164-a09e-527b-9641-fd90c939f98c | note | Verifying Document - Supplier test report
1e857470-6285-5d95-9ac0-5e7986219ff9 | note | Record Location - Tech Mgr office
83a0c381-226a-50d7-87b6-b3e025e4ef20 | checkpoint | 3.7 - AS1379.2.3
b463dc6c-6a7f-5d03-97b5-82b728dff5c2 | note | Inspection Description - Petrographic Analysis
1f9f802f-a09e-56a4-b9f3-e74f84bab64b | note | Test/Inspection method - ASTM C295
eedfbc46-e6d5-590e-9da1-eb543ac8ee4a | note | Acceptance Criteria - AS1379.2.3
83a90181-dbfd-55f7-9829-7b7480a99318 | note | Frequency - 1 per 2 years
44e063b5-4ac1-513a-a5f2-dcb89f30d3f1 | note | Initiated by - Supplier
09d38fe5-9784-5f59-b41b-7ec96c806188 | note | Approved by - Tech Mgr
3bb3982a-464f-582b-a837-8fc2aa6ffc9e | note | Verification/Witness: Supplier - W, R
67c73329-0ac8-571d-921b-6ebf494ebe95 | note | Verification/Witness: HOL - W
26fa76af-a295-597f-b2fd-6f4347c3c79f | note | Verifying Document - Supplier test report
7646f751-c2cf-5272-8240-7cfe5d45c67d | note | Record Location - Tech Mgr office
96127b49-2878-5c5c-afb8-3692ed0a25b7 | checkpoint | 3.8 - AS1379.2.3
b6c26665-5ac8-5e66-bb3e-0f5d9d3845b2 | note | Inspection Description - Sodium Sulphate Soundness
f3b58125-d5fe-5ef1-96f6-d0d159fc1f47 | note | Test/Inspection method - AS1141.24
c1e4fa64-6b6c-5e9e-bf37-7fa10b623c18 | note | Acceptance Criteria - AS1379.2.3
95448144-7b59-587b-830d-e74f9a3538a5 | note | Frequency - 1 per year
5261eded-37c7-51a3-b022-76899d6b282f | note | Initiated by - Supplier
43cf3a88-fee2-5c11-a303-610764a6089f | note | Approved by - Tech Mgr
becb2948-1558-5b62-9f21-332e6d2cc6fd | note | Verification/Witness: Supplier - W, R
9e2f1709-9d4a-5cd3-adaf-a04de8f283a6 | note | Verification/Witness: HOL - W
e7bb28a2-b3ef-5888-8cac-2615ce247c99 | note | Verifying Document - Supplier test report
d4b72f93-bc74-521a-b677-5a246cc356f4 | note | Record Location - Tech Mgr office
72370808-aa65-502a-9694-95fc4b916a1e | checkpoint | 3.9 - BECA Cl 11.4.6.2
772b14dc-db2d-5310-8e06-3eeb599c8cee | note | Inspection Description - Reference Sample
82468b8b-714a-5c37-a6df-cb0c6be997ee | note | Acceptance Criteria - -
366af996-8450-553a-bd47-bf28d24e5dd7 | note | Frequency - Once Only : 2 x 25kg samples of each coarse aggregate fraction
a2ded056-c7d6-5171-b6f9-3a17482d82e6 | note | Initiated by - Supplier
fdfcbd0a-98db-51e5-807c-afb2ca347437 | note | Approved by - Tech Mgr
e226a775-e113-5f96-b44a-0680cc11b5ad | note | Verification/Witness: Company - W
acaaa783-556c-582f-8f46-d97d6659a9d4 | note | Verifying Document - Record only
8de157b8-2b3c-5a84-ba39-83a0f5b7232a | note | Record Location - Tech Mgr office
b2563f1d-4aef-5fa3-9870-0c6a03784189 | section | 4 - Fine Aggregate
5fc44e36-7fa0-5d7d-a20e-b0d4a06a601c | checkpoint | 4.1 - AS1379.2.3
91a7f04c-6174-5cbd-81fb-8e809b5629ad | note | Inspection Description - Particle Size Distribution
a0095355-387b-5fdd-80c0-59a3228d2799 | note | Test/Inspection method - AS 1141.11.1
12406254-bfc4-593f-89aa-2d5a6583aa10 | note | Acceptance Criteria - AS1379.2.3
f01b2fc1-3e64-5b5e-8b61-e68890c10b7a | note | Frequency - 1/1000 tonnes
460289a1-f106-5554-915a-79af4262e6ab | note | Initiated by - Supplier
49f42c2c-1354-5d0d-bb68-b83a80606302 | note | Approved by - Tech Mgr
5cdd97fe-5016-54b0-b2cf-fa03557bbc67 | note | Verification/Witness: Supplier - W, R
462e47af-aac5-5f0b-9cce-bd4bb573bf9a | note | Verification/Witness: HOL - W
7008a2d9-0a29-597f-bfb4-12d0ed12c4e4 | note | Verifying Document - Supplier test report
a73a4a31-e837-5f97-b6cc-336eb3a0a470 | note | Record Location - Tech Mgr office
f19e05e1-9030-5629-8ef4-6a295bf9049d | checkpoint | 4.2 - AS1379.2.3
a479e826-a0c1-58a9-9c12-46b01790c724 | note | Inspection Description - Sodium Sulphate Soundness
ad4fed8d-fd24-5f65-a31d-8bed878b32c7 | note | Test/Inspection method - AS1141.24
2a14e042-2fc3-5bb9-8ca7-6990dc585985 | note | Acceptance Criteria - AS1379.2.3
32208901-2adc-5443-be69-df267f5d1085 | note | Frequency - 1 per year
024077bd-21f7-59ae-b227-e2854a87b0b0 | note | Initiated by - Supplier
d047ef0d-c0d8-5048-80ec-edaed8462bd6 | note | Approved by - Tech Mgr
545b60c3-9a61-53c7-8276-0dacae83b151 | note | Verification/Witness: Supplier - W, R
bc30ef70-2a5a-5f4f-b5db-5b079ab49bc0 | note | Verification/Witness: HOL - W
613e4bef-9be5-58af-bf3c-41b4c40f1feb | note | Verifying Document - Supplier test report
21c54219-2acc-5809-849d-007c0efcd879 | note | Record Location - Tech Mgr office
d475187e-ea0d-524e-ab0d-0d0880da5db4 | checkpoint | 4.3 - AS1379.2.3
bc956910-fa68-5041-b4dd-f7e4b9094652 | note | Inspection Description - Particle Density & Water Absorbtion
36d7d301-2c90-5eee-a4ea-4eb2aa424595 | note | Test/Inspection method - AS1141.6.1, AS1141.5
04f941df-938d-503f-9c1f-090c5e278c93 | note | Acceptance Criteria - AS1379.2.3
190b9600-7a5f-5522-8ebb-5282359aeb71 | note | Frequency - 1 per 3 months
64dfe3cf-39da-575d-a0e2-47bba7f1920d | note | Initiated by - Supplier
33084b4e-2b4f-5d20-99eb-ac33be4d24a2 | note | Approved by - Tech Mgr
c3174e94-e0e3-5f3d-ab66-0166c34c52f9 | note | Verification/Witness: Supplier - W, R
6192201b-ebff-5f79-b33d-d1d3cd8ad352 | note | Verification/Witness: HOL - W
6cc35bd8-be4a-5b18-b4ff-1c8484f1edec | note | Verifying Document - Supplier test report
70d64e6f-7c36-5f71-ac2b-1a70141f8abe | note | Record Location - Tech Mgr office
b34923f2-ce05-5a63-89b6-c19892d24abc | checkpoint | 4.4 - AS1379.2.3
5f86ec19-9421-5071-b572-9334f65a5c35 | note | Inspection Description - Petrographic Analysis
e0dbe218-dabb-5a8c-b24c-3c7436386b46 | note | Test/Inspection method - ASTM C295
60dcc288-cd44-5452-b9ce-0a8f77d1580b | note | Acceptance Criteria - AS1379.2.3
52fa2847-38d2-5d50-9a1c-81fc8080c9e3 | note | Frequency - 1 per 2 years
b48651d2-de84-5296-b25c-a53da4746b06 | note | Initiated by - Supplier
07df4faf-8ccb-5c64-bca7-73ff66277bde | note | Approved by - Tech Mgr
e8b23dbb-23a4-578a-b9fb-8a76d7747c70 | note | Verification/Witness: Supplier - W, R
b7441240-b060-5784-b22b-5bdd8062aa57 | note | Verification/Witness: HOL - W
8018a892-db82-53b3-bfb9-36ad591ac064 | note | Verifying Document - Supplier test report
d4c51f49-885a-56b8-a684-18f7369922ad | note | Record Location - Tech Mgr office
810d35c9-a489-52f1-b0df-7c70b4124cac | checkpoint | 4.5 - AS1379.2.3
f637c367-2a49-5804-9b9f-81e1b15e473a | note | Inspection Description - Sugar Content
872be669-cfda-539d-bef3-d05adbac06c5 | note | Test/Inspection method - AS1141.35
6041b2fa-59d6-598b-944d-988a0e06eb8e | note | Acceptance Criteria - AS1379.2.3
b640ca0b-a92f-5ac6-9eda-5a332a8f8cc0 | note | Frequency - 1 per year
f3895a18-2634-58d2-bffd-e7ec5329f6fd | note | Initiated by - Supplier
de40d2e8-169f-50a9-a913-89f3f8bc33a3 | note | Approved by - Tech Mgr
73fe4fee-ce58-5e47-977f-edc1ea66e2a6 | note | Verification/Witness: Supplier - W, R
8cd2ec01-e76d-564d-a1e9-a4fa8bd4baf2 | note | Verification/Witness: HOL - W
7a8df9f5-3483-5931-b767-c2517b0955d6 | note | Verifying Document - Supplier test report
5fb18956-3aba-5a1a-93b1-14e8132d6176 | note | Record Location - Tech Mgr office
0a3e5c3a-71b6-5949-aea4-3e0723b4e25e | checkpoint | 4.6 - AS1379.2.3
9a8c871b-3927-5c29-a314-74698e27a118 | note | Inspection Description - Clay & Fine Silts
784bf440-a5d9-58bc-b298-c6560028660b | note | Test/Inspection method - AS1141.33
23849356-ae11-5012-b18d-eef06b7cecbd | note | Acceptance Criteria - AS1379.2.3
b4fc7a27-eb5f-58cd-b509-688d39148169 | note | Frequency - 1/1000 tonnes
3fcd12b8-1091-58a6-9b68-f6699f433a06 | note | Initiated by - Supplier
11fbac60-ef98-51ad-a04f-44fae04669fb | note | Approved by - Tech Mgr
2ce00b08-45a5-55d6-b983-1bb2221780c4 | note | Verification/Witness: Supplier - W, R
e6118be6-3bee-5bcd-89ef-ccc0c5cec3cf | note | Verification/Witness: HOL - W
daa78a73-916c-552c-9deb-25c2c53dd136 | note | Verifying Document - Supplier test report
9b8e68de-ced3-502e-ad3a-e88a4192c08e | note | Record Location - Tech Mgr office
5d2b7abc-2be1-5b91-8db8-83e1dfcecd26 | checkpoint | 4.7 - AS1379.2.3
f6f14299-8296-54ae-94fa-61e22d6f1193 | note | Inspection Description - Organic Impurities
2d0e78af-5196-5838-ab1c-db807c1b22b4 | note | Test/Inspection method - AS1141.34
fef298e1-6611-5eee-aae7-356335b7fb52 | note | Acceptance Criteria - AS1379.2.3
47422149-e177-57a4-8116-9cdb10cf2844 | note | Frequency - 1 per month
c76e64ff-0f87-5bbb-83b4-2ec57d836947 | note | Initiated by - Supplier
86f9f2c2-7c0a-5ad1-ac13-3549d7b658f5 | note | Approved by - Tech Mgr
05e94dbf-f486-5f95-9f8c-4d1235413d66 | note | Verification/Witness: Supplier - W, R
96150f32-c3e3-5371-bfc2-aa61268a5c7f | note | Verification/Witness: HOL - W
bc7eacfb-5787-576a-9e3e-498bdfb2ee00 | note | Verifying Document - Supplier test report
9673972d-5e7c-5f9e-bdc4-d3994313a734 | note | Record Location - Tech Mgr office
d610d698-50c7-54dc-bbb0-a3a5195da543 | checkpoint | 4.8 - AS1379.2.3
0fd9ee91-a161-593e-8343-547b5ee63894 | note | Inspection Description - pH Value
28a6bfd6-6bf2-516d-a727-10b9712b7213 | note | Test/Inspection method - AS1289.4.3.1
ef2939e4-d143-5b7e-88c3-113bbaf9bacf | note | Acceptance Criteria - AS1379.2.3
31850176-3d8d-574b-a473-5140164eba5c | note | Frequency - 1 per year
feb1ac21-9126-524f-ab83-00b12020b868 | note | Initiated by - Supplier
b9d1defe-0cf7-5a62-b77c-2bbe0f346e9c | note | Approved by - Tech Mgr
1e7473b4-1fb0-5220-8b76-dda1f4803b71 | note | Verification/Witness: Supplier - W, R
a4e941c5-4923-5dad-95e8-492b28844597 | note | Verification/Witness: HOL - W
820e6ce2-1db5-5aa3-8585-7a63aa5687bd | note | Verifying Document - Supplier test report
e0e623d5-817f-5d1f-ab0d-3d99c95ff021 | note | Record Location - Tech Mgr office
36ae7dab-6136-5351-b7b5-6ddd1b071af4 | checkpoint | 4.9 - BECA Cl 11.4.6.2
a699308f-7f0e-5c35-8cf3-68cd8bce5732 | note | Inspection Description - Reference Sample
e8dd2da3-062c-5e66-a095-3721789f14ce | note | Acceptance Criteria - -
de751385-d2cf-59b0-9ade-d9e7a18d5da0 | note | Frequency - Once Only : 2 x 25kg samples of fine aggregate
8b516e56-c066-5d4f-a347-092d28be179e | note | Initiated by - Supplier
bbf06296-4832-5e89-94ac-22dccb679be0 | note | Approved by - Tech Mgr
4f1ad25a-7a3b-5c43-9e04-037e2a0a1a42 | note | Verification/Witness: Company - W
c22df78f-1138-5d0c-8bc9-5f2c8db3698e | note | Verifying Document - Record only
088dec74-7049-59e1-971b-7dbc7c0f4bfc | note | Record Location - Tech Mgr office
4ba8f446-d7ca-5cae-9321-342cea4afdda | section | 5 - Water
9248abba-5aa2-575b-ae02-45ef91bf702d | checkpoint | 5.1 - AS1379.2.4
efc3429b-9077-57db-8b17-438a429d0fb6 | note | Inspection Description - Mains water
2b0352df-726a-53e1-a469-d27ef6c8673a | note | Acceptance Criteria - Main complies
6ad14ccc-645a-57ea-a785-e3f9cff43ef8 | note | Frequency - Nil
33a58d6d-3f93-52b5-9fbb-5ef96287095e | note | Approved by -
42da8b0c-8014-5bd9-a73a-1013ebf1d1c7 | checkpoint | 5.2 - AS1379.2.4
6050ac90-f7d2-5d16-b7e1-018d7fb3543e | note | Inspection Description - Non mains water
18f0c1e1-fea7-5c85-bc4f-fb596794b0be | note | ~ Sugar
d42317e8-27cc-5c22-ba29-6815d01403e1 | note | ~ Oil & grease
9bd5d003-1f10-5256-8a71-a61f20620f31 | note | ~ pH
3272e43d-92ac-5639-8ebf-b3f90e39db5a | note | ~ Chlorides
c7d913e5-6184-5f2c-9c60-d0778b4be5e5 | note | ~ Sulfates
9a59e793-63b7-570f-9fdd-816a43d97ce0 | note | ~ Total suspended solids
ec04db76-54e5-5610-a7e9-514826b90894 | note | Test/Inspection method - AS1141.35 APHA 5520 AS1580.505.1
fc083733-280e-5437-8054-a6379a117460 | note | Acceptance Criteria - 100 mg/L max
4c78f8da-b910-589c-9175-8db8bd7ce72f | note | ○ 50 mg/L max
31b9d76e-f855-5163-aa8e-c9dccefa4f4f | note | ○ > 5
8625774b-50a0-55f1-8bc6-6b21bf216824 | note | ○ 500 mg/L max
d855d1ab-19d4-575c-8604-548e0b1f2b1c | note | ○ 500 mg/L max
7aa71ddb-5144-5846-a3f6-5b5784a40558 | note | ○ 2000 mg/L max
5e666e01-a75c-581a-9e60-90f2a3ba5bd9 | note | Frequency - 1 / 6 months
2b80f98b-9f39-5ad0-a1cf-39ccc89aac5a | note | Initiated by - AOM
0fb812ed-63ad-5a2f-9023-3bfc55c15def | note | Approved by - Tech Mgr
7776c732-147c-5674-ab90-74b7e023c2c0 | note | Verification/Witness: HOL - W
02cd6f1d-0d30-51c5-bfaa-f04d7aa2530d | note | Verifying Document - Lab report
02f8fe04-5380-54aa-95d3-693e0100fbe8 | note | Record Location - Tech Mgr office
82172cdd-75bd-5224-abe8-68e843bd97be | section | 6 - Admixtures
f91fd035-5479-576b-936d-9e6ada6f25c9 | checkpoint | 6.1 - AS1379.2.5
5a9a3039-b856-5dbb-bd8b-7200d9d24f52 | note | Inspection Description - WR Admixture general acceptance
d9bac8f9-cdfb-5f05-951b-69f7243c8317 | note | Test/Inspection method - AS1478.2
14f4a1a2-2822-57f6-8d1e-614baa13911f | note | Acceptance Criteria - AS1478.1 Table 2.1
bcd34a34-91bf-5490-80ad-c942cd1e15a3 | note | Frequency - Initial
4f415136-6b00-5405-a131-9f14b59a3ed3 | note | Initiated by - Tech Mgr
d98d6d36-272a-588d-ada7-66b459f8b9a9 | note | Approved by - Tech Mgr
78b48b48-3894-5ddf-a9e2-271741b8cc6f | note | Verification/Witness: Supplier - W, R
5f0f8b2f-9c28-55bf-95ee-c0928f582bd9 | note | Verification/Witness: HOL - W
a8fa61cf-702b-58ba-b831-01e13a4ac6b7 | note | Verifying Document - Supplier report
341fadab-bafa-5c68-bb82-9b4506cea225 | note | Record Location - Tech Mgr office
4e4a638d-2dd2-5211-a648-d67d85c14ba9 | checkpoint | 6.2 - AS1379.2.5
40be135b-821d-5d27-a5c2-15a6493c768c | note | Inspection Description - WR Admixture Uniformity test
c0597203-692b-545f-ba4d-cc293f0c1762 | note | Test/Inspection method - AS1478.2
4c2771b5-63fe-589b-98e3-ad10f202ca04 | note | Acceptance Criteria - AS1478 Cl 2.1.3
8ee3b20b-480a-513f-9737-795e2a60bcb3 | note | [Supplier specs for pH (+/- 1), Relative density (+/- 0.02), Non-volitle content (+/- 2%)]
aaeadb47-ba68-588a-9636-01eb680eaae2 | note | Frequency - MBCC Supplied (Each Batch)
9183ac6b-5f48-58ee-9bd1-f3574d0a64fe | note | Initiated by - Supplier
7aba0526-fb01-5191-b174-992245861299 | note | Approved by - Tech Mgr
6958eb3c-8a5c-530b-a38d-f190cfddfc1c | note | Verification/Witness: Supplier - W, R
b87f26c1-c35b-52cf-9665-56814f2d2d8b | note | Verification/Witness: HOL - W
2c905e60-a062-5f23-a260-21cd16357205 | note | Verifying Document - Test Reports
cad48da2-4e31-531b-9be2-0d8774711c84 | note | Record Location - Plant
cef5e708-184d-5b4e-8957-167b54d47b26 | checkpoint | 6.3 - AS1379.2.5
971f9dad-fcdf-5006-a7d8-59d02ae99e0d | note | Inspection Description - AEA Admixture general acceptance
c2f5feea-ffa8-5f2d-8e0a-5a72355b1b1d | note | Test/Inspection method - AS1478.2
f1c4ca3c-5d57-5694-b534-c54b254e640c | note | Acceptance Criteria - AS1478.1 Table 2.1
bbdcb664-0095-5321-b3a7-17d2f5b6e9c6 | note | Frequency - Initial
4dbf63df-2e5e-5f15-9728-7384abb8c54a | note | Initiated by - Tech Mgr
60699419-4f16-53e7-8bb7-22cb09c901a9 | note | Approved by - Tech Mgr
0bfe4df1-901b-5b72-b44b-211ace33d09a | note | Verification/Witness: Supplier - W, R
ed89ab92-3ff4-547b-9a8f-60c461d21aa0 | note | Verification/Witness: HOL - W
d6ed629c-4529-5435-8916-fa7d1f81fb12 | note | Verifying Document - Supplier report
1279fcca-41cc-5a08-b40d-dfa6d667a3ca | note | Record Location - Tech Mgr office
5ab4d9d7-2bbe-54c7-b7a4-bd3039c618b0 | checkpoint | 6.4 - AS1379.2.5
97edff47-9a2f-5a96-a91d-c99209efafc4 | note | Inspection Description - AEA Admixture Uniformity test
dbc1981c-c4ad-5e9b-ade1-2b55479799fb | note | Test/Inspection method - AS1478.2
7f272233-7875-5780-95ba-1d7bb91713dd | note | Acceptance Criteria - AS1478 Cl 2.2.3
13b47d1d-9ac7-5ad3-a465-3f7a1913a4a9 | note | [Supplier specs for pH (+/- 1), Relative density (+/- 0.01), Non-volitle content (+/- 1%)]
0f022f6a-904d-5876-904b-d66750fc52fc | note | Frequency - MBCC Supplied (Each Batch)
8d3af956-a914-5603-90ff-735099caf42b | note | Initiated by - Supplier
548b92e5-6718-538c-9b7d-9fd26515d47d | note | Approved by - Tech Mgr
31329bfb-1996-5f23-b81e-04171442d096 | note | Verification/Witness: Supplier - W, R
9ef2cdc5-4250-5b30-845a-a7b5e6d68413 | note | Verification/Witness: HOL - W
428e968b-2712-5af9-82f2-71065f8113d0 | note | Verifying Document - Test Reports
023053fa-86a4-5a7f-a8f4-6a58fa8c3b85 | note | Record Location - Plant
c7a9e9cc-e4f7-5ac5-ae90-c0930acd2ae1 | section | 7 - Transport
87c85bb4-1a58-56da-b8b1-d4b1c3d65ca0 | checkpoint | 7.1 - HOL QMS PN6.1
8602acab-3d14-53b4-9d19-2122a671fb55 | note | Inspection Description - Agitator blade inspection
fab122c6-09ca-5d09-b971-811c80aed791 | note | Acceptance Criteria - Concrete Barrel Solution - No excess buildup, No excess wear
69e4f90c-7429-5bbd-9365-28224629cf7b | note | Frequency - 1 / 3 months
b0d4b03b-c057-5fcb-81c3-cc6a989eec3c | note | Initiated by - PS
578f8000-e5ac-58a1-9469-8700e856a6b5 | note | Approved by - AOM
c34facf5-53eb-5972-8e9b-217aab3ef0a4 | note | Verification/Witness: HOL - W
45d843ba-c6c5-52d5-8afc-e9206ddfdf19 | note | Verifying Document - Inspection report
647f4bf8-e3e4-510f-b16e-e8227e672668 | note | Record Location - Plant
187e8e76-2885-5aa9-a78a-6539d1e1a50a | checkpoint | 7.2 - AS1379 3.5.1 (a)
7da0c1dd-5335-528a-b846-8713ea5a6763 | note | Inspection Description - Mixer uniformity test
db07f433-f819-5b57-8be3-65e069b2bc3e | note | Test/Inspection method - AS1012
b1b661f9-510a-5981-8c43-e4c18682bed0 | note | Acceptance Criteria - AS1379 Appendix A Table A1
2f07405d-f6e4-5588-ae98-df31f1a2ffd8 | note | Frequency - Initial for agi type
6ba29222-f6d7-5b5b-ab79-5c96a60fe9e9 | note | Initiated by - Trans
0d9d05bc-2de8-5720-9990-c08e638162ae | note | Approved by - Tech Mgr
ad482c10-7eec-588d-9904-c8746dec0930 | note | Verification/Witness: HOL - W
aa6ee9ec-4c79-538a-abb5-1c2775a053ab | note | Verifying Document - Manufacturer report HOL test report
b7893fb9-d6b8-54e7-9877-f2c5a013d719 | note | Record Location - Tech Mgr office
82d23ddb-a1eb-47d1-a0d2-701243a4e79d | checklist | FH-ZU2-QU-ITP012 - High Early Strength Lean Concrete Pavement Production - Rev 0 | itp | ITP012 - High Early Strength Lean Concrete Pavement Production
edc13f40-3e52-41b4-bd32-2185b2c2a11c | section | 1) Plant
a97e1d8b-341c-4100-8fef-4008139a4533 | checkpoint | 1.1 - Batch tolerances
b9943286-8c92-57b6-8049-dbdb04338ccf | note | Code / Spec Ref - AS1379 4.2.1
86ed0e80-443a-5fea-bdac-d56be1f3b475 | note | Acceptance Criteria - AS1379 Table 4.1
438fd021-7306-5e5b-85c2-a6c6da35918a | note | Frequency - Each Batch
991f71dd-1f32-5959-846a-8c657a14ee5b | note | Initiated by - PS
52dacf51-9d99-59ea-a2f2-0eff4322163a | note | Approved by - PS
0f36ef84-1915-54ff-befe-7b83b6322f0e | note | Verification / witness: Supplier -
5ed1d111-6563-5dce-b984-57648edd3b09 | note | Verification / witness: HOL - W
ef37a3e1-6b7d-5491-a4fa-8980d1fc1a53 | note | Verification / witness: Company -
81f94c7a-6d9d-560b-9e02-a6ecb4655c47 | note | Verifying document - Electronic
8c735506-9d18-5521-a82a-f0aaddc76ced | note | Record Location - Batch computer
c9cf40f4-9d20-5456-b00b-6575ee66c9f3 | date | Date Completed:
f72d9654-71c9-46a6-9383-c16c41657ced | checkpoint | 1.2 - Record Plant Malfunctions
fe5e3b38-fcda-55b4-bd5c-a8d47237cee7 | note | Code / Spec Ref - HOL QMS PN6.1
fd8dc4bd-0324-5423-ac5a-4c4fc3cfbdc3 | note | Acceptance Criteria - All plant mulfunctions are to be documented
fa562d49-2d3c-54a3-b504-abf4eb5e5c7c | note | Frequency - Each Time
a77816f3-1199-5280-87a3-b348fad9f61f | note | Initiated by - PS
2acd8d79-7e14-5bf3-8667-2a75277aac05 | note | Approved by - AOM
7ef783a0-3483-50ac-966d-6dbaffb65ca7 | note | Verification / witness: Supplier -
2340a1e6-0420-5658-8e73-7d486bcc1fe3 | note | Verification / witness: HOL - W
ed8034bd-4577-5e5c-9e78-fe782cf7d08d | note | Verification / witness: Company -
75bde53d-1704-555d-924b-d889c46e7f90 | note | Verifying document - Register
719e1c61-189d-5f8b-ace8-01a4b17e7a32 | note | Record Location - AOM office
16ef357f-fe6d-54d6-a477-722d60637304 | date | Date Completed:
6e321a29-a1a9-443a-ac3c-99a45d07f169 | checkpoint | 1.3 - Weigh Hopper (Cem & Agg)
8f8727e7-bb5a-58c7-babe-2a01b8e9aa85 | note | Code / Spec Ref - AS1379.3.3.2
77cb045b-bd2d-596f-b45a-b2fa9aa82ac4 | note | Test / inspection method - AS1379
b0a12989-e5a4-56c9-bcdd-199a675ed144 | note | Acceptance Criteria - ± 0.4% of the Max. Scale Value
4c829d85-4c34-5612-b7ed-e52d02c53364 | note | Frequency - VicRoads Min. 3 Monthly
861febb3-c911-5b32-853a-94698ce7913b | note | Initiated by - PS
8966815a-2b52-5a13-b454-e5b942003cbc | note | Approved by - AOM
7b665053-3076-5875-8d77-77bb185af44b | note | Verification / witness: Supplier -
402ac3d2-d7ab-5bf6-b77e-0d583d52e373 | note | Verification / witness: HOL - W
ed307eb9-8c24-5e11-988b-7b082b8e3621 | note | Verification / witness: Company -
cb38e24f-e083-5e4b-a9a9-fb8f7e5c1e1b | note | Verifying document - Calibration Report
9f4f4427-faa7-57bc-9a79-7d1fb2f67792 | note | Record Location - Google
987e736e-eda1-5a16-b3cb-91600626b098 | date | Date Completed:
ff794717-2dbe-4b63-886a-209589a07787 | checkpoint | 1.4 - Water Meters (Plant, Slump Stands & Trucks)
8737d837-cb76-5753-b12b-0f1c82033495 | note | Code / Spec Ref - AS1379.3.4.2
13907fc4-b467-5aa5-966d-634a8a1bde9c | note | Test / inspection method - TRBE652973
a5dabc9d-bd5c-56d4-8e3e-256d9016ea45 | note | Acceptance Criteria - ± 2%
59aa70a1-64a1-59d5-bb7e-1c53db6991a8 | note | Frequency - VicRoads Min. 3 Monthly
96a20af5-6096-5ac0-9ccc-02bce14a4426 | note | Initiated by - PS
cf97e23d-10dc-5d23-9ef5-5ac39f854645 | note | Approved by - AOM
d5f30f2c-9142-5be5-af17-4c69c8bcbbd5 | note | Verification / witness: Supplier -
44894843-f68a-56b1-a7ed-9e2a3734d130 | note | Verification / witness: HOL - W
1c60cf52-ec20-57a5-b04f-caea0692f527 | note | Verification / witness: Company -
b8b650c1-f80e-5863-a273-765098ab3fd0 | note | Verifying document - Calibration Report
671fb2df-5f1b-5ce5-8839-10ac711f29f1 | note | Record Location - Google
9ed791ab-abd0-5dfb-bf23-42518c4f3174 | date | Date Completed:
1c5e587f-7cb4-412c-9325-ea44b82aeb31 | checkpoint | 1.5 - Admixtures
dbc3652c-886d-5280-b661-09bb4dd05cf9 | note | Code / Spec Ref - AS1379.3.4.2
9d33f62f-3fef-54ef-9f0a-a4485ffdadf5 | note | Test / inspection method - BASF TM033
8fc3ef05-0cc3-50fc-9de4-a93e5cf484f5 | note | Acceptance Criteria - ± 5%
eb2b3ef3-112f-5f9e-8a02-dd9842a9961e | note | Frequency - VicRoads Min. 3 Monthly
dc8c6ef6-c267-5003-adc6-8b9a5c8dceee | note | Initiated by - PS
1765eb1f-111c-580f-9c76-475eb0f8ba0f | note | Approved by - AOM
6271488d-95b7-5a75-9308-43bcf4fd8ca3 | note | Verification / witness: Supplier -
a981b4b2-dc29-5de4-9a9d-209358a26b92 | note | Verification / witness: HOL - W
237a327b-545a-5b8a-88e9-7929885889e6 | note | Verification / witness: Company -
54bafa72-211e-5270-b8ad-095504023831 | note | Verifying document - Calibration Report
cfb54465-b38c-5646-b0fa-ad55e1019ab7 | note | Record Location - Google
a45981de-03ad-5c34-8f01-dfc4d7434eb9 | date | Date Completed:
44755269-56df-49f8-a9d6-fa3fac84acf1 | section | 2) Cementitous materials
5c4173fd-eb55-473e-bd54-9203a8887f3c | checkpoint | 2.1 - Type GP cement
abd9caf3-6de1-5b89-bf0e-af93c59d9b2a | note | Code / Spec Ref - AS1379.2.2
f527d512-9e4f-5f43-aae2-a35480a5e8a0 | note | Test / inspection method - AS2350
70fadb4a-2d8e-54bb-a193-eefc88327446 | note | Acceptance Criteria - AS3972 Table 2
6b750388-405b-59a3-b257-3767b2d2d3b6 | note | Frequency - Cement Australia Supplied (as per AS3972 Clause 5.2)
5a603310-b5d1-5c43-9f1a-21af3b7ed1ca | note | Initiated by - Supplier
17633baa-3e25-5ed9-9c8a-6f08b45a1924 | note | Approved by - Tech Mgr
56a56fec-353d-5dbf-9f3f-4948f301508e | note | Verification / witness: Supplier - W, R
8236fa2e-ab76-54d0-8114-8d626fbc4294 | note | Verification / witness: HOL - W
a63f8795-017b-57e7-ad6e-19d834fea97d | note | Verification / witness: Company - H
a620975f-eec0-5127-a7ba-f33524a88673 | note | Verifying document - Supplier test report
f0349a24-e372-5beb-a1d4-e3b389ab2ea8 | note | Record Location - Tech Mgr office
47764ccb-0b61-5953-9e73-bef1b35e915c | date | Date Completed:
cfaf8949-7e4e-4d2b-8a4d-a876d082c59a | signoff | AUTHORITY HOLDPOINT
1add049b-66b2-4e75-ac26-531062f481db | checkpoint | 2.1 - Reference Sample
25854f03-0728-59e8-baf5-79efe4f27226 | note | Code / Spec Ref - BECA Cl 11.4.7, 11.24.5
8eb96525-2c07-5fe0-a757-41120e367171 | note | Frequency - Plant Sample : 10kg / 1000 tonnes
305ff2f3-7d72-52ab-9416-a222915fe4b2 | note | Initiated by - Supplier
eeb149b4-4e4e-5da8-b274-99b9dd5ebd62 | note | Approved by - Tech Mgr
66bc2e17-426b-541b-9bcf-9cad10c9283c | note | Verification / witness: Supplier -
7e4fbcf0-248d-53d8-8d62-52196e66b15b | note | Verification / witness: Company - W
eced0314-0172-5a5e-9472-82020e1804e2 | note | Verifying document - Record only
a2348df5-c85c-54f0-886d-f8e90e63ce9a | note | Record Location - Tech Mgr office
9053c326-82bc-5f22-afa9-3083c2564b15 | date | Date Completed:
d2caa701-36a4-4898-9e08-8229fa96b7df | checkpoint | 2.2 - Flyash
35a50202-cbeb-552a-91e2-89ebb2419b6e | note | Code / Spec Ref - AS1379.2.2
196e0c95-307a-55d7-9158-bbe967f2143b | note | Test / inspection method - AS3583
881112d6-e264-56f6-afea-b62657d41ce2 | note | Acceptance Criteria - AS/NZS3582.1 Table 1 - Grade 1
9315388a-767c-5c27-affe-b8c84000936e | note | Frequency - Cement Australia Supplied (as per AS/NZS3582.1 Table 2)
81a16c49-3dc7-5dc0-9e53-78c677ca8d0e | note | Initiated by - Supplier
132c0c7d-551e-5948-a6b2-fe43cefc1790 | note | Approved by - Tech Mgr
65bdabf6-21ea-51d8-9ca5-7af837745e1f | note | Verification / witness: Supplier - W, R
14d8f749-0946-5114-8b8b-61d235d14e94 | note | Verification / witness: HOL - W
3253f6c3-e5d2-5fb0-9e03-6eb075c5b4b6 | note | Verification / witness: Company - H
01e627b7-84e4-557a-b6f8-e4158425f6b4 | note | Verifying document - Supplier test report
83c5c614-1db8-5201-a22a-74534600c133 | note | Record Location - Tech Mgr office
ae0e60c4-b12f-59f8-95ba-6260049ed66e | date | Date Completed:
ba8e3df9-e5c3-4fda-8d19-45ac6bc4bcde | signoff | AUTHORITY HOLDPOINT
9118d094-5b36-4aed-ba31-12b6aba78cc1 | checkpoint | 2.3 - Slag
b4d3bed5-111a-5b44-8fca-9583230a163f | note | Code / Spec Ref - AS1379.2.2
b6e05616-5f6f-59ec-b607-7af329169d7e | note | Test / inspection method - AS3583
6e99ddfc-5001-5c89-af73-a4e50f8dcfb0 | note | Acceptance Criteria - AS3582.2 Table 1
dce785c8-6fae-56bc-91d5-9908a5585c5e | note | Frequency - Cement Australia Supplied (as per AS3582.2 Table 2)
8dbf925d-b67e-58cf-ad91-c18d1295db7b | note | Initiated by - Supplier
5a350411-7449-5907-a527-80335836962f | note | Approved by - Tech Mgr
cc9ad5f7-b490-53e7-8cae-12f3b5c9eece | note | Verification / witness: Supplier - W, R
eed9fba9-3735-5ef2-a46b-2e7499ebff7f | note | Verification / witness: HOL - W
5a5f6935-dac5-5bd8-8a5a-ddc4893382ac | note | Verification / witness: Company - H
b835140d-975f-5a72-997d-e0916d3f6417 | note | Verifying document - Supplier test report
6057b23b-09f7-5197-b78d-fbc1207438c6 | note | Record Location - Tech Mgr office
9e9a3f08-79dc-5ffb-9afb-0dd603ada1d3 | date | Date Completed:
3375405c-09ae-412d-bc1e-c6c95858e421 | signoff | AUTHORITY HOLDPOINT
f9f313ab-5df7-4c5c-beec-376bf9901ed9 | section | 3) Coarse Aggregate
8386e72a-f117-4f99-aaf4-101e6367e4c0 | checkpoint | 3.1 - Particle Size Distribution
24abf56c-1fa2-5227-a967-b5f12fb2275a | note | Code / Spec Ref - AS1379.2.3
afe34448-4998-5d03-8fdc-f1e77a480e4c | note | Test / inspection method - AS1141.11.1
b369a75b-aa1c-5206-a034-b72081a88e64 | note | Acceptance Criteria - AS1379.2.3
db2bdf35-74da-515f-9eb7-a2761d4d7a5b | note | Frequency - 1/1000 tonnes
ee7d4c66-dcf5-5825-ab49-ef36066d1c3d | note | Initiated by - Supplier
df25e526-3f46-5822-b756-610881baa325 | note | Approved by - Tech Mgr
2317cbad-f96e-5abf-8a3b-a52819813ddf | note | Verification / witness: Supplier - W, R
b9b8a7f5-5d21-5ed6-a8a9-70d5674f9885 | note | Verification / witness: HOL - W
e9af74c1-a573-59b4-8eb6-73f189315af0 | note | Verification / witness: Company -
d4ab6bb1-e724-5653-9e3b-25f3289dd6ef | note | Verifying document - Supplier test report
667b1d8d-7279-5877-8a72-f02c2fb0da42 | note | Record Location - Tech Mgr office
7200c1c0-aedc-5096-858a-9d02f673796b | date | Date Completed:
05928d06-835a-4f40-bfe7-a766574f9e68 | checkpoint | 3.2 - Flakiness Index
fe0dd362-fd47-5b37-9520-88d0d47b6d2e | note | Code / Spec Ref - AS1379.2.3
bc9f6c7d-3fcf-5c40-804c-6de3e3877cbe | note | Test / inspection method - AS1141.15
6e163739-97ef-56d6-a587-d3f5f9075dfb | note | Acceptance Criteria - AS1379.2.3
a439f23d-e9b8-5e87-b876-d06b4c72c586 | note | Frequency - 1 per month
0d3e5d88-c116-568c-9130-67ee2da56187 | note | Initiated by - Supplier
3c340d15-04bf-5dae-a944-f9243f1f272e | note | Approved by - Tech Mgr
a82ba656-862f-515e-b307-9d83a696815d | note | Verification / witness: Supplier - W, R
72aefff8-3025-5e12-a91b-879f5a509e13 | note | Verification / witness: HOL - W
26792800-4226-50f9-bae4-58db968d7551 | note | Verification / witness: Company -
41c51e60-0787-5e53-8427-f7b8dbd83b71 | note | Verifying document - Supplier test report
32110826-f48b-5137-88bb-aaa7a059d9d2 | note | Record Location - Tech Mgr office
864c1dae-d55b-5584-80c1-ae8ddf2954b8 | date | Date Completed:
debe25b4-f429-4cad-895e-ef8c8d75baa7 | checkpoint | 3.3 - Particle Density & Water Absorbtion
66d4a083-122e-5d71-b1cc-35607ac603a7 | note | Code / Spec Ref - AS1379.2.3
f2274462-dd70-59d1-b18d-cc1632e914ea | note | Test / inspection method - AS1141.6.1, AS1141.5
9c147e9b-129d-5239-84d7-fa59ea82ca85 | note | Acceptance Criteria - AS1379.2.3
09388605-9785-5866-b21b-a656f7deacd5 | note | Frequency - 1 per 3 months
9d4c5e9a-b0b8-52ab-b56f-1412c984cbd6 | note | Initiated by - Supplier
92057d16-cbe9-5e0a-bd29-b201ff7d50b4 | note | Approved by - Tech Mgr
3573a764-b5de-5a2e-8e51-9a557df9b29f | note | Verification / witness: Supplier - W, R
2a14c62e-7293-5833-bd17-27b9113010eb | note | Verification / witness: HOL - W
7937b1f7-987c-5bd1-8c40-9cd0d60f553e | note | Verification / witness: Company -
290fbbe7-26ad-59a9-abbc-a218231eeffa | note | Verifying document - Supplier test report
5a31faa6-1e4b-56c0-ab7f-854044dffb52 | note | Record Location - Tech Mgr office
48aa82df-fd5b-58d2-8e60-cf86a2a3b592 | date | Date Completed:
7b33ed51-2ecd-45d0-b4da-8b43af1c20b6 | checkpoint | 3.4 - Los Angeles Abrasion Index Value
734675c4-069c-53ff-b9ce-bc14fabea4f2 | note | Code / Spec Ref - AS1379.2.3
fbd44e06-4c91-5dda-a175-a68eb3b195fe | note | Test / inspection method - AS1141.23
18f2bb70-40ce-5dcf-b3fe-1c91b4fae187 | note | Acceptance Criteria - AS1379.2.3
726b883a-3343-561c-b4b9-e1991dec7941 | note | Frequency - 1 per year
f101ba7c-18d7-566b-824c-83bdecdca52b | note | Initiated by - Supplier
96513496-d2cc-56d3-9505-59d43f913538 | note | Approved by - Tech Mgr
0b7bad7e-a33b-5e69-9f07-ffe3087536b3 | note | Verification / witness: Supplier - W, R
94c01655-29d3-5f3d-aafa-45a449d28160 | note | Verification / witness: HOL - W
ab45d0a2-a135-5bfd-b024-c39e393b6dec | note | Verification / witness: Company -
2a642e70-e572-5188-b997-3e332e6ff716 | note | Verifying document - Supplier test report
d4b01e58-4bce-53ab-bfbf-3136413dfb86 | note | Record Location - Tech Mgr office
bb4c3505-e86c-5d5c-a0d3-be86d3b2655c | date | Date Completed:
2b66769f-6cba-42fe-ba43-b4ad46ef35ab | checkpoint | 3.5 - Weak Particles
439cad58-f79a-5e7f-8fdb-fd199b7dac95 | note | Code / Spec Ref - AS1379.2.3
9387e032-2fc4-5238-906b-aed2a4b61c3d | note | Test / inspection method - AS1141.32
775e9ee4-5d68-5ab0-9fd3-92350a9bf4ff | note | Acceptance Criteria - AS1379.2.3
f417dc5c-ef2a-5fb7-87c2-db6088b87927 | note | Frequency - 1 per year
cfa8cfb9-85d1-5910-b710-decf5b159156 | note | Initiated by - Supplier
2decac55-f4bd-5f09-97af-40da04bad463 | note | Approved by - Tech Mgr
03bc8377-c14c-5be8-af44-2b2bb37f8875 | note | Verification / witness: Supplier - W, R
b2166747-199a-51f4-bbb4-ab89ab3f7cd9 | note | Verification / witness: HOL - W
b812baa0-fe2e-5398-afda-5496113e2c5c | note | Verification / witness: Company -
ed87ed9b-ae0f-583c-ae77-e23bd175af2f | note | Verifying document - Supplier test report
b70d9a9a-9ad0-5bb5-99cf-2486c56f4b37 | note | Record Location - Tech Mgr office
5c8bb934-9bbe-5c58-bf1c-96b2464223a9 | date | Date Completed:
d4356f01-ef51-407c-b2c2-b76fa841c474 | checkpoint | 3.6 - Wet/Dry Strength Variation
0d4bb3b7-c7e3-540c-94dc-c16374437bd3 | note | Code / Spec Ref - AS1379.2.3
9e8d7adc-1c35-5f5b-af26-08f9f41aee83 | note | Test / inspection method - AS1141.22, AS2758.7
b9276b80-8244-5861-94b1-3efe63e43974 | note | Acceptance Criteria - AS1379.2.3
bcbda685-4dd7-566e-8349-9545c0ba441e | note | Frequency - 1 per year
54490f29-1984-599a-a603-19191ac06ab1 | note | Initiated by - Supplier
191963d2-3b59-5cbf-80a4-faece6a8d21f | note | Approved by - Tech Mgr
03806560-000e-550b-acd8-e0129322de17 | note | Verification / witness: Supplier - W, R
80cec203-6e6d-5bc5-8aff-32aa454a398b | note | Verification / witness: HOL - W
e6381391-c899-55df-9b5d-5d6a5b4c4c6a | note | Verification / witness: Company -
e8fda191-ec1e-5129-b851-e6e565546e19 | note | Verifying document - Supplier test report
bf2daf6f-06f9-558a-8124-4fc0b631ba31 | note | Record Location - Tech Mgr office
9a5bba11-aba5-5b3c-9c3f-3b79c2f7ade8 | date | Date Completed:
3c7b6ed7-b8ea-48b7-ae09-c85377ca19ff | checkpoint | 3.7 - Petrographic Analysis
53c8293e-5da3-55c8-b611-497a45577359 | note | Code / Spec Ref - AS1379.2.3
b8ebd582-479f-599b-9545-378ca18be74f | note | Test / inspection method - ASTM C295
5202357e-23a2-5434-ab83-d7684284b69b | note | Acceptance Criteria - AS1379.2.3
16761214-a63c-5de9-95dc-3e5b6e817599 | note | Frequency - 1 per 2 years
bd187a6f-035a-5ef5-82dc-9affd03061eb | note | Initiated by - Supplier
d23cbde1-78b3-520c-8107-1acf381ae7e7 | note | Approved by - Tech Mgr
6cf61d7f-fed2-54a2-9c19-baaa9ab4b2de | note | Verification / witness: Supplier - W, R
99f11b19-545d-5d86-aa70-47d0b40a568b | note | Verification / witness: HOL - W
42f1d435-0e89-5208-a124-6117552e98ee | note | Verification / witness: Company -
469fb7af-7262-59d2-8d3d-5af09aacb83b | note | Verifying document - Supplier test report
ff056798-31d7-5651-956e-5d1879b491e6 | note | Record Location - Tech Mgr office
b8db1986-b065-529d-b3a0-4999e5c5b938 | date | Date Completed:
57f025f8-2d24-4ab0-9d0b-7b8f4c4dc539 | checkpoint | 3.8 - Sodium Sulphate Soundness
2b8cd169-086a-5087-981b-720a44c296c1 | note | Code / Spec Ref - AS1379.2.3
4383fe7f-3046-5a0f-b16e-8b7691e5b1d8 | note | Test / inspection method - AS1141.24
5794c874-0527-5251-a934-c288853c1f38 | note | Acceptance Criteria - AS1379.2.3
4fbdef96-4e39-52e7-847c-d58ca1007198 | note | Frequency - 1 per year
2cd4e689-e209-5709-9546-31e6e71e80ec | note | Initiated by - Supplier
0b044a2d-b8db-58b0-a4d8-a7116135d47b | note | Approved by - Tech Mgr
cd5646a5-011f-59fe-97e4-0021bf7276dc | note | Verification / witness: Supplier - W, R
8e558b51-da9d-5d9b-8679-47627b8587c5 | note | Verification / witness: HOL - W
e9e46ed8-e88f-5729-abac-83b988dca861 | note | Verification / witness: Company -
25848c49-acb7-5913-8b49-75393cee6310 | note | Verifying document - Supplier test report
b8bffa43-4346-5bd5-bf84-74b9fb37f436 | note | Record Location - Tech Mgr office
cf077a02-ccaf-5653-a87a-25c8b54fdec4 | date | Date Completed:
d9281a25-bd39-4fe3-aabc-c0c63de31a35 | checkpoint | 3.9 - Reference Sample
7e74408e-8e5b-5ce6-87df-f2ccff62b9d7 | note | Code / Spec Ref - BECA Cl 11.4.6.2
d1f7f0c0-e629-5792-a9f6-ad231dd04d96 | note | Frequency - Once Only : 2 x 25kg samples of each coarse aggregate fraction
320703a5-3379-5f50-ab30-738118fc9b14 | note | Initiated by - Supplier
9ae42a6a-b4fe-534d-8359-6e14bad864bc | note | Approved by - Tech Mgr
977fb99f-96e8-5a2d-ac68-0aa6dcb260a5 | note | Verification / witness: Supplier -
04459358-b523-5743-a11f-6269abfc2d43 | note | Verification / witness: Company - W
8394b42e-d4d6-5dcd-9b63-4311738d0908 | note | Verifying document - Record only
92f682c1-1f0d-5bff-9d5b-4d85f51d25ff | note | Record Location - Tech Mgr office
d245be3a-ad15-5e11-9b2f-f43e35a69781 | date | Date Completed:
c79db396-6d98-4852-8ff7-8527edb277f7 | section | 4) Fine Aggregate
f6163620-bd4d-42f7-8bac-05084565a8f4 | checkpoint | 4.1 - Particle Size Distribution
265dc824-7729-54f1-9932-8ed6e1b0f860 | note | Code / Spec Ref - AS1379.2.3
9011214c-9d41-5906-82df-59ed4cfcec8b | note | Test / inspection method - AS 1141.11.1
e6e0ef2f-e30c-5fc7-a767-4ee704235a9d | note | Acceptance Criteria - AS1379.2.3
7a169ac1-f15e-51a8-90f4-4caaf6699db7 | note | Frequency - 1/1000 tonnes
964cf094-7536-5970-a2aa-543759e52fa9 | note | Initiated by - Supplier
44911cd1-3cef-5b3c-916e-71e92d3e90b5 | note | Approved by - Tech Mgr
55538d17-c012-5f00-9adf-f65ae9d2ea21 | note | Verification / witness: Supplier - W, R
f95d52a1-582b-5ac7-aa4e-2816eb7a1946 | note | Verification / witness: HOL - W
612ea03f-b3bc-5eb4-98ee-7bca5d762238 | note | Verification / witness: Company -
846d54d4-94fa-519f-adec-3aee0b08298d | note | Verifying document - Supplier test report
b5f9f5eb-dd0c-51b8-ad70-277d070a5bae | note | Record Location - Tech Mgr office
fe8148f9-5938-50a1-b320-83e3d40cf663 | date | Date Completed:
8955db6d-dc83-4b7a-a6ab-e91ad4a401b3 | checkpoint | 4.2 - Sodium Sulphate Soundness
b28f07df-1ccc-5837-9f5f-6fa0906ab4c2 | note | Code / Spec Ref - AS1379.2.3
48615c85-086e-52cf-9364-cca6b4cb7d6a | note | Test / inspection method - AS1141.24
154b4160-0f10-509d-bfb2-bb993f72f295 | note | Acceptance Criteria - AS1379.2.3
f6f04c40-5a0b-524e-81f6-e6c51880f083 | note | Frequency - 1 per year
028ab878-6ede-5733-aa4b-6b128b1df54b | note | Initiated by - Supplier
e73118e9-dfdc-5bea-a792-3cb65bdbb13e | note | Approved by - Tech Mgr
cf5b7bc9-86a5-5601-af41-ea8123425a12 | note | Verification / witness: Supplier - W, R
17e5b110-1731-5258-a5fb-090d960b90b8 | note | Verification / witness: HOL - W
6c73d8da-8b23-545a-a7f6-47b7269c7026 | note | Verification / witness: Company -
3adf876a-d6b4-5fe8-b366-70210ea45d63 | note | Verifying document - Supplier test report
c7c2ec74-6ef7-59b4-989e-c3455cf0aa50 | note | Record Location - Tech Mgr office
d6ea75a3-9441-5015-88c4-9eb858fb7d9c | date | Date Completed:
0b9e8909-1ff9-47ca-948a-f3339329c1d6 | checkpoint | 4.3 - Particle Density & Water Absorbtion
dd920061-a60d-56e1-bb03-de880c7efb6f | note | Code / Spec Ref - AS1379.2.3
1e9b8f72-0598-5e9d-be5d-6bab30622be3 | note | Test / inspection method - AS1141.6.1, AS1141.5
739dbaa5-e143-5f7f-885a-22fdcdcd2b49 | note | Acceptance Criteria - AS1379.2.3
ca7536c1-a2a4-50c7-8069-5edfd58c667c | note | Frequency - 1 per 3 months
aa180572-4f03-5ce0-8b38-97d8eaaf3235 | note | Initiated by - Supplier
2c75d8f0-9eb1-53fe-bd1c-c314883a7ee3 | note | Approved by - Tech Mgr
452cc093-ec42-5a4c-846c-c8e837e7d310 | note | Verification / witness: Supplier - W, R
d7704e8d-58bb-53bf-a63f-a73da3a44fc5 | note | Verification / witness: HOL - W
db37dbc0-20a4-5a5e-bdb9-14c094e105e4 | note | Verification / witness: Company -
837d27e8-541e-5148-b677-e6905e98f134 | note | Verifying document - Supplier test report
9f7633c1-a1ec-5775-919a-30c3f7a57033 | note | Record Location - Tech Mgr office
5c240f65-c32e-544b-9257-fa81b62c8000 | date | Date Completed:
06e98540-1cab-40b8-85e9-0deb902673aa | checkpoint | 4.4 - Petrographic Analysis
e855bcc3-01c5-5051-86f7-a170413f5fbc | note | Code / Spec Ref - AS1379.2.3
a5a1e08f-007b-5eac-9aac-ec2578e0563f | note | Test / inspection method - ASTM C295
fa8f7394-839d-557b-907c-63a551301df7 | note | Acceptance Criteria - AS1379.2.3
83c1b91e-fb58-5f7b-9bba-fb245fb63597 | note | Frequency - 1 per 2 years
358f1ef1-e001-5d13-94ed-09093c8bb312 | note | Initiated by - Supplier
3d6eb783-82ee-5b27-bfb8-56a703c2e774 | note | Approved by - Tech Mgr
07861264-5199-515f-af5b-412e0b5ba11c | note | Verification / witness: Supplier - W, R
8f097f4e-ba9c-517d-bd26-bbe1aaa1dcea | note | Verification / witness: HOL - W
3a676df1-7e20-5218-9b7b-07b23f399ce1 | note | Verification / witness: Company -
bd7d7035-b7f5-58ea-a0ab-37d00493df18 | note | Verifying document - Supplier test report
159c93a6-92a1-5a25-b51f-81430f5a4bcb | note | Record Location - Tech Mgr office
4fda0539-34fd-5b59-bfd5-df0f566ced18 | date | Date Completed:
42f0f619-7b79-45a2-b23e-f64ab492b0fb | checkpoint | 4.5 - Sugar Content
8600aaa1-c6fd-58eb-a76a-bd087e951647 | note | Code / Spec Ref - AS1379.2.3
84832ebb-71eb-56c5-8d7f-766ff3d809bd | note | Test / inspection method - AS1141.35
b433c2d4-e502-55fb-a0b0-5f2cd97a600e | note | Acceptance Criteria - AS1379.2.3
eb26ce3b-ac28-5b74-9811-bc58db801733 | note | Frequency - 1 per year
3f906e54-1b9e-517f-8b63-6fa9974f3958 | note | Initiated by - Supplier
0122dd7e-6fa2-5e07-a0bf-bbf543eef85e | note | Approved by - Tech Mgr
fc01066f-c10e-5287-8cca-ba2594ffb3f6 | note | Verification / witness: Supplier - W, R
b622e21f-09b6-51e3-8a72-ff655913f630 | note | Verification / witness: HOL - W
ec4c4773-accf-5295-b3fd-684d4d7b379e | note | Verification / witness: Company -
c366cd37-a3c5-5920-8616-13543b256e28 | note | Verifying document - Supplier test report
9b8db1f8-d570-537c-980b-5b862025333f | note | Record Location - Tech Mgr office
69f4bafa-5820-54ab-97f2-5cd00ddf7029 | date | Date Completed:
7d76f84b-0be7-41f8-a32a-dea1046e8e54 | checkpoint | 4.6 - Clay & Fine Silts
b672ea4e-06a8-5d58-b5ca-eb8db359f158 | note | Code / Spec Ref - AS1379.2.3
64a39945-3dd5-52b2-98d1-25a61cef07b2 | note | Test / inspection method - AS1141.33
d3cbc6f6-beeb-5068-9d9d-979dd39aa4cc | note | Acceptance Criteria - AS1379.2.3
871c0dc6-70e6-5a6f-bfab-4d3711fcef08 | note | Frequency - 1/1000 tonnes
81843c1a-abbc-59f0-a5eb-0bc3e680b29f | note | Initiated by - Supplier
449618cc-37a0-59b1-ba94-d777af1d8d12 | note | Approved by - Tech Mgr
cf5fd661-bf27-54ba-98cd-7588246d297c | note | Verification / witness: Supplier - W, R
72320293-2db7-5750-b63a-b6098347fb54 | note | Verification / witness: HOL - W
2482b533-7703-5a9f-9d35-a5b8fb594b79 | note | Verification / witness: Company -
6a6c7254-8524-510c-8364-839fe45ac37a | note | Verifying document - Supplier test report
9b552528-b025-5608-bf95-8a7465e345a9 | note | Record Location - Tech Mgr office
e0e6842d-7550-5e08-9652-d696bd9cc4eb | date | Date Completed:
d9cd53bb-32cc-4407-9309-617159e9b43a | checkpoint | 4.7 - Organic Impurities
5161c61f-dcd4-5169-8d04-72fc82235d5a | note | Code / Spec Ref - AS1379.2.3
95494532-92fb-518f-80dc-a4042d710aab | note | Test / inspection method - AS1141.34
b0f2d7af-ded4-5e08-8ff7-a3849ed6102e | note | Acceptance Criteria - AS1379.2.3
d26135c0-61f6-5c20-8c17-4eccbce7b687 | note | Frequency - 1 per month
830624ad-97fd-5b84-9c21-3922e5bb27cb | note | Initiated by - Supplier
78857267-0631-5832-aad6-fd17b0d9f52a | note | Approved by - Tech Mgr
7be7e075-2280-5d2e-bdc1-3382df5b0350 | note | Verification / witness: Supplier - W, R
690b7cf1-61f5-5e18-9426-352586b28089 | note | Verification / witness: HOL - W
58705b69-dbdd-5e9d-8dde-7568763ecd77 | note | Verification / witness: Company -
70795400-5487-527a-8701-b902aabfc089 | note | Verifying document - Supplier test report
328abee1-4402-5fb1-80bb-9564fbeaa6a1 | note | Record Location - Tech Mgr office
6e5dd8bf-6205-5ea8-a53d-f2e752610998 | date | Date Completed:
9f04d081-0b0b-4ae3-af45-a04144b6fdf0 | checkpoint | 4.8 - pH Value
56f2d134-a7e6-5c8c-8f69-1a1464af6801 | note | Code / Spec Ref - AS1379.2.3
6a8a3800-e44f-55ce-bd88-0cccbd95ec58 | note | Test / inspection method - AS1289.4.3.1
b1ccb5b4-0755-51fd-b8af-5a46a55ecd5b | note | Acceptance Criteria - AS1379.2.3
9fd7e24d-98f9-5919-906d-53240467cfa2 | note | Frequency - 1 per year
b8dc4b55-5423-5dbd-ad94-e92ff8101f60 | note | Initiated by - Supplier
8845a840-848f-5636-a7c4-ec6a02c1618d | note | Approved by - Tech Mgr
b8af71a3-d20a-57ec-8268-3b81e318603d | note | Verification / witness: Supplier - W, R
58f4db40-8bfd-5774-9ac5-ae972e4ceddf | note | Verification / witness: HOL - W
d0bcbe4d-c059-596f-b251-17232551e0de | note | Verification / witness: Company -
f9d76d07-3470-51bd-ae49-81273530bc61 | note | Verifying document - Supplier test report
bca0a5da-6efe-5fc4-bfb3-0cac3fb0135d | note | Record Location - Tech Mgr office
a9605e53-c04e-57ec-8d06-549aaabae551 | date | Date Completed:
f3173211-2957-42f6-ba76-2671c221c52f | checkpoint | 4.9 - Reference Sample
18a7b16c-9934-5d17-887a-2c01d48f07d6 | note | Code / Spec Ref - BECA Cl 11.4.6.2
f55d8740-acc3-57c4-bdd8-eaa27f7d5b3f | note | Frequency - Once Only : 2 x 25kg samples of fine aggregate
89bd1f9a-225e-563e-8308-ffb084e13164 | note | Initiated by - Supplier
6675574d-9988-58c5-9258-8d628999d95c | note | Approved by - Tech Mgr
e3739c5b-e62d-5403-a5bd-265561b6a789 | note | Verification / witness: Supplier -
a5568099-95d5-519d-97ec-e8301d98610a | note | Verification / witness: Company - W
1e77db03-8f73-55f5-b4f0-5142a7d0f527 | note | Verifying document - Record only
de633890-e5f6-5a31-a2a9-377ab12aa5dc | note | Record Location - Tech Mgr office
8a073d03-11dc-52d9-9c1d-82f7801e6f95 | date | Date Completed:
bf1a24c6-0106-416f-950b-de106dee6f30 | section | 5) Water
e4958b36-5af1-486e-b025-504e4af7524b | checkpoint | 5.1 - Mains water
739f1a57-d6c3-5829-b3fc-67c7eba95a45 | note | Code / Spec Ref - AS1379.2.4
9c1aac09-c3ed-5038-96dc-c8d9c654828f | note | Acceptance Criteria - Main complies
1a48c4bf-0c18-5e7a-8428-0dccda502dd5 | note | Frequency - Nil
302bff83-a342-5613-b8f7-f283c3bfc9b4 | note | Verification / witness: Supplier -
708bd87d-1d39-5671-be1a-485e77e1a279 | note | Verification / witness: Company -
5c1261fa-bbfa-505e-a14a-0549c977b3fe | date | Date Completed:
a5e0eff7-dbe0-4141-ba6f-9d54b1dcb4a6 | checkpoint | 5.2 - Non mains water
0d7fbfe5-c3ce-58db-b635-76054b34aa32 | note | ~ Sugar
47cab301-998b-5630-a401-3b86738800a8 | note | ~ Oil & grease
4bf50379-2c7f-5306-b773-cc8c29bfd6c7 | note | ~ pH
6e36a87e-91c4-53a1-a938-967ae61edf3f | note | ~ Chlorides
de14b083-c518-5ac0-a9c4-c58ec7014128 | note | ~ Sulfates
2f254903-e15d-59ee-bed1-ebe7a94affbc | note | ~ Total suspended solids
56c067a6-c169-52c8-a97d-b47e0ff09017 | note | Code / Spec Ref - AS1379.2.4
a99c7530-35f5-53b9-a3a5-c6d411992ae3 | note | Test / inspection method - AS1141.35 APHA 5520 AS1580.505.1
c2c1a316-786e-59f9-a606-d331d89a5ead | note | Acceptance Criteria - 100 mg/L max
08eb84fd-635d-5849-acc4-9a724549c3ab | note | ○ 50 mg/L max
a7efaa1e-d8b6-5cee-880e-69abc504530b | note | ○ > 5
c28aa2b0-c947-5e7b-a546-c5f43b602a6b | note | ○ 500 mg/L max
be3c79eb-0730-53b2-be56-e8bad243b8bc | note | ○ 500 mg/L max
d9c4adf5-5bbd-5186-b475-e043bc1e9a66 | note | ○ 2000 mg/L max
6ff2960e-92aa-5575-82c3-31a1bae9bdf0 | note | Frequency - 1 / 6 months
3e83e77d-558a-5fce-9cdd-e45f9d8b1d91 | note | Initiated by - AOM
532b1225-d4fc-552e-8795-9f6621ee3a42 | note | Approved by - Tech Mgr
3990ee8c-dcce-5241-8e4b-48d16c466f91 | note | Verification / witness: Supplier -
2f2f7e12-6fd9-5b8a-9634-cf7b3d134657 | note | Verification / witness: HOL - W
947d78a7-ed4d-59dd-8ed0-bd752821a278 | note | Verification / witness: Company -
d367d6c3-7163-54d5-965b-5988967773fb | note | Verifying document - Lab report
89084002-7431-5b60-aeec-ae7f705223e2 | note | Record Location - Tech Mgr office
9b7da4ba-77a8-5ace-8e25-0425c8bf4f62 | date | Date Completed:
bee1cb3c-fbd4-4d98-bcdd-ffb71d631ce8 | section | 6) Admixtures
8e866bae-dbdb-4482-9bfe-fe14d9341d43 | checkpoint | 6.1 - WR Admixture general acceptance
32ef3038-b2c1-578a-b2c8-6694085d868a | note | Code / Spec Ref - AS1379.2.5
e017325c-d848-56be-b333-61bc6d70f0b8 | note | Test / inspection method - AS1478.2
27d4abdf-a1c4-514a-82ac-a06df84e52ea | note | Acceptance Criteria - AS1478.1 Table 2.1
548e1033-e7f8-5bbc-9441-4c40e02b4eb4 | note | Frequency - Initial
d8b661cd-9100-5050-82e3-69cd69a929f2 | note | Initiated by - Tech Mgr
5fecc664-07bb-578f-9bb1-00249a8a8bf0 | note | Approved by - Tech Mgr
53d4bfbd-a9a8-53e2-8ad3-e0725986c153 | note | Verification / witness: Supplier - W, R
9cc5e599-54af-5c7c-b721-f436b15681df | note | Verification / witness: HOL - W
7cdfa390-80cd-5b82-9cff-e7fe73e6c7e6 | note | Verification / witness: Company -
fde02f4d-a38b-5603-9fb7-2b2b54215e6c | note | Verifying document - Supplier report
776cb84a-69fb-51fe-ab89-556b762b5b3f | note | Record Location - Tech Mgr office
4c92f3e5-b31e-5d63-9ffb-1ca5e021d092 | date | Date Completed:
c17536c6-7ad8-4161-a7dd-29cfe776155c | checkpoint | 6.2 - WR Admixture Uniformity test
2c96429b-7f7e-5f06-a32b-0ca65a94f24a | note | Code / Spec Ref - AS1379.2.5
2c33913d-50e1-5756-bf33-6edb9c8ed1b2 | note | Test / inspection method - AS1478.2
13ab7c5b-6508-572e-9cca-329274694d39 | note | Acceptance Criteria - AS1478 Cl 2.1.3 [Supplier specs for pH (+/- 1), Relative density (+/- 0.02), Non-volitle content (+/- 2%)]
fec106eb-ec39-5813-b403-ea3e51a1af50 | note | Frequency - MBCC Supplied (Each Batch)
ac27d7f1-b1ba-53bd-9193-c9d0fd57aac4 | note | Initiated by - Supplier
e4ea178a-8e9b-5569-92ee-c234b6aea117 | note | Approved by - Tech Mgr
a5eae0a1-642f-5aa2-a3b4-4721cfe67ba8 | note | Verification / witness: Supplier - W, R
7c61e25b-4b9e-5de4-8a9d-053dfbe310d5 | note | Verification / witness: HOL - W
f634618f-5e9c-5b35-87e2-1548c067c3fd | note | Verification / witness: Company -
6b310bec-dd12-5009-989c-a1adcca405d4 | note | Verifying document - Test Reports
c3b2942c-9a41-54fc-ad52-bbac9ad78fa5 | note | Record Location - Plant
13d3f9b3-5b4a-538d-81e8-40d63d377249 | date | Date Completed:
3677ac7b-a4ca-479c-b299-e4ed16fdf049 | checkpoint | 6.3 - AEA Admixture general acceptance
fbce964f-1cfd-5107-8bc8-8fdefbc6d69a | note | Code / Spec Ref - AS1379.2.5
d56e860a-5276-501a-8505-adea39917cdf | note | Test / inspection method - AS1478.2
410ea710-5bea-509f-aa4f-c68f36291e2b | note | Acceptance Criteria - AS1478.1 Table 2.1
0784fea4-6565-582a-b9da-73354ba0f81d | note | Frequency - Initial
0c1e90ea-0f71-5e19-bafb-4c38e2ea49fe | note | Initiated by - Tech Mgr
6a5784e4-0abc-5ea3-9419-610d3dd4931d | note | Approved by - Tech Mgr
7f52bebd-ac54-5711-8e2f-3cd3b6a309a6 | note | Verification / witness: Supplier - W, R
45eb6dde-dea7-5cb6-a70f-6edb25a963d3 | note | Verification / witness: HOL - W
154437f7-f37f-5ff2-905d-db3aa8b8a7bd | note | Verification / witness: Company -
17ab35b9-9666-59b1-ab2d-34d5580b9ae1 | note | Verifying document - Supplier report
7a2898a4-837a-53e2-aa5a-a2daa226db39 | note | Record Location - Tech Mgr office
0dfa31e7-6d19-541b-a653-1b5cfbf20d8c | date | Date Completed:
68ea1408-52cd-41a9-8f92-700b5f1177e9 | checkpoint | 6.4 - AEA Admixture Uniformity test
768545db-b25e-54df-99ec-1ba4c59149d4 | note | Code / Spec Ref - AS1379.2.5
1d859487-c514-5ba8-a84a-188ebdc00426 | note | Test / inspection method - AS1478.2
01944d28-b580-5795-90d3-ea8b4ce4e9f5 | note | Acceptance Criteria - AS1478 Cl 2.2.3 [Supplier specs for pH (+/- 1), Relative density (+/- 0.01), Non-volitle content (+/- 1%)]
e38cfe13-3b6f-5153-b648-fe59e662ae48 | note | Frequency - MBCC Supplied (Each Batch)
149c03b5-05d3-5ad4-986a-183e16824b5e | note | Initiated by - Supplier
e13aec75-a0c6-52c6-a861-33f12da6b6ad | note | Approved by - Tech Mgr
a2432470-f9ef-5b01-b1ac-2876cc12d7b4 | note | Verification / witness: Supplier - W, R
44155c7c-1adf-53b7-9f61-0ca66cfe69cf | note | Verification / witness: HOL - W
fa80b449-a508-5c99-8067-340238a4138b | note | Verification / witness: Company -
44612794-0a2d-5c7c-9d77-98544694ecd7 | note | Verifying document - Test Reports
821ce458-c0de-5a9b-8070-5f367babf404 | note | Record Location - Plant
a7eac26a-2e36-52a8-9a0e-a2e0c5da0da3 | date | Date Completed:
7885c182-92fa-4d9c-8284-ca8dc0aea61d | section | 7) Transport
2025ed9a-440c-45ac-959c-3b46641c5fb4 | checkpoint | 7.1 - Agitator blade inspection
0154cb5f-044e-5adb-8d26-2b17f9b3f064 | note | Code / Spec Ref - HOL QMS PN6.1
4c66916e-4dd6-5472-8225-7ed70b32fb26 | note | Acceptance Criteria - Concrete Barrel Solution - No excess buildup, No excess wear
f8cb1f7b-f014-5eca-ab14-35ad04c8781a | note | Frequency - 1 / 3 months
0bd6d022-3a40-5cf1-a4fd-c74222c60ae9 | note | Initiated by - PS
578c5f96-41de-594b-874c-6c933302d006 | note | Approved by - AOM
8f372499-cd98-5674-a730-0049322f439d | note | Verification / witness: Supplier -
965221ca-0b26-514b-b825-5a08ec59a134 | note | Verification / witness: HOL - W
60a21f04-3371-5fae-b9ed-94dd11c67075 | note | Verification / witness: Company -
07058526-ae29-5d1d-8e1b-66d4dc1990fe | note | Verifying document - Inspection report
33d32fd8-2585-58e6-a97f-b78c6d2aeedc | note | Record Location - Plant
72829e5f-45f0-54a3-b932-05d8b1ed1fb6 | date | Date Completed:
eba9820f-0ec4-4fa6-9f86-0a4c24f21205 | checkpoint | 7.2 - Mixer uniformity test
11b82338-3d53-50b7-8033-497387529f5b | note | Code / Spec Ref - AS1379 3.5.1 (a)
e2364057-d541-54b0-9eee-afc4da035004 | note | Test / inspection method - AS1012
00d60fda-a8cd-5adb-8215-0de259032427 | note | Acceptance Criteria - AS1379 Appendix A Table A1
9e532a9a-337d-50e9-9a24-93c9729cb56e | note | Frequency - Initial for agi type
807626fe-ed64-52e8-9892-9637d88c262a | note | Initiated by - Trans
19c89b18-5b56-5bb3-b40e-ecfbcdc29f6c | note | Approved by - Tech Mgr
75b2fc1e-4532-5976-97b0-57af251ababd | note | Verification / witness: Supplier -
be6a21f8-3a5a-5cfe-9992-b45f3ce95497 | note | Verification / witness: HOL - W
2447e2f5-5480-53b9-8dde-bbfbee0193e6 | note | Verification / witness: Company -
c9f02420-9128-5266-9f24-660b3693d41b | note | Verifying document - Manufacturer report HOL test report
bc113c25-9c7a-56e7-b459-716193e1c06b | note | Record Location - Tech Mgr office
96027749-61bb-568d-bc85-cdd4478538b5 | date | Date Completed:
87901550-6417-4b8e-8442-3b1539f23c56 | checkpoint | Final Inspection
6991fea1-3028-55b4-9395-ecb1e4d1da0d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
20dfdf9b-e685-541b-9396-f33c964fd08c | textbox | Print Name:
e3cff430-b5a2-5528-82ca-020210bae7b9 | textbox | Position:
ef54da13-444d-52b8-8e14-4f34e0a2a092 | date | Work Completed On:
20576092-0f9b-5cec-87f2-cbce8fdc3611 | date | Date:
29c3eab3-bbc3-481e-89be-7eb15b1611ae | checklist | FH-ZU2-QU-ITP013 - PCC Pavements - Rev 3 | itp | ITP013 - PCC Pavements
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
2907e598-3fa6-573d-bd16-0574524c85dd | note | Frequency - Prior to commencing works
b9918449-71ab-57a3-8fb9-16b7aa22b72c | note | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
e00f65c1-9d2f-5be2-a812-fb0d735c5f0c | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
fcc655b9-fbb7-56a9-a250-a3e6ddfcdac9 | note | Reference Documents - Current Revisions in Aconex or ACC
7c8e2404-1102-5ee8-a17e-bf5965da5090 | note | Inspection/Test Method - Verify
bbf512ae-8c96-50fe-ab8e-041fb46b2033 | note | Record of conformity - This ITP signed
50155e9b-2035-554f-a3b9-dc1292319b1d | note | HP*
c857cb14-757e-552e-a08f-8d2f33488cba | note | Responsibility - Project / Site Engineer
7985f0ba-6f2a-53e3-86b8-8d2bb4b8fa9e | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
f76991b4-2e34-58da-a5a7-07c02f17fe3d | note | Frequency - Prior to commencing works
c651df4c-8e29-5d2d-9375-da49ffe74cdf | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
48b636c8-8a77-5c74-8d2b-2a67f6f57838 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
396ec348-d33a-5b4c-8f22-e1c5c2acb765 | note | Inspection/Test Method - Visual Inspection
7cf37097-e48c-53c0-8bbf-4d645002a09d | note | Record of conformity - This ITP signed
811f2fa4-250a-5ede-9e06-77ba08912d60 | note | HP*
3d378ac4-0b26-56cd-9c2f-4fba1d62a6ed | note | Responsibility - Project / Site Engineer
91cced02-0c77-52ba-9865-19bd3dc69329 | date | Date Completed:
7e28438e-f51f-55d2-9f71-e8c9c5437afc | checkpoint-no-value | 1.3 - Mix Design Report Submission and Approval
4507ccca-25f6-5ce8-996e-f117534195a8 | note | Frequency - Prior to commencing works
5b39bd65-bb88-5915-86f4-2d1b0165bfb7 | note | Acceptance Criteria - Theoretical mix design and preliminary trial mix results submitted in a report to the Contract Administrator for review and acceptance prior to full trial mixing.
98bbfa8e-9bff-5a20-994c-001991a18233 | note | Reference Documents - Beca Spec 002 - 11.5.3
85cbfe58-d6b7-5804-b260-f5c730fa1f47 | note | Inspection/Test Method - Verify
a862afaa-1ec6-58ad-b24c-6eacb2fca986 | note | Record of conformity - Aconex Reference
cb6a07a3-cb1d-5b7a-a016-a5b1ac8a4d5b | note | HP
ab6e881a-aab1-5c9a-9521-b29a5139afc2 | note | Responsibility - Project / Site Engineer, Principal’s Representative
2d313683-5885-50c2-9eb2-66762b61c470 | note | Date Completed: 01/06/2024
3211cacc-9c39-5b9a-9514-0f07b88fe014 | note | Principal's Representative - 40mm mix (VF509BW45):
84f2c6ec-2285-5279-86ba-6375805fd62e | note | ○ BecaCPL-GCOR-000846
8a2b4f38-e070-563f-89e6-2652276dfa46 | note | ○ 01/06/2024
af758d18-438a-568b-aca3-c11da299b6ba | note | 20mm mix (VF502BW45):
9caaade9-c98b-55ae-9c22-254acf3da8f5 | note | ○ BecaCPL-GCOR-001287
a0a6fe69-cc88-597f-8f4a-419d9b363215 | note | ○ 08/11/2024
1d417a20-1781-524c-8f26-32728ee4d344 | checkpoint-no-value | 1.4 - Job Mix Formula
8b89fdfc-d9d1-527e-8a5a-973029e07bae | note | Frequency - Prior to commencing works
7614f9ac-8801-59ee-a747-c145e86ec76c | note | Acceptance Criteria - The Job Mix Formula must state the mass proportion of all ingredients per cubic metre of concrete. The allowable limits in the Job Mix Formula (when compared to the agreed theoretical concrete mix design) must be in accordance with Table 11-2 of BECA 11.5.4 (see notes section).
57149b72-6f59-5d04-86e7-4525b9b35b55 | note | Reference Documents - Beca Spec 002 - 11.5.4
b51a7841-f170-5d47-8f36-c8cd85564a64 | note | Inspection/Test Method - Verify
503bc281-5ed7-58d1-aa06-fb549f758ad5 | note | Record of conformity - Aconex Reference
93011ee0-68cc-5e96-bafe-17d75aa2198c | note | WP
5375edff-176c-5d66-988f-1c14a5004c0b | note | Responsibility - Project / Site Engineer, Principal’s Representative
71a389be-f505-5ac1-9f06-a680d8c8848e | note | Date Completed: 30/05/2024
e0d8cbf6-790b-5a21-8182-cc284a5187fa | note | Principal's Representative - 40mm mix (VF509BW45):
f1cb4aba-994b-58ad-97ca-6a9734093c24 | note | ○ BecaCPL-GCOR-000839
64bc81cf-2010-53ee-9cd6-4f7bfaf5e6c1 | note | ○ 30/05/2024
fd5fdb17-cd07-5841-8914-7830b146f80e | note | 20mm mix (VF502BW45):
fc4d967a-9522-5257-b009-dcc6e570b1c7 | note | ○ BecaCPL-GCOR-001287
28165a08-3a4a-56d9-986e-bd752ae5c4dc | note | ○ 08/11/2024
ea2ed3cc-4240-5302-a62f-08cf18713d1a | checkpoint-no-value | 1.5 - Production and Construction Trials
e5fdbc46-719d-5942-8304-c39bd3e2059a | note | Frequency - Prior to commencing works
19475a37-83f9-5590-bea2-9dc4e0ea4477 | note | Acceptance Criteria - A production and construction trial must be completed as per the requirements in the specification.
1b130452-3c22-5b57-96d2-d425c83968d6 | note | ○ The results, control procedures, construction methods and completed trial pavement will be presented for review and approval by the Contract Administrator.
468ed8d3-72e9-5e5e-9e7c-4cd84000cb62 | note | Reference Documents - Beca Spec 002 - 11.6.1 to 11.6.4
4077b7bd-82bc-5ac9-8abf-482efd9b2c4b | note | Inspection/Test Method - Verify
df708af5-9f11-534c-af7d-32a465b86af9 | note | Record of conformity - Aconex Reference
528f6782-a3f3-5bce-bf62-414e8a0aa3b5 | note | HP
08bcb58d-ea03-5f6c-8d87-068ee9a666c4 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a044b821-045c-516d-806b-4adbf19eae93 | note | Date Completed: 19/08/2024
3f498654-9c27-5215-b0b9-26044de9c986 | note | Principal’s Representative: 40mm mix (VF509BW45):
81643bfe-3698-5b80-9071-a5f82bcec8cc | note | ○ DCWC Mgt-GCOR-009917
1fb47955-bcee-5abb-b197-b9499f180dd0 | note | ○ 19/08/2024
45488478-feca-58bd-a9a9-54b4cdbdcd50 | note | 20mm mix (VF502BW45):
215f77b1-87a4-5e94-843b-8dc75692be21 | note | ○ BecaCPL-GCOR-001287
e06a0fb4-fcd4-5e41-9d70-c55a7166d782 | note | ○ 08/11/2024
e5f4e390-d859-5bb8-8754-88a6610c4a41 | checkpoint | 1.6 - Curing Compound Material Submission
9b855dfe-dcaf-5780-a60c-3107674b9ed2 | note | Frequency - Prior to use of curing compound
83186ab9-3183-5a0d-8af9-d95cee37cc97 | note | Acceptance Criteria - Membrane curing compounds shall be a white pigmented type confirming to AS 3799, Type 2. Wax based compounds shall not be used.
f420a157-3565-5505-8230-a10228b203ee | note | ○ No compound shall be used without written approval by the Contract Administrator.
25cd7b38-ee48-596d-b07d-17fa9f379210 | note | Reference Documents - Beca Spec 002 - 11.4.11.1
60e9e8c5-b8ed-5bd9-a26e-3382693460cc | note | Inspection/Test Method - Verify
c0fd41e0-1e99-5cb1-b48f-4c618b1231d9 | note | Record of conformity - Aconex Reference
725ec045-95ca-572c-9b4e-9c371e3ec53f | note | HP
f35c5635-fb93-5f33-b60d-c63641ec0278 | note | Responsibility - Project / Site Engineer, Principal’s Representative
696d3ed0-b889-5758-aec5-19902ec4d780 | note | Date Completed: 22/05/2024
a818c49e-eaec-5a25-8530-c20a4d5b18bd | note | Principal's Representative - BecaCPL-GCOR-000791
ba929a80-28cc-56d4-987f-a6898a2999b4 | checkpoint | 1.7 - Impermeable Blanket Material Submission
761302c5-7075-519c-9d7b-694b9d82823c | note | Frequency - Prior to use of impermeable blanket
b5091c95-16c2-5ef1-a417-df9805b7c0ab | note | Acceptance Criteria - If required to be used, impermeable blankets shall comply with the requirements of ASTM C.171.
db67cc05-0893-5f00-99ff-d92e8f8fca9b | note | ○ The blankets shall have sufficient strength and weight to meet the required conditions of service and shall be approved by the Contract Administrator before use.
46bd5aaf-a712-5584-9956-c7ddf7e3671b | note | Reference Documents - Beca Spec 002 - 11.4.11.2
40d7a594-43f0-57e3-8f8e-430fd5f4061f | note | Inspection/Test Method - Verify
6af78c57-3fbc-5181-a1c9-23ad09bdf0ba | note | Record of conformity - Aconex Reference
bb338aed-f7e8-569f-995d-e97baa3ee2b6 | note | HP
4768e536-db22-57da-8f25-3e8dfeda92eb | note | Responsibility - Project / Site Engineer, Principal’s Representative
fdd17bfc-d0c1-55b5-88b6-5f825b05769a | date | Date Completed:
5885abc0-a77e-5d54-803d-3fd1515e6818 | section | 2.0 - Pre-Placement Activities
16ee8263-a125-5876-ab26-79db8c104fdd | checkpoint | 2.1 - Formwork Installation & Pre-pour Inspection
65a8de96-f184-5a0b-af0f-2fd24a991fb5 | note | Frequency - Prior to placing concrete
1f1a7b28-fea3-5aa9-b6c2-a714d1d257f5 | note | Acceptance Criteria - Formwork must rest firmly on the base to eliminate gaps and ensure no leakage of concrete will occur during placement.
a5ca7930-6074-5fd1-9a44-03273fc974f8 | note | ○ Formwork must be secured into position and locked together during placing, spreading and finishing of the concrete.
1e88b2e3-5eaf-5da0-8afd-bc24150e6b21 | note | ○ The top of the form must not deviate by more than 3mm from the required level.
2f868783-cb5a-598f-8cfa-65f1caec0add | note | ○ The form face shall be vertical and not vary more than 6mm from the required alignment.
259c41d0-ea10-543b-a179-74feefe07e9c | note | ○ The area in which concrete is proposed to be placed shall be inspected and checked immediately prior to commencement of placing.
31c77cba-682b-53dc-87ae-5baea14f37a7 | note | Reference Documents - Beca Spec 002 - 11.8.1.1, 11.9.1
6ef34b37-ea17-5ff3-ae4b-e99491dfaaaf | note | Inspection/Test Method - Visual inspection
a9ebca94-422a-50d0-83cf-12869d540e0b | note | Record of conformity - This ITP signed
f249917f-23af-5d15-86c4-a29b6426d2d9 | note | WP
5b8afdc5-c63f-53f0-a861-23a7b328949e | note | Responsibility - Project / Site Engineer, Principal’s Representative
7409513b-e0b7-52ca-8954-8936dd8759d3 | date | Date Completed:
fd1f1b65-94f0-536d-a050-a134453028a2 | checkpoint | 2.2 - Pre-pour checklist
ab32c07d-9a9d-53ce-b9b5-123154b34553 | note | Frequency - Prior to placing concrete
18c8a68c-2470-5f7a-a086-63658f6c6540 | note | Acceptance Criteria - Completion of the pre-pour checklist: CL013A – Pre-Pour Checklist which details various checks required for formwork, reinforcement, joints and the pour area.
b28cd113-7abb-5137-9cf8-2b694ff03494 | note | Reference Documents - Beca Spec 002 - 11.8, 11.10, 11.13
be572c26-123b-5025-998f-2abc96f9640b | note | Inspection/Test Method - Visual inspection
d984894d-908e-5b6f-ad12-8ad9faed8fba | note | Record of conformity - CL013A, This ITP signed
d8b6310c-914c-575c-865b-9033ff0b5181 | note | HP*
7a14446c-e20a-5723-ad87-0f7c48d3e202 | note | Responsibility - Project / Site Engineer
ae723b76-57c3-5197-94af-ab6ad7d4b3a6 | date | Date Completed:
d9388486-1250-5ff8-b9ad-8d44105f357b | checkpoint | 2.3 - Weather Forecast Checks
d43c1ab9-5201-5007-b19e-cb14e0ad0be0 | note | Frequency - Prior to placing concrete
0a8b717f-0ec7-5292-8236-466654675c31 | note | Acceptance Criteria - Check the weather forecast for unfavourable conditions (rain, wind, hot weather or cold weather) on the day prior and immediately before confirming
ed0bef5e-c778-5d14-9786-2791f8899413 | note | Reference Documents - Beca Spec 002 - 11.9.5.1
c980c01d-b749-5c67-a48b-015656e8fe01 | note | Inspection/Test Method - Verify
5740e4c3-89c1-5bdd-a073-809a08fe31b8 | note | Record of conformity - This ITP signed
a2371590-dbcb-552a-9f00-aa021e745a5c | note | HP*
20538a2e-8184-5d34-a5e7-dbca391524b0 | note | Responsibility - Project / Site Engineer
10ba42c8-0df4-561f-89da-75552b10f2ca | date | Date Completed:
cd1921f5-0447-55dd-a906-346b6c56d7e0 | section | 3.0 - Placing Concrete
4ce1dbde-921b-5f12-92f2-cb172108eb2c | checkpoint | 3.1 - Place, Spread and Compact Concrete
7665b879-a2be-524d-ac3e-ecf0582e021e | note | Frequency - Each concrete pour
723f9130-2ba8-5f32-8090-706d2a025af7 | note | Acceptance Criteria - Concrete placement must be at a rate appropriate to achieve a consistent high quality resulting pavement.
80257cee-5638-514e-a8ff-24d1c99ba788 | note | ○ During placing, the concrete must not drop freely by more than one metre onto the base of the paving lane.
ede5d52d-6d18-5925-a3b4-ed8eb0fbe3a1 | note | ○ Concrete shall be placed uniformly over the width of the slab and in a way to minimise segregation.
fb7bb21a-0517-5585-8cba-f749e3db01cb | note | ○ Concrete to be adequately compacted by internal mechanical vibration.
47ad46e2-d1bd-59d1-992d-bbe52b4d9cbd | note | Reference Documents - Beca Spec 002 - 11.9.1, 11.9.4, 11.11.2.1
638de61b-8375-576b-9262-504c09b1a131 | note | Inspection/Test Method - Visual inspection
39a74bcb-e849-515c-9206-afe7bbf2cd12 | note | Record of conformity - This ITP signed
73d72013-09b1-5d43-9fe7-bab4cde0554c | note | IP
bc0e21bc-775d-5d51-b0cb-529089e2bd84 | note | Responsibility - Project / Site Engineer
4fad147d-594c-5d20-96cf-f52b3f9b9d35 | date | Date Completed:
01340969-6666-50d8-81f7-9de3ba0476a1 | checkpoint | 3.2 - Concrete Deliveries
8246b40e-a538-5ae2-a7e5-ff27722c2f97 | note | Frequency - Each concrete pour
ff9bb630-b1de-5601-afdb-7766627168d9 | note | Acceptance Criteria - Each concrete delivery to site is to be recorded on CL013B – Concrete Pour Record Sheet.
c719bd61-97e4-5c4c-84ed-af3fe5c02149 | note | ○ Concrete shall be placed within 90 minutes from the time of batching and before the concrete has attained its initial set.
fb71dde1-c897-5894-867b-60edb818ef6e | note | ○ The pour location, direction and order to be recorded on CL013C – Load-Batch Traceability.
04107314-7b34-53c4-8165-e6655e2e25de | note | Reference Documents - Beca Spec 002 - 11.9.1
1ad59df4-04e9-5aaa-acc6-fcecf0a20d1e | note | Inspection/Test Method - Verify
3945ca57-c77b-5137-bdc3-c380e553e0df | note | Record of conformity - CL013B CL013C, This ITP signed
b03e5d32-467f-5422-9751-5cd135c27c28 | note | IP
45e148b9-6d9b-5f88-a000-ad7e6419a0c2 | note | Responsibility - Project / Site Engineer
ba507cfd-70e3-534c-bfd9-36d529c0cfe7 | date | Date Completed:
a8846c82-3dab-5b97-8463-d576a7c411cc | checkpoint | 3.3 - Evaporation Rate
620b32c5-666d-5ac5-9d40-c190badf7dab | note | Frequency - Each concrete pour
65d8d07b-bb3e-5b85-89c1-9dcc1f61a1be | note | Acceptance Criteria - Concrete must not be when the evaporation rate from the surface of unprotected concrete is in excess of one (1) kg/m²/hr.
5245a27c-ae3a-572e-82a2-c0a5168e075d | note | ○ When the evaporation rate exceeds 0.6 kg/m²/hr, precautionary measures to prevent plastic shrinkage shall be taken.
1f0914c8-b9e4-5490-8cb3-4394352605b4 | note | ○ Evaporation rate to be recorded on CL013D – Rate of Evaporation.
a658725f-486e-574f-83ff-b8cc2eb40700 | note | Reference Documents - Beca Spec 002 - 11.9.5.2
1f4e2277-f1ef-5141-bc8f-dd05fc26f7a0 | note | Inspection/Test Method - Verify
f76b01c6-bd98-5ff3-9e87-82bc36a34708 | note | Record of conformity - CL013D, This ITP signed
3e4d1077-a8f0-5a0f-9fa6-30268bc119ef | note | IP
acaccec8-ef2c-51a4-a20c-aef89753f903 | note | Responsibility - Project / Site Engineer
cb08b5a5-0abd-51b0-8c20-fdbdb49bb359 | date | Date Completed:
6bde1751-12a1-5704-bd61-b45ba632ac70 | checkpoint | 3.4 - Hot Weather Concreting
744e946e-f126-5621-9e7e-a4972f3ef9ba | note | Frequency - Each concrete pour
a1e7bd7d-1f73-5185-bd3f-77e0967bec30 | note | Acceptance Criteria - Undertake additional precautions when placing concrete in hot weather.
7d9e13d6-291a-5804-8258-3aaced05a93f | note | ○ Ensure the concrete is placed at the coolest temperature practicable – the concrete temperature should not exceed 32°C.
78f48efa-0ae5-5dc1-8f31-3313b3109889 | note | Reference Documents - Beca Spec 002 - 11.9.5.3
d831f3f8-c332-5686-bda4-38c911c66549 | note | Inspection/Test Method - Verify
10d0b85b-3d61-5194-8f9d-e39d2c381564 | note | Record of conformity - CL013B, This ITP signed
4807115e-733f-50c1-b298-52829bceea88 | note | IP
37c77533-2901-5453-b540-56df0c72adc4 | note | Responsibility - Project / Site Engineer
60155a52-54ab-55ff-9c03-8d923452d239 | date | Date Completed:
0a674bc7-9c0b-59d4-b89b-165fe5156d0a | checkpoint | 3.5 - Cold Weather Concreting
b46d4377-743b-5e2c-9a62-72656b686c51 | note | Frequency - Each concrete pour during ‘cold weather concreting’ conditions
7fe02ad8-3085-5f3a-ad2a-0d86841ffc75 | note | Acceptance Criteria - Cold weather concreting applies when placing concrete when the temperature of the air, aggregates or water is below 10°C.
d01a9e14-2976-5bf7-af7e-f001c89aa7a4 | note | ○ Placement of concrete can only proceed if the ground temperature at the concreting site is greater than 5°C and the temperature of the concrete is not below 10°C.
14bec05b-75b6-5cbd-8313-7107a72b00fb | note | ○ Refer to checklist CL013E – Cold Weather Concreting for ground temperature records.
2c83eea4-ede8-58de-8a96-8fdc2ca50a2d | note | Reference Documents - Beca Spec 002 - 11.9.5.4
5400d6da-e277-5552-934d-295719475b4a | note | Inspection/Test Method - Verify
0cf4e0f5-f7b0-591c-a4bc-a74cc1925e3f | note | Record of conformity - CL013B CL013E, This ITP signed
f7ee5f93-57e9-570b-80b5-7e193fd5587f | note | IP
4121e0e9-6a3c-5dea-90e4-8dea93d0437c | note | Responsibility - Project / Site Engineer
16188178-5de4-56d5-bf57-fb2443ec071b | date | Date Completed:
bce17218-2b32-50e2-99bf-8851b7031e92 | checkpoint | 3.6 - Concrete Surface Finishing
b26ed40c-f7fe-5c69-a471-0ad5980c219a | note | Frequency - Each concrete pour
3dd3cb8a-4d02-5a4b-a302-32045875d4e6 | note | Acceptance Criteria - Finishing operations shall compose transverse finishing, longitudinal straight-edge finishing, floating and broom finishing, in that order.
53be0521-6bdd-50fc-b99c-5d2a91eb7f37 | note | ○ Finishing operations must be started immediately after compaction of the concrete and completed as soon as possible but not later than 90 minutes from the time of batching and prior to the concrete attaining its initial set.
2ba31877-3f8d-5551-bf43-08e177e81c36 | note | Reference Documents - Beca Spec 002 - 11.11.2.2
e09b32d0-416e-5346-9c9b-1220537934c9 | note | Inspection/Test Method - Visual Inspection
6e7e4584-a8b0-595f-a24d-de612f1127a2 | note | Record of conformity - This ITP signed
ad934164-50ae-59cb-98b2-675b58179b25 | note | IP
699e0910-0d47-5413-9c83-c52b19be34c6 | note | Responsibility - Project / Site Engineer
6abdad8c-dc11-55fd-8218-36822687b6ab | date | Date Completed:
d4da5116-30ab-56c9-b1eb-849f5003fc96 | section | 4.0 - Sampling and Testing Concrete
43ff8655-1595-5766-8438-ea3569c93eaf | checkpoint | 4.1 - Slump
e7dc755c-ff25-50ee-96af-ff0dab3dcd19 | note | Frequency - 1 test every 2 trucks
9fbac8e6-40ae-5a64-ae00-e85f95490dd9 | note | Acceptance Criteria - 60mm +/- 10mm
1e1c2738-c8ef-566d-b4ef-c0a06b1b95d1 | note | Reference Documents - Beca Spec 002 - 11.24.17, BecaCPL- GCOR- 000846
631b6b02-f4ee-54f6-aab2-f4606e4be2b8 | note | Inspection/Test Method - AS 1012.3.1
6e0d6122-3d83-517b-9fb4-9810dfb73c77 | note | Record of conformity - NATA Test Certificate
3799165a-793c-5f52-9e99-1bc8e66aa85d | note | TP
f33f7e7f-5c6b-5a6f-90b3-368d440763fa | note | Responsibility - Project / Site Engineer, Laboratory Technician
edc8ffe1-57f1-5325-886e-40e630995883 | date | Date Completed:
df8751f1-b783-5ced-bb43-a84f6efb9e3e | checkpoint | 4.2 - Temperature
0c42cd12-866c-585a-869b-e826adc3da04 | note | Frequency - 1 test every 2 trucks
92d7b2a7-237c-52b8-badd-e661cea05acb | note | Acceptance Criteria - Minimum 15°C (except in cold weather concreting where minimum is 10°C)
1ac66703-6f4b-5503-a481-2cd5bf33c432 | note | ○ Maximum 32°C
065863ac-e20e-5236-a611-2c120f585201 | note | Reference Documents - Beca Spec 002 - 11.24.16
867d37cd-753b-5c5e-baa0-37d9c5934684 | note | Inspection/Test Method - AS 1012.3.1
ecc7394e-9e35-58b5-b477-c08cd31a0447 | note | Record of conformity - NATA Test Certificate
be4204fb-85e0-5c77-a84d-bf595ef132ea | note | TP
0b169908-fbcd-530e-a69b-735905db5c2b | note | Responsibility - Project / Site Engineer, Laboratory Technician
dd04c20d-b5c7-5091-8993-9cb5aee071da | date | Date Completed:
2ffe1a6e-8b66-57f5-bbd8-0c2e46eccdea | checkpoint | 4.3 - Flexural Strength (7 day)
506d83af-a213-50cf-bd4c-086b494c9637 | note | Frequency - First 5 lots: 2 Beams per 75m3 or part thereof.
d1c99a14-cafa-596a-96d4-30a78dab4373 | note | ○ After 5 lots: 1 Beam per 75m3 or part thereof.
4a796ae1-7593-5083-acbc-16b5ce896c8d | note | Acceptance Criteria - Results for information only
f079ae4f-0da6-55dd-8f57-d175df0f1741 | note | Reference Documents - Beca Spec 002 - 11.24.10
6f6c0f31-b5d0-51b0-b720-0309c7e52034 | note | Inspection/Test Method - AS 1012.11
909c13bc-855e-5784-919c-3711ccbebb19 | note | Record of conformity - NATA Test Certificate
85fe830c-74ec-52ff-b129-4a3ed94a9760 | note | TP
0c8466ea-46f8-563c-980b-4ccf33c2a639 | note | Responsibility - Project / Site Engineer, Laboratory Technician
7d92ade6-8787-586c-a9f9-909bcaec1671 | date | Date Completed:
f5e85626-3e87-51d9-b123-8dbe71828123 | checkpoint | 4.4 - Flexural Strength (28 day)
68bc7023-086e-52c4-a527-072e730877c5 | note | Frequency - First 5 lots: 2 Beams per 75m3 or part thereof.
25a96de9-b8aa-5d12-9823-ba69d74ca852 | note | ○ After 5 lots: 2 Beams per 75m3 or part thereof.
dc2be2b2-4f0f-552f-8dcf-b7bab6ae9120 | note | Acceptance Criteria - Mean of the pair of beams > 5.0 MPa Individual beams > 4.8 MPa
6f64e51f-d32c-5c63-8e3a-7d51f1de2841 | note | Reference Documents - Beca Spec 002 - 11.24.10
34161891-b4e6-5856-a5cd-40d95a043493 | note | Inspection/Test Method - AS 1012.11
3af3ca24-1695-54ac-ae7f-fbc32c179aab | note | Record of conformity - NATA Test Certificate
0da54949-117b-58bf-b3cd-c3583c3829b3 | note | TP
a3663f3b-081d-58c3-91a7-c63a62d9874a | note | Responsibility - Project / Site Engineer, Laboratory Technician
7eddf880-425d-5c79-88c0-4b9f42dd923a | date | Date Completed:
9e886210-4b93-5748-a95e-ad183ab45c95 | checkpoint | 4.5 - Air Content
beb5fad9-719b-5f31-9ca2-bbe8fea2632b | note | Frequency - 1 test per Lot
cce2068d-7751-5d08-b115-9c85be983a61 | note | Acceptance Criteria - 3% - 5% ±1%
cce38939-39dd-5930-b456-e385fde10ce4 | note | Reference Documents - Beca Spec 002 - 11.24.8, 11.24.9
4f873026-9a91-58f9-bd7f-32975b9c9630 | note | Inspection/Test Method - AS 1012.4.1 or 1012.4.2
96ae24eb-2d77-5f28-89c2-4f1dc3ced80b | note | Record of conformity - NATA Test Certificate
f0e67256-3950-55e7-a7f5-ff9fb9edfb96 | note | TP
c7616360-f69d-5c7a-a9a4-e385f182e23f | note | Responsibility - Project / Site Engineer, Laboratory Technician
eed76a32-8847-5b9f-bcd9-7ac60e6b2939 | date | Date Completed:
9ad6888c-fa3b-5efb-b8a6-dea67ddcb735 | checkpoint | 4.6 - Mass Per Unit Volume
249ca4b9-5f12-5647-bd16-61bb71132964 | note | Frequency - 1 test per Lot
914a1061-d7db-5862-80b3-2dc51c3bbd66 | note | Acceptance Criteria - Results for information only
d61bce60-4427-5438-a778-ac44dd2b9ac6 | note | Reference Documents - Beca Spec 002 - 11.24.9
56516493-bebe-5e10-94d5-968d50da156a | note | Inspection/Test Method - AS 1012.5
89fec65b-8936-51e1-b966-5a9bc9bb695e | note | Record of conformity - NATA Test Certificate
cea769a3-8529-5654-8e6d-9695b25c878c | note | TP
813e7f85-510e-53fa-b17a-6671485216dc | note | Responsibility - Project / Site Engineer, Laboratory Technician
7655c7ad-d1c4-5ddf-a170-5835f574c71f | date | Date Completed:
784088d9-4c0a-591a-bcd5-f66d2ffb7819 | checkpoint | 4.7 - Wet Analysis
343a3167-cf90-59c7-bf56-10568edf0ef9 | note | Frequency - 1 test per Lot
ed0a84e9-18b8-512b-89eb-0fa090f32c09 | note | Acceptance Criteria - Results for information only
a23c85d7-48fb-5dca-accc-8001ad078bf1 | note | Reference Documents - Beca Spec 002 - 11.24.9
b0493a50-ceb7-5173-b70b-785e23524ab0 | note | Inspection/Test Method - AS 1289.3.6.1
715add53-bd8f-5fd2-a2b2-69d474fbef00 | note | Record of conformity - NATA Test Certificate
79d6b9e1-35e3-5868-a636-e5b774e97e92 | note | TP
d74d9e31-040b-53aa-8098-f3eafa8096f7 | note | Responsibility - Project / Site Engineer, Laboratory Technician
c49d4dd6-001e-5b3d-acf4-c27d4f3d7767 | date | Date Completed:
21046b26-0f7a-50ea-a8d4-20fcdb40c85b | checkpoint | 4.8 - Concrete Core Analysis (Density & Compressive Strength)
44ef0abf-113d-5a24-b205-4a368131b77d | note | Frequency - First 10 lots: 6 cores per Lot
8dda6e55-4e3f-5481-a80c-36712dd44c50 | note | ○ After 10 lots: 1 core per 75m3 or part thereof
f698075e-11c4-5bff-b6a4-f3df2e4eb701 | note | Acceptance Criteria - Cores must be not less than 120mm diameter.
f121d421-0622-5526-b970-29ddf62c3769 | note | ○ Calculate the degree of compaction by comparing the density of individual cores with the average density of flexural test beams (exclude beams whose density is less than 97.5% of maximum theoretical density). Refer to notes section for acceptance requirements.
93ff3a2a-1e34-5537-a2c0-92305264f999 | note | ○ If a lot requires 3 or more cores, one third of the cores taken shall not be tested for density but shall be tested for compressive strength and results submitted for information purposes only.
0295f8e9-35c9-5910-a337-ecbe4ad45c22 | note | ○ Refer Aconex: DCWC Mgt-RTRFI-001244
8998f956-5b2b-5eba-abc6-3cc8f555afbd | note | Reference Documents - Beca Spec 002 - 11.24.12
81946f43-f32b-5770-847b-fca603623b71 | note | Inspection/Test Method - AS 1012.12, AS 1012.9
c579b5f9-7653-5159-950f-b218a132b5a9 | note | Record of conformity - NATA Test Certificate
d065c9e2-e7de-5724-81b2-3ff5c52b422c | note | TP
9d2eceff-0e85-554e-8aa1-6229bdbf671a | note | Responsibility - Project / Site Engineer, Laboratory Technician
59c3b69c-68da-5505-8ce0-3f8a9ece2c03 | date | Date Completed:
782b8ec4-e2e7-589a-bdec-0fe6bc056628 | section | 5.0 - Post-Placement
cf47b8f0-f88a-54c2-b407-91f44e2a654f | checkpoint | 5.1 - Curing
d935de30-5a7e-5f55-8a4c-05bb1a5194a1 | note | Frequency - Each concrete pour
0b1553ac-4ec0-5a8e-8d8f-f4260aefd946 | note | Acceptance Criteria - Concrete shall be cured by protection against loss of moisture and rapid temperature changes for a period of not less than seven (7) days from completion of the finishing operations.
40e0f672-c0b1-5de3-939a-86d62221b715 | note | ○ Curing of the concrete shall comprise an initial mist curing followed as soon as possible with continuous wet curing with hessian matting for the duration of curing period.
a2c4a646-91dd-5a03-97cb-f09b867f8363 | note | Reference Documents - Beca Spec 002 - 11.12.4
8441d7a4-4ca1-5d1d-b5a9-8246823633f8 | note | Inspection/Test Method - Visual Inspection
5ecbc6a7-bdf6-5d88-b7fb-dfe592caf6cd | note | Record of conformity - This ITP signed
da2577af-fbbe-5cc3-836f-f2db59d57582 | note | IP
d887255a-6945-5b74-8988-38edbf9405af | note | Responsibility - Project / Site Engineer
586a76b4-cd49-5ad5-9eb3-335564e3ab27 | date | Date Completed:
aa609089-ea6f-521a-b2a7-7cd41a2d5d49 | checkpoint | 5.2 - Cold Weather Concreting Concrete Protection
b72a3ea0-9cf3-54a7-beec-14b61b7a485d | note | Frequency - Each concrete pour during ‘cold weather concreting’ conditions
bf428b0e-8c96-580d-9b28-a5f2c3a1450c | note | Acceptance Criteria - The surface of the concrete must be maintained at a temperature of at least 10°C, for not less than 72 hours after placing and at a surface temperature above freezing (0°C) for the remainder of the curing period.
f9469610-5e96-5a78-922e-b7dee55d8e29 | note | ○ Concrete surface temperatures post-pour to be recorded on checklist CL013E – Cold Weather Concreting.
a429a458-d908-5b2c-ac3a-8f1ba931df5e | note | Reference Documents - Beca Spec 002 - 11.9.5.4
4f84e7fa-b264-5dfe-bca2-9a95248c0896 | note | Inspection/Test Method - Verify
410a28c0-f2e4-5be6-9d42-669ddbe29548 | note | Record of conformity - CL013E
71518393-0ca3-58de-b30c-7e807bd704e0 | note | IP
148e7960-cfe8-5c7b-a158-389cc3f3c208 | note | Responsibility - Project / Site Engineer
bc31c826-5b56-59c5-9460-f2f09b4366fc | date | Date Completed:
82b7f08a-ab9e-5a58-be5c-738ceda7b9f1 | checkpoint | 5.3 - Inducement Saw Cutting
ba74ad63-a217-5659-8789-4213c2ef4104 | note | Frequency - Each concrete pour
9d64d094-2296-50a1-b47e-7ab9a78b0e8b | note | Acceptance Criteria - An initial 3-5mm wide saw cut to a depth of T/4 to T/3 where ‘T’ is the concrete thickness (generally 150mm) is performed along transverse contraction joints as early as possible post pour.
125b6f42-2b3a-58fe-b46a-92a76549fb7a | note | ○ The concrete must harden sufficiently to permit cutting the concrete without excessive chipping, spalling, or tearing.
1a776220-10f0-5a53-b868-97fef033431d | note | Reference Documents - Beca Spec 002 - 11.13.5.2
30288578-007f-585f-a161-4929011df0c2 | note | Inspection/Test Method - Visual Inspection
377ff993-cbe6-50a7-aa30-10d2d23a7839 | note | Record of conformity - This ITP signed
2b2e9676-0d95-5bfb-9060-7ae0fcc14764 | note | IP
ac9e5c42-5d54-51f0-92a6-47743e8b6671 | note | Responsibility - Project / Site Engineer
ec669d6c-1236-5ce8-b376-bbfb38d60b30 | date | Date Completed:
1415f254-48b2-52a5-8aea-2df0d8845449 | checkpoint | 5.4 - Formwork Removal
4c9f9ded-2540-5aa1-a9b7-1549da9de3ad | note | Frequency - Each concrete pour
c89af9fa-9c3c-5b89-9507-b7f0b4112f66 | note | Acceptance Criteria - Forms must remain in place at least 12 hours after the concrete has been placed (but no longer than 48 hours).
28e65d8a-e481-5fae-b3c1-156e31999afd | note | Reference Documents - Beca Spec 002 - 11.8.1.3
a1b1af8d-5887-5e45-80c8-c711f63c9273 | note | Inspection/Test Method - Verify
f4445baf-2265-5b77-9a96-a3717922e231 | note | Record of conformity - This ITP signed
5d0613f6-7e0b-5386-9b7c-f4e76151a0d6 | note | IP
6d4b2aac-9612-5e27-a9cf-153d627386ae | note | Responsibility - Project / Site Engineer
18f2ef5c-d133-5162-88cf-ce695de1233a | date | Date Completed:
69489b9b-1e23-57b3-b09f-8b123c4734fd | section | 6.0 - Completion
8fa0b7c0-e1be-5bfb-a603-8cd013fc6298 | checkpoint | 6.1 - Surface Smoothness Testing
55e7de99-3c61-538a-a173-cbdebe5c1754 | note | Frequency - Per Lot
0c6efdae-61ee-505e-af82-1add84557269 | note | Acceptance Criteria - The finished surfaces of the concrete pavements shall not deviate from the testing edge of an approved 3.5m straight-edge more than 5mm longitudinally and 5mm transversely. No ponding of water is permitted.
32222931-7dbf-5c57-a8be-fb36823b71be | note | ○ Points exceeding tolerances and any observed areas of ponding water will be recorded on ArcGIS.
8789dc0b-3a2a-58b2-89a8-c6643a4d1cac | note | Reference Documents - Beca Spec 002 - 11.14.3
9d59607b-536c-51a3-b9b8-f275e3994b93 | note | Inspection/Test Method - Visual Inspection
d920b062-aab2-5cc1-8472-ec4909ccab24 | note | Record of conformity - ArcGIS, This ITP Signed
2d893d27-0cfb-5e97-acd3-5a846b45f93c | note | IP
168e7066-b2f9-5912-8c30-42b0df934b3f | note | Responsibility - Project / Site Engineer
4799c1ed-759e-577d-acbc-1c9e9a389eb2 | date | Date Completed:
91cbcdd4-c964-5ba9-81ea-9199af3ff529 | checkpoint | 6.2 - Pavement Surface Levels
f7b31f9b-21d2-5bd8-8aca-6bac5928cc2c | note | Frequency - Per Lot
445217a3-704d-54d0-91f1-f47b50e14278 | note | Acceptance Criteria - The Contractor shall take levels on the finished pavement surface at the corner of each slab.
986af59c-af1b-54e1-b235-cc9960654cdb | note | ○ The finished surface levels taken shall be within ±5mm of the design levels shown on the Drawings.
54cd0821-1456-58c9-9edb-34ea1dfb4396 | note | ○ The levels shall be measured to an accuracy of 2mm.
2479533d-2d5a-5645-94a5-2f3915c91011 | note | Reference Documents - Beca Spec 002 - 11.14.2
7d131307-0cf5-5fb5-a872-6605679b0156 | note | Inspection/Test Method - Verify
30637c20-3975-54ca-b8e5-98e5838a8c78 | note | Record of conformity - Conformance Report
91934272-5c06-53f9-bced-b8f5a45c58a2 | note | SCP
942d3878-1a64-50ba-9f33-700d3f5365a2 | note | Responsibility - Project / Site Engineer, Surveyor
c89333bd-fc10-5caf-a06a-0387ff3ec9a7 | date | Date Completed:
4ea2f5f4-1037-54b8-98fd-5a7f56de6983 | checkpoint | 6.3 - Protection of Slabs
e0a272cc-8031-5c13-94e7-2c52940c54d6 | note | Frequency - Per Lot
ca4200e7-3811-542f-9623-95ab15582db2 | note | Acceptance Criteria - Concrete pavement must not be trafficked until 7 days old or early strength results are obtained. Steel tracked or steel wheeled equipment is not to be used.
d0d67642-8c06-5e46-8e83-6af9a4ec16ed | note | Reference Documents - Beca Spec 002 - 11.17
1981dabb-a7d4-56cc-a815-bb0ec0aac791 | note | Inspection/Test Method - Verify
d9f99ce0-fd9f-523d-b3b0-028767f2b5d5 | note | Record of conformity - This ITP signed
536c33e3-9e33-5297-a415-b849c3716a6b | note | IP
a9977ffb-173a-5f9c-a3fc-11de956a432f | note | Responsibility - Project / Site Engineer
5f06486e-2a73-588f-a366-13292ebceedf | date | Date Completed:
2c5ed52b-149f-5ba6-86ad-1a18b9ce8a73 | checkpoint | 6.4 - Defects to Slabs
3f516d19-5afa-50e8-8656-411903a8c112 | note | Frequency - Per Lot
150631ea-1856-53df-a83c-9a9317be8056 | note | Acceptance Criteria - Check for any nonconforming defects (cracks) in the concrete slabs.
94aceb5c-6f5d-54f3-bdd1-ca5bc232a8a3 | note | Reference Documents - Beca Spec 002 - 11.19
ec7e76c9-dc53-5142-98bd-3df83042df78 | note | Inspection/Test Method - Verify
ff40cd6d-cd44-56b9-a6a1-b07d689665dd | note | Record of conformity - This ITP signed
d109b0da-565c-5772-9e5b-2c8a5ff335e3 | note | IP
36bc9767-f10d-5220-8856-df85756fe6b7 | note | Responsibility - Project / Site Engineer
c9833f31-e161-56f7-9594-e08d707687aa | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
6ec667d0-0f8f-5ddb-9183-5e7d582c3f27 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality/System Procedures and verifies lot compliance with specifications.
d2e6550e-c607-57f6-87e4-4aa671b9d4d2 | textbox | Print Name:
870a6224-29d1-5697-b7e0-a4aee1ba336c | textbox | Position:
3b5d58b4-9d81-5add-bb5f-d6993954ebd6 | date | Work Completed On:
94480ab5-0fac-571f-9c29-dad8053606d3 | date | Date:
b94f9830-e527-4da2-9d1a-30a1abb50bff | checklist | FH-ZU2-QU-ITP014 - Sawcutting & Joint Sealing - Rev 1 | itp | ITP014 - Sawcutting & Joint Sealing
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
fbd6ef58-7046-5030-bc38-d0da69c3974d | checkpoint | 1.1 - Check for Correct Documentation
79bd05d0-9a65-5949-b1aa-d4a42fc4e829 | note | Frequency - Prior to commencing works
31adfb6e-d09a-5768-8b5b-c2053849fb88 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
5d8b007b-08f3-5787-8929-bf98bc3e325d | note | ○ Current revisions of these documents to be obtained via Aconex or ACC
fee07b74-ed1e-5be5-bf5f-59b71136dd74 | note | Reference Documents - Current revisions in Aconex or ACC
da8dd3cc-19e3-5726-b492-cba5176eab7e | note | Inspection/Test Method - Verify
b231cc0c-dad8-53ec-b88f-e9c0bc8f723f | note | Record of conformity - This ITP signed
7235dad4-6d0b-59a9-8eed-fbebbba2a3c3 | note | HP*
5c7ff4ef-cb14-595e-b46d-97dfd87a16cd | note | Responsibility - Project / Site Engineer
3e94d70a-74f0-5061-98da-8624cc10e016 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
3303edab-5b66-5af1-b8d1-22ab8495cee9 | note | Frequency - Prior to commencing works
be859a16-d2c6-53c3-9eda-012f04d455a3 | note | Acceptance Criteria - All necessary measures and controls are being implemented in accordance with PSP, EMP, TMP, JSEA, SWMS & WP
dbcba871-bf73-5749-8b4e-72cae0e93402 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
a0786763-a24a-554c-b4b4-6fc9d456cccb | note | Inspection/Test Method - Verify
d3393572-6931-512b-8426-8ac8490b3c40 | note | Record of conformity - This ITP signed
18970737-ee7c-5380-85c4-295e20dbdb59 | note | HP*
ac463377-a89f-5219-a70a-255e42583d57 | note | Responsibility - Project / Site Engineer
1e1c368b-64cd-5b5b-a437-b6e79ffd73ad | date | Date Completed:
6388a249-3345-585a-b094-a82a42091183 | checkpoint-no-value | 1.3 - Materials
104cfd90-1f66-5422-ba65-37d3da17529b | note | Frequency - Prior to commencing Works
04426826-43e9-5e13-9ab8-c8fd7051ae59 | note | Acceptance Criteria - Joint sealer shall be Dowsil 888 silicone joint sealant or approved equivalent.
d6909b33-132b-5a99-9c4d-9d6f19d6a2c7 | note | ○ Manufacturer’s instructions shall be provided to the Principal’s Representative prior to works commencing.
196df762-12b9-59fd-a43e-07f70198a115 | note | Reference Documents - Beca Spec 002 - 11.4.15 & 11.13.7
ec797054-95f2-4c19-80dd-7f72509b3664 | note | Aconex reference: FHPL-TRANSMIT-001667
8015b1e2-15af-5303-b7fc-371f61f1f555 | note | Inspection/Test Method - Verify
36243bbf-6174-5952-8558-8d07c07db877 | note | Record of conformity - This ITP signed
1c190af6-c392-51f3-a584-d381a85854fd | note | WP
1c777fe5-4e59-5b43-9ad5-8a5f0e3b41e7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
17db4f34-6db8-5fb1-8daf-c848d4036aef | note | Principal’s Representative - BecaCPL-GCOR-000749
a2a7b1bb-5e91-5211-9836-b63962a93b8a | note | Date Completed: 13/05/2024
62cb0e25-66ef-5565-83f6-0dac7af7e013 | section | 2.0 - Installation
80fb73ed-9148-5be9-84ce-96314adc85d5 | checkpoint | 2.1 - Define Area of Works
295d7320-011a-559c-a972-4aed72dd5c8d | note | Frequency - Prior to commencing works
c1de4dee-b4bc-55c7-90e3-f8968bd9f205 | note | Acceptance Criteria - All joints shall conform to the details and shall be constructed in the locations shown on the Drawings.
5939cd03-4fd1-5d3d-82f6-15ba24074494 | note | Reference Documents - Beca Spec 002 - 11.13.1 to 11.13.5
722d964b-67c3-5d03-ad10-f925c6693338 | note | Inspection/Test Method - Verify
63562468-3c10-533c-bd0c-8b100a446611 | note | Record of conformity - This ITP signed
c1528537-18cf-598f-b010-d783ae5d9fb6 | note | IP
0a85ca7f-f949-53e8-8449-464fb9998035 | note | Responsibility - Project / Site Engineer
8ceb191f-f8d6-5a46-8a48-8d31b0754533 | date | Date Completed:
9ad22714-45c3-594f-bafc-69cb92633a96 | checkpoint | 2.2 - PCC Curing
31744c6d-8b9e-5970-ba1d-a84974b2d5c0 | note | Frequency - Each Lot
230244ca-7f00-5c06-964a-22aed6882ccb | note | Acceptance Criteria - In areas where sealing works are planned, confirm PCC has been cured for a minimum of 7 days prior to sealing.
f93d14d2-c38d-5953-8a9c-76b4355bcc0c | note | Reference Documents - Beca Spec 002 - 11.13.7
3e1be03d-3f7e-59a2-8fc5-5da68d188d6e | note | Inspection/Test Method - Visual Inspection
d4439ab2-6542-58e0-aa12-6ef6c03afed2 | note | Record of conformity - This ITP signed
ed398638-07e7-5a6e-b3d2-236d2382808d | note | HP*
f36e53b7-aa1e-5d8b-840b-da3b6b51c409 | note | Responsibility - Project / Site Engineer
d18e00cc-bf4f-59b3-be8c-05e630d9b96b | date | Date Completed:
f9a30c12-b07c-5b7a-a70a-74c6dc3b696e | checkpoint | 2.3 - Cleaning of Joints
54a84945-1e69-597f-b3da-e8f0613d560c | note | Frequency - Each Lot
8d1e99cf-2220-5158-a456-6350bb440f3a | note | Acceptance Criteria - Joint faces shall be thoroughly cleaned and dry prior to sealing. This shall be approved by the Principal’s Representative.
76b748eb-a640-5b9f-abff-577239a7e83d | note | Reference Documents - Beca Spec 002 - 11.13.7
3f303229-fda5-55cd-80a2-1ec9c63f5bc3 | note | Inspection/Test Method - Visual Inspection
5029e114-3f54-5c3a-957a-b36a2e35ad46 | note | Record of conformity - This ITP Signed
a4970c7c-ab86-5b24-b946-10cfe343ba20 | note | HP
dd3d86b2-47be-5f2e-bb01-be9bb380d7c0 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a3590dfe-3c4f-5768-b7ae-73cb1bc9d759 | date | Date Completed:
ba83cded-4d09-50d7-a949-2a60a3a7c8c2 | signoff | AUTHORITY HOLDPOINT
9a279428-8bb3-5f72-acd3-3d377212d952 | checkpoint | 2.4 - Backing Rod Install
825ca411-5727-5ec3-ab0c-19d7c3092ad8 | note | Frequency - Each Lot
7905221d-1424-5c4b-b9c7-3761007aa3b9 | note | Acceptance Criteria - Backing rod to be installed to depth shown on the drawings.
4c33455f-d134-56b9-bd91-914522f6aaa4 | note | Reference Documents - Beca Spec 002 – 11.13.7
d2303ef6-434e-5eb4-a00e-a4ee33374713 | note | Inspection/Test Method - Visual Inspection
64a37ad5-f09b-52f9-b76b-c67f1920410f | note | Record of conformity - This ITP Signed
847a7d15-8584-5e8d-ada6-d4c079607b83 | note | IP
be167dd5-d048-5341-927a-74ada804837a | note | Responsibility - Project / Site Engineer
da094bf1-5076-5913-93c2-aaf21e393771 | date | Date Completed:
0439dd16-c209-52bc-9c79-8b4362871d01 | checkpoint | 2.5 - Sealant Install
5e294b05-1fc6-567f-850a-edc8fc6ef83d | note | Frequency - Each Lot
9e69eab8-128a-5236-9b3c-14420c4b12dc | note | Acceptance Criteria - Sealant to be tooled off to correct recess. Excess sealant to be removed from the surface of the concrete.
5318b95d-2c17-5177-be5b-77c7e07c7f66 | note | Reference Documents - Beca Spec 002 – 11.13.7
66de4527-e36e-5cf2-8bbb-f15f283e02da | note | Inspection/Test Method - Visual Inspection
165c9f15-ca4b-5e66-a171-a5fa68fd6053 | note | Record of conformity - This ITP signed
723c8b20-6353-5b5a-b67f-425d9e2bc5d0 | note | IP
873f9e41-1b9d-5139-aede-4a5e8a601dc0 | note | Responsibility - Project / Site Engineer
99785c1a-a191-5411-9d83-66073b0d8f49 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
2032242e-37a0-5afc-b658-cf9d20792b14 | note | This is to verify that the final inspection has been carried out in accordance with the Fulton Hogan’s Quality Procedures and Project Quality Strategy and the product is hereby certified to confirm with the contract specifications:
86eb545f-008f-5daf-9ba8-17e663686c8b | textbox | Print Name:
98c0cebe-8793-50d3-959c-8570dee248eb | textbox | Position:
6d2a49ff-3315-51d0-aca3-72cedec50543 | date | Work Completed On:
7347a2ab-2fd0-59f3-ba1f-0f8ea233c1f7 | date | Date:
c42b8440-350c-4784-a821-ba509f755a03 | checklist | FH-ZU2-QU-ITP015 - High Early Strength Lean Concrete Placement - Rev 1 | itp | ITP015 - High Early Strength Lean Concrete Placement
dfbc0e0a-0cb2-49ec-94fc-753028b5d0c2 | section | 1.0 - Preliminary Activities
6712e7e7-b913-4cad-a29c-d541f7808afb | checkpoint | 1.1 - Check for correct documentation
7944f4f4-2a7a-5b80-aa50-6767d0d2a5e8 | note | Frequency - Prior to commencing works
f78851a2-a7c1-5009-8726-89dff85b0b83 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
bd0154f6-5203-5aee-9602-24cd92746f32 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
737d535a-d507-5293-aee6-e96722b043f8 | note | Reference Documents - Current Revisions in Aconex, ACC
2a9991a1-400e-52d2-a532-7c07c7c0f57f | note | Inspection/Test Method - Verify
6c4719c8-cfd5-5c14-8b15-4824ff243cd5 | note | Record of conformity - This ITP signed
019d1d84-5721-5b7f-a59b-8509ce6e90b9 | note | HP*
e6cf1f99-cbf2-58eb-9268-b1748e0f9127 | note | Responsibility - Project / Site Engineer
8349b8d3-a86f-5134-93be-469508f9ce73 | date | Date Completed:
c2beb12b-988d-46c5-99a1-f440f3242bf0 | checkpoint | 1.2 - Implementation of all measures and controls
432a4e6e-49ef-58ed-a8a7-792bf669b352 | note | Frequency - Prior to commencing works
77347a37-aaa7-50b9-b751-d3da9b490b48 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
48b83619-aa46-5c5d-8f2c-cbd47ffd2b35 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
9ee7ac61-d46f-5209-9d46-a57bee5b6b9b | note | Inspection/Test Method - Visual Inspection
f2e279a5-f5d7-512a-9af9-61084ae4e1a0 | note | Record of conformity - This ITP signed
3b4c2eb5-4c7b-537e-a5a1-d528932c95b8 | note | HP*
ef2e5bba-dce8-51f0-a266-d8cb8d4e8862 | note | Responsibility - Project / Site Engineer, Site Supervisor
368187d3-5373-5a5b-9483-ec1d6809aa93 | date | Date Completed:
3d6b455e-7ff5-4469-bd24-cc6f221f9106 | checkpoint | 1.3 - Plant & Equipment Check
c131f583-5e95-53f8-8e87-f799b68dcd9b | note | Frequency - Prior to commencing works
c87e5796-f7d5-5b43-a828-389c557654eb | note | Acceptance Criteria - Plant and equipment items used in the Works shall be appropriate for the intended purpose and shall be maintained in good and serviceable condition at all times during which they are operating.
2508810e-4f7a-5111-9299-e2166eb1baad | note | Reference Documents - Beca Spec 002 13.3
2acf9b97-26ae-50ab-b157-0579f2313003 | note | Inspection/Test Method - Verify
40d5b898-284e-598a-9d79-7f6d5ec8ecbb | note | Record of conformity - This ITP signed
dba5bad5-efb6-5bd2-82a4-a771a148fb1b | note | HP*
477374f2-efd5-54d6-9b29-5f492eb70a16 | note | Responsibility - Project / Site Engineer, Site Supervisor
61d9259b-8795-5c12-b319-472fe87b587f | date | Date Completed:
2b718a27-b6f1-4b3d-b17c-ca03606fe914 | section | 2.0 - Production and Construction Trials
682b747b-5a82-4c22-81d8-df8c9c975ef7 | checkpoint-no-value | 2.1 - Mix Design
690fb887-aaf5-5226-9877-6b127492e350 | note | Frequency - Prior to works
a9f9ff38-7b55-5999-a385-0e900bf245c5 | note | Acceptance Criteria - Theoretical mix design and preliminary trial mix results to be submitted to the Principal’s Representative for review and acceptance prior to full trial mixing.
ef34d970-9ec5-569b-b469-92d280482227 | note | Reference Documents - Beca Spec 002 13.5.1
dbc726aa-9b61-50e0-9236-cf4018222388 | note | Inspection/Test Method - Verify
7ec50637-b5d7-5df8-b9b8-e5ea03059f97 | note | Record of conformity - This ITP Signed / test reports
2082d925-a5e5-5f6d-aed5-63a4acdf504f | note | HP
fe96dc1b-a0de-5c7e-844b-aa56582e1472 | note | Responsibility - Project / Site Engineer, Principal’s Representative
e2f09bb8-e62f-5e1b-a563-1758942f5573 | note | Date Completed: 13/09/2024
58ea452f-e285-5a95-9e6e-51546848526b | note | Principal's Representative - BecaCPL-GCOR-001171
d5308491-7824-4983-88a3-fe3bc5cf80e8 | checkpoint-no-value | 2.2 - Mix Design Report
1902e885-fe4b-5de8-bb33-b97d18928d62 | note | Frequency - Prior to works
99825237-1513-5b47-a4f9-14cdb6fbd36d | note | Acceptance Criteria - The theoretical mix design and preliminary trial mix results to be submitted not less than seven (7) working days prior to full trial mixing.
fefed4a2-c7a1-5821-9d41-c085c23a9c29 | note | Reference Documents - Beca Spec 002 13.5.2
c7a78384-dfc8-51f5-9036-0840ca99f8f9 | note | Inspection/Test Method - Verify
86e01fb3-8fa8-5538-8987-f640cec437ed | note | Record of conformity - This ITP Signed / test reports
7bdda105-e475-52a5-9ffe-6e50afbeffd8 | note | HP
67104860-a283-5f86-bd09-b8b1e3ec176f | note | Responsibility - Project / Site Engineer, Principal’s Representative
155e5b71-3c9c-57d3-a4b8-b5b060abd230 | note | Date Completed: 13/09/2024
52723341-65e8-5ae5-870c-17371d770fef | note | Principal's Representative - BecaCPL-GCOR-001171
9d264ec7-add2-4523-9072-8300d10e3b7b | checkpoint-no-value | 2.3 - Mixer Uniformity Test
39fbdbd6-5d06-5d8e-ad5a-d02c35330554 | note | Frequency - Prior to works
2feafff9-77db-59b5-ac91-4f22dd3efc47 | note | Acceptance Criteria - Mixer uniformity tests shall be undertaken on the fully operational mixing plant at least seven (7) days prior to undertaking production trial and submitted to the Principal’s Representative.
c16eb7fd-72c0-5540-ba90-0ea9e0f0c32d | note | Reference Documents - Beca Spec 002 13.6.1
264b4f9e-78d2-549a-8abe-4a07fc9c04da | note | Inspection/Test Method - Verify
e0edec82-428d-5bc1-a745-56f0bc2ba6c9 | note | Record of conformity - This ITP Signed
b3680153-cce4-58fe-b2e3-f758c7903ae3 | note | WP
35194a59-3a43-5c36-842d-5c56cd2b61aa | note | Responsibility - Project / Site Engineer, Principal’s Representative
ebd8659c-617c-5ed5-b4df-cc4cf4ffe9fa | note | Principal’s Representative - BecaCPL-GCOR-001240
63e223d4-8c2c-5ce1-97e4-5c41c3794a37 | date | Date Completed:
1de4b53c-11e2-48b5-9a89-4d47793e3511 | checkpoint-no-value | 2.4 - Production Trial
d25a798d-8df3-5b3a-b5c9-c5cf88574f2d | note | Frequency - Prior to works
c52d8fae-5752-57cc-92c3-f68a7a6b7be9 | note | Acceptance Criteria - A production trial must be completed as per the requirements in the specification.
fb197d40-b81c-5a53-9f40-7a0848d671dd | note | ○ The results and control procedures to be presented for review and approval by the Principal’s Representative.
5b529e85-01fd-5471-85a3-cc7e0065022e | note | Reference Documents - Beca Spec 002 13.6.1
563c748f-2c3e-57c6-b5f2-f00ee0a1b924 | note | Inspection/Test Method - Verify
be1949fb-49bb-5210-b8de-d94a7d613739 | note | Record of conformity - This ITP Signed
415d955e-e8e5-54ec-ae80-2ddbd50e9806 | note | HP
2f9850dd-98ac-526d-8d4e-d21e020f7fa8 | note | Responsibility - Project / Site Engineer, Principal’s Representative
f4e45751-aebd-5cae-abe2-b516e6dbca3f | note | Principal’s Representative - BecaCPL-GCOR-001240
4755571d-c41f-544b-97b4-80e8972d5ec0 | date | Date Completed:
7e751069-aa7a-4226-9427-79d195756c82 | checkpoint-no-value | 2.5 - Compliance
1aaea2fb-0862-5079-ad10-7925bdd82753 | note | Frequency - Prior to works
0c8dbc77-ecc3-5b9e-b0f2-008c10230ada | note | Acceptance Criteria - Provide evidence to Principal’s Representative of concrete supplier demonstrating compliance to AS 1379 or is a third party accredited to AS 1379.
d84f4476-71ff-56cf-a3c4-4fef572eba5b | note | Reference Documents - Beca Spec 002 13.7
7101cd85-203e-5797-8cb6-5d817d1f2179 | note | Inspection/Test Method - Verify
c001f072-6adb-5fd8-9486-4e1925866f82 | note | Record of conformity - This ITP signed / evidence documents
f6694ee0-d210-5607-9700-c4e65ea9a4a0 | note | HP
50edde23-2933-56b0-b478-d16c475f2595 | note | Responsibility - Project / Site Engineer, Principal’s Representative
ed00a9df-0ce8-57ec-8ac4-acf65c95455d | note | Date Completed: 13/09/2024
cf51fd12-128c-538b-bde5-9e64cbf7c0ce | note | Principal's Representative - BecaCPL-GCOR-001171
b4e29d90-5665-43d5-998a-f0fff578eb70 | section | 3.0 - Pre-Placement Activities
3809d3b0-56fd-4685-b8b4-1e09ae8a3836 | checkpoint | 3.1 - Surface preparation
9d5e19e6-7aa0-5a95-8111-4e454dd24bec | note | Frequency - Prior to works
e3bd3171-cd44-5af5-9a7e-d1d1cccfb054 | note | Acceptance Criteria - The surface must be clean and inspected by the Principal’s Representative prior to placing.
169928af-7fe9-5337-b889-23f4ba40159c | note | Reference Documents - Beca Spec 002 13.8.1.5
0c8ab2dd-d061-527c-847a-f6b344f10af4 | note | Inspection/Test Method - Verify
94d79d16-dfb7-58d5-bf0d-f4214fc52a30 | note | Record of conformity - This ITP signed
01ea45ac-e65d-5f54-affe-9e98b567dfda | note | HP
e349923d-b6f3-5ab3-a104-2b91a2c06302 | note | Responsibility - Project / Site Engineer, Principal’s Representative
cd097b79-d737-5421-b4e2-334bdf0dfbc5 | date | Date Completed:
74e2efbd-a79c-4ce3-b24d-e90583b74c08 | signoff | AUTHORITY HOLDPOINT
5262d2f8-2f71-489b-b857-ca06cb282b87 | checkpoint | 3.2 - Weather Conditions
6caf6fec-cfa2-56aa-a829-c287a6af9ba6 | note | Frequency - Prior to commencing works
45ba7fd4-3722-5daa-b9bf-55c6f4468e68 | note | Acceptance Criteria - HESLC shall not be placed when the shade temperature is below 5°C or above 35°C.
8a5364ea-2313-5bac-9a1f-9b293dcb7b95 | note | Reference Documents - Beca Spec 002 13.15
49c4d3f1-eae2-508d-b3f1-9d3296c9d2f0 | note | Inspection/Test Method - Verify
06f3d9a4-1c58-5464-8272-ec125f9b63d9 | note | Record of conformity - This ITP signed
b0297096-a032-5d1e-b7f2-fd073dfa4e21 | note | HP*
54f874d9-6831-5c9f-a6e4-7eedd5a12ce2 | note | Responsibility - Project / Site Engineer, Site Supervisor
97547145-88dd-5914-aa8a-56cbbd362bdd | date | Date Completed:
a1407878-971c-458b-9a7e-de1ab5605e91 | section | 4.0 - Placing Concrete
0507a2ed-1c43-4e70-890a-8f1142b40462 | checkpoint | 4.1 - Place, Spread and Compact Concrete
198a3453-4bf6-5ca5-b68f-444692cf8198 | note | Frequency - After completion of works
7680b5f8-0138-5407-8a54-42d62336f866 | note | Acceptance Criteria - Compaction of HESLC shall commence immediately after placing and shall be by internal vibration.
97aa61b3-6a5d-5c15-a4dd-875663f53968 | note | Reference Documents - Beca Spec 002 13.10
b4162197-ce02-56b8-8c14-c8d61ad0a7ec | note | Inspection/Test Method - Verify
a8b66a92-9486-5c8c-a5c7-3d825ce53d43 | note | Record of conformity - This ITP signed
94e3dd4a-c354-55d2-913f-91cb96ebf710 | note | IP
b2e5153c-0b85-5df3-9590-26439120c522 | note | Responsibility - Project / Site Engineer
be46e53f-2abd-5b7f-bbcd-0cb4f0d7ae63 | date | Date Completed:
3922c64b-5eb2-409d-b3b7-b403d2905d30 | checkpoint | 4.2 - Slump
e268e261-039f-583e-a796-c3c0bf173246 | note | Frequency - 1 test every 2 trucks
8d013726-3126-5a3a-95fa-5cfb8364b328 | note | Acceptance Criteria - 100mm +/- 20mm
be6c938b-6766-5da8-8a53-2be35de8289e | note | Reference Documents - Beca Spec 002
1779ad00-433b-5aec-b466-6a6f45219e24 | note | Inspection/Test Method - AS 1012.3.1
7a9d68bd-236f-5fb9-8b9f-8e5476f56534 | note | Record of conformity - NATA Test Certificate
babc4247-da89-53f6-8be8-c40801383605 | note | TP
bbd92bf4-d2fd-55eb-85ed-1fe463b3414f | note | Responsibility - Project / Site Engineer, Laboratory Technician
f761a99a-8c40-58fc-99c2-693dd338ce9e | date | Date Completed:
f4f6a52e-67cc-420f-b926-0e4b3d172c8d | checkpoint | 4.3 - Temperature
14c5c469-01dc-578b-aaf1-d632d8466bc6 | note | Frequency - 1 test every 2 trucks
0b5ee5cb-be0d-56ac-9466-d13a1e639996 | note | Acceptance Criteria - Minimum 10°C Maximum 30°C
6fd17808-4107-5121-8e61-0190ae37fedc | note | Reference Documents - Beca Spec 002 13.15
414c748b-c490-59e4-82aa-499c77e8ecfb | note | Inspection/Test Method - AS 1012.3.1
eb8c0ad9-0dc6-5995-9dfe-a3b79a59b855 | note | Record of conformity - NATA Test Certificate
1c3ce3f0-279e-5678-95cc-b61bb6b94424 | note | TP
13107dce-39a0-51d2-bc57-88e0fa901d33 | note | Responsibility - Project / Site Engineer, Laboratory Technician
9eee4560-09ce-57b6-98d8-dd5ac6709ee5 | date | Date Completed:
66240731-3b85-4826-8867-0188c1b6708b | checkpoint | 4.4 - Density of Cylinders
1dcad014-72b0-580c-896d-cad6cdd3b8ca | note | Frequency - 6 cylinders per Lot (same cylinders used for compressive strength)
b4d23261-a7e5-5e93-9668-f23a3aacedf6 | note | Acceptance Criteria - Results for information only. To be used to determine density of cores.
a9a32d5a-2cf4-54be-8603-320e9a2699f3 | note | Reference Documents - Beca Spec 002 13.17.3.6
08f6dbdb-93ec-5a8f-8ba0-6da359bf7d1d | note | Inspection/Test Method - AS
c80d4005-469d-5dc2-8e83-3a0b5846f89d | note | Record of conformity - NATA Test Certificate
9e4aa837-c55a-5e6e-b38b-55177c77dd50 | note | TP
4e697d4c-5c94-59fa-b889-6a2ad547bb54 | note | Responsibility - Project / Site Engineer, Laboratory Technician
3780cf11-63bb-5b7c-82ca-b48480d3dd2c | date | Date Completed:
16cfd622-7461-4109-b108-e0f0ef57be08 | checkpoint | 4.5 - Compressive Strength (7-day)
d7318c78-b9c2-5888-9999-e7d6257abcf2 | note | Frequency - 4 cylinders per Lot (same cylinders used for Density)
86980492-a652-5124-8380-c1b078c46f6a | note | Acceptance Criteria - Mean of the 4 cylinders to be minimum 10MPa and maximum 15MPa.
d079095e-5bd2-5047-b991-83f0460c0502 | note | Reference Documents - Beca Spec 002 13.5.1, 13.17.3.6
c2e00e97-b9a7-5c6e-ae69-55eca92b6446 | note | Inspection/Test Method - AS 1012.1, AS 1012.8, AS 1012.9
ed217bc4-1326-53d5-bf1a-2259e992356b | note | Record of conformity - NATA Test Certificate
04c09162-9be2-59c0-a507-2d76bf9194c4 | note | TP
3146a27d-074f-5de3-afa6-704c297ef0c3 | note | Responsibility - Project / Site Engineer, Principal’s Representative
d3ab9044-ef99-5639-9017-2712987f9d54 | date | Date Completed:
cbe4abae-ff1e-478d-b434-3d0fe258f8b0 | checkpoint | 4.6 - Compressive Strength (28-day)
14d20435-e543-5925-b31d-61c96e0754e5 | note | Frequency - 2 cylinders per Lot (same cylinders used for Density)
c4f7131a-fd02-500b-89df-74d7c4827700 | note | Acceptance Criteria - Each sample to be minimum 20MPa.
111b6e38-baf1-5917-9948-a981684b25b2 | note | Reference Documents - Beca Spec 002 13.17.3.6
3b7af89a-2fd2-5582-acc9-75f4d6356f5d | note | Inspection/Test Method - AS 1012.1, AS 1012.8, AS 1012.9
21b83c28-2f3e-578d-bb60-d738036d51e7 | note | Record of conformity - NATA Test Certificate
55d40b35-fd58-5994-8633-3b1846c3e7de | note | TP
0958e6a3-2480-5148-9acc-2707aa8a3eac | note | Responsibility - Project / Site Engineer, Principal’s Representative
322f68d4-95cd-513c-828a-8a12e623888e | date | Date Completed:
b55478d7-beb0-4753-bf39-36b977686a22 | section | 5.0 - Post-Placement
e1ecbfa8-be77-447c-b41f-91a19770aa03 | checkpoint | 5.1 - Construction Joints
f5716e6a-c228-5890-b1fc-6f41bf60ed17 | note | Frequency - Each Concrete Pour
822e004a-cfc8-5701-80c2-b38124bbbd4f | note | Acceptance Criteria - At the end of the day’s works, the HESLC to be feathered out and cut back before work restarts to give a straight, vertical face for full depth of layer.
991e214b-a324-5a1d-8826-35595e7047ce | note | ○ Edges of construction joints shall be painted or sprayed with bituminous emulsion.
9b5838f4-e83f-5d78-a095-9153083db635 | note | Reference Documents - Beca Spec 002 13.11.1
71a40074-8816-5dbb-b8b9-74e7e39b2fb3 | note | Inspection/Test Method - Verify
4ece3e36-a3f0-5e1d-a5f2-d7cef8123b47 | note | Record of conformity - This ITP Signed
38eb2330-8653-515c-9658-2ef5bf5bbc69 | note | IP
b47ea37e-416a-52f4-aaa0-3f28030725a1 | note | Responsibility - Project / Site Engineer
2ad772d0-d82a-544b-b176-7c8f8cd09edf | date | Date Completed:
22888a47-37bf-439a-aa02-1d55dcedade4 | checkpoint | 5.2 - Saw Cut Joints
d844226a-0d5e-5911-ba9a-9f573347673c | note | Frequency - Each Concrete Pour
c1d75f63-edfe-5dc4-a80a-df9412220ffd | note | Acceptance Criteria - HESLC to be sawcut into maximum slab spacing of 5m x 5m. Where pavement width is less than 5m the spacing shall be reduced to obtain slab dimension ratio of maximum 1:1.25.
0274fc1d-a0a1-5c41-b3a1-e58cc2d31cf4 | note | ○ Sawcut to be approximately one third of the layer depth.
a3a692db-5ed4-555c-9df7-2fbfbc1cb6fa | note | Reference Documents - Beca Spec 002 13.11.2
d81f8a7c-3cce-50fb-b821-afe2351f9aba | note | Inspection/Test Method - Verify
0cfdc788-f9ed-5373-9584-c0df96e6f26b | note | Record of conformity - This ITP Signed
9fa58922-7e05-5e5d-8dd9-78ada9d6e23e | note | IP
d562e3e3-50e8-59b5-913e-b8d3ab586c46 | note | Responsibility - Project / Site Engineer
389162fe-6238-54d5-ad14-e21bbe7f3f34 | date | Date Completed:
95953ac6-73b9-49dd-9d69-0640ad1e9571 | checkpoint | 5.3 - Layer Thickness
cea64afc-f762-5e98-9681-6e015b522cb6 | note | Frequency - Each Concrete Pour
b4148477-3aa8-5151-a5de-cf735bb73aaa | note | Acceptance Criteria - Finished surface of the HESLC to be picked up by a surveyor to determine the thickness of the layer.
83c7ed0d-1cdc-5db7-a534-8dbafa9d7d5d | note | Reference Documents - Beca Spec 002 13.17.3.4
a0ad0340-a950-5d9c-be86-bc34d632d744 | note | Inspection/Test Method - Verify
b8e3e630-4b57-5cc8-a59b-1ddec90966ed | note | Record of conformity - Survey Report
0e9c8a07-3c0b-53e7-8f93-fe4d7efaa67f | note | HP
9d171493-7d25-5ee3-a152-aa5861210ad6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
91943864-c9ac-5d94-b206-486c43219ac1 | date | Date Completed:
68f9d247-c764-41be-a855-17a6e87826f0 | signoff | AUTHORITY HOLDPOINT
31e8d669-82ee-4911-acf0-3f5040c60faa | checkpoint | 5.4 - Core Analysis – Density
8a32859c-6326-5a94-bfad-3c1b77f0c7bf | note | Frequency - Refer to markup in notes section
93b111bc-6750-536d-b57a-b167d9a3e7ed | note | ○ Aconex: BecaCPL- GCOR- 001038
3cc692e1-73c5-527a-885d-2c57b23acba5 | note | Acceptance Criteria - Cores shall be 120mm diameter.
f644fa61-c994-5fc2-8df1-492456b372fe | note | ○ Calculate the field density by comparing the density of individual cores with the average density of four (4) compressive strength cylinders taken.
b1eddd99-d299-58fc-9453-d33aaefaaf2f | note | ○ Field density to be not less than 98%. If the density is less than 98% then a Hold Point to be raised for the nonconforming Lot.
9676ae89-d884-5414-b875-8640a92ab949 | note | Reference Documents - Beca Spec 002 13.10.1, 13.17.3.6
8c142d85-2d87-5fba-bcaf-b81cf7214dbc | note | Inspection/Test Method - AS 1012.12
699297c0-a312-5aaf-8494-759917f169c4 | note | Record of conformity - NATA Test Certificate
96dab2b9-b40c-59ca-a412-382d18e893d8 | note | HP
360145fd-647c-5054-9656-c4ba6b553063 | note | Responsibility - Project / Site Engineer, Principal’s Representative
666d2443-3749-5d7a-9a1c-0e472a7d14bb | date | Date Completed:
ece3e311-0c3f-4fba-8f66-ecb2ca20e876 | signoff | AUTHORITY HOLDPOINT
19706174-acba-4f32-a556-9d706fc7e282 | checkpoint | 5.5 - Testing Records
063e25ab-0b06-5f4b-aada-48c43a54a028 | note | Frequency - During works
920f3643-3897-547a-9edc-a08af95f34f2 | note | Acceptance Criteria - Within three (3) weeks of completion of the Works, the Contractor shall supply two (2) copies of a report detailing the results of all quality control and testing undertaken.
d9ef0c7f-0d58-516c-8678-ca24c8756a61 | note | Reference Documents - Beca Spec 002 13.17.4
6c35228b-0aa6-54e5-94c2-f2e8784f97f0 | note | Inspection/Test Method - Verify
4c883190-17eb-5617-8001-1c778157c280 | note | Record of conformity - This ITP Signed
e68bc714-671d-5ed5-a051-d8179d95a353 | note | HP
8b8e84ca-616c-59fc-a610-56eeb0503ed9 | note | Responsibility - Project / Site Engineer, Principal’s Representative
1895af9d-ad24-553e-b0e3-93a6ef5f869c | date | Date Completed:
4a36c140-21b2-4a2b-a784-0bc385adbb65 | signoff | AUTHORITY HOLDPOINT
d711f7e7-c7d5-479f-be7c-4355519473d9 | checkpoint | 5.6 - Protection of Layer
24b8d90e-66b7-58b0-9f36-b3ae516dbb09 | note | Frequency - Prior to placing subsequent layer
485c7c4a-6d49-5efc-b6db-01b933afb611 | note | Acceptance Criteria - The Contractor shall protect the HESLC from damage until surface layers are placed. The layer shall not be covered by any further pavement layers under it has been accepted by the Principal’s Representative.
79615dd0-439e-585a-809f-a38198c4a0ff | note | Reference Documents - Beca Spec 002 13.16
297329e7-d81f-56b8-86c1-51f357a9bb22 | note | Inspection/Test Method - Verify
17eade7b-1b04-5cb6-984c-a27b2470e231 | note | Record of conformity - This ITP signed
75dae2b9-d1bf-5796-8a8e-dede46d87257 | note | HP
68d21345-fb7c-5b5f-bc54-aba360ab5f9d | note | Responsibility - Project / Site Engineer, Principal’s Representative
da4a7eb1-e932-5eac-ae88-e84ab23f68f1 | date | Date Completed:
22ceabd1-017f-4aa0-8cea-6d27a135d9eb | signoff | AUTHORITY HOLDPOINT
363ad996-7d75-43a6-aaf5-3344a19cc577 | checkpoint | 5.7 - Removal and Replacement of Defective Pavement Areas
3d0d5f43-8940-51d8-a952-03bed5b29970 | note | Frequency - After completion of works
bdce08f2-e264-5753-8632-35a84e07a7a1 | note | Acceptance Criteria - If required, defective pavement areas shall be removed and replaced as specified herein with pavements of thickness and quality required by the specifications.
5fe8f3a8-d4f6-5512-98d4-d9d20c24efd4 | note | Reference Documents - Beca Spec 002 13.13
bf2d7e60-a9a4-5b2a-8fba-714f41a1b796 | note | Inspection/Test Method - Verify
fe6a6ce0-8a8c-5a7b-ab9b-619775918fbf | note | Record of conformity - This ITP signed
db99968f-a872-5fd5-92bc-a381d79af903 | note | HP
76f382d2-7b39-544d-9219-e8db84c0c486 | note | Responsibility - Project / Site Engineer, Principal’s Representative
7c4db7a6-e8d3-516d-ab5b-f2c780fe2e77 | date | Date Completed:
a9bb2736-b53f-4e46-a4d2-82b7952032ca | signoff | AUTHORITY HOLDPOINT
d4b3bc14-209d-4ad8-a59b-994cf644c80a | checkpoint | Final Inspection
fb09fa88-8452-58fe-9547-4a9286c54640 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
c968d22d-31b1-58c7-bbdd-ee3958476419 | textbox | Print Name:
77552f1a-bb76-5cf3-a1fd-d5ec1f4d22fb | textbox | Position:
70826dfb-3325-56fe-b490-9de374be0465 | date | Work Completed On:
253be1d8-576f-5155-a005-1f7e75432430 | date | Date:
c897c68c-2835-4240-8263-e069ecf8db84 | checklist | FH-ZU2-QU-ITP016 - Asphalt Production - Airport Mix - Rev 0 | itp | ITP016 - Asphalt Production (Airport Mix)
b41961d5-4119-4626-b3fc-679d1745872b | section | 1.0 - General
213a28e7-7ceb-47e1-8bd3-6d8b4a54334c | checkpoint-no-value | 1.1 - Submission of ITP
bdb86153-7552-500e-8f93-f680066d86a0 | note | Frequency - Prior to commencing works
fc00ea1a-bdb0-535e-96d9-d1d31af385b1 | note | Acceptance Criteria - All relevant ITPs to be submitted to the Principal’s Representative.
de394c33-05bc-56eb-b400-797193b958f6 | note | Reference Documents - AfPA Sec 4.3 Cl 14-18
3e8e4dc0-efa5-5a4f-949b-73676461d3fa | note | Inspection/Test Method - Verify
107a0054-60a9-5b95-b574-dc4a1b8e6037 | note | Record of conformity - Aconex Correspondence
618aa47f-38a3-581c-9ddf-46f3bd9d4de7 | note | HP
0928a277-eb96-5151-9126-d20f482b2bd6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
62f5f381-fcd5-5ddb-ba64-a88d9b1c19f6 | note | Principal’s Representative - BecaCPL-GCOR-001247
8cf1fee8-4ef3-557f-8b06-e87675881549 | date | Date Completed:
5e1b307b-9f93-42bc-8656-f2bc5f0a1a88 | checkpoint | 1.2 - Change in Mix Design
e0b10024-a57f-595c-92fc-6f472f6baf9f | note | Frequency - During the works
ec91254c-1b34-50a6-b95f-ffb034761db0 | note | Acceptance Criteria - Any change in the constituent materials or mixture design must be immediately reported to the Principal’s Representative. The Contractor must detail the proposed mixture design verification testing to ensure that the performance of the asphalt has not been adversely impacted by the change.
e82de9c5-6859-505d-b24c-def456c82a7e | note | Reference Documents - AfPA Sec 6.2 Cl 75-77
96f2221c-f401-564d-b7ea-637f3a01a5a5 | note | Inspection/Test Method - Test Method and Results
88837a84-5897-5cbe-bbd8-233af8d90d14 | note | Record of conformity - Hold Point Release Form
9cc8679a-a8f4-5e6b-adc4-24c1c650aae4 | note | HP
1213d8f5-3664-56cb-a4ca-c27548a507f9 | note | Responsibility - Project / Site Engineer, Principal’s Representative
d9dae5ca-98f6-5bb8-b964-5dbe4744915d | date | Date Completed:
e5c6366a-eea3-42d9-81e3-89b1aa01192a | signoff | AUTHORITY HOLDPOINT
14f868aa-5be4-4a6f-ae49-8b593c5881e2 | section | 2.0 - Manufacture of Asphalt
5cffe477-9835-40f4-833b-d716ad63ccd3 | checkpoint | 2.1 - Monitor and Control Asphalt Manufacture
1d2ab844-92d2-551b-979d-377b158615e8 | note | Frequency - During the works
588c88cd-202e-502d-aab3-be6702e9080a | note | Acceptance Criteria - The Contractor must produce asphalt to be consistent and uniform in temperature, and composition, consistent with the approved Construction Procedure.
7b52b539-ae14-51f8-a6f0-92142028951e | note | Reference Documents - AfPA Sec 9.1 Cl 138 - 142
01bb9c2a-1212-587a-8ace-2151d55c75c2 | note | Inspection/Test Method - Plant Process Controls
845fa0bd-025a-5dc3-a636-57f73d7a3890 | note | Record of conformity - Process Control Records
6534fbfc-a7fe-54a4-bde2-9b45bd3c5cc0 | note | TP
4c1df650-8e8f-5e9f-990e-52b6fa0c6846 | note | Responsibility - Laboratory manager
3cabcf51-1b16-5945-857e-4cd8d85a29f4 | date | Date Completed:
511eb577-fa50-42cc-b3a8-d197a255adab | checkpoint | 2.2 - Conformance of manufactured asphalt
edd20ad6-d43e-5830-8382-3a5c95ded1bb | note | Frequency - For each truck load of Asphalt
fd7ce31d-4a67-5830-a029-de1dea6cf910 | note | Acceptance Criteria - Segregated or not fully coated asphalt must not be used in the works. If required, the Principal’s Representative is to be advised of steps to be taken to remedy the non- conformance.
484d2af3-cfb0-5440-8294-2492c5b66ce1 | note | Reference Documents - AfPA Sec 9.1 Cl 142
a30ed5bc-78e8-5e2b-a59c-cdb36be3f79e | note | Inspection/Test Method - Visual
d91deb6b-787a-51e6-bfa0-97cfad63e1df | note | Record of conformity - Delivery Docket
850c1bda-5498-5ec3-9b5f-5242a738cb05 | note | HP
29139b30-193e-52cf-8c06-58f204891791 | note | Responsibility - Quality manager
b1c4df93-e48c-5001-a2ec-19ee9eaa9f91 | date | Date Completed:
ba1a3238-cda9-4991-9356-545f961e6fe1 | signoff | AUTHORITY HOLDPOINT
3b597e55-788b-442f-8b0a-52853d6ca78d | section | 3.0 - Sampling and Testing during Asphalt Production
23ccaa9d-a2a0-4bc0-b95c-995f35d929ee | checkpoint | 3.1 - Coarse Aggregate Testing
a589ffa6-3941-5878-81a1-9c3e11de7ecd | note | Frequency - During the works at prescribed frequency
278d875f-47d6-5154-a150-a69d627c22ba | note | Acceptance Criteria -
ed80d4a3-3ed5-5dc7-8320-d5fde476417b | note | – – – – – – – – –
02e8c6ae-1ce7-5ac3-b686-f17a00e63c38 | note | Test property ¦¦ Test method ¦¦ Test frequency
bd30ab7c-fd80-532a-8650-e77f51cb143b | note | – – – – – – – – –
5a6ff7b8-a14b-55e8-a820-b41edf1676ec | note | Particle size distribution (grading) ¦¦ AS 1141.11.1 ¦¦ 1 test per 500 tonnes aggregate
f3373b76-1de8-53eb-ab7f-140e9f5e7925 | note | Material Finer than 0.075 mm in Aggregates (by washing) ¦¦ AS 1141.11.1 ¦¦ 1 test per 500 tonnes aggregate
8def2738-96b2-5c0b-908e-c0c4a82729ee | note | Flakiness Index ¦¦ AS 1141.15 ¦¦ 1 test per 1000 tonnes aggregate
4585bbe8-3fc7-5b68-b719-fc803f891366 | note | Weak particles (including clay lumps, soft and friable particles) in coarse aggregate ¦¦ AS 1141.32 ¦¦ 1 test per 1000 tonnes aggregate
90fdd0c6-802a-5fa3-8db6-bb24d2371ebd | note | Particle density ¦¦ AS 1141.6.1 or AS 1141.6.2 ¦¦ 1 test per 2000 tonnes aggregate
5ae59ed8-0955-5e80-887a-3d5192b95415 | note | Water absorption ¦¦ AS 1141.6.1 or AS 1141.6.2 ¦¦ 1 test per 2000 tonnes aggregate
7a522877-0447-5986-95e1-4127f3c85984 | note | – – – – – – – – –
10128205-fe76-5770-a3e3-1b69eaf63b66 | note | Reference Documents - AfPA Sec 11.2.1 Cl 187 - 190
22ad8606-c742-51d8-989f-083af10caed0 | note | Inspection/Test Method - Test Method and Results
4da7247d-04bf-532a-82f2-6b3ca73c6f26 | note | Record of conformity - NATA Test Report
7dc3e140-2984-5312-8b1d-c4635d723512 | note | TP
f4aa7687-ab12-5718-82ee-824f34ce1a89 | note | Responsibility - Laboratory Manager
b380921e-6cc1-5dd4-b6f4-a949f56f6ef5 | date | Date Completed:
6eb9dd08-65e0-4eb0-aebc-e2750aab3017 | checkpoint | 3.2 - Fine Aggregate Testing
c6ed84fb-d0dc-5b5c-b7b2-50640acfa70a | note | Frequency - During the works at prescribed frequency
380f506a-f8ef-5887-bbe3-6fa922809534 | note | Acceptance Criteria -
0ac214ed-4103-5c42-9c7e-cea4cba6b163 | note | – – – – – – – – –
a3fac0a9-418a-5f2a-beff-5dc638a04395 | note | Test property ¦¦ Test method ¦¦ Test frequency
31505897-1742-57e8-9cd7-5a6a6546ab1c | note | – – – – – – – – –
7b01bf2f-7f4c-546a-9579-49fb4c964e28 | note | Particle size distribution (grading) ¦¦ AS 1141.11.1 ¦¦ 1 test per 500 tonnes aggregate
f2fd70b1-48a4-575a-a434-edd443668121 | note | Particle density ¦¦ AS 1141.5 ¦¦ 1 test per 2000 tonnes aggregate
5f189cf0-5ea0-5134-9622-cf4d4f1f49f6 | note | Water absorption ¦¦ AS 1141.5 ¦¦ 1 test per 2000 tonnes aggregate
421ede66-372b-5958-b960-7c97ea60a58b | note | – – – – – – – – –
2a8304d3-b91c-5f6d-8e11-c8e70d1bf852 | note | Test property ¦¦ Test method ¦¦ Test frequency
43cd3dc0-a854-555b-8a3c-5519754a65b1 | note | – – – – – – – – –
30ad53a0-d68a-5791-aabe-b01e7c757620 | note | Plasticity index ¦¦ AS 1289.3.3.1 ¦¦ 1 test per 2000 tonnes aggregate
d10de4e5-121e-5b87-be74-86104cc76a15 | note | – – – – – – – – –
7e0de98a-14c5-5b0f-a8b5-8aaf55f975ef | note | Reference Documents - AfPA Sec 11.2.2 Cl 192 - 196
a3f40e26-1053-5c1f-8c11-0aa7b4538e66 | note | Inspection/Test Method - Test Method and Results
60812e7c-09a0-543a-92b8-89ccf51aa220 | note | Record of conformity - NATA Test Report
7461fcd1-5fcc-560f-9166-10876c624148 | note | TP
22e1719d-8c71-5334-96a6-3aeca69cd5d6 | note | Responsibility - Laboratory Manager
8c63fffa-2dc6-5c74-a4ee-023c06a75be6 | date | Date Completed:
4033ea5a-2881-4b8a-a312-b6775b38ad27 | checkpoint | 3.3 - Binder Compliance Certificate
bebb093f-d2cf-57d0-ba1b-981fcb1628ff | note | Frequency - Every Delivery to Production Plant
0b00c7ab-15be-59e2-a39b-d3c9a7b27cef | note | Acceptance Criteria - A test certificate to be supplied for every delivery to the asphalt mixing plant.
b9d9ab14-df05-56cc-b48c-4d8a0eb8f4b0 | note | Reference Documents - AfPA Sec 11.2.4.1 Cl 200 - 201
0bdec986-d568-5350-98ce-bb7f458fbabe | note | Inspection/Test Method - Test Method and Results
09395b7d-1508-5b87-b5c6-318c9dcd70bb | note | Record of conformity - NATA Test Report
189a8f28-347a-5c9d-b8eb-ab4825164002 | note | TP
093d02dc-2d76-504b-ac94-593a4d60e15f | note | Responsibility - Laboratory Manager
753ebc6e-4fdb-50d6-812f-c7595c68bd22 | date | Date Completed:
dc8b5b2f-13b0-43b3-bb6a-4f7577c41a70 | checkpoint | 3.4 - Binder – Binder Consistency Testing or Confirmation
6fec9a16-ad29-5e15-9623-6e3c2cd92aca | note | Frequency - Every Delivery to Production Plant
30593879-397b-5bf5-afa3-65fd3cc173ba | note | Acceptance Criteria - For every batch of polymer modified binder production either:
9103259f-5c4d-54e5-a2e1-dbbca6a44ce6 | note | a. Provide written confirmation that the raw ingredients are consistent with the modified binder used to produce the asphalt mixture.
fa8306b5-0ed0-5994-9020-65c4d10f1c44 | note | b. Sample and test the binder according to Clause Cl 204.
10911447-8029-53b5-8bbf-d2d3e5d1330b | note | Reference Documents - AfPA Sec 11.2.4.1 Cl 202 - 206
72ee71a7-d799-5a3d-b3ef-9fece61cda14 | note | Inspection/Test Method - Written Confirmation/ Test Method and Results
04be4585-2cac-5d25-b9bf-3520fb6692c1 | note | Record of conformity - NATA Test Report
a2fdac23-cb4c-5a44-a0c8-a9832dd987c4 | note | TP
2973c3d1-6a8e-5465-9348-104299c4bfe5 | note | Responsibility - Laboratory Manager
b384c805-b2f4-58a3-a5a2-0555779d1e61 | date | Date Completed:
59c3cdd1-cd11-40e8-854d-857a37b065c2 | checkpoint | 3.5 - Binder – Point of Production Testing
bfabd134-3db0-55fa-94e2-ce9f9c34e71c | note | Frequency - Every Production Batch
26eb3474-e3cc-5363-b5e1-0b7267e44a66 | note | Acceptance Criteria - Every production batch of binder must be sampled at the point of production and tested by the Contractor, for:
28667a45-5b11-5a1d-9a66-d424e1d39fa3 | note | a. Viscosity at 165°C according to ATM-111.
a399fc40-20aa-5af1-8bb0-84136c627ecd | note | b. Torsional recovery at 25°C, 30 s according to ATM-122.
ec012d61-e469-5539-919b-4f74843b87c6 | note | c. Softening point according to AG: PT/T131.
b05dbcff-c507-57fe-9a85-aba99b79d539 | note | Reference Documents - AfPA sec 11.2.4.1 Cl 207 - 208
91bed82c-b871-5b74-a566-7ae06895b1ac | note | Inspection/Test Method - Test Method and Results
c7de522e-f3a1-5d53-af75-fdf7f0c97d3d | note | Record of conformity - NATA Test Report
c92ec59c-90be-5674-986a-e85278bfc01f | note | TP
05230d3b-6692-5df0-ae61-47bac645a28d | note | Responsibility - Laboratory Manager
2c1f15e6-476f-5584-b029-c28fef3dcc28 | date | Date Completed:
c699d2da-112f-422a-a713-5b7b435d4d55 | checkpoint | 3.6 - Binder – Addition Production Testing
2e8318e4-8141-523e-893d-46d1635ac860 | note | Frequency - Every Ten modified production batches
a3b2d33c-5853-5f24-931a-762beaf467e8 | note | Acceptance Criteria - Additional production testing must be performed at least once every ten modified binder production batches, or once every 250 tonnes of modified binder production, whichever is more often.
5f167e36-559e-50e9-bf04-0c11d11ab8c4 | note | Reference Documents - AfPA sec 11.2.4.1 Cl 209 - 212
e87de267-89c7-5062-b388-14afc99aeb05 | note | Inspection/Test Method - Test Method and Results
c355b42e-2334-589b-be88-a77530fbbbac | note | Record of conformity - NATA Test Report
8c623087-ca89-569e-b052-bd8261fa86fc | note | TP
c95c3355-3bf4-54fa-b96f-a4e51c90e54f | note | Responsibility - Laboratory Manager
55f7f0ef-447d-5c5d-aedd-063b9ece7136 | date | Date Completed:
6df675b8-46ab-48da-ade5-9575b3b8d1ca | checkpoint | 3.7 - Binder – Point of Delivery Sampling
18bbc93f-ef11-5d51-9db0-4b33cba1ddba | note | Frequency - Prior to the commencement of asphalt production
0b8178b9-e58b-5149-a803-5461b414f811 | note | Acceptance Criteria - Binder must be sampled for each delivery vessel/tank, not more than four hours prior to the commencement of asphalt production or transfer of binder to the asphalt product plant binder storage tank.
32360183-99a3-5b0d-8608-190fabf75db3 | note | ○ A minimum of two samples, each not less than 0.5 L in volume, must be obtained in accordance with ATM-101.
8021f184-afbd-57c5-8ac2-0934eddbf017 | note | Reference Documents - AfPA Sec 11.2.4.5 Cl. 213 - 219
f3d07810-5a00-51e4-9435-25503bfd7619 | note | Inspection/Test Method - Test Method and Results
1ba73a66-9465-5cc7-8693-cbf9f861638b | note | Record of conformity - Sampling Process Control Charts
91316cb1-3e3a-54b1-a7a9-0f379a71da1b | note | WP
2a2045d7-e46a-5745-93dc-2e1c6801b2c0 | note | Responsibility - Laboratory Manager
23bed54d-7d7a-5cb8-a933-3109a2d53563 | date | Date Completed:
ad006504-9776-4bb9-af98-ae8d634ec43a | checkpoint | 3.8 - Point of Delivery Binder Testing
2c481049-9b18-5ea1-93f9-25926ef860b1 | note | Frequency - Before each production shift
ec345c81-bc09-5647-9a49-362d59da0bbb | note | Acceptance Criteria - The point of delivery sample, to be retained for point of delivery testing, must be tested by the Contractor, prior to the commencement of asphalt production for the work period, for:
a0179994-a9d1-5485-b5f3-f085cb918142 | note | a. Viscosity at 165°C according to ATM-111.
5adc816b-ad8b-5114-a7b1-2014f1a7d6a2 | note | b. Torsional recovery at 25°C, 30 s according to ATM-122.
b7d1fc02-9b70-59d6-a283-89ef40c92066 | note | c. Softening point according to AG:PT/T131.
0756f038-4269-54cf-84e7-cca22efd4bba | note | Reference Documents - AfPA Sec 11.2.4.6 Cl 220 - 221, Sec 12.2.4. Cl 275
c0755e9e-7bd1-59a2-952f-e511cd0011cb | note | Inspection/Test Method - Test Method and Results
57947390-eb09-5b86-8f4e-ba5a1a96541e | note | Record of conformity - NATA Test Report
a154cded-a9cc-551c-a000-e10bc90c566a | note | HP
d809409a-ea71-5ba8-9fd9-1301e7cfce56 | note | Responsibility - Laboratory Manager
f9dc76d4-084d-5928-b723-c75872d3cd2a | date | Date Completed:
f101fb55-9014-4442-b49e-d709cb525aec | signoff | AUTHORITY HOLDPOINT
8c8f4048-3830-4521-8212-baacf0bc7a37 | checkpoint | 3.9 - Point of Delivery Binder Testing
dbf1b64a-429e-5988-93b8-4f7fb3f07ace | note | Frequency - If binder test results nonconforming
d026923b-cb3c-565f-a179-78dd41a82950 | note | Acceptance Criteria - If required, the Contractor must prepare and submit a disposition regarding the binder point of delivery test result for approval by the Principal’s Representative.
f8f9e935-37e6-528c-8642-930dbf3beb34 | note | Reference Documents - AfPA Sec 12.2.4.6 Cl 220
3a6fc9c6-d9b2-5bdb-95dd-b90daee15515 | note | Inspection/Test Method - Test Method and Results
b29f90e5-38b4-5367-ad4f-9f3bafe0e921 | note | Record of conformity - NATA Test Report
6daceb26-ed63-5010-b6cd-20b47aba59bc | note | HP
e8975e6d-8ed6-587b-b772-b303da3efae0 | note | Responsibility - Laboratory Manager
c4a30661-a1be-5324-85ff-efcd3cbe1721 | date | Date Completed:
a7411e21-30a6-4bcb-b471-2825cd91a494 | signoff | AUTHORITY HOLDPOINT
257a3c60-7c42-46ae-8e04-7956a9eff190 | checkpoint | 3.10 - Tack Coat Testing
1a4ad729-36ee-51c6-ae73-bae92326454b | note | Frequency - Every Delivery to Site
8c6e8380-eadd-591a-9eb0-3cec33dedf9d | note | Acceptance Criteria - A test certificate which demonstrates that the tack coat complies with AS 1160 or approved modified tack coat production properties, must be supplied for every delivery to site
5e000a3f-e3d8-567c-bc44-dcb03e02b32f | note | Reference Documents - AfPA Sec 11.2.5 Cl 222
19e722d2-5038-514a-a51d-893baed51deb | note | Inspection/Test Method - Test Method and Results
c1b8d57c-8a01-5186-a49d-904ecd63bd2f | note | Record of conformity - NATA Test Report
9f89b204-d8c9-586c-862f-1fafca77c1fc | note | TP
46478128-8323-5fb6-b96a-d99f22ca1deb | note | Responsibility - Laboratory Manager
0b8bac05-3628-5471-a51b-abbcdda5d3a2 | date | Date Completed:
da8f8b5c-2011-4d4a-8168-a2611612fb53 | checkpoint | 3.11 - Asphalt Production Testing
6d0c45b3-1fdd-590a-ab81-96201165568c | note | Frequency - During each production shift as prescribed by Table 16
74559471-b76c-52c9-96e3-486587055b7c | note | Acceptance Criteria -
9e8a9a21-f829-590e-bc3b-784ee8a02205 | note | – – – – – – – – –
fa40e1d4-6611-51d0-b793-05a1ed5bbe39 | note | Tonnes of Asphalt in the Lot ¦¦ Number of test sets
03423c16-0592-5b0a-9f07-5f1b9ae5ac8c | note | – – – – – – – – –
3b5af6e6-edff-5f8a-87a2-14888f2dba2c | note | Not greater than 300 tonnes ¦¦ 2
09f194a9-40f2-5453-a377-91cf8d4036c3 | note | 300 to 600 tonnes ¦¦ 3
0b1c640a-bc2d-56bc-8871-cb9f3f3ff083 | note | 600 to 1,000 tonnes ¦¦ 4
c791ee2f-e7c4-5d5e-ab4f-349cae9f5e41 | note | Greater than 1,000 tonnes ¦¦ 5
cbe5cff0-25e7-583f-9bcc-4499dc85e068 | note | – – – – – – – – –
ed4837bc-1654-5cca-85ea-a383853347d3 | note | Reference Documents - AfPA Sec 11.3 Cl. 222 - 223
2f4a9018-277e-51f7-940d-b48eb4c5194e | note | Inspection/Test Method - Test Method and Results
544dff85-7e8e-5eeb-b052-a2ac149f2350 | note | Record of conformity - NATA Test Report
4e629fe5-85c1-5a40-9ac5-afe0e13cbd8f | note | TP
5c0fe24c-e79b-58d2-9c0f-30063f210cc8 | note | Responsibility - Laboratory Manager
28ead5a8-bd0f-5af9-8aaa-f97965b9c592 | date | Date Completed:
764137e8-9d81-4d10-8dc9-0ea4dc20ad92 | checkpoint | 3.12 - Shift Usage Calculations
faaf521b-92a6-50df-8535-ec736841d65a | note | Frequency - For each Production Shift
24e7f157-c004-532f-a3ab-7507c5741919 | note | Acceptance Criteria - For each production Lot calculate; bitumen usage, mass of asphalt produced & average bitumen content
f5ac51c1-f9e3-5d01-a45d-4f2d89392e1a | note | Reference Documents - AfPA Sec 11.3 Cl. 231
3b0a2aee-502a-5ef3-8950-a639eceab280 | note | Inspection/Test Method - Test Method and Results
2af0204a-8661-5666-b8f9-cdb8cc23aa95 | note | Record of conformity -
d4a1286d-976f-55f0-ae4c-2cf06b4bfd7c | note | TP
e218ab39-4df2-5c12-9dcd-893f9f6c4899 | note | Responsibility - Quality Manager
8730c74a-c1b2-5223-9292-cac37675767c | date | Date Completed:
9c429be7-1d6e-4cd7-89c2-88c6e935d0dc | checkpoint | Final Inspection
446f4f0d-6b42-57b4-9d71-8605f0ad6a62 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality/System Procedures and verifies lot compliance with specifications.
c4ccd037-d93b-5d43-bc88-6900cdd0f281 | textbox | Print Name:
4d872769-1e8f-57df-8f5e-dff23968f387 | textbox | Position:
c6caefae-8487-5714-b3b5-0f639054a1ca | date | Work Completed On:
0fb1d074-49ad-5ce7-aa18-408c0e89bee0 | date | Date:
708316ac-02fb-483f-95b2-466bceb8bac2 | checklist | FH-ZU2-QU-ITP017 - Asphalt Production - 14H Mix - Rev 1 | itp | ITP017 - Asphalt Production - 14H Mix
f86777f9-a770-4934-a24b-541bc96183de | section | 1.0 - Production of Asphalt
eaaec954-116d-4024-87db-232a2a30ee5f | checkpoint | 1.1 - Temperature
2136a98f-0f15-5f52-85c7-06d7028892b8 | note | Frequency - Every loaded truck or at intervals of 15 minutes if more than one truck is dispatched in 15 minutes.
e26f2526-7f2a-5df3-9364-36f41f40718b | note | Acceptance Criteria - ≤175°C
68626ca3-b1c7-5a27-a698-395cb41050cb | note | Reference Documents - Section 407.11(a), 407.15
2abcfc10-e37c-5778-b206-1113eefbbd80 | note | Method - Thermometer
0251ebb7-b7fc-5bc0-98fc-7c23769607e9 | note | Record - Load inspection sheet / docket
d036dbfb-a5e3-5dd5-8486-2e3efa8d4ddd | note | Responsibility - Plant Operator / Technician
88336bbf-a546-5acd-bd41-83c71158ad15 | date | Date Completed:
743a8212-06f3-426a-a48f-e99cdecb310e | checkpoint | 1.2 - Visual inspection for segregation, uncoated particles, separated binder, excess binder or overheating
1018d5ac-5d5f-59ff-9719-9e106c2ca447 | note | Frequency - Every loaded truck
2ae6731c-f507-5d24-bdcf-a9be66dd32f1 | note | Acceptance Criteria - >95% coarse aggregate coated with binder, no obvious separated binder or uncoated particles
0c1149d4-90aa-5652-801f-03844b21b09f | note | Reference Documents - Section 407.11 (b)
adfe9b46-8eea-5c12-9109-db5859473831 | note | Method - Visual check
10402f32-95fa-5554-883b-a881b5bf552d | note | Record - This ITP signed
d2106aff-5e01-584a-9213-6f8f39e37029 | note | Responsibility - Plant Operator
cfd97c38-5421-5620-b1e4-4c96a69d1469 | date | Date Completed:
d78471cf-c969-4471-928b-c942877fdcee | checkpoint | 1.3 - Maximum density
02444fba-2830-54bb-a705-ab1583a61bc7 | note | Frequency - On every production day
74334de1-e815-5bfb-ba81-3b67c6d6ca11 | note | Acceptance Criteria - ± 35 kg/m3 of its 6-point rolling average
65f1c12f-22c0-507b-bfb8-0bb6ac8f984b | note | Reference Documents - Section 407.11(e), 407.15
a123ccd7-18f7-5523-aa3b-7c9103a7fc6f | note | Method - AS2891.7.1
9ef899f2-fffa-5675-89dd-74a9925b4bc0 | note | Record - NATA-endorsed test report
aa50b84a-8988-5a34-b4a3-e914bc380ae0 | note | Responsibility - Technician
27d00282-d869-5768-a3a1-3cb441453f77 | date | Date Completed:
9530b9eb-8080-49ad-9361-898907e44dbb | checkpoint | 1.4 - Binder content
d5c44728-de7b-56e1-855e-7132303988d9 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
4093e520-9d53-5a08-a182-7516042f0d97 | note | Acceptance Criteria - ±0.3% of mix design specification
b00a84b8-7aa1-5e4b-b901-b5a198eaa074 | note | Reference Documents - Section 407.10, 407.15, 407.11
dd8ab117-c9a8-524c-81e9-d173e9ff402e | note | Method - AS2891.3.3 or AGPT/T234
8b6ffe09-c588-5b80-b826-7a1bbfd2b339 | note | Record - NATA-endorsed test report
6d97f0fd-6496-5194-9a83-17f5d888cca0 | note | Responsibility - Technician
df8027cf-71ed-57f1-9f23-ac47475ea03f | date | Date Completed:
b29a3f10-60ef-48ca-a517-26fc00581ffc | checkpoint | 1.5 - Full sieve analysis
f0673b06-a08c-5b88-9219-306a17a575b2 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
1c0c29a2-9aa6-55d5-8694-2f7c3d001351 | note | Acceptance Criteria - See Table 1 of this document
b62f08c9-2498-58db-b7ff-6c1c4882336d | note | – – – – – – – – –
ad595973-74f5-559f-8826-1c783fafd1f9 | note | Table 1: Production tolerances for mix grading (Table 407.101 in DTP Section 407)
1986e833-45bb-5d3d-bfb7-0734c5f003d5 | note | Sieve size AS (mm) ¦¦ Size 7 ¦¦ Size 10 ¦¦ Size 14 ¦¦ Size 20
a562349c-9085-51b6-97aa-5c2969948449 | note | – – – – – – – – –
750b82b3-32bf-5faf-91b5-d1a2f4954f90 | note | 37.5 ¦¦ Nil ¦¦ Nil ¦¦ Nil ¦¦ Nil
63bbcf48-8dc4-5e00-9708-fe1412642bf7 | note | 26.5 ¦¦ Nil ¦¦ Nil ¦¦ Nil ¦¦ Nil
feff2b7e-4e12-5cdf-a6ba-579ab2e97326 | note | 19 ¦¦ Nil ¦¦ Nil ¦¦ Nil ¦¦ ± 6
309ca4e4-d840-5f85-b6fe-28aecd1ccad3 | note | 13.2 ¦¦ Nil ¦¦ Nil ¦¦ ± 6 ¦¦ ± 6
4e5e2d66-ef24-5631-929a-709514186e50 | note | 9.5 ¦¦ Nil ¦¦ ± 6 ¦¦ ± 6 ¦¦ ± 6
61f2e34a-5c7a-5b05-9751-9c286908d8ac | note | 6.70 - 4.75 ¦¦ ± 6 ¦¦ ± 6 ¦¦ ± 6 ¦¦ ± 6
d5026ce2-fc7c-5121-88f8-cad462df8a5e | note | 2.36 – 0.600 ¦¦ ± 5 ¦¦ ± 5 ¦¦ ± 5 ¦¦ ± 5
4d6a97d1-0796-5cc4-a5e9-8e2ba8104595 | note | 0.300 – 0.150 ¦¦ ± 3 ¦¦ ± 3 ¦¦ ± 3 ¦¦ ± 3
f99a305b-efb0-53e1-92c0-1f24f9fe98c1 | note | 0.075 ¦¦ ± 1.0 ¦¦ ± 1.0 ¦¦ ± 1.0 ¦¦ ± 1.0
5a9d41f4-d17e-5767-b2c9-da52f87f5a97 | note | – – – – – – – – –
b57ad8a8-eee3-5246-8447-20280811450f | note | Reference Documents - Section 407.10, 407.15, 407.11
646a96cf-e543-562d-9a24-918a99a87666 | note | Method - AS2891.3.3 or AGPT/T234
c6a0205c-ae02-5244-82e2-8f57d4b75a7c | note | Record - NATA-endorsed test report
29eeeffa-264f-51d2-b315-51044e0fd4ff | note | Responsibility - Technician
3d932bf7-07d0-54d7-87ae-45508e749800 | date | Date Completed:
763b54f1-29b7-4eaa-bac1-52b4bc08f122 | checkpoint | 1.6 - Moisture content
863688e9-5ca2-5f3a-9a41-3585e2198bb7 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
5bd2c25d-e131-50c2-a5c1-637769a96ab7 | note | Acceptance Criteria - ≤0.5% moisture
2645a2de-a383-5afc-8501-45b50203adf6 | note | Reference Documents - Section 407.11 (b)
f3fb828c-12b7-546e-9438-2a91b5723f9d | note | Method - RC 211.01
5a4cf3ae-3975-59bf-8852-70fe1e08e5c2 | note | Record - NATA-endorsed test report
286f3db1-4a4b-5d83-9a79-524eb1cb5792 | note | Responsibility - Technician
a68a7adb-9b0c-55d8-870a-5ca2bc037fab | date | Date Completed:
1090299c-4a54-4d52-b60f-93012ebb2b05 | section | 2.0 - RAP Testing - RAP Level 1 and 2 (as per Table 407.121 Section 407)
2671db02-eef4-4e14-89d7-ec6052cca18e | checkpoint | 2.1 - Moisture content of RAP
fa4b27d3-15c6-506c-a591-d59718edc1a1 | note | Frequency - One test per 500 tonnes of RAP
569097ff-6fed-5066-b163-48d6b1d87dfc | note | Acceptance Criteria - Not exceeding the maximum moisture content acceptable for the asphalt plant nominated in the RAP Management Plan – Fulton Hogan Infrastructure Services. Any materials with moisture content greater than the nominated moisture content should be allowed to drain before being utilised
4d99a431-c908-5185-b14a-6bc6df2aa691 | note | Reference Documents - Section 407.13(c), FH RAP, Management Plan Section 3.2
2aca144f-9ec3-57d1-a4c4-7ce0f939f963 | note | Method - AS2891.10
b4f62afa-b0ac-5586-ab28-431dc27f1d12 | note | Record - NATA-endorsed test report
d1c25ef9-c694-5a0a-b1db-d5c3b7f9f616 | note | Responsibility - Technician / RAP Yard Supervisor
c7d86439-f754-5e47-af6c-b941c93dc36c | date | Date Completed:
6f582191-4b15-445c-a3ac-b0a7071367d4 | checkpoint | 2.2 - Binder content of RAP
31ba157a-abad-5cf8-9799-db4b3b34fd2a | note | Frequency - One test per 500 tonnes of RAP
7622cb69-d19a-50f2-953f-a94324340172 | note | Acceptance Criteria - ± 0.5 of target binder content
f27ecee2-29b3-5371-a504-1932adef6c00 | note | ○ 1 out of 10 consecutive results is allowed outside tolerance
edfb08bf-fce3-5257-afe0-62d8a94c7708 | note | Reference Documents - Section 407.13(c), 407.11
d82a0091-a207-54f1-be61-9d791adf5d16 | note | Method - AS2891.3.3
a345f482-d7b1-543f-9b56-8c2f19432367 | note | Record - NATA-endorsed test report
ae4ced9e-da1b-5cf9-b76b-df1790026fb0 | note | Responsibility - Technician/ RAP Yard Supervisor
9f1500ff-b0fe-57bb-95ad-2c2ac811d418 | date | Date Completed:
0b835721-220f-4456-a337-c8ec984de7c2 | checkpoint | 2.3 - Sieve analysis of RAP
62e86c66-0fe2-5ded-a7e2-b67de9c29e39 | note | Frequency - One test per 500 tonnes of RAP
b95bc3aa-cc43-5446-86cc-bc51c5570192 | note | Acceptance Criteria - See Table 2 of this document
bac122dd-9df9-57c0-afe8-1515bb54f248 | note | – – – – – – – – –
7efaf993-0f42-5347-b4c1-5a3f5d57311b | note | Table 2: RAP grading tolerances (Table 407.131 in DTP Section 407)
2e960692-6314-51c8-b9f7-68854cead5ec | note | Description ¦¦ Tolerance (from target grading) ¦¦ Allowable number of results outside of tolerance
8d77efa3-47d6-5346-9f34-f86b3093bfc8 | note | – – – – – – – – –
015e08a4-383d-5476-9d79-a6aaaa04dc01 | note | Passing 26.5 mm sieve and larger ¦¦ ± 10 ¦¦ 1 out of 5 consecutive results
96e479ac-1008-570a-99a3-ed582b426d6f | note | Passing 4.75 mm to 19.0 mm sieve ¦¦ ± 8 ¦¦ 1 out of 5 consecutive results
c02f4821-aa32-5c9f-a7b6-fbe8d7242eff | note | Passing 1.18 mm and 2.36 mm ¦¦ ± 6 ¦¦ 1 out of 5 consecutive results
75f728e5-4a9a-55e0-9007-ce97ab775d89 | note | Passing 0.300 mm and 0.600 mm ¦¦ ± 5 ¦¦ 1 out of 5 consecutive results
cd8d2ed2-5fc0-59b3-91a5-17264ce1ed7c | note | Passing 0.150 mm ¦¦ ± 3 ¦¦ 1 out of 5 consecutive results
9d255828-626a-56ff-810b-8ca4f640b4d5 | note | Passing 0.075 mm ¦¦ ± 2 ¦¦ 1 out of 10 consecutive results
4f29aa99-6ce8-590e-b1b0-895c58a2fe7b | note | – – – – – – – – –
1e3611a3-90df-594f-8bf4-8394902af3bf | note | Reference Documents - Section 407.13(c)
0a914e54-db27-5b23-9713-dc16c30e2673 | note | Method - AS2891.3.3
9b5e61aa-9fe1-5b70-bc66-4b2be2389863 | note | Record - NATA-endorsed test report
5682ed41-dfdc-5f26-8a7a-29957d686185 | note | Responsibility - Technician/ RAP Yard Supervisor
9ea1785d-de8f-5d23-8fcb-3f6e4d31e9e7 | date | Date Completed:
9021a7a2-e8e4-4164-a22e-154398838c07 | section | 3.0 - RAP Testing - RAP Level 2 (as per Table 407.121 Section 407)
a70a1afc-6796-4f98-a60c-b1322b06c88a | checkpoint | 3.1 - Binder viscosity
c9b859f2-2f52-526e-b046-dfd87f11dff2 | note | Frequency - One test per 1000 tonnes lot of RAP used for Level 2 mixes as per Table 407.121
638e570c-ad4d-51cb-9036-cce9b4bc8d16 | note | Acceptance Criteria - Viscosity of the blend of virgin and RAP binder shall fall within the range in table
57787fb8-7372-531d-abdf-3e0e09d1b881 | note | – – – – – – – – –
0b8c88ac-b440-5647-a9ba-da4a4e6ccc73 | note | Specified Binder Class ¦¦ Binder Blend Viscosity Range (Pa.s @ 60°C)
b2e34c0d-c16e-5e62-b89b-4ec57bc22a0d | note | – – – – – – – – –
a8c51968-b615-5b12-a5ea-5a9cbf3ba3d1 | note | C170 ¦¦ 170 – 240
ea70d51e-d6bc-5d05-8821-6ff2b17b71d8 | note | C320 ¦¦ 320 – 500
ef9cbafd-cd29-5ab5-b40f-f967279f213c | note | C600 ¦¦ 600 – 880
099695d9-d773-5540-9ee9-4cdb0b41adf3 | note | – – – – – – – – –
e9422418-3469-5762-a057-29d7ca81f80e | note | Reference Documents - Section 407.13(e)
dcab2c91-298e-5731-9c9e-3858ffc3c7af | note | Method - AGPT/T192 or AS 2341.2, AGPT/T193
d3aa5934-9e09-546f-9635-9462a80030ef | note | Record - NATA-endorsed test report
a8a5d9f8-2092-59bf-9ca1-4ea03e650e0a | note | Responsibility - RAP Yard Supervisor / Laboratory supervisor
3ee7ecb4-1890-539b-9896-1db869c75f4f | date | Date Completed:
7a651e5a-b4a3-4d04-9949-cff44d93eb3c | checkpoint | Final Inspection
2d1d16f5-5a8f-5846-878d-ffe1d9a36f89 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
3bd77594-0b9a-56f2-9d5f-cf6a79df486f | textbox | Print Name:
527695d8-93f9-50a2-abf0-56dc7bfce049 | textbox | Position:
1adf7434-14bc-5860-92a1-759173af3782 | date | Work Completed On:
095a949d-a150-58f5-8b0c-171799497afb | date | Date:
e7bc0006-0449-4020-a680-827e38c80b9a | checklist | FH-ZU2-QU-ITP018 - Asphalt Placement - Rev 1 | itp | ITP018 - Asphalt Placement
9f2884d8-204c-4a8d-8a71-c6e6449c515b | section | 1.0 - Preliminary Activities
f9f9bade-be5c-4e37-9b6f-87558c7464d8 | checkpoint | 1.1 - Check for correct documentation
a5f9aed7-8e63-5dda-9f83-59b1caf55907 | note | Frequency - Prior to commencing works
62caa993-c7b0-5913-ac1d-d31314032ddf | note | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
57a4295e-8bd6-5c03-92d4-379b93c11fa3 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
fb9ae8ff-8531-572c-9794-d1245faeae5e | note | Reference Documents - Current Revisions in Aconex or ACC
d3ea8f0f-7f2e-5f67-ae22-0da0e0523b54 | note | Inspection/Test Method - Verify
3aa525f1-e8c3-5b2b-beb4-fe2bd8f50e49 | note | Record of conformity - This ITP signed
11bb45cb-f28b-524c-b7f4-105132e67009 | note | HP*
78324ebd-00a9-5887-bd39-689ae15436c2 | note | Responsibility - Project / Site Engineer
c71ae7c0-25e9-5c3c-80c3-9f3aa604f96e | date | Date Completed:
1b0d1945-ba45-49a1-bc53-a2c6293444f9 | checkpoint | 1.2 - Implementation of all measures and controls
b68c1335-9ce2-5ac6-94fc-a2752ff12ea9 | note | Frequency - Prior to commencing works
1b6eb168-ef14-543d-8908-f5a6d134139e | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
df3f696c-f4c5-5025-ab6c-982cf912fcef | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
da5647da-699b-5876-b8fe-f39669d4cab8 | note | Inspection/Test Method - Visual Inspection
0548f38b-76c7-5d93-8856-121e4f8636cd | note | Record of conformity - This ITP signed
0c394852-2286-5f12-ad60-a4d52ee11dd6 | note | HP*
b1024191-3b75-5777-9b53-075e00e18054 | note | Responsibility - Project / Site Engineer, Site Supervisor
516afb68-8bdf-5654-8b8d-23388ae689e3 | date | Date Completed:
108cd8a0-6efd-4313-89c5-c1008ebeb015 | checkpoint | 1.3 - Plant & Equipment Check
b042bd38-3294-597e-92f2-cc1403ca2c8e | note | Frequency - Prior to commencing works
051f61f5-5ff2-5606-ba22-ca18522f21ef | note | Acceptance Criteria - Asphalt plant & equipment meeting the requirements of Project Specification.
48f08a81-f61a-50d0-bab9-26102264dde4 | note | ○ Pre-Start checks completed by operators of plant and equipment. All plant and equipment are acceptable for use. Any faults are reported. Standby equipment in place where required.
74d44a80-c7a4-55b3-a0b5-3c32b28ba157 | note | Reference Documents - AfPA Sec 7.1 Cl 91-100
2a1ccd91-733c-5faf-a811-4f132cb811b1 | note | Inspection/Test Method - Verify
022476df-5970-565f-b0a6-0aead13c9076 | note | Record of conformity - This ITP signed
b6103524-bb1a-51cc-9f50-7222fc0f4327 | note | HP*
8283dd86-33c8-5e69-b1dc-a1990bba54b3 | note | Responsibility - Project / Site Engineer, Site Supervisor
db4cb085-a78d-5ed0-86ca-f8c0812b85d6 | date | Date Completed:
0c3e6d21-8357-46e2-848b-15fe6a08b1fb | checkpoint-no-value | 1.4 - Tack Coat Material Submission
bf603bbc-8b9a-5609-9c31-24241ba39f7c | note | Frequency - Prior to commencing works
7542c7a2-bac8-55d2-a2b4-12fa0c17b7b3 | note | Acceptance Criteria - Details of the proposed tack coat and test certificates shall be submitted to the Contract administrator for review.
c1d6a3c7-51ff-5df8-b763-4eaa8513b64d | note | Reference Documents - Beca Spec 002, 9.4.1, 9.9.1
3f504c9b-03e6-5e29-8d1e-dd15d83572d3 | note | Inspection/Test Method - Verify
fd0ab66c-99df-5d4d-bcca-df381b2a263c | note | Record of conformity - Aconex Correspond ence
035dfd60-95c4-5688-8116-afff433c2dd0 | note | HP
4fff7910-1b74-5a0a-a10a-8af5a3f88971 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a0527df7-a487-5284-90be-b18ae0e82fb5 | note | Principal’s Representative - BecaCPL-GCOR-000967
3f20c2e4-acd6-5c46-b2cf-8274b8debc4a | date | Date Completed:
4953225d-5ded-4192-97fc-21a96922a99b | section | 2.0 - Tack Coat
84bc005b-5e84-4d02-90ec-b11c2423a625 | checkpoint | 2.1 - Surface Preparation
47766e02-13e2-5cf9-949f-d9989cb75713 | note | Frequency - Prior to applying tack coat
b69269c7-9b38-5d4d-9f9d-fdd746b6e0eb | note | Acceptance Criteria - Immediately before applying the tack coat and following all cold planning activities, all loose and foreign materials shall be removed from the surfaces to approximately 150mm beyond the edge of the area to be coated.
8598bb11-aa76-558e-8ec4-469626fea4c4 | note | ○ Tack coat must not be applied on a wet surface, or when the surface temperature is below 5 degrees Celsius.
8e5f6818-1379-5010-a8da-54b575cf5f73 | note | Reference Documents - Beca Spec 002, 8.5 & 9.5
a9f35569-5ae8-5b49-8339-88f474b7086f | note | Inspection/Test Method - Visual Inspection
c7adcae1-e616-5408-b0d5-cba668ad0083 | note | Record of conformity - This ITP signed
ff7d2081-f834-5ba8-970d-795e4aa5f8dc | note | HP
6801e94d-4647-5de5-b39e-d6451b1f9b61 | note | Responsibility - Project / Site Engineer Principal’s Representative
87c9411f-3137-5c10-8215-53bd51008a0c | date | Date Completed:
2a78a280-0174-461e-81e8-0f3926f5db41 | signoff | AUTHORITY HOLDPOINT
3fd7c619-20bf-40f9-9f01-fd2fb7595208 | checkpoint | 2.2 - Weather Limitations
c2a26f77-89f6-5fbb-b122-d418d308c7ba | note | Frequency - Prior to works
eadca574-9ef9-5a8f-bc24-1120ee28f823 | note | Acceptance Criteria - Tack coat shall not be applied on a wet surface, or when the surface temperature is below 5°C, or when the weather conditions would prevent the proper application or adhesion of the tack coat.
fec2bef3-c907-522c-b743-69fc7f4347b4 | note | Reference Documents - Beca Spec 002, 9.7
f901a7c3-7b05-5fc2-92a9-a008f77bd9e9 | note | Inspection/Test Method - Verify
671c43c2-4458-5f70-b0b8-852e1915d8fb | note | Record of conformity - This ITP signed
9370743f-41d9-5cc9-97b9-1ab0fc841db8 | note | HP*
e7f22c4b-8163-5d1a-96c8-4b11dcd4d120 | note | Responsibility - Project / Site Engineer, Site Supervisor
65ee4d3f-d779-580d-a277-bb8b8776c26e | date | Date Completed:
e46bd571-7112-4706-b2b3-2d357f0f9db2 | checkpoint | 2.3 - Application of Tack Coat
ef0cfcc9-1da0-50b0-b3f4-7b4274abe427 | note | Frequency - During Works
6a3523b1-20ec-55cf-b2ad-3f6b38afc9a0 | note | Acceptance Criteria - Tack coat must be applied to the prepared surface at a rate of 0.2-0.3 L/m2 of residual bituminous material, calculated at 25°C.
d869ee84-c759-57c5-a131-73ea86fff1cc | note | ○ Vertical faces of milled and excavated existing pavement must be thoroughly tack coated by hand lance or other method.
7d2587a3-26cd-58b1-b82c-36ed591a89a3 | note | ○ Tack coated surfaces must be protected from construction equipment trafficking to the extent reasonably achievable.
6d4dfb3e-ccc2-50a8-a987-933bc740eebd | note | ○ Asphalt paving must not commence until emulsified tack coat is substantially broken over more than 80% of the surface of the paving run.
53ad700b-f6d1-5d22-9382-331bbdb8c1dd | note | Reference Documents - Beca Spec 002, 9.9.3, 9.6, AfPA Sec 10.3 Cl153-156
a2538ff4-291c-58ba-a121-5252afaa2ad0 | note | Inspection/Test Method - Verify
4f2d60a1-00a6-5951-8702-849c76a20b49 | note | Record of conformity - Spray Rate Record Sheet, This ITP signed
679563c0-0697-519c-81fe-754fa5acc007 | note | WP
5cc1ec7a-434b-5737-82c9-b7243c0f60b6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
e2d25fa6-6833-5d61-a723-54a4e5a00bb9 | date | Date Completed:
64658685-fe27-4cdd-ac2b-4549a7330c9a | checkpoint | 2.4 - Test Certificates
a9a27fd4-abdd-55e4-b628-8556a7264c61 | note | Frequency - During works
ea3f92ac-7f6d-5770-b520-e1f4082498fa | note | Acceptance Criteria - If during the progress of the work the Contractor desires to use other materials or materials from other sources or materials produced from the same source using method of production different from those originally agreed, new samples shall be taken and tested and the results shall be submitted to the Contract Administrator.
810325e0-6ac2-5c81-872c-2b59960d405d | note | Reference Documents - Beca Spec 002, 9.9.1
2bf44c31-b1c7-53bc-9d70-80f6a53d8372 | note | Inspection/Test Method - Verify
de741aeb-88bd-5092-a94d-c31c91b612c5 | note | Record of conformity - This ITP signed, Test Reports
b8c777fc-0cc4-5934-ac6c-ffa5b957dc28 | note | HP
c84bbd9e-5aaa-5cb0-a7ec-460b5d7bef4b | note | Responsibility - Project / Site Engineer, Principal’s Representative
c42c3400-4221-5ffc-8501-61cf1d41b774 | date | Date Completed:
31f66bbc-f152-4adf-a435-516b83d5180f | signoff | AUTHORITY HOLDPOINT
e2542c4c-923f-4bc0-9f2a-f62375759b49 | section | 3.0 - Hot Mix Asphalt Placement
4ba75adf-7760-45bb-bb6f-355827c08a53 | checkpoint-no-value | 3.1 - Construction Trial
b84d28a8-9929-5d70-97ff-0e53d10f2b2c | note | Frequency - Prior to commencing works
4a17730b-d2bf-5cad-8d96-683cf8140c42 | note | Acceptance Criteria - A construction trial must be completed as per the requirements in the specification.
c5772dad-ba86-5906-8dc2-e89e0a85ca84 | note | Reference Documents - AfPA Sec, 8.3 & 8.4
e6511b96-c544-5242-bf12-12564331e895 | note | Inspection/Test Method - Verify
c465d417-fa23-5b16-9644-7448e5707044 | note | Record of conformity - Aconex Reference
5ebc8428-cf20-5234-8445-d1c3b84bb012 | note | HP
2d827f24-bba3-54dc-89ea-c194c2cd0ae7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
7ab1ce8b-0f5b-503a-b4b3-cc522aea7e6e | note | Principal’s Representative - 14H Construction Trial: DCWC Mgt-GCOR-010226
dfd0770e-5ac8-5069-9054-ad0a062e6391 | note | ○ A10E Construction Trial: BecaCPL-RTRFI-000265
b8e798a4-b66e-5aae-a948-b342729a707b | date | Date Completed:
5df4a6be-d7f6-4f8e-9d1b-509eca6c9074 | checkpoint | 3.2 - Ambient Conditions for Placing
79839c47-2778-51bc-86d9-fd04a46d1e58 | note | Frequency - Prior to placement
c2838b20-7eb8-5a2b-b2d9-e61b4457693d | note | Acceptance Criteria - Asphalt must not be produced and constructed during weather, or expected weather, that may be detrimental to the quality of the finished asphalt surface layer(s).
bc654fdd-f7b9-5290-8c58-718e4fedb8b3 | note | ○ If required, where the existing surface temperature is below 15°C, the Contractor must develop and submit cold weather construction procedures for the Contract Administrator approval.
d73b971c-0d21-59af-9adf-0dbe751cc05b | note | Reference Documents - AfPA Sec 10.1 Cl 145-146
09f2a1d3-41d7-547a-85ca-7e75c1d9869a | note | Inspection/Test Method - Infrared Thermometer
55b086f1-c840-5443-b5be-c5b98739870c | note | Record of conformity - This ITP signed
73f0e451-f488-5e78-8bd8-07f9e6e6cbfc | note | HP
14286aa6-2b9a-5dcf-802f-e0b1f5365bae | note | Responsibility - Project / Site Engineer Principal’s Representative
5b5620cd-5938-5f07-986d-05d56fbd3ce7 | date | Date Completed:
d34b09a5-878a-41bc-899d-f558efdff5ab | signoff | AUTHORITY HOLDPOINT
15e52648-fbe7-4534-b4b4-46fe42c3932e | checkpoint | 3.3 - Surface Preparation
79e3704d-42f4-5643-8fb8-729e37e6326d | note | Frequency - Prior to placement
3ce9eecb-71b2-5e1a-8f8e-1c7d03133187 | note | Acceptance Criteria - The surface on which the asphalt is to be placed has been jointly inspected by the Contract Administrator and the Contractor, and it is agreed to be suitable.
fd35128b-8025-5291-88b5-5a87bb4468f4 | note | Reference Documents - AfPA Sec 10.2 Cl 147
84e8b29c-c59b-51a3-9526-afa88ef46280 | note | Inspection/Test Method - Visual Inspection
4983c872-056d-5676-a87b-609a7b4f0aa0 | note | Record of conformity - This ITP signed
1f503468-09a6-5523-b76f-27db8e2f5976 | note | HP
d41d03ea-96de-552d-9569-834480f7b52b | note | Responsibility - Project / Site Engineer, Principal’s Representative
9232169d-ad2c-574a-935c-862b37671421 | date | Date Completed:
5a4d6fa6-eff8-4908-aeec-2541fc0bd6ee | signoff | AUTHORITY HOLDPOINT
142b296d-56a3-4576-9c5c-0b29f6f3bbfa | checkpoint | 3.4 - Asphalt Placement
0f3da3cd-bc5d-5689-aa59-8652039ec1dc | note | Frequency - During Paving
76ec15fc-338e-541d-b5a2-5821ed495eb9 | note | Acceptance Criteria - The following processes to be monitored with the Contract Administrator to confirm consistency with Construction Trial:
6e637df4-83cd-5d3e-ab89-19ece676732f | note | – Roller patterns
0a89e57f-8c51-580f-8e00-935758dde67d | note | – Surface texture within paving lanes
71c92926-13dd-5961-8478-373fe002cb12 | note | – Surface texture at the joints
134582bb-dff3-587c-94b9-7575c09e6eff | note | Reference Documents - AfPA Sec 11.4.1
cb4e5f95-4459-54f8-a91f-0ee027ab93c3 | note | Inspection/Test Method - Verify
82daf4a7-2650-5b15-8fd6-5a714933d924 | note | Record of conformity - This ITP signed
85015cef-7985-54f2-9768-8b468e2cc983 | note | WP
5094bbd6-ac4a-5586-8670-9b177d36c2b7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
870b5305-8aa7-5028-9197-2a9d4405b024 | date | Date Completed:
5a7a5f30-cd93-45ca-a0a3-4fd0ba23f096 | checkpoint | 3.5 - Longitudinal Joints
619d9178-dc5d-52cb-bf6b-859e782302fa | note | Frequency - During Paving
0925c409-735c-560d-a580-ebd41d244628 | note | Acceptance Criteria - All longitudinal joints shall be constructed as hot joints (exceeding 125°C upon placement of the adjacent paving run) unless restricted by staging constraints or in constrained working areas.
0e2ef384-b47f-517e-8f79-387d9bbd0b0a | note | ○ Gas fuelled infrared joint heaters may be used to reheat the joint and create a hot joint where the measured temperature has not fallen below 90°C.
c9d82ab5-3da3-5f24-82f0-df129a7af676 | note | Reference Documents - Beca Spec 002 10.5, AfPA Sec 10.4.4
39df120d-2163-5a39-a86c-214aedbd31ae | note | Inspection/Test Method - Verify, Infrared Thermometer
171bf6f6-35cb-557a-8111-8fab28ad0d77 | note | Record of conformity - This ITP signed
4adb2a41-7300-5dcf-ac31-251a81331fa4 | note | HP*
60547fd5-58c6-535d-a8a3-c9436bb0bd51 | note | Responsibility - Project / Site Engineer, Site Supervisor
934ed53a-3fa4-54ea-a96c-11ef015fef21 | date | Date Completed:
9d1b5089-fbca-4929-acef-8c10a2267407 | checkpoint | 3.6 - Surface Finish of Wearing Course
21fcb48b-1259-5831-ab67-4ea5876059c7 | note | Frequency - During paving and after final roll
5596fd42-29d0-5d18-bd3e-850dfbe73e60 | note | Acceptance Criteria - The finished surface of the asphalt must be a tightly bonded, closed textured, surface of uniform appearance, free of dragged areas, cracks, segregation and open textured patches. Joints must be tightly closed. Surface finish must be consistent with the asphalt construction trial.
c5ba9a73-63fd-5815-b26f-6871758a4b4f | note | Reference Documents - AfPA Sec 12.4.1 Cl 288-291
a35847a5-a752-5894-a474-1d74a5aeda7e | note | Inspection/Test Method - Visual Inspection
8845183d-ac15-504f-9673-cc51e4e2a444 | note | Record of conformity - This ITP signed
d8d46058-0cd3-562d-abc1-6baaf6ef4c00 | note | HP*
0824a6e9-4325-5c3b-a8fa-dd30a620d63f | note | Responsibility - Project / Site Engineer
fdd7b257-b107-5384-826e-f90f5e6565d0 | date | Date Completed:
8cb930ae-52c9-4e44-8e8d-2eba25935a42 | section | 4.0 - Compaction Testing
65918363-6123-4bbf-a500-09863b051283 | checkpoint | 4.1 - Compaction Testing (AfPA Mix)
5b5e0720-9ba9-5ca8-b6b1-e76d0a53d518 | note | Frequency - See Note 1.
990733fb-00d8-55f6-bd8e-d1af740d4de1 | note | Acceptance Criteria - The in-situ air voids content to be determined using calibration between the nuclear density gauge (NDG) and the asphalt cores developed during the Construction Trial.
07cb5bd2-2c4f-5f50-8bf4-1b8e14c1e604 | note | For test locations away from joints:
bf682df4-a28a-50ae-a8fc-dbe8587a2967 | note | ○ Individual Air Voids: Minimum 2% and Maximum 8%
c9a25a06-f594-55c1-93a2-cd84bb394fd7 | note | ○ Average Air Voids: Minimum 3% and Maximum 6.5%
65758bb4-6d1e-560e-b938-2478bee7b78c | note | For test locations on longitudinal joints:
16e1d95b-6321-5b92-a5e3-dce46f78dfdd | note | ○ Individual Air Voids: Minimum 2% and Maximum 9%
b077ab9a-869d-5b8a-9681-137185741295 | note | ○ Average Air Voids: Minimum 3% and Maximum 7.5%
5c99acb6-bb52-51bf-917c-2492ca5d594c | note | Reference Documents - AfPA Sec 12.4.2 Table 22
c075ad1d-7fa5-53b7-b9a3-b57a30a0c645 | note | Inspection/Test Method - Verify
f20839b2-94d2-5d01-a79b-734c6462b437 | note | Record of conformity - NATA accredited test certificate
c4571efc-9490-5578-a62b-cfe0cebe1985 | note | TP
bef2ed99-72f7-5036-835a-9f27ea19b464 | note | Responsibility - Project / Site Engineer, Laboratory Technician
fc5f5a58-40dc-5d7c-9c3a-8ca819ada0e0 | date | Date Completed:
099bf5a9-42e3-4058-8cfb-a636699af661 | checkpoint | 4.2 - Compaction Testing (Type H Shoulder Mix)
9b48356e-602d-559e-8a70-19606954c66f | note | Frequency - See Note 2.
a8551a37-bdba-521c-80f9-474ba6a6831d | note | Acceptance Criteria - The in-situ air voids content to be determined using calibration between the nuclear density gauge (NDG) and the asphalt cores developed during the Construction Trial.
0c7e4376-0e2c-5857-924b-0120a7ed0450 | note | For test locations away from joints:
107aea62-354c-53e3-9115-eb9771885bcb | note | ○ Individual Air Voids: Minimum 2% and Maximum 8%
473a830d-3b43-58bd-9e47-4a383d38304e | note | ○ Average Air Voids: Minimum 3% and Maximum 8%
2ba06b15-8b0b-5278-9835-4f90f88aa04c | note | For test locations on longitudinal joints:
5afbb6a7-a4a1-560e-b022-82e9bad1ac09 | note | ○ Individual Air Voids: Minimum 2% and Maximum 9%
6d90001c-c503-5e9b-8633-69a430cf8c68 | note | ○ Average Air Voids: Minimum 3% and Maximum 9%
cc46bb88-056d-53d7-82ce-d6c48ca4ae8f | note | Reference Documents - AfPA Sec 12.4.2 Table 22
b0191cb8-548b-5422-bde2-f41df3842d66 | note | Inspection/Test Method - Verify
d1b883be-5e5f-5ed4-b140-3befcf9b1ad2 | note | Record of conformity - NATA accredited test certificate
3fbdf891-67af-5c38-ab0c-79f738d20de3 | note | TP
6be359d7-c79a-5104-bb58-32105d588c66 | note | Responsibility - Project / Site Engineer, Laboratory Technician
285591af-2d8b-5f00-927a-b4fc49ea144c | date | Date Completed:
18252a39-32ab-442a-9d38-6c7bfe17dd9d | section | 5.0 - Completion
f135dadf-31b5-4ee1-8ff7-5a5dd8677e8c | checkpoint | 5.1 - Surface Smoothness Testing
c5b297c9-1eaa-5d22-b991-d7370db8f6b4 | note | Frequency - After completion of pneumatic tyred rolling
b8ef7f30-9a88-58b1-a959-233eb3238049 | note | Acceptance Criteria - The finished surface of the surface layer must not deviate from a 3.5 m straight edge by:
1c97bc8e-013f-5cc6-9051-95b3b7691b8f | note | – Full Strength Pavement (AfPa Mix)
a52d80a4-e60a-5e0c-a30a-08ce049272a0 | note | o Longitudinally: Max 4mm
2667ae6b-1201-57c3-910f-80419cb48b72 | note | o Transversely: Max 6mm
76e76f41-9bd0-57f9-a873-544c2cbc3215 | note | – Shoulder Pavement (14H Mix)
cd9cc2e5-680b-5aa0-94d7-a143aab8c022 | note | o Longitudinally: Max 6mm
b8766bfd-c89f-5557-8d40-dce12e9795bc | note | o Transversely: Max 7mm
b15d9a54-5ff8-57ac-973a-23ba0bcb77c5 | note | Reference Documents - AfPA Sec 12.4.3 Cl 293.
45da2edb-bcd3-5f1f-82f4-b03962d62b13 | note | Inspection/Test Method - Visual Inspection
cfe9e470-6d0b-5f2b-88ac-6e6d1c58af01 | note | Record of conformity - This ITP signed
61c443ad-591f-5ec9-a841-8ded3f0ddbe6 | note | HP*
624295ee-5c1c-5bf9-a4e3-eaf1381950f9 | note | Responsibility - Project / Site Engineer
a264105a-ffcc-579a-9d8b-8c89d1dae253 | date | Date Completed:
43fe13a2-0a84-4e51-82f6-ca67366a4941 | checkpoint | 5.2 - Finished Surface Levels
66876240-1348-5152-ac6d-41ce6367c2df | note | Frequency - Per Lot & Per Asphalt Layer
4cefae3a-08a3-5f96-80cf-af2c2804403e | note | Acceptance Criteria - Surface level must be as per following:
3c26b3ae-1fd7-5f3d-bee0-61edba6d1384 | note | – Full Strength Pavement (AfPa Mix)
c9ad5d4a-fd55-5803-8cfa-519b19ad020b | note | o ≥95% of the deviations between design surface level and finished surface level must be maximum 7mm.
2ad96614-1c2b-5c2c-b8cf-fdaa3b4d1095 | note | o ≥95% of the finished surface deviations between design surface cross fall and finished surface cross fall must be maximum 0.3%.
914f0b94-6f35-5076-9c01-9f1643c1286e | note | – Shoulder Pavement (14H Mix) (14H Mix)
ffaa615c-26b4-5a2f-a2d0-a1ed3a8c9fee | note | o ≥90% of the deviations between design surface level and finished surface level must be maximum 7mm.
59bb3e47-78dc-596d-932a-d61366e367c5 | note | o ≥95% of the finished surface deviations between design surface cross fall and finished surface cross fall must be maximum 0.3%.
9c5be199-f41d-51ef-a6b0-5b574c0a900c | note | Reference Documents - AfPA Sec 11.5.1, Sec 12.4.5 Cl 298-299
22178bd7-0fcf-5c93-a8ab-c2723d84fd25 | note | Inspection/Test Method - Verify
7e22766e-22e3-56d7-9c4c-e9df49aa9a3d | note | Record of conformity - This ITP signed, Survey Reports
e7c89dad-45b0-551d-8de5-254576255443 | note | SCP
988132d4-0915-57d6-bde2-14bab73e2dcd | note | Responsibility - Project / Site Engineer, Principal’s Representative
5d806959-75fa-5932-be18-d1cb9f89ec36 | date | Date Completed:
b253de93-fa93-48b5-a4e2-0c9980e58583 | checkpoint | 5.3 - Surveyed Average Layer Thicknesses
63e6e4f7-0a51-5e46-9448-c0f8df6a6857 | note | Frequency - Per Lot & Per Asphalt Layer
405b7330-f7cf-56e1-9351-f2a60f83585d | note | Acceptance Criteria - Average layer thickness must not vary by +7 / -4mm from nominal thickness.
4d9b7a63-151c-59f3-9591-f2623e2c7ca5 | note | ○ Refer Aconex: BecaCPL-GCOR-001149
f9a244f1-abe1-50a7-9fb4-8eb14124edde | note | Reference Documents - AfPA Sec 11.4.5 Cl 247-248, Sec 12.4.4 Cl 294-295
1d83e7a2-aaea-5045-9c0d-22d3430eec75 | note | Inspection/Test Method - Verify
578da9fa-c510-5aad-ac01-c3e36ce4ee63 | note | Record of conformity - This ITP signed, Survey Reports
d48ca06e-97df-596d-918b-21331cd7c500 | note | SCP
de4108f9-392a-53d2-9ef1-b3a49aa27687 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a770faed-91f7-5d62-b114-4a6ef6765ce8 | date | Date Completed:
a5eb0caa-ec90-4ffb-a402-1b1c3a0c235c | checkpoint | Final Inspection
a2ac3a83-86a1-5bf8-b2ff-78c908b1a89d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality\System Procedures and verifies lot compliance with specifications.
594d0e9b-0456-5ab9-ae14-07100c0e9d21 | textbox | Print Name:
248be112-e257-515d-be95-4a4ca261c02a | textbox | Position:
42c4f1e7-3c8c-538f-acb9-b809dabca7df | date | Work Completed On:
ff9187ca-a632-5f3b-8c55-892c5854bac5 | date | Date:
51cd3abb-73a8-4f95-8c6e-63aa55ada85a | checklist | FH-ZU2-QU-ITP019 - Spray Seal Placement - Rev 1 | itp | ITP019 - Spray Seal Placement
e8bcd4ad-4c6e-425f-9433-981140c4ac85 | section | 1.0 - Preliminary Activities
57149455-e3a9-4ad5-b430-af51d0a24901 | checkpoint | 1.1 - Check for Correct Documentation
99d26f55-d53b-5be9-919d-f74e244ca72b | note | Frequency - Prior to commencing works
f44b925b-8ef3-5cbf-9564-c18048cf1da7 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
fd728d1f-dbca-598f-9a99-380ce33e6d02 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
385bde3c-18ea-5756-af9a-b177f4adb1f1 | note | Reference Documents - Current Revisions in Aconex or ACC
a1ce4557-03f4-56fb-b37d-e20fd3a97e9a | note | Inspection/Test Method - Verify
9ae40c17-71da-5e69-bf13-bed52a2dcc8a | note | Record of conformity - This ITP signed
ea1bf8a7-8bcf-5839-b274-32d5f5d551e0 | note | HP*
4970d0c4-183e-511b-91e6-99185641679a | note | Responsibility - Project / Site Engineer
cf668b44-5796-50eb-b82c-3a3544c86e42 | date | Date Completed:
e6fe80b7-4f90-4fdd-8026-1a074f6808cc | checkpoint | 1.2 - Implementation of all measures and controls
515120e3-76b8-51ab-b2b7-8575773312c4 | note | Frequency - Prior to commencing works
e4195976-f45f-5f6c-9bff-330c716b3ef3 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
946ef10d-cc61-510c-810b-1c33215ca0e5 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
6407e481-51ff-5c31-bdeb-c4bd3b171a2e | note | Inspection/Test Method - Visual Inspection
68c2ba93-d343-5ef3-b7a2-03296d418963 | note | Record of conformity - This ITP signed
1f5e4321-6d40-55ba-b88f-4d8a837ad394 | note | HP*
e99d7166-ace9-52a2-b86a-1b8473160663 | note | Responsibility - Project / Site Engineer
19946092-3c09-5298-9e35-05f392ce81f1 | date | Date Completed:
d23305ae-bacf-43fa-b4b5-d08430aa855b | checkpoint | 1.3 - Plant & Equipment Check
9a2b3deb-4d64-50b5-85a9-039b86918458 | note | Frequency - Prior to commencing works
279b0fe8-bad9-5bab-8b28-1a4cef298b56 | note | Acceptance Criteria - All equipment shall comply with VicRoads Section 408 and VicRoads Bituminous Sprayed Surfacing Manual.
b0a61a36-6acb-55d1-aef5-93a93bf4ad11 | note | Reference Documents - Beca Spec 002 - 12.3
4e9e834e-f65f-50b1-80e9-176cc7e50741 | note | Inspection/Test Method - Verify
305535f9-f829-5f08-a2f4-f9b183621e3e | note | Record of conformity - This ITP signed
c4287885-cd53-5223-b23d-ebd5531c6f3f | note | HP*
401e6ef2-678d-5abb-9c2e-fe54abe0e62f | note | Responsibility - Project / Site Engineer
f76a6910-fd36-5143-b7cb-7c09734ff325 | date | Date Completed:
86e65bcb-0044-42c5-800f-41bbe5723b10 | section | 2.0 - Materials
51c9704a-2a0c-4520-9081-782837612c4a | checkpoint-no-value | 2.1 - Material Approval
0180bf66-82fe-5bdf-b75d-a5a3a494916a | note | Frequency - Prior to Works
b7f612c1-825d-5eca-82ac-c5078adca858 | note | Acceptance Criteria - The binder used shall be class 170 residual bitumen complying with AS 2008.
ad3c639b-e0c7-5c6c-9468-955e077988f7 | note | ○ All aggregates used shall comply with VicRoads section 801 and 831. Material and Test Reports to be submitted to the Principal’s Representative prior to commencement of works.
4b76e043-3a96-5d84-9078-cf3a5e38d0fb | note | Reference Documents - Beca Spec 002 - 12.6.1.1 to 12.6.1.3
1c829db9-cd91-555c-9bf6-2690806079dd | note | Inspection/Test Method - Verify
026372fd-6f92-5df9-85e1-172497381ef3 | note | Record of conformity - Test Reports, This ITP signed
306957d8-b06d-52b1-a97f-0cb06468180b | note | HP
5960453d-3adb-5f5c-aa48-22864a93455a | note | Responsibility - Project / Site Engineer, Principal’s Representative
4a2f89ba-db0c-5606-92d1-5c6c6f1f3ea3 | date | Date Completed:
6b43d63c-ba7a-5475-83d2-8e8eb4441002 | note | Principal’s Representative - DCWC Mgt-GCOR-009596
8a2cad47-c623-4226-a99f-55e64477505a | section | 3.0 - Construction
0336702c-135e-4a8b-ad26-5e786bff34ef | checkpoint | 3.1 - Underlying Surface
b55c9220-1218-5b6b-9965-d5a620d7c5c5 | note | Frequency - Prior to works
8a6942f8-87cf-5f67-93a5-19f8b664c1bb | note | Acceptance Criteria - The pavement surface should be cleaned to remove all mud, carried on material, dirt and dust.
a1905cf2-aa5d-5c68-a05d-e3ea0e2adf5b | note | ○ After cleaning the surface should be swept with a suction sweeper, supplemented by hand brooms where required. Seal coat should only be applied to a sound clean dry surface.
c4b95760-ee66-5f4b-967e-ae1bd2dbbe9e | note | ○ Preparation of the underlying surface shall be approved by the Principal’s Representative.
da482898-a99b-564f-bf91-ea0730671827 | note | Reference Documents - Beca Spec 002 - 12.4.1 to 12.4.5
907dac99-ae2e-5ab5-ba6b-e820b1135a56 | note | Inspection/Test Method - Verify
6b71389b-b533-5318-bf2b-2369ac003a3a | note | Record of conformity - This ITP signed
e732b59b-9a25-55a6-a246-675f1888c65c | note | HP
dec31d14-7e78-5705-981d-5900356a0d60 | note | Responsibility - Project / Site Engineer, Principal’s Representative
4a94e1b2-3c5a-554b-83fa-72558f4fe7f0 | date | Date Completed:
389b6e60-5f91-4cee-8bac-b00d91a6eb23 | signoff | AUTHORITY HOLDPOINT
bc827790-c421-43a3-b33a-9c4c2631347f | checkpoint | 3.2 - Binder and Aggregate Application
460ff129-e91b-5d1c-8557-f539998c1c2a | note | Frequency - During works
e9108c97-6a3c-5c77-9af1-b4d273309262 | note | Acceptance Criteria - Application rates shall be:
e5dc51ac-c7a5-53f0-a742-63910cb561d0 | note | ○ Binder: 0.8 – 1.2 L/m2
55f29abb-e7ad-5805-bcf6-8c98d32ca74b | note | Refer Aconex: DCWC Mgt-RTRFI- 001272
10bcf56c-1534-59b1-a1b9-5cb997b62e67 | note | ○ Aggregate: 8 – 10 kg/m2
17fc8aaf-1094-56d0-9a29-213c3b45e032 | note | Reference Documents - Beca Spec 002 - 12.6.2
91bd4695-dbc1-5301-83a8-d81418984ff4 | note | Inspection/Test Method - Verify
afeecce6-979e-5a3f-b14e-964698b0d649 | note | Record of conformity - This ITP signed
22069dc3-6f08-5b8a-a768-17492cc4da03 | note | IP
f1650274-2108-54b7-9557-c47b13242630 | note | Responsibility - Project / Site Engineer
caa491e8-6357-53b2-9b3f-896606b18a58 | date | Date Completed:
3558efa7-7cce-4cc8-a9b7-c5c80dddb2a0 | checkpoint | 3.3 - Aggregate Spreading
5aaaeec4-daca-5031-82ff-6f3d20e0dace | note | Frequency - During works
90f2b260-756d-598a-b1d5-115f70a2538d | note | Acceptance Criteria - All aggregate spreading shall be undertaken using forward aggregate spreading and discharge plant.
e9df92de-0853-5fdd-9e67-e76b4b0e2b1d | note | Reference Documents - VicRoads Section 408 – 408.13(e) to 408.13(f)
91deb454-fb48-5ee9-9a00-d53385df6b64 | note | Inspection/Test Method - Verify
376bbbbc-c41f-5c66-b4b4-251f3de0f271 | note | Record of conformity - This ITP signed
3e762456-f42d-5369-96e4-1f2d7569ccfb | note | IP
3b210cfd-cb73-54cb-90ce-9757b15569b8 | note | Responsibility - Project / Site Engineer
b95944c8-e12b-577c-825d-a7fc3c9a1fff | date | Date Completed:
ecb510a8-5206-4b93-9181-49dc76567198 | checkpoint | 3.4 - Rolling of Aggregate
a7fce128-f8e8-5077-bf89-7a3c37aa1b55 | note | Frequency - During Works
d22150a9-200e-5a7f-8cdd-186dba96b56f | note | Acceptance Criteria - Rolling of aggregate shall be undertaken over the full width of the pavement being sealed. Works to be undertaken by static rubber tyred rollers or otherwise approved by the Principal’s Representative.
e464d500-9632-55b9-b873-6bd8740f7323 | note | Reference Documents - VicRoads Section 408 – 408.13(g)
7f6376ab-8124-5c2d-84c6-2bb3a7bd4e99 | note | Inspection/Test Method - Verify
2049228d-37a6-5e50-b5f9-90730444ff19 | note | Record of conformity - This ITP signed
123b39ab-4d8b-5fda-846f-2b4fa2145053 | note | IP
93355f4f-e6ed-5e20-b491-da8d2e372b00 | note | Responsibility - Project / Site Engineer
8672d42b-ebe7-550d-a954-d270e4c03e8a | date | Date Completed:
f94df72a-e1c3-4079-b178-e65baa3d3c27 | checkpoint | 3.5 - Removal of Loose Aggregate
086d6c37-30fc-500b-bd7b-dac102a3cd08 | note | Frequency - During Works
0f19303d-5fc5-5200-b707-0294471d0d79 | note | Acceptance Criteria - At completion of sprayed seal treatment, the Contractor shall remove and dispose of all loose aggregate.
18eef251-bc87-5480-ae5b-f73eab77b998 | note | Reference Documents - VicRoads Section 408 – 408.14
cc9ae318-b7a0-5772-bddf-62c993fee511 | note | Inspection/Test Method - Verify
8a30db57-cb6a-558c-b399-f5afba5e132f | note | Record of conformity - This ITP signed
0af44172-96bd-5bed-a873-9c16b72fdd11 | note | IP
e96c6382-4a04-500f-91bf-2d846f2d2fe3 | note | Responsibility - Project / Site Engineer
eb44069f-d261-5957-951c-6b9cb9c899f7 | date | Date Completed:
ee618c11-52bb-4dd3-9c47-0be815c7da71 | checkpoint | Final Inspection
093a37ab-ed53-55a4-8356-00f47ef65b7d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
7d02be77-d93e-5a61-8cb6-2a7e1eb9340a | textbox | Print Name:
b229b7f5-c9f1-5ed5-9d70-14a8e2cdcc0a | textbox | Position:
4e1a7de0-332c-5b3b-9cb1-37894f0e6a5b | date | Work Completed On:
e70f894e-7cbb-5c5b-8ee6-58631cf99e2c | date | Date:
a6b7a591-f6ee-4685-8c6e-b1a2f8568032 | checklist | FH-ZU2-QU-ITP020 - Prime Coat - Rev 2 | itp | ITP020 - Prime Coat
a1e0cb8c-28cc-424c-a78f-7fe526521fc2 | section | 1.0 - Preliminary Activities
1c0bdf25-0790-4f04-9077-28744eba5206 | checkpoint | 1.1 - Check for correct documentation
80e5f155-88d5-5bcd-ad99-df4b0aa779bf | note | Frequency - Prior to commencing works
fa088635-6c35-5834-bf44-3c991561f76b | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
cf1d362b-a3f0-57b5-b609-b432a06fce79 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
64334896-b042-5621-9ccf-8c4ea78a093e | note | Reference Documents - Current Revisions in Aconex or ACC
60d86afc-e4e5-5400-910d-b781e2c1d2f8 | note | Inspection/Test Method - Verify
38f6b59d-c829-5bca-9a30-6991bd840622 | note | Record of conformity - This ITP signed
090a4366-69ed-5b45-b3fe-28db780f2220 | note | HP*
4b1083bc-f58e-5105-9dca-8cb800f274fb | note | Responsibility - Project / Site Engineer
ef660620-3032-56b3-9d60-7fd7b4e39609 | date | Date Completed:
6c32f2ec-3e86-4bbf-8f8c-f2f619a03918 | checkpoint | 1.2 - Implementation of all measures and controls
d195e0c3-5608-569b-8fb1-e9a47e8db907 | note | Frequency - Prior to commencing works
9781b6d1-2003-5001-a1b2-ef0efc3311f0 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
ab7d6a29-018a-5822-9d9f-e2a713da4961 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
fcaee547-ed53-5cc0-8382-af25d76b5701 | note | Inspection/Test Method - Visual Inspection
083c25b2-2d46-500a-9a4f-c0ef5c2be2a9 | note | Record of conformity - This ITP signed
552fa7c7-a655-5b9c-bb10-711a3e743a9b | note | HP*
a58521ca-b4e7-5e86-b970-de24b28d6237 | note | Responsibility - Project / Site Engineer
1dbf899d-f489-5014-99f0-1b3c7b6d278b | date | Date Completed:
0a8af407-f3e0-4db0-a9a0-b4e782f6cd47 | checkpoint | 1.3 - Plant & Equipment Check
81e69d9a-5b44-5a8f-97f9-ce234fc7934f | note | Frequency - Prior to commencing works
de60ea39-2dc1-537a-8055-1bbcd19fdb31 | note | Acceptance Criteria - The Contractor shall provide equipment for heating and uniformly applying the bituminous material and blotter material.
1d90ffca-4aeb-5243-bd6e-4a3fc9a5f562 | note | ○ The bitumen distributor shall comply with the requirements of NAS 70: ‘Bitumen Sprayers’
e9e12f20-535b-54d5-83bb-156ac23d53b8 | note | Reference Documents - Beca Spec 002 - 7.3
42cd1320-3e39-55fc-a72a-00de41869e8a | note | Inspection/Test Method - Verify
680136a9-700a-5c42-96fe-f6a727c2a548 | note | Record of conformity - This ITP signed
72d6fd55-3c22-557a-b5e6-70b7c1db44a0 | note | HP*
3d9c33c4-db18-594b-a41c-b41ea185598b | note | Responsibility - Project / Site Engineer
88ffee46-8ff3-53f4-8227-30547653838b | date | Date Completed:
bbf324f0-fc6b-4983-8b48-4014871db62e | checkpoint | 1.4 - Weather Conditions
0f3982b2-bce5-5f5e-a2bb-71b976f8ecef | note | Frequency - Prior to commencing works
4805e412-0a30-55d6-af8b-97c13f793f9d | note | Acceptance Criteria - Prime coat shall not be applied on a wet surface, or when the surface temperature is below 10°C, or when the weather conditions would prevent the proper application or adhesion of the prime coat
d5f38335-254e-5f61-87c6-2ade1cc6f1dc | note | Reference Documents - Beca Spec 002 - 7.9
b67973ed-5400-544b-abcc-eb581fb36be3 | note | Inspection/Test Method - Verify
3c9d6a8f-19cb-58ca-a6df-7fe4ab9e183e | note | Record of conformity - This ITP signed
30700ce1-4ee6-5f7e-9317-366c06df8d7f | note | HP*
21402070-1d8e-57f4-b7fb-812c8ea5873a | note | Responsibility - Project / Site Engineer
68cbdc38-a1f4-5bdf-a13a-8e82d1885305 | date | Date Completed:
8a688cd1-e3a9-4ec0-adbc-05fc02ee376e | section | 2.0 - Materials
0d86362b-32ea-4f97-acbe-04e1e519108a | checkpoint | 2.1 - Cut-back Bitumen
edfce6ca-9860-547f-b246-713a7eef731d | note | Frequency - Prior to commencing works
be71cd22-df92-56a8-a2e5-572e4559b377 | note | Acceptance Criteria - Cut-back bitumen for prime coat shall comply with AS 2157 and shall be class AMC0, AMC00 or AMC1.
750cf271-f13e-5f7a-a9c3-d9bb75f66257 | note | Reference Documents - Beca Spec 002 – 7.4.1
9c39bdf3-7644-5b4c-b564-a2012325bb97 | note | Inspection/Test Method - Verify
0b57be03-5f65-5306-a59e-51d4ff1e5c2d | note | Record of conformity - This ITP signed
bdd0e7ae-f106-5d5b-9327-0bf3ba56a034 | note | HP*
fbc590d7-2ec0-58f4-93cf-1133ed77e60d | note | Responsibility - Project / Site Engineer
76913f32-d7b9-5876-859d-ce0afeaaea0b | date | Date Completed:
fdca09e4-1270-418f-9fab-dd36cbb42333 | checkpoint | 2.2 - Cutter
eefb8dcd-9b67-57f7-8363-a117e2ae0719 | note | Frequency - Prior to commencing works
0c87aad9-c9fb-5cb6-b412-a955c0a5f327 | note | Acceptance Criteria - The cutter for use in cutback bitumen shall be a suitable petroleum-based material complying with the requirement of AS 3569.
f9b606b3-73e7-5a30-8537-07106222a4de | note | Reference Documents - Beca Spec 002 – 7.4.4
19f8b060-d4d5-59a8-99b6-bcbcd0125ae2 | note | Inspection/Test Method - Verify
39148fc5-a21d-5962-bc1a-3eba6e10b7e7 | note | Record of conformity - This ITP signed
efbfb421-afa6-5e3f-9a8c-37445c679a72 | note | HP*
4e5fabdf-7445-5200-bf77-3fbfc79fb308 | note | Responsibility - Project / Site Engineer
458994b8-8aa5-5452-ba83-20c89d7b158f | date | Date Completed:
4fe7170e-50f9-4a44-90f1-4455616e3c1c | checkpoint | 2.3 - Bitumen Emulsion
aca34ed8-1ba0-515c-8116-163da6ad041d | note | Frequency - Prior to commencing works
b5f24114-5738-56ca-8e0d-242c3cdad483 | note | Acceptance Criteria - If directed by the Principal’s Representative, bitumen emulsion complying to AS 1160 shall be used as a prime coat.
e54f8d7b-5b04-5f97-8118-c33fa28654e1 | note | Reference Documents - Beca Spec 002 – 7.4.2
e9292f53-667e-5ec0-be49-cf0a66a59fb6 | note | Inspection/Test Method - Verify
c6f17cb2-f3e2-5c15-a49c-a878cbeef3b7 | note | Record of conformity - This ITP signed
68d8c2db-1067-5ad8-9eb2-23934fa25f48 | note | HP*
b2f87684-4113-5683-8389-21850ac419e4 | note | Responsibility - Project / Site Engineer
4e13904f-923c-5def-9741-ca93c6b29373 | date | Date Completed:
fc81c373-2332-5513-bf5c-ec962a3bbeb3 | note | Principal’s Representative - BecaCPL-GCOR-001036
361bc83d-b2d6-4456-8522-651de250b869 | checkpoint | 2.4 - Blinding Sand
011dff3c-cf11-513d-9e0b-a424ee1aaf96 | note | Frequency - Prior to commencing works
15385523-4d24-5e1a-a3ad-c811ca137a74 | note | Acceptance Criteria - If required, blinding sand to be used for absorbing excess primer shall comply with the following PSD.
2282c032-deb0-5f5f-be2e-a9476b4bac43 | note | – – – – – – – – –
4b68975f-d3bd-5155-b43f-58df01d6a150 | note | AS Sieve Size (mm) ¦¦ Percent Passing Sieve by Mass
0b774250-d152-5c76-bb81-e385511f2370 | note | – – – – – – – – –
8b212033-13e5-5f5b-b3c4-0a228318e308 | note | 6.7 ¦¦ 100
1e7a34d6-2f1a-56c0-95a9-b152ed54bdf0 | note | 4.75 ¦¦ 85-100
56e98935-3c6a-5607-839b-71da3f382d77 | note | 1.18 ¦¦ 40-100
978f3888-ceb9-57d4-98f4-bd102d4c6340 | note | 0.425 ¦¦ 10-50
acc5274b-bdb6-5588-858b-a1e12aef68a7 | note | 0.075 ¦¦ 0-5
03e9d942-3ff4-5260-9013-9efe247af5d7 | note | – – – – – – – – –
0c7ad2b4-7b69-5f37-ac63-73811b15fc0b | note | Reference Documents - Beca Spec 002 – 7.4.5
3339a759-c873-5713-8a9d-cde03860859c | note | Inspection/Test Method - Verify
a7f6daed-3c94-56df-b417-fe5fc0a37d68 | note | Record of conformity - Test Report
101888bf-2192-59ba-9475-afa6361e60c1 | note | TP
57de1639-c4d6-5695-94db-3a8287d54203 | note | Responsibility - Project / Site Engineer
a039e763-d319-59ef-95b2-b5c4f884abaf | date | Date Completed:
ca3eedf5-d89c-4186-9ffc-98f3e42542cc | checkpoint-no-value | 2.5 - Test Certificates
bd78bbfc-6b47-5001-8f1e-fb689f3a301e | note | Frequency - Prior to commencing works
4c5eedd5-396d-53fc-9749-55b6260bb7f2 | note | Acceptance Criteria - The Contractor shall submit a Test Certificate for each material proposed for use in the Works indicating compliance of those materials with the properties or requirements specified.
1e833167-31a8-56b8-a943-a3ddce13cc07 | note | Reference Documents - Beca Spec 002 – 7.11.2
967d1733-74ed-5952-9e01-b5a7366a283b | note | Inspection/Test Method - Verify
638b1d31-d5fb-5015-8bc6-07ff05209404 | note | Record of conformity - This ITP Signed
d16d41fc-ad72-5d5f-b5f4-75e6f8a908a1 | note | HP
1a8d1b10-7809-5069-81f0-f47131eb4e06 | note | Responsibility - Project / Site Engineer, Principal’s Representative
58b5c9bb-8669-519a-987c-6d73cb25fa82 | date | Date Completed:
55db0188-58d2-529b-8bd6-4460bdcd3764 | note | Principal’s Representative - BecaCPL-GCOR-000967
ecb49382-18fc-4eed-901a-408364f65541 | section | 3.0 - Construction
299089d7-10a2-4393-8a92-efe8d2b2848c | checkpoint | 3.1 - Trial Application
d144b3dc-64ed-5441-9b7f-c21dcb62a4b4 | note | Frequency - Prior to commencing works
bf4aa8bc-c909-54eb-a3b8-96e6fd37be54 | note | Acceptance Criteria - A trial application, to be conducted as part of permanent works, shall be conducted on an area of the Works agreed and witnessed by the Principal’s Representative
8fb97ab8-eaf8-5049-9422-386843d03e93 | note | Reference Documents - Beca Spec 002 – 7.5
cfe67c4c-15c1-59a5-9f39-9b382c8a83b3 | note | Inspection/Test Method - Visual inspection
1352953f-e4ac-59e1-ba7b-fcaf05f8dccb | note | Record of conformity - This ITP signed
3ff84b75-5407-539d-b851-f5cecf0b7b54 | note | WP
1c433402-1cda-5e93-a5b2-d0ef2fa1eb6d | note | Responsibility - Project / Site Engineer, Principal’s Representative
510ad5fe-5493-5a6d-9c53-b2d58b5f811f | date | Date Completed:
fd86f1c1-1d8c-4f6a-ba0d-e2961e358854 | checkpoint | 3.2 - Surface Preparation
5235856a-71f1-5bef-ad2d-647a8243a109 | note | Frequency - Prior to commencing works
b1d7c351-0622-5a32-a8ac-e793dc2fc850 | note | Acceptance Criteria - Immediately before applying the prime coat, the full width of the surface to be primed shall be swept to removal all loose dirt and material. The prepared surface is to be inspected by the Principal’s Representative.
5cc7f860-8c1a-5be2-8dc5-e550b89bfcb8 | note | Reference Documents - Beca Spec 002 – 7.6
901c69c8-d778-54e3-8215-5c43ff811247 | note | Inspection/Test Method - Visual inspection
2ef648d3-937e-538f-b17d-b13eaf318e1d | note | Record of conformity - This ITP signed
603fa105-9807-58ba-9a7e-1d644d6785f6 | note | HP
0450a84b-92ad-5df4-a3c5-4bb3999f537a | note | Responsibility - Project / Site Engineer, Principal’s Representative
5d17e978-e38c-5df7-ba97-6b2eee630565 | date | Date Completed:
812d3bc8-5983-4d8b-a284-7d3e9bfba958 | signoff | AUTHORITY HOLDPOINT
39ef0bc9-5453-4150-afd4-7ad1ceac2d05 | checkpoint | 3.3 - Application of Bituminous Material
07d3d7c5-b8ba-55f9-b5c0-58764fb49c6e | note | Frequency - During works
5baa220f-ed69-5830-989b-75b3b6736363 | note | Acceptance Criteria - The prime coat shall be applied at a uniform rate and shall be between 1.0 and 1.4 litres/m². The depth of penetration shall be a minimum of 6mm and maximum of 10mm
b03d062c-7d38-51c8-ba8c-45d9794ae3f9 | note | Reference Documents - Beca Spec 002 - 7.7.1
52be890b-5661-506d-b696-c3a1726b2fe7 | note | Inspection/Test Method - Visual inspection
492c42ab-98a7-5688-a2ac-94d8d5c7355b | note | Record of conformity - This ITP signed
3efbcb93-5f7b-512f-b49a-b1fd230fbd7e | note | WP
1ad3a74a-ad26-5172-9180-c0a4a9d90e17 | note | Responsibility - Project / Site Engineer, Principal’s Representative
68355d5c-0c4d-5e60-810f-135a9636b53c | date | Date Completed:
b5be9366-9f29-4c85-b275-a3adc09d7414 | checkpoint | 3.4 - Job Samples
3b9a3b34-f253-5b54-8edc-845f9c40e66a | note | Frequency - During works
f6bb36ca-d851-5d00-aa04-7377f9b443d9 | note | Acceptance Criteria - Samples of each bituminous material shall be obtained from the delivery vehicle at not less than one sample per 10,000 litres of bituminous material sprayed.
974acb5d-d74f-5838-9e5d-b517b0b9ba3e | note | Reference Documents - Beca Spec 002 – 7.11.3
c5aaf87e-97d8-545d-b640-bf8e0c18d9e2 | note | Inspection/Test Method - Verify
6eb4f2f3-2f56-55dd-afae-4ae1de94d265 | note | Record of conformity - This ITP signed
454a022a-e3a8-5dde-bc65-68d29eff10d9 | note | WP
3a0f3209-dd41-562f-9762-1de6531f5db1 | note | Responsibility - Project / Site Engineer, Principal’s Representative
b242dd58-a2c4-5650-8498-a39b2073ee5b | date | Date Completed:
380b9c8c-4f81-4e01-a1b2-58fb404f6199 | checkpoint | 3.5 - Spray Rates
868ac34f-59cc-5b7d-a286-1adcc0c9e3a3 | note | Frequency - During works
bd2a5f0a-7689-5183-a3a1-8d43ffb60014 | note | Acceptance Criteria - The Contractor shall submit records of spray application rates at completion of each mobilisation
964d3547-e807-5322-a762-51f1bf390cfd | note | ○ Refer Aconex: BecaCPL-RTRFI-000164
e6ba7726-410c-5af3-8b3f-143425285d6b | note | Reference Documents - Beca Spec 002 - 7.11.4
49ec4345-619c-509f-9ce5-ff4fdef9d760 | note | Inspection/Test Method - Verify
c8c8a3a4-4b14-536f-9c64-55c31f1a51ae | note | Record of conformity - This ITP Signed
aeef1bda-d3be-562a-8ea9-5a8985d0f1b4 | note | HP
6c0f3a68-b9da-5565-8b34-a91678c98257 | note | Responsibility - Project / Site Engineer, Principal’s Representative
8f57e5ff-a979-5812-aa1a-2c606dc62777 | date | Date Completed:
986974b7-9e9a-4beb-b57b-cda2b791ee73 | signoff | AUTHORITY HOLDPOINT
b406b5cd-d6ad-4c01-9333-64cebc0a3a17 | checkpoint | Final Inspection
c0962a4a-b69c-5e1b-88c9-9f018ec5c44f | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
92af86fd-5fe0-53a2-8875-03fde9ada4de | textbox | Print Name:
2be8e558-029f-5e73-af51-f5ff22bbd11c | textbox | Position:
852864a7-7c13-5d8b-864f-8b2460177ef6 | date | Work Completed On:
1cbb886e-5c23-579a-970a-252094c725e6 | date | Date:
42ae4dbf-3caf-42c7-ac96-0e8bdd0c4de1 | checklist | FH-ZU2-QU-ITP022 - Hatelit Install - Rev 1 | itp | ITP022 - Hatelit Install
6bc8eb5b-477b-4042-babb-3146a6873793 | section | 1.0 - Preliminary Activities
0d347d33-2891-4382-9c28-6a6f35594b21 | checkpoint | 1.1 - Check for correct documentation
fe8ec0d2-1652-5981-a4f0-535d6de7b482 | note | Frequency - Prior to commencing works
fab6a839-e954-5ff7-80d9-ab5b3a1e48a1 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
a4f2392d-8f1e-57ff-8b7a-5aff62d805fd | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
9c710b9b-74a3-5ed7-8eef-5d2733d62035 | note | Reference Documents - Current Revisions in Aconex, ACC
4982040e-3988-5e94-8294-ff3faf0f4577 | note | Inspection/Test Method - Verify
8245a88e-f653-5775-a1d0-234e6fc4ba4c | note | Record of conformity - This ITP signed
459f7d5c-0ba6-5b9a-baa6-e5c810116ae5 | note | HP*
795dfdfa-7874-59e0-984f-287a48aaed7b | note | Responsibility - Project / Site Engineer
cf716e5f-76f7-5aee-9735-0288986f3092 | date | Date Completed:
bbaa98b3-bae0-4735-abdf-9e22130c368b | checkpoint | 1.2 - Implementation of all measures and controls
bc148166-d093-5c81-9388-1cfd64b2ba6f | note | Frequency - Prior to commencing works
8fa509c0-ee5d-5e65-b46b-553cb5cccd46 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
c32b3392-7d90-562a-99ec-c4bd3d9fb812 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
477aa62e-c5f1-5949-b9b9-6c284825a576 | note | Inspection/Test Method - Visual Inspection
e53b282d-6654-5abd-8855-9cd14fa4a1a9 | note | Record of conformity - This ITP signed
a4faf0ac-25ca-535a-a761-8200c18d958c | note | HP*
f3d028cd-6ee3-5a89-b3bf-4076c5e0c8a1 | note | Responsibility - Project / Site Engineer, Site Supervisor
09c16e9a-861c-5f6e-9246-db315f42905e | date | Date Completed:
4fa1d1e6-5777-4f0a-aa29-8e84bb3359ee | checkpoint-no-value | 1.3 - Equipment
272633c6-1fc7-5cf2-a8e2-dd4e72feef16 | note | Frequency - Prior to Commencing works
35d5d63a-5c2d-5c2b-a512-c722589e74f8 | note | Acceptance Criteria - All plant and equipment to be used in the constructed of the works must be deemed acceptable to use by the Principal’s Representative.
cda47b3e-1add-5037-921f-a664579c3a53 | note | Reference Documents - Huesker HaTelit C Specifications 1.4.1
139ac96f-d512-5273-988f-74d2c4a4c8f4 | note | Inspection/Test Method - Site Inspection
c93c7c50-505c-5973-b7d4-9b27958670c9 | note | Record of conformity - This ITP signed
9042bb6d-5a32-5c61-a3c9-dd1e44f8fbf7 | note | HP
b28982af-f8b7-57da-a97d-a5ec782fb95c | note | Responsibility - Project / Site Engineer, Site Supervisor, Principal’s Representative
d968b299-3189-5d2f-b056-462f9944e049 | note | Principal’s Representative - BecaCPL-GCOR-001407
83cb149f-6216-5f32-9be7-f86a2d9afe21 | date | Date Completed:
b4d9b665-6961-4e3d-85f1-bc904b77a984 | section | 2.0 - Materials
52866c82-e5fb-4b1a-a69a-901250eb4b8a | checkpoint-no-value | 2.1 - Tack Coat Material Acceptance
7e0d55c8-462f-54de-be33-477f787e7886 | note | Frequency - Prior to commencing works, not less than 10 days prior to commencement of delivery
3344c660-6a5e-52f7-8ca5-4031ae8fb73e | note | Acceptance Criteria - Proposed tack coat material and test certificates shall be submitted to the Principal’s Representative for review.
9226a2e1-7a0a-5e0f-a8ba-079522b5e11f | note | Reference Documents - Huesker HaTelit C Specifications 1.10.1
6a0c7f57-2012-54c1-be1e-7c99c7f46125 | note | Inspection/Test Method - Verify
b021f3a4-2a6f-5bf6-8b9d-504f7d874287 | note | Record of conformity - Aconex Corresponde nce
801e8926-5318-594f-ae97-185cb10f18f8 | note | HP
68a456bb-1658-54cc-8097-8178cfacc3fc | note | Responsibility - Project / Site Engineer, Principal’s Representative
6c46e76c-09ac-5267-be08-61039223b6c8 | note | Principal’s Representative - BecaCPL-GCOR-000967
0db0a516-4559-57e3-a199-2e162a1e745a | date | Date Completed:
ccb715f6-6da2-4866-82fa-b307ece78b6d | checkpoint-no-value | 2.2 - HaTelit C Material Acceptance
e2aaf721-7970-5676-b31e-2be913b2382e | note | Frequency - Prior to commencing works, not less than 20 days prior to scheduled commencement of application
1f487632-ff56-58df-ac6e-f75c7ba9fa40 | note | Acceptance Criteria - Information on proposed HaTelit C manufacturer and test certificates to be submitted to the Principal’s Representative.
4a8b75fd-8d24-55f3-b4a2-2cf21262a4fa | note | Reference Documents - Huesker HaTelit C Specifications 1.10.2
2b303032-c2a7-53a6-b52b-8d613a77d637 | note | Inspection/Test Method - Verify
45859df7-4fdb-535f-868a-c091c3c30506 | note | Record of conformity - Aconex Corresponde nce
d43c360a-5efd-5477-a08f-4056aa9246bd | note | HP
6b961f63-6a0d-5696-a738-2b00e9ace95b | note | Responsibility - Project / Site Engineer, Principal’s Representative
b6192bc9-2828-51d0-9383-3780903dca00 | note | Principal’s Representative - BecaCPL-GCOR-001178
24b16133-02c4-5a16-80a7-814ba4c2f469 | date | Date Completed:
57cf3a97-43ba-4c6b-acbf-db85a9ad33ff | section | 3.0 - Surface Preparation & Tack Coat
6849b183-cbe8-4337-b9d3-edd40420caf5 | checkpoint | 3.1 - Surface Preparation
32a77ac6-f3c0-587c-b794-aa9341294367 | note | Frequency - Prior to Works
ae612268-10c6-5bc8-9f8b-0aa82321a613 | note | Acceptance Criteria - All loose and foreign materials must be removed from the surfaces to a distance not less than 150 mm beyond the edge of the area to be tack-coated
a53f0137-f67b-56d3-977f-37006ee75fbf | note | ○ All treatments within area to be tack coated to be inspected by the Principal’s Representative.
4831e874-8d2a-511f-9e48-28d24b622af6 | note | Reference Documents - Huesker HaTelit C Specifications 1.6.1
ff9f51df-3dc0-5304-ac07-6686e39fa7c7 | note | Inspection/Test Method - Site Inspection
c34a2050-f5c1-522f-9248-a37bb78ebdf2 | note | Record of conformity - This ITP signed
e410af66-4d28-58e1-a032-7aff3a168130 | note | HP
e49985fb-4326-5b7e-a025-9afa3d51dbc6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
b21de6dc-93f6-5e2a-979a-3182886244b7 | date | Date Completed:
7320c9a6-5add-4862-bbef-78dc8ad9426d | signoff | AUTHORITY HOLDPOINT
a7d10a46-ea30-4ecc-b03f-7dfeec3ac83c | checkpoint | 3.2 - Spraying of Tack Coat
afa2c015-45a6-5fd4-97da-71d113c3ff7c | note | Frequency - Each Shift
74f3f3d7-ad7b-566c-ac28-a8c6ba67475e | note | Acceptance Criteria - The tack coat shall be sprayed evenly at the required spray rate of 0.4 - 0.55 L/m2 to achieve target residual bitumen as per guide.
3a7a394f-a247-5187-bbdd-437168194be5 | note | ○ Rate may be adjusted based on site-specific conditions ensuring HaTelit C is bonded to underlying surface.
1a591022-abe6-55c6-81e6-f24ca0c07b0f | note | Reference Documents - Huesker HaTelit C Specifications 1.6.2
ccac4f47-2d35-540a-818b-a9a3ba729487 | note | Inspection/Test Method - Visual Inspection
c90db9dc-c712-5992-a7a4-67cf4369d2ae | note | Record of conformity - This ITP signed
d310d4fc-96b9-515f-bd07-c778e831d795 | note | IP
1790a5b6-13c6-5819-958f-365e4b0976e5 | note | Responsibility - Project / Site Engineer, Site Supervisor
8857be56-ddfc-51e4-b1f2-cff21571ab05 | date | Date Completed:
8ff253e8-234a-426e-945a-13cc3c8692ff | section | 4.0 - Placement
905319cb-332c-4583-aa0e-b3e286218653 | checkpoint | 4.1 - Prior to placing HaTelit
b4265550-c3bf-5b4f-8f06-d4a282b84b63 | note | Frequency - Each Shift
f5915ba1-db42-56ba-b8f2-08fc23571495 | note | Acceptance Criteria - A minimum of 48 hours’ notice shall be given to the Principal’s Representative prior to the commencement of placing the HaTelit.
c52d0313-603d-5036-aaa1-e61947832a1b | note | Reference Documents - Huesker HaTelit C Specifications 1.7.3
008db338-5c67-5bd1-adcb-e530b059d1f8 | note | Inspection/Test Method - Visual Inspection
23093d03-0a3f-5dbb-a0a4-795ef7fc7f83 | note | Record of conformity - This ITP signed
e6960f47-ef78-5994-96a3-f33762b2b033 | note | WP
15a869d1-d930-598a-9b3b-7c69a1fee506 | note | Responsibility - Project / Site Engineer, Principal’s Representative
859b2eaf-0a36-5df2-95d3-2dafb773b9e8 | date | Date Completed:
0c3531ae-3754-405a-9ea7-52ab36cd3aa7 | checkpoint | 4.2 - HaTelit installation
25491cdb-51a5-5b49-9c2e-22a961328a5f | note | Frequency - Each Shift
9245fff0-348b-560b-8436-3e7222976d59 | note | Acceptance Criteria - HaTelit to be installed to Manufacturers Specification. Where placing multiple rolls, an overlap of 250mm transversely and 150mm longitudinally is required. The overlaps shall be treated with tack coat and rolled to bond to one another. For small areas, manual installation is acceptable provided a fully flat and crease free installation is achieved.
4c324ba5-83cf-5cac-9d93-4f18a1ca7b02 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.2
08bd3837-8272-5c7d-af67-86ea640b873c | note | Inspection/Test Method - Visual Inspection
cc24844b-86a0-5eae-b19d-0423130cd4ff | note | Record of conformity - This ITP signed
4cc2a9ab-7593-5326-abc1-c63253b40466 | note | HP*
102bbd1b-e63a-5497-84d0-fbcc8becc5a4 | note | Responsibility - Project / Site Engineer, Principal’s Representative
978c385c-eab7-5749-bbc6-ad058bafeb03 | date | Date Completed:
5566f46b-1958-405e-bddb-579f6890be4a | checkpoint | 4.3 - HaTelit Rolling
979ae15e-de2a-56fe-b5cc-9b1b42d5ae1d | note | Frequency - Each Run
af49bb2b-99eb-5c95-a365-5b63d2135780 | note | Acceptance Criteria - Rolls applied to tack coated surface without wrinkles, creases and folds. HaTelit to be rolled with 2 passes using pneumatic tyred rollers following application.
e76b356f-6c2d-57c2-9584-63bf1dbe5581 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.3
5481f69d-3a75-55cc-9e32-bed7b3817204 | note | Inspection/Test Method - Verify
70def9b9-a338-54a0-964d-493f31264e65 | note | Record of conformity - This ITP signed
4599d628-a39f-5cd0-84c5-b9541a59f97f | note | HP*
1ec9fdee-3fba-5bbc-91df-8e5bf469b19a | note | Responsibility - Project / Site Engineer, Site Supervisor
66de617c-698f-54bc-94e9-5fbb6d89e4d9 | date | Date Completed:
b77fe150-eaee-432f-8f81-fa7b94680fdd | checkpoint | 4.4 - Surface Finish Inspection
1828e8a6-0e11-5554-ae7c-07625c4e931b | note | Frequency - Each Shift
6cc26bc3-694a-5014-88a7-c75c356a7534 | note | Acceptance Criteria - Installed HaTelit surface to be inspected and areas recorded where required for flatness and saturation.
62e91eb3-bb8c-5335-bf92-533c6c9b0787 | note | ○ Surface to be free from any loose or deleterious material.
094b8f7f-f4c0-5218-89d1-1c7a863ed108 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.3
186f480c-5404-527e-8c9c-f1c7141f1022 | note | Inspection/Test Method - Visual Inspection
7df486d6-2118-5d81-bdeb-1d15587811b3 | note | Record of conformity - This ITP signed
bcf895da-238c-5d8d-88e1-9c37f6ac5049 | note | WP
cb496516-171a-5bd1-9507-a50b59222499 | note | Responsibility - Project / Site Engineer, Principal’s Representative
f3049765-5ece-52ca-98fc-c84b9ee6d654 | date | Date Completed:
08348277-ec6f-4c95-9dfb-f225c5eb239d | checkpoint | 4.5 - Spring Balance Adhesion Testing
bf3a9662-78c4-5774-a483-e0b9d2e55bbd | note | Frequency - 1 every 50 to 150m2
e080bfca-23d5-5051-bc13-9a490953d3b3 | note | Acceptance Criteria - Test locations to show adequate bond between HaTelit and tack coated surface.
7dd62148-0c53-50d4-b3ff-fee5855fba59 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.4
c0e76782-aacb-5d02-ba11-2648a44cef57 | note | Inspection/Test Method - Test Point
536a00b3-43ae-5ee8-b903-a03f8dd73190 | note | Record of conformity - This ITP signed
e1c8dbcf-db55-52a0-b938-3d6380baa1c9 | note | WP
50ee9d3a-2266-5752-b9db-2033d405a278 | note | Responsibility - Project / Site Engineer, Principal’s Representative
91898df6-2d34-5c79-9046-1c055b1f35cf | date | Date Completed:
a406d039-6ebe-4cba-b395-9e7ec98e7d10 | checkpoint | 4.6 - Asphalt paving over HaTelit
cea011ed-3dba-57d8-8670-e9b0fe1fd275 | note | Frequency - Each Shift
a3d59164-7e33-55cd-a69b-4a90064960e3 | note | Acceptance Criteria - Ensure that the surface of the installed HaTelit and the underlying asphalt layer is dry, clean, undamaged and free from loose material until the completion of paving over the installed HaTelit.
1f27c1e0-76e0-52c6-9edf-38387e05e15d | note | Reference Documents - Huesker HaTelit C Specifications 1.7.5
b5386e15-c8dd-5d4a-921e-6bdfb6bf111f | note | Inspection/Test Method - Visual Inspection
a0c8e412-a38c-5766-9472-25f18c4316d8 | note | Record of conformity - This ITP signed
f05e026a-276d-5e0e-90b4-f58f5ca70c97 | note | IP
d48bc467-ef2b-5a70-9d5e-02fec495a012 | note | Responsibility - Project / Site Engineer, Site Supervisor
7c4c1939-313d-5e55-b683-d22464184d3d | date | Date Completed:
b6db0038-bb2f-439e-9f37-af756f09e6e3 | section | 5.0 - Quality Assurance
8b6bdac1-8694-4698-9d49-3209be89fdcb | checkpoint | 5.1 - HaTelit Surface Conformance
20c67dec-9398-5456-8e61-a2ec224ed04f | note | Frequency - Each Lot
956a2fba-cc72-5356-bb16-b6d35517ee67 | note | Acceptance Criteria - The Contractor shall assess the conformance of the surface flatness and saturation of the installed HaTelit surface
4a200501-bd0e-50a1-8e3b-a7cc6316a7d1 | note | Reference Documents - Huesker HaTelit C Specifications 1.12.1
c14e827b-6ef4-51c2-bd6c-bbe5a77c4961 | note | Inspection/Test Method - Survey Report & Visual Inspection
43d53241-1fb7-5087-a6c3-fe4a887a5cc5 | note | Record of conformity - This ITP signed
68e22f3a-0ddb-58f1-ae0c-94b555197b70 | note | HP
9b84d4fd-5492-516d-832d-373d4dc519d5 | note | Responsibility - Project / Site Engineer, Principal’s Representative
4fc0e46b-780c-548b-a2f7-d098d369a1dd | date | Date Completed:
2914a338-9bc7-4878-ac1d-44c51d437206 | signoff | AUTHORITY HOLDPOINT
c510222d-7d53-409f-babb-145b8f045d5e | checkpoint | 5.2 - Nonconforming HaTelit Lot areas
e90312d1-0277-5893-9eb9-7a73142177f2 | note | Frequency - Each Lot
ac5147ee-d2cf-5942-9748-337340752818 | note | Acceptance Criteria - If required, any sections deemed nonconforming shall be removed and replaced according to Manufacturer’s Specifications - FH NCR Procedure to be adopted when lot area is deemed nonconforming.
9e04a652-662a-5ee2-a8cd-6251d87df491 | note | Reference Documents - Huesker HaTelit C Specifications 1.13.1
3d6f2628-3913-57d9-8f68-2b5c1c37917a | note | Inspection/Test Method - Visual Inspection
c409c60e-a456-519f-b0fd-cde38fd8a1f8 | note | Record of conformity - Nonconform ance Report
58d9cb3b-1b7d-543a-9ef7-9a37c5c184ec | note | HP
e5c153ea-14cf-598d-aa8a-53e828231c3a | note | Responsibility - Project / Site Engineer, Principal’s Representative
115d9055-3e44-5308-a2a4-13496030db40 | date | Date Completed:
f02561f4-f59f-4692-96ed-a5877fc14740 | signoff | AUTHORITY HOLDPOINT
50e79eb9-6ce9-45ac-83f7-92e11a3f7043 | checkpoint | Final Inspection
173b0058-bb77-5e89-bd98-2e79ba84542b | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
934f17bb-c4dd-5150-b8d8-e299a363d351 | textbox | Print Name:
66cb06fd-c54e-51d3-88ad-6d43e3a33b94 | textbox | Position:
b1d141aa-a90f-5146-8be8-f61e957ac211 | date | Work Completed On:
602f60e6-bc64-5dfa-98f3-3fcd848960c7 | date | Date:
3a5a8c4d-f5de-43d5-8221-26c5eda8b31a | checklist | FH-ZU2-QU-ITP023 - RBB Install - Rev 1 | itp | ITP023 - RBB Install
dcdaef01-6bd5-4a06-ac1a-58e2c5b6d29f | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
4fcd1e68-80e5-4bb7-8e19-d3bc4cf48d97 | checkpoint | 1.1 - Check for correct documentation
076989a2-7070-5129-8757-c1049d765e54 | note | Frequency - Prior to commencing works
8ab324a6-d792-50c9-9522-bf1d24063433 | note | Acceptance Criteria - Current revision drawing is being used including the Subcontractor’s copy.
2cc89f1a-6980-5a3d-bd29-76588fb9e1f7 | note | ○ Current revision to be obtained via Aconex.
096b2722-38a4-535f-8eb8-cd5cc091787c | note | Reference Documents - Current Revisions in Aconex or ACC
e120386b-0744-5b4e-b0ca-e871cd1caa9a | note | Inspection/Test Method - Visual inspection
671d1b0d-4961-534e-b4d7-950c894a8383 | note | Record of conformity - This ITP signed
68c78ca3-feab-53e1-9e4d-96f99bb3f966 | note | HP*
fe5140a3-526f-5dac-a580-d55946e8ee60 | note | Responsibility - Project / Site Engineer
2dbdf7a6-7f02-5f6b-a503-5106c718f14c | date | Date Completed:
8b85f332-4477-4c84-9f4a-ae9595c78b88 | checkpoint | 1.2 - Implementation of all measures and controls
d021a529-7fe6-5df3-a58c-23cb69fb83ca | note | Frequency - Prior to commencing works
83549a14-23a5-5f24-8c24-7d95e54f9c48 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
a74f2587-6a16-566c-8605-a831de28358e | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
99ed3f38-ac8d-5a3e-a4fd-43207a8ec220 | note | Inspection/Test Method - Visual Inspection
d7084fb2-a245-5971-95b0-d1dc5e55922a | note | Record of conformity - This ITP signed
ed1458d1-45b6-561c-9e4b-3506c8524308 | note | HP*
fc337892-9734-581b-8dac-79a5aff5f45f | note | Responsibility - Project / Site Engineer
e6b73a27-a34e-5b03-a259-8c5bce6c73e9 | date | Date Completed:
94262c83-1e3f-4cbe-a5a4-c4a1eb3f0901 | checkpoint | 1.3 - Definition of the work area
1a5e2cc3-a3fd-5a1e-ab3d-4bd57f1374b8 | note | Frequency - Prior to commencing works
c1f23998-33aa-52ea-9436-28846c4be2b8 | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of work clearly defined.
ac3357d8-f66a-577d-bcdf-cc5fa629b795 | note | Reference Documents - Drawings
6dc96475-832e-526b-89de-c4d1d3c65e6b | note | Inspection/Test Method - Visual Inspection
7bd6fbca-c7a4-53ed-bc19-ec0fac2aadd9 | note | Record of conformity - This ITP signed
b28ac2c2-baa6-56ee-88cd-8894704fdf97 | note | HP*
9e86b5cf-f894-5bbd-9b70-0ef43b2e7bd2 | note | Responsibility - Project / Site Engineer
fbfab279-813c-5a6c-b752-f8a105943905 | date | Date Completed:
fed9bf3e-e7d7-4c36-bf3d-e9beb1ab0dd7 | section | 2.0 - Materials
d336e5a0-3f30-4c5c-944e-7199ca2e0a06 | checkpoint | 2.1 - Rubberised Bituminous Sealant
46c20e35-100d-5502-bd8e-5393ddc96e42 | note | Frequency - Prior to commencing any activity
b71ea934-32f1-5210-b963-72e8919cbd94 | note | Acceptance Criteria - RBB must be a proprietary polymer modified bitumen (PMB) crack and joint bandage product and have the following properties:
931300e2-bc2b-5eea-8773-a3866c81c6db | note | – Minimum softening point to be 95°C
68e41a9d-6658-57cc-96d6-b9cca9083f2a | note | – Penetration at 25°C between 20 and 50
f5c0e729-388e-57a6-a283-d1c9cd6566aa | note | – Flow at 60°C at 5 hours to be maximum 5mm
c5dfb34f-e2f3-57ed-b2db-511b538a26d4 | note | – Viscosity at 180°C to be maximum 3Pa.s
061fb492-70d9-5864-9a6a-df7276616a1b | note | Reference Documents - Beca Spec 002 – 10.7
09d4a1c6-e2ae-5cf3-9065-6707c3a6b62a | note | Inspection/Test Method - Verify
2742e306-541f-586e-9807-e4c0a6981811 | note | Record of conformity - Manufacturer’s Datasheet
71220d4d-abc3-53ca-a04d-63f612aa2817 | note | HP*
3f673356-3a53-588c-b1a5-c807cb95ed90 | note | Responsibility - Project / Site Engineer
a5499590-02f5-594e-bde8-60eb9d06ec3e | date | Date Completed:
01d7c12d-26c6-5652-9d64-72480eb0bb01 | note | Principal’s Representative - BecaCPL-GCOR-001062
56fc0e9a-9b61-4a0d-917a-8ed0fa3a3cb9 | checkpoint | 2.2 - Material Sources – Conformance Test Certificates/Reports
787aba00-eee8-599f-9626-ebfc860c4e09 | note | Frequency - Prior to commencing works
8d2628a7-7a9d-5065-b1c4-e9bada109c94 | note | Acceptance Criteria - Test certificates and matching production batch numbers are to be provided for each product used
b5da5be3-4bfa-5164-84b7-63e3f2f33e06 | note | Reference Documents - Beca Spec 002 – 10.7
e148dd43-abe8-5f65-a485-4db1ea878bc9 | note | Inspection/Test Method - Test Certificates
5b40d57f-5c0a-5c55-a20d-7016a6410114 | note | Record of conformity - Aconex Reference
0a98c9a0-b359-5379-ba41-d76fe29d580c | note | HP*
999e91f5-4f36-5ac9-990b-3c7fc6f3bacd | note | Responsibility - Project / Site Engineer
d68b3006-3f52-56ae-855d-2424ee86b33d | date | Date Completed:
d365a1f9-54af-4dce-8c2d-8d60f70cd91f | section | 3.0 - Sealing
482c8dde-014d-4e9d-aaf5-7aa772f825d3 | checkpoint | 3.1 - Applying Sealant
9a756b36-40eb-5ada-9195-c5104d5ba09a | note | Frequency - During joint sealing works
0893c822-f2d4-51a7-9f7d-f0f065e672b0 | note | Acceptance Criteria - Sealant bandage is to be between 50mm and 75mm wide or as per drawings.
146426d9-4d8c-5f10-9952-2fbaf0e58cac | note | Reference Documents - Beca Spec 002 – 10.7
aa6fd26e-650b-5f09-b33e-e6cb2367c1fd | note | Inspection/Test Method - Visual Inspection
ecf7c0e0-50c9-5c76-8e93-2dc32c98dfe6 | note | Record of conformity - This ITP signed
392d5474-73d9-5241-9f11-47852ba9d032 | note | IP
eda2d52e-1965-573b-b5d3-858102d764b1 | note | Responsibility - Project / Site Engineer
2e27a488-3a39-50db-bd91-6adc8dadd495 | date | Date Completed:
413e0bb0-b3d5-443d-aa69-3d467ceec380 | checkpoint | 3.2 - Protection of Applied Sealant
f1bf55ba-e32a-54be-b92b-6cf9a53b2035 | note | Frequency - During joint sealing works
86bc56ab-d80d-5518-a3f1-a3832a896dd7 | note | Acceptance Criteria - Installed sealant must be protected from damage by traffic (and possible pick up on construction vehicles and aircraft tyres) until it has cooled to ambient temperature.
28e6b8be-ef23-5c14-9757-264ce692aa0f | note | Reference Documents - Beca Spec 002 – 10.7
21247d4d-52b7-5de3-b28e-491a0dbd1bd0 | note | Inspection/Test Method - Visual Inspection
fbce94d7-4564-5fe6-9232-5f0c9e52eacc | note | Record of conformity - This ITP signed
67197ec3-d4e2-55db-8401-6d2a3017c736 | note | IP
686a0439-61b6-57ff-a2af-46e13d05cd0d | note | Responsibility - Project / Site Engineer
01725427-4a4e-5d92-9954-6b43381320f6 | date | Date Completed:
8b87b40c-e1f0-4db7-8933-2393d3bcfa9f | checkpoint | 3.3 - Cleaning up
2e7b0d4f-6245-586d-bb38-cc655cc828d1 | note | Frequency - After sealing works
289efcc6-085b-5160-993c-8d3aa14f68af | note | Acceptance Criteria - Any sealant split on surface of pavements must be cleaned off immediately.
11fde04e-72b0-5aef-8cae-99a6b2ef0e3e | note | Reference Documents - Beca Spec 002 – 10.7
8fc5b485-d548-5b58-8d77-4001e75598f4 | note | Inspection/Test Method - Visual Inspection
8d9245d8-afa5-5d65-b818-788d066cb935 | note | Record of conformity - This ITP signed
2e0246b9-3808-5855-90ed-36022d27595d | note | IP
3763f5e2-7141-5813-a984-71c768f5d0dc | note | Responsibility - Project / Site Engineer
dbc7c48c-8731-5ca4-bed5-493b207f3e2b | date | Date Completed:
279b1e7d-3230-4c14-affb-ef5dac9bef03 | checkpoint | Final Inspection
aba71fc6-9e1b-5918-889f-808b781c76fa | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
13f73ea6-e61a-50b4-bd59-d5feef7e77d2 | textbox | Print Name:
ad82700b-e91c-5752-8002-6277c2b5121a | textbox | Position:
9a55fab0-5494-5ac2-8676-5f7538c7ee96 | date | Work Completed On:
ef1ec8a0-88f4-5097-b918-f4eb4872b7d9 | date | Date:
0167ee88-4c50-4b65-8a52-3446ac6d1a17 | checklist | FH-ZU2-QU-ITP024 - Line Marking - Rev 1 | itp | ITP024 - Line Marking
a299e125-7c64-4afd-a2e2-d4471a03b878 | section | 1.0 - Preliminary Activities
f0317af8-8c31-415c-8892-cdceda1b2037 | checkpoint | 1.1 - Check for correct documentation
1c95aad2-4d03-5f6a-9184-2163d9fd3936 | note | Frequency - Prior to commencing works
d0a8f690-1a31-5e04-85be-55feedda7db2 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
a34ab5a9-d383-521f-b12f-ea63c1852b56 | note | ○ Current revisions of these documents to be obtained via Aconex.
6a5efa0e-2e4c-5200-8112-ba29953976f5 | note | Reference Documents - Current revisions in Aconex
cc825b48-d061-5643-a41c-9df4bb176038 | note | Inspection/Test Method - Visual inspection
d4c00f5f-8db5-55ba-9f3b-f2269bdb26aa | note | Record of conformity - This ITP Signed
831ca973-204b-5441-b6c9-f7bca1db966a | note | IP
e274bf2d-29d7-5392-89bf-82cba6c946f5 | note | Responsibility - Project / Site Engineer
607ab3b5-faca-5e7b-aaba-0196390c8611 | date | Date Completed:
7354dc44-71cf-471b-abfd-980d23843a87 | checkpoint | 1.2 - Linemarking Plan Approval
37f17cd7-b5a0-5e46-a18a-e66ca4a5960a | note | Frequency - Prior to commencing works
ec63fb9b-7fde-5502-a4fe-9834104b2b06 | note | Acceptance Criteria - A linemarking plan showing which lines are to be removed and which lines are to be applied needs to be approved by the Contract Administrator prior to commencement.
6c7fbfcf-1f53-515b-8442-50d21b0d5767 | note | Reference Documents - FH Internal
b592e6c7-972e-5a74-87e9-944ea4a9e884 | note | Inspection/Test Method - Aconex Correspondence
f6b2ac78-5899-59d3-b86d-98e25f7e44c2 | note | Record of conformity - This ITP Signed
fe376690-52ba-51db-b942-732a5ff9c76a | note | HP
167646d4-47fa-5192-804d-4572606fea56 | note | Responsibility - Project Engineer, Principal’s Representative
35cc15ee-56dd-5cbb-a4f5-15a4e018d3f3 | date | Date Completed:
cb2a21f6-fb4c-4544-b255-69d3f20df216 | signoff | AUTHORITY HOLDPOINT
ff5bdf16-6926-4b6e-a4b6-b993ccbe9f46 | checkpoint | 1.3 - Implementation of all measures and controls
8f3f67a2-b768-5bbf-a5dc-976aaf2d4913 | note | Frequency - Prior to commencing works
d92786a5-edfc-5401-bbee-d0b187d71770 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
9030c3d9-e64b-5b45-8190-fee14814841c | note | Reference Documents - PSP, EMP, TMP, WMS, SWMS
203d6f66-289e-55f8-a2c6-edf495358df2 | note | Inspection/Test Method - Visual Inspection
4ce9e843-66f8-5480-a9c9-3d8ce4d46202 | note | Record of conformity - This ITP Signed
ddef3d95-5462-5444-ac10-e1b7bf678e44 | note | IP
1ba9a100-05a0-5da0-ae3e-c9feded8f14a | note | Responsibility - Project / Site Engineer
2564380b-255b-5b79-a891-29176703d3e9 | date | Date Completed:
b105acad-d456-4c83-87de-0cec95778938 | checkpoint | 1.3 - Plant and Equipment
b0975770-804c-5145-bd18-e380afec0178 | note | Frequency - Prior to commencing works
2ee3312b-928c-5762-97d5-d1e1dbb34aa6 | note | Acceptance Criteria - Plant and equipment used in the works are appropriate to achieve specification requirements.
02023e64-f85f-55ea-b6f3-577de5e9b79c | note | Reference Documents - Beca Spec 002 15.3
54f9fefa-6bd7-58ee-ac6b-55c3d18cd4a3 | note | Inspection/Test Method - Verify
a027c058-e51d-55d2-a7b4-9afbdacfdd04 | note | Record of conformity - This ITP Signed
4a601782-6b71-50c4-8cf3-6ac74ba3bb1c | note | IP
670cb1e9-174f-5cd6-aadf-0fba227ba420 | note | Responsibility - Project / Site Engineer
0b713300-d79a-5720-af08-80567420d30a | date | Date Completed:
2760ee2e-8cc6-4a9c-bbc4-73a92d7bb4bf | checkpoint | 1.4 - Materials
cf0db8c5-4235-5b49-8379-e0c6a63d77bc | note | Frequency - Prior to commencing works
8445c45a-206a-5068-8bac-e82e32f02b94 | note | Acceptance Criteria - The paint to be used shall be a premixed synthetic latex-based paint (such as WATTYL AIRPAVE or approved equivalent).
fd5aa652-fc05-5132-b3fc-55a67cf8ecef | note | Reference Documents - Beca Spec 002 15.4.1
2d68c304-ecbb-5a28-a723-c0cb0809ff08 | note | Inspection/Test Method - Aconex Correspondence
07bb3d86-0c29-5fdd-8abd-36257538cef6 | note | Aconex ref: FHPL-TRANSMIT-001678
a4a67aa3-dbc1-5d6b-885e-a4896aabb98c | note | Record of conformity - This ITP signed
36200506-3e84-57a9-b113-8c5ef71c3417 | note | HP
24576453-a408-5e01-8d8c-9e5e7e054fda | note | Responsibility - Project Engineer, Principal’s Representative
8ef096ed-e8ec-51b4-afeb-ae2f3ad275d6 | date | Date Completed:
913d4602-695f-5337-8706-fed16c659486 | note | Principal’s Representative - FHPL-TRANSMIT-001678
d5b4157b-e53a-4848-ac04-442f47508617 | signoff | AUTHORITY HOLDPOINT
adfb61f7-c09b-4e39-89ab-d77d74981ca6 | checkpoint | 1.5 - Material Handling
1112afe0-cc4d-5df4-9411-2bd33eca6780 | note | Frequency - Prior / During works
9052b74d-63f3-5f90-9c22-4d154eef1746 | note | Acceptance Criteria - The paint Is to be packaged in 20 litre containers that are of durable construction without sharp edges. Paint containers are to be clearly labelled “Airport Pavement Marking Paint” as well as being labelled with the following: Manufacturer’s name, Colour, Batch number and Date.
5d3c3329-5657-5cb9-9efd-e1346664a23a | note | Reference Documents - Beca Spec 002 15.4.2
1ff988d2-c6f4-5281-a330-6ca62588a509 | note | Inspection/Test Method - Visual Inspection
03229cbf-536a-5571-becc-40707289d0f2 | note | Record of conformity - This ITP signed
97df309b-9d4b-593c-a0f0-808e1d7dc9ca | note | IP
1c44103e-32fc-5db0-9965-35c9b0f60ad5 | note | Responsibility - Project / Site Engineer
46e585b5-3519-546c-9bee-296fe203fddb | date | Date Completed:
bc71a1b5-eb4e-44dc-a17c-45095bbea9e3 | checkpoint | 1.6 - Survey and setting out
359fe79d-356a-54e8-9f56-35f73c1ddb11 | note | Frequency - Prior to commencing works
62050159-c89f-51dd-ab80-8b0cf01c3671 | note | Acceptance Criteria - The Contractor shall carry out the setting out of the pavement Markings as shown on the drawings. This shall be approved by the Principal’s Representative.
9355a37f-b923-561b-bd56-55b8ab6a06d4 | note | Reference Documents - Beca Spec 002 15.7
0e2fa374-70f7-5468-8f8a-24e27672b3db | note | Inspection/Test Method - Verify
83f9096e-647c-58f5-8aad-ef7b49339da0 | note | Record of conformity - This ITP Signed
0b27f0fd-f8e0-54c7-81d1-ff17491437ae | note | HP
b94edfcb-2744-5677-b3bb-10193da5d706 | note | Responsibility - Project Engineer, Principal’s Representative
6ff6d711-c088-587c-9075-46b39836b935 | date | Date Completed:
83c92210-7c93-443c-9583-637380fc5bde | signoff | AUTHORITY HOLDPOINT
5f7c8c18-50d4-4fd6-9258-c165f78903c7 | section | 2.0 - Construction
6f813773-e496-4db1-bf52-3f85374433a3 | checkpoint | 2.1 - Removal of Existing Line Marking
f93552ff-2dc0-5ef4-8a03-60614968b111 | note | Frequency - Each Lot
d7d59580-70a4-5e65-aa24-2fe9d10d1d9a | note | Acceptance Criteria - Existing pavement markings, at the locations shown on the Drawings, shall be removed by water blasting or other approved means that is non-destructive to the existing pavement surface.
824f8fcc-dba6-5e2e-877d-311790c59662 | note | Reference Documents - Beca Spec 002 15.5
1949ecf6-b6cb-5b1f-8243-b714444f192d | note | Inspection/Test Method - Verify
cda23d5c-51e3-5dd6-8ba2-7b8e4d8f55f4 | note | Record of conformity - This ITP Signed
9fd8c0ab-7e78-59d5-bbb5-e781bcadd297 | note | HP
45f07539-bab1-58bb-a242-2863705837c6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
60b4b4d7-2c2e-5794-87c5-408a629ea992 | date | Date Completed:
ef1902be-f39f-48bd-95a3-dc072b9b7252 | signoff | AUTHORITY HOLDPOINT
1972b639-66e8-4c44-9f71-a9589c08b9b8 | checkpoint | 2.2 - Surface preparation
a7cd42a2-4467-5d0c-9123-fd5fd5517a17 | note | Frequency - Each Lot
0047f222-e84c-50c7-bca1-92b122b6e308 | note | Acceptance Criteria - The surface of the asphalt or concrete pavement in the areas to be painted shall be thoroughly cleaned prior to the application of the pavement marking paint. This shall be approved by the Principal’s Representative.
dc708d1c-009c-558c-9fc0-ea136e878581 | note | Reference Documents - Beca Spec 002 15.6
c510abd7-c15d-5386-b960-797f54ddaa70 | note | Inspection/Test Method - Visual Inspection
ba692d16-82b4-5117-8538-bdda2d74a71d | note | Record of conformity - This ITP Signed
040b17db-4273-57dc-854d-f5c26dedf176 | note | HP
2a635c34-e75c-5367-9fe9-7aa6fb5009d6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
eda5414d-0f9a-5cdf-b388-427d18290fb6 | date | Date Completed:
bfa4638d-d74f-410b-8e38-6c2041ef95a5 | signoff | AUTHORITY HOLDPOINT
c58ae312-07cc-448e-b608-0d03c1a712a5 | checkpoint | 2.3 - Weather Conditions
5f5d2f60-115f-5941-9ad4-9bfa1444d790 | note | Frequency - Each Lot
2389c5e2-5911-5def-8db4-147198dd3d01 | note | Acceptance Criteria - Pavement marking shall not proceed during wet weather or when the pavement surface is wet or when rain is likely or during high winds.
ba28dc58-594a-5cd5-88a5-905c735c0ee5 | note | Reference Documents - Beca Spec 002 15.10
7e221c9e-7fdd-5fc9-82a2-6afe5041f16b | note | Inspection/Test Method - Verify & Visual Inspection
bb8215e6-a5e3-53d6-8580-a4bbc9277bad | note | Record of conformity - This ITP Signed
d8ef71e6-4abc-5786-abef-1aedafc23270 | note | IP
0290e50d-b501-529e-a8e8-1175415fa108 | note | Responsibility - Project / Site Engineer
83244b9d-88ec-5d66-be11-ee7e40b9440f | date | Date Completed:
e99a8e2e-5747-4615-9f71-8bf4f6a7ba2d | checkpoint | 2.4 - Application
cfc6a77b-a432-5242-b898-367538f2f851 | note | Frequency - Each Lot
6a5972e3-5300-5d24-b237-7a908e61f527 | note | Acceptance Criteria - The paint must be applied in two even coats to provide the required minimum total dry film thickness for the two different paints are:
170c31ca-aa67-5b7d-bac1-5a6783623d2e | note | – Dulux Roadmaster dry film thickness (210µm)
512af01e-eff5-57ae-bbfa-11ad07c3a1f7 | note | – WATTYL Airpave dry film thickness (60µm).
14cdb87d-2623-5f58-933c-68db27764cc8 | note | ○ The second coat is to be applied no less than three days following the initial coat.
b7ea9683-aa0e-5bf3-bda6-4bddae569b41 | note | Reference Documents - Beca Spec 002 15.8 / Manufacture rs Specs
2c30166a-3203-5547-ba76-a8f32407e78a | note | Inspection/Test Method - Visual Inspection
6b1634ca-913d-5754-b1af-a287d16e0706 | note | Record of conformity - This ITP Signed
460f4178-c9b1-5fb4-b4c6-3ae52b2505e6 | note | IP
91bfbfd2-b001-57d0-b256-374661ed3ce4 | note | Responsibility - Project / Site Engineer
0b933190-6814-5f5d-a6c6-575eb6ee43b8 | date | Date Completed:
8fc6fb5c-3f14-4012-9598-7da5b74c387b | checkpoint | 2.5 - Application Rate and Conformity of Application
2d92bcc1-6de7-5e3c-bdd1-be5b141c705e | note | Frequency - Each Lot
a97115b8-8eeb-5c19-b6fc-1f3b91012ac9 | note | Acceptance Criteria - Daily records of paint usage and the area covered shall be maintained by the Contractor.
e38371ea-78c5-52a5-8e44-85c7d55d1dee | note | Reference Documents - Beca Spec 002 15.12
3e39d713-f152-59df-b0ab-baa370a5c716 | note | Inspection/Test Method - Verify
82678e9e-a5c7-55e6-beac-4a0883bca80b | note | Record of conformity - This ITP Signed / Daily Records
34646071-82ff-55ba-9b97-277227e24c1f | note | IP
605058c2-584f-5f7e-b3ce-a2c570d849d6 | note | Responsibility - Project / Site Engineer
474613d1-4204-56ce-b1d0-64d4ce23d864 | date | Date Completed:
3e5f7e68-ecb1-4aee-8a2c-0cf4539844ce | section | 3.0 - Post Construction
4d8cb768-212d-400c-8ed8-80492a32d25f | checkpoint | 3.1 - Records
d5c7358e-1f33-5705-b408-736e05383966 | note | Frequency - Each Lot
f0e2c474-7bbc-50d4-a553-e33a9c9177f0 | note | Acceptance Criteria - Finished pavement markings shall conform to the following tolerances:
3ad955ea-ebde-57c9-b83c-9f928b34b751 | note | – Location of pavement markings ±10mm
ad1896b1-7d54-5a4b-9b5b-1d3f23cbee34 | note | – Width of any line or line forming an alpha/numeric symbol ±5mm
ea691ebc-baf6-5caa-86fe-55cd05d00ee0 | note | – Length of any line and the spacing of broken lines ±50mm
c7270f38-4826-50db-acfb-341b7db8a2b4 | note | – Dimensions of any alpha/numeric symbol ±10mm
72ef3a4c-66d1-513e-9f04-87c08fac1111 | note | Reference Documents - Beca Spec 002 15.9
116fcd21-9260-51f7-b9fd-f964684f4433 | note | Inspection/Test Method - Verify
df62826e-24db-52d0-9f4f-6a277fb28ad2 | note | Record of conformity - Survey
95e9d011-caa7-5ff1-bfaf-4142677fbd19 | note | SCP
83102d1e-685a-567c-b93c-4e15bd4b8642 | note | Responsibility - Project / Site Engineer
005a68c9-7e8e-5686-a098-fc13c86c10cb | date | Date Completed:
484101ca-0126-4182-84a6-58c3c059b05e | checkpoint | Final Inspection
fc3dbe4d-1b31-544b-b7ca-9ac225ab4b25 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in a ccordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
50301623-e6bf-51a3-adb5-4d912e8f3190 | textbox | Print Name:
7becb5e9-8fd1-53c6-add9-4aca6843ab22 | textbox | Position:
2f040c82-6f78-5cb0-b295-195fd2363c42 | date | Work Completed On:
4b6a41e3-e571-5d4e-a0f0-1ed4cd73d2bf | date | Date:
9c50517b-d80f-55e3-90fa-62076d1f1ebb | checklist | FH-ZU2-QU-ITP025 - AGL Conduit and Boring Installation - Rev 0 | itp | ITP025 - AGL Conduit and Boring Installation
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
b8a32079-1aa5-57e6-8a66-15d046efe9a4 | note | Frequency - Prior to commencing activity
dca089ff-fabe-5dfd-9155-fd95e5e738e2 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
dba1a5c0-d0de-5d6d-b571-cae043ee78fd | note | – using the correct and complete set of drawings.
99e63a8b-aa25-5791-87ed-2128adff683e | note | – all drawings are the latest revision.
0d37360b-f68e-5e84-8b12-8e39c9daf073 | note | Reference Documents - Drawings / Aconex Register
e1eaf8d7-ca21-5f67-8a56-b4657842d17c | note | Inspection/Test Method - Verify
8d9414de-68d1-5128-86de-09bf100caffa | note | Record of conformity - Drawings and drawing registers
cac2c81a-95d7-527f-ba64-e416799584f2 | note | HP*
7f726786-8251-5e46-83af-455cd1302016 | note | Responsibility - Project Engineer
10a06d2c-0727-5f35-9bdc-3e4672b3a79c | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
9e830bc9-6113-5cb4-9a34-eba9ba021b42 | note | Frequency - Prior to commencing activity
9418b1c8-716b-5ea0-a719-ba1ccd42d304 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
81fa21ec-76e9-5833-816a-8d4f88d14f18 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
5b75c70f-9e38-5946-9d65-a6a3204df160 | note | Inspection/Test Method - Visual inspection
1deda285-60ca-5351-b3d3-e42caadce55e | note | Record of conformity - This ITP signed
3767b002-064d-5f2b-a08e-c974d9b21578 | note | HP*
4cbb564b-8fa9-59a0-893a-1706d763fe3f | note | Responsibility - Project Engineer
343fa595-a04c-5db6-b296-f79f8b91a9a9 | date | Date Completed:
a3708d55-ad49-5ddc-9f9e-a05b95777606 | checkpoint | 1.3 - Definition of the work area (survey)
2a01ebfc-039d-5ba5-a171-e3056faf5778 | note | Frequency - Prior to commencing activity
ff5b4170-c852-50d2-86d7-a1bfe1389ea8 | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined.
2360f750-b416-5fe2-bb88-558bdaeec326 | note | Reference Documents - Drawings
d84c98fa-fcb1-575a-a417-1f8ecf6ca0a3 | note | Inspection/Test Method - Visual inspection
79ded8b4-2e16-52fe-b9f2-cb72048a09e9 | note | Record of conformity - This ITP signed
3de3e26d-10d8-5785-bd23-f9c04341127d | note | HP*
bf9859db-19aa-5d27-9a66-8544815d825c | note | Responsibility - Project Engineer / Surveyor
b31fbb3b-c423-5d91-a5ab-4207c71c863d | date | Date Completed:
69a20f57-e9c4-5c06-8e72-d3bebb914fa4 | checkpoint | 1.4 - Check conduit compliance
ca75f7e2-9fe0-5872-8553-2e25ec68ebeb | note | Frequency - Prior to commencing activity
bda3bffd-140a-5c53-a9d5-ed07bf6460c2 | note | Acceptance Criteria - Ensure that uPVC conduits comply with AS 1477 or equivalent AS 2053. Shall be heavy duty, orange for electrical services and white for communication services.
0a9b4a58-a26a-5475-97ba-dfaf945b9ef1 | note | ○ Ensure that pipe diameter is correct as per the drawings.
2228e221-89bc-5623-96c3-d7daf7b13c94 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.4 AS 1477, AS 2053
cf302bda-01b5-536e-9688-e3b16a7a9c35 | note | Inspection/Test Method - Verify
86110fe3-7368-5cab-a456-dd3623a8f731 | note | Record of conformity - Aconex reference This ITP signed
5af08d7a-b984-5b02-9978-fc0db3cb6214 | note | IP
593f0f5e-a639-5aa7-b8c4-36cdafa92cab | note | Responsibility - Project Engineer
cec57df8-208a-5528-9608-2e86de3bf819 | date | Date Completed:
82950bf0-d615-5ff3-a99f-7bf277f6815e | checkpoint | 1.5 - Check bedding material compliance
5f2c1b92-3599-5a8a-834a-427ad7a18190 | note | Frequency - Prior to commencing activity
6fb6c1f2-9d81-5b59-b99f-e5f49ee6ddb5 | note | Acceptance Criteria - HOLD POINT
020b801f-5412-5d77-9d2a-2145dfd4cc60 | note | ○ Ensure that conduit bedding material is non- plastic granitic sand complying with Table 3-1 and 3-2 under cl. 3.8.3.3 of the Works Specification.
8727225b-c976-525a-8b39-a8a70dd7c5b2 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.8.3.3
7636d754-0604-5df7-9841-02fb51f9bc27 | note | Inspection/Test Method - Verify
c4bc2b8d-464c-5b8b-a1ce-34e10567a9a9 | note | Record of conformity - Aconex reference
c202e6eb-af88-5ad4-b192-43b7eadbf787 | note | TP / HP
c7e23314-96b2-5d4f-95ae-b805ad0bb910 | note | Responsibility - Project Engineer / Principal’s Representative
f52f6ef1-99d5-583b-9def-0012f8fe7415 | date | Date Completed:
172b0902-de79-58d1-95cc-4735738969af | signoff | AUTHORITY HOLDPOINT
684111da-41f7-5ea1-aa5a-130ec2c9ca08 | checkpoint | 1.6 - Locate and prove existing services
b481a873-1b9b-587c-bb85-6db6664f6e12 | note | Frequency - Prior to commencing activity
079fe04c-e0fd-5abd-89d5-2beade7873ef | note | Acceptance Criteria - Location of services to be found and marked on the ground within the works;
cab71392-4f1d-5730-b896-8dc966adc310 | note | ○ Contractor to obtain excavation permit from APAM prior to any demolition works.
c12281a4-c363-5678-af29-17485de6279a | note | ○ Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
e3f2e297-de92-5390-a29a-e6ecffaa0e1b | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.15
f37db078-ea05-5781-947a-5141c960d86d | note | Inspection/Test Method - Verify
47c50d96-5b10-547a-b164-c366eded8ae3 | note | Record of conformity - Melbourne Airport Excavation Permit
6ae7ada3-828e-5efa-b02d-1f97814f83c4 | note | HP*
21f800ce-67b2-55b4-b05d-59bd92905a1b | note | Responsibility - Project Engineer / Surveyor
22b782f4-e33b-586a-9f54-a5ccbadb9f8b | date | Date Completed:
648931ca-ea92-5007-b762-3e625bbef167 | section | 2.0 - Construction
2b66cee4-ab86-506c-82c0-b3598e5d3273 | checkpoint | 2.1 - Excavate trenches for conduits
5bd4a899-f778-5d8c-b992-335b43cabe80 | note | Frequency - Each lot
47fee060-3be0-5cd5-92ff-7cc2ecafb650 | note | Acceptance Criteria - - Trenches for conduits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
08811dd7-8796-5bb3-8ac0-cdca7c1dae5f | note | ○ The level at the bottom of the trench shall not be above the required level at any point.
6b0450c6-a3f2-5f66-89e7-7f3673de58ad | note | ○ Any over excavation under pavements shall be restored using 5MPa lean mix concrete in conjunction with the embedment.
80e258da-eebe-5947-af44-4382d2235a85 | note | Reference Documents - Drawings ZULU-BECA- 001-SPC-00004 cl. 3.6
6ef7be7b-a588-5265-ac5d-3cdc2601cbf3 | note | Inspection/Test Method - Visual inspection
8be7f315-2c5e-5326-8ad1-19ab81608184 | note | Record of conformity - This ITP signed
4c8ef0f8-c97d-5915-a9db-4f39a711b06a | note | IP
01d592f3-fdb5-502b-82ac-c60be15407cf | note | Responsibility - Project Engineer / Foreman
21de2358-3437-5033-a795-74e2bc6a791b | date | Date Completed:
35a2a621-7af0-57be-b8a1-332a08eb0e12 | checkpoint | 2.2 - Existing services crossing new conduits
ad540ad0-90dd-5cfe-b7b4-cd38d1129a8b | note | Frequency - Each lot
8610695a-f5b6-5cde-aede-10dd232465a0 | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
15c7adb2-452b-5f6f-903e-0b6b2d59e030 | note | ○ Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
8c691458-22ee-56c5-8d0c-e75f284652b2 | note | Reference Documents - WMS002 – Working Near Existing Services
c4d3d455-51a3-5cf5-bc75-56a0a78aa1bc | note | Inspection/Test Method - Visual inspection
62d0f4e4-b8ea-51a3-badf-52674410f43c | note | Record of conformity - As-built survey report
cb8ad14c-84af-5a07-9bcf-1568b1c7441e | note | SCP
8a014a96-019e-5793-8c6b-9d9a6c7f2a18 | note | Responsibility - Project Engineer / Surveyor
b9cd8c33-d715-597c-b3a2-9debd806dc21 | date | Date Completed:
1d54f976-f7c0-5a5c-8aaf-b6c27df0189f | checkpoint | 2.3 - Laying and jointing of conduits
a6d44dc9-0037-5d39-8d4a-0172eede369a | note | Frequency - Each lot
f32cb045-a292-5246-87d4-d27f7f190010 | note | Acceptance Criteria - - All conduits shall be rigidly supported and positioned by concrete or plastic spacer blocks so that no displacement occurs during backfill.
a339ad4c-3e9f-59ea-b9f1-185bbda9515c | note | ○ Where conduit ends are not open to a pit, UPVC end caps shall be temporarily fitted to each end.
cff3ddce-2f19-59ad-b7ba-f60ad7f88809 | note | ○ Number of conduits and duct route to be confirmed for conformity with design.
a0edff87-a828-5c1e-8c99-46f0d6a2a643 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.7
9101403f-eeba-575d-82b0-a0702d54a132 | note | Inspection/Test Method - Visual inspection
df67a876-f59e-5da8-97cb-148c5ebf4c95 | note | Record of conformity - This ITP signed
2aeb0379-0633-5c03-af97-8446cd0ed6ba | note | IP
8e72718a-8e55-528f-8731-d5c59ffe18f2 | note | Responsibility - Project Engineer / Foreman
e4395f7c-9b90-5450-bc92-c1e031fe526d | date | Date Completed:
52ec0b35-2d23-569c-af3c-96adb7e7aae9 | checkpoint | 2.4 - Survey as-built
8ae894e3-637b-5fdf-a08c-96583d56b234 | note | Frequency - Prior to backfilling each lot
7d523446-7f0c-5c9e-839a-bcbb7c6c5b79 | note | Acceptance Criteria - Surveyor to pick up completed conduit runs before backfill
b3ba4b9a-ccd1-531e-96fd-fd243d60682e | note | Reference Documents - FH QMP
4d18d776-ce5e-598f-81ad-04054ca2922a | note | Inspection/Test Method - Verify / Inspection
3f74a3af-7a35-51d7-bdae-fd3f196f6863 | note | Record of conformity - Survey report
83f3fdd7-21a2-5f4a-b12e-2487dac36cee | note | SCP / IP
99848c36-7396-5e20-b1bc-49bfd1f61ff2 | note | Responsibility - Project Engineer / Surveyor
69571608-498b-5acb-b8a7-5ef9bf8be068 | date | Date Completed:
4ac71dda-3d00-5e58-b229-b9125906adbe | checkpoint | 2.5 - Pre-backfill inspection
63e1ddfb-324e-5352-9960-19ac059be51f | note | Frequency - Prior to backfilling each lot
6ca47f8f-1783-5edc-9745-8a5e7115652f | note | Acceptance Criteria - WITNESS POINT
30198f96-49f8-5a96-8f9d-8b6683ec08e9 | note | ○ The Contractor must provide the Contract Administrator with five (5) working days' notice of intention to backfill trenches within a Lot. This must include details of the date and location of the proposed work.
e44ee0b4-2433-5de2-ac27-d8b2b4fde155 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.8.1
8562ecdb-2c4f-5f07-b889-1f23e5f9f6ed | note | Inspection/Test Method - Inspection
652e0800-e063-5a07-ba7f-3bc1de37badc | note | Record of conformity - This ITP signed
43d6d4a8-04db-576a-b546-2c9247a84fc5 | note | WP
cdb2e9f2-10a0-504c-af39-93028bb6a316 | note | Responsibility - Project Engineer / Principal’s Representative
573ab9dc-8565-5dac-ad8b-861c41d100c2 | date | Date Completed:
e682c742-f93b-5e2c-89bd-4ca838794a9a | checkpoint | 2.6 - Backfilling conduits
9b79ab7a-473c-565a-a81c-bb41bd53e5af | note | Frequency - Each lot
84a78bd4-7be1-5deb-bfa2-179e60c267dd | note | Acceptance Criteria -
abc9cbbe-1707-5518-b988-c316816c6500 | note | – Concrete encasement of conduits: –
566010c6-75cd-57c1-8111-ec78c8b7c60f | note | ○ Conduits to be encased in 5MPa lean mix concrete as per drawings.
fa092b72-e40e-55ac-98ab-6d7b0007dfee | note | – Trenches in existing pavement: –
de46ec6a-dabe-58d8-8332-7a8328fca9ab | note | ○ Surface shall be reinstated to match surrounding pavement.
1e85192b-473e-51fa-b43d-fedae8eb6680 | note | ○ Unless noted otherwise, reinstate asphalt pavement surfaces to a minimum of 70mm (or to match existing depth (whichever is greater)).
59f28043-12cd-563f-a677-368f1909068b | note | – Trenches in new pavement: –
9fe060f9-0b13-5bae-a2af-be5f946c1a9c | note | ○ Pavement shall be constructed as per the drawings and specification.
26f5dcc8-5e5e-530f-9875-62c54f019961 | note | – In grassed areas –
565604c9-ed7f-5020-8def-0499a9cb91e2 | note | ○ Conduits to be encased in compacted sand bedding. The material shall be non-plastic and comply with properties specified in Table 3-1 & 3-2 of the specification.
12860750-fde5-5604-8134-1a02f743e65e | note | – Backfill layers: –
a744eb01-f590-5431-8686-57e6fd14281b | note | ○ Not exceeding 300mm compacted thickness.
db2c2dad-8f21-55da-88e2-08aee972a7b5 | note | ○ Not less than 90% maximum dry density (test no. 5.1.1).
4cf81bc4-7e92-5a64-a0bf-ff13456f981a | note | ○ Not less than 70% of density index (test E6.1).
dbbd9d0e-81bf-518b-aa0c-e8531768a32f | note | – Compaction testing carried out at a rate of not less than: –
1bb80dc0-28a3-57ad-9a07-c358bd21d958 | note | ○ Bedding: 1 soil test report from the supplier per 300m3 of dust supplied.
dedee7fb-9db4-5c23-90a0-35190daff671 | note | ○ Backfill: 1 test per 400m of conduit laid per 0.5m of backfill depth.
7550c732-f38c-537f-9200-c01e9ff9a7d8 | note | Reference Documents - Drawings ZULU-BECA- 001-SPC-00004 cl. 3.8.3.1, cl. 3.8.3.2, cl. 3.8.3.3 AS 1289 Test no. 5.1.1, Test no. E6.1
3a66f37e-934e-56f1-886a-3e68eae11bff | note | Inspection/Test Method - Verify
c5efc8e5-daf7-5e6f-ab90-b25e211022dc | note | Record of conformity - Test report Aconex reference, This ITP signed
5f74d6c4-d856-5fc1-8b57-bf837c2a8afc | note | TP / IP
1c9176f5-613e-565a-a8f8-7dec5cc6ab00 | note | Responsibility - Project Engineer / Foreman
e5b430f5-d150-5815-94e9-18ca37d37822 | date | Date Completed:
6db2beff-d160-5ad0-b44e-6a0604821a02 | checkpoint | 2.7 - Conduit markers & warning tape
45368ed3-77e7-5171-ae93-bcbf8cd8ee0b | note | Frequency - Each lot
29da3ecb-bb95-5c21-b2a4-32111784782f | note | Acceptance Criteria - Pavement edge duct markers shall be installed at the edge of pavements immediately over the centreline of duct banks.
59d30ef8-d784-5d37-8c08-6a0a18f2bed1 | note | ○ Warning tape shall be to AS 2648.1, and coloured orange for electrical/white for communications conduits.
28cf0053-f801-58d7-b6cb-b6e4e75f8fc3 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.11, cl. 3.12 AS 2648.1
433db3cd-880b-58a5-96bb-b64607ef2cca | note | Inspection/Test Method - Visual inspection
4c8cc8c4-fe17-5dec-9fdf-60b2222e0f42 | note | Record of conformity - This ITP signed
edc91752-a980-5b96-8dc6-f1574072c350 | note | IP
baaf9703-c6e3-5675-8495-e3496825ad94 | note | Responsibility - Project Engineer / Foreman
d5d45f2f-1e5f-5b35-b476-6a00e3449a19 | date | Date Completed:
94428992-2156-5864-9d44-a4e563d52ab6 | checkpoint | 2.8 - Checking of conduit lines
6ea7d1b1-ffa1-5921-83a5-3151011919a2 | note | Frequency - Each lot
de28fb13-ba74-59ad-8e7a-eeeab8d601aa | note | Acceptance Criteria - HOLD POINT
bcbeb64e-f56a-569b-8128-3ed37af656e4 | note | ○ Following installation, the conduit shall be checked by passing a mandrel (not less than 300mm long and having a diameter of not more than 6mm less than the diameter of the conduit) through each way, followed by a brush with stiff bristles to clean the conduit of any foreign materials.
38f811d4-24d1-5c07-9dac-4c36110837a8 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.9
6634aa92-d07c-546d-a377-973a89791ee2 | note | Inspection/Test Method - Visual inspection
66351acf-25c2-572e-ab3d-e8deb113b632 | note | Record of conformity - This ITP signed, Avionics Primary Trenching Checklist
b4c3b1d6-8dc3-5b46-9a4c-652f4e4c3e1e | note | HP
4bae3308-85c1-5999-a239-9a56912eb3a0 | note | Responsibility - Project Engineer / Principal’s Representative
c6c08a2b-8e73-5271-b9f4-e2d11ff92c70 | date | Date Completed:
11c0ea96-4007-5115-b506-238100aaa986 | signoff | AUTHORITY HOLDPOINT
dfb3fc63-1dd7-5f16-8bb7-58300a6a0328 | checkpoint | 2.9 - Conduit draw cord
8df5d2ce-8815-57bc-921e-dc99ad009ab5 | note | Frequency - Each lot
16282afc-900c-56dc-8833-be8ad010029a | note | Acceptance Criteria - Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be nylon rope and be 6mm in diameter, blue in colour. The ends of the rope shall be coiled at the bottom of each pit or wound around a stake.
68f2e7f4-e2ad-5085-8702-3990e8c8fc8a | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.10
5b24093c-85b7-51d8-84d5-238e6ef03f3e | note | Inspection/Test Method - Visual
89ce2275-1a9c-5b93-a389-9b14dc59ca27 | note | Record of conformity - This ITP signed, Avionics Primary/Secondary Trenching Checklist
883bc1e9-e8ae-54f0-a3c5-3319d36a752e | note | IP
33cd7518-82c4-584a-a692-fd104f0153a6 | note | Responsibility - Project Engineer / Foreman
d83875da-a9e6-515e-856e-19e14be8752f | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
39a43258-897d-53f9-8eb9-2a6c7ad42338 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
53ed455d-bef3-5f8d-9f79-194429c69199 | textbox | Print Name:
665cc1aa-388f-535b-8ea2-10b9cf3d21f6 | textbox | Position:
4f86ab93-9bc3-5ff3-b5ad-bb0b015601ba | date | Work Completed On:
24a47102-b649-5f4b-8d21-4dc7e7aff131 | date | Date:
c8da1dde-5978-4410-a455-d90d7dba90af | checklist | FH-ZU2-QU-ITP026 - AGL General Works, Testing & Commissioning - Rev 0 | itp | ITP026 - AGL General Works, Testing & Commissioning
47cea424-9504-4731-a931-416e1783d65f | section | 1.0 - Preliminary Works
08b4e3e8-9854-4c2f-b443-abb154f03522 | checkpoint | 1.1 - Enabling works
2f77fba1-3b6f-5057-9b68-59b2ee39b16b | note | Frequency - Prior to Start
05837fc3-b93a-5ba7-a385-392659bde697 | note | Acceptance Criteria - The contractor shall provide enabling work details for approval before commencing of any works where existing services to taxiways not part of the works will be affected.
9e2cce5c-a5e9-517f-b4ae-042e70c10d88 | note | Reference Documents - ZULU-BECA-001-SPC-00003
bda368e7-7b35-5d1d-a1b1-3b59cf7b53f4 | note | Inspection/Test Method - Verify
2c1e8158-88c9-500f-bd8e-e9c40cc75fe8 | note | Record of conformity - Letter of Approval
46732de7-56f5-5f62-a5c4-16708d3ea34b | note | AP
032af227-217b-5acb-96ce-03ea4a676d4c | note | Responsibility - Project Engineer / ADB Safegate / Principal’s Representative
ea5eca66-5fb0-5e81-905c-3ded4525d2ec | date | Date Completed:
9de08a4a-91c7-4c71-b6e8-6ed649b505e2 | checkpoint | 1.2 - AGL control system
fe2c9bc3-2ed8-52c7-9f6b-680720bca2f8 | note | Frequency - Prior to Start
4c1a6343-1ff8-5183-af41-2b7cfbafbcbd | note | Acceptance Criteria - Changes to existing AGL or new AGL being integrated into the existing system must be done so in a manner, which allows continual operation of the existing system.
6f012421-03d8-593e-aa30-30c6e267004a | note | ○ Prepare and submit for review, a detailed implementation plan showing proposed works methodology allowing continual operation of existing systems. This plan must include contingency to revert to a suitable system in the event of faults.
94bd7a08-72e4-5da4-bddf-395b341c9071 | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 9.6
f4569ec7-74a6-53d5-ae3a-7de0221c0529 | note | Inspection/Test Method - Verify
f5e596db-c279-56e4-8601-31e51b5ea97e | note | Record of conformity - Works Methodology Plan Submission Reference
a694d830-49c5-56bc-a450-acffa11965fa | note | AP
33ada6f1-5a3b-5e19-9f51-fa03f7ac5cf7 | note | Responsibility - Project Engineer / ADB Safegate / Principal’s Representative
d0f0dbbd-9801-51bb-891e-940ba2bbbe22 | date | Date Completed:
36ae649a-1076-4dad-a401-496404603f93 | section | 2.0 - Testing & Commissioning
b3163dc5-a588-4687-8c91-e2a9163f9f7c | checkpoint | 2.1 - Constant current regulators
b0463e4a-510b-529c-9a31-a451220e6ef6 | note | Frequency - Each Lot
c678da9f-b155-54b9-b8b1-48f39b017f02 | note | Acceptance Criteria - Commissioning shall include:
5689313e-cb53-5928-bcfa-519c5cd05954 | note | — Checking all connections
b4a3c3fc-ca3b-5772-891f-dab10fd3a6f6 | note | — Input voltage check
622e45e8-6f43-5afc-b8a3-64f070635e04 | note | — Output tapping check
144d3c5d-6edf-5de7-a3c0-505970d2ea0f | note | — Open circuit trip
d4c35038-7fa3-572d-8303-d39da44567ff | note | — Over Current trip
82aaf884-b23d-5a0d-8fec-a27221a95d31 | note | — Brilliancy Check
0b7a6feb-8e77-5590-958b-ee1bd882cf9a | note | — Lamp Outage alarms (if applicable)
cfef7d5f-3cca-597b-a0a2-92e1f775aace | note | — Earth Fault Alarms (If applicable)
ca306864-efad-5976-bf07-82934a02cda4 | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 4.8
c581eaa1-a8b4-5f79-ac26-dbe88ec35d02 | note | Inspection/Test Method - Verify
83f736f9-65cb-5657-9108-fff3852fc5f8 | note | Record of conformity - Commissioning Checklist
df7bd381-4bc6-5f61-88e9-43e480bb7159 | note | TP
f9e84841-91f9-585e-bae0-86d2ad2fddc7 | note | Responsibility - Project Engineer / ADB Safegate
e18a4b0b-0828-5c49-948e-946211871b83 | date | Date Completed:
d83d4217-4288-436d-952d-2c59510f0961 | checkpoint | 2.2 - Circuit insulation tests
c43f83f9-ba9a-5183-a3f5-621aeda6bea7 | note | Frequency - Each Lot
e40af524-dbe8-55eb-8c6d-8c71a83fc323 | note | Acceptance Criteria - The minimum acceptable reading is 1 Giga-Ohm to earth initially upon cable installation and 500 Meg-Ohm to Earth after at completion of the defects liability period
a87ef5bd-42fe-5eca-97d9-4f6eb242b1e9 | note | ○ Readings shall be taken before and after the following task:
39bc8d47-88dd-5a83-86a0-bb5ad85479af | note | a) each new section of cable is laid
89ca0096-503b-52cc-9203-bdcb4020015d | note | b) each section of cable is jointed and buried
9454d77a-26ad-5e83-a945-a92e2fae529d | note | c) the connection of the SITs into the circuit
382c44bf-5dd6-57a9-aa8d-be8eb868d8bc | note | d) prior to connection into supply feeders by others
e51c2139-f5e0-5da3-9447-e4863b01343e | note | e) before any “return to service”
4721e157-a0ee-5556-91c5-ec28b49dcbbe | note | ○ Tests to be performed as per the works procedure.
55cdc38e-d759-5074-b568-caf4dd3581fd | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 9.6
42ec72a2-f50f-5757-90b5-a8a772ba7156 | note | Inspection/Test Method - Verify
6fc420a6-c54c-562d-81e7-09202b0deeb8 | note | Record of conformity - Test Report
d2bdbfc3-f96a-5b99-b2c1-2c2070d0b112 | note | TP
321a0b8d-149f-5c0f-a8c7-1fc297ac23f5 | note | Responsibility - Project Engineer / ADB Safegate / Principal’s Representative
dc7d1b85-4319-5f2d-84f9-96c42c165139 | date | Date Completed:
efb4da52-1e91-456e-aeb6-d004467c5bca | checkpoint | 2.3 - Photometric performance
cc1aa30f-b79b-5304-bbac-a322306e131f | note | Frequency - Each Lot
7fd1c59a-1c73-50fd-a4e8-fb8ef6c7f98b | note | Acceptance Criteria - Photometric output performance of all AGL light fittings to be in accordance with the requirements of MOS 139.
aa19d9eb-ca36-5238-91b8-8478981b08ba | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 4.4.3
fd168ffc-c7dc-58aa-9ef8-885427fb67b5 | note | Inspection/Test Method - Verify
16a029f7-f02b-58f3-9108-b511b064ab28 | note | Record of conformity - Test Report
537ef145-d4e9-5aca-b9b9-557d8d2f7a0b | note | TP
ca4211cd-f726-583f-bc88-7ca817cf07c3 | note | Responsibility - Project Engineer / ADB Safegate / Principal’s Representative
2da0924f-da11-5b88-894b-61206a454ce6 | date | Date Completed:
d7460459-188d-48eb-a314-9ca2bfcf5759 | section | 3.0 - Post Construction Submissions
9af73d69-242c-4d02-a4a0-c47df1a6a4d9 | checkpoint | 3.1 - AGL components list & spare parts
7786e601-f6da-52cd-93f1-950af26f5616 | note | Frequency - Prior to Practical Completion
3ae0ff4c-f2b5-5604-8a79-5e7345a188e7 | note | Acceptance Criteria - The Contractor shall supply spare equipment as detailed in the cl 11.3 of Zulu Spec Volume 3. A spares Bill of Quantities (BoQ) shall be provided to APAM OPS at the beginning of the project and be handed over to APAM OPS with a signed hand over sheet at the completion of the project.
15728b07-9945-5269-8748-1e6daac9945d | note | ○ Spare equipment shall be as per the levels stated below at the end of the designated Defects Liability Period.
373a74c8-7786-5cdb-a2be-2c1c09cad141 | note | ○ All spares shall be delivered to Building 52 and evidence of quantities and types of spares including handover to APAM OPS shall be included within the Operation and Maintenance Manuals.
62575da8-58cc-5a5f-bc87-ad9b6a7647be | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 11.3
7d4082c5-0fda-55f1-96b1-c4e6577db72e | note | Inspection/Test Method - Verify
d9c7dd84-6520-560c-9c92-dcf653d23589 | note | Record of conformity - Component List Submission Reference
93161aa9-603e-58c9-bb0d-a487c719b246 | note | IP
8049dae6-023b-54a5-aaaf-2ee75f0529ef | note | Responsibility - Project Engineer / ADB Safegate
506015d8-56b0-50b4-9ff5-0fe3530e2d96 | date | Date Completed:
cea9329c-a2f4-4782-a5af-5d08bccbb979 | checkpoint | 3.2 - Training airfield maintenance
b03a1fb3-d293-59d7-9b7e-fc76938a44fb | note | Frequency - Prior to Practical Completion
3a676c41-0928-5acb-a57b-46e0fb61c8f7 | note | Acceptance Criteria - Provide training on all equipment installed under the project to the satisfaction of the airfield maintenance team.
b701cf33-8200-593c-9b09-8cd82d5cebf8 | note | ○ Such instruction shall be at a time and for a period as necessary to demonstrate the operation and maintenance requirements for all installed equipment and make the APAM/APAM OPS personnel competent in operating and maintaining those systems.
c674f85d-10ab-54e6-b604-527961bf70f0 | note | ○ Contractor to submit a training plan outlining items to be covered during training.
3c36f16c-80a4-53e3-8791-38c84b33a00a | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 9.10
55ce80f5-dacd-521b-ac53-d7a245e969ca | note | Inspection/Test Method - Verify
9f4d25de-513a-5068-bdbf-fb1c30a793c9 | note | Record of conformity - Operating and Maintenance Manual
ed84b4a3-9ca1-509e-8eef-5591981f9cfa | note | IP
638adc32-5459-5548-96f4-73c5e7bc6dd5 | note | Responsibility - Project Engineer / ADB Safegate
cffad1fa-b732-57cd-b09e-383bf81c1dec | date | Date Completed:
4fbfe384-b567-4a7e-aec6-a0fdcf867e64 | checkpoint | 3.3 - Certificate of electrical safety
f07f0f40-2798-50a9-9556-4fd8323590b5 | note | Frequency - Prior to Practical Completion
474c1659-dd6e-5166-b40b-abd81d455dbc | note | Acceptance Criteria - Submission of a certificate of electrical safety for all new electrical systems installed in the project
424f340c-9c14-5d81-bc27-298f57baa0c7 | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 10.5
a9312f81-05b5-5c0c-96f2-a4c2bd68f8c7 | note | Inspection/Test Method - Verify
becf135f-50ab-5efb-a465-41b267cfc782 | note | Record of conformity - Certificate of Electrical Safety
836b04a0-ea39-511d-85ca-4eac670b0476 | note | IP
e9e456ed-bf30-51ae-a0c7-b5c0b46785fa | note | Responsibility - Project Engineer / ADB Safegate
7e164fc4-8735-5994-99e2-b15c23b7df21 | date | Date Completed:
817bd817-6c2d-4614-9f04-a16446945521 | checkpoint | 3.4 - Handover documentation
42144d5a-e480-5905-81ac-22278df8769e | note | Frequency - Prior to Practical Completion
fa2d6aae-6c7f-5438-8866-d967f23dfc01 | note | Acceptance Criteria - Submission of all quality assurance documentation including as-builts and schedules to the Project Manager.
1d92baea-50b7-58f2-b3de-a174c4c295a6 | note | ○ Information provided shall include:
2cf787b5-cbc8-55d5-9d67-d0964db3f38d | note | — Circuit details including cable route, loading, Quantity per conduit, origin & destination.
4195e120-b062-5474-a048-56954c36961b | note | — Number of series transformers and location of joints.
9163b570-b5ff-5da5-a6ca-a5d7095d0609 | note | — Equipment and materials used.
d619dcaf-2cda-5bfb-908c-be4ae13a8f72 | note | — Testing and commissioning values for all modified or new equipment.
a1bb0322-ee59-5e19-b1ac-37e943051b65 | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 11
309d188a-dc53-5b7c-adbf-b68e8218f93b | note | Inspection/Test Method - Verify
22fde21c-30f9-5e9a-9f56-74aba15513a3 | note | Record of conformity - Submission Reference
f1be9bd7-9f4e-5c7a-aed2-5cef8ddc8ce1 | note | HP*
0fd000f2-5cf6-539c-a795-d9cec2adc5df | note | Responsibility - Project Engineer
0d7abbf3-bfed-50fe-b254-989c45a170d8 | date | Date Completed:
4d95cb9c-73f1-40de-a4e7-7e07974b03fa | checkpoint | 3.5 - Acceptance Testing
3a741f58-976a-577c-bb32-a3c221bec62d | note | Frequency - Prior to Practical Completion
d30a3476-a015-5f29-8aff-362edafa1d23 | note | Acceptance Criteria - HOLD POINT
d86fe14c-31be-5f2b-9e05-70b7fea4c4c2 | note | ○ Submission of the results and records of the commissioning as well as any further commissioning testing shall be undertaken in the presence of Contract Administrator and representatives of APAM
450e044d-629a-5159-a29b-211b613a8863 | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 9.7
702c7db7-7d8f-5093-94a2-c014dbe78995 | note | Inspection/Test Method - Verify
18ac1302-b51c-5b7f-b1ea-efc8bbc31f75 | note | Record of conformity - Letter of Compliance
974bfb78-15e0-5e30-beeb-893004385e1a | note | ○ Primary Circuit Commissioning Sheet (Testing of Primary Circuits: Existing + New for IR, Continuity)
8c7dc23b-776d-51fc-a893-1f9704bacd28 | note | ○ JCOES (Electrical Safety Certificate for compliance with Electrical Safety Act 1998 and Electrical Safety (Installations) Regulations 2009)
44b062b2-8710-5d77-bced-e99f448d985a | note | ○ Light Fitting MOS/NATA Reports (Covers MOS compliance for fitting brilliancy)
1d9a3649-9fd8-549e-802f-aef3714d8143 | note | ○ O&M Manuals for Materials Installed
604b8df9-08dd-5ad1-b534-a2841483fbf9 | note | ○ All standard AS/NZS 3000 cable tests on all power supplied cables
5b556657-82a5-506b-aa6f-ce84ff4a3ba4 | note | ○ Additional – AC 139.C-11 V1.0
d7c091ca-9826-50b1-82b8-1fb3394ab899 | note | ○ Ground check report to satisfy requirements around ‘flight testing’ etc.
d420fc5a-7ad3-582e-a20e-2345e2647dba | note | HP
f8695647-9ca6-5d3d-a79a-81b4b79bd76c | note | Responsibility - Project Engineer / ADB Safegate / BECA
d422c2a6-d1c6-59f0-952f-104262caac32 | date | Date Completed:
920e3c9c-b5fe-4d56-a0ac-a5c53062f13d | signoff | AUTHORITY HOLDPOINT
b2c3e92b-0960-4f3d-b23f-86fd3b5f830d | checkpoint | Final Inspection
f0250adc-ff8a-5500-b251-46036ff4936a | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
d955dd9f-1f94-53cf-a1df-32febd56861f | textbox | Print Name:
18f785c2-f26b-5ac2-8ffd-5b308599ae6d | textbox | Position:
7d1140c8-9b5e-5744-9463-82334377001a | date | Work Completed On:
8f4d244a-3150-5b2f-910b-92963cb3356f | date | Date:
d0319b60-9681-5d64-8f93-33fe55208828 | checklist | FH-ZU2-QU-ITP027 - AGL Cabling - Rev 0 | itp | ITP027 - AGL Cabling
6607cab9-33c5-558e-bbf8-f1706ae449f8 | section | 1.0 - Preliminary Works
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
084ecec0-08c1-5480-8d74-efa85d9a76ee | note | Frequency - Prior to commencing any activity
9cf17b9a-0296-5121-bb59-c09361c4f722 | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
c79d28c3-2ad0-5255-8028-702fc73647b9 | note | Reference Documents - IFC Drawings
fc5214f9-eb77-50a2-b18d-2cb2846dce3b | note | Inspection/Test Method - Verify
f53bce20-91ed-5f05-8562-ea715bec3633 | note | Record of conformity - Drawings
3956a579-86ec-5eff-9e4a-7cb57c2eb271 | note | IP
15d1bba0-187d-5a60-9f6a-74c25f25b456 | note | Responsibility - Project Engineer
1d8ecb9a-5b52-5485-b3b7-52afe398bc4d | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
c6e968b0-29d1-5fc3-a00b-f3487f707c88 | note | Frequency - Prior to commencing any activities
e14bf65a-9dc4-5e81-ac7a-17abebc913e8 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
b0147824-8e3a-580c-9a41-7035645ed709 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
e9e53ba2-3666-573d-8745-b4f4b768c75b | note | Inspection/Test Method - Verify
5ee7f0d3-73d9-5ebd-995e-3226eb9d0f9a | note | Record of conformity - Site and office inspection
4ccf422a-beef-54e9-9e0f-58c36f451a5d | note | HP*
a0b07714-756d-5a16-80f7-dd77e5338b67 | note | Responsibility - Project Engineer / Site Supervisor
5b08f91e-7c1b-542d-9d0d-13ac51c58d6f | date | Date Completed:
520fc374-5377-50ba-b879-f98bb15b317d | checkpoint | 1.3 - Existing service location
f7e0a76f-bb66-599b-8dc6-5c96fecf6108 | note | Frequency - Prior to Start
8b5366c1-2c24-522f-b19b-28fd5bc1b429 | note | Acceptance Criteria - Prior to installing any fittings, location of all existing services to be identified and marked onsite.
73376e7b-6ec6-580d-b9d0-34afd28e1bc4 | note | ○ Services located in the works area to be proven.
9c79d5f1-9689-52f1-9398-fb9f9771e9c0 | note | Reference Documents - SWMS
eea18c1d-6def-5b6b-b17e-24506aa8f41c | note | Inspection/Test Method - Verify
dff13372-6be7-5222-b692-73cfc179bbb3 | note | Record of conformity - APAM Excavation Permit
b56d90d2-979b-5488-a1bf-01570a99015c | note | HP*
d5c96297-fe67-5e2c-85c2-7f12b293f64c | note | Responsibility - Project Engineer/ Site Supervisor
23a9c78d-9f3e-5f6b-8fdb-ebd1dc1753f4 | date | Date Completed:
b4360bab-78b3-5063-ae73-2589e72b2f02 | checkpoint | 1.4 - Cable route
03bcb88c-dbb4-5a7c-8025-39e72b794caf | note | Frequency - Each Lot
a0bcbaf1-c3f4-5bab-a543-7fa6c5d4066e | note | Acceptance Criteria - HOLD POINT
9a5ce38e-3353-5874-b422-019c9ab8302b | note | ○ Primary cabling route installed as per path shown in construction drawings (and/or approved markup).
90d91336-1d81-5d57-801c-c3a066eaf8ee | note | ○ See relevant lot from ITP 025 – AGL Conduit Installation for cable route.
44c77117-fef3-567e-87e8-19d52c85c1ef | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.1, ITP025 – AGL Conduit Installation
2e613ce2-b0af-5d92-a459-99d17ae91845 | note | Inspection/Test Method - Verify
3d98ff75-4225-596b-9e58-e1a3c8c2539d | note | Record of conformity - This ITP signed, Aconex reference
b625d644-30b5-51e1-9af1-cccc76587060 | note | HP
01e00bb4-877a-5213-b35e-a1ebdf6557b0 | note | Responsibility - Project Engineer / Beca
29c73fdf-273b-5d49-b87c-712ec8e4165c | date | Date Completed:
5245df6c-7530-5e73-8dbf-68583d02af62 | signoff | AUTHORITY HOLDPOINT
43b5292c-d817-5d31-a654-aa9a9fb6996b | section | 2.0 - Material / Equipment Approvals
122f376e-e033-556a-af86-1b7db76a3bb9 | checkpoint | 2.1 - Primary cable
a4cfcd29-f001-5898-99d5-aea2ed7dae11 | note | Frequency - Prior to Start
20690dcf-c0f0-5f39-8aa8-2fde40a065b5 | note | Acceptance Criteria - Primary cables shall be:
9670b5af-42c5-5b09-bf68-75b15edff80f | note | ○ 6mm2 cable with black polyethylene jacket and copper tape screen
e637605e-20ef-58b9-90e2-6be82f3e36a7 | note | ○ Rated for 5000V
d326591b-4763-538d-83da-89729d6a441f | note | ○ 7 Strands
ee079a69-7ee0-5d57-849b-4011e89e0ce7 | note | – or approved alternative.
c0c1ca0c-b955-5091-923f-7ed9c45285c9 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.2.1
c563a629-6af2-5db4-910c-9e5cb7e36225 | note | Inspection/Test Method - Aconex
d377bcc3-b1b0-52ec-b726-e8eaf8ee04f9 | note | Record of conformity - Datasheet
4f6e1f99-b816-5649-902a-f1371e263942 | note | HP*
50157a5e-7a28-57ed-b565-fc6723f7cfd2 | note | Responsibility - Project Engineer
2ff1bf0e-8e3b-51f3-b9f1-8f1a2390a308 | date | Date Completed:
3432dcfd-91fe-5c00-854b-7b55f23a5161 | checkpoint | 2.2 - Secondary cable
02c825d0-9463-5d10-908a-5776a6ee38c1 | note | Frequency - Prior to Start
52f4d154-8af1-5719-8224-0f418e45606c | note | Acceptance Criteria - Secondary cables shall be:
44d71d7e-47f4-53ca-8fe0-dcdbf79ac714 | note | ○ Min 4mm2 cable with black nylon jacket.
7a40335d-5509-539c-924c-6fcda49c0716 | note | ○ Rated for 600V
3872fc69-1b47-510d-907f-98720bfaf136 | note | ○ 56 strands
e8ab4674-6ef6-53e9-a70b-7f0d461d0da5 | note | – or approved alternative.
8aff2a2b-fe11-52f6-b2e3-23abc4326c74 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.2.2
4ae35278-4742-5729-8cfd-68865b2188b6 | note | Inspection/Test Method - Aconex
3e6ca5c6-27ef-542a-97b7-94c52dd40f63 | note | Record of conformity - Datasheet
0301d6eb-5530-5d94-9a47-18403d44c79c | note | HP*
3f600ea7-c96b-5ede-aeb1-e1890b3f777e | note | Responsibility - Project Engineer
29144972-5c24-503e-ba07-de15f3241fda | date | Date Completed:
262538c1-c2d6-51b8-95ee-efd3a2cfd00b | checkpoint | 2.3 - Cable connectors
91357c0b-6615-5f70-a6d6-3e23d4560efe | note | Frequency - Prior to Start
c92cf1f7-00a2-526f-8576-138d0d9873c3 | note | Acceptance Criteria - Plug and sockets shall be further sealed by the application of double lapped layer of self-amalgamating tape protected with a double layer of PVC insulation tape.
b99c8fd4-8940-5c39-8668-8f6a4f175a5b | note | ○ Field attached plug and socket connections shall be constructed in accordance with the manufacturer’s instructions.
4417737e-8692-58bf-8c97-f3b6cdff95d2 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.3.3
f3e252d4-b3cb-52d1-8e5a-23b63082c72f | note | Inspection/Test Method - Aconex
bb294352-9e84-5ee6-8863-ac6ad920bfa5 | note | Record of conformity - Datasheet
d4a2e8f6-4eff-535e-9cd8-cf7e67cd3e05 | note | HP*
1331058a-48b5-5da6-a7f9-208bfa631de0 | note | Responsibility - Project Engineer
3f816d24-9eef-5296-a933-b1e06087f758 | date | Date Completed:
0f506738-ab3b-55ca-85b8-126890ec5d15 | checkpoint | 2.4 - Series isolation transformers
6d768cdd-92c9-5df0-b66f-03310679378c | note | Frequency - Prior to Start
58cc99f6-1105-50d9-9640-c9b017da833e | note | Acceptance Criteria - New SITS shall be:
36cdee4a-1209-55b0-9a64-12ebbb5cffd0 | note | ○ Fully encapsulated synthetic rubber watertight (IP68)
0f66dc6f-e6c1-5947-ab6b-b7f626d5f9a7 | note | ○ 6.6 Amps rating
9e43bca9-5498-5d13-b69e-72fbf134f526 | note | ○ Minimum 600 mm long primary tail/1200mm long secondary tail
aa3245e2-c20b-5312-94f0-c807b7047f1e | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.3
d8e756e7-9177-5d62-bf54-1db70c39f9bc | note | Inspection/Test Method - Aconex
ad67297c-22b9-5468-9afe-e2de309eebb7 | note | Record of conformity - Datasheet
58c85867-a8e0-5bae-8e91-893355021d6e | note | HP*
c19a30da-ceda-51d4-9c29-64d1c6f68cf4 | note | Responsibility - Project Engineer
aa5c7237-766a-5f7f-ba7c-231f10cec1ab | date | Date Completed:
577a7835-cc47-549f-b10f-2fe7edb3af10 | section | 3.0 - Cable Installation
5592fe8f-ccb0-5b75-99f5-348b238dc66c | checkpoint | 3.1 - Primary cabling connections
ea9d079c-2a66-55c9-bb18-242e37729a70 | note | Frequency - Each Lot
2243b91b-3809-53de-b099-828910c65b19 | note | Acceptance Criteria - Underground primary cable joints are only to be made where the cable length exceeds the maximum cable drum length or jointed to existing cabling. These joints shall only be made in pits. The joint shall be waterproof and shall allow the jointed cable to be installed within the pits without causing damage or undue strain on the joint.
043c37d0-da9d-5747-bd65-773ae0272a95 | note | ○ Use only approved plug and sockets for joints in primary cables. Primary cable must be jointed to the primary cable tails of SITs using approved cable jointing kits.
6c40c918-3883-5df6-aad4-88a5c5ed27aa | note | ○ Plug and socket connections shall be constructed in accordance with the manufacturer’s instructions paying particular attention to the screen continuity joint and ensuring the rubber housing and insulating silicone remains free from moisture, dirt and debris.
6c65db7a-3b38-512a-be73-ae5e9b1146ca | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.1
e13925a7-705a-5c56-b184-22641a23caf9 | note | Inspection/Test Method - Verify
846b7873-773c-51e1-9e00-f184596e2726 | note | Record of conformity - This ITP signed
5f3c0794-3a9e-52c7-8071-6008d5ab6eaa | note | IP
508909fd-f8cc-5530-ba2b-0e5bc3884e17 | note | Responsibility - Project Engineer / Site Supervisor
b019303d-e7e5-5e18-a362-fbdeb9436f53 | date | Date Completed:
2cdc1460-dc79-5817-9790-ff12ef77b52f | checkpoint | 3.2 - Secondary cabling connections
15614fa1-b345-5403-9db2-3c9f0d2ffb08 | note | Frequency - Each Lot
bffd1973-f393-5401-8d63-a0570a17a67d | note | Acceptance Criteria - Individual secondary cables shall be provided for each lamp contained within individual lights. The secondary cable shall be installed in a single, unjointed length from the SIT to the AGL light.
4b01cb52-b615-5ade-bc21-bcf411c5277e | note | ○ A secondary cable that shares a common slot shall not be installed under any light base. Any joints within the slot shall be made utilising crimped links “staggered” and be installed external to the light base.
afdd9390-f698-535e-b1c6-527752df2859 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.3
8ca84581-aadb-5430-8c67-78e90d21cd14 | note | Inspection/Test Method - Verify
9304141f-7b41-57c3-98d7-5392d95ffc0d | note | Record of conformity - This ITP signed
13e87572-3f6c-53aa-a953-1be7bb496315 | note | IP
c4862c2c-2c95-5f55-9d2b-c389b45c68db | note | Responsibility - Project Engineer/ Site Supervisor
47ae2efa-08a3-51a3-a7b6-964e99817080 | date | Date Completed:
903fd3d2-62dc-5f1a-a81e-4e63048c1527 | checkpoint | 3.3 - Secondary slotting
9e096c81-d57e-52de-aca2-c387d8e3d981 | note | Frequency - Each Lot
48ee0b44-923a-5497-ad9f-8d80f41f7cb5 | note | Acceptance Criteria - Pavement shall be saw-cut to specified depth and thickness and slots cleaned/free from debris.
d9f87c01-cdd0-503a-b474-f622021a407b | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.5
0165c77b-68c1-57d5-99ba-46d16a829b60 | note | Inspection/Test Method - Verify
48f4a900-5a6f-59b6-8d1d-400ca5d8111b | note | Record of conformity - This ITP signed, Avionics Secondary Slotting and Sealing checklist
549d7b64-d47a-550f-ab5e-1402dff8847f | note | IP
2b2115c3-a236-5ea3-a202-5f0e0fa7d70a | note | Responsibility - Project Engineer / Site Supervisor
6c2a9dff-ac7d-53b5-be06-592d0d48ddd8 | date | Date Completed:
d66caef2-751e-5767-b48b-3bfa0b4bb7bb | checkpoint | 3.4 - Max conduit capacity
b6b31181-2c85-5d37-8d46-a75bbb4e7e8d | note | Frequency - Each Lot
1b87870c-f6d7-5e0e-b697-a38d3829ca60 | note | Acceptance Criteria - If APAM approve three or more cables enclosed in conduits and/or ducts, the total cross sectional area of the conductors must not exceed 40% of the internal area of the respective conduit and/or wiring duct as recommended in AS/NZS 3000 for short distances without bends.
333a725b-5074-5b9a-ae2e-c774ef15a1cd | note | ○ No more than 10 primary cables shall be installed in a conduit
0bd5e56b-56cc-5808-8b49-a3cdf5ed0f66 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.2.3
f1737631-1a73-5351-9176-dc1ede50b9ce | note | Inspection/Test Method - Verify
4d8d6ccb-8ba4-52f7-a489-6cd2068f8376 | note | Record of conformity - This ITP signed
c7ded4d5-231f-5382-bde9-aa38ed255345 | note | IP
6d7361e5-1b4c-52bf-9fa4-0c30d11ac193 | note | Responsibility - Project Engineer / Site Supervisor
e226c20e-d9ce-5287-86b9-610eee1e2e48 | date | Date Completed:
e507161a-d055-5c27-8551-5f26faa6d11c | checkpoint | 3.5 - Secondary sealing
f062f36f-3fa7-5e14-b5de-d61d9ea3b475 | note | Frequency - Each Lot
1adcea5f-6e85-5300-9bcd-c69c1f01545a | note | Acceptance Criteria - Backing rod shall be installed on top of the secondary cable, followed by flexible sealant:
aa8d978a-c98e-549a-9289-0b3b5c4655d8 | note | ○ Dowsil 888 to be used in concrete expansion joints.
5ef02737-3cc2-55cf-abfb-49a9350af82c | note | ○ Dowsil 890SL to be used in asphalt slots.
14f281c1-a5d0-5029-8cd4-1f58a35b8d27 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.5
2ae4e0a1-e1a0-5ce2-8843-962ababbc36f | note | Inspection/Test Method - Verify
b37e2ee4-593d-58af-8372-8386987aef16 | note | Record of conformity - This ITP signed, Avionics Secondary Slotting and Sealing checklist
fff47d18-3cb4-5870-b270-f3edbd0d0f6f | note | IP
64903664-af96-53a8-81e5-5638822bd6b4 | note | Responsibility - Project Engineer / Site Supervisor
ec73ec40-fd32-5e9a-a5fb-1503f94d5f0f | date | Date Completed:
b20adada-f2f8-51de-bde6-091148b0e106 | section | 4.0 - General Works
5442b8e1-6da8-5222-b6f0-f588fc9cc3ae | checkpoint | 4.1 - Protection of existing cabling
3bf93f01-555b-54d4-a582-037f3bbb5d03 | note | Frequency - Each Lot
248d71c1-0b97-55f6-8e5f-7236a7339eb2 | note | Acceptance Criteria - Where the crossing of existing secondary cables cannot be avoided, the existing secondary cables shall be reinstated and made good.
614967ac-49be-5eb3-b4a4-5e2a416fe8dc | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.3
197c8456-1b37-576d-b956-4c9dfb1ecfc6 | note | Inspection/Test Method - Verify
f140fba5-11b8-5a1a-8466-c67126c7eb90 | note | Record of conformity - This ITP signed
251241da-1c79-5865-ad28-350adca01eab | note | IP
7fb33dc8-893f-5f67-bda9-36b54ed65019 | note | Responsibility - Project Engineer / Site Supervisor
80dbe2aa-e49d-5f8f-91da-5a384a46d295 | date | Date Completed:
7aaaccdc-6334-521c-8b32-81e7323ac175 | checkpoint | 4.2 - Slack
5bca6755-97ff-5b88-b7ca-e3148358c514 | note | Frequency - Each Lot
cdedd2a9-f061-5069-9b6a-059946986c83 | note | Acceptance Criteria - Primary Cabling – a single minimum 500mm diameter loop shall be made in each primary cable where they pass through a pit other than a SIT pit.
d5ba2815-1717-57c3-aae8-1159abdf46e2 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5
e94e0a39-5c2a-5943-9aa6-a1c3d52fafcd | note | Inspection/Test Method - Verify
6621fec5-b16e-52a2-b4a9-9e931b50831e | note | Record of conformity - This ITP signed, ADBSG Installation of Primary Cable checklist
52ae351d-e471-5fe6-918e-14decf9c1691 | note | IP
b267a4d4-a105-5628-83f3-576bf3477c0a | note | Responsibility - Project Engineer / Site Supervisor
dbcf3142-60f1-5794-960a-1cc3d3e52aa5 | date | Date Completed:
08e5f340-f964-53f9-9d5e-d37deed19b8c | checkpoint | 4.3 - SIT pit earthing rod
a14c2c6f-127a-5a25-a0f4-5c1bdeb75cf0 | note | Frequency - Each Lot
7b891f9c-47f9-57ca-a3b9-2c4ddb46a812 | note | Acceptance Criteria - Earthing inspection pits shall be provided with earth electrodes of sufficient length to achieve the required resistivity of less than 6 ohms. Earthing electrodes shall be copped clad stainless-steel rods of minimum size 13mm diameter.
762d0357-b40a-554d-8701-108c165fcc01 | note | ○ The earth wire size shall be 16 mm2 PVC insulated copper, other than where equipment is wired in PVC/PVC cable in which case the earth continuity conductor may be enclosed within the PVC/PVC sheath.
521a7e30-fe6b-5679-8531-dafd848094db | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 6
2c89753b-8848-5daf-9cb0-974bfbce040c | note | Inspection/Test Method - Verify
e89b7054-9b6d-546e-a45e-54c3166779d3 | note | Record of conformity - This ITP signed
e24392e3-32ab-5e0f-b556-44280a507148 | note | IP
c3b3db98-4d1e-533c-82e4-315160b85025 | note | Responsibility - Project Engineer / Site Supervisor
7f0d89f1-0c1d-5e4c-b946-b26987e2976b | date | Date Completed:
b6ec13a1-58c8-59f1-8549-f219e0c553bf | checkpoint | 4.5 - Identification of configuration
8d761c6c-2d7d-5fb8-a94a-0edb816aa6ff | note | Frequency - Each Lot
76f55867-4af1-5970-addb-837d87187468 | note | Acceptance Criteria - Label all cables for new and existing circuits remaining in service at every access location such as pits, duct crossings, and ALER. Position the labels such that they can be read without displacement of the cables.
82e52b35-f14d-51bd-a162-8bfe8c2d6a02 | note | ○ In transformer pits serving multiple taxiway lights, the Contractor shall label each secondary cable at the transformer connection to indicate the designation of the associated light connected.
d8f2b1aa-e672-58e9-9d9d-a554cb0f8c11 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 7.2
2326d521-a431-5428-aab0-e20472db1be7 | note | Inspection/Test Method - Visual
410ba2ff-f505-5e22-b7e3-dcacb0bad6d6 | note | Record of conformity - This ITP signed
6218bb73-084a-5d77-b9f0-be4ffb63a444 | note | IP
99074f27-35e3-5c20-8bef-1e9b8369b278 | note | Responsibility - Project Engineer
e7cd0188-1683-5cac-854b-edca2a3e23a4 | date | Date Completed:
3e68cc9c-da03-5c12-a911-0dcb053881a0 | section | 5.0 - Post Construction
a033fb3e-023c-53fe-b5e0-911e943a0480 | checkpoint | 5.1 - As-built Documentation
11dd7507-b970-571b-ac32-4491371ee8ff | note | Frequency - Prior to practical Completion
5d2dc373-07b2-5763-ae3f-1a29a8fb553a | note | Acceptance Criteria - Submission of as built report showing cabling route submitted to the Principal’s Representative prior to practical completion.
36472891-ad44-5c25-b118-0d207308de4c | note | Reference Documents - FH QMP
0e8769aa-d815-501c-96e3-f869244cd8fa | note | Inspection/Test Method - Verify
9c3385b9-97e5-5e23-9ea1-df36f907e5c1 | note | Record of conformity - As-built survey report
ac3a000e-49d2-54d6-89d3-bf30c8214e2d | note | SCP
d1d4caef-8eb9-5a1f-a947-1be67b7498a4 | note | Responsibility - Project Engineer
0901d4b2-d248-5567-9637-773d8239ebee | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
c3c0d97b-0908-5237-a1f1-72513f227cb3 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
05edde7a-f08f-5c70-b88f-1accb1d8d8e4 | textbox | Print Name:
5bdcbcc6-9a38-590f-8004-c7bbf198ca9e | textbox | Position:
31a47a32-f239-5abd-b74e-9127e755a3b1 | date | Work Completed On:
cdce0b6e-8f82-5da0-9dbc-cd8e91518eac | date | Date:
24b923b5-1a36-5875-8feb-802ee8863ecb | checklist | FH-ZU2-QU-ITP028 - AGL MAG Signs - Rev 0 | itp | ITP028 - AGL MAG Signs
6607cab9-33c5-558e-bbf8-f1706ae449f8 | section | 1.0 - Preliminary Works
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
8ddc60c2-52d6-5ba3-bb5f-c822692ca78e | note | Frequency - Prior to commencing any activity
6df18c19-7c6f-50f9-b677-3f2b959531f8 | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
f9da8ea9-89b7-5f0e-b989-84b6a8b80b8e | note | Reference Documents - IFC Drawings
4683521a-f900-5473-98f3-a67b4f6ea1e5 | note | Inspection/Test Method - Verify
674379bd-c284-5e3d-873f-ce09bf739c70 | note | Record of conformity - Drawings
d8eb3e01-fda0-5c31-856a-83c759b25a3e | note | IP
175b6b71-cc52-516e-8e9f-846a379cfcc0 | note | Responsibility - Project Engineer
dfc620fd-985a-53d1-b486-992f4c1d8362 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
260a7c4b-a99c-5a02-adad-d000ceabfd8b | note | Frequency - Prior to commencing any activities
813e3056-3b3e-51c9-8d23-d749416004b0 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
c9605aa4-86a1-52a6-83ce-2ee4605031fa | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
b313f28e-2438-582e-ab7c-e25ba2da9340 | note | Inspection/Test Method - Verify
2224f6d5-342a-592e-9d5c-41029967a1a7 | note | Record of conformity - Site and office Inspection
d87775a1-ef24-51a6-a318-1ccc0adeec75 | note | HP*
cf72e15b-9c45-5942-92d3-14461509a1d6 | note | Responsibility - Project Engineer / Site Supervisor
0b8b7bbc-9c92-59c0-8160-fb26bad4aa5b | date | Date Completed:
6950b5cb-7d87-5252-8927-66c6362f45bc | checkpoint | 1.3 - Material/Equipment Approvals
48893bdb-4389-5907-9976-dd6ddf0f8c56 | note | Frequency - Prior to start
34c061f0-7aee-5109-a88b-625ab5d38f62 | note | Acceptance Criteria - All materials shall be proven to meet contractual requirements prior to acceptance.
5fe73daf-9af6-5110-a145-b770a0022e1e | note | ○ MAGS shall be from ATG Airfield guidance signs range.
a6532fa3-d5e3-5a41-b2ab-395352d6acc5 | note | ○ Any deviation from the above suppliers shall be submitted to the Contract Administrator for approval prior to ordering.
13379fa6-158f-5a66-95b5-84d65aff3b24 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl 2.3
cb7f38e8-7634-5cc9-9ed5-70723d66218a | note | Inspection/Test Method - Verify
e44fdd8a-7997-5917-bd17-07bd45a39200 | note | Record of conformity - Aconex reference(s)
919a5e4d-2e49-546d-8fa5-373dcb126d7d | note | HP*
d445324b-b5cb-5add-a93b-5fb130ce1c55 | note | Responsibility - Project Engineer
bd170232-4df1-5bea-aee7-01b489ce921c | date | Date Completed:
9eb64960-a579-5c04-a038-8713272d9ee7 | section | 2.0 - Installation of MAG Sign Footing
7242a731-b698-5c5a-a5d7-fa8ee5d5f578 | checkpoint | 2.1 - MAG Sign Base
b5e75d4b-ba5e-512f-b305-af4a72153d70 | note | Frequency - Each lot
54b5f099-4b4e-5e08-8742-199530135d52 | note | Acceptance Criteria - Position of rectangular base to be as per set out coordinated listed in MAG schedule.
68a3f16a-00de-5635-ac38-c10fc7eb2b48 | note | ○ 150mm thick class 2 crushed rock base layer compacted to 98% STD on prepared subgrade.
efcf5c26-7fbd-57b8-b37e-3b3bbed3a269 | note | ○ Subgrade Bearing strength of 130kPA confirmed by a qualified geotechnical engineer on behalf of the contractor before placing membrane, reinforcement or concrete.
26c34011-20fb-5b2b-9342-d03d93dab5ec | note | ○ 50mm blinding concrete between subgrade and foundation.
1361518f-7030-5a8b-a82c-5bf3e706f9a8 | note | ○ Slab thickness to be 300mm for all H<900mm signs, min. 32 MPa concrete.
28cefa2c-b332-5be7-8348-f7c0639fcf1a | note | ○ Footing to be placed flush with FSL when placed in pavement surfaced areas.
d3bc008f-5ac3-5001-965d-721918b27030 | note | ○ N12-200 top and bottom reinforcing bars with minimum 50mm cover from edge of concrete.
0e9e1085-36c9-552e-a6f2-0803bba1b4aa | note | ○ Sign mounting brackets and frangible coupling as per manufacturers guidelines
99b4b9d2-8f6f-5b2c-bbe0-ca5e4ef81b1a | note | Reference Documents - ZULU-BECA-023-DWG-07502
2c46142e-8c92-580a-b15c-8143787bd00b | note | Inspection/Test Method - Visual Inspection
fa5695c3-bc1c-5393-a2dd-5c2d327be5c6 | note | Record of conformity - This ITP signed, DCP test result, Concrete test certificate, Avionics Installation of New MAG Slab and Sign checklist
fbd2220d-bd86-5e38-a782-43c2d0712fe1 | note | IP
17c8bcb1-6358-5a68-826b-72b35e9e546e | note | Responsibility - Project Engineer
1661ae28-e9c6-53cb-88e0-dcd5b3024934 | date | Date Completed:
bc20e016-f324-5514-b18a-ef482ef032e2 | section | 3.0 - Installation of MAG Sign
daf0a513-a1d3-5af9-aea4-370e647fd5d5 | checkpoint | 3.1 - Luminaire Circuit
649045eb-7b83-5714-8fcd-5679b6a48f55 | note | Frequency - Each lot
35f7888b-a995-585d-ba71-3d5588cae03a | note | Acceptance Criteria - Each luminaire fitting shall be installed on the appropriate circuit as specified in the AGL schedule.
c4f8306d-842a-546b-83a0-de6e924ee263 | note | Reference Documents - ZULU-BECA-024-DWG-09001-16
4736f50d-ba8b-5e52-8973-cfffbf02d65d | note | Inspection/Test Method - Verify
b74f2399-6413-5405-8088-8793ec0d8281 | note | Record of conformity - This ITP signed, As-Built Documentation
f7953965-0b65-517b-aa70-b79462b51b48 | note | IP
3b31a614-8e8a-556a-b653-a0225400d8e5 | note | Responsibility - Project Engineer
0b78267f-d355-55de-877f-46da63527d4b | date | Date Completed:
c7451fec-d8cc-5895-b0d6-abb96dbfa9ff | checkpoint | 3.2 - MAG Sign Face
e271b798-8392-52fa-bbc9-fcc5c50d9445 | note | Frequency - Each lot
65e89ebe-45e9-5dfe-9fb5-16068bb9c2a4 | note | Acceptance Criteria - All MAGS that are to be mounted on frangible couplings. The provision of internal illumination of the MAGS shall be as detailed on the Drawings.
2418b2c0-d908-590e-a501-656146b5875f | note | ○ Bird spikes provided with MAGS Chain tether installed on side further from taxiway and installed as per manufacturer’s recommendations
aae51f8e-af26-5831-b4e5-ee1b4d57ac58 | note | ○ Where multiple panels are required, the inscription shall appear continuous over any joint and shall only include a bar if the bar is part of the inscription.
9d39b429-0499-5f89-8c13-88ff7fa8ee14 | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 4.7.1
ddb0b542-b302-5082-8da0-213b3846b37f | note | Inspection/Test Method - Verify
bc671c39-5ef8-5b06-bc94-7c327ca06502 | note | Record of conformity - This ITP signed, Avionics Installation of New MAG Slab and Sign checklist
807e5a06-a1dc-5e4c-8900-cab92739b26f | note | IP
f1ab977d-08e0-5a56-bc90-8394e3858bd3 | note | Responsibility - Project Engineer
41095d3a-5d75-5593-927e-01d84d3868f8 | date | Date Completed:
d0dd6e34-86d2-5297-913f-37b8b638172d | section | 4.0 - Post Construction
fc9c9030-8e63-5899-b7a4-3ce432cd125e | checkpoint | 4.1 - As-Built
d2db8983-8962-5251-8907-3a1af8d4868b | note | Frequency - Each lot
d40e1033-e6a3-5a67-ba70-c917adff63e0 | note | Acceptance Criteria - Submission of surveyed luminaire position to superintendent prior to practical completion
13b6ec89-5610-5d0c-bab6-59a273075fdd | note | Reference Documents - WP-001-09
887bebae-c0ad-58b6-85b9-cd2ff8c8f678 | note | Inspection/Test Method - Verify
61623fca-ce75-5d91-8d5d-d6ab18564d4d | note | Record of conformity - SCP
a5c81aff-54c0-5186-b766-f50c3760b787 | note | IP
f9903796-9cf8-5ea2-b162-9e3f120f9827 | note | Responsibility - Project Engineer
bb1d6c76-c8ea-5a38-b46f-92638b522829 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
c44b9953-a27c-53c7-86a8-3482ecbc51a0 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
dadff64c-aa37-5bda-834d-acbbc2fccf63 | textbox | Print Name:
b3256f93-fe30-5261-ba15-c2ca5080105d | textbox | Position:
22333328-1ec8-5b1f-b442-2c4df6d45cbc | date | Work Completed On:
915032fe-efc9-5633-8c63-2d8aa5994c45 | date | Date:
6006b4cb-b0a6-5fca-873e-b21b8b4167c0 | checklist | FH-ZU2-QU-ITP029 - Topsoil and Grassing - Rev 0 | itp | ITP029 - Topsoil and Grassing
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
3b455b0c-df8a-5f1c-a79d-c52ea7a6a8ab | note | Frequency - Prior to commencing any activity
29a5a0fb-8c5f-5829-97c4-410a0803f5db | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex.
5eda98ec-8fb0-5741-a8e1-c7c40ccd2dad | note | Reference Documents - Drawings and Aconex
195bdef3-62b1-5bf1-beda-08a907688282 | note | Inspection/Test Method - Verify
4b5a655d-77ec-5c91-bd29-6a80e9931a2d | note | Record of conformity - This ITP signed
3ccce2ad-1d19-5b28-b3b3-7dee77eb89fc | note | HP*
25e4db16-7785-59d5-87e6-cc0420ae4731 | note | Responsibility - Project Engineer, Site Engineer
a93086e7-5190-5256-8d5d-1717712b6210 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
e6b2b67c-e0e8-5f5f-a2f9-e1a3c81010e5 | note | Frequency - Prior to commencing any activity
dc31e77f-30f1-5b15-aff1-6c4d965a4c8b | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
4c3546f3-020b-55b8-a279-10f8c0c10cc9 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
6724336f-d1f3-53d4-aeed-2b90dd156027 | note | Inspection/Test Method - Inspect
84f6f406-6ed0-5476-a871-03a19d856734 | note | Record of conformity - This ITP signed
b3972c52-fb7e-5b81-a56f-df6f0f80d788 | note | HP*
dbfa3b13-0391-5e7d-8b30-4ee248da766c | note | Responsibility - Project Engineer, Site Engineer
73e35de8-dacb-575e-91ee-4937df969a01 | date | Date Completed:
7eb2974f-59a3-5b8d-a6e0-aa0c675c7b2b | checkpoint | 1.3 - Material Approval
e69a4fd6-eb2b-5c83-946d-b8c141f28e0c | note | Frequency - Prior to hydro seeding
76f70115-2ab2-5dff-970d-59a9e457cb7e | note | Acceptance Criteria - Hydro mulch supplier are either to be Flexterra HP-FGM, Vital Bon, or Hydro Mulch 1000 unless agreed otherwise by Melbourne Airport.
47ba3291-edb8-59a2-9c2c-c0f1fe8ce22a | note | Reference Documents - Grassing Spec cl. 7.2
ddb7657a-4539-5c8f-92f7-f61cd4c30d23 | note | Inspection/Test Method - Verify
f319968e-522a-583f-ad61-408af2693a4f | note | Record of conformity - ACONEX, This ITP signed
774542f1-492c-5de9-a65b-e4b5e53c1d23 | note | HP
6fe8fdbf-d96f-54de-ae62-65012f523451 | note | Responsibility - Project Engineer, Site Engineer
895a271b-e90f-59de-89e8-ef64c690a0b0 | date | Date Completed:
19d86115-8851-5070-b2a5-57661884286d | signoff | AUTHORITY HOLDPOINT
b50dde49-0719-5a28-aac3-589ad521f851 | section | 2.0 - Herbicide
10ee340d-ecf7-5aad-bf29-b25b09c9c16a | checkpoint | 2.1 - Topsoil Material
121fea79-5a6f-5520-9736-6f5ecc0f1b3a | note | Frequency - Prior to topsoil placement
68d37ac7-884c-5db6-ba8f-2254cd6f50d3 | note | Acceptance Criteria - Topsoil material is to be virgin topsoil free from clay lumps larger than 50mm in diameter, contaminants, pest, weeds, stones, subsoil, tree, and shrub roots.
c2738e77-b8fb-53e9-b554-5b1c71779944 | note | Reference Documents - Grassing Spec cl. 7.4
4ed17697-54e6-5fe8-a4a4-44103ffea086 | note | Inspection/Test Method - Visual Inspecti on
afd1e987-a2a8-5c61-8c03-378ed2ada6fd | note | Record of conformity - This ITP signed
4735cb8a-826f-5729-91d1-f9a4f753861c | note | HP*
3f8a9cbc-78f6-5230-a3bd-1458d3bd77c6 | note | Responsibility - Project Engineer, Site Engineer, Enviro & Sustainability Advisor
97fcac60-3ba7-5750-87ae-af29d5c984f5 | date | Date Completed:
1dfea3b9-d16a-5f2e-a8be-72e3a8adb60a | section | 3.0 - Placement of top soil
fdd73569-43c3-5ac6-9387-4ec01cfd9142 | checkpoint | 3.1 - Topsoil placement
332dff45-1f69-58a7-bc82-5d383410af29 | note | Frequency - Each Lot
0182e849-7f3c-5fde-9854-a88538c8193b | note | Acceptance Criteria - APAM engineering standard (MAS- CVL-001-V1-1-Grassing-Standard – Dec 2022) calls for a uniform thickness of not less than 100mm of topsoil prior to seeding and subject to the Contractor making necessary allowance for compaction of the topsoil prior to Hydro mulching.
4f2616c8-7420-56b4-8c1f-ccb232e64981 | note | Reference Documents - Grassing Spec cl. 5.2
c87334f3-efe4-5932-8782-061264e8c10a | note | Inspection/Test Method - Verify
102ee9d9-bb4f-57ff-b3b3-dcb3e3b24887 | note | Record of conformity - Survey data
be0ec143-e6cb-5e9a-b00f-9ff7baafa4d8 | note | HP*
18308c07-7d0a-51e5-9d23-2b94196ce4a7 | note | Responsibility - Project Engineer, Site Engineer, Foreman
b30a613c-9fa5-56b3-a547-31bfd246ee0f | date | Date Completed:
8401add0-f8c6-5126-85ad-957bd9c9d47e | section | 4.0 - Hydro seeding
522eab20-d28d-56ce-a99f-6f8fe47a5d5a | checkpoint | 4.1 - Grass Seeds
a62c0590-1756-53d9-ae85-4fd1f451ba31 | note | Frequency - Each Lot
ab8fbaa1-3def-5c8a-9785-23cc7789537b | note | Acceptance Criteria - Grass seed to be used during hydroseeding is to be the following:
b9157f92-2f32-5304-861e-c35d5cf27906 | note | ○ 50% Common Couch & 50% Colosseum Ryegrass during the warmer seasons (October to March)
8156911c-89b2-56af-ab66-c62045259e17 | note | ○ 100% Ryegrass during cooler seasons (April to September)
8194b431-f749-51c3-ad13-95ae4720fc93 | note | – Use of other grass seeds to be approved by Environment and Sustainability Manager.
2fe5a693-3a69-54ec-a9e9-bd8ed78cc0d7 | note | Reference Documents - Grassing Spec cl. 7.1
ab2487d0-5ba7-5eab-88b0-3d3f44a07e3d | note | Inspection/Test Method - Verify
7de79e55-493a-5453-beed-82c3888744eb | note | Record of conformity - Aconex material submission
5e722056-6c3d-5120-b734-29e4054fda1d | note | HP
e28aed0d-e6a2-59d0-b171-68a6ce0ed6ab | note | Responsibility - Project Engineer, Site Engineer, Enviro & Sustainability Advisor
ffb78f2c-484c-55cd-8e72-82650909293e | date | Date Completed:
7059c742-95e2-5e4e-9420-0139ba15f2e4 | signoff | AUTHORITY HOLDPOINT
1bd80803-d9e9-5db0-a5cd-014ba6cfa644 | checkpoint | 4.2 - Coverage / Tolerances
d50c7e95-efad-5cc6-910a-e17952611883 | note | Frequency - Each Lot
11ed75f1-485a-507c-b69f-973d461d6a27 | note | Acceptance Criteria - A minimum of 95% healthy cover it to be achieved. 95% grass coverage will not take into account any growing weeds as part of the cover.
713141ba-d806-5c54-b6e1-6c607774aca7 | note | Reference Documents - Grassing Spec cl. 5.6
e0b141db-bab3-5044-bb3c-2d2b7977aaeb | note | Inspection/Test Method - Visual Inspecti on
24855dfb-da22-5ee7-bca7-934d64c0d7a0 | note | Record of conformity - This signed ITP
612abc13-5422-58a3-aa38-2b87270048ba | note | HP*
850f33a0-9d7f-57aa-b254-5a41e55ef2d3 | note | Responsibility - Project Engineer, Site Engineer
4c2eca47-c97f-522c-907e-2369fffa30c5 | date | Date Completed:
65a8a184-fa65-5663-8723-e9738e5bb431 | checkpoint | 4.3 - Stabilisation Treatment
5d2b062d-d5cd-5f57-bce5-82f643e4acf2 | note | Frequency - Prior to opening area to airport traffic
d438457d-ea2c-5c11-97ea-f263705e337b | note | Acceptance Criteria - Use of Vital Bon-Matt Stonewall, or equivalent, is to be prioritised instead of the use of bitumen emulsion in areas prone to jet blast following topsoil and seeding. FH will use bitumen emulsion if directed by APAM Operations.
b3f56920-bc7c-595f-b9f3-cdbb81213829 | note | ○ Use of alternative stabiliser to be used for the works is subject to approval by Environment and Sustainability Manager.
1ff87080-2032-5cb1-a5c2-08b1a814197f | note | Reference Documents - Grassing Spec cl. 4.9
6726ede9-0d8f-5224-8833-51abc2a3663e | note | Inspection/Test Method - Verify
e38b7577-8613-555b-8e6b-623d7b0fed74 | note | Record of conformity - This signed ITP
add1b41e-bf73-5cea-8b88-e85a5a088f19 | note | HP*
e8125edf-99fe-58a8-ac07-4bced42ad9f4 | note | Responsibility - Project Engineer, Site Engineer, Enviro & Sustainability Manager
1f7ab866-31ba-5af1-bddc-cbbaec7d8825 | date | Date Completed:
d4b3c58c-425e-5d48-8e64-d4a361d36b8e | checkpoint | 4.4 - Hydro seeding
e63160d6-a6ab-5e9f-83c5-e8fc11c7e451 | note | Frequency - Each lot
ef2f4f6d-29be-5685-9cbc-502309f650cc | note | Acceptance Criteria - Application rates shall be more than six tonnes/ha flexterra or alternative (vital bon / hydro mulch 1000) unless agreed otherwise.
8d7990e9-0478-505a-a5e4-8e2bcbceac4e | note | Reference Documents - Grassing Spec cl. 5.5
0dc89bc2-906d-5b9a-8697-4a2ef9ee1c74 | note | Inspection/Test Method - Visual inspecti on
1ee2b8d2-a991-5301-b613-1e2cd9287d74 | note | Record of conformity - This signed ITP
1ea3ef8f-bbf3-54b8-aaae-853c50c9ac3a | note | HP*
c148f76b-5bd7-5aba-84cb-a3a2755c676b | note | Responsibility - Project Engineer, Site Engineer, Foreman
4cff54af-709f-51da-8da6-10a9d99aa1d3 | date | Date Completed:
9e7d1168-4b28-5f78-bd22-f2a3ef41bd04 | checkpoint | Reinstatement of Disturbed Surfaces
44776fcc-d25e-5d37-a936-9c9634567373 | note | Frequency - As Required
85f4fbd6-d095-5d42-995f-7a751b5ff116 | note | Acceptance Criteria - Hydro mulched areas are not to be trafficked for 3 months or until grass has been established.
3898c38d-53f4-5ea1-9b61-98e2a492c9ba | note | Reference Documents - Grassing Spec cl. 5.5
29f39ab4-605c-5081-9e0d-88ee910f6fe3 | note | Inspection/Test Method - Visual inspection
4c19778d-19d1-50fe-8735-ce062c0811ea | note | Record of conformity - This signed ITP
def3e65b-0887-51cb-a2b1-73b176057165 | note | HP*
560c63db-1426-52d4-82c7-6f350cb5a7d6 | note | Responsibility - Site Engineer, Foreman
4631bfec-a164-59e4-aa7e-e4147cc7a84d | date | Date Completed:
3e68cc9c-da03-5c12-a911-0dcb053881a0 | section | 5.0 - Post Construction
c6cdc8e3-eecd-54bb-b50d-c535e7bdab5b | checkpoint | 5.1 - Reinstatement of Disturbed Surfaces
02f8159d-348b-5556-809b-b39c7131cd7c | note | Frequency - As Required
a62a8e47-63c1-538d-bff8-756ef9d0d9e3 | note | Acceptance Criteria - Disturbed surfaces are to be reinstated to their original condition. In areas prone to jet blast, the topsoil surface should be sprayed with bitumen emulsion, Vital Bon-Matt Stonewall, or equivalent, following seeding if grass strike has not been achieved prior to opening the area to aircraft traffic.
1703378e-f25f-552c-bca3-85e58d5b900e | note | Reference Documents - Grassing Spec cl. 4.13
30eb13d0-5cd3-58bc-82c1-05d4a8f892f2 | note | Inspection/Test Method - Inspection Point
e063f192-ac41-5209-9b71-6da2e67c3dd6 | note | Record of conformity - This signed ITP
191b7b79-b18d-5ab6-b43a-84d36a3b8f99 | note | IP
dc9c7e00-6ea9-5017-a9f8-956e1642bc72 | note | Responsibility - Project Engineer, Site Engineer
1ec2c84b-c1b6-56d7-917e-7615d8ee093c | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
2420c0c4-f05f-565b-9c33-0f000dc15e8d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
765bf4a2-cae1-5a9e-874b-770434bb0e32 | textbox | Print Name:
51ad3199-cbb8-55c8-90f6-ada6168f2c26 | textbox | Position:
1c53a362-da89-5590-8a58-2c8453cb7311 | date | Work Completed On:
c62ac221-9d9a-52d2-93b2-3ac632e66716 | date | Date:
d8fe27e8-cb1d-4b8d-bc8b-16f64532cfd8 | checklist | FH-ZU2-QU-ITP030 - ALER 3 Groundworks - Rev 0 | itp | ITP030 - ALER 3 Groundworks
b6468ec3-8d28-4866-a8b9-1846dabd52f2 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
66c85a2f-f057-4eda-9b4a-0eb363d6ba82 | checkpoint | 1.1 - Check for correct documentation
4fd13d14-090b-5076-ac1f-ecc61124a60c | note | Frequency - Prior to commencing activity
66ee8ce2-d804-583e-84be-8dd6493254f0 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
33969afe-b5cf-52a8-a8ee-c7305ceb1024 | note | – using the correct and complete set of drawings.
4ad42863-9d5f-558c-8cae-922d6c8dce5d | note | – all drawings are the latest revision.
e06cdbc1-70db-5fff-bd97-3eac98c3fea7 | note | Reference Documents - Drawings / Aconex Register
32b2e300-4a2a-5a41-88c4-c83393942f68 | note | Inspection/Test Method - Verify
9f34f180-b0c1-59e6-b72b-bcbc3addfcbf | note | Record of conformity - Drawings and drawing registers
605bea02-42f2-51f5-bc5a-abc010f8b98f | note | HP*
5931ba92-403e-598f-95ed-74351fb48958 | note | Responsibility - Project Engineer
83b8fee5-2ecf-56a0-9e37-1c4a08fb5fdb | date | Date Completed:
6d968585-c3bb-4939-9757-7e877650b3c5 | checkpoint | 1.2 - Implementation of all measures and controls
bc21d9bf-a06e-5d0b-80d8-09383f0b14c3 | note | Frequency - Prior to commencing activity
66e6b91e-5004-5583-8d6e-4bd4b6ed912f | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
73a67ea2-d588-5579-802a-a126654f83ee | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
beb68b6a-7030-5486-ab53-1ad3d4863dde | note | Inspection/Test Method - Visual inspection
e92999bb-8a27-5b7f-906c-be877169e219 | note | Record of conformity - This ITP signed
ee57f482-9fc5-5460-b260-c1029f2723b6 | note | HP*
4b6d6c39-7a60-5db2-bf6e-f44477c81d88 | note | Responsibility - Project Engineer
7565f229-73f0-5739-88af-b61738bf7aa4 | date | Date Completed:
d2f7d06a-c661-4d8a-8167-ece6323dbfc7 | checkpoint | 1.3 - Definition of the work area (survey)
ca4fd58a-4d48-5325-9f6f-fb32632d747e | note | Frequency - Prior to commencing activity
3f2ebf23-beae-5655-9f48-87e05b8921bd | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined.
534cadbf-0d90-5378-9662-c73301a8c5d7 | note | ○ Pits & trenches all marked out prior to excavation commencing
be75a025-544d-549a-b98f-c36e554c854f | note | Reference Documents - Drawings
bbe7f2ef-81de-5c14-b811-0acb91b61238 | note | Inspection/Test Method - Visual inspection
c5a3c469-7c65-5bfb-ae5d-03f6817cbf18 | note | Record of conformity - This ITP signed
d24585e5-489f-5ade-ae17-37a251d4abbb | note | HP*
01848afa-0402-5502-ac45-d78d1275fd6d | note | Responsibility - Project Engineer / Surveyor
3a62ee66-cf07-5408-84f8-a018dd89cf80 | date | Date Completed:
1e131eaa-7821-4f44-b73d-ceac8fa3c7c8 | checkpoint | 1.4 - Material submissions and pipe compliance
e529b769-9685-5c50-8c29-6405989279a0 | note | Frequency - Prior to commencing activity
8b4b40d9-8edb-5396-8656-62adcadc7912 | note | Acceptance Criteria - Material submission of:
92a93712-2d9a-5ed4-9941-c60fb9650c44 | note | ○ Electrical
ef6323ae-3e8e-579d-8f5d-065889712ef7 | note | – Ensure uPVC conduits comply with AS 1477 or equivalent AS 2053
f15b70b8-e314-5c4e-9e18-cb1872fa617e | note | – Shall be heavy duty, orange for electrical services and white for communication services
6c996737-cf7e-5127-8d68-3b4ca2a136ca | note | – Ensure pipe diameter is correct AS per drawings
22ad7d40-ef26-584c-9bc7-aab1cb4149e8 | note | ○ Stormwater/Sanitary Drainage – Below Ground
ab4d9dbb-7d98-572a-97b0-958e5191b1d8 | note | – uPVC Non Pressure Pipes shall be DWV MIN SN8 Solvent Welded to AS 1462 with an environmental product
c9c95f8e-d928-51fd-bbcc-14471f906789 | note | – uPVC pipe Shall be SN10 SWJ AS per DCWC Mgt-RTRFI-1317
c76a3bbf-224c-5cbb-92e7-75836ca79517 | note | ○ Cold Water – Below Ground
8f32d90e-0051-5f46-9a76-48e1eb34dd22 | note | – Polyethylene pipe shall be used conforming to AS 4130 & 4131
8551ae16-112a-55e7-b304-85939201e469 | note | Reference Documents - Drawings
c38a792d-9147-5e17-ac5d-0740859d1644 | note | ○ ZULU-BECA-001-SPC-00004 Cl. 3.4
23c569e8-f561-573f-9368-032ac9d6a1ac | note | ○ ZULU-BECA-001-SPC-00005
153a5404-1c21-54d5-9fa1-0a15003e1d50 | note | ○ Table C1710-A, AS1477, AS 2053, AS 1462, AS 4401, AS 3500.3, AS 4130, AS 4131
2dedd07d-f11e-525c-b5f5-22c5b7826aaf | note | Inspection/Test Method - Verify
02e62425-76fd-512c-9cfa-0c871530b9ac | note | Record of conformity - Aconex Reference, This Signed ITP, Building Engineering ITC
10250a77-29f9-50d0-8322-7acb541d92df | note | HP
a02efb04-7c6a-5b89-9981-80b5658cffc1 | note | Responsibility - Project Engineer / Principal’s Representative
945b580f-83a9-5739-b42d-09c405369bba | date | Date Completed:
41e9f41d-fe99-477f-80c6-d0a927e00b72 | signoff | AUTHORITY HOLDPOINT
77ae5afc-71c3-4b95-840b-0e97bf4b69d4 | checkpoint | 1.5 - Check bedding material compliance
2c571580-0f5d-5a8f-b4e8-49866a0b9bb3 | note | Frequency - Prior to commencing activity
f2262bcb-e41e-5008-b7d8-91e3658d9bda | note | Acceptance Criteria - HOLD POINT
6a39db73-051a-53bc-abf4-f6c274bb9f1b | note | ○ Electrical
34ad3722-4931-58ba-9480-fc3876ec1abe | note | – Ensure that the conduit bedding material is non- plastic granitic sand complying with Table 3-1 and 3-2 under cl. 3.8.3.3 of the Works Specification
259fad47-231b-57df-9caa-46eb71e9827d | note | ○ Stormwater/Sanitary Drainage/Water
296ba5dc-3d60-59ce-b7d2-3c3bea4e5de5 | note | – Ensure Bedding Material is Well Graded
849716ba-8e45-54ad-8e91-e6cd6abaf3f4 | note | – Manufactured Sand to VicRoads Specification 407 Clause 407.03(f).
433a39d8-b085-5306-9e51-bdb2a1d3821f | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.8.3.3
c0117bee-0129-592b-bd1d-90f917b2e783 | note | ○ ZULU-BECA-030-DWG-00201 Note D03
b7bc1ac2-7338-5914-a0cc-fee7b0f26726 | note | Inspection/Test Method - Verify
d2f4e54d-854b-5ed4-a373-74e87b28e66a | note | Record of conformity - Aconex Reference, This Signed ITP, Building Engineering ITC
eb768e6a-d13d-5fe6-9fc9-d4d6e9d2ab5f | note | HP
a1e47a2b-45ff-5d53-9bfe-e83a2cb544da | note | Responsibility - Project Engineer / Principal’s Representative
d2eb2153-bf94-5670-ab74-55f405b308be | date | Date Completed:
3ed30c02-9996-4b05-aef0-30472fa95cbb | signoff | AUTHORITY HOLDPOINT
b17c037c-22de-44f9-9f8b-1aa2be406fb5 | checkpoint | 1.6 - Material Submissions and Shop Drawings
6ca2d775-fb67-57c2-bcb7-f169e726aaa8 | note | Frequency - Prior to commencing activity
bb11dd27-cb59-57db-8985-3505ca7fd6f7 | note | Acceptance Criteria - Submission of:
bda42b8b-f270-5fb6-870e-2209767d7653 | note | – Spel Puraceptor for approval prior to commencing works.
dc6f1b00-7d1a-50d5-93c9-cb0ee83cb16d | note | – Septic Tank & Sewer Disposal Unit Design
368ce014-ff40-5866-9474-f27b325bd217 | note | – Pre-cast Pits for approval prior to commencing works
6c26b4e5-074a-5dd7-aaaa-a7d6ff28fadd | note | – Precast headwalls
06d207ee-435f-5bda-bed3-41c35734acab | note | Reference Documents - ZULU-BECA-001-SPC-00005
f37e4e7b-5cf8-5f88-b3df-a2e1dcce8efb | note | ○ Drawings C1700 cl. 3a AS 1546.1-2008.2
e1aac23b-37b0-5101-bf9b-b4918f5ef176 | note | Inspection/Test Method - Verify
be4b2ca1-0aa6-5531-ba66-f2e92ad429b1 | note | Record of conformity - Aconex Reference, Building Engineering ITC
8e7206b0-e55c-5177-bfd5-53b1f170d305 | note | HP
d46655db-4d3e-5cc9-b699-6fb5d487464f | note | Responsibility - Project Engineer / Principal’s Representative
e0259936-f34a-5afd-b1af-75e3c44dd954 | date | Date Completed:
a930f738-bf4e-4e0a-bf81-4d91a24ea9f4 | signoff | AUTHORITY HOLDPOINT
9db186c0-1e25-48d1-8fb8-8434e932368b | checkpoint | 1.7 - Permits & relevant approvals obtained
385c4c59-a517-5a27-9a60-718de9816a2e | note | Frequency - Prior to commencing activity
6606e056-2df4-5056-971d-e35c19b3d09a | note | Acceptance Criteria - Excavation Permit
b30fc166-7862-5d4a-8c74-443951a866f9 | note | – Location of services to be found and marked on the ground within the works;
ee709bc7-42da-5680-9978-e24c553b5be6 | note | – Contractor to obtain excavation permit from APAM prior to any demolition works.
00cafb75-1109-52aa-9d25-8b5e31c179fd | note | – Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
50ba3d0f-dfd0-56d5-a9f7-9d88e6065bcf | note | ○ Service conduits shall be protected from damage due to subsequent construction operations as required using whatever measures are necessary. Any damaged conduits shall be removed and replaced at no cost to the Principal.
bb5e8056-c0d8-54de-81df-155dfdd2d480 | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.15
eea5bde8-2ac7-5f81-b624-f68a093dc1b2 | note | ○ WMS-002
07024245-5c42-568d-9ec8-31b0dc64cb51 | note | Inspection/Test Method - Verify
ce2806fb-d9c5-5bca-b0ab-a21f6afa8c73 | note | Record of conformity - Melbourne Airport Excavation Permit, PIC
0011384e-cd88-50ab-95f9-5bcd6b3eb54b | note | HP*
5c25b1c1-d7b2-5b77-8725-fba76adcdb6b | note | Responsibility - Project Engineer / Surveyor
768dd82a-4187-59a4-8f64-a4c8a7e1e8ee | date | Date Completed:
e34e05f3-7263-493d-9287-26943a6513d4 | checkpoint | 1.8 - Native Grass Protection
6d9ea899-ed7d-5cd4-bdd1-864c2e77ee73 | note | Frequency - Prior to commencing activity
04d0e116-764c-5b6c-8452-a09259c4c8bd | note | Acceptance Criteria - Native grass protection installed. As per native grass model
acc04b65-cd9c-5d84-b51c-fe2f73953b09 | note | Reference Documents - Relevant Native Grass Permit
a592f9e2-dfd2-5d8c-9ffa-b4f17f734b63 | note | Inspection/Test Method - Visual Inspection
c1328a0a-e5bd-5710-9fb6-5b5f010fc21a | note | Record of conformity - FH-ZU2-QU-ITP038, This ITP Signed
709d56e4-413c-5228-8c5a-b937bbfb83d6 | note | IP
4a688fb7-6a49-5746-af79-91da6cc34551 | note | Responsibility - Project Engineer
9adecd8f-fe56-5561-8d00-8b3788fb5564 | date | Date Completed:
28bcf6d2-69df-4511-a469-d9c1a5b98b10 | section | 2.0 - Construction - Stormwater
a5c7ba1b-e6a0-4407-b5dc-7428727f9261 | checkpoint | 2.1 - Excavate trenches for pipes
a297126c-6462-516c-8d87-7287b313d33c | note | Frequency - Each lot
7db50315-8217-555e-8791-602e869eccce | note | Acceptance Criteria - Trenches for pipes shall be excavated to the width and depth required enabling construction of the pipes to the requirements specified on the drawings.
24995865-d116-546e-a2aa-be5d0ce60668 | note | – Inconsistent, rocky or soft material at base of trench shall be excavated and replaced with compacted select fill
fcdb807a-9818-5b8d-8180-fc77e1670a7f | note | Reference Documents - Drawings AS 1289
5b177ddc-f874-5248-817e-acd5abdac2c2 | note | Inspection/Test Method - Visual inspection
c77a8d0e-01cf-59dc-bb85-afa2845fee8c | note | Record of conformity - This ITP signed, Building Engineering ITC
1a361107-a5dd-53a6-8c40-43841bcf9d1c | note | IP
e21baca4-f35b-579e-87be-4e71782116de | note | Responsibility - Project Engineer
4091c989-2a94-5de9-b5a1-89dcf36100c1 | date | Date Completed:
ba24ed20-ea59-4f10-bb43-57c72c6a82ae | checkpoint | 2.2 - Existing services crossing new pipes
d92c0b18-c8a9-51f4-9cc9-104ce5aec41f | note | Frequency - Each lot
5010d2ea-2941-5f73-8936-0c9144b300c6 | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
31ef19cf-489e-5457-ac19-91d625ee7559 | note | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
b1860150-edd0-5019-b4a6-ea9c3e10de18 | note | Reference Documents - WMS002 – Working Near Existing Services
07149115-db0e-5dde-a8af-8ac1f4fa8611 | note | Inspection/Test Method - Visual inspection
a4b79c8a-70dc-52a9-9d00-198343fc87c0 | note | Record of conformity - As-built survey report
2f65b858-b802-5acf-a039-1c30be8e8abf | note | SCP
b1c281b9-3c27-5f6c-acab-ae3fc138c776 | note | Responsibility - Project Engineer / Surveyor
540963c4-0151-5478-a1c1-1a640ff3e46e | date | Date Completed:
2f2fa42e-8012-4b84-80f9-fc2a588b17d9 | checkpoint | 2.3 - Laying and jointing of pipes
3b0353e6-89ad-5bf0-b4b1-1cec099ce7e3 | note | Frequency - Each lot
f0255c12-7a5a-5e67-8d56-a3645a707622 | note | Acceptance Criteria - Pits, pipes & structures shall be constructed to the line, levels and dimensions shown on the drawings
ad4fe8e0-f82d-5216-89d5-d496c1d4acce | note | – Pipes shall be bedded evenly on sand compacted to min 100mm thickness below the socket
89e13217-42bd-5237-8be4-3a16a6cc516b | note | – Pipe laying Shall be constructed at the downstream end of the pipe run. all Pipes Shall be laid with sockets pointing upstream
e5184946-c419-5c79-b0b7-62a7ab146937 | note | – Lay at MIN grade 1:100 UNO.
f42c536d-ef8d-5b10-829a-1db2e7ad839b | note | Reference Documents - Drawings
35977add-9a8f-5b43-9ad9-2dd7d75cfc94 | note | Inspection/Test Method - Visual inspection
d729777c-7f25-5e60-ae61-df9d25306255 | note | Record of conformity - This ITP signed, Building Engineering ITC
edbb05b8-8f4f-5580-b736-8ec15e831b31 | note | IP
7a8a5c57-c27a-5e5e-8399-956edfea2f97 | note | Responsibility - Project Engineer / Foreman
b28533cb-a986-5b6d-8faa-a94b736f8ffe | date | Date Completed:
54d6deab-1aae-420f-a0b3-2bb039f7f191 | checkpoint | 2.4 - Pre-backfill inspection & testing
ad1b93f8-7ea8-501d-a5b0-42815fdcde5c | note | Frequency - Prior to backfilling each lot
1903e199-f368-57da-8f31-8db52d06993c | note | Acceptance Criteria - HOLD POINT
9b76851f-2c9a-55fb-8014-57d4ca17b863 | note | ○ Backfilling of the trenches shall not proceed until the pipeline has been tested and inspected.
89294627-ab01-5f5c-874b-79572ceca63f | note | ○ Check for leaks to the requirement of clause 15.2 of AS3500.2
6c63ecce-3b32-5e88-a30d-41899cdd1080 | note | – Inspect for proper laying and jointing
d19b5c23-9882-5e22-9c88-da8f70ed4f76 | note | – Pipeline has continuity in fall
14e783ec-8e44-5f96-a6e8-cf2c755a317d | note | – Expansion/swivel joints provided for all pipework
c5a05143-f7e7-51fc-98df-c8861ca721a1 | note | – Testing as per AS 3500.3 to be carried out
d5f7a963-39f7-59c6-8106-814a35e720f7 | note | • Water Test
69c2e0de-4baa-5f33-824c-907f16fd0a4a | note | • Air Test
8c84844e-a097-5fdd-bdef-991963b4c684 | note | – Building Engineering to run camera through Stormwater pipeas and upload link
78f6ae3b-bc4f-540d-bb9a-1ff53c99e4e3 | note | Reference Documents - Drawings
2fe3129e-3876-5549-a904-e683046269e9 | note | ○ ZULU-BECA-001-SPC-00005 C1700.8 2c, C1700.2 .2a, AS 3500.2
ce1e34ef-a18a-58d6-8558-132cbed74279 | note | ○ Building Engineering ITC
f8892474-3e96-5e03-afe0-3170054665db | note | Inspection/Test Method - Visual Inspection, Test Result
2cbbe4f6-e42f-5895-b531-345782795ee5 | note | Record of conformity - This ITP signed, Building Engineering ITC
b2e1a587-00d7-5534-8e67-cf88d8f6990d | note | HP/TP
3a9104e5-e23f-58ff-9700-48323346cfab | note | Responsibility - Project Engineer / Principal’s Representative
4ba30ac0-ef6a-52ae-874f-49ce1ca8494f | date | Date Completed:
446d6d2f-6184-4352-b1d7-a072096bb9b3 | signoff | AUTHORITY HOLDPOINT
45bea17c-342b-4836-acc0-0cc82a6026e1 | section | 3.0 - Construction – Sanitary Drainage
cf6b6159-2553-4bf4-bd61-1241af222729 | checkpoint | 3.1 - Excavate trenches for pipes
8c7806ff-fcf1-5d77-9651-875b47e91825 | note | Frequency - Each lot
97fa39f0-7a07-5f44-b035-511f15d296fb | note | Acceptance Criteria - Trenches for pipes shall be excavated to the width and depth required enabling construction of the pipes to the requirements specified on the drawings.
e9b8f515-43d5-5246-bc25-aec171ba758f | note | – Inconsistent, rocky or soft material at base of trench shall be excavated and replaced with compacted select fill
db972636-738d-52b8-b1a6-bf8641a54edd | note | Reference Documents - Drawings AS 1289
847355f3-bcfa-5e6f-a113-c73eec5f2aa3 | note | Inspection/Test Method - Visual inspection
6a017eeb-82e2-5aae-9bd9-7d38cfda2bd6 | note | Record of conformity - This ITP signed, Building Engineering ITC
19564aa9-d5b1-5136-972d-42ff0ccf2a0f | note | IP
7c3e7145-ef72-5f1b-a854-72b746008998 | note | Responsibility - Project Engineer
9b87dc8a-9175-5136-8adf-1459fe00fefc | date | Date Completed:
313915e0-3116-4c3e-b2bc-0b4204e3e243 | checkpoint | 3.2 - Existing services crossing new pipes
7d4f33b2-53b8-58b3-97a8-9eb83f209ae7 | note | Frequency - Each lot
3ea30ad9-4d5f-5af0-9d0d-0fd38cfe6639 | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
85d0e942-0de6-5e25-8817-9539547a34d9 | note | ○ Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
e57e27cb-9734-5ebb-b921-25e5b835fbd0 | note | Reference Documents - WMS002 – Working Near Existing Services
4ab38647-b782-52b2-add4-19b6b7453ee9 | note | Inspection/Test Method - Visual inspection
46a5157e-e298-5bad-81a7-b234ac6f0f00 | note | Record of conformity - As-built survey report, Building Engineering ITC
664e5aff-79f3-5396-aeeb-2e2789b1a0e0 | note | SCP
6c7035c0-0af2-5e7a-abd7-644de0da6c49 | note | Responsibility - Project Engineer / Surveyor
0f307240-1886-5595-9770-30e0b5073b9b | date | Date Completed:
457d19e5-721c-46a2-8416-df9b81c3638e | checkpoint | 3.3 - Laying and jointing of pipes
fdfa6d0f-69c3-5e81-b8c0-2b9a826a1402 | note | Frequency - Each lot
c056fa19-12d9-5bd6-a898-1cb5280b5e98 | note | Acceptance Criteria - Pits, pipes & structures shall be constructed to the line, levels and dimensions shown on the drawings
c6b9e4ba-6f7c-5162-a26c-4148f8f7d97d | note | – Pipes shall be bedded evenly on sand compacted to min 100mm thickness below the socket
c885d1e8-af72-5704-bff4-effcddba9d85 | note | – Pipe laying Shall be constructed at the downstream end of the pipe run. all Pipes Shall be laid with sockets pointing upstream
8d3aa237-1eff-56a0-afa5-d8dbdc11a5f9 | note | – Lay at MIN grade 1:100 UNO.
272f9eda-98a7-51a0-984b-516ac8aae7e6 | note | Reference Documents - Drawings
374bda96-7306-5842-8369-b3aa3947323c | note | Inspection/Test Method - Visual inspection
ebb9770d-e041-55ed-9b97-a182f1d19175 | note | Record of conformity - This ITP signed, Building Engineering ITC
63d35e62-8c40-540a-8965-916d5f7753bd | note | IP
5b1934f1-1960-5aa1-8a50-2693c8aa6852 | note | Responsibility - Project Engineer / Foreman
65e06c3f-5a90-5b4f-bbc0-49eb02567a32 | date | Date Completed:
82509668-c645-4694-bc10-6d7ff2b86c23 | checkpoint | 3.4 - Pre-backfill inspection and Testing
010361f1-9638-5f07-9d43-713dcdeac719 | note | Frequency - Prior to backfilling each lot
a2d1ab62-9c0f-5658-857b-6c32e1719d40 | note | Acceptance Criteria - HOLD POINT
c03b6a47-bba7-5833-a378-6cce1e2c78ee | note | – Pipeline will need to be tested and inspected prior to any backfilling
d4b6f60f-9d91-5174-81dc-fece7fa9d8fa | note | – Inspect for proper laying and jointing
923ce56b-236f-5985-8aa1-78b32583a867 | note | – Pipeline has continuity in fall
4cc55a83-2ec5-54dd-92d1-9b875ffa300a | note | – Expansion/swivel joints provided for all pipework
bbc18ff3-05ac-5d31-a3bd-56b480b90e39 | note | – Use temporary capping to isolate piping to be tested; fill piping with clean water and check for leaks to the requirement of clause 15.2 of AS 3500.2
e1759dc0-771b-5d21-a922-203313d2430a | note | – After testing, drain and reconnect the piping, flush the drains clean with water and check for fall to discharge
f7792468-6687-5f89-a33d-5886aa5dd77b | note | – Building Engineering to run camera through Sanitary pipes and upload link
eb56aebd-8a9a-52c9-84ee-cb01a872c8ed | note | Reference Documents - Building Engineering ITC, ZULU-BECA-001-SPC-00005 C1700.8 .2 C AS 3500.2
44535d90-c902-5a89-8b00-801064c63011 | note | Inspection/Test Method - Visual Inspection, Test Result
5528d656-826d-58bc-9341-51a3a0d0ce69 | note | Record of conformity - This ITP signed Camera Footage, Building Engineering ITC
4b6cfe42-cf01-5160-9d38-6607291d2165 | note | HP/TP
edf4398d-9c58-5167-974e-17d25204f0f6 | note | Responsibility - Project Engineer / Principal’s Representative
07cd460d-a6e7-59f2-9166-98f39b1d92f1 | date | Date Completed:
68c7d6b5-9ccc-492b-8589-b0b880af2c66 | signoff | AUTHORITY HOLDPOINT
3eec507e-58f8-4ddf-95e4-cc94027267d4 | section | 4.0 - Construction – Cold Water Pipes
b4fab121-db22-46d6-8ef8-de9ccaa2c7d8 | checkpoint | 4.1 - Excavate trenches for pipes
a9c67a52-74de-5457-b4ad-d9be3d5f0374 | note | Frequency - Each lot
b34b0b63-7c0f-5ddc-a625-bae9bb8c5d87 | note | Acceptance Criteria - Trenches for pipes shall be excavated to the width and depth required enabling construction of the pipes to the requirements specified on the drawings.
a529069b-7344-5925-8506-8e95f7dc822f | note | – Inconsistent, rocky or soft material at base of trench shall be excavated and replaced with compacted select fill
2b633649-3547-5002-9792-ee3cc6e09a08 | note | Reference Documents - Drawings AS 1289
9aaf3c8b-9d5d-5615-93e6-f551885e9455 | note | Inspection/Test Method - Visual inspection
2d0925ea-e711-5521-9fa3-1d20b609cffb | note | Record of conformity - This ITP signed, Building Engineering ITC
4b56bee5-4977-5d20-bbed-4db5a5d81f38 | note | IP
6bf0f3ff-1472-5548-8181-a5f664e73ad7 | note | Responsibility - Project Engineer
6c4f094f-cbe9-57d8-9f5a-2605f5f17d4d | date | Date Completed:
f381e59a-5d2d-4824-bb46-ca2a925075d5 | checkpoint | 4.2 - Existing services crossing new pipes
e96cc255-8921-55f3-962c-0c6e6c746f79 | note | Frequency - Each lot
8101c81d-1a1e-5837-8653-5cb80ae036a7 | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
408741dc-d324-5476-9603-e1e240c27958 | note | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
8680bcc5-58c3-5d9d-8548-99b15c8b0c60 | note | Reference Documents - WMS002 – Working Near Existing Services
ab3c8806-b6ae-5754-9ab7-d78b4399b4c3 | note | Inspection/Test Method - Visual inspection
e15a76b5-b809-5acd-bed5-db69f2ee4f96 | note | Record of conformity - As-built survey report, Building Engineering ITC
5e710dd0-d88f-5167-8df0-9ca38c6ae3b8 | note | SCP
241ab6e3-b2d7-5601-89de-873898e5b728 | note | Responsibility - Project Engineer / Surveyor
04e2ba2e-696a-5eb2-b60e-8e176421c2a5 | date | Date Completed:
f2224ebf-ef15-497d-8ea8-952316e2b618 | checkpoint | 4.3 - Laying and jointing of pipes
1443e3e3-606e-5d4c-bfe4-e9e27c2a6713 | note | Frequency - Each lot
d7c6b4b0-6619-51cf-b374-40c3308627e0 | note | Acceptance Criteria - Pits, pipes & structures shall be constructed to the line, levels and dimensions shown on the drawings
6c7a9112-f5d2-5cf5-a1e1-509559f7eaf2 | note | – Pipes shall be bedded evenly on sand compacted to min 100mm thickness below the socket
794ee1b3-05ff-5069-94a8-28bdcf0f023a | note | – Pipe laying Shall be constructed at the downstream end of the pipe run. all Pipes Shall be laid with sockets pointing upstream
7b1ddd85-54f0-568f-aeb1-99ac422f45f3 | note | Reference Documents - Drawings
4a7702c1-69fd-5e41-b2b9-135a589de5f2 | note | Inspection/Test Method - Visual inspection
0b528149-7ce8-504c-b95b-9120c2ce531b | note | Record of conformity - This ITP signed, Building Engineering ITC
fc01a11f-6de9-5e89-bbfe-8dff256561ae | note | IP
09515fc1-3968-5c77-912f-0349666cb3f6 | note | Responsibility - Project Engineer / Foreman
6984ec20-2520-5287-8b75-3b3ffe366be0 | date | Date Completed:
191d9742-27c9-49ad-a940-9b07e7a2704c | checkpoint | 4.4 - Pre-backfill inspection and Testing
038c5a50-849b-57b7-8247-ff9532e56f0b | note | Frequency - Prior to backfilling each lot
aa796a9c-748c-5829-829b-5636ecc4e979 | note | Acceptance Criteria - HOLD POINT
a0e36d3d-9bd3-5c79-bec7-cd04d9e0d2b3 | note | ○ Pipeline will need to be tested and inspected prior to any backfilling
43ebdf66-a270-5f48-a717-e8c97988d904 | note | ○ Inspect for proper laying and jointing
9663fa0e-9052-5d5f-a679-63422163c57a | note | ○ Conduct Pressure Test and Flushing of the Pipeline
c85dc92d-791b-5b62-809c-a92e4739d813 | note | – Prior to testing, flush all pipework and equipment with clean potable water until the flushed water runs out completely clear
df1c667d-a770-5273-b5c6-fe317984fafc | note | – Pressurise with clean potable water (free of oil and other impurities) and maintain the test pressure for 2 hrs
2719480c-d263-5ba8-b54d-214d8767c0a7 | note | – Immediately after successful testing, final flush all pipework and equipment with clean potable water at “full flow” for at least 10 minutes
f51140fa-4aaa-589c-a2b6-014a35ec4879 | note | ○ In addition to general flushing and cleaning requirement above, disinfect and passivate pipework systems in accordance with AS 3500.1 and any relevant manufacturer written instructions
92b0e9c4-46b4-5d2d-b098-5f3608c0e05e | note | Reference Documents - Drawings ZULU-BECA-001-SPC-00005 C1700.8 .2 a AS 3500.1
616e2453-617a-5bb1-989e-9de29875cf1a | note | Inspection/Test Method - Visual Inspection
d540ab4d-500b-5d4c-8b61-f5d10953a948 | note | Record of conformity - This ITP signed, Building Engineering ITC
826406e1-0eac-5b47-b8cf-98b27206b514 | note | HP/TP
604553a3-a815-526c-b84d-072f523c7336 | note | Responsibility - Project Engineer / Principal’s Representative
ef0aaa0c-ba2c-5bc5-b326-5098c7bfabbd | date | Date Completed:
af20ff8c-4f8a-490a-af70-397667aaa1e4 | signoff | AUTHORITY HOLDPOINT
ab3bb048-b91b-47ee-bf23-378288646064 | section | 5.0 - Construction – Electrical & Comms
12f75b6e-fa0e-475f-9b7c-fd6dfcc25333 | checkpoint | 5.1 - Excavate trenches for conduits
ea48a8a0-a34c-5b2a-8ea9-5fa59533d22a | note | Frequency - Each lot
a99dc15c-51b5-5731-b84e-4f22fff719aa | note | Acceptance Criteria - Trenches for conduits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
0f8bb527-9406-5506-aa76-f1037f41c65a | note | – The level at the bottom of the trench shall not be above the required level at any point.
8c381322-01dd-5d43-8e4e-c9c08354bd3e | note | Reference Documents - Drawings ZULU-BECA-001-SPC-00004 cl. 3.6
97f3c284-e9b7-5f31-b3e5-7a2b26bcecc5 | note | Inspection/Test Method - Visual inspection
4eceafbb-071d-59f6-a8b1-9bad0780826b | note | Record of conformity - This ITP signed, Building Engineering ITC
0ff200b0-8d09-5d5e-9989-546de0b09b95 | note | IP / TP
416072d5-ec89-5983-af65-5337d4e34eb8 | note | Responsibility - Project Engineer
5d7caf50-514c-5d6c-b2ce-4034c1955745 | date | Date Completed:
ba2c1b87-56f1-4a83-97b5-5a4efa084fa8 | checkpoint | 5.2 - Existing services crossing new conduits
6f790e3b-b6c3-5a66-8d47-24bd0fcb7705 | note | Frequency - Each lot
a22872f2-6f64-59df-8109-e03e88fde06d | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
fa61938c-1e7f-5c27-95cf-d6a0986196be | note | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
4a5741f1-e307-5256-9dbc-08e56f8b0586 | note | Reference Documents - WMS002 – Working Near Existing Services
623d9add-e448-5ca9-a20e-c07a468ddc3f | note | Inspection/Test Method - Visual inspection
a81e8d2d-3c5b-51c8-b837-14cf235b5282 | note | Record of conformity - As-built survey report, Building Engineering ITC
77ee8d0b-44c9-59cc-93a5-1cfc28011f7a | note | SCP
066fd1fe-213a-567e-9126-e7c286956531 | note | Responsibility - Project Engineer / Surveyor
dc5b7dcb-8f3e-5779-a8ce-bd6940678159 | date | Date Completed:
9aae277d-3059-4106-94be-ce9c7378f29e | checkpoint | 5.3 - Laying and jointing of conduits
d2ddef4f-853b-5036-9173-f09d5b205f72 | note | Frequency - Each lot
aa44c76c-2b31-54a0-96c7-a96ec8717ab3 | note | Acceptance Criteria - All conduits shall be rigidly supported and positioned by concrete former or plastic spacer blocks so that no displacement occurs during backfill.
00784a6b-90f6-5efe-9fee-79c6912d4969 | note | – Where conduit ends are not open to a pit, UPVC end caps shall be temporarily fitted to each end.
2836e5b5-ed9f-56ab-86f0-a2aa3d236b15 | note | – Number of conduits and duct route to be confirmed for conformity with design.
7982d891-b717-51e0-bf12-8a49312bf42e | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.7
19965150-2551-5f1b-9a92-7da6a778108d | note | Inspection/Test Method - Visual inspection
6425c996-03ee-544c-81f7-6f4d278ca9d9 | note | Record of conformity - This ITP signed, Building Engineering ITC
8a5fb23e-2cdd-50d5-a120-714c483664b5 | note | IP
c6b7a6e6-c2ee-58b1-85b1-f84e9ee04a3c | note | Responsibility - Project Engineer / Foreman
7aaaef6e-ccc6-51a8-a741-e17d1e9b95b6 | date | Date Completed:
db4eaadb-801f-4c93-95ed-5f94f5ec27f7 | checkpoint | 5.4 - Pre-backfill inspection
92f399bf-89fb-5731-959e-2337afdacc25 | note | Frequency - Prior to backfilling each lot
4d9c51d2-d47b-5209-bc97-2cb4faf54593 | note | Acceptance Criteria - HOLD POINT
715bed06-a062-5962-8787-4f720cd609a1 | note | ○ All trenches shall be inspected by the Contract Administrator before backfilling takes place.
d856aac9-e53f-5eaa-8c81-e5625aef521d | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.8.1
f477b7fe-e890-5197-8761-034bdfa692fb | note | Inspection/Test Method - Inspection
3cffa7d2-4747-5f80-932a-15a36bbf223f | note | Record of conformity - This ITP signed, Building Engineering ITC
058655c7-1868-5b04-ae59-d8d7bec82512 | note | HP
9563c4a6-61bf-546d-987e-a81d09aff01f | note | Responsibility - Project Engineer / Principal’s Representative
41546e4a-fd84-52cb-a7c7-354a1704b002 | date | Date Completed:
4fb50c44-6943-4843-9475-b235f57a004f | signoff | AUTHORITY HOLDPOINT
a44902a2-81d5-4e2b-a482-9ee7ce19c18c | checkpoint | 5.5 - Conduit markers & warning tape
a839ac4b-3b2e-52c2-8cdd-9357fc2b0951 | note | Frequency - Each lot
3568bef5-f477-5059-9e8d-c803cb4b839d | note | Acceptance Criteria - Pavement edge duct markers shall be installed at the edge of pavements immediately over the centreline of duct banks.
b0e8397d-bfbd-5a2a-bba3-cbb9e8a8e5e2 | note | – Warning tape shall be to AS 2648.1, and coloured orange for electrical/white for communications conduits.
2f25a123-0f35-5f6d-a993-44258c2e69b2 | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.11, cl. 3.12 AS 2648.1
8789eff7-4966-5a9c-9f70-0ea61420b2d6 | note | Inspection/Test Method - Visual inspection
d4814b27-351a-5fc7-8e75-6f757c71e018 | note | Record of conformity - This ITP signed, Building Engineering ITC
0c2aa1a8-d499-5c31-812d-325a4fee3764 | note | IP
95caea90-6fdf-5476-8e9e-f0ff29538591 | note | Responsibility - Project Engineer / Foreman
cc41c03f-97fd-5e88-a7bb-655d53943695 | date | Date Completed:
f9e480ca-b4d7-4f4a-8794-784db2eed334 | checkpoint | 5.6 - Checking of conduit lines
a25d8438-4008-539d-a81a-2e0a272ad43b | note | Frequency - Each lot
37ab6ccb-721c-52b9-a439-f6b45d0bcfea | note | Acceptance Criteria - - Following installation, the conduit shall be checked by passing a mandrel (not less than 300mm long and having a diameter of not more than 6mm less than the diameter of the conduit) through each way, followed by a brush with stiff bristles to clean the conduit of any foreign materials.
43559418-18ff-5e2c-bcf4-c2cb615be3c1 | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.9
cd73e86d-5feb-53d4-b047-bae5de9c43a5 | note | Inspection/Test Method - Visual inspection
dd054580-aece-57ca-971e-78d663ad9f4b | note | Record of conformity - This ITP signed, Building Engineering ITC
ff58b552-0d40-51bf-8e06-07af90ae3ada | note | HP*
ce2479e4-fac7-5daa-a65e-69f522ba9e2f | note | Responsibility - Project Engineer
3292ccfd-114a-506f-bc82-f085caaa7bd5 | date | Date Completed:
2d4b5f44-5098-4a1f-8433-fb1456e5f95c | checkpoint | 5.7 - Conduit draw cord
80ca212e-99a0-53eb-8634-4825927f2180 | note | Frequency - Each lot
b3b006a2-caa7-5a9b-bd9f-94ec2e14c491 | note | Acceptance Criteria - Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be nylon rope and be 6mm in diameter, blue in colour. The ends of the rope shall be coiled at the bottom of each pit or wound around a stake.
81657ff7-6287-5c5c-bf7c-2ef57f73ab7a | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.10
5ddb686e-14e7-53dc-a90c-29f22ec41b13 | note | Inspection/Test Method - Visual inspection
595ed43f-f051-5055-a40f-e71c177de1c1 | note | Record of conformity - This ITP signed, Building Engineering ITC
99934019-7ff6-54d3-b085-a86806ed335b | note | IP
a4a6f2b6-aed9-5587-845c-4edda9221723 | note | Responsibility - Project Engineer / Foreman
8167ccdc-a59f-51a9-a4f6-3ff2b01a150a | date | Date Completed:
ec8762e3-bfbe-49dc-ae3d-eb8418ebffd3 | section | 6.0 - Backfilling
7bd2c996-de43-48c2-bc13-e07297400737 | checkpoint | 6.1 - Survey AS BUILT
3666eead-6c3d-5f27-a128-6af2d3511781 | note | Frequency - Each lot
b7d8dba4-b8ad-5e6f-a263-632872289ef5 | note | Acceptance Criteria - Surveyor to pick up completed pipe/conduit runs & underground tanks before backfill
69812a03-2647-54c9-a892-cc190a73ae47 | note | Reference Documents - FH QMP
b5e66ec3-d332-5ddc-8719-d916eb4f1d8e | note | Inspection/Test Method - Verify / Inspection
f1856722-ea30-5fc7-9aeb-abb45990bed2 | note | Record of conformity - Survey Report
b3e1d7a5-cdc9-533e-be89-153ef6d8f18c | note | SCP / IP
91e49d0c-4baf-5372-b1c4-bf54ed69c6bb | note | Responsibility - Project Engineer / Surveyor
15b51c45-79fa-5d1b-9d20-d18643b9d9cb | date | Date Completed:
1e7b5f5f-5ca2-406e-adbd-7f6f46574828 | checkpoint | 6.2 - Backfilling Conduits/Pipes
74c4b981-4976-5da4-92b5-e9e4ee8c98cf | note | Frequency - Each lot
cdb4ec65-1ad1-5326-aaf4-b90047db4ef5 | note | Acceptance Criteria - Bedding
040cd87b-ae88-5112-92c3-4657c99f8661 | note | – Bedding material shall encase the pipe to 100mm compacted thickness above the pipe and be compacted simultaneously around both sides of the pipe
efcd0867-f5dc-5529-a398-de036df479c0 | note | ○ Backfill
6f14e4a1-fa51-5918-b08a-a81ea550fc5f | note | – Backfill remaining area with site won material from excavations and compact in minimum 200mm thick layers
73504798-d733-553b-ad69-dd79fcf7f5e8 | note | Reference Documents - Drawings
5e68a8c9-94a7-5ee1-8a92-685668f704bf | note | Inspection/Test Method - Verify
8d6316b7-d157-5fe0-ac59-4d035d0894f1 | note | Record of conformity - This ITP Signed, Building Engineering ITC
745e37ee-6739-5941-9a84-35861f57682e | note | IP
9aae55b7-a8a5-5f79-bb4f-07d87f25f853 | note | Responsibility - Project Engineer / Foreman
43787b90-4fe2-5d30-878a-2a1ae3e7df38 | date | Date Completed:
f4590df8-cedd-429a-9df5-ef6ac2c718ca | checkpoint | 6.3 - Testing of Trench Backfill
6b599328-9a1a-5ae0-a504-ca71d5461088 | note | Frequency - Each Lot
11d44802-531b-5e0f-8a92-16ac127528d2 | note | Acceptance Criteria - The minimum frequency of field density tests shall be in accordance with AS3798 table 8.1 and not less than 1 test per 50m of compacted backfill in each layer of pipe trench fill.
fea8b0b3-600d-5862-8be3-750dbf4bd7a4 | note | Reference Documents - Drawings AS3798 Table 8.1
fec390af-5b73-5e04-a987-53e46dc8d15c | note | Inspection/Test Method - Verify
71e5dd2d-cd88-5c42-ad27-0ff37f2af590 | note | Record of conformity - This ITP Signed Test Results
7f139c6a-2e7c-5096-aee9-f0d998587d4e | note | TP
516aa523-194d-51db-8e17-86dec4438cb8 | note | Responsibility - Project Engineer / Principal’s Representative
43875871-eb4a-5648-b38e-547c51be41c3 | date | Date Completed:
58b9ed52-0183-41c5-970a-65fadd3e7aee | checkpoint | 6.3 - Surface Reinstatement
ebae4922-f6d3-5eb0-a2c8-ac693cbe6b87 | note | Frequency - Each Lot
046b12e6-58c3-52d7-92d2-9b3389afb0aa | note | Acceptance Criteria - Pavement Areas
84969a25-d46b-5401-abef-8c9e5d9da545 | note | – Final backfilling in existing pavement areas shall to 100% compaction
6940e089-6459-56d9-a2e7-8de27d6b3ce8 | note | – Mechanically compacted in max 150mm layers
7b62a47c-b401-5d88-b454-439bd5a9a881 | note | – Basecourse depth shall be 400mm or existing pavement depth, whichever is greater
89553e26-6299-5913-9ed6-672fb0645399 | note | ○ Grassed Areas
c9c00cec-c189-5416-a926-a28dfda4c69f | note | – The final 100mm of backfilling shall be clean topsoil
80b7788b-6328-5af8-b0e2-cc8ec641ceed | note | Reference Documents - ZULU-BECA-001-SPC-000All 05 C1772.6 .1 AS 2566
5654ca50-d931-5be9-828d-8a79a1973864 | note | Inspection/Test Method - Visual inspection
27c38f08-3efe-50e0-a17c-bf8466ed2039 | note | Record of conformity - This ITP Signed, Building Engineering ITC
12bc3994-0178-5a0a-b585-6cc649ad837d | note | HP*
d9bc858c-589f-59e3-a354-1e3003599a66 | note | Responsibility - Project Engineer / Foreman
9168f713-c112-56d0-98cc-f849e21df182 | date | Date Completed:
b63fb0ae-aedf-4f41-9cf6-54d0250ef2d8 | section | 7.0 - Construction – Precast Pits, Headwalls, & Underground Tanks
e9a16b50-db1d-4351-9e80-d48b07a61ba4 | checkpoint | 7.1 - Placement of Septic & SPEL Tanks
b9f9c4cb-e6b2-537c-90a0-b2032c2b6a4c | note | Frequency - Each lot
1909c6dd-a2c1-5eb4-a564-6c39d6236c7a | note | Acceptance Criteria - Ensure placement of tanks is as per manufacturer specification and as per design levels
6abd49df-145c-521d-9145-40247c7ccfbf | note | Reference Documents - Drawings, Manufacturer’ s Specification
601356bf-7049-5c4e-81d4-6029633a14c8 | note | Inspection/Test Method - Visual inspection
57632bc3-0cb4-5752-a02b-d7bc95c9fe7a | note | Record of conformity - This ITP signed
b5870f44-a6a5-5ec1-96f0-0f21c844ae2f | note | IP
686ba71f-ff41-5c89-836b-e064096b534c | note | Responsibility - Project Engineer / Surveyor
6397d9b3-2a82-506f-8ab1-12704413e8ef | date | Date Completed:
1b835e34-786d-4fae-8c1b-ff4a21434c26 | checkpoint | 7.2 - Placement of Pits and Headwalls
3c9770b5-9846-518b-a0cf-cfc95422ed12 | note | Frequency - Each lot
aea96644-782c-5459-82e0-cb4a5c5daed6 | note | Acceptance Criteria - Pits placed and levelled as per survey set out
558f354d-a694-5ddf-b616-63d91894172b | note | Reference Documents - Drawings
0f974dbb-10aa-54d1-ab77-e319bb8ba432 | note | Inspection/Test Method - Verify
7d0dd19a-8163-5731-a354-4a6ded4ecbb2 | note | Record of conformity - This ITP signed.
a901e1c9-d700-5aa2-ac6a-fde143f76ca2 | note | HP*
4852fa40-84ee-52db-b18b-493c0e801126 | note | Responsibility - Project Engineer / Surveyor
9fdced34-b459-50fb-a47e-e5333a6b79b4 | date | Date Completed:
4b7199b5-ec6c-4661-8adf-88775109d70e | checkpoint | 7.3 - Bedding & Backfill of pit surrounds
491a2254-d951-5a20-a4cb-43111c804f9e | note | Frequency - Each lot
70cd62b5-6ed4-5321-a5ff-d771aabeb42a | note | Acceptance Criteria - WITNESS POINT
a13d0159-b532-5a22-8176-674402d197ef | note | ○ Each pit/headwall shall be bedded and be backfilled with stabilised sand for grassed areas.
51cd9c6d-49d5-5f40-89e7-676129c08bab | note | ○ Principals Representative shall be notified to inspect installed pits with all connections prior to backfilling
dd56d547-8b6f-5c49-821c-433c75077ce0 | note | Reference Documents - ZULU-BECA-001-SPC-00004 Drawing 00201
b3cd6eb6-cbad-59b1-bf9f-7aa9dff0dbf6 | note | Inspection/Test Method - Verify
a10d794e-d1d9-5788-83d1-75b1e8bbfb2d | note | Record of conformity - This ITP signed
f9e711e0-aa38-5042-94eb-1238979b606d | note | WP
f823c198-3a30-5be4-93e1-348005daf2b1 | note | Responsibility - Project Engineer / Principal’s Representative
2076cd90-a3f8-532f-8e2a-486cc5d271da | date | Date Completed:
0bf232dc-2b46-4f6f-b371-a25fd0e73b5e | checkpoint | 7.4 - Pit Close out
03d8b536-4452-55f7-9895-31b240c47c6c | note | Frequency - Each lot
0bd307ba-7dbb-5d42-a0d0-0a60e826435f | note | Acceptance Criteria - Pits shall be labelled and directional markers placed. Lids to be secured and area cleaned/demolished
daf720c2-73e5-56fb-bf47-05c64d64ad84 | note | Reference Documents - ZULU-BECA-001-SPC-00004
3af00308-ba8f-5ae8-b192-0b1443880898 | note | Inspection/Test Method - Verify
a244b536-edd4-581e-9d1e-024481d0f797 | note | Record of conformity - This ITP signed
bd18a973-f699-57ea-b421-6e51ce22805a | note | IP
6fd38751-2b0c-5a99-bdba-ddb861a0c597 | note | Responsibility - Project Engineer / Foreman
bfc9c50e-bf0a-5e92-b128-ca44187e5c4e | date | Date Completed:
d08703af-c3ed-4d80-bb62-7ab3063625b1 | checkpoint | Final Inspection
e8d02f10-c3df-51e3-a112-260136929242 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
eef03edb-87bc-5217-9f85-849473fca17e | textbox | Print Name:
490b2658-d57f-507e-9bfd-92c569e044bb | textbox | Position:
9037209b-09e3-5d81-aeba-402cc1a94e93 | date | Work Completed On:
e9bb53cb-110d-5264-88f7-ad6532d986d8 | date | Date:
ba60b548-85d5-4034-8570-b242c8a5e8de | checklist | FH-ZU2-QU-ITP031 - ALER 3 Onsite Concrete - Rev 2 | itp | ITP031 - ALER 3 Onsite Concrete
6948bf25-b06f-4052-94da-8405ce0aed89 | section | 1.0 - Preliminaries
75d43096-9e2c-4e24-a8a7-56c2d793a2b3 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
a422b6e8-fa7b-53c7-adad-ae05e4b7d4fc | note | Frequency - Prior to Start
11908449-132e-51d8-a534-72d3f35d42f2 | note | Acceptance Criteria - Current revision drawing is being used (including the subcontractors copy). Current revision to be obtained via Aconex or ACC
057365b5-e355-5eab-8423-cc53456fc87d | note | Reference Documents - Drawings and drawing registers
b0278b08-c129-53cb-b7eb-47b0b65ec362 | note | Inspection/Test Method - Verify
859e098e-a515-59d8-b125-20daf2fe19d8 | note | Record of conformity - Up to date drawing sets and this ITP signed
cc783ca9-7934-5b7f-a01a-23e338769c5e | note | HP*
f8e2a17a-8073-5923-a132-f3c119f66970 | note | Responsibility - FH Engineer
94f062fb-aa11-5bbe-bd06-43c7cf348653 | date | Date Completed:
3a87a17e-5c33-42e9-bda8-e325dda7feb2 | checkpoint | 1.2 - Implementation of all measures and controls
0133ae82-59fb-5ad7-b145-7ea2c6d66889 | note | Frequency - Prior to Start
564c5a30-df25-5182-96c2-71f4e4aadbcb | note | Acceptance Criteria - All necessary measures and controls being implemented, that is CEMP, TMP, SWMS, & WP
7d0c5b6b-b3b2-549c-94d3-5798ed11d19c | note | Reference Documents - CEMP, TMP, SWMS, & WP
9fcfe3d8-ba91-5027-b7ce-71d3c9b82083 | note | Inspection/Test Method - Verify
6c4c8c3b-90ab-5229-9502-38c2d13a4741 | note | Record of conformity - Site and office Inspection
94b6073c-f0b2-5d19-a73e-0f40ceae307e | note | HP*
28ae5c66-2f44-5d2b-8cf3-f7d3ad8fc10c | note | Responsibility - FH Engineer
e1d19827-23c1-5301-a9ee-55668524d2f9 | date | Date Completed:
2b67bf4d-20e5-493a-83cd-f7178548244f | checkpoint | 1.3 - Excavation Permit
140100c0-3402-5899-9ae5-aa568f6c63d9 | note | Frequency - Prior to Start
29e5de58-dbb9-570a-956e-6defbe48d8b8 | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
6c648f12-7ef1-5140-a057-3d42f7525121 | note | Reference Documents - APAM Excavation Permit
6d14e30f-e367-5277-87ca-60ba5d6c9914 | note | Inspection/Test Method - Verify
1ffe5cce-a972-5690-9192-c9aeba6445bd | note | Record of conformity - Proof of & permit ITP sign
3f384132-067a-539d-94ce-7fd2388f61b6 | note | HP*
1e97d16f-bc1b-5d36-a894-831b4d81a34f | note | Responsibility - FH Engineer
67bd6c66-cf34-5d8c-b745-d4ba9e391818 | date | Date Completed:
06924904-462e-4a0b-8cc4-434a0618f133 | section | 2.0 - Supply of Materials
a6f7e7a6-7563-4c89-b8fb-15d9bcb30701 | checkpoint | 2.1 - Reinforcement
5f98a600-47fa-5fdd-8095-a79354d22af8 | note | Frequency - Pre-commencement
f2b273a2-65ad-5617-9cf3-6be48649e62d | note | Acceptance Criteria - HOLD POINT
1fb478cd-9463-56b3-aaaf-cd91e0fec29d | note | ○ Test Certificates demonstrating compliance of the reinforcement with the requirements of AS 3600
aadbe98a-50a4-5928-9ba0-352ff7952ddd | note | Reference Documents - Drawings and Specification
42fc78df-7fa1-5307-a69d-69de88604dcc | note | Inspection/Test Method - Verify
8857cf69-a904-5760-9357-7d97829c9e46 | note | Record of conformity - Aconex Reference
8f16e9e8-b6bc-5c65-b1f7-c7f3ee07f119 | note | HP
55394a10-aabd-5307-82ff-1480ceb34c41 | note | Responsibility - FH Engineer / Principals Representative
3e87fa72-d77c-5f42-afd6-1936c4f362c2 | date | Date Completed:
83b0674a-c70f-4c0d-9e9a-520ea2a080cf | signoff | AUTHORITY HOLDPOINT
f508ded0-a2a5-4109-9bb6-f355b48b52b7 | checkpoint | 2.2 - Concrete Mix Designs
2a6ab837-9588-5d53-a2e8-2cc99f04c046 | note | Frequency - Each Lot
77f14c5c-034e-5b01-b534-558efc499b34 | note | Acceptance Criteria - HOLD POINT
266a9d5c-3603-53a7-b8b6-2c46533f0035 | note | ○ Mix design to be submitted to contract administrator for review and acceptance.
3ea672e0-a779-5a9a-be85-11657934528b | note | Reference Documents - Drawings ZULU-BECA-014-DWG-00201, ZULU-BECA-030-DWG-20001
df798642-f8f7-583c-9d2f-b813f6e224e9 | note | Inspection/Test Method - Verify
952e5765-cf79-5c55-810a-c6cce3dac122 | note | Record of conformity - Aconex Reference
733552a0-482e-5452-ac19-0d40c734ff15 | note | HP
e33b3875-1b6a-5a3d-a1fd-2a3b077d0e82 | note | Responsibility - FH Engineer / Principals Representative
8ad39eb2-eaca-545b-b6b2-b9232323cac7 | date | Date Completed:
4fa3493f-7f6c-4635-aad2-d2b4fe40048b | signoff | AUTHORITY HOLDPOINT
d7cb4790-a882-48a2-b927-269fef81be3c | checkpoint | 2.3 - Review of Curing Regime
9c445b28-9d61-5e63-b152-423034ba21af | note | Frequency - Each Lot
6136d551-42f3-5af5-807a-a1c665f04897 | note | Acceptance Criteria - HOLD POINT
dd1718e1-0498-5737-928d-b0466da45d86 | note | ○ Concrete curing regime to be reviewed and approved by the contract administrator prior to use
37e01a2a-f88d-501d-8e70-f1889813ad51 | note | Reference Documents - ZULU-BECA-030-DWG-20001
61012e22-37fe-590d-9307-95a0c9809f11 | note | Inspection/Test Method - Verify
d4a7865a-2846-54fd-8900-14ed1308a9f5 | note | Record of conformity - Aconex Reference
6da6a845-1865-5dbd-9f53-9a3aab9c3ed5 | note | HP
01181b4b-65cd-5fea-9512-ac7295ba6342 | note | Responsibility - FH Engineer / Principals Representative
19c3d60e-1691-55bf-810f-1e0b560abefd | date | Date Completed:
46ffdeb7-cd0a-47cf-a336-33305a4ff1de | signoff | AUTHORITY HOLDPOINT
955f43dd-4c96-4c44-9ac3-5b19608ea085 | section | 3.0 - Construction\Erection of Formwork
519735f3-6ee8-4404-81f2-8dc9f7d72ce0 | checkpoint | 3.1 - Setout
01f5fb81-4741-5bbc-9df1-12cce73459c5 | note | Frequency - Each Lot
cc5ce666-b5a5-5f7a-8643-d4a91e4e80a9 | note | Acceptance Criteria - Setout completed and conformance with Beca IFC Drawings.
e2e72094-7958-5ec2-9d13-e5677219c3b8 | note | Reference Documents - Drawings
aa483015-3742-5257-a8aa-3dd3f59b12e7 | note | Inspection/Test Method - Verify
be01ddb3-463e-5a14-b188-62c6328246e6 | note | Record of conformity - Survey Report
4da6edbe-2c34-56b9-9917-c3cad88862eb | note | SCP
fd64baef-c545-556a-98a3-afe19ce5caed | note | Responsibility - FH Engineer Surveyor
5fa2bdb4-3c41-5d94-bd75-71320fb593fa | date | Date Completed:
c8a91548-298a-412f-80d2-018b619e28df | checkpoint | 3.2 - Excavate
453ce0c1-79d1-5cd6-9879-12c4dcfa3d42 | note | Frequency - Each Lot
e3993aea-083a-522e-a284-f8026206f0f6 | note | Acceptance Criteria - WITNESS POINT
5896c6c9-2757-50c9-8631-e4345694c095 | note | ○ Excavation depth shall be as per specified or as shown on Drawings to accommodate structures.
9861e9fe-a6f1-529a-af14-400e6a3145db | note | ○ Principals representative to be notified for at the completion of excavations for inspection prior to any blinding being poured.
5aaf2454-393f-5eb9-92ce-2ed502317475 | note | Reference Documents - Specifications as per Drawings
9a5ccca7-bd90-51fb-ab79-9d8297f30470 | note | Inspection/Test Method - Verify
a5377817-24cc-5084-a8d2-2ec81359884a | note | Record of conformity - This ITP signed
8f9b33f9-6d5d-5576-b341-c5ec14305f80 | note | WP
56b31d25-a46a-5d29-9f09-89bfc91e8605 | note | Responsibility - FH Engineer
8625207a-1b94-5f68-854f-fb23881d55d9 | date | Date Completed:
467dc3bf-971b-4fef-aeff-c20c602e235c | checkpoint | 3.3 - Confirm Ground
6762a9d4-198b-5976-a1d0-e52e0de89aa8 | note | Frequency - Each lot
d1c438cb-811f-589b-a9c5-79377baf9f4b | note | Acceptance Criteria - HOLD POINT
ac10d939-7be5-5f2e-bc4a-932178bcbee3 | note | ○ Completion of excavation and inspection of subgrade materials.
ab24bdfa-fa68-51c4-bf99-d3cbb972b143 | note | ○ No soft spots, unsuitable material. Confirm ground bearing pressure
26336ac5-19d8-5292-bfb2-4269bec9772f | note | ○ Density Testing to be carried put at a minimum of 1 Test for each 100m2 area per layer of compacted excavations for footings & concrete works
889d983d-7a8a-52d6-bf84-f2560cf52040 | note | Reference Documents - Drawing 00201 Note E40
44cc7732-8541-511e-a131-8f072689020e | note | Inspection/Test Method - Verify
5f098c33-7283-5625-9f85-d2da2d285003 | note | Record of conformity - DCP Test Results
6a357823-b0c5-5652-b59a-d5519526df6a | note | HP
9b021284-ba37-5686-b9c9-38010ff24ee9 | note | Responsibility - FH Engineer
98eb8b72-8e64-574a-87ba-f1d2b9b8e803 | date | Date Completed:
5e7775be-3f5a-4837-a536-c4f9b894ec99 | signoff | AUTHORITY HOLDPOINT
a242da1a-7df7-43ef-92d8-594b861b1c3f | checkpoint | 3.4 - Concrete Sub-Base
b5ffbcab-c705-587d-a7ae-e33588490ee4 | note | Frequency - Each Lot
da3ed9d5-99bc-5f91-9a70-5094d84e743b | note | Acceptance Criteria - Blinding layer is installed as per drawings
3e92f572-9420-5b47-ab8b-17c5775c8abb | note | Reference Documents - Drawings
15e8abea-b764-5684-862f-f55c55fb064c | note | Inspection/Test Method - Visual Inspec tion
1b29d700-046f-5a45-944c-f1a9c853f6b9 | note | Record of conformity - This ITP Signed
9c0d44c0-fa72-586b-b8bc-672a9e2d8d68 | note | HP*
2f5fb405-7016-54b4-8ee9-378b3b9e07d6 | note | Responsibility - Site Engineer / Foreman
e7d21575-fc40-563a-80e0-1b0e27dd5d76 | date | Date Completed:
d3ed2862-a19a-4a29-afdb-5012fa96e558 | checkpoint | 3.5 - Formwork
b5b1508b-02b3-5207-b90e-494fd692ef83 | note | Frequency - Each Lot
10c586d8-3e5d-5bfa-a7a9-6072e53ca912 | note | Acceptance Criteria - Formwork / Reverse Shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
a1c6ea17-8f8e-545f-998d-63f09d04f3ba | note | Reference Documents - Specifications as per Drawings
9e53e121-4cc2-52a2-b665-54fa714317fe | note | Inspection/Test Method - Verify
2082e783-8ca8-5591-8b28-8cd448f836d9 | note | Record of conformity - This ITP Signed
51d1ad77-778f-5d6f-bdae-2e5414ad89e1 | note | IP
92097536-815c-5457-9f37-e436d0128eb1 | note | Responsibility - FH Engineer Surveyor
163ed35d-cf70-57e7-bc98-958781229ab4 | date | Date Completed:
61a8d8c2-c50b-4eed-9a8b-7311af89cce9 | checkpoint | 3.6 - Penetrations/Cast in items
bce3617e-f178-553f-b884-6b64076feee8 | note | Frequency - Each Lot
79a6edf2-d063-5269-a461-8b4a0ffec4d5 | note | Acceptance Criteria - Penetrations/cast in items are present in the formwork.
5be6fc80-0b46-51f9-850c-ce09b43bdd2b | note | Reference Documents - Drawings
0a0cfeee-c5b8-57aa-8b41-a550586a2df1 | note | Inspection/Test Method - Verify
f4babcd9-79fa-557f-ae6d-6621fb6c04c1 | note | Record of conformity - This ITP Signed
2f93e3ed-7721-595f-8c87-f20fd564f91b | note | IP
354e6475-b53f-5e09-bcaa-a4f7a3029aa3 | note | Responsibility - FH Engineer Surveyor
f1236b2d-6ffd-5ce4-894e-5db60ac619ef | date | Date Completed:
bc9de108-9493-462d-b5c4-31d88c153991 | section | 4.0 - Reinforcement
66611056-ece5-4207-bfe6-1b99e75ebaed | checkpoint | 4.1 - Reinforcement installation
86a171ac-4663-540c-988b-0b8bbe0b2b36 | note | Frequency - Prior to concrete pour
a450dc0f-adeb-5400-a9d9-e0bcb1d0c0f2 | note | Acceptance Criteria - Pre-Pour Checklist Completed:
ea3072b0-6481-56c9-accc-371754df2fdf | note | ○ Position and spacing check and recorded.
137f500f-ddc7-5169-8a73-1d56684d1e21 | note | ○ Cover checked and recorded.
f42ea4dc-c7fe-5d1b-b6f5-adeba925b579 | note | ○ Reinforcing supports checked and recorded.
196fac07-17a0-5de1-8510-db4e89079714 | note | ○ Laps at required length.
7f888212-0fe0-55f0-a6da-42e7ad44f582 | note | ○ Penetrations/cast in items
9f377d94-37ed-5a7b-9b13-1ffdc4679716 | note | Reference Documents - Specifications and drawings
97b4dcee-84ae-53e9-86bb-84755231bd91 | note | Inspection/Test Method - Verify
0fe01ab0-5276-5bfb-90d4-158c2517e3eb | note | Record of conformity - Pre-pour inspection List CLA31A
e1aed6a5-3b86-54d9-a15a-b785272b1911 | note | IP
50200178-28da-59c5-8544-906dbf19edf6 | note | HP*
5639dc52-28be-570d-be08-21e6057678a1 | note | Responsibility - FH Engineer
113a05dd-c6d0-5bf1-8bc5-0efb3c8268ee | date | Date Completed:
caa8e37c-1770-4eab-8e83-995f500b2424 | section | 5.0 - Pre-pour Planning and Inspections and Placement (1st Pour)
c98c3db5-bb23-454c-95b1-8b7f8ac7c99b | checkpoint | 5.1 - Pre-pour Inspection
57456c64-23fa-5e86-a51d-b0b529c592c9 | note | Frequency - Prior to concrete pour
7036c3bb-5b9b-5985-a460-3b4958e01c3f | note | Acceptance Criteria - HOLD POINT
1a166c8d-4243-51cb-9475-a0abbc08550e | note | ○ Superintendent or Engineer to conduct pre-pour inspection prior to concrete pour
cf7b013c-df25-5497-a7af-c78b81a822fd | note | ○ Principals representative to inspect formwork and steel fixing
f6086b9c-f43f-53fd-9826-57cb19232b5b | note | ○ Provide the Airport Building Controller with 72 hr Notification for mandatory inspection prior to pouring footings.
d4de2a70-5614-5c4d-86f6-f9bf2e7a22a8 | note | Reference Documents - Specifications and Drawings ALER 3 Building Permit
2855f3e4-ecad-54fc-8a63-974d2c98a4b3 | note | Inspection/Test Method - Verify
b06ad95d-0fa4-5772-a9c2-861de7c7a0e9 | note | Record of conformity - Pre-pour inspection List CLA31A
41cea30d-5120-5359-bc86-4d41b5bece41 | note | HP
fac8f5ef-b142-5ac4-9c5f-ce1959a2036f | note | Responsibility - FH Engineer / Principals Representative
637ef9d2-df70-57bd-a8ff-377b8b44f3e6 | date | Date Completed:
5527f884-b03e-4f12-af76-113ce282b6a3 | signoff | AUTHORITY HOLDPOINT
31ffa32c-09cc-4b50-be27-3f491b6f8ecf | checkpoint | 5.2 - Pour in-situ
5bd18c46-1f7d-5aa5-803f-4c199eb4dec9 | note | Frequency - Each Lot
173817f4-bcce-5c9b-9d2a-764e7e112b57 | note | Acceptance Criteria - Concrete shall be placed within 90mins from batching.
cfa67e2b-b96e-588c-987f-8880d1a2342e | note | ○ All concrete supplied for concrete structures shall be subject to project control testing in accordance with AS 1379.
46ab178f-2d50-5979-9f51-d8259d03a303 | note | Reference Documents - Specifications and drawings
7cfe2f1d-4b01-5d01-8769-88219eb95fce | note | Inspection/Test Method - Verify
ad3e08c6-98c2-5456-b88b-e6b7ee6b3c4f | note | Record of conformity - This ITP signed
7b9c968c-d705-5b18-bcdb-7c9b1b499409 | note | IP
60597fb6-38a6-5a79-8196-50a6a6ee9f7f | note | Responsibility - FH Engineer
3c05f2a1-d4f1-589e-9b30-6e13064c088a | date | Date Completed:
f3b89482-5a2c-46a9-a2d5-f5c4dd14ba11 | checkpoint | 5.3 - Concrete Testing – Compressive Tests
8edd9489-9459-5f50-9a15-2bcc84b19535 | note | Frequency - Each Lot
a635230d-e818-5b15-befb-885225acde11 | note | Acceptance Criteria - Composite samples to be taken in accordance with AS 1012.1.
141e32ab-2941-5f9c-b728-0336a82cf477 | note | ○ 2 – 7 Day cylinder and 2 – 28 day cylinders to be taken.
2055ea40-3238-5db9-811a-73ed7b3b149a | note | ○ Frequency of testing shall be one sample taken either every 50m3 or once per day, whichever yields a higher frequency.
930d644e-8ff0-55d7-8015-824ed217adae | note | Reference Documents - Drawing 00201 Note 51.AS 1012.1, AS 1012.9
dc93f8c2-88a6-5e4a-8615-348a81e80635 | note | Inspection/Test Method - Verify
fd5d3a6c-e7f4-5d17-8826-a3402a245be9 | note | Record of conformity - Concrete Testers Sheet/Results
52c8a096-ff9b-5d1c-995f-fdc4ef787bf6 | note | TP
e9df4350-03fb-5a45-b945-3bbfc4f99074 | note | Responsibility - FH Engineer
baf27e96-7496-5ead-acaa-8453b5ad98fa | date | Date Completed:
e70d1fb6-1fb6-457e-b24d-a6877e22bbed | checkpoint | 5.4 - Concrete Slump
ce0eff17-90ce-504c-92bb-f6d7fecd2bf5 | note | Frequency - Each Truck
5e7176b4-67e5-5bfa-b1cf-efa10e2c040f | note | Acceptance Criteria - Slump test is required for each load per day
bb658036-5aba-561f-9427-9c811b8a96a8 | note | Reference Documents - Drawing 00201 Note 51.
01c64560-3cbe-56e8-b8fd-39dac2cca5b0 | note | Inspection/Test Method - Verify
3068f993-d981-5fae-8138-2c5881eb6e86 | note | Record of conformity - Concrete Testers Sheet/Results
844ac218-d02f-5fe7-b774-c0d5948561bd | note | TP
3291bc48-c400-5443-867e-0a97044aacf9 | note | Responsibility - FH Engineer
f44fa094-4be7-5315-98fa-191cb9b13034 | date | Date Completed:
ae550f1a-ae95-4a1a-95ef-83bd4657bf3c | checkpoint | 5.5 - Finishing & Curing
7e2a0692-369f-5b02-bb39-33f8e5905954 | note | Frequency - Each Lot
dd630cb7-0b97-5e49-896f-b83a50547235 | note | Acceptance Criteria - Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces.
4b097956-412d-53e8-84c9-9cfc3ea83fa2 | note | ○ Concrete shall be moist cured or coated by an approved curing compound for a period not less than seven days unless approved by the Superintendent.
4591fa42-445f-5a2b-ba52-58327d94b33b | note | Reference Documents - Specifications and drawings
5b7bac6c-dcf5-506e-9e84-51c7c9d1f445 | note | Inspection/Test Method - Verify
868dc4d7-5bcb-5550-b5c1-38d3af590402 | note | Record of conformity - This Signed ITP
30c9ac4a-bf1b-57ef-a0f5-0653d501e761 | note | IP
7f35d1d2-d97d-5e68-9a3b-bdbef3d99915 | note | Responsibility - FH Engineer
177b704b-4cc6-5a92-8709-aaa1b75428a0 | date | Date Completed:
756a7492-02da-43b3-92ba-dc3ab35a3233 | section | 6.0 - Post Pour Details and Inspections
10298557-4bab-4c42-b508-cc7eb50dd893 | checkpoint | 6.1 - Removal of Formwork
6714b99d-9799-501a-9102-c09aa44fec36 | note | Frequency - Each Lot
c7a6f847-2002-5ad4-8337-f7f260b59be2 | note | Acceptance Criteria - Forms shall remain and be maintained firmly in place until the concrete has attained the necessary strength to support its own weight.
09097216-7ded-5ed6-9d39-e427bcdd61a6 | note | Inspection/Test Method - Verify
d5f5e0f9-8aea-5d9d-aa04-e56ac5021e8c | note | Record of conformity - This ITP signed
f739ca53-8f28-56df-9b0e-df2c247bd68a | note | IP
54c03863-469f-5300-8d3b-4378614d0378 | note | Responsibility - FH Engineer
2d8f7d73-2a63-59aa-8011-883ae31d20c3 | date | Date Completed:
c647dd95-3fbf-4d18-b0bc-7427a8412eb6 | checkpoint | 6.2 - Review of Test Results
47061202-ec0b-5c47-b30e-bec5de9150a0 | note | Frequency - Each Lot
ed1ad7de-8cb2-52c2-9c74-1c716769a022 | note | Acceptance Criteria - Review of 7 day and 28 day test certificates
cc9eb4b1-5704-54a1-ac81-d74e6f91e142 | note | Reference Documents - Drawing 00201 Note 52.
0c836263-d166-52b7-b8c5-79e6a12f37ee | note | Inspection/Test Method - Verify
fbcf4434-bcda-5b89-9419-8556368c1605 | note | Record of conformity - Aconex Reference
354175f3-4b19-5127-8714-db7a4b338f80 | note | HP
3f94a842-320c-5c75-9649-6864bf246745 | note | Responsibility - FH Engineer / Principals Representative
b6b70276-5626-56f8-bb3a-7eb061d535f8 | date | Date Completed:
ece0c74c-d93f-40bd-92d8-ae2d17338d45 | signoff | AUTHORITY HOLDPOINT
5f3d2bae-31fc-48ee-8125-7fec61df0c05 | checkpoint | Final Inspection
6c893bd1-a3e0-5bb6-9a6e-42ed8687d650 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
aebfff51-1ba7-5b06-8454-7b1cf36a7401 | textbox | Print Name:
3d4c5395-6440-5f7b-ae4e-fc88244784ba | textbox | Position:
892b9f69-c137-5145-accf-95e011f624f6 | date | Work Completed On:
aed138d7-3f6d-5329-9c0c-5e6276de1a83 | date | Date:
cf939dde-910e-4a0b-ac53-327fe503dc0f | checklist | FH-ZU2-QU-ITP032 - ALER 3 Structure - Rev 2 | itp | ITP032 - ALER 3 Structure
da604e6a-18b4-4d23-94f9-4b8dcf8224cd | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
32d8866e-7749-4e1d-89d0-66e34655ad9e | checkpoint | 1.1 - Check for correct documentation
7c355e4a-89dc-520e-a43f-08001b6b2173 | note | Frequency - Prior to commencing activity
226226d9-c476-5a9f-a54d-036cf3879dbd | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
f1194ebb-9b3a-5e1f-9aa1-a2ce831b5d9c | note | — using the correct and complete set of drawings.
241c0746-9044-515e-b217-ad4284f39b98 | note | — all drawings are the latest revision.
cc5283df-8c06-5f0c-be3d-173327422ad1 | note | Reference Documents - Drawings / Aconex Register
a0b6ac93-dc6a-5e5c-97fd-14ab51ae7991 | note | Inspection/Test Method - Verify
a523b193-600f-5605-94e0-8f504a60351e | note | Record of conformity - Drawings and drawing registers
9f41f4e8-e111-537f-82f9-a7b99383577f | note | HP*
a6d9c328-332e-5ef2-b13c-0c05d922058a | note | Responsibility - Project Engineer
1c26cc8e-222b-53b6-bb78-e4aa7e606ff7 | date | Date Completed:
30b0b7bc-eaef-49b4-ba30-673093e0b43d | checkpoint | 1.2 - Implementation of all measures and controls
cd7cdcb8-b153-5351-a751-afcc6a34c032 | note | Frequency - Prior to commencing activity
04bbc392-7146-5c4b-a166-0700d45458ef | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
5475cb4a-8a99-548b-b38e-301bb2b889a6 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
72d5622e-5e21-55e8-bcc0-c9c5ad8e1187 | note | Inspection/Test Method - Visual inspection
2b72bec2-e6f1-54c1-b667-2cad7515e9f1 | note | Record of conformity - This ITP signed
852c6373-e797-5656-817d-794beaa8a3b6 | note | HP*
d42fddbf-02ee-5442-8d04-509edeac8a9b | note | Responsibility - Project Engineer
10963abb-96e7-5793-8c8d-32bc8b6fe11b | date | Date Completed:
ce64c3be-05f6-4a78-b60d-e71ece2dea75 | checkpoint | 1.3 - Survey Checks
79b8941a-8ecb-5a56-bb43-cdb8663f8579 | note | Frequency - Prior to commencing activity
063912c3-420d-511d-be48-fa3ac6b92399 | note | Acceptance Criteria - Check survey to be completed of all footing positions prior to placing any of the panels.
43b8397e-2021-529c-b8d8-d2757244feb6 | note | Reference Documents - Drawings
6739b750-4d6b-524c-8132-217bdbc275e4 | note | Inspection/Test Method - Verify
60e4a22f-1036-5e9f-aa9f-27b197708b7b | note | Record of conformity - This ITP signed Survey Report
e14dd37c-08f9-5791-8f8c-1697028ba024 | note | HP*
29483447-99ee-5a46-9333-19c6a18c9ca7 | note | Responsibility - Project Engineer / Surveyor
1d51861c-9982-592c-8933-f7cb12c49447 | date | Date Completed:
24800a53-e827-4828-be45-97bb77ca46d9 | checkpoint | 1.4 - Submission & approval of precast shop drawings
1099d67e-75cc-56a4-897c-474142b1cfa5 | note | Frequency - Prior to commencing activity
51b16bf3-3dcf-5346-9999-a3523156c5d5 | note | Acceptance Criteria - HOLD POINT
e4b657ec-d212-5f90-8703-2bdba2ce5cca | note | ○ Submit precast wall panel shop drawings to the principal’s representative for approval prior to fabrication commencement.
488e07f0-832f-564d-b12b-c9d567a8aac3 | note | Reference Documents - ZULU-BECA-001-SPC-00005 0321 cl 1.16, Drawing 20003 note PC7
598a21b7-987d-53d4-a0cd-b4224855bbdd | note | Inspection/Test Method - Verify
435496ad-a461-5f41-b73c-7de163e1fcc2 | note | Record of conformity - Aconex Reference
c4966e54-a425-5ff7-b042-9bbcae45b2c8 | note | HP
3831aeb3-5339-5897-be20-7731ea9d7418 | note | Responsibility - Project Engineer / Principals Representative
86f84417-e754-5004-b360-78ff8e22e794 | date | Date Completed:
dc48684c-ccab-4b6f-ab85-f1280fc321a7 | signoff | AUTHORITY HOLDPOINT
f96dbc9e-cd2f-4e0e-a2a6-02fceb22e6db | checkpoint | 1.5 - Submission & approval of structural steel shop drawings
f6fb871f-a953-51d0-8a87-1186f539afbb | note | Frequency - Prior to commencing activity
257adc40-a845-598b-adf6-e9daf6d75f7e | note | Acceptance Criteria - HOLD POINT
e41b78b6-7e38-5fac-860b-6a3b6e964a94 | note | ○ Submit structural steel shop drawings to the principal’s representative for approval prior to fabrication commencement.
bd93fe76-2ed9-5f72-bba8-e646850bcf38 | note | Reference Documents - Drawings 20002, 20020, 20113, 20221
a705612b-c7b4-57ff-882b-b2c170c71fb1 | note | Inspection/Test Method - Verify
9b3dac7c-f305-5265-8a82-6c258c32216d | note | Record of conformity - Aconex Reference
b5f1f732-1266-5ae6-9817-18760aedb93c | note | HP
52f45dab-dd4f-550a-9e83-23f0d4934087 | note | Responsibility - Project Engineer / Principals Representative
e2099029-3497-57ef-b6b1-adbadebf5095 | date | Date Completed:
530d7935-2978-4a39-a96e-4217c508b8d0 | signoff | AUTHORITY HOLDPOINT
788ff20b-1e3b-46cf-98a3-e14152c66de0 | checkpoint | 1.6 - Material Submissions
35b585c9-bf8d-53c0-81e8-fda2d5c98725 | note | Frequency - Prior to commencing activity
086ecbb1-0fab-5714-92e5-acc13e2bbc80 | note | Acceptance Criteria - HOLD POINT
867ec0eb-ab90-5604-8fe2-ea16ae548ed2 | note | ○ Items to include but not limited to:
906cda9a-94f5-553b-8aff-b109eed0af37 | note | — Concrete Mix Design
aa6c69b4-5499-5392-ba82-22fa0d491e75 | note | — Element Casting Checklist
e0e4d6dc-549b-5330-82e7-f87fc7cb8df3 | note | — Steel Reinforcement
259b6b05-cebd-5cb8-a097-4187b0ec5a9c | note | — Precast Sample
a2bcde34-d23d-532d-8430-18690f2ca7fa | note | — Bolts
a776a9a4-6830-5301-9650-2d07513a0bc2 | note | — Ferrules
8d19cdcb-b09f-5cda-b251-c50d846576ed | note | — Grout
322bd507-9486-56c4-bccf-7337d24e2405 | note | — Incompressible filler
e22fb135-6e1d-5117-a2a3-c619b6905108 | note | Reference Documents - ZULU-BECA-001-SPC-00005 cl 1.16, Structural Drawing Set 030-20 AS/NZS 1252.2
e34f2487-830b-5aae-b26d-e67cb38ba137 | note | Inspection/Test Method - Verify
d5528ca4-e2bd-564f-a0e1-f28f6cc3568f | note | Record of conformity - Aconex Reference
e30195f5-3035-5c66-9350-c313162bb8b7 | note | HP
1ec700a3-d59c-5616-986b-e799e878334e | note | Responsibility - Project Engineer / Principals Representative
9ca5c81f-954b-58b8-bf66-922d521a7f14 | date | Date Completed:
f9ad00e1-14c8-4b08-b595-39fd98488f6e | signoff | AUTHORITY HOLDPOINT
ef056269-1a2c-43eb-bf4d-beb5fe31389d | checkpoint | 1.7 - Welding Certification
2e2bfb11-1c82-54b3-9114-2b71ac73b4bd | note | Frequency - Prior to commencing activity
2cdf28bc-2cb9-56b1-8b7a-c04e40d5abfd | note | Acceptance Criteria - Submission & approval of the following:
e5b947af-076a-50e1-81b6-9f5da6456a71 | note | — Welding Procedure Qualification
fc699360-6cd7-5853-9149-84589601c35a | note | — Welding Procedure Specification
1c5fee45-db6b-5702-96fa-b0218bcc062e | note | — Welder Qualification
02c01339-39f9-53b1-9dce-748817967364 | note | — Approved Consumables
54ce3c0a-acd6-5794-8d1b-d140da58d0d9 | note | Reference Documents - AS1554.1
917d3271-b973-5cb8-835e-1b407aa9beec | note | Inspection/Test Method - Verify
00362234-2867-5172-93be-8f5ed3506f19 | note | Record of conformity - This ITP Signed, Qualification Documents
450d96f9-b7e1-5550-9bb7-31b000134679 | note | HP*
afa44590-6ab1-53ee-a5dd-ebe80303308b | note | Responsibility - Project Engineer
21ace4fa-bff4-5bca-8c5a-f9bdcf4bcc55 | date | Date Completed:
9fcfdce8-5abb-44c8-a7a5-106e03abc599 | checkpoint | 1.8 - Temporary Works – Pre- Cast Concrete Panels
99a0a409-7857-5eea-9fb4-a28942a99261 | note | Frequency - Prior to commencing activity
9ab425d5-6c45-5f5c-8292-a382c3a6fa2f | note | Acceptance Criteria - Submission and approval of the following documentation by the FH Temp Works Coordinator (not limited to):
d265c5b2-eefb-52c9-8006-1555eb83a9db | note | — Certification of Lifting Points
444a2aed-b1b8-588e-98ab-8bb0bd04e74e | note | — Propping plan
c0802cb0-adcc-53e0-8c8c-54b1cf54710f | note | — Erection sequence
db023486-1536-5299-bc07-e50d5691ae70 | note | — Lift Plan
d19ccbca-21f3-53bb-bd71-49209d9a2f0f | note | — Certification of Ground Platform for lift
c38b7ede-26b0-587e-91e6-5a40d193ec40 | note | — Lifting inserts
d32e6ce6-08c3-5126-8de1-8e4ec70adee0 | note | Reference Documents - Structural Drawing Set 030-20
a9f2fad5-a9ce-58e3-b671-dbcf43b09a6f | note | Inspection/Test Method - Verify
85f9d944-cab0-5169-b7d5-00fdafd9083e | note | Record of conformity - Certification of lifting points, propping plan, erection sequence, lift study, Geo Report
bba6696c-55a3-50a5-aceb-3151fab3690f | note | HP*
f30cabe5-fc09-5f56-aa9a-4009031e28f7 | note | Responsibility - Project Engineer
1fc22e52-598a-5f2c-98b5-f7ebd965243c | date | Date Completed:
e4ea0eaa-1f71-4d80-80b5-1b8ef4d262aa | checkpoint | 1.9 - Temporary Works – Structural Steel Roof
718bd0c7-893d-5600-9d3c-72a9188d65a7 | note | Frequency - Prior to commencing activity
64ef3b56-9af8-5ebe-a7c3-5ca6a3812501 | note | Acceptance Criteria - Submission and approval of the following documentation by the FH Temp Works Coordinator (not limited to):
18b2b294-68da-5ee4-b100-e47dfdbe097b | note | — Certification of Lifting Points
422f7a32-25fa-5df1-8693-b6d259f0f6f0 | note | — Installation sequence
dc90a506-3d95-5871-b9b2-3a9a9e67ba01 | note | — Lift Plan
f9dd3169-3ae7-510a-9f8a-0af699b02d4b | note | — Lifting Point calculation
126cc9bb-c43c-5a11-8ebe-b51327abb87e | note | — Certification of Ground Platform for lift
7fc570ad-e1d1-5a26-ab63-d8eafa17b957 | note | Reference Documents - Structural Drawing Set 030-20
96295fe3-231f-5eb6-948b-6b3e1759860d | note | Inspection/Test Method - Verify
4fb41381-69f2-507b-a3bf-e1e2b4cef5ef | note | Record of conformity - Certification of lifting points, erection sequence, lift study, Geo Report
c9f9f112-4186-5900-a305-f8247d1e0298 | note | HP*
a59a740e-7e80-5331-8eee-4bd2aadc3a5c | note | Responsibility - Project Engineer
6d9fb1d1-d7b9-54ab-be28-9017f7ad025d | date | Date Completed:
fbaa66f9-418c-4d89-9a7a-4ab31f0ec917 | section | 2.0 - Construction - Precast Concrete Panel
249afd3a-0ed4-492d-a2ea-4655a16c9c32 | checkpoint | 2.1 - Fabrication Inspections
da94efe2-caf6-5001-8ea4-db8bf40b5c79 | note | Frequency - Each Lot
81f3cee7-4515-5e20-a227-a58f7082f54e | note | Acceptance Criteria - Inspection of the following prior to casting:
8f915a59-384f-5b28-a856-a2e59c0779ed | note | — Formwork dimensions & stability
6933cbb6-2fc8-57dc-9d67-2d011fc6e1a5 | note | — Edge details and penetrations
6805f212-a9f4-5635-9338-f75289752c98 | note | — Connection materials and inserts in place
8d00b931-840e-5f16-8ba0-aef00d113c18 | note | — Reinforcement
751c0798-489d-55dd-b4ac-403bfacabf0b | note | — Concreting
a947bb90-3c8a-5067-8fe5-19888ac899a2 | note | ○ Inspection of the following after casting
0d04d6f1-1536-575d-a011-ca79c0434c5a | note | — First precast element of each type at the earliest possible time before and immediately after stripping
56720e04-1612-577c-8c9a-55e3c001dd60 | note | — Stripping & storage
acdee0ff-18a0-5625-a39b-4cd553ca56ae | note | Reference Documents - ZULU-BECA-001-SPC-00005 0321 Shop Drawings
9c1a850d-57fe-5d5c-9a34-dcc57458c2c5 | note | Inspection/Test Method - Verify
4b2b8dfe-a9ad-5cd1-9f2c-8c30fbf9dde4 | note | Record of conformity - This ITP Signed, Element Casting Checklist
ceec0016-6926-5745-984c-f94b4c138a46 | note | WP
94425407-3e8a-54cb-a627-c9a2d42385a1 | note | Responsibility - Project Engineer / Principals Representative
92c1eedd-7df6-5c1a-b86f-be4700df31b6 | date | Date Completed:
ec5d9c02-aea8-4a69-b93e-358e2067841d | checkpoint | 2.2 - Delivery of Precast Panels
0963e8eb-e2c1-5e79-8f3d-3481c91d8e0d | note | Frequency - Each Lot
f5164d33-0ec2-5244-aca1-f982ff121138 | note | Acceptance Criteria - Complete inspection of precast panels whilst still loaded on the truck prior to accepting the delivery on site.
336248ef-2bb5-58e7-97a9-88158a6f0030 | note | ○ Identify any damage/defects prior to unloading of the material and correct panel being delivered as per the sequence.
02ff43c5-1ee0-5872-8522-6a5dac8c8256 | note | ○ Precast element identification is available on each panel
c8a51499-cdfa-5b4e-8b8f-00a264b591c8 | note | Reference Documents - FH Quality Process
331294d9-bbff-52fa-a8ae-4f2a28d70d40 | note | Inspection/Test Method - Visual Inspection
b61c9d22-91e3-59f3-b926-cdc9afb6d4aa | note | Record of conformity - This ITP Signed, Materials Inspection Checklist on Conqa
f855f9cb-0ec5-55d1-9f25-66a01264d425 | note | IP
b083594d-fabb-530e-8b3a-207298575b4d | note | Responsibility - Project Engineer / Site Engineer
19cff88e-1d31-5577-b63b-9dde13da0bbb | date | Date Completed:
de2d270e-8f81-4f8c-aab7-a80ed353a49f | checkpoint | 2.3 - Erection Preparation
82fbf92f-d28a-56e7-b777-18181634b76c | note | Frequency - Each Lot
831bc499-a28e-509e-9dc5-e91cf2423352 | note | Acceptance Criteria - Complete Pre-Lift/s Commencement Checklist
3739b2b5-fd34-5748-a996-da06ae404188 | note | ○ Ensure erection drawings & propping plans available to the crew
b2c8074c-7d75-5bfd-8de5-bd1aa17289ec | note | Reference Documents - ZULU-BECA-001-SPC-00005 0321, AS 3850 cl 4.4.2
ad1e87a1-979d-5312-881d-4ccf2d363781 | note | Inspection/Test Method - Visual Inspection
f734f5c5-ae37-59d1-9a41-ceef1dce2bd7 | note | Record of conformity - Pre-Lift/s Commencement Checklist, This ITP Signed
0ac93dda-e517-5dc9-b82d-d9219411a9d0 | note | IP, SCP
f1a6eca3-36b2-5596-8da7-a74dd3b47245 | note | Responsibility - Site Engineer / Foreman / Surveyor
223db3c4-d584-5d7a-867e-889675e0b135 | date | Date Completed:
3a2cd550-1987-4a32-9bb7-b3f095930b65 | checkpoint | 2.4 - Panel Placement
4d163078-0a60-5486-8913-d34a0282d5d4 | note | Frequency - Each Lot
7a02a727-4c12-5ddf-9862-3a397d4cab0f | note | Acceptance Criteria - Levelling shims have been set correctly and gap between the footing & precast panel is not greater than 40mm
00aa9f62-53ff-5654-ab5f-23cfe3e2528f | note | ○ Survey to confirm panel placement as per the design
afd97b72-8f24-5d70-a846-f5d06289b8e0 | note | Reference Documents - ZULU-BECA-001-SPC-00005 0321 Drawings
715ce228-7f52-588e-9e08-772ae14c0b7b | note | Inspection/Test Method - Verify
711855bd-3553-5444-a40e-928e82d5ccba | note | Record of conformity - This ITP Signed
5a5d9fe2-b835-5e85-b6ab-75f9d38a5b61 | note | IP / SCP
22dc27e6-5110-5310-8d59-d1b868abed93 | note | Responsibility - Site Engineer / Surveyor
470d748f-eaef-56ad-9256-f8a9aede842c | date | Date Completed:
c9e16d65-56b7-42f2-9414-f3c587295f3f | checkpoint | 2.5 - Propping & supports
7fca6c3e-3f3b-50aa-9f50-70d2bbacee39 | note | Frequency - Each Lot
3644fb02-0326-5d24-af50-8a4dc6a5e173 | note | Acceptance Criteria - Witness Point
2b5cdef7-3619-577a-9453-257a0bb4e207 | note | ○ Propping plan is available for each precast panel
5a0d4d23-ac6a-56be-b260-ad113110b869 | note | ○ Ensure propping is installed as per engineer’s design and/or conforms to AS 3850.2 Sections 5
38858e64-5faa-56f3-a9e6-0cba7297e649 | note | ○ Inspection Notice provided for installed temporary bracing
845df5da-6844-512a-9cea-a81637df390f | note | Reference Documents - ZULU-BECA-001-SPC-00005 0321, AS 3850.2 Section 5
d7469f77-fe27-5507-befc-0ccf94b7d4e2 | note | Inspection/Test Method - Visual Inspection
4cdacf3d-9027-57ec-8960-6a11f1b9d047 | note | Record of conformity - This ITP Signed, Building Engineering ITP
c9a86c84-3220-5f5b-aedc-ac2b6aacb40e | note | WP
68279ee0-8bcf-578c-942a-af0f871f186f | note | Responsibility - Site Engineer / Foreman / Principals Representative
dac54f02-5278-5669-a6ca-0c1ddcc5aea0 | date | Date Completed:
5c762cc4-94da-48b4-9a32-8193170294c4 | checkpoint | 2.6 - Fixing & Welding on Precast Elements
617ce996-8a57-5015-9878-881a6e1e3ab0 | note | Frequency - Each Lot
d00dc752-4028-5bc2-893b-fa1c9db8625b | note | Acceptance Criteria - Install all fixings as per the drawings & engineers plan
5fd8a5e8-7c3e-5f3e-bfce-cf0c27ed7ae4 | note | ○ All welding shall be carried out in accordance with AS 1554.1 unless noted otherwise, all welds shall be 6 continuous fillet category SP using E49XX electrodes - butt welds shall be complete penetration butt welds, category SP.
d231c235-e322-5d7b-8541-6b7dc30990ed | note | Reference Documents - AS 1554.1 Drawing 20002
36df6213-aa81-5377-ab20-6a721248047e | note | Inspection/Test Method - Verify
eda2b672-17c2-5290-98f1-91267019e081 | note | Record of conformity - This ITP Signed Welding Certificate
14ade121-5f9d-59e1-be36-f1173d0c4747 | note | HP*
d7c0eb35-d283-5f75-9268-976539b68b09 | note | Responsibility - Site Engineer / Foreman
6cbf68e0-2fe0-576e-82a1-80429c8fdd79 | date | Date Completed:
3d5eb739-1361-4ed8-9266-be84de515f7e | checkpoint | 2.7 - Testing of Welding on Precast Elements (if required)
7b565fe0-a4fd-53d5-ad65-637358c17464 | note | Frequency - Each Lot
e8706ddf-9cd5-5e93-86a4-109280cd9127 | note | Acceptance Criteria - A competent inspector shall inspect welding works as per the below table or as otherwise stated by the engineer:
4d066bb9-1a3d-5bd5-b9a1-219d2b94ebfd | note | – – – – – – – – –
f2b22a3f-2a65-52f2-8480-73fc930e7806 | note | WELD TYPE ¦¦ % OF WELDS TESTED ¦¦ TESTING PROCEDURE
4cef1085-e35c-5cbe-bc56-5f3571dba6ee | note | – – – – – – – – –
f0dc9dc5-ba9d-5e9f-a6b5-a4033ae8035d | note | ALL GP/SP ¦¦ 100% ¦¦ VISUALLY SCANNED
776900ec-27d1-52dd-9c6d-bd8c29e1895f | note | SP ¦¦ 20% ¦¦ VISUALLY EXAMINED
125e71d2-bd25-5714-921c-c61cdcf3d623 | note | SP BUTT ¦¦ 5% ¦¦ ULTRASONICALLY OR RADIOGRAPHICALLY
c46a84c3-261d-5b9d-9cbe-1eab98348210 | note | – – – – – – – – –
c5f28dcf-03f4-55d0-81eb-ccb486fb97c0 | note | Reference Documents - Drawing 20002 Note S8
2fe091ea-906e-5fcd-a15a-97a81684862c | note | Inspection/Test Method - Verify
31ca6b5c-1a86-5cdb-94f5-d15d96f8a0b2 | note | Record of conformity - This Signed ITP, Welding Test Certificate
faf4ed83-23f3-532d-a1e2-bfdcfa2ceb07 | note | HP*
c4f1c274-2571-5d6d-9bfc-906f89ee3a73 | note | Responsibility - Project Engineer / Site Engineer
a428003c-87fa-5e03-b4c8-264dd20657eb | date | Date Completed:
2fb0f814-0b96-472d-8e24-e141d34446a2 | checkpoint | 2.8 - Grouting
8ca66cdb-2e00-5e67-90f6-585a9788086b | note | Frequency - Each Lot
c174b55c-f8d7-5490-b767-094c8c73d072 | note | Acceptance Criteria - Grout to be used shall be non-shrink and have a 28 day characteristic strength of 40 MPA. Details of the proposed grout used to be submitted to the engineer for approval.
1d997adb-e02e-5853-b8f8-441aafd76acc | note | ○ Note: sealing of the panel vertical joints will be by the precast contractor.
c9ff5cc5-5deb-5741-b1a1-f1493b5b66a0 | note | Reference Documents - Drawing 20003 Note PC35
b53bca2e-4058-520e-8910-898e37b7570f | note | Inspection/Test Method - Verify
fc19ee69-a3ed-5f95-9c1e-7ca7a2474492 | note | Record of conformity - This ITP Signed, Building Engineering ITP
c80aadec-40fc-5f7b-972b-f71b23730298 | note | IP
57ee8a4b-c02b-523a-9b41-30cdca97b6d0 | note | Responsibility - Site Engineer / Foreman
34bf48ab-5362-5524-b280-9db76bafda68 | date | Date Completed:
917ba98a-82d8-4c72-9a14-5e193dfc1aea | checkpoint | 2.9 - Removal of Props and Inspection of Completed Precast Walls
9ea7723e-30e8-5a7c-9226-e056043a43e1 | note | Frequency - Each Lot
16ada410-8285-555d-8f7d-9d36b7900573 | note | Acceptance Criteria - All propping must remain in position until all structural elements (roof beams, bracing, struts and purlins) affecting stability are fully erected and braced, securely fixed to the panels and the panels have become an integral part of the structure. During construction the builder must ensure no panel props are disconnected by contractors other than the panel contractor.
fe123380-9114-57fa-91ad-081ad2761fd3 | note | ○ No propping is to be removed without the written consent of the temporary works engineer
43ef42a0-e56a-55b4-ad85-d2dff024cbb8 | note | Reference Documents - Approved Shop Drawings Drawing 20003
bc6cafa0-866a-5d0a-86a4-1ce42cdd65ac | note | Inspection/Test Method - Visual Inspection
96cd1e12-058f-573d-a156-a36b2ddc7fbd | note | Record of conformity - This ITP Signed, Engineers Written Approval, Building Engineering ITP
3123aadf-503f-592d-963d-26666cc79d1b | note | HP*
5ec14204-ddf6-52ae-9f8b-40e544a9b4c4 | note | Responsibility - Project Engineer / Site Engineer
4b1eea38-75c6-59c9-8d59-8a5b4f2d7cb2 | date | Date Completed:
26a10640-de4b-4347-8182-151ec05e63a2 | section | 3.0 - Construction - Structural Steel Roof
9b003894-db6d-47be-8317-d01ef52733fa | checkpoint | 3.1 - Delivery of Steel Sections
bdc9830c-4283-54e4-8e79-7342d9e2395d | note | Frequency - Each Lot
740a1965-87d6-58e2-a5fb-ba575a6a4bfc | note | Acceptance Criteria - Complete a materials inspection upon arrival of steel sections.
2b26ffbc-867f-5ebf-9788-83d4f66e3a56 | note | ○ Ensure correct components and sections have been sent
f11dc666-8ffc-5894-9c13-b5dd127c3d15 | note | Reference Documents - FH Quality Process
668e3c2b-b578-58ff-a88a-db88ce8c8fe2 | note | Inspection/Test Method - Visual Inspection
4f1c5e87-2219-5192-a10b-389e8e545bb0 | note | Record of conformity - This ITP Signed, Building Engineering ITP, Materials Inspection Checklist on Conqa
f9f07b99-d592-5098-9618-8e68182c684f | note | HP*
b47291b7-5d82-54f4-8b39-89a62d31ee57 | note | Responsibility - Project Engineer / Site Engineer
89d1af5e-047c-500c-93de-85eb70595dc6 | date | Date Completed:
0e1b0f0f-7041-46eb-8fca-cc0c55bc7bc1 | checkpoint | 3.2 - Erection Preparation
36830239-cf60-54e1-93a5-e2cc1ae03187 | note | Frequency - Each Lot
32942208-6064-5766-9834-2d4369179b71 | note | Acceptance Criteria - Complete Pre-Lift/s Commencement Checklist
556e573e-1781-5d20-aa7d-a876f0abb570 | note | ○ Lift sequence/arrangement of steel members available
ca40cbe3-7045-50e4-b7ed-0ad21d418417 | note | ○ Adequate fall protection in place eg guard rails, safety mesh
fca6e940-8b09-574f-a724-7aebe42d6224 | note | Reference Documents - Drawing 20002
6f4916d4-060c-51ab-80db-dc0edaf41194 | note | Inspection/Test Method - Verify
977aa463-e702-5e40-beed-99a82e0039c9 | note | Record of conformity - This ITP Signed, Building Engineering ITP
ba6a247d-1729-5709-a8e9-ca9cad8e5636 | note | HP*
3946c6c4-7942-518a-84ef-fecaa18a3ad3 | note | Responsibility - Project Engineer / Site Engineer
efcd1830-ac6d-555d-825d-b2f7bd4e6948 | date | Date Completed:
e69240e5-6f30-4d35-94be-06e33fd355d4 | checkpoint | 3.3 - Erection of Steel Members
bb49ddc4-0318-5409-83c6-7ce7ae92696a | note | Frequency - Each Lot
868d2b71-ad3c-55ff-9296-308b330d14d4 | note | Acceptance Criteria - Steel Members erected as per design layout and Steel Framing Schedule
25b244d4-7861-50ec-9710-2c92f8dfe4ea | note | Reference Documents - Erection Sequence Approved Shop Drawings, Structural Drawing Set 030-20
685a4595-d339-5816-b8a6-f00395372f76 | note | Inspection/Test Method - Visual Inspection
b3340cb2-1af0-53ab-bfee-56e9702e8dc5 | note | Record of conformity - This ITP Signed, Building Engineering ITP
df044819-4489-5c24-bee9-9a628c026571 | note | IP
070d2b7d-771c-5956-b10e-ef4cc591850e | note | Responsibility - Site Engineer / Foreman
4c806dd4-79a5-554d-9759-122ab8060046 | date | Date Completed:
12822e1b-cbaf-4834-b92a-9ddcddb5d006 | checkpoint | 3.4 - Bolt installation
dbd7b1c2-ed9a-5633-a43e-f0de6ef62393 | note | Frequency - Each Lot
85c6e8eb-9d23-56b2-9dc3-717fe3883fa5 | note | Acceptance Criteria - Unless otherwise noted, all bolts shall be M20 Grade 8.8/S, all H/D bolts shall be grade 4.6/S.
f0c8714e-6a13-563f-8927-0e8c5a4ff031 | note | ○ No connection shall have less than 2 bolts
31f18543-3f7e-5756-8af5-1239fd5ba16f | note | ○ Bolts to be installed as per manufacturer/engineer specification
990024d3-7289-5c74-a1f1-4e7c26f3810e | note | Reference Documents - Drawing 20002 Note S6
f39b661a-e6bf-55e9-960b-ea6504b9692b | note | Inspection/Test Method - Visual inspection
6147f49c-891e-58f1-827f-71a79d4b4571 | note | Record of conformity - This ITP Signed
4bd1e4c5-65c7-5b4c-a46a-eb28d31fe2b4 | note | IP
d09a5e1f-bb81-5b8c-b45b-4c6c62b025d6 | note | Responsibility - Site Engineer / Foreman
3f536564-2ea1-5dea-aa78-4f0c36e218ab | date | Date Completed:
8b49cf40-4a05-465c-997e-96f4d33a4e5f | checkpoint | 3.5 - Welding on Steel Framing
43bc7846-b4f3-5b1e-a331-cb847fb8870e | note | Frequency - Each Lot
b203ca90-ac26-5306-9dbc-cb1c61eaf609 | note | Acceptance Criteria - All welding shall be carried out in accordance with AS 1554.1 unless noted otherwise, all welds shall be 6 continuous fillet category SP using E49XX electrodes - butt welds shall be complete penetration butt welds, category SP.
95e12cac-3c85-52a0-b645-79a1dc634545 | note | Reference Documents - AS 1554.1 Drawing 20002
a370217d-6a8a-5b73-8814-789af9286473 | note | Inspection/Test Method - Verify
8435eea3-1542-5866-ad7c-7df0cd144447 | note | Record of conformity - This ITP Signed Welding Certificate
fa484a78-b5f1-5d38-90f8-807bf216dad0 | note | HP* IP
ccfb08f1-3600-51f1-8ec5-5d148b7d7c29 | note | Responsibility - Project Engineer / Site Engineer
28dd321f-4b79-5869-982b-f65126b26c96 | date | Date Completed:
15fe4e6f-aea7-4543-8bc8-18720b1277e4 | checkpoint | 3.6 - Testing of Welding on Steel Framing
ecd39c90-6d35-5236-a0a9-20ffa9a0df2d | note | Frequency - Each Lot
59856f88-70d3-5fb2-8e9f-a127fd1fa564 | note | Acceptance Criteria - A competent inspector shall inspect welding works as per the below table:
6c0432e0-bc14-5729-9863-1b0ff8855861 | note | – – – – – – – – –
7a93941f-9817-56ed-a23b-e35dd2892320 | note | WELD TYPE ¦¦ % OF WELDS TESTED ¦¦ TESTING PROCEDURE
aaa8063b-3070-5cdb-ab60-f6f17b3ab947 | note | – – – – – – – – –
f53ca713-bc33-5a25-874b-0d06da7e2b66 | note | ALL GP/SP ¦¦ 100% ¦¦ VISUALLY SCANNED
b4c5c6ae-bb98-5173-b6ed-83e8adf0d776 | note | SP ¦¦ 20% ¦¦ VISUALLY EXAMINED
73fde17f-dd2d-5af6-9eec-c8493dade9b7 | note | SP BUTT ¦¦ 5% ¦¦ ULTRASONICALLY OR RADIOGRAPHICALLY
aeae3d0b-5e6e-5a33-8a0d-df37acf728a7 | note | – – – – – – – – –
34bb1725-edf2-5e43-ac22-476c479c0551 | note | Reference Documents - Drawing 20002 Note
473b139d-ac9d-592f-9ab0-d0812677fde0 | note | Inspection/Test Method - Verify
39c96f4f-82a6-5be1-a727-ae2d66882eda | note | Record of conformity - This Signed ITP, Welding Test Certificate
b88c568d-ee09-5dcc-82f8-d383a498a038 | note | HP*
1f95ab89-9dd3-577a-9a30-9f0d7c7c889d | note | Responsibility - Project Engineer / Site Engineer
7f8a620e-a390-5f57-ab53-8a5d8e4762c5 | date | Date Completed:
3353926a-1127-4ad4-9d3d-5e6bfbeade14 | checkpoint | 3.7 - Inspection of Completed Steel Framing
bee679c4-4931-57ab-a321-d688d0a780f0 | note | Frequency - Each Lot
f8b872ca-3510-5701-9053-114e5df59618 | note | Acceptance Criteria - WITNESS POINT
7de1abac-a010-533b-9b34-5f91153a0ead | note | ○ Provide notice for an inspection of the Steel Framing erected on site before installation of roofing sheets/lining.
1834f0aa-4195-548e-ab67-06d6b5218fa1 | note | Reference Documents - ZULU-BECA-001-SPC-00005 0342 cl 1.17
db1feb12-e56a-54aa-b71f-a9b5f25d5c96 | note | Inspection/Test Method - Visual Inspection
8e1bbb72-fbf1-5b57-9a99-2bf4e32e93cc | note | Record of conformity - This ITP Signed, Building Engineering Structural Steel ITP
79466241-f6bd-51f3-b34d-8cb16a96ab5c | note | WP
f544fbf8-dda3-579b-a1c5-136ebbdfd0ca | note | Responsibility - Project Engineer / Principal’s Representative
af280d3a-95e2-5e15-820c-8e6ab6cfc940 | date | Date Completed:
8f13865f-84aa-4c98-8806-d1bb24edac05 | section | 4.0
c199956c-9bcc-4b17-9c30-32fba3616e3f | checkpoint | 4.1 - Airport Building Controller Sign Off
96208133-ae7f-5c3c-8a45-7c68159aa230 | note | Frequency - At the completion of works
d14af70f-c62e-567e-ba3f-b17df4095efa | note | Acceptance Criteria - HOLD POINT
5cb38d3d-6dbd-5c72-9e1d-d87b0755b81f | note | ○ Give 72 Hr Notification to the Airport Building Controller for Mandatory Inspection of completed precast & steel framework.
e8048d1e-d680-58c3-b5d3-12979b2c96c5 | note | Reference Documents - ALER 3 Building Permit
6852560b-3ad3-582c-8a07-77ec61809e1a | note | Inspection/Test Method - Verify
2701c5e3-17d1-5f59-a2b2-d5d0c33e93c9 | note | Record of conformity - This ITP Signed Inspection Certificate
b04d0aba-cb5d-5856-bb01-e0b577b16a71 | note | HP
570fb9f5-3520-5efc-a5ea-284b631b3d84 | note | Responsibility - Project Engineer / Principal’s Representative
afe66c70-78a4-56d9-9190-11a647ed39d7 | date | Date Completed:
45462c05-a40b-4d39-bda0-f02f19f94eaa | signoff | AUTHORITY HOLDPOINT
4ca4a586-ecf6-4d2b-8aee-6bcfe7066931 | checkpoint | Final Inspection
6dca4a6b-b170-58d3-98d3-f48b5bc891cf | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
737cd6a5-c435-5a6b-b20c-861732d9b368 | textbox | Print Name:
d5d7dc71-fbf5-582e-b582-0eac79c1213a | textbox | Position:
262e9f4c-a796-5f7f-a8b5-055bc03c7420 | date | Work Completed On:
965c8fa8-5d77-5ba1-9543-99e1b29b1d4e | date | Date:
6071bb66-23a5-4bea-bd73-82683155d2cb | checklist | FH-ZU2-QU-ITP033 - ALER 3 Pavements - Rev 0 | itp | ITP033 - ALER 3 Pavements
5ac2c73f-3f0c-4b8a-a066-339a1eece0d4 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
445ada65-6830-4a00-b122-28511631b8db | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
88f4ee42-4f3a-5560-8f50-3501199bc53c | note | Frequency - Prior to commencing works
e94b9078-3574-5ce3-b3be-e41cda0376ad | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy.
575eecbd-7015-5f56-a778-0b4cd176c74e | note | ○ Current Revision to be obtained via Aconex
293b7aa7-44ce-59f6-af43-104d16f3f2a8 | note | Reference Documents - Aconex
8915edc3-23eb-5f12-8d65-315cd42bcb27 | note | Inspection/Test Method - Visual inspection
6a88908e-dbac-5341-bd5d-032afd65fd73 | note | Record of conformity - This signed ITP
348f8050-fcd8-5ed0-b106-e94e637a9ce4 | note | HP*
3ed65b8d-cf56-52db-9ba7-1aefa291612b | note | Responsibility - Project/Site Engineer
e9ce13fa-cf24-56df-980c-b9ccebbe3747 | date | Date Completed:
85ba6a0b-726b-443c-89cb-f2bef807b51a | checkpoint | 1.2 - Implementation of all measures and controls.
5c5ab2ed-c390-5485-a898-530ea598a359 | note | Frequency - Prior to commencing works
928e1ecb-68b6-566b-b8cc-41de2ecefcf8 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
8ee31ea7-d49a-576f-953e-ea080fea9ae2 | note | Reference Documents - PSP, EMP, TMP, WP SWMS
3b681da3-e9a7-5ca8-9f22-c8553304f77e | note | Inspection/Test Method - Visual inspection
e9b43486-6d94-5312-83f0-249018ce796d | note | Record of conformity - This signed ITP
c39127ef-6a1a-5cb4-a0da-6a515be27a21 | note | HP*
a9f983fe-739b-5e0f-bcf4-c5971feea801 | note | Responsibility - Project/Site Engineer, Foreman
d813f8aa-b039-539a-9119-0840f538cc78 | date | Date Completed:
b3b0f833-8361-47ea-a92c-d4c612cb1e39 | checkpoint | 1.3 - Survey
8f879784-4f8c-593f-a0ca-dd10fa197c6f | note | Frequency - Prior to commencing works
9a7eff4a-b2b9-5532-9b78-dc957e1ec882 | note | Acceptance Criteria - Area has been surveyed, highlighting any areas where excavations should not occur (e.g. exclusion zone).
48273b2e-0fbe-5d5f-8eb4-bccfefb5a7d9 | note | Reference Documents - PSP, EMP, TMP, WP SWMS
7062702d-1d1c-59d0-9320-8423183d01e5 | note | Inspection/Test Method - Verify
dacd2f74-d85f-57fa-8e04-73acc4f0c5fa | note | Record of conformity - This ITP signed
8591ff03-9709-59fe-b0a2-c4fa376459ba | note | HP*
097460e1-aad9-5107-95f0-9ca0ad9ff4b9 | note | Responsibility - Project/Site Engineer
d53b527c-7e03-5edb-80b1-de63f6d0eee4 | date | Date Completed:
4f793d20-6078-4cd8-82d1-6e3cbce390ff | checkpoint | 1.6 - Material Test Certificates
69ae8658-8346-557d-8387-dcfd6306a3cb | note | Frequency - Prior to commencing works
2a5dc16a-f8f6-5371-a46d-3e87d89b7f7b | note | Acceptance Criteria - Source Rock shall comply with VicRoads Specification 801
aa6da287-72f9-5209-b0a7-7b1731598783 | note | ○ Crushed Rock shall comply with VicRoads Specification 812. The contractor shall provide test certificates confirming that the supplied crushed rock meets this specification
a6004a84-7dd4-50c9-917b-232d0392391e | note | Reference Documents - Drawing 00201 P04 & P05
7b167b48-5d4d-5398-95d3-c97686167e45 | note | Inspection/Test Method - Verify
e48ca7b7-4d43-5e28-a7b3-438b321c5ca9 | note | Record of conformity - This ITP signed, Material Test Certificates
b008d7e2-30bd-5037-82cc-51df7c41f51f | note | HP
b004d303-f081-5765-a9ab-6b3f24f0cf54 | note | Responsibility - Project/Site Engineer / Principals Representative
cfd1d36f-906d-5542-b792-5f0b22ef5106 | date | Date Completed:
063c82f1-dc76-4dd9-ace3-453f9563989a | signoff | AUTHORITY HOLDPOINT
723c67c7-7889-48bb-ae06-9d6dc3dc52db | section | 2.0 - Placement of Sub-basecourse and Basecourse
99b2f682-83f7-4c66-ae1c-aee7465fb8a3 | checkpoint | 2.1 - Layer Placement
2955139e-eb49-55ac-99e4-322a0426fa25 | note | Frequency - Every Lot
e67d59d7-214b-5230-8a7b-c1486f45ac76 | note | Acceptance Criteria - Place in horizontal layers of approximately equal thickness. The loose thickness layer shall not exceed 300mm UNO, and in any case, shall not exceed the depth for which satisfactory compaction can be achieved
5c33d27d-cde3-5d17-9fdc-5ca658f2e808 | note | Reference Documents - Drawing 00201 E32
4abec461-6ace-5882-8f11-ee711390fc89 | note | Inspection/Test Method - Verify
74f85e10-8f79-5cd5-b0bd-206c63e0112e | note | Record of conformity - This ITP signed
033c3253-0a9f-5a17-b121-f72d88bcd98b | note | IP
ac8718b1-8e4a-596b-b4e2-9b2c7fb1eaba | note | Responsibility - Project/Site Engineer
4047700a-90f5-5e4b-9965-c12c5a57317a | date | Date Completed:
695b0d73-daf9-48e2-b017-fc4dd5e2cc2f | checkpoint | 2.2 - Placement Checks
bfb48b94-e814-5ae0-a2bb-dc6c14920e2e | note | Frequency - Every Lot
10bb4a2e-bbde-52e6-9ea6-917c5a8bf469 | note | Acceptance Criteria - During placement of the material check;
25e95d64-5474-5683-860b-c531e1c37d8d | note | ○ Where engineered fill is used to construct permanent batters, it shall be overfilled, compacted, and cut back to the dimensions, levels and design grades to ensure that the final batters have the required compaction
6f71faff-fb98-5402-b447-ec926283efe1 | note | ○ Place in a manner such that handling and spreading of materials does not produce gradation of the materials
ef2948ec-ef74-539b-abf0-cd05f818f5d0 | note | ○ Place so that the surface is always self-draining
cebf26ea-65dd-52d7-bb46-0339180f36f4 | note | ○ Engineered fill shall not be placed adjacent to concrete less than 7 days after final placement of the concrete UNO
9b461ba2-b7ba-5e61-99b8-cc568054104b | note | Reference Documents - Drawing 00201
35c691a2-dfe3-5ace-a717-de6048e75c76 | note | Inspection/Test Method - Verify
619b9d31-d217-5225-88dc-765dfeed5e25 | note | Record of conformity - This ITP signed
d857ab14-ea04-5716-a3a5-ec8a3dffaf14 | note | IP
6170092b-5477-58d4-bf50-006e0a2f4059 | note | Responsibility - Project/Site Engineer
e2e986ca-e9f7-549b-af5a-085675dd7720 | date | Date Completed:
2d9769c2-8a2f-4f26-80c9-fffe59470d7e | checkpoint | 2.3 - Compaction Check
467ef36d-89f0-519f-87ed-79752fa80a10 | note | Frequency - Every Lot
c58cd845-a544-5be2-a17f-5faed2d24c22 | note | Acceptance Criteria - HOLD POINT
b1e170c2-fecf-5841-83e9-4923ee0ba4f5 | note | ○ Engineered fill material shall be compacted by Tamping Rollers and methods approved by the superintendent.
469d0b0d-e363-5a1c-a8d6-af359e41437b | note | ○ In areas where access by such plant is not possible, it shall be compacted by a method approved by a qualified geotechnical engineer.
013c3104-d744-50b8-b672-cc1c5759728c | note | Reference Documents - Drawings 00201 E37
1c005822-8f2e-582f-a2ed-2a852db954fa | note | Inspection/Test Method - Verify
b5215b41-0d2a-5638-8edb-0d45549e91d3 | note | Record of conformity - This ITP signed
fb9a8d0f-493d-575a-a50d-e1723607f9fa | note | HP
37afa677-2927-5b5c-8908-7123fa4a9bcb | note | Responsibility - Project/Site Engineer / Principals Representative
f1f7c6e9-dc8a-541b-b837-efd3b9b4ae04 | date | Date Completed:
31afa2bd-e086-40c9-97aa-57e1af5cb37e | signoff | AUTHORITY HOLDPOINT
e7dcdc09-4fd6-4575-b1c5-b0e704ca4365 | checkpoint | 2.4 - Services & Culverts
bda8b430-90dd-5918-9aa6-12fa4200bfbb | note | Frequency - Every Lot
0eafddff-19f9-5066-a3e0-f7f65338f809 | note | Acceptance Criteria - Check if any culverts or services are with the influence zone for compaction.
e15d1518-607b-570a-9ecd-f37533c8adfd | note | ○ A general rule, FH will seek advice from the Principles Representative if any culverts, duct banks or RCP pipe are identified closer than 1m from pavement layer surface. If identified, Fulton Hogan will maintain a 1m exclusion zone either side from centre of service for vibrating compaction activities. Hand held DPU’s/whacker plate to be used in lieu of rollers in restricted areas.
74bac026-79b7-5512-b1b3-e3cb7e04b675 | note | Reference Documents - PSP, EMP, TMP, WP SWMS
c9e7c9a5-016c-599b-a27c-fb465b4bc773 | note | Inspection/Test Method - Verify
1eb4bca5-58cd-553d-a1a6-fa242626fc25 | note | Record of conformity - This ITP signed
dc2d12b7-5b52-51cb-9142-fb0ce4efade5 | note | IP
02a685f9-1262-562e-b190-1854bc6b06d7 | note | Responsibility - Project/Site Engineer
9d2a1379-0df0-5de5-ad1f-ffa210a37b94 | date | Date Completed:
32aa72e9-7fe3-4b27-9b63-5bb141e16039 | checkpoint | 2.5 - Protection of Layer
04b57935-93e2-5019-8209-d83f214ad272 | note | Frequency - Every Lot
bb193365-f6a8-5041-be77-983533a75970 | note | Acceptance Criteria - Protect area from undue deterioration by;
deaa5041-2142-53aa-bb20-dd73db17f0a7 | note | ○ Section off area for at least 12 to 48 hours to allow material to dry back.
80f90b7a-4419-5462-95d9-ea3d83247786 | note | ○ If unable to do so, keep traffic to a minimum
418ea7b2-5ebd-5c03-b662-5437504cc25e | note | ○ Or ensure any traffic that has to cross pavement layers, do not follow the same driving line.
9bb03056-8df2-51f7-b218-38d1d16219e9 | note | Reference Documents - FH Quality Process
673abed8-8885-50d4-857c-e293f27f8a9a | note | Inspection/Test Method - Verify
3eac1684-79ff-5e17-9419-2afbbc097063 | note | Record of conformity - This ITP signed
8bab9735-d6b6-5a47-8e9a-7b4e37a86d09 | note | IP
9b5fbc16-3399-554b-8fe7-707c2e4461e6 | note | Responsibility - Project/Site Engineer
e501a9e8-667d-5057-b062-bc71eb03b604 | date | Date Completed:
31353c85-d03c-4aa1-853e-6a0bb058ee5d | checkpoint | 2.6 - Proof Rolling
223fd7de-82ab-59fa-9a61-b68eab86db89 | note | Frequency - Every Lot
7212f9f8-8ad4-5cac-a82d-3d173347491f | note | Acceptance Criteria - On Completion of Density Testing, Proof Roll with either:
1ee52363-40f8-545c-8bae-78d94e64f696 | note | – 20 tonne pneumatic tyred roller with individual tyre pressures of not less than 450kpa per tyre.
4ad4854d-095a-5c6c-ac8c-b943f5262229 | note | – 12 tonne static smooth wheeled roller with a load intensity on the wheels of not less than 6 tonne per metre width.
13c4dd3f-1c42-586e-9f61-44957580257d | note | Reference Documents - Drawing 00201 P07
064a291c-ed40-5d82-a416-3fd360775aa1 | note | Inspection/Test Method - Verify
5df29650-d510-5230-a23e-2ad748606112 | note | Record of conformity - This ITP signed
24273eb5-732d-526f-b4f0-3f2dbe655be3 | note | HP
3260b1bf-5167-5162-9abb-54b24c4c6d73 | note | Responsibility - Project/Site Engineer / Principals Representative
ee4dabf0-043e-5396-90f3-13a6bce3c61c | date | Date Completed:
4dbe3bd0-1442-4f7c-8608-0434350d38aa | signoff | AUTHORITY HOLDPOINT
d961ae71-745a-4a95-a8ca-23841b7f39b2 | section | 3.0 - Testing, Lot Size and Compliance
2b0d4d0f-eff5-4f0d-8cec-2f43442044d3 | checkpoint | 3.1 - Surface Smoothness
56b57348-e2a8-5f99-8614-e0960e588d32 | note | Frequency - Every Lot
d25f327f-1dcb-5791-990f-b1681f1a8dce | note | Acceptance Criteria - No point on the surface of each base or subbase layer shall lie more than 10mm below a 3m straightedge laid parallel to the centreline of the pavement
b3801b68-416d-5bce-8a4a-f0fe1635ee32 | note | Reference Documents - Drawing 00201 P11
856271b7-345d-57ec-a6ad-25622396049b | note | Inspection/Test Method - Verify
8eecb32a-7273-5597-84d1-2fb742752c6c | note | Record of conformity - Report
61ec9127-32b6-5334-ac6a-c41a819e861e | note | IP
ad8adbd0-a8cf-5068-9e52-13ebcfa98bb2 | note | Responsibility - Project/Site Engineer
e36e34ad-7baf-566f-9cf6-5731aaf4fec9 | date | Date Completed:
7705c47d-a842-464c-bb46-b8a086d9b1eb | checkpoint | 3.2 - Layer Thickness
36b436e3-b651-5437-856e-c06eb2ec14d1 | note | Frequency - Every Lot
b01f381d-f2cd-5282-9e38-1ed3eed7e586 | note | Acceptance Criteria - Pavement layers shall not be less than the design thickness.
6fb818ac-9602-52c4-9da7-509c157df575 | note | Reference Documents - Drawing 00201 P09
64b0b7a4-809b-57ce-9af5-5ecd4d58b010 | note | Inspection/Test Method - Survey
a5c47d17-9c1e-5f06-913e-bdd0660a586f | note | Record of conformity - Survey Report
b5b38f0c-aee2-594c-86fe-5f4c09786fba | note | SCP
7a8bbd07-e2c1-5eba-a10a-404ce0504e7d | note | Responsibility - Project/Site Engineer
bbe50f61-d3c4-5511-aa18-ab14b871c188 | date | Date Completed:
27e62f33-67b3-4a06-b194-a8e411ae3e1d | checkpoint | 3.3 - Field Dry Density Tests
cdc7c6e8-1e6a-529e-97bc-53efc17c3e07 | note | Frequency - Every Lot
e8ac1bdc-5da4-5d11-b800-7accc6f38744 | note | Acceptance Criteria - The minimum frequency of field density tests shall be in accordance with VicRoads specification 304 and not less than:
f8a86f0d-f30f-5633-9938-125132b14c0b | note | — Base each lot is 5,000 m2 or one day's production
9ba38813-6e27-5309-a723-c5fe38e74a51 | note | — Sub base each lot is 10,000 m2 or one day's production
29ffaf5d-50c2-550f-bd41-e6a992fdc107 | note | ○ The minimum number of tests per lot shall be six.
82512a02-46dd-5a62-b1a9-ab3fa3e41bc7 | note | ○ Field Dry Density Results shall satisfy the specified values as per the drawings
5fddeb53-8bcc-5a4b-8315-5f68f7e3d7d8 | note | Reference Documents - Drawing 00201 P06
389bb620-2b7b-5d0c-bd0d-3d1f18533b29 | note | Inspection/Test Method - Test
971e9bf7-cc66-5bfb-9a37-8a5beb177d73 | note | Record of conformity - Test Report
cadb3b60-f591-5001-a9e3-8c5606a3564e | note | TP
787b94d6-a085-5a01-93c8-100da701ef4f | note | Responsibility - Project/Site Engineer
fb78378d-1580-5047-a493-61e0436bbf52 | date | Date Completed:
c1eb0201-3c55-43b3-a0f7-e6dd7bab4b06 | checkpoint | Final Inspection
44a5a93d-61ac-50a6-b543-eb82d98b3309 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
bc7c16c9-1ae2-535d-888b-ebd18d79dee2 | textbox | Print Name:
2e1954cc-fcbc-5220-9517-bf2d9ecd09b5 | textbox | Position:
5d72e439-78e0-562d-a885-48f1874f0582 | date | Work Completed On:
0e7daf17-1aaf-5a3a-aa87-924fc2553022 | date | Date:
3e43bf19-a27b-4b15-a6f5-53a48039f35c | checklist | FH-ZU2-QU-ITP034 - ALER 3 Electrical - Rev 0 | itp | ITP034 - ALER 3 Electrical
d5d92316-6109-4992-8e9a-38c4c46c8468 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
38b57148-e67f-4e2b-8629-7cb582c96acb | checkpoint | 1.1 - Check for correct documentation
5658a060-8ea0-5049-913b-39de37f7da2c | note | Frequency - Prior to commencing activity
401bbfea-2ad9-5bae-81aa-d66389207177 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
01ab8519-dc07-59d5-8c6d-ecc2b8a8f931 | note | – using the correct and complete set of drawings.
c1e0b9d0-f7b2-560c-811a-398b35cb493f | note | – all drawings are the latest revision.
27d3d264-69fc-5697-ad66-499159e9492e | note | Reference Documents - Drawings / Aconex Register
ab166e40-db8f-5bd1-bdfc-97d2e30f0753 | note | Inspection/Test Method - Verify
cc71632e-05c1-5e80-8b2c-34584f6004bd | note | Record of conformity - Drawings and drawing registers
c5b8f1de-9e69-534e-9344-e100c13df7cd | note | HP*
83836b1d-2fca-5064-a9de-f87e37d65d8b | note | Responsibility - Project Engineer / Site Engineer
18ed6aa1-7f66-5ad0-9961-aa767df86553 | date | Date Completed:
35770f3a-66a2-4e73-9c84-80a7bacfa7d4 | checkpoint | 1.2 - Implementation of all measures and controls
9ba7dc39-65c4-500b-8439-f3df76d023bc | note | Frequency - Prior to commencing activity
0292e8e1-825c-541b-adde-3e5d3de0dc29 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
aff256a9-2ed2-5b12-889b-25d3d57c8f6c | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
e07c6143-1009-52cc-83e0-5d5ff56a67e6 | note | Inspection/Test Method - Visual Inspection
e67aa557-43ea-5b99-ade0-4306a5f8c36a | note | Record of conformity - This ITP signed
c9434cc5-efb0-5fd7-95a8-93dc8a2b9fd2 | note | HP*
5be3e001-f374-54ac-9377-3ef182c3bebb | note | Responsibility - Project Engineer / Site Engineer
e9390c22-f442-5111-87fe-bc3d058eaa96 | date | Date Completed:
75ff4442-b649-4824-a296-dec2e1242af1 | checkpoint | 1.3 - Survey Checks
ac09f1a6-e80e-5b57-a3a5-7834aea1c261 | note | Frequency - Prior to commencing activity
3b338e97-bb4d-567d-ba4a-01bd59ce2a04 | note | Acceptance Criteria - Survey set out to be completed for all assets
34d980ab-1181-5233-a55a-a8ccc74c9f14 | note | Reference Documents - Drawings
3f6dd552-6d9e-5a2b-97f5-1af765b03f28 | note | Inspection/Test Method - Verify
ad72947a-f227-5a8a-b687-30bf07188c15 | note | Record of conformity - This ITP signed
0027da92-1409-5b66-94a7-474fd5b083e3 | note | HP*
2de7ae4c-4468-5472-9e0c-f2feff0e572d | note | Responsibility - Project Engineer / Site Engineer
fc686924-e9ea-5490-90bf-7814128ffa09 | date | Date Completed:
fe007a2b-a210-4ec4-80c4-fe46d2be7443 | checkpoint | 1.4 - Submission & approval of shop drawings
4f3a0965-449a-53d3-a953-ff342fd30b92 | note | Frequency - Prior to commencing activity
6bf94701-4d6a-5bca-a689-146ba06570fb | note | Acceptance Criteria - HOLD POINT
fbc73973-85cd-5ddb-9118-17fb547ed10f | note | ○ Submit shop drawings to the principal’s representative for approval prior to fabrication commencement. Items to include but not limited to:
1c667610-9fb0-5123-8c33-d72757cfd3fe | note | – MSB, DB-A, DB-C, DB-L&P, DB-EX1, DB-EX2, MSSB, DB-MGC, DB-GCP, DB-LBC, Luminaires, Light Control Systems, Lightning Protection and Earthing
183b145f-d612-5501-a720-1927bb77ca1f | note | Reference Documents - ZULU-BECA- 001-SPC-00005 C2100 Page 8, Drawings 030-3100 set, Approved Shop drawings
3baec183-37ce-53c4-b464-82f584b271e7 | note | Inspection/Test Method - Verify
0952a933-3e0a-5e85-b167-1866e786ab33 | note | Record of conformity - Aconex Reference
23197780-36a2-5a06-9c7c-0da45a694d61 | note | HP
ad645f2f-2a26-5a51-a1f2-5db9f7f6b38c | note | Responsibility - Project Engineer / Site Engineer /Principal’s Representative
bb5175b4-782f-52c9-93ae-5e89b57db612 | date | Date Completed:
f5f76f41-262d-48b4-8516-b4e4c5816372 | signoff | AUTHORITY HOLDPOINT
18212709-b96d-4083-951d-4dfbb4dadaf3 | checkpoint | 1.5 - Material Submissions
605fdd4a-df73-509a-b06e-130a3edb6342 | note | Frequency - Prior to commencing activity
3d440ef0-4c9d-5a58-8f67-cb41fe75644d | note | Acceptance Criteria - HOLD POINT
37faff1d-8bff-532d-9b93-e413a669ffc4 | note | ○ Items to include but not limited to:
70c8ebbd-ed31-5a9f-9b6a-d0213a8c47a2 | note | – Cables, control panels, luminaires, lighting control, switches, isolators, contactors, circuit breakers, earthing system, cable trays, ladders, etc. (all containment)
c89b29c1-60c6-5df7-8e64-ac3b7097c3e3 | note | Reference Documents - ZULU-BECA- 001-SPC-00005, AS/NZS 3000, Drawings 030-3100 set
48cfaaf0-3b47-512c-8d98-a512764b770f | note | Inspection/Test Method - Verify
ee599290-118c-5606-a495-1796373935e6 | note | Record of conformity - Aconex Reference
fae437c4-fecf-5167-a29f-90bb6a55eb44 | note | HP
c0c16721-3eba-51eb-8473-d5ea6afaa6ef | note | Responsibility - Project Engineer / Site Engineer /Principal’s Representative
190ee62a-c33a-53bc-abdf-e05506d4789d | date | Date Completed:
0196aa96-07a4-42b8-a08b-a3102cd3632d | signoff | AUTHORITY HOLDPOINT
09daa396-fa2d-4dce-9f50-c57c9e76738c | checkpoint | 1.6 - Temporary Works (if applicable)
511e3211-5617-5d7c-b6b8-b4249e34c0d7 | note | Frequency - Prior to commencing activity
de4e7cb6-d24c-54af-ad55-7af91f6390b2 | note | Acceptance Criteria - Submission and approval of the following documentation based on the Temporary Works Design Process Matrix.
429f0be9-4672-5008-8446-3d06dcd46116 | note | Reference Documents - ZULU-BECA- 001-SPC-00005, Temporary Works Design Process Matrix, Drawings 030-3100 set
70570813-d901-583e-beff-62e85a4c804f | note | Inspection/Test Method - Verify
d13b7691-260b-5ec8-9660-196402a36f72 | note | Record of conformity - As defined by the Temporary Works Design Process Matrix (where applicable)
7942268e-6bff-5c37-8ee5-45bf836a4013 | note | HP*
9dd5863d-cfcf-5dbb-9303-4079f6f68a5e | note | Responsibility - Project Engineer / Site Engineer
a57b3906-0e05-530b-bfdb-5edddacf8070 | date | Date Completed:
1419ee79-1165-4bb2-ab79-ebcbc38fc132 | checkpoint | 1.7 - Off-site Inspections
959f33d0-7c0c-5daa-88fc-39cd42be5f82 | note | Frequency - Each Lot
22d91d8a-347a-5652-967e-b757cf73d954 | note | Acceptance Criteria - WITNESS POINT
5324443d-e36a-560c-b098-150180397503 | note | ○ Inspection and attendance on site for Factory Acceptance Testing for:
721a0132-b01d-5846-a5d3-23f20fe5c06b | note | – Switchboards
e0e82dee-1aad-5e26-989c-0d2343167345 | note | – Distribution Boards
4b49278f-bac6-5a9b-8891-d9d9887410c9 | note | ○ Following these inspections FAT testing shall be submitted.
d6e5a86a-032a-5438-8480-88f31ea5c98d | note | Reference Documents - ZULU-BECA- 001-SPC-00005 C2121.20, AS/NZS 3000, Drawings 030-3100 set
3baa812c-1f40-5781-9638-94ae9759eba4 | note | Inspection/Test Method - Verify
3965e0f2-1885-5d17-8805-c66d2f7a9b16 | note | Record of conformity - This ITP Signed, Factory Acceptance Tests
3d7832d5-9669-5be9-8119-f6187a58cd53 | note | WP TP
548cd5c0-e9cd-597a-a4d4-55a03528f9c7 | note | Responsibility - Project Engineer / Site Engineer /Principal’s Representative
37c771c8-5242-5cd0-b7c3-3254cfbfaa90 | date | Date Completed:
e7c2eadd-a130-4eeb-b45b-756c5f8163d6 | checkpoint | 1.8 - Certificates of Compliance (prior to delivery to onsite)
14755f68-0211-5f53-bfb7-74c758a57a11 | note | Frequency - Each Lot
393c41b7-2d26-5819-bca6-a36e99786f84 | note | Acceptance Criteria - Provide Suppliers Certificate of Compliance and Spatial Certificate of Compliance for
21a1c3a8-57c8-5d6c-8516-2006a20ab1dd | note | ○ Switchboards
ecdeea41-70fb-589b-96a3-06939e75d7fe | note | ○ Distribution Boards
898b246e-a49e-5dc8-b07e-f955e6e9623f | note | ○ Control Systems
d2a851d7-ce72-54be-90bb-844bfb46cd3c | note | ○ Power Control
48507762-565b-539d-890d-fa121f34d47e | note | ○ Switchgear
30164df9-d4ea-5ab7-b5ce-0f1b18cd9b29 | note | ○ Cables
1872a3dd-a9ed-5740-988c-71320b17138e | note | Reference Documents - ZULU-BECA-001-SPC-00005 C2100.3, AS/NZS 3000, Drawings 030-3100 set
2b5388b1-3953-5c10-a7e5-c1c01475b055 | note | Inspection/Test Method - Verify
e8e8a060-bc14-5286-a376-34896c8705d8 | note | Record of conformity - Supplier’s Certificate of Compliance, Spatial Certificate of Compliance (where required)
a842663d-e9bd-5c24-bc30-295ded4f1a60 | note | HP
81233438-7722-5682-9806-6ed11e2b4df0 | note | Responsibility - Project Engineer / Site Engineer /Principal’s Representative
415e1894-7af2-510d-ba59-7e58d4664ddc | date | Date Completed:
ea539fee-74a1-4dc2-911e-9efd5ea531ab | signoff | AUTHORITY HOLDPOINT
0eaa1c40-f29e-450e-ae63-1bbb95ea06e6 | section | 2.0 - Construction
26f08c8a-a997-4632-9998-f89f89c41670 | checkpoint | 2.01 - Delivery of Materials to site
81033c6f-366d-5152-8a27-ced8ecf4bd53 | note | Frequency - Each Lot
44b54af9-0177-5555-acf9-bdbc042fb93e | note | Acceptance Criteria - Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site.
6cc4a4ab-9136-5385-85dc-1fe54e1a7689 | note | ○ Identify any damage/defects prior to unloading of the material.
0aa4640e-606a-5909-b265-331b86c1ffb8 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
ab395022-b5da-5634-b6cb-30bd802e086a | note | Inspection/Test Method - Visual Inspection
21a344e7-4149-5b48-8549-60d28cec7537 | note | Record of conformity - This ITP Signed, Materials Inspection Checklist on ConQA
bcb266f6-ba37-57fb-bbd0-4cc6b6820641 | note | IP
654128f9-cc8f-55f5-beee-06377476e0f6 | note | Responsibility - Project Engineer / Site Engineer
0bb5312f-63cd-5a8e-9ac0-d943c9f8e0f9 | date | Date Completed:
5aaaa8da-0db9-4c0a-8c2e-36e3300f76c2 | checkpoint | 2.2 - Conduit / Containment Installation – Walls and Ceilings
371be01f-9d83-5888-a26c-5dd4d0d23fdd | note | Frequency - Each Lot
5278d628-7aa9-52b7-81c1-997b5773d0c3 | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
37d971c7-a656-576c-8ef2-90030d46d60e | note | ○ Fixings secured in walls/ceilings.
8d6e10ce-0264-553a-a23b-dd24a6251f99 | note | ○ Conduits, bends, and junction boxes
29b04621-9910-5212-9f53-91df37d7b721 | note | ○ Draw wires installed
9a80988d-241a-510f-a8b1-5c1c82d4fed6 | note | ○ Fire-stopping and fire protection
891231c5-a654-5bfc-987b-f96ca39c618e | note | Reference Documents - ZULU-BECA-001-SPC-00005, AS/NZS 3000, Drawings 030-3100 set
d1a2fb05-dc2f-5c56-918b-fd4e0e581c4e | note | Inspection/Test Method - Visual Inspection
d69aa4e5-b2aa-5d20-a829-1970959322c2 | note | Record of conformity - This ITP Signed Building Eng ITC
3d9e315b-964d-5e95-b9ff-f820edf57c74 | note | IP
c512fedb-62e0-5700-9d48-1dd6ea6fe638 | note | Responsibility - Project Engineer / Site Engineer
70316113-e459-55a6-b41f-41b681297866 | date | Date Completed:
c500226a-52bc-4e7e-8c91-a9b83d483ed2 | checkpoint | 2.3 - MSB, LV Distribution Boards, and Control Panels
9f02c738-8af6-5d1c-9b9e-0005c79b7e27 | note | Frequency - Each Lot
011feaf1-a82d-5143-8995-d93e8133739c | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
f9b4a245-ac00-5177-a576-fa7095dc5581 | note | ○ Size, colour, location
2663cd3a-206b-52ee-8397-65fe8f8f3b89 | note | ○ Plinth (if required)
8399bc9c-3122-58b7-a36d-28dbb5d0adeb | note | ○ Secure and anchored.
cbc026a2-3170-5fc3-9e1e-86d5c236ccc0 | note | ○ Labels
db7caf65-d17a-564a-bb66-4e91bc61d37f | note | ○ Switchgear and M.E.N Link
c80d7982-8dc0-5fef-b44f-9a1fbc5f7d16 | note | ○ Tightness & alignment
767e13c1-d278-5202-a7b2-082ee00c38dc | note | ○ All wiring tidy and neat
7a2edff9-6467-5a78-8203-9eec4b43e1fe | note | Verify and confirm the following tests (not limited to):
9ec56de6-a96f-52b8-805e-be80eb091806 | note | ○ Polarity Check
5bbe49be-6a8c-5c48-9cfc-33a316773387 | note | ○ Cable Loop Resistance (Ohms)
610ee532-1004-5ab1-aaca-b5ef313217c1 | note | ○ Insulation Resistance (Core-Core& Core to Earth)
8f81af0e-f701-5cf0-8733-efaf3dcbd633 | note | Reference Documents - ZULU-BECA- 001-SPC-00005, AS/NZS 3000, Drawings 030-3100 set
c4b42bdf-16b7-5efd-a7f8-ff94c05dc09f | note | Inspection/Test Method - Visual Inspection
1ea5e483-c833-5a06-86f0-9359ed43134a | note | Record of conformity - This ITP Signed, Building Engineering ITP
b4614707-69ea-51f1-942c-be6a50fc8891 | note | IP
d953e9dc-8d5a-538e-88c8-40314a0f1637 | note | Responsibility - Project Engineer / Site Engineer
894dec6c-aff8-5dc7-a5e6-e41f3488cecd | date | Date Completed:
32db58e2-86c0-4f19-ac26-b0c524688c47 | checkpoint | 2.4 - Cable Tray & Cable Tray Support Post Installation (Comms, Electrical and AGL)
232f5ce7-b0af-5733-98ee-a48325582e46 | note | Frequency - Each Lot
3903c6e9-7598-5bc5-a569-5f88494e1916 | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
ec2fe34e-5893-5c57-ac29-ae8f74d44715 | note | ○ (i) Provide cable support system throughout, including cable trays (both power and Comms/ELV), cable ladders, trunking, conduits and catenary wire system.
fff0e6d1-3472-5f9b-8966-d96ae37376e7 | note | ○ (ii) External ducts and draw pits for the incoming LV supply shall be provided by the Civils Trade. Ducts connected between building and external pits to be of flexible type and be able to withstand building movement.
5830933b-d409-54c2-9138-ee35b3ee2cce | note | ○ (iii) Provide cast-in conduits with draw wires as required.
8e9a97c2-ecac-5b2c-9991-2fc65750168c | note | ○ (iv) All safety services shall be installed on fire rated containment. Where fire rated cable share containment with general services reticulation, all containment and fixings shall be selected and installed to suit the requirements of the safety services installation.
a96b83e7-ba77-503f-b9d1-0f285490d936 | note | Reference Documents - ZULU-BECA- 001-SPC-00005-C2100, C2112 AS/NZS 3000, Drawings 030-3100 set
a1a0b256-e602-521d-b96b-51ff4b8d635d | note | Inspection/Test Method - Visual Inspection
af59238f-500c-5261-a769-655d89fd8226 | note | Record of conformity - This ITP Signed Building Eng ITC
faa47499-9644-5877-83e2-5b835f6a14ac | note | IP
50b109a3-6638-5009-9191-eb8696e8cab2 | note | Responsibility - Project Engineer / Site Engineer
2df11083-58cf-5522-a245-c0bad3c63677 | date | Date Completed:
36ed3683-07a9-40b6-97da-0fd8b1c88ac0 | checkpoint | 2.5 - Cabling – Mains, Submains,
b8e1f460-8310-5ac2-9909-b63c5e7aa542 | note | Frequency - Each Lot
d17bcfa3-1f91-5445-b973-8b7e28283668 | note | Acceptance Criteria - Confirm cabling is constructed in accordance with IFC design and AS/NZS 3000.
dc82bfd0-f20d-5c66-8f97-3c7246050c00 | note | Verify and confirm the following tests (not limited to):
04fd8258-a89a-5d61-9e8e-aaac53e67770 | note | ○ Polarity Check
35403573-3df2-5d7c-a571-0302cb3f55b5 | note | ○ Cable Loop Resistance (Ohms)
d21bef7f-9e49-5a7f-bc6c-6f3d2b0f0809 | note | ○ Insulation Resistance (Core-Core& Core to Earth)
5c2630b1-8f19-55d1-9fd3-3e8d85376c5d | note | Reference Documents - ZULU-BECA- 001-SPC-00005 C2111.5, AS/NZS 3000, Drawings 030-3100 set
80451fff-607c-5d32-8b26-83d2b3f78e54 | note | Inspection/Test Method - Visual Inspection
25b813ac-204e-5819-8879-3b58fd6533da | note | Record of conformity - This ITP Signed Building Eng ITP
78cf5392-6745-5705-b49d-90b3af811b91 | note | IP
78f505c7-012e-55f4-ae81-7f962fcc822f | note | Responsibility - Project Engineer / Site Engineer
a29547ff-6e4c-5205-9da2-e6503c630ac4 | date | Date Completed:
28a1f69f-14ca-46ae-a89e-3cf126a56cd0 | checkpoint | 2.6 - Emergency Lighting and Illuminated Exit Sign Installation
d529422e-41cb-5c31-87a2-f3a9c37778dd | note | Frequency - Each Lot
07b521d1-579e-5171-af14-024b2486eb64 | note | Acceptance Criteria - Confirm cabling is constructed in accordance with IFC design and AS/NZS 3000 & AS/NZS 2293
94d8bdfe-b9ff-5ebf-94ca-b16fce970b13 | note | Verify and confirm the following tests (not limited to):
55ab9c1a-03fc-50bb-983c-5ac86577fdb4 | note | ○ Polarity Check
11be10e3-79b1-5759-b128-e3e32fac1e89 | note | ○ Cable Loop Resistance (Ohms)
45384a17-7043-5f3d-9b43-0001945daa56 | note | ○ Insulation Resistance (Core-Core& Core to Earth)
64f7c03b-6a47-5919-bed4-5de7b63f3c97 | note | All Emergency luminaires, signs and exits labelled as per ALER 3 Emergency Lighting Schedule.
5b5a5f07-0050-5e84-aa91-2900c91b3a51 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 C2132, Drawings 030-3100 set, AS/NZS 3000
5b52a66e-e420-58b0-9948-978d9456a04b | note | Inspection/Test Method - Visual Inspection
43a0fdf4-91bd-5006-ab71-34f2ca680b24 | note | Record of conformity - This ITP Signed Building Eng ITP
8b4bf88c-022c-5974-90b8-8e15635c8b3a | note | IP
2c502d7b-397d-5a29-af98-dc3490593e83 | note | Responsibility - Project Engineer / Site Engineer
36436b19-a68b-50ed-b515-df85bad49a93 | date | Date Completed:
4556d435-1fec-4cf8-8930-78e8983baa75 | checkpoint | 2.7 - Light Fitting and Light Control Installation. (External/Internal Luminaires, PIRs)
9f538717-0301-571d-910d-8f2149cceb97 | note | Frequency - Each Lot
885b71a6-87b5-5c37-a646-3093b331a3db | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
bb7ae5ef-0b55-5639-b328-688f365e8d84 | note | – Type, size, colour, quantities, location
2eec8108-ecd4-5766-804c-1ac8df5231b1 | note | – Secure
a8041118-d0fd-5469-99da-18c9408af6af | note | ○ Verify and confirm the following tests (not limited to):
a108e84f-2489-57a1-b2a5-2be2628d7294 | note | – Polarity Check
378f90ca-0790-5a33-be1c-88cd1668989b | note | – Cable Loop Resistance (Ohms)
2b55a8c1-66b1-5fb5-94d9-9eb0dd0fefc6 | note | – Insulation Resistance (Core-Core& Core to Earth)
d9393d94-1bc9-5cd9-aa7d-7136ace4a7b7 | note | ○ DALI control and lighting devices has been provided where dimming or time scheduling is required.
ef8003eb-749d-599a-9625-5d6672322bcc | note | ○ External lighting must meet spill requirements of Part 139 (Aerodromes) MOS 2019 (i.e. downward facing so no spill light above the horizontal) and must not cause glare or distraction to pilots during aircraft movements.
4c3f774a-d7ea-5ee3-8b89-4fafe836044e | note | Reference Documents - ZULU-BECA- 001-SPC-00005 C2133 C2130, Drawings 030-3100 set, AS/NZS 1680.3, AS/NZS 3000 MOS 2019 – Part 139
24db8cc2-0301-5276-ad8e-faa58553260f | note | Inspection/Test Method - Visual Inspection
84f98c86-4ede-595d-a6ac-84550048101a | note | Record of conformity - This ITP Signed Building Eng ITP
ba0067de-a75f-5f0e-a9da-d19592a3c361 | note | IP
65083376-e2a0-562c-a550-f7bf2eb48288 | note | Responsibility - Project Engineer / Site Engineer
1714d631-f2a8-597c-a786-4b613bbfde1b | date | Date Completed:
e77c058a-7d15-4744-b8bd-edd3de66f978 | checkpoint | 2.8 - GPOs / Data / Antenna outlets & WAPs
06fe905d-8a6b-5faa-954a-56da364ab755 | note | Frequency - Each Lot
9daebde5-94f9-52dc-aef3-14a3bfcf3f9d | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
9999cd6c-4c69-5ad8-a91d-3acd4382fe2d | note | ○ Quantities& location
5c4b952a-47f4-52b7-ba64-8fcb7e6fa182 | note | ○ Secure
dbd1caa1-6141-5305-b943-7a2a3c458602 | note | ○ Fitted off and level.
f007aecb-bcff-5cf6-bb18-262f92b787e8 | note | Confirm mounting height of outlets on site with the Superintendent. Generally, and unless otherwise shown on the drawings, outlets shall be mounted at:
d0b277bc-6b75-59bb-900b-560ae6b379c9 | note | ○ 300 mm above floor level or 200mm above benches in commercial areas.
0b8d5f6a-7d2a-56d7-9aba-ed8c1521163a | note | ○ 1400 mm above floor level in plant and industrial areas.
8f38d648-451f-5449-8935-31deeddc1a1f | note | Reference Documents - ZULU-BECA- 001-SPC-00005- C2141, Drawings 030-3100 set, AS/NZS 3000, AS/ACIF S009:2006
3ffa6c54-35e4-5448-8f60-f35590c87754 | note | Inspection/Test Method - Visual Inspection
883156b5-155f-5180-be11-af7d7fb9e951 | note | Record of conformity - This ITP Signed Building Eng ITP
50590047-7d60-5c29-a8ed-c7d9d8b1138b | note | IP
62daddc7-30df-53bb-9a42-3db18efd652a | note | Responsibility - Project Engineer / Site Engineer
8591ff9a-89b0-55a8-b98f-d3150c46e38c | date | Date Completed:
8bedeeb2-9c05-40c0-ac34-719ead38078d | checkpoint | 2.9 - Access Control systems Installation (Security Panel, Card Readers, Mag locks, Reed switches, REX, UPS)
82f053c4-3cc4-57dd-9cc1-8720d8bcf430 | note | Frequency - Each Lot
0405ee2c-dc5c-5a1c-8bb6-2ee058ae7d9a | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
7c2bb04e-31e8-5cfd-adb9-40bcfa2ae6d0 | note | – Size, colour, quantities, location
91a2e6e9-a385-525e-962d-a2b48d9aa346 | note | – Secure
a59f9700-dfdd-55b1-bd3c-1f5c27387211 | note | – Fitted off and level.
431da557-6b46-5956-9c22-c6b2a17886a3 | note | ○ Check that the card reader is installed:
39db7b42-e6a5-525e-8139-c28f46225a13 | note | a) at 1000mm above floor level; and
13e0434b-0b35-524e-9135-38e3d1f4332d | note | b) on the access side of the door, on the mullion or within 600mm of the door / egress area as applicable.
5436eb1a-9c8f-570f-b634-73271220b2de | note | ○ Verify battery and/or UPS capacity can operate normally for a duration of Eight (8) hours.
c7938b37-f825-557e-8143-88e28bf5246d | note | Reference Documents - ZULU-BECA- 001-SPC-00005 C2701/C2703, Drawings 030-3100 set, AS/NZS 3000, AS/NZS 2293 AS/ACIF S009:2006
f37e8910-4d1c-5b67-a37b-53ebea629698 | note | Inspection/Test Method - Visual Inspection
58aeb3d3-f4da-5d1a-9851-b29d1b51391a | note | Record of conformity - This ITP Signed Building Eng ITP
b0715686-cbda-530e-9afb-51cb743c63bf | note | IP
25d9540c-bbeb-566e-8aca-c8f901468e63 | note | Responsibility - Project Engineer / Site Engineer
77c5b9df-8d44-51ff-a680-34f0e2df88c5 | date | Date Completed:
bc09811a-dc7d-4ff6-b947-425f3ba92118 | checkpoint | 2.10 - CCTV Systems (CCTV Racks, CCTV Cameras, Archivers & Monitors)
6832b1a6-bc1b-56d6-bcef-fc43dc90c707 | note | Frequency - Each Lot
dd9cf5c8-5f09-53e6-8984-51e69daefcba | note | Acceptance Criteria - Verify that CCTV rack installation quality are satisfactory as follows:
599e394f-06ec-5d75-a5bc-2930ad270036 | note | – Equipment layout per IFC layout drawing.
7702b35e-5024-5a58-a18a-4afc8517be3f | note | – Equipment are securely fastened.
5371c63f-6076-58ac-9747-84967d30015a | note | – Connection & terminations are securely fastened.
7099a4ad-c7ce-5f3a-8280-3c4d6061a1ca | note | – Racks (internal and external surfaces) are clean and free from any drilling dust, cable tie or cable off cuts and other debris.
38613189-bf39-5fd4-8576-7de0fe61c8c1 | note | – Verify that all cables, patch cords, terminations and equipment are correctly labelled in accordance with the Cable Schedule, Patch Record and Label Schedules as well as the IFC Drawings.
6f2b17ab-9d44-5d25-9393-d095022a1d2d | note | ○ Verify that all cameras and mounting brackets are installed as per the camera coverage plans and camera schedule.
cad0da00-9bcb-5e51-a9b8-511b6fcb787f | note | Reference Documents - ZULU-BECA- 001-SPC-00005 C2705, Drawings 030-3100 set, AS/NZS 3000 AS/ACIF S009:2006
3a3dd8c9-d7b2-5c05-a7c4-189bbd991a21 | note | Inspection/Test Method - Visual Inspection
8aa06323-6e8d-54c4-ae84-e2520712781d | note | Record of conformity - This ITP Signed Building Eng ITP
e225217f-ec73-5407-8f44-a3cf5d1e4083 | note | IP
6a64e9d2-ba60-53f5-b864-aa2c4e3072f9 | note | Responsibility - Project Engineer / Site Engineer
01a7d690-2dc2-5632-a45e-4ce6a8c6b334 | date | Date Completed:
0079f718-a6a0-4ef2-a1d5-55bdbea3674c | checkpoint | 2.11 - Lightning Protection and Earthing Installation
33c3fd1b-7308-586d-b43a-679820818b9e | note | Frequency - Each Lot
aff08d66-9bc1-5ea1-8b75-69f17d937a6c | note | Acceptance Criteria - The external lighting protection system shall be constructed as per AS/NZS 1768 and APAM standards
9ef2c658-837a-5c70-967a-97ead3a646ec | note | ○ Structural steelwork, cable trunking, metallic cable support systems, metal equipment and pipework shall be bonded as required by the regulations, AS/NZS 3000.
f3e229d3-75e1-53bf-acf2-f69ca067c566 | note | ○ Provide a main earth bar in the main switch room in a convenient location at 300 mm above finished floor level. Each bar shall be copper and be bonded to two local building earth plates using single core 70 mm2 green PVC sheathed stranded copper cable.
19b29550-eb78-51ca-9721-b73c377e7a97 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 C2160 / C2161, Drawings 030-3100 set, AS/NZS 1768, APAM standards, AS/NZS 3000
029ef79a-6c90-5056-9c8a-61f211be7b1b | note | Inspection/Test Method - Visual Inspection
57631363-4330-5851-bb61-000691c123c2 | note | Record of conformity - This ITP Signed Building Eng ITP
a221b49a-ecaa-5155-8597-e5234b3b8dd6 | note | IP
094b7d4e-abdb-5395-8713-66b4e2dde256 | note | Responsibility - Project Engineer / Site Engineer
8f613518-89a6-5759-9afb-e3af430dced2 | date | Date Completed:
eeb786f8-7008-4a9e-a24a-af0a77afe55a | checkpoint | 2.12 - Existing LV Services Migration
bfe5af9d-8ce8-5f3a-9410-3915b8648aec | note | Frequency - Each Lot
2c0fbc11-5251-5b8a-9dac-fd5e6b6ba065 | note | Acceptance Criteria - The following existing services have been migrated to the new ALER3 MSB:
65b50e2a-f9e9-5ac8-bff7-ce566032569e | note | ○ Building 18 LV Supply
a0ed4c28-ed76-5cc7-a243-90cca0b4e5ea | note | ○ MISC LV supply
5f5e6d89-e319-56b5-b09e-4f17ced18a2d | note | ○ VOR LV supply
9ba5f177-f093-5586-894b-1258b7ecc4b6 | note | ○ IWDI-1 and IWDI-2 LV supply
b439281e-0c7b-59b2-91f8-196c8d157295 | note | ○ SFAL LV supply
805df7a2-e21a-5065-9add-d0455ca87ad2 | note | ○ RAF LV supply
4ab098b5-d530-5ca2-a766-d7de84bc2355 | note | ○ DME LV supply
15825907-74dd-537d-bf24-e27893bab4ed | note | Reference Documents - ZULU-BECA- 001-SPC-00005 C2160 / C2100, Drawings 030-3100 set, APAM standards, AS/NZS 3000
b900af5c-1bf9-5524-94fb-7d0a19d12361 | note | Inspection/Test Method - Visual Inspection
f6517485-5a1c-5dc9-b164-644e0dffe8ba | note | Record of conformity - This ITP Signed Building Eng ITP
163bf6f9-5ea7-55f7-ab96-68d3196737b3 | note | HP*
ba7730d1-bce0-5df7-9313-b99814b46890 | note | Responsibility - Project Engineer / Site Engineer
8df24122-3251-5b6e-9ff6-8f8bd5c11a1a | date | Date Completed:
d674d09a-f500-40fa-838f-23c8e2b0de87 | checkpoint | 2.13 - Survey As Built
78afa53b-93ac-5ac7-b957-e150c36b37d7 | note | Frequency - Prior to Covering Services
4c490ce7-6c3c-588c-baa3-2cf18a773ef2 | note | Acceptance Criteria - Survey to pick up services prior to covering
3e4d337b-f162-5b03-9422-0e010ea14c9c | note | Reference Documents - FH QMP
2e8a3c17-b0c2-59db-beba-a530aba0804a | note | Inspection/Test Method - Verify
7d16fb59-612c-5b59-afd2-7526fc2ec330 | note | Record of conformity - Survey
5c8378ed-ca36-5d75-a79d-09ba801ad54f | note | HP*
2345f8e3-cd97-5265-8b39-c899346c82f3 | note | Responsibility - Project Engineer / Site Engineer /Surveyor
c3b2c0d5-5e87-5f8d-8caa-c32a550f0899 | date | Date Completed:
1b1d4e0d-04a7-495e-8734-89ac811def02 | checkpoint | Final Inspection
36f80794-5a76-52ef-aad8-98316102c8f4 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
c18e7ef1-dcca-5e42-9191-8af72a7f9b58 | textbox | Print Name:
654029f7-7259-52a2-80ea-dc3db5ad3c81 | textbox | Position:
007ec203-1c32-58cd-a251-b889e74cef88 | date | Work Completed On:
679b6bce-47f4-5cf4-89ad-8d0d10932831 | date | Date:
04c0f8a4-ad51-480d-97c7-63aba4ee9724 | checklist | FH-ZU2-QU-ITP035 - ALER 3 Plumbing - Rev 0 | itp | ITP035 - ALER 3 Plumbing
6f953a84-e7cf-432d-8b90-27465bff7f51 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b5dd0516-c611-42de-a872-54371fe7c2a5 | checkpoint | 1.1 - Check for correct documentation
02c7e387-0538-5328-b15a-3b1762f4d64c | note | Frequency - Prior to commencing activity
63ce54ce-2f98-5153-b433-7e1c96888bed | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
62db98c5-e1de-5d50-bcdf-86d0c67665e8 | note | — using the correct and complete set of drawings.
fbfd5095-aaf0-5c69-a81f-decf8bbcf240 | note | — all drawings are the latest revision.
18908c46-f49f-5b4a-9f1b-53ba64a09b24 | note | Reference Documents - Drawings / Aconex Register
1a73b37d-9cf9-5870-99be-aef52c11fa24 | note | Inspection/Test Method - Verify
94dd70e6-fdf9-5b7f-baec-61fd56c50f93 | note | Record of conformity - Drawings and drawing registers
fb4c8ad0-9414-5815-8ed2-479a4950a3a2 | note | HP*
044a68dd-51f3-58b7-9926-15f00abda4b8 | note | Responsibility - Project Engineer
15407532-df65-575b-a136-f865b0e05c03 | date | Date Completed:
6134959d-c9b0-4a42-ac75-9f16f1eee8b7 | checkpoint | 1.2 - Implementation of all measures and controls
216ce1d4-2614-5ee3-a737-ff59a0494d35 | note | Frequency - Prior to commencing activity
9becfb2a-cc71-5455-b808-05f8a0ad4c1c | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
0425fc1f-925a-59b7-8966-032324f0d68f | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
01aee0b1-35ce-5f72-a10b-381fb5e272a8 | note | Inspection/Test Method - Visual inspection
efb093be-7025-50ae-bc04-b0e2274f3d5f | note | Record of conformity - This ITP signed
0de2cb22-6ace-5d6d-99a2-0d4c10d88d21 | note | HP*
6c9ed1b9-4862-55d2-b92a-f93562b6163d | note | Responsibility - Project Engineer
b7840eb2-9195-543d-9447-fa067287abd5 | date | Date Completed:
95ae6ba7-69d0-4f7b-84e0-90fd2276da8e | checkpoint | 1.3 - Survey Checks
ce350b45-87aa-57b6-a683-1f5a1c122161 | note | Frequency - Prior to commencing activity
1e37b79d-64be-5916-857e-039330c6906b | note | Acceptance Criteria - Survey set out to be completed for all assets
acb700bd-2e0d-54e5-99bf-d4121341b5f7 | note | Reference Documents - Drawings
2d247369-12c2-5fef-89e4-835525007161 | note | Inspection/Test Method - Verify
bc1981ce-d84b-5033-b155-72af1bd95638 | note | Record of conformity - This ITP signed
76b5b83c-c6dd-54c0-8f0a-9907d1dce6cc | note | HP*
8a716d68-9c37-51a3-9508-db59bb86a205 | note | Responsibility - Project Engineer / Surveyor
2237321d-fbd8-51ab-9957-881217ddf133 | date | Date Completed:
e11fb116-52d1-448f-b8ef-0c4f0d9d9f5f | checkpoint | 1.4 - Submission & approval of shop drawings
463349bb-2080-5560-b4bb-31cb68d81f46 | note | Frequency - Prior to commencing activity
f99821db-fae5-598d-b321-58b447e82b38 | note | Acceptance Criteria - HOLD POINT
9fa18167-496a-5b2a-8f9d-e0d13925022d | note | ○ Submit shop drawings to the principal’s representative for approval prior to fabrication commencement.
5bca4a3f-0688-54e1-b814-4234c89b7456 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings, Shop drawings
d8b469c4-768c-5c58-b4d9-08891230e4cf | note | Inspection/Test Method - Verify
a3c934af-2937-5cd0-8484-88884f613d07 | note | Record of conformity - Aconex Reference
534dc057-8e3a-5432-83d9-204ddee6a83d | note | HP
7b88337d-4abe-5203-8380-6b559aad1f00 | note | Responsibility - Project Engineer / Principals Representative
d94d74de-b69f-55c0-9ed2-922e36446d22 | date | Date Completed:
00c3035f-0f64-4b2d-8bc9-f22d2b74241d | signoff | AUTHORITY HOLDPOINT
556cf7ee-55fb-43db-92bc-9cf1e3a573bb | checkpoint | 1.5 - Material Submissions
24065b0d-ca16-54d9-b396-1780e07ef29d | note | Frequency - Prior to commencing activity
08c52f40-210b-5927-9785-c7e1488b57e7 | note | Acceptance Criteria - HOLD POINT
f126f031-616e-5493-a44c-f00f74733502 | note | ○ Items to include but not limited to:
8fcde12a-b1f6-587c-ad7c-fabdb5993cbb | note | — Refer to materials register and list items
82627934-63fd-5328-85e1-5888f0f2a07e | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
13fac967-0c45-56db-a673-bdcb21b73335 | note | Inspection/Test Method - Verify
b1ac039b-c745-58c8-81be-10aaa317e331 | note | Record of conformity - Aconex Reference
7b3e96a6-b4cc-5849-990b-c515869a6d7f | note | HP
ac8186e3-32ac-5a1a-8284-eda29dfcfa40 | note | Responsibility - Project Engineer / Principals Representative
d9a93dcd-526e-5976-af68-7e4ecbb4da56 | date | Date Completed:
58c74dc5-8da8-4d1e-8949-0a512634a21f | signoff | AUTHORITY HOLDPOINT
ccef563b-ea2c-44b9-ae52-5874a49060db | checkpoint | 1.6 - Temporary Works
e09b6dd5-cb75-5397-8e02-000b8b95a771 | note | Frequency - Prior to commencing activity
b071804f-7571-54db-be99-1929cae55540 | note | Acceptance Criteria - Submission and approval of the following documentation (not limited to):
df9be4e3-35aa-542f-9781-885dabdfb939 | note | — Certification of Lifting Points
a2fb32a3-5dd7-5ba1-8bfb-603c15997764 | note | — Lift Plan
50da25a0-5f5d-509e-b1b1-e29e8242087b | note | — Certification of Ground Platform for Lift
4033ee20-cd01-558d-87f7-cf360f89601a | note | — Lifting inserts
bc2836b0-7063-5200-85ce-4abd7c14e979 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
6d413e64-98cf-5529-8280-f6cab8f95b36 | note | Inspection/Test Method - Verify
de2dd5c9-8a9c-5db9-802f-a743f16a1b04 | note | Record of conformity - Temporary Works Geo Report
0b19e98b-e5e9-5ce5-bed8-ecd0774c0a4e | note | HP*
9f2a9364-b267-539f-96ff-218840aa8539 | note | Responsibility - Project Engineer
e7f1a390-5a08-5c22-85dc-80b22084bb36 | date | Date Completed:
9f98d6b1-156a-4060-9773-5031d1e69eb0 | checkpoint | 1.7 - Certificates of Compliance
e80280b7-0577-5ced-b8ef-b7a3eb246147 | note | Frequency - Each Lot
422b7760-f524-5387-8f58-c7a7bd303bcc | note | Acceptance Criteria - Provide Suppliers Certificate of Compliance and Spatial Certificate of Compliance for
a30ab8a6-2a22-5ee5-a95f-00001c9c72d4 | note | ○ pumps, hot water units, and valves.
684de616-28fd-5436-b4fa-85cce0b66cfe | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings C1900.6
14efd4a2-c6de-534c-8e77-56afb3400e4f | note | Inspection/Test Method - Verify
55e80a06-97be-5404-8896-aa75787cfe0d | note | Record of conformity - Supplier’s Certificate of Compliance, Spatial Certificate of Compliance (where required)
1c32e1e2-3cec-522a-9d59-1c025162913c | note | HP*
fea09bc1-50df-5c64-9678-c8689d8918b5 | note | Responsibility -
4471ed57-7e91-572e-be0b-5f91ba86625a | date | Date Completed:
4160d44b-2a0e-4d2a-a1d7-4491c8ef93ea | section | 2.0 - Construction
73b9ef4f-3d09-4a5d-8adb-ac868a1df3c4 | checkpoint | 2.10 - Delivery of Materials to site
46b86071-1c81-5e51-a5b1-aa325a159938 | note | Frequency - Each Lot
d8b04172-7c03-5d15-9844-46a5188e48e7 | note | Acceptance Criteria - Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site.
7601d5b8-1433-54e1-8e22-123ec2ac4aa0 | note | ○ Identify any damage/defects prior to unloading of the material.
37864b01-9996-5aa5-85a0-afe2cc1084d1 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
475df8f3-8028-51d7-8b42-bb7e778c6bc9 | note | Inspection/Test Method - Visual Inspection
57fc66a5-66e9-564f-a927-0a5f0a5d95f8 | note | Record of conformity - This ITP Signed, Materials Inspection Checklist on Conqa
359fdf01-b817-5f37-b3ac-1e0f90009940 | note | IP
35d5425a-4564-58bf-91c6-1ec01fed0850 | note | Responsibility - Project Engineer / Site Engineer
409b44b3-9226-5b54-8c75-9995bcdbd321 | date | Date Completed:
e31e786f-47ef-415c-ac6a-70cfdf4d5b55 | checkpoint | 2.11 - Installation – Cold Water System
17109bb1-cecc-58be-98d4-155525e1e39b | note | Frequency - Each Lot
3d1c53a1-3b05-53d7-90c5-2ffe4894c552 | note | Acceptance Criteria - Verify pressure and flow, installation of water meter assembly, isolation valves, and boosting/reducing systems.
82c94806-b6a1-504b-a043-2ed4c95291ee | note | Reference Documents - ZULU-BECA- 001-SPC-00005, C1700.2.2(a), Drawings, AS/NZS 3500.1
6593f8e6-f69f-5e23-9371-23ec96dce0de | note | Inspection/Test Method - Visual Inspection
71f47f8e-8d9c-59c9-ab48-8d918228b4a4 | note | Record of conformity - This ITP Signed Building Eng ITP
12765087-0398-5d2c-bd29-9057ad866ebb | note | IP
06038f3e-96ac-5cdf-a184-763a06e249e3 | note | Responsibility - Project Engineer / Site Engineer
42ddb03d-fbc3-5558-83b7-0cd971b29362 | date | Date Completed:
0cee4759-1127-4b87-a424-7c56ad8931bc | checkpoint | 2.12 - Installation – Hot Water System
c7663622-37e3-5af3-960b-90413b496ce1 | note | Frequency - Each Lot
5be88188-d99c-5afd-9a0c-b1175956c1ec | note | Acceptance Criteria - WITNESS POINT
52d6f5ed-c607-503b-b731-866beb04d6bc | note | ○ Installation of electric instantaneous hot water units, temperature control, and thermostatic mixing valves.
abbd6460-ff28-501d-b767-1559764b9aec | note | ○ Give notice for inspection of installed elements prior to covering/lining.
c5f9618f-e4e8-5ab1-aa07-1cf873f3bfde | note | Reference Documents - ZULU-BECA- 001-SPC-00005, C1700.2.2(b), Drawings, AS/NZS 3500.4
25f4a4a0-0dfd-55e9-9be8-1902f3c7def3 | note | Inspection/Test Method - Verify
ac853173-3a74-5357-9eee-80842c6442a4 | note | Record of conformity - This ITP Signed Building Eng ITP
004f4466-66d9-567c-a631-89fb253bfe5f | note | WP
e8377a1d-d5bf-59b8-9800-64b309f88600 | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
6d54c2a9-f2ea-5be1-9f11-ec81b2e715f1 | date | Date Completed:
a6556823-7df6-4540-ac18-d957aa4d31d6 | checkpoint | 2.13 - Installation – Sanitary Plumbing & Sewer Drainage System
6be82402-2d3b-5399-8da3-65c9eeca8c9c | note | Frequency - Each Lot
43011fd4-95aa-5acd-bfdb-b31092bc5ba2 | note | Acceptance Criteria - WITNESS POINT
2b637d00-9014-59bf-897f-43d6fbefe206 | note | ○ Installation of vented gravity sewer drainage, floor waste gullies, and inspection openings.
7f6160c4-d432-57ef-a803-dbdee8f823f6 | note | ○ Give notice for inspection prior to backfilling any pipework.
72678597-1bde-5731-893f-eb6fb2ba8b80 | note | Reference Documents - ZULU-BECA- 001-SPC-00005, C1700.2.2(c), Drawings, AS/NZS 3500.2
c2de968e-0a98-52c4-85df-e5104bfa2c07 | note | Inspection/Test Method - Verify
4ee44bfb-6a04-5bee-8220-dad6dd98a4f0 | note | Record of conformity - This ITP Signed Building Eng ITP
a05ca3ca-b061-500c-b083-c26840d2f928 | note | WP
fea58b92-748f-5fb8-9651-7ffbc6fdc544 | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
5404fea3-67ae-5d1a-bcf2-ea0be6e8fdde | date | Date Completed:
44e19a7a-a0c7-48e3-b126-c472a6d8d686 | checkpoint | 2.14 - Installation – Roof Drainage System
7b582d63-9d67-575c-b85c-22828a7b4645 | note | Frequency - Each Lot
083401c5-9717-5559-b524-f1777ff12a2f | note | Acceptance Criteria - Installation of downpipes, eaves gutters, and stormwater drainage systems.
037dc26e-9a11-50bb-9510-04fbaaa3de51 | note | Reference Documents - ZULU-BECA- 001-SPC-00005, C1700.2.2(d), Drawings, AS/NZS 3500.3
6a2be6a7-2fcb-553b-85da-d1030017976e | note | Inspection/Test Method - Verify
e8c8feb5-0834-5e01-b4e9-f054ca39ff19 | note | Record of conformity - This ITP Signed Building Eng ITP
9f6c07f8-9c94-5144-8887-fdcc63137ef8 | note | IP
d1cc75ee-a7d5-5a6d-8a7f-72fd47c21f8e | note | Responsibility - Project Engineer / Site Engineer
e60b9d61-6e1e-5e13-ba89-168e0e6a2373 | date | Date Completed:
d9f3c123-18d1-4557-9561-635ce0f429c8 | checkpoint | 2.15 - Installation – Insulation
70894d2c-cbc1-50ab-84a6-746551233bb4 | note | Frequency - Each Lot
aeef321f-2302-5357-9cac-2dbddd317958 | note | Acceptance Criteria - Application of thermal insulation, fire properties, and vapour barriers.
d1e68e95-b7c7-50b7-bd63-3bb5b429c728 | note | Reference Documents - ZULU-BECA- 001-SPC-00005, C1715.3, C1715.4, Drawings, AS/NZS 3500.4
ff7e8474-84a2-57d5-868a-5c658a8bfda8 | note | Inspection/Test Method - Verify
9db76a87-7f5a-5657-a8a2-f12770cb0ff0 | note | Record of conformity - This ITP Signed Building Eng ITP
3834c000-5cfc-5871-8357-4606abdf5542 | note | IP
bf6e05a6-7d73-5bb0-b013-2d2bc5ed7a1e | note | Responsibility - Project Engineer / Site Engineer
49b8a36a-ffdc-5f06-8632-6348a656f99c | date | Date Completed:
ae3de4b0-583a-49e8-a655-2ad2cd2e2554 | checkpoint | 2.16 - Installation – Pumps
016d912d-6551-5590-a25d-40013196a8fd | note | Frequency - Each Lot
4ac996e7-1b52-5671-add9-48af807a3ecc | note | Acceptance Criteria - Installation of submersible sump pumps, control panels, and electric motors.
f2cfc067-f6bb-5648-921b-0bc8f8c98c71 | note | Reference Documents - ZULU-BECA- 001-SPC-00005, C1719.4, C1719.6, Drawings, ISO 2858, BS EN ISO 9906
abc593ba-36a9-5668-9368-3809e7a72252 | note | Inspection/Test Method - Verify
c7eed040-6b7e-5d58-91a3-6472ba4799df | note | Record of conformity - This ITP Signed Building Eng ITP
0250bcef-642f-5401-a316-d6377f5c6265 | note | IP
f3b25e19-3a51-505d-9fe9-15057c46eb7d | note | Responsibility - Project Engineer / Site Engineer
b1a85666-e139-5f42-b7ee-0e63c1de5f44 | date | Date Completed:
98dd6845-c12e-40ac-b29d-e2b80a05fb0b | checkpoint | 2.17 - Installation – Fixtures, Fittings, and Appliances
d83e1725-f447-5425-83a2-698694a8860e | note | Frequency - Each Lot
0e1b300d-df78-55e4-839d-42cb5efdc70a | note | Acceptance Criteria - WITNESS POINT
79f0919f-88a9-50dc-8fd7-456bb5cf09e0 | note | ○ Installation and connection to water supplies and drainage piping.
0dd9d9a9-da00-5771-bc78-2b6fdfc71fec | note | ○ Give notice for inspection after installation.
293b0fe0-cb65-5acc-ab8f-87519ccf0dc3 | note | Reference Documents - ZULU-BECA- 001-SPC-00005, C1750.1, Drawings, AS/NZS 3500
95ed9df9-7ee2-5a92-8163-699212314c42 | note | Inspection/Test Method - Verify
785d0b37-b90b-58d5-8980-015da204b048 | note | Record of conformity - This ITP Signed Building Eng ITP
a9a32e72-cdb4-55f0-998f-6ec4f2c64642 | note | WP
12c843ad-c13d-54db-b94e-28d04f90625d | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
90203330-d5ac-53c3-8d25-76062fab32aa | date | Date Completed:
55497c93-cf57-4fd1-9a45-41ceacad5c9f | checkpoint | 2.18 - Testing
a5338ec7-b7ab-56c3-a8ab-2269d64e63ea | note | Frequency - Each Lot
83f95296-5abb-57aa-9cc4-6b6cd6f99f64 | note | Acceptance Criteria - Carry out testing as per requirements in C1700.8 for water and sewer services. Conduct flushing, pressure testing and disinfection.
77a05776-d06f-5986-ba06-2920edec3af8 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 C1700.8 Drawings
f91455e9-9082-52a8-870a-efd3b6637719 | note | Inspection/Test Method - Verify
826db8da-f09e-5d19-9435-e32762fb26c6 | note | Record of conformity - This ITP Signed Building Eng ITP
107e296f-04df-53fe-b27f-71cae0238985 | note | IP
d44eb901-c91e-5329-bae7-b2434652aed8 | note | Responsibility - Project Engineer / Site Engineer
06558ee5-d14f-513c-925c-20ae2dc84b23 | date | Date Completed:
c1703884-7384-4083-9011-379a729edc02 | checkpoint | 2.19 - Survey As Built
528ae495-4c6c-5631-b793-694a104bd9ee | note | Frequency - Prior to Covering Services
0decbcf6-8208-574d-b02d-2cbfe0960099 | note | Acceptance Criteria - Survey to pick up services prior to covering
8c45bebd-8b35-5c98-b3c4-a5f8028d3e5e | note | Reference Documents - FH QMP
d16554ac-4e85-5a78-90c2-60a5d0423be8 | note | Inspection/Test Method - Verify
9972e67d-bb84-5af1-8bde-c2029fdf1e7c | note | Record of conformity - Survey
57f76097-081c-5137-9560-b56b2691da2b | note | IP
ae25b533-2470-5092-86a7-1f471a6d0436 | note | Responsibility - Project Engineer/Survey or
a96ae255-b7d2-5a41-a711-e6e9aee06f8c | date | Date Completed:
26abb576-0ae8-4715-b322-cf8d68cb9f0a | checkpoint | Final Inspection
80daf9f0-a3f9-5f7f-8e7c-64b3be7acd77 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
0109e836-3a00-5fcb-8598-d41c61099368 | textbox | Print Name:
8a7af719-b177-5f61-b69a-09a73d932c00 | textbox | Position:
c0f26398-072e-548e-b5e0-34425e005de1 | date | Work Completed On:
96d22004-48a8-5599-b6ea-f435e4d9293a | date | Date:
10961f06-016b-4dfe-866e-495f1ac8ece7 | checklist | FH-ZU2-QU-ITP036 - ALER 3 Mechanical - Rev 0 | itp | ITP036 - ALER 3 Mechanical
6f5fd37d-fa0e-4391-a33b-3474cc930326 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
8155a847-a0e1-475f-b997-9c677da8459d | checkpoint | 1.1 - Check for correct documentation
57e93820-4473-5f15-8ebd-2c21825f1072 | note | Frequency - Prior to commencing activity
3d85a171-8349-53c9-b0cd-94dc608ed1be | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
850c5f4c-fd8c-52a0-a4bf-506c596be0b8 | note | — using the correct and complete set of drawings.
e436c536-5680-514c-8170-58ad22b90eb1 | note | — all drawings are the latest revision.
5ecee2d0-ba10-59d0-b96a-cc50ee4c641b | note | Reference Documents - Drawings / Aconex Register
67ca2c5f-71ff-55a2-b18b-f19d3d7eb917 | note | Inspection/Test Method - Verify
fa5c25f0-f8cf-5559-8a14-b98410909ce8 | note | Record of conformity - Drawings and drawing registers
c1c054b1-cfa9-5783-8ec3-7d98eca587ec | note | HP*
c7cc48ea-52b2-537c-8a95-2690c2342a7d | note | Responsibility - Project Engineer
9d846e2e-8b0e-5576-ad13-69bc8eeb6626 | date | Date Completed:
5d79d893-bfe2-4749-be0f-b0f114fd024c | checkpoint | 1.2 - Implementation of all measures and controls
3f35e1a2-5271-59a4-a2e7-1f67c1f9af65 | note | Frequency - Prior to commencing activity
bf5992cd-712d-5e81-a337-3a2ab21bce91 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
545b9eb3-9cc9-5d5a-88e3-d4c4634b2fce | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
2d004950-77a0-52fb-bf87-91e838a85063 | note | Inspection/Test Method - Visual inspection
c5b7aca1-caf8-5488-a762-63b0cc57d5c5 | note | Record of conformity - This ITP signed
d5f7aea9-4b45-5d05-b36b-bec75fc57429 | note | HP*
e451e72c-359f-50fe-b70a-ef7850f75406 | note | Responsibility - Project Engineer
72e6b979-2a6a-56ad-8c9a-68466ee2791a | date | Date Completed:
db317233-26bc-4999-b7f1-058cf113607b | checkpoint | 1.3 - Survey Checks
495da4fe-c977-5fac-833f-f719c4b09bd2 | note | Frequency - Prior to commencing activity
30fd66e0-a0d8-5cd1-97e8-143a24ef4982 | note | Acceptance Criteria - Survey set out to be completed for all assets
1428889c-66a5-5380-a59b-08f2fd8b281e | note | Reference Documents - Drawings
cc004111-b42e-5d2c-adfb-8afa22f353a4 | note | Inspection/Test Method - Verify
6da4a279-2830-5075-a261-e3a41f463bf1 | note | Record of conformity - This ITP signed
dd581121-30f3-526f-b3d4-a33592dee335 | note | HP*
cab0e6b0-0f0c-5059-b96a-a602921f790e | note | Responsibility - Project Engineer / Surveyor
99350b8c-cd7e-5a26-b919-6fde20c418a4 | date | Date Completed:
eeb09da2-9afd-440c-a566-9ddd7d5bb2e7 | checkpoint | 1.4 - Submission & approval of shop drawings
f222828a-291f-5c05-9960-81b3919c9c56 | note | Frequency - Prior to commencing activity
b7d22d01-bf6d-5d8a-abc4-53b27e171428 | note | Acceptance Criteria - HOLD POINT
59448a5e-b596-5b93-8203-40e5223334b6 | note | ○ Submit shop drawings to the principal’s representative for approval prior to fabrication commencement.
a560ea2c-6c95-5dfc-ab98-b34f7c0b85f6 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings, Shop drawings
9f1bb257-11da-5f92-a60b-e87aa918b9b5 | note | Inspection/Test Method - Verify
900f0aea-06e0-5c8e-b71b-b3c3c86e47c0 | note | Record of conformity - Aconex Reference
46e7885f-7ada-58b5-9458-aecc49dffd85 | note | HP
58087feb-2035-5450-addd-a96997808234 | note | Responsibility - Project Engineer / Principals Representative
8ce31cb2-9667-5587-b948-1c9154d38ec6 | date | Date Completed:
948df1ae-50a3-4b8c-844d-1b13c08d2c26 | signoff | AUTHORITY HOLDPOINT
1edd93e5-2201-40b6-831f-80230acec82c | checkpoint | 1.5 - Material Submissions
4c611176-71d5-5f11-a221-a67c2273b117 | note | Frequency - Prior to commencing activity
9426c863-2d85-5fff-b545-4b87b5d927ed | note | Acceptance Criteria - HOLD POINT
b8500d93-d304-510c-bcba-5f1458baf654 | note | Items to include but not limited to:
acf92a7b-001b-5c3b-a501-d02838ea1398 | note | — Refer to materials register and list items
f47fd511-3773-515b-bdeb-c22819a1754e | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
f23c846c-3299-5636-844b-f46bcc45056a | note | Inspection/Test Method - Verify
a2e17775-a4fd-52d4-84f1-25811924549a | note | Record of conformity - Aconex Reference
8c35a547-a819-5cbd-9e63-9a28a476a5f1 | note | HP
2774f676-963d-50c2-9c03-19e9a6961862 | note | Responsibility - Project Engineer / Principals Representative
d02d885e-cefa-5c65-9770-621843e76bd0 | date | Date Completed:
15b0e863-e257-4ac2-a363-6cdfe773beab | signoff | AUTHORITY HOLDPOINT
0195197b-6b41-437e-8e3e-7ebf2e0b4381 | checkpoint | 1.6 - Temporary Works
427f46ea-1db3-5880-9c5c-8e61af6ef9ad | note | Frequency - Prior to commencing activity
ffba9a27-6379-5f88-9397-47c32b56ce8d | note | Acceptance Criteria - Submission and approval of the following documentation (not limited to):
38465f12-abd4-5036-9fed-436d7b0ed4bb | note | — Certification of Lifting Points
4d66a5e2-e991-5d7c-b1c0-dbd770997988 | note | — Lift Plan
396e9de4-6ea0-5739-beda-43d36893b4e1 | note | — Certification of Ground Platform for Lift
e232fea4-1f9d-5ff4-99c2-cd0d3da011bf | note | — Lifting inserts
f6204b44-2c02-520d-9882-566ac92c5972 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
cdcf8d65-4e44-52c6-abf2-8923f31bdb1b | note | Inspection/Test Method - Verify
9967f0e3-a7bf-50e9-b889-75cd19f3e6f1 | note | Record of conformity - Temporary Works Geo Report
ee4feb72-9a90-5db0-9e1b-8661ae6b81e5 | note | HP*
a16ee2ff-9b43-50db-84e1-8d428f5dedb6 | note | Responsibility - Project Engineer
f4bae352-d49a-5b66-bc75-27fdc7170268 | date | Date Completed:
ab7389ed-3747-476e-92a5-59e3db40b1b3 | checkpoint | 1.8 - Certificates of Compliance
c4bd98d2-4bb9-53c6-8aeb-cb84f75364a5 | note | Frequency - Each Lot
bd7dbd8d-d47d-518b-bdd7-238f49a3c7be | note | Acceptance Criteria - Provide Suppliers Certificate of Compliance and Spatial Certificate of Compliance for
34c640ee-d497-5fa1-b513-b860f6788c9c | note | ○ Split system/process cooler air conditioning units.
e43bd91a-5a32-57f2-8925-ea857d41547b | note | ○ Control systems.
d122561d-9ecf-57c3-8e1d-91256ba4a571 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings C1900.6
4e13d4c1-0f12-5c6b-906b-3a55c026447e | note | Inspection/Test Method - Verify
e290085f-a48b-57d0-b6b1-eae01b386eff | note | Record of conformity - Supplier’s Certificate of Compliance, Spatial Certificate of Compliance (where required)
606b5001-b560-5957-905c-d4b5fe6104bc | note | HP*
f4214def-83a4-5d46-8455-99272ecb7e0d | note | Responsibility -
a3130780-20e8-5c08-b9d7-b81c794c481f | date | Date Completed:
3338adfd-a8b1-45a6-add5-ca0634eebd2d | section | 2.0 - Construction
b3c08ab2-8f31-4986-b321-c51cf28a9199 | checkpoint | 2.10 - Delivery of Materials to site
b526f905-9573-568c-94b2-78702b3bdb58 | note | Frequency - Each Lot
7ce0b1ec-b617-5291-88ca-1cc05e373f3c | note | Acceptance Criteria - Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site.
451c2268-6dc5-57b5-a86c-44d8d5e2e85b | note | ○ Identify any damage/defects prior to unloading of the material.
a51b7d95-c418-5707-be61-20540ca0a2ad | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
7a0f44cf-a9d2-575e-8b19-d93e93cdabe9 | note | Inspection/Test Method - Visual Inspection
c8528088-cf01-5c5b-b922-f90bfc811070 | note | Record of conformity - This ITP Signed, Materials Inspection Checklist on Conqa
1d7841bd-596f-5135-8f4d-edc25d190250 | note | IP
b56c7bfe-cd81-573b-a344-c336207f295a | note | Responsibility - Project Engineer / Site Engineer
37b4b8ad-fff7-5893-8c0b-9963adff14e3 | date | Date Completed:
c5a843b6-78ce-4e2a-afea-b8a209f1ee4e | checkpoint | 2.11 - Pipework installation – General and Refrigeration
5b55c8d6-5ad0-53c1-8a0a-c7c6fc45b0df | note | Frequency - Each Lot
93b40983-b159-51e1-a132-a4c72a20d190 | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
c683bdd6-760e-5993-b05f-2e2040fad67d | note | ○ Brass fittings
c95a87f1-a340-520e-b6a1-fd6984ff14db | note | ○ Mechanical joints/couplings
7717c49a-c975-53b6-9bff-8b560c62a49f | note | ○ Bends/Branches
d740351b-12bd-5157-9870-d3b36a56588d | note | ○ Sleeves
bd34d98b-d0e1-5356-ba79-00c4559405e1 | note | ○ Drains
c90c3480-9474-548a-a35b-ce69c311c665 | note | ○ Escutcheons
4440312d-d659-5fd0-96d3-fa149cdcdd82 | note | ○ Pipe Supports
f59fcd58-a85b-5bac-91ec-df3d97fb6966 | note | Reference Documents - ZULU-BECA- 001-SPC-00005, C1910, C1912, Drawings, AS 4041, AS 1432
4e504908-2c17-5c99-b728-fa198ef1e920 | note | Inspection/Test Method - Visual Inspection
5dc20558-2f6c-5dcd-a10b-18027bacadd2 | note | Record of conformity - This ITP Signed, Building Eng ITP
d55fbd91-6909-5c3e-b720-32ee85800807 | note | IP
62275889-338e-581c-8a3c-d72c8454f2c8 | note | Responsibility - Project Engineer / Site Engineer
5e9d06fc-38a2-5d4c-8025-880221552d46 | date | Date Completed:
12eb9595-2ce2-4ea5-86db-dda409837f2f | checkpoint | 2.12 - Ductwork Installation
5a02fb88-99d8-54fb-b101-4bccbad705fe | note | Frequency - Each Lot
e1d1e520-f71d-513d-9271-9c6d58da121c | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
e46057f0-0500-50f6-937c-cf09b0c9e6f5 | note | ○ Ducts
45d1d185-b6bb-5898-9af0-f235ce552d84 | note | ○ Duct Sealing
f6b838ec-2bb5-513b-a9be-af1e3487a068 | note | ○ Bends, tees, transitions,
ddf3eaa4-d7c2-5fe8-8eb9-b9583620fd16 | note | ○ Test holes for commissioning
c02e0d50-5537-5214-b4a5-7086e80bfd26 | note | ○ Outdoor air intakes and exhausts
abac7e73-d8c8-59be-bb75-432bf76d559b | note | ○ Duct and fan Intakes
7162f57e-8023-5f96-86cd-b581f0214100 | note | ○ Duct support and restraint
6b389b8a-67b0-5a0c-abf9-e98c9f6d4c77 | note | ○ Access hatches
f7e2d847-b4d3-590d-872f-63cd34383554 | note | ○ Balancing/motorised dampers
f51fd1d3-14f4-5708-b7f1-969f294d24e5 | note | ○ Smoke and fire dampers
33e049a8-ddba-564e-8849-455af84b6914 | note | Reference Documents - ZULU-BECA- 001-SPC-00005, C1940 Drawings, AS 4254
08fc9303-12e5-5e52-8749-fb6c38c7acb3 | note | Inspection/Test Method - Verify
b20ca9a9-f47e-5e91-a377-a0d29c9c4be8 | note | Record of conformity - This ITP Signed Building Eng ITP
5d491a6f-a223-53ad-9041-e86e913e6dae | note | IP
aeb076ea-d804-5270-b13b-63b8dc31532f | note | Responsibility - Project Engineer / Site Engineer
65ca1b6a-4a68-5603-ac82-e5c3324b179e | date | Date Completed:
1e53629a-3dd6-427e-9b79-78f0878eb16e | checkpoint | 2.13 - Mechanical Components Installation
2ea59207-2ab5-5356-a7d3-ac198827e8cf | note | Frequency - Each Lot
5bf58eec-c650-5179-be1c-ebf33d13d730 | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
e49d6b00-d99a-5c6f-90e7-1ab35d7cb9e3 | note | ○ Split system air-conditioning/heat pump units
49460807-51ec-5dce-97b1-7629b1c88497 | note | ○ Grilles, diffusers, louvres
0721fa67-95bf-5c7c-8fb1-a0b59a87646f | note | ○ Fans
26c8e48a-5358-5bb2-8649-e03eaf930817 | note | ○ Filters
83666446-6884-5f1b-ac54-22d84449d2bf | note | ○ Insulation
1419baf2-f1cd-550d-a8ab-22311ce80ec8 | note | ○ Vibration Isolation
08bd10e5-a1b0-56c0-91a4-1b5d5d6e9654 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
7e7b52bf-ca32-5eaf-8517-b52ba012c49e | note | Inspection/Test Method - Visual Inspection
cc5d62ef-5f8e-556f-aca2-cb1e54e5140f | note | Record of conformity - This ITP Signed, Building Eng ITP
049c2297-2c59-5ebc-b5da-56dde00295b5 | note | IP
75757051-146c-5064-982f-d20a861ee98a | note | Responsibility - Project Engineer / Site Engineer
97cef573-69f9-5225-90a1-fc3f94707e56 | date | Date Completed:
1b1a9580-9f73-4147-bcb9-ea230d95525d | checkpoint | 2.19 - Survey As Built
f6678233-8c09-51f5-9fa9-2a790a4c59c6 | note | Frequency - Prior to Covering Services
f41bf945-c745-5d06-906e-99001de0d475 | note | Acceptance Criteria - Survey to pick up services prior to covering
de85aa77-3843-5907-8edd-5648da923f08 | note | Reference Documents - FH QMP
02af66a4-e66b-54d2-b305-26467551a764 | note | Inspection/Test Method - Verify
df9f0964-0717-5dcf-b185-8f0dea01c23b | note | Record of conformity - Survey
a816eb72-314d-520f-91fa-34229142cd6f | note | IP
7cd7e66a-fe54-5c6a-b4e6-cec960b066d7 | note | Responsibility - Project Engineer / Surveyor
7341a102-d29f-5847-bc20-02b3f6afce2f | date | Date Completed:
9110212a-08ac-4896-8dc2-cc09c227b693 | checkpoint | Final Inspection
d811d2d5-c23a-51e4-8e78-05bbd9b2ed3b | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
fbe1810f-cdc7-5d39-98e0-364800d0544d | textbox | Print Name:
fb47ef3a-2258-5e6b-a826-621581f7c4ba | textbox | Position:
54a2835a-e347-5dcc-9731-47572ec63499 | date | Work Completed On:
908c7ca8-f768-5763-a7b2-e869b667d05e | date | Date:
d00908ec-06f5-531d-80b7-513b040c8fbc | checklist | FH-ZU2-QU-ITP037 - Miscellaneous Concrete Structures - Rev 0 | itp | ITP037 - Miscellaneous Concrete Structures
d7d6e24a-41e3-57a2-9551-08a3da3fcd83 | section | 1.0 - Preliminaries
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
b002ba69-0846-5329-95ce-92f03f564abd | note | Frequency - Prior to Start
d8391e9f-1a44-5702-aef6-8577473f863c | note | Acceptance Criteria - Current revision drawing is being used (including the subcontractors copy). Current revision to be obtained via Aconex or ACC
ba926b1d-10b8-58fb-a7bc-9b6a8d9899ef | note | Reference Documents - Drawings and drawing registers
6beae9ca-6003-5dc0-8b00-9ca675b37513 | note | Inspection/Test Method - Verify
ff5f5844-0a83-50a8-9c95-0b825d27f00c | note | Record of conformity - Up to date drawing sets and this ITP signed
1e654ed5-18c9-562b-87f2-c955c4c71664 | note | HP*
8012b25b-e817-5a3f-8ee6-bfe51d9af523 | note | Responsibility - FH Engineer
4365fa68-3bd9-5848-9e9e-533dcc9f0e1f | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
1d9cc5c7-0673-5e58-88a8-60c4d75582a2 | note | Frequency - Prior to Start
634d8de1-d01f-561a-9505-1d0b8205b529 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is CEMP, TMP, SWMS, & WP
6e079538-eb45-5aea-887c-cc9c4f74e3c9 | note | Reference Documents - CEMP, TMP, SWMS, & WP
c692070f-9ea4-5141-bc9f-c65f7ffd125f | note | Inspection/Test Method - Verify
f5968200-60cb-5ba1-9094-752543eb917d | note | Record of conformity - Site and office Inspection
06401db3-a8ee-5ef0-8fc4-edb90f316767 | note | HP*
794f01f8-8193-57c3-b868-48dc722fedc9 | note | Responsibility - FH Engineer
cc491c4d-c944-5731-9871-48b7c14f518b | date | Date Completed:
ddc68377-ad92-57e5-8ab0-c671f713640c | checkpoint | 1.3 - Excavation Permit
51936bbc-89ac-5300-b17d-a44005c8c819 | note | Frequency - Prior to Start
acc161e6-c2d7-5969-9825-e697f799d996 | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
48e02164-f603-59a3-b0ea-242bdd0383ff | note | Reference Documents - Approved permits
3ff52c1c-655b-5826-91a1-39bb19b0455d | note | Inspection/Test Method - Verify
cf0672b5-9c02-58d7-bd8a-b83d9c93ac64 | note | Record of conformity - Proof of & permit ITP sign
cf001051-31d8-5980-9f25-7e0560163a74 | note | HP*
3adbc93d-03e7-5bed-abef-f2776deee7a4 | note | Responsibility - FH Engineer
db49ea9c-6ec0-5611-9344-5007c07330c3 | date | Date Completed:
e7d6a2c5-dfe1-564c-bad6-fb4b3c19c030 | section | 2.0 - Supply of Materials
4efdd4d4-52fc-5940-a0b5-06a09948b577 | checkpoint | 2.1 - Reinforcement
6dd6df10-7cfe-5e8d-afee-e3e7b54830f2 | note | Frequency - Pre- commence ment
9ffb0ef0-8d49-5f7b-a4ed-90e614c70010 | note | Acceptance Criteria - Test Certificates demonstrating compliance of the reinforcement with the requirements of AS 3600
5a748777-13fb-5181-bece-6b8cc438ffc0 | note | Reference Documents - Drawings and Specification
4d91bbf2-c284-5e3d-94e7-0a04c1ab6c6a | note | Inspection/Test Method - Verify
5b2a4c52-5f7b-50ee-8f20-43d8faa7ad4a | note | Record of conformity - Aconex Corresponden ce
0af55697-203a-5361-9e22-256e4cfe8da5 | note | HP
951c0b47-36fc-5543-8442-0f0e8ecb09be | note | Responsibility - FH Engineer and Beca
8e7a6589-ad12-52a1-90d1-32380abf4a18 | date | Date Completed:
1e9728dd-8dcc-5f23-9080-8091cd6934b0 | signoff | AUTHORITY HOLDPOINT
bd5c6996-6a22-5c02-8b2c-9467cb09ea22 | checkpoint | 2.2 - Concrete Mix
05b5a876-6948-5102-acb6-334622009e75 | note | Frequency - Each Lot
882bc682-54c0-5930-9599-b66fd67c952f | note | Acceptance Criteria - Mix design to be submitted to contract administrator for review and acceptance.
beaf99eb-1d35-5b05-867a-de0471448acb | note | Reference Documents - Drawings
be7ef34d-785f-53f5-a7a3-cea6573f64b9 | note | ○ ZULU-BECA- 014-DWG-00201
18de00ac-d5b6-59e3-a39e-9be1cf27d974 | note | ○ ZULU-BECA- 030-DWG-20001
c2e5796a-863c-5b85-a118-fdcca1081a20 | note | Inspection/Test Method - Verify
714d9154-957a-5b59-a557-b60ef3a2ae9c | note | Record of conformity - Mix Design
8f171c0b-7de9-5954-9053-3e7d62187d50 | note | HP
2431fc77-5022-5730-9e24-5c59a6c6e101 | note | Responsibility - FH Engineer and Beca
2aae881a-8ed9-523b-a4e5-c218cb27eac7 | date | Date Completed:
36b14944-6e88-561e-afa6-593f076ee8f1 | signoff | AUTHORITY HOLDPOINT
a5f0f7e3-a1a9-5d5a-b4c7-f7af01a7861d | section | 3.0 - Construction\Erection of Formwork
eb40cfd1-0f1d-5fe1-8994-e0241de1ab9a | checkpoint | 3.1 - Setout
cb4664e4-487f-53de-aa32-acba96015630 | note | Frequency - Each Lot
33d4cf1b-28f4-5c78-b033-6390eedb8469 | note | Acceptance Criteria - Setout completed and conformance with Beca IFC Drawings.
85eef7fc-9248-54d5-85c3-f5437cf815ad | note | Reference Documents - Drawings
252acc84-8359-5556-9cbc-c26c32ab5e35 | note | Inspection/Test Method - Verify
36355643-4806-5297-a104-ee063e497057 | note | Record of conformity - Survey Report
38e3e112-a3e5-5b29-94a0-0662954157f0 | note | SCP
5bd9fa8d-b965-594e-bd97-03b423689422 | note | Responsibility - FH Engineer Surveyor
70e6cd01-f7de-5761-b30c-bb38a9d347c2 | date | Date Completed:
e9ad5079-1a8d-53f6-8a56-43fcffd1e2ce | checkpoint | 3.2 - Excavate
322c8298-b2fa-5059-b3f3-5826bb211460 | note | Frequency - Each Lot
a22ca8d8-49b1-5073-97d0-33dcde9e2494 | note | Acceptance Criteria - Excavation depth shall be as per specified or as shown on Drawings to accommodate structures.
9d45e13c-9688-5560-b325-5c5428592a70 | note | Reference Documents - Specifications as per Drawings
43e7751b-257e-5a6c-a831-2abdca374e77 | note | Inspection/Test Method - Verify
da445de3-a803-53aa-89be-29edbcc332d8 | note | Record of conformity - This ITP signed
d57e5973-35c0-5703-b69d-911e946b7593 | note | IP
397d5975-c942-5cf9-a7e5-3c7185cb4a18 | note | Responsibility - FH Engineer
e89f4d3b-5145-5c80-8df8-723b301359e0 | date | Date Completed:
86d44e27-ac01-56fa-afcb-52c35ccaab9b | checkpoint | 3.3 - Confirm Ground
46baabf9-0a9e-53de-a0c0-fcf4b622e5b5 | note | Frequency - Each lot
97b9c041-e7d5-527f-8cbc-0b430f7c3fc6 | note | Acceptance Criteria - Completion of excavation and inspection of subgrade materials.
30960d7f-c649-5339-bac2-6e827bc07af1 | note | ○ No soft spots, unsuitable material
aefa6754-73e4-578e-a804-e759637e8a02 | note | Reference Documents - Specifications as per Drawings
01b9c0a2-2b40-5a2b-8aab-609423388437 | note | Inspection/Test Method - Verify
faa64974-476c-54af-8f12-d6fc764c49ea | note | Record of conformity - DCP Test Results (if required)
b2f7662e-fece-5afa-875f-f9993f948509 | note | HP*
dd7c4fc9-4f64-5572-b779-5ed2219ed47c | note | Responsibility - FH Engineer
586c461c-9afd-5edc-943c-5a278c9e6cf0 | date | Date Completed:
5703acb3-5611-53ad-af4e-6d13ccd382ba | checkpoint | 3.4 - Formwork
e127324e-adb3-5d9c-bf9a-b0b4e56c0743 | note | Frequency - Each Lot
45f3589f-3933-545d-acb4-fef602f9e8bd | note | Acceptance Criteria - Formwork / Reverse Shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
a61bb31a-062d-5370-98cc-d23e7493d056 | note | Reference Documents - Specifications as per Drawings
9cab4f30-f75e-5034-8d49-da596e80a40c | note | Inspection/Test Method - Verify
7b436f07-e3c9-5bb5-a6e2-0c035a2bdda4 | note | Record of conformity - This ITP Signed
92e5a57b-7738-5394-b8ce-1681795b1ac5 | note | IP
1d7c03e0-82ae-59a6-9827-71639098fc4b | note | Responsibility - FH Engineer Surveyor
c8d76fee-e5eb-5767-9311-87caa8f8c7ed | date | Date Completed:
adeebccf-6b68-5500-9d1e-f9eac973e561 | checkpoint | 3.5 - Penetrations/Cast in items
bf19c4ef-18bc-54f7-8b9e-5edef28b24a3 | note | Frequency - Each Lot
9c0fc27a-9bef-5e55-88b8-1c55c67d9448 | note | Acceptance Criteria - Penetrations/cast in items are present in the formwork.
c8545872-ae2b-5d9a-a16f-ed32383c1068 | note | Reference Documents - Drawings
cf71dbe1-53b7-5974-91ec-3cac5232f8bc | note | Inspection/Test Method - Verify
4c3e5912-07bc-5588-b3ac-7e8c846bb328 | note | Record of conformity - This ITP Signed
9a242af2-de27-5e33-b6bc-de8a275d4503 | note | IP
20b8f032-b3d2-5389-94c2-1f32e4de4f98 | note | Responsibility - FH Engineer, Surveyor
cb544ac7-6e46-5a24-9da8-2ccf03183ed9 | date | Date Completed:
f41a2245-b899-54e2-bb9f-e76b7215b2ea | section | 4.0 - Reinforcement
512b0bdc-7032-5766-8b6d-3372bfa7e3ec | checkpoint | 4.1 - Reinforcement installation
8fd9431d-02db-5e3b-8092-18313e55918d | note | Frequency - Prior to concrete pour
78d14bd8-1a1b-527d-af58-09cc231d8436 | note | Acceptance Criteria - Pre-Pour Checklist Completed:
2aa385ea-f6ef-5fb5-a2ce-8dcdb29e80b8 | note | ○ Position and spacing check and recorded.
89e1959f-7517-5e7e-bf37-9304178d7bca | note | ○ Cover checked and recorded.
3776f8f3-f157-5ae4-b1b9-3d0b477ccc07 | note | ○ Reinforcing supports checked and recorded.
f707f26b-b8f8-5d7a-8f12-e7b3f11a01e4 | note | ○ Laps at required length.
e1d1b015-7e2d-5e59-91ac-b7c6b87db2a2 | note | ○ Penetrations/cast in items
20d5cfc4-2a13-59de-8730-9a43f649c067 | note | Reference Documents - Specifications and drawings
e2555919-a29a-5ef2-8f65-da84fb8f07d8 | note | Inspection/Test Method - Verify
19649ed9-c55e-5769-a6c8-add8e6b20fe9 | note | Record of conformity - Pre-pour inspection List, CLA37A
7d322283-b189-5fea-8c72-afb768a1102a | note | IP, HP*
174f4201-bf3d-5f42-af73-2a6b154558cb | note | Responsibility - FH Engineer
f213532c-5214-58fd-850d-e5097ed96bed | date | Date Completed:
90bb8dc2-5a3a-51ca-a065-52ad2ad32000 | section | 5.0 - Pre-pour Planning and Inspections and Placement (1st Pour)
928544de-658c-58de-82ea-71841e5b0101 | checkpoint | 5.1 - Pre-pour Inspection
cfc4eb44-5ca5-5665-ad86-50a9d4a3e147 | note | Frequency - Prior to concrete pour
88462cc6-bec5-5300-ade2-4131b5969922 | note | Acceptance Criteria - Superintendent or Engineer to conduct pre-pour inspection prior to concrete pour
6fb00c53-aef0-5d94-b851-ef4e438d7510 | note | Reference Documents - Specifications and Drawings
55f4e114-6c5b-5d87-b449-f7e20d6bb744 | note | Inspection/Test Method - Verify
3165fbed-7c58-54ed-a53d-7f8d86108f71 | note | Record of conformity - Pre-pour inspection List, CLA37A
e0882f08-8cc5-5e22-b64e-4fecf6c1e587 | note | HP* WP
b5238538-31a9-5400-a80b-d3cf7e826de3 | note | Responsibility - FH Engineer
39cd7b95-5e90-5250-875e-0c6f127226c0 | date | Date Completed:
edb492b0-0eae-5705-bd33-a10de3855a95 | checkpoint | 5.2 - Pour in-situ
89dd0caa-9a3f-544f-b8fd-d9a1412b757f | note | Frequency - Each Lot
ff9ec6ae-f6af-59f6-a7e2-210a24136436 | note | Acceptance Criteria - Concrete shall be placed within 90mins from batching.
2718c38d-36b6-5d35-a289-ac3e1133b283 | note | ○ All concrete supplied for concrete structures shall be subject to project control testing in accordance with AS 1379.
fe15d65f-b580-5d16-9b31-da24c225f54a | note | Reference Documents - Specifications and drawings
15e0bf2b-36e7-545e-9d84-6b5fb087ae92 | note | Inspection/Test Method - Verify
8f133827-c2c1-59de-88ce-8c575499a238 | note | Record of conformity - This ITP signed
adfb4b9f-cc62-579b-a54d-567565e2f47b | note | IP
24b1f373-a4fe-5053-bb67-cf3cd5e001ba | note | Responsibility - FH Engineer
3bd96a6f-7074-5a47-9cc7-6e6a336eff88 | date | Date Completed:
65a98220-5434-5fe0-af42-69dd7525cf8a | checkpoint | 5.3 - Concrete Testing
4452631d-37c2-5909-915f-fba055363fde | note | Frequency - Each Lot
a1760154-9536-5337-84c2-31fe92d069cc | note | Acceptance Criteria - 1 – 7 Day cylinder and 2 – 28 day cylinders to be taken.
0bbdfac9-b805-5c30-b04f-c5ddbafe4712 | note | Reference Documents - Specifications and drawings
1fe14439-bcb0-5b9b-8f6e-68c7601989ce | note | Inspection/Test Method - Verify
dde80bfe-a25c-54af-86e3-67ed0d000b08 | note | Record of conformity - Concrete Testers Sheet/Results
bcc7a6e2-f826-5f77-b3e3-6a71bebfdb84 | note | TP
d307e6be-c353-5543-928a-54465e8f0b87 | note | Responsibility - FH Engineer
bf20fdbc-fc84-5337-8872-e50d1efe2bc9 | date | Date Completed:
2d730bb0-a0c9-5bf9-8741-c1d322ef6473 | checkpoint | 5.5 - Finishing & Curing
5123af1d-eb68-593f-8e99-276fa702cf55 | note | Frequency - Each Lot
1c7b4f41-794d-5ffa-890c-ce8a5bbefd90 | note | Acceptance Criteria - Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces.
a7df4d8c-c931-5099-af0e-27329040c70e | note | ○ Concrete shall be moist cured or coated by an approved curing compound for a period not less than seven days unless approved by the Superintendent.
6317a0da-e5ca-50e5-b8b5-58561832257d | note | Reference Documents - Specifications and drawings
657bf579-b764-52fb-8d25-68827f8fcc6f | note | Inspection/Test Method - Verify
076f546b-3a68-5fd4-9e0f-68d7196f50ce | note | Record of conformity - This Signed ITP
6dde9b4c-e5da-53df-85de-ebba798dd290 | note | IP
6b18dded-1116-5dbe-a95c-e4fc443edef2 | note | Responsibility - FH Engineer
7faef982-f091-5ce8-82a2-4126d3ce3355 | date | Date Completed:
17539653-d776-53de-bfd3-447b816c62c0 | section | 6.0 - Post Pour Details and Inspections
02678ea3-cea5-5a84-ac58-34fff2215224 | checkpoint | 6.1 - Removal of Formwork
a6db7816-ff3c-5c5e-96cf-396d11f05153 | note | Frequency - Each Lot
eceda214-c95c-56eb-8abb-789fc22da409 | note | Acceptance Criteria - Forms shall remain and be maintained firmly in place until the concrete has attained the necessary strength to support its own weight.
8d67bdf9-1be6-5e86-8cac-1c908186c57d | note | Inspection/Test Method - Verify
d58b5ae9-f06b-5951-9e7e-beb62712dd4d | note | Record of conformity - This ITP signed
e025797a-e93d-585a-ab61-6bc1ebfefaef | note | IP
8142acc9-cef6-5637-8b28-3e40a1dba1ff | note | Responsibility - FH Engineer
18055ab2-5f70-5619-8492-84dc6b888d1b | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
cfe2ee0b-7871-501f-9116-490a2f406f57 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
c0b07b42-38e4-5cac-bd5d-71842dfc70e2 | textbox | Print Name:
ba181add-0945-5b9d-ba3d-3e1f62886868 | textbox | Position:
99be15b3-36a2-506d-8fdf-82a92df837a9 | date | Work Completed On:
ab7e37fc-72bf-5311-be07-2b569d866995 | date | Date:
1efdf959-8248-5807-8569-01db5e6ceb81 | checklist | FH-ZU2-QU-ITP038 - Native Grass Protection - Rev 0 | itp | ITP038 - Native Grass Protection
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
216f13c0-631a-5de2-b0e8-fa6c90d79a55 | note | Frequency - Prior to site establishment
4865a96d-3c1c-56af-ac3c-5e4505e5a0ca | note | Acceptance Criteria - Review whether a preliminary report has been completed for the project which will outline where the Significant native grasses are and what protection has been specified.
a8a796cf-5317-54bd-91f0-127b840b229c | note | Reference Documents - Consultant reports
dfc0e17f-a7fb-5399-964b-061ad1ddcade | note | Inspection/Test Method - Visual inspection
b60740c1-039b-5ee9-ad44-5eb87146d68c | note | Record of conformity - This Signed ITP
a12a05ea-f6c1-5ec7-90cf-9d30a6834ce0 | note | HP*
d8df4a35-931a-583d-9715-e1beb93e2b7d | note | Responsibility - FH Project Engineer
46867ecf-e671-59a9-882b-a222ccf7f921 | date | Date Completed:
a6a1e302-9d33-53a4-be2b-e1ef735da4c4 | checkpoint | 1.2 - Check the Google Earth Mapping
7d49b9ed-235a-52ce-a8f4-2de6272b0539 | note | Frequency - During site establishment
0935c216-bfa9-53fa-aa5e-6a24aadf877e | note | Acceptance Criteria - Review the Google Earth / GIS mapping which outlines the boundary of the native grasses at the time they were mapped.
890b0dca-2ad6-57f6-a256-cfbac6c3fd1e | note | Reference Documents - Google Earth Mapping
e828aed7-b6b9-5af5-b39a-7cfd2ba13139 | note | Inspection/Test Method - Visual inspection
4c63015d-0410-5dfe-84b1-0f2a44f6494f | note | Record of conformity - This Signed ITP
3f02a3d8-03b7-52b6-bcef-69cc7373f799 | note | HP*
5fa5b223-a8d4-5c5f-a979-66255446357f | note | Responsibility - FH Project Engineer
66c722a9-7fb1-53a7-a3c3-49221e73ac68 | date | Date Completed:
44272205-ef92-5f59-a531-1196a8a07cb4 | section | 3.0 - Implementation of Controls to Protect the Native Grasses
42562f14-5665-51df-93f1-f6c8326afa31 | checkpoint | 3.1 - Mark out the exact Significant Native Grass Boundary area
7b9cc617-651f-548d-84f2-c5bfa7195818 | note | Frequency - Prior to commencing any activity
9e5247df-1849-5d0a-ac94-738ed0a240e9 | note | Acceptance Criteria - Work with the surveyor to mark out the Significant Native grass boundary. FH Project Engineer must verify the set out survey data file matches the ECP and GIS.
cd48b603-4e2c-5241-977e-2b838e386106 | note | Reference Documents - CEMP & ECP
f03b23f5-4e4f-5063-9515-445644e52b43 | note | Inspection/Test Method - Inspect
9c11c12f-352e-5db0-92c6-9953921e13eb | note | Record of conformity - This Signed ITP
604250c5-a2c0-5718-be33-25a53ed49fc6 | note | HP*
9405f436-a806-556a-ba3b-73cb5cfa7103 | note | Responsibility - FH Project Engineer
9d3efbad-6c9d-5657-8277-15af080be725 | date | Date Completed:
4e01a72f-07ff-5070-a5d3-484e91bdc8b2 | checkpoint | 3.2 - Use temporary fencing/bollards and signage to block access to the Significant native grasses where we are working in close proximity.
55b2ead0-5305-5d1f-ba70-df0cc5ef6528 | note | Frequency - Prior to commencing any activity
d56d6f01-1109-59d9-a58c-202e8297dc02 | note | Acceptance Criteria - For works in close proximity to the native grasses, use temporary fencing or purple bollards to block access with signage stating “NO GO ZONE NATIVE GRASSES”. Where possible, this fencing will be installed at a distance (1-2m) away from the actual native grass boundary to act as a ‘buffer zone’ but still allows works to progress.
231e9034-3722-5440-abdd-2a691a73f168 | note | Reference Documents - CEMP & ECP
a6e5d715-ee40-54cb-b489-1074dc6ab1ef | note | Inspection/Test Method - Inspect
684fa277-9e04-5df0-973b-bd4fabbba96d | note | Record of conformity - This Signed ITP
de894924-de20-55a4-b2fe-e3e9090e645a | note | HP*
6518d271-ff9d-52a6-968d-1aad7fb2d35d | note | Responsibility - FH Project Engineer
2ecb63d8-d93a-5324-8656-94f77f649fcc | date | Date Completed:
af813026-2a0e-56b8-b954-2a26dfe86740 | checkpoint | 3.3 - Implementation of control measures required to protect the significant native grasses around our project area
ce3ec308-c40b-5654-b01b-fa9c462bc99b | note | Frequency - Prior to commencing any activity
70eb4d5a-2c35-533f-ba80-b2090e69c2d5 | note | Acceptance Criteria - Inspected and validate native grass delineation has been installed correctly using GPS mapping and against the design drawings.
8c06eace-458d-5889-9803-a0bfb7305238 | note | Reference Documents - CEMP & EMP
2ce81219-11a7-53b2-a7c1-08a4a9fa3dff | note | Inspection/Test Method - Inspect
57032812-6950-579e-9bdf-0d3204896163 | note | Record of conformity - This signed ITP
15f24092-ef40-59e0-ab53-bbc888e9c3b8 | note | HP
590151ac-7781-5df5-aa78-61f32f38673c | note | Responsibility - FH Project Engineer
62376a53-799c-5c5d-8b46-8a01aacbcda3 | date | Date Completed:
cf3529b9-ad34-5792-b2a0-f66e6d945212 | signoff | AUTHORITY HOLDPOINT
e7187eb1-074a-53f4-9d79-9ca9cfcd975b | section | 4.0 - APAM Hold Point Release - Second Inspection
3fad56da-64fa-5bd4-a2e8-866684b1f99a | checkpoint | 4.1 - Release of Hold Point for Native grass Protection
1514a478-e8a2-5956-97af-5aac277f7c60 | note | Frequency - Prior to commencing construction
16698acc-f712-57d3-b446-36cc47b8d676 | note | Acceptance Criteria - Arrange an APAM inspection to confirm that the native grasses are protected with the required temporary fencing or bollards and correct signage where required.
aaf09a0d-10a7-5d7f-a40f-7880b7f29fff | note | ○ All parties are to sign off on this Hold Point
a554ba14-e259-5b74-b82d-e33ccc278e93 | note | ○ Release document
67135554-3eb0-59e4-a017-9fb6cf9b2ec2 | note | Reference Documents - CEMP and ECP
caa3d8fb-e362-53c7-9629-09e294870f5e | note | Inspection/Test Method - Visual
ed9995a5-92ad-5c82-9a71-76ef981f15f0 | note | Record of conformity - This Signed ITP
1d5a99cf-1eba-516a-bf5d-b9c2d13d1c2a | note | HP
bfc9749e-effb-5925-9977-03a5ebc89408 | note | Responsibility - APAM, Fulton Hogan Environmental Manager or Project Manager
848286a1-04f4-5425-ba4c-0c33c6fc3015 | date | Date Completed:
adad0398-bccf-511a-a4c3-0cbadb72ff49 | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
c1cfe4e5-b9a8-5a77-804a-a216757322c9 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed above have been reviewed and implemented in accordance with the Construction Environmental Management Plan and conform in all respects with the requirements of the Contract.
1686e2cb-e6db-57e3-9eb5-1b42be8b4ad0 | note | FH Environmental Team
e2acd868-285d-5070-b4a5-44cdc9e52994 | textbox | Name:
359709b0-92ea-5762-b403-eb9708784de7 | textbox | Position:
a0ff56c3-768f-5bb6-8989-1c9828e97505 | date | Date Completed:
c839de23-6ced-54fe-91ad-70b2eca78835 | date | Date:
543635cb-6dfd-4f0f-b2bf-d8544fabcb8d | signoff | Add Signature:
c9944d37-6106-4e50-9742-85b7454d1fcf | checklist | FH-ZU2-QU-ITP039 - AGL Boring Installation - Rev 0 | itp | ITP039 - AGL Boring Installation
1dd2d3d1-1568-4aa4-9bb3-841f3043c321 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
4dd46308-4b6e-4750-8634-aaab33d7b382 | checkpoint | 1.1 - Check for correct documentation
8ab37f9f-8f1b-51de-912e-b6fa76a6d279 | note | Frequency - Prior to commencing activity
75fbddfc-db58-5dc5-a182-cd4888907403 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
465ea8e6-eef1-5bc8-b9cd-d348239521d7 | note | – using the correct and complete set of drawings.
9fa3feee-ce9b-5618-93fd-885eab9c4247 | note | – all drawings are the latest revision.
2a2a2801-a222-599e-9cf2-b17a2037ec87 | note | Reference Documents - Drawings / Aconex Register
22ef2956-07f3-5335-bf04-bd472e44747d | note | Inspection/Test Method - Verify
31ffa833-4c77-5e2a-a8ae-5f92105aeec2 | note | Record of conformity - Drawings and drawing registers
16eb0b6b-cd98-5f3c-81ed-5701eab898ea | note | HP*
afa681a4-9f46-59f8-b3ec-d3db808d3c6f | note | Responsibility - Project Engineer
8cbadbdf-73cc-5676-a9ef-3cf257352b0d | date | Date Completed:
abe7982b-b654-4048-954a-438f87e9420b | checkpoint | 1.2 - Implementation of all measures and controls
6b48f58b-3080-5a7f-af80-f5bce9ebbcb8 | note | Frequency - Prior to commencing activity
5183872d-f4d6-54cd-9015-258e0e7c2608 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
5ca885fc-c26c-5326-a5b3-bd944bb64bb0 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
04e699aa-2ece-53b6-b501-a1be308fd83a | note | Inspection/Test Method - Visual inspection
68a6dffe-3eef-58a5-a80e-254252f5f1be | note | Record of conformity - This ITP signed
1d37e191-ec2f-5849-a090-3869956bddeb | note | HP*
2bb1f8b4-e62c-5d48-9da0-8195c755f81a | note | Responsibility - Project Engineer
6e1e9fd9-32f1-563e-a3d0-fe7669073b8d | date | Date Completed:
02ca07be-eefb-4b88-a161-b3f81f7e6415 | checkpoint | 1.3 - Definition of the work area (survey)
e4923513-5907-56b9-b6e6-da742579ef89 | note | Frequency - Prior to commencing activity
591feb0a-23c6-5959-8943-8b44f2f99442 | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined.
a41765cb-bd08-5558-a2fb-587b4e9ed264 | note | Reference Documents - Drawings
3ed0ff72-f241-5ff1-a02f-70ad13618c68 | note | Inspection/Test Method - Visual inspection
740124b6-c4e4-5959-a122-921bd454e14d | note | Record of conformity - This ITP signed
1bea879f-6b5a-5cb4-820e-c46154b126ad | note | HP*
0ea5da2e-bcf6-5e52-8117-93fe5f457478 | note | Responsibility - Project Engineer / Surveyor
a08d871f-1bcd-5213-9a16-9f3842f9dc3e | date | Date Completed:
f50ceda2-8ab9-426e-81cc-44566ee02ffe | checkpoint | 1.4 - Material Submissions
bce64033-335c-5624-abd0-7b012cde628f | note | Frequency - Prior to commencing activity
92102d15-1c0f-540a-b38f-296a0414c404 | note | Acceptance Criteria - – Ensure material submissions for the conduits and grout are submitted
95230e63-7f50-5239-89a5-37fb7abc2309 | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl. 3.4, AS 1477 AS 2053
444d8bcf-3a7b-5ac1-b15f-754d1a07777b | note | Inspection/Test Method - Verify
e5a44b90-a2dd-5789-bd22-ed96d774abe2 | note | Record of conformity - Aconex reference This ITP signed
203a6394-9e8b-55e3-b454-137b1ed7160e | note | HP
3ba7f3a0-4385-5edc-bda4-f4bced7fdf97 | note | Responsibility - Project Engineer / Principal’s Representative
0557817b-f687-5567-b560-ef3a4b76354b | date | Date Completed:
40d34b22-12e9-410f-95cf-45c48b9e81e7 | signoff | AUTHORITY HOLDPOINT
1c1e652d-09e0-4918-ad23-daf1c74bc0cc | checkpoint | 1.5 - Methodology
c4e5bb14-dcfc-5429-905e-486592ec573e | note | Frequency - Prior to commencing activity
25875e28-5521-5d9a-bff1-46c7f7334c2f | note | Acceptance Criteria - Prepare and implement a Methodology that includes the following at a minimum:
1fac605b-b0e9-5da9-8bed-3e64d62c3632 | note | – Full details of the steps to be taken for the underbore works; and
07e46cbe-1259-5bc2-828d-d0da7fc29042 | note | – Details of equipment to be used.
5ef0eea1-08f6-5c1c-ad38-7c0e3d1deefe | note | ○ This must be submitted at least 7 days prior to the commencement of site work
c7b48d2c-219f-5a42-b959-5aba0646338c | note | Reference Documents - ZULU-BECA-001-SPC-00004
9005ee01-e0e2-520e-9c54-cc7db47d6db6 | note | Inspection/Test Method - Verify
89f49906-aeab-5dfb-9f24-c5ff47b11624 | note | Record of conformity - This ITP Signed
feec2805-9347-5a5f-8850-ae713c11e28b | note | HP
c3bf587b-51c5-5c29-8d96-499045132975 | note | Responsibility - Project Engineer / Principal’s Representative
802a744d-5d88-51ee-a4e5-320de14e8643 | date | Date Completed:
11d9840d-c7a3-478a-8e1d-f0bc43d0f045 | signoff | AUTHORITY HOLDPOINT
237d8f23-d932-4e1a-a619-6be77c884cfa | checkpoint | 1.6 - Locate and prove existing services
a8216cb3-1b29-5ab3-8052-853646695259 | note | Frequency - Prior to commencing activity
e8ee3b84-9831-5338-b685-722cfc90c623 | note | Acceptance Criteria - Location of services to be found and marked on the ground within the works;
ddb38a73-fe74-568a-b554-8d29c31f9b7f | note | – Contractor to obtain excavation permit from APAM prior to any demolition works.
4059bfa4-2d34-58bf-8671-4aa124a815f1 | note | – Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
8be4cfe0-9f45-5b74-8ac2-9d07967b1163 | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.15
c9616e44-bfd5-51e2-85ee-b0147e4962ae | note | Inspection/Test Method - Verify
d83d4485-e6dc-5ea9-bf1c-bc7edabbc5c2 | note | Record of conformity - Melbourne Airport Excavation Permit
43fd562f-805b-5bf3-bcd1-2d1ad15929db | note | HP*
32363155-b144-578a-92ca-e576d638b1f0 | note | Responsibility - Project Engineer / Surveyor
a06f6d05-e6ed-58e4-ac7e-cea6566b3240 | date | Date Completed:
dbe230e1-8c49-4353-9c66-454e99afff55 | section | 2.0 - Construction
95a05716-6f49-49d1-9154-913f03de96b5 | checkpoint | 2.1 - Excavate trenches for Entry and Exit Pits
686c449f-56be-5291-967a-e75169edb20a | note | Frequency - Each lot
ec58db07-ca1a-5ebf-9d8d-8315a9b6343a | note | Acceptance Criteria - Trenches for entry and exit pits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
c25550dc-47f9-57d9-99e1-17155a84781b | note | – The level at the bottom of the trench shall not be above the required level at any point.
991b7411-471c-5aa3-9a15-9ae3de8e844e | note | – Any over excavation under pavements shall be restored using 5MPa lean mix concrete in conjunction with the embedment.
98a952ca-5afc-5492-9fc1-6948a43f0458 | note | Reference Documents - Drawings ZULU-BECA-001-SPC-00004 cl. 3.6
396c5c05-ed8a-5c44-9784-3dcc16e65fe0 | note | Inspection/Test Method - Visual inspection
ca7f27c8-47f7-5599-b5b1-0d5801a1510d | note | Record of conformity - This ITP signed
517c0393-3370-5c30-99e6-f61683e0d559 | note | IP
98fe19c7-7845-5348-b10b-b42d18175b10 | note | Responsibility - Project Engineer / Foreman
706104a7-b532-5398-ba53-6c9cf0ce3ba9 | date | Date Completed:
d05caa38-7965-4f4b-a2c0-9ccf70697fb7 | checkpoint | 2.2 - Existing services crossing new conduits
8cf2c76d-d351-5897-a313-880e01d8d078 | note | Frequency - Each lot
8c9bc625-6825-5989-a71c-43e45d0a5ba8 | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
a0232d63-2440-5bde-9df4-0c35fb362a99 | note | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
48bb5b33-b1ee-5f40-b555-ada1832b0fef | note | Reference Documents - WMS002 – Working Near Existing Services
8d0cf3cb-d4e4-5455-ba17-705f671386cc | note | Inspection/Test Method - Visual inspection
d79661f9-e176-58d1-a939-9c9ab5af8d3c | note | Record of conformity - As-built survey report
837479af-7c03-50e4-8545-6c66c2af19a7 | note | SCP
1dabdde8-ed9f-5807-911f-5591df133963 | note | Responsibility - Project Engineer / Surveyor
fe7fbaf5-1f6b-59f6-b347-ee6c6c1a34cc | date | Date Completed:
b55e9f73-72c7-4b27-afdf-e5cda015f1bf | checkpoint | 2.3 - Survey as-built
c91f79ce-676d-5b56-bb34-1e31f99c5042 | note | Frequency - Prior to backfilling each lot
a4d26a17-4845-5b97-93cc-b0b0f444d0ae | note | Acceptance Criteria - Surveyor to pick up completed conduit runs
40e53e11-5ea4-57e2-8e00-b5d25048d12d | note | Reference Documents - FH QMP
ba82ad69-493c-58f3-864c-3082d71c52e4 | note | Inspection/Test Method - Verify / Inspection
28fc3ee0-d912-5087-abd8-44fc4528dc38 | note | Record of conformity - Survey report
e68205fd-517d-5409-9304-061840ca6721 | note | SCP / IP
73202358-8197-55d7-9f44-5753f724e472 | note | Responsibility - Project Engineer / Surveyor
6263a239-dcb6-5fe9-bee0-8ce279363cac | date | Date Completed:
54db02b5-57c6-4391-bb41-0211e766da10 | checkpoint | 2.4 - Cover
b16395e7-6fc5-5972-b03d-78cbfbb000d9 | note | Frequency - Each lot
25feb980-cf61-53ab-821d-a9e2468f8660 | note | Acceptance Criteria - Services installed under road and taxiway pavements and shoulders by under boring must have a minimum cover below the surface as shown in the drawings.
c7d5181b-f22b-59ed-b98d-4d0dc3e977f6 | note | Notify the Contract Administrator at the following stages of construction:
be157b8a-03c4-5e5f-b712-b060c91c957b | note | – At setting up for the commencement of drilling; and
b3c89995-374a-5e36-8377-1e7587296aa6 | note | – At completion of drilling prior to connection of ducting to pits and backfilling
0327f377-edbe-57b9-9a8b-aa1395f9ec7f | note | Reference Documents - Drawings, ZULU-BECA-001-SPC-00004
dcac4b05-5629-5b30-8e30-ec177ba30132 | note | Inspection/Test Method - Verify
cc44090c-f732-5a51-8da5-c3bb91895ebf | note | Record of conformity - Test report Aconex reference, This ITP signed
3617394d-9a26-5174-be97-5e31cfc5958f | note | HP
ac16a190-8944-5ac0-88a4-1b820c4f6835 | note | Responsibility - Project Engineer / Principal’s Representative
ba41df33-3667-5308-81ec-0ad91f909b2b | date | Date Completed:
09b1a7ab-4988-4f4e-83d7-5bf6e52c2670 | signoff | AUTHORITY HOLDPOINT
a2393ced-944b-458e-8af1-36418a08136c | checkpoint | 2.5 - Conduit draw cord
b453fe96-68d3-579a-ab20-9fc4a46a2f50 | note | Frequency - Each lot
76c513a4-1a74-55a6-b40c-17cd7eb814cb | note | Acceptance Criteria - Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be nylon rope and be 6mm in diameter, blue in colour. The ends of the rope shall be coiled at the bottom of each pit or wound around a stake.
f8c625a1-18f9-577e-bde9-c3015de6ee3a | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.10
b40c5c56-a51f-50fa-b36a-248bb853cbb1 | note | Inspection/Test Method - Visual
62fc937a-c367-5f55-bcab-934b1a0c9918 | note | Record of conformity - This ITP signed
86d9371e-5255-5336-8323-93fee565e904 | note | IP
44559499-2f22-5a5b-8a35-a7bb8f5710bf | note | Responsibility - Project Engineer / Foreman
18f27341-aaee-5895-ba9c-807e0a1036b0 | date | Date Completed:
f31bfbfb-bda3-4ed4-a964-defed583f84f | checkpoint | 2.6 - Grout
30c37451-82ca-5273-9af7-4dc06c9cb8bc | note | Frequency - Each Lot
6c9ff11a-7526-5071-b3c7-149152e59e9b | note | Acceptance Criteria - 1. Verify that pulling back of 63mm diameter grout lines are limited to 10m.
a67aefb0-9b97-5a6e-9427-8142592f1333 | note | 2. Measure volume of grout used per pull back to identify where full encasement may not have occurred.
e1d5acaa-210c-5291-93d8-a3da69aa3784 | note | Reference Documents - DCWC Mgt-CONTIN-000853
e71a527f-d8d4-5e16-9495-5acded646ec8 | note | Inspection/Test Method - Verify
f7bf587a-f081-56e1-b79c-dce078d4860c | note | Record of conformity - This ITP signed
710a10ba-198a-5506-9b1f-a616b9a9468a | note | IP
7f082b04-28dd-5541-ab37-bf8e3029fbd3 | note | Responsibility - Project Engineer
e3665cb0-8a64-57a0-9d47-b236b6ac3bfa | date | Date Completed:
4feae5f2-ef45-4abc-9b89-190686aed4d0 | checkpoint | 2.7 - Bore Logs
f20aec68-ad33-584d-bdc9-ca94b7d20bdd | note | Frequency - Each Lot
1cf635ce-8018-58f1-b451-6aa4ce559c43 | note | Acceptance Criteria - Submit bore logs for the underbore
e764a2b8-7242-5335-bf79-95e38ed83c81 | note | Reference Documents - ZULU-BECA-001-SPC-00004
7b3529b8-1fa1-55b0-8182-2019641d2d01 | note | Inspection/Test Method - Verify
c017e335-524d-5683-9e07-b783034db6c1 | note | Record of conformity - This ITP signed JLM Borelog
722a52df-3377-5d10-913d-4ca809e2ee17 | note | HP*
bf9311e8-993c-582d-a842-e2d25fb46893 | note | Responsibility - Project Engineer
daf10916-402c-5ebc-97df-3c85381374fe | date | Date Completed:
fd8db534-8151-4f78-9713-0afd67efe047 | checkpoint | Final Inspection
36a76881-262c-5507-9686-ce76864e1264 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality\System Procedures and verifies lot compliance with specifications.
87a7b0b4-a4c0-5539-a492-03b4962effbd | textbox | Print Name:
ed54656c-8099-5a22-a661-ccf1834e7219 | textbox | Position:
f02942b5-5b3f-5ea5-826c-002d5d54533c | date | Work Completed On:
9b29e317-e4e0-5d14-b289-e5defc57984f | date | Date:
d97f0d59-b93c-5191-a93b-57e1bf473bb0 | checklist | FH-ZU2-QU-ITP040 - AGL Pit Installation - Rev 0 | itp | ITP040 - AGL Pit Installation
6607cab9-33c5-558e-bbf8-f1706ae449f8 | section | 1.0 - Preliminary Works
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
93a3c36d-9405-521a-981f-c0e2f20861af | note | Frequency - Prior to start
8f81ed97-d054-58ad-83df-7bd70705e3bf | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
4acb2f82-cd70-5f2e-932f-efb2463644cf | note | – using the correct and complete set of drawings.
0f18b6ec-606d-52bd-8758-1a828ec9a50f | note | – all drawings are the latest revision.
a6514ab2-6b1c-5870-bad0-40911095837b | note | Reference Documents - Drawings / Aconex Register
24ce4b84-a465-5dcd-b5a5-ba1fb795ea18 | note | Inspection/Test Method - Verify
08e0dba2-b0f1-5910-ace8-6343b28d0b5c | note | Record of conformity - Drawings and drawing registers
e67b0def-bce4-5026-be58-258ae961d0b9 | note | HP*
c4f30c0d-24a8-5049-9c8b-3e58702e2c72 | note | Responsibility - Project Engineer
2ad62c75-b770-5f05-8546-e8dec48a678c | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
cb44b0ee-ddc3-59a5-9b01-fd796455120b | note | Frequency - Prior to start
a04b67ab-d134-534f-a12b-0ce3e1ec2961 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP
32b1c5c9-92c0-57b9-b152-6da10866cd3f | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
eb80c0cc-4ae7-5468-9978-37b054b2ed94 | note | Inspection/Test Method - Visual Inspection
488ae265-0f75-5ebf-864d-20506f94586a | note | Record of conformity - This ITP signed
3338f42c-ed1f-5c39-ba8d-67191b026722 | note | HP*
45ba5fb6-9913-5512-910b-83373fcc3239 | note | Responsibility - Project Engineer
27c5d8b1-df3f-5a38-bb30-9fddf7a16688 | date | Date Completed:
ae6436fe-7531-56f0-a722-60b6fb9a6221 | checkpoint | 1.3 - Definition of the work area & survey check
21a4bd21-1d6f-5969-af07-a6cf15a0b448 | note | Frequency - Prior to start
382cbcf8-fcdb-5a4c-8e44-0f53767fded9 | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Work area to be clearly defined as per For Construction drawings prior to trenching and install.
7967d7c7-151b-56da-a6f9-a13f3d54555c | note | ○ Ensure excavation permit obtained and (if required) services in work(s) area isolated.
e1fbbff1-43d8-5caf-b475-76f3a375d74e | note | Reference Documents - IFC Drawings, Excavation Permit
29fc7d55-3be2-5c93-ac6e-07fec38f05d9 | note | Inspection/Test Method - Verify
6554d266-2afd-5a6e-9811-3fb0dc801fb5 | note | Record of conformity - This ITP signed
f0167f8e-1fbc-55c1-b8d7-5b5a29db7ab2 | note | SCP
975ce107-a7b0-5ec1-b4fe-2846662d0894 | note | Responsibility - Project Engineer / Surveyor
aa08de9b-0d4d-5231-98e1-73a73ae08dea | date | Date Completed:
99f218db-300b-5379-a490-7ab3b2cd49e9 | section | 2.0 - Installation of SIT Pits
a3a9bb2a-fe1c-55a8-8745-a8c59cc3b6b8 | checkpoint | 2.1 - Pit excavation and placement
b1aa87de-8941-52c4-ae1e-cbd6c3386fe2 | note | Frequency - Each Lot
7f00b3ee-82cd-50a6-ab8d-da13544ebe19 | note | Acceptance Criteria - Dig zone marked out and excavation undergone in accordance to relevant permit. Pit placed and levelled as per survey set out.
88320882-d267-5c65-b0c9-ffeb4aa09f6e | note | Reference Documents - Drawings
a08ea9e6-e9bc-59bf-bd9a-3ca6a327682e | note | Inspection/Test Method - Verify
4b9e583e-e91a-5ab8-9cd0-98c0c8e8a504 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
498a3e52-d1e9-5c15-8635-8ede62e2ad61 | note | HP*
a1e6a782-300f-557f-935f-3b27a02f2b4f | note | Responsibility - Project Engineer / Surveyor
a39cfd65-f408-5691-b6b2-5bba04c37e05 | date | Date Completed:
0c5c50bd-1203-58f5-b22f-20573c0cc028 | checkpoint | 2.2 - Conduit positioning
825c3163-719d-514a-a4c5-6fb033ea5244 | note | Frequency - Each Lot
cb486f7e-0b4f-5291-8777-81c0ce18c878 | note | Acceptance Criteria - Primary, secondary and earth conduits (and subsoil outlet) positioned in pit according to IFC drawings.
7767da57-ad8d-5f4b-a0d7-f29a1e24c799 | note | Reference Documents - Drawings
0bd9bf46-de3d-5080-a48c-79e232dc507b | note | Inspection/Test Method - Verify
34dc86e5-6784-5fc5-a53a-2e12ad8b88a6 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
e34fe305-f865-5b19-943c-072efdcd8ec1 | note | IP
9310505d-1daa-593e-8cb6-72f741b454ed | note | Responsibility - Project Engineer
1982680d-1f45-5a51-ba83-79b92a3d18a8 | date | Date Completed:
092214eb-c6d0-5808-bbbf-c0491fc4b589 | checkpoint | 2.3 - Bedding and backfill of pit surrounds
4b186fa2-f184-590d-ad55-5105f504257b | note | Frequency - Each Lot
ca07663d-cc5e-56ea-a1ca-24222408e656 | note | Acceptance Criteria - Each pit shall be bedded and backfilled with stabilised sand.
eb30b916-c418-575e-a787-abbad059487a | note | Reference Documents - ZULU- BECA-001-SPC-00004
9fcc546b-8bb3-53d7-a3aa-38aa72c315ae | note | Inspection/Test Method - Verify
11eea8d8-40c8-59f6-a612-b9150f4527e1 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
3977f371-0ecb-5b6c-84bf-c2f351cf5af8 | note | HP*
951ea51d-91e8-54e2-ba6b-e51cd7bb4609 | note | Responsibility - Project Engineer / Site Supervisor
34932360-fa14-504d-acb7-5a8f9b3a809d | date | Date Completed:
0f3fde11-e097-5dde-ba07-77f40f8d8cac | checkpoint | 2.4 - Pit close out
11a6e9cb-0d23-5a95-b7f4-e5b658de2aa7 | note | Frequency - Each Lot
637cc6a6-2df5-5e42-8ed9-c4676b149da9 | note | Acceptance Criteria - Pits shall be labelled and directional markers placed. Lids to be secured and area cleaned/demolished.
070d84fa-0983-518a-b7ca-f09814c2b9a6 | note | Reference Documents - ZULU- BECA-001-SPC-00004
5f93bf0b-6961-5c0b-adb9-1335fe96ab69 | note | Inspection/Test Method - Verify
9499f1b4-8ea2-5dab-ad5c-70aec5570da5 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
7a970c99-db2b-5a0a-af7e-7e88c582fd8a | note | IP
b8ce93ae-69f0-5952-84d3-2632120a4018 | note | Responsibility - Project Engineer
3d54c413-8f03-51df-9bf9-49ec49b9a002 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
7d42f0e4-b240-5f8a-a1ee-10f6db69d435 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
34d9fe97-fdd9-5dff-8883-1161c772b954 | textbox | Print Name:
fc50cc42-87b8-565b-8c8e-57447d8be83c | textbox | Position:
4f666da9-4ed6-5496-b82a-dfcf4d3df362 | date | Work Completed On:
d1df7862-b616-5d7c-a8ce-c03826bac0c1 | date | Date:
6fcaf60a-5b72-498b-bbc2-d8dd3440f930 | checklist | FH-ZU2-QU-ITP041 - AGL Pit Fit Out - Rev 0 | itp | ITP041 - AGL Pit Fit Out
e3e69a5f-a70c-4446-a566-b4e2fa174f5f | section | 1.0 - Preliminary Works
e7aaeb7f-0529-4696-a275-e897e7645de9 | checkpoint | 1.1 - Check for Correct Documentation
9938f68c-882c-508f-ad9d-11628639465c | note | Frequency - Prior to start
b714c4d6-9600-5712-9898-30b23674da8f | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
60b4b1e3-465c-5c72-bfc9-baa57fb06ac3 | note | – using the correct and complete set of drawings.
d0fb0b9c-6e11-5e4d-93b0-8da374e5b87f | note | – all drawings are the latest revision.
d84e82dc-de29-5916-8d19-a6c733bdaa6c | note | Reference Documents - Drawings / Aconex Register
e26c7269-157a-5718-adc4-f0ac4c1bc4ad | note | Inspection/Test Method - Verify
4903ca76-4a3f-5cac-aaf3-85e29e3cbf50 | note | Record of conformity - Drawings and drawing registers
96078eea-8943-517e-80e1-bdc4a287ec8d | note | HP*
34e8073f-7486-5397-a512-794fbe4cc99f | note | Responsibility - Project Engineer
cec84d2d-925c-5b24-8c1a-b017769d315c | date | Date Completed:
6146396d-1a46-4094-97fb-ba388a4e8a22 | checkpoint | 1.2 - Implementation of all measures and controls
7bd9dd9e-4534-582b-92fd-9ccc10748c3f | note | Frequency - Prior to start
b1bb67cb-d279-59f5-ad30-946cbb48d2b4 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP
696e5f06-8a98-5803-bad0-5a0c8e82ff38 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
388684ad-2125-5cc0-bb03-241f35fe7073 | note | Inspection/Test Method - Visual Inspection
f9904c9d-5f7d-528c-9f87-2c27e410902d | note | Record of conformity - This ITP signed
43575bdf-8acf-526c-9c28-8b0cdbc04d17 | note | HP*
e34f371b-71a7-53ba-873f-aa2e586d7814 | note | Responsibility - Project Engineer
e0601152-d3ff-5baf-9c2c-9bbd361ab10d | date | Date Completed:
2c0efefb-7cd1-4f97-b240-1c3d0f558a3d | checkpoint | 1.3 - Definition of the work area & survey check
631648cb-134d-58fe-8769-03ca5b4be7f9 | note | Frequency - Prior to start
d90d03cf-7739-563a-bf5b-53bc033b4d0d | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Work area to be clearly defined as per For Construction drawings prior to trenching and install.
fe44393b-1844-5e6a-a188-935c01dc9b95 | note | ○ Ensure excavation permit obtained and (if required) services in work(s) area isolated.
cab015bc-7680-57fe-845c-c048ac04dd60 | note | Reference Documents - IFC Drawings, Excavation Permit
3084b2d7-059e-5bf5-8064-caaae1c50503 | note | Inspection/Test Method - Verify
d3fe0067-82f4-50e5-839d-1ef64c96f5c2 | note | Record of conformity - This ITP signed
8b509f8a-f7b4-5472-bc69-1cd67ac5934e | note | SCP
4293ede1-c836-5f07-b535-f25cffc15416 | note | Responsibility - Project Engineer / Surveyor
fc62d973-7c89-55bb-9e15-ec0a17b6553c | date | Date Completed:
d9cb289c-630a-4663-8648-e8115dd48b9b | section | 2.0 - Installation of SIT Pits
c6de2c07-9046-4eba-ac99-fba960383690 | checkpoint | 2.1 - Pit excavation and placement
46d02a2b-6f3c-5bb3-9b5b-a52faa18e168 | note | Frequency - Each Lot
92fabfd1-db51-545a-acb7-3288ecd20709 | note | Acceptance Criteria - Dig zone marked out and excavation undergone in accordance to relevant permit. Pit placed and levelled as per survey set out.
8b0a9d5f-031c-5ce7-9b9c-56ad7605db06 | note | Reference Documents - Drawings
0d8dfceb-476a-5669-bc3a-2a910430e082 | note | Inspection/Test Method - Verify
a10c07e1-e046-5159-a94d-f438fc6cbea0 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
202cd08c-487a-5e71-9be9-4aedf30172e7 | note | HP*
2086ca64-7529-53fc-8c20-e1cc464d745d | note | Responsibility - Project Engineer / Surveyor
2057c85f-4e75-5e26-a67c-f93fef89c724 | date | Date Completed:
9fdb35ba-57aa-4b97-b10a-9a2d468de54a | checkpoint | 2.2 - Conduit positioning
ec15a841-1601-5cfe-bafa-de9c2dd4acea | note | Frequency - Each Lot
4f3193bc-ce44-562f-876d-e46321dccb1c | note | Acceptance Criteria - Primary and secondary conduits positioned in pit according to IFC drawings.
85a0747b-7a86-5688-9539-37c08398028b | note | Reference Documents - Drawings
9a23f126-f192-5b1a-a6e9-f77426dd8e03 | note | Inspection/Test Method - Verify
dda215bd-412f-5d4b-8895-eb96c5a5abbb | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
4895e570-adf7-5f74-9847-fc548a3726f8 | note | IP
09ae9fea-ff2c-53c3-8010-d6e7da0b3963 | note | Responsibility - Project Engineer
641f6876-1650-5382-b06c-b717d5532769 | date | Date Completed:
ba3f0693-c4db-4a77-a128-89ba8a2b53ec | checkpoint | 2.3 - Bedding and backfill of pit surrounds
53e79679-3522-5863-9d39-3a4a90e0728b | note | Frequency - Each Lot
3983aa13-74be-5a74-a15e-8827c1e5e8ed | note | Acceptance Criteria - Each pit shall be bedded and backfilled with stabilised sand.
5a70875a-0728-5481-82b3-8324c8b09f3d | note | Reference Documents - ZULU-BECA-001-SPC-00004
d477dc77-566d-5c08-82fe-e6e61405476a | note | Inspection/Test Method - Verify
9d3e6f21-0fe5-5af2-ad5c-f99dcce19350 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
a748e5f6-e463-5e0c-ad88-186be65c6b42 | note | HP*
99dcf07b-ed8c-5197-a202-1b7a8ddf420e | note | Responsibility - Project Engineer / Site Supervisor
9b98b593-8e9f-5a2a-b420-9f8eabe29c0f | date | Date Completed:
5ea599e7-59e4-44c8-b4fc-62fd23f4b41a | checkpoint | 2.4 - Pit number labelling
73368c57-aa68-51fb-986e-701110f35720 | note | Frequency - Each Lot
89d708e7-39da-58e5-8194-136b2b3f9fe4 | note | Acceptance Criteria - Each pit shall be painted with the pit number with black waterproof paint on the inside and top half of the pit wall. Characters shall be 50mm high.
970ff74b-98bb-5ba5-bd2c-8bac754f52b2 | note | Reference Documents - Drawings
18249689-3ead-5a24-a946-20382347f0c9 | note | Inspection/Test Method - Verify
c48f05a7-d5e4-5d5f-ac31-c140589a0449 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
84f6a03e-3d4f-5050-acf7-c92f299a4929 | note | IP
609eefc5-6c61-51bd-8c78-bb8cdb190242 | note | Responsibility - Project Engineer / Site Supervisor
08e2f6d3-f96b-5b45-9de6-98ff11101a89 | date | Date Completed:
624f5035-07a1-4abc-81af-a7fa12f7fcca | checkpoint | 2.5 - Pit close out
8c1de8f1-1e5b-5cd7-9384-26bf8396e388 | note | Frequency - Each Lot
2ce581a7-5bc5-52c7-9734-449fcb2cdb53 | note | Acceptance Criteria - Pits shall be labelled and directional markers placed. Lids to be secured and area cleaned/demolished.
61cf3af4-2577-5385-aa1d-b3b84f2f0ea0 | note | Reference Documents - ZULU-BECA-001-SPC-00004
43dc711a-7110-551b-b6b7-31aeb55d22bb | note | Inspection/Test Method - Verify
073b2afa-590b-5438-b9d8-5bd029a50e6b | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
6a216ef2-e2a8-51b5-b25f-2c101bafe9ef | note | IP
42c8065f-ed43-5adf-a0d0-318afa8fa8f8 | note | Responsibility - Project Engineer
a8d66af0-0537-5897-a7ca-c4f8c668949d | date | Date Completed:
339df2dc-42e4-41c7-a001-35dd364e219e | section | 3.0 - Earthing & Fit Out
4c6333f2-193e-454b-8403-9b5f4651360a | checkpoint | 3.1 - Earthing & pit fit out
f3d6b092-136d-5a2c-87fe-b817e5d966ff | note | Frequency - Each Lot
f77b8688-e7b9-50af-b1eb-6082b714a092 | note | Acceptance Criteria - If no SITs:
360d29a9-ee56-5324-96ff-ed2a6033a09e | note | ○ 16mm Earth Cable Terminated From Earth Rod to Earth Bar
424d18a2-9da0-58d1-b77c-00eb9b528e59 | note | If pit houses SIT:
fe9454ef-1256-5b03-95a0-400a66a31bcb | note | ○ 6mm Earth Cable Installed From Earth Bar to SIT, 10 holes to be pre drilled into Earth Bar
1e56f727-cfc9-5dc0-b751-d5ee8b148475 | note | ○ SIT Mounting Tray Installed
554ea88c-cd51-5b11-83b1-0c0fe951ed1e | note | ○ SIT installed on the same tray which supply different circuits to have a 300mm gap clearance (Second tray to be provided if 300mm separation cannot be achieved on a single layer)
bbac32b7-579c-591c-bb1d-2689279708a4 | note | Reference Documents - Drawings, ZULU-BECA-001-SPC-00004
b1f07e2c-f391-5299-83b8-b735169f6302 | note | Inspection/Test Method - Verify
5446aafd-2955-59ab-b34a-511705f0f118 | note | Record of conformity - This ITP signed ADBSG, Earthing & Pit Fit Out checklist
6bfb6867-ce1b-50a1-a6bf-bfee2455b759 | note | IP
471e6096-fc6d-53c5-a2ba-838d641696a9 | note | Responsibility - Project Engineer
8ceb9e9e-49ff-5d4c-8717-ac85fd8d1f9c | date | Date Completed:
e018c3b9-6d65-45b1-aa32-71cd4f29f521 | checkpoint | Final Inspection
3ff28426-670f-54ba-bb5c-51f3db742023 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
805cbee4-258a-5d83-a469-0d55f38a61c6 | textbox | Print Name:
abf44f54-d65a-5244-bdbc-dea7376f5af1 | textbox | Position:
87faa2b3-1f35-5e73-866c-429725f22dd5 | date | Work Completed On:
1339a5b2-c4f5-5f49-981d-d6bbddad505e | date | Date:
5d3de49b-e505-5ec6-a691-69b12b12bf06 | checklist | FH-ZU2-QU-ITP042 - AGL Shallow Base Cans - Rev 0 | itp | ITP042 - AGL Shallow Base Cans
6607cab9-33c5-558e-bbf8-f1706ae449f8 | section | 1.0 - Preliminary Works
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
c2322c0b-6788-5c16-a6b2-b5f52c3f4b1a | note | Frequency - Prior to commencing any activity
582e3dce-a077-5116-bcb1-896a02192280 | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
e3466404-cd66-5ad3-816f-0b07f2710d0a | note | Reference Documents - IFC Drawings
e0254087-d69f-5d9e-b0cb-32aaaa397665 | note | Inspection/Test Method - Verify
9672afbb-f6c7-55d5-be1c-0648961a7f7f | note | Record of conformity - Drawings
1f7997ad-9e29-5091-99ce-a1541b6d5d23 | note | IP
0f48af26-3a1b-5468-b326-e04676008e08 | note | Responsibility - Project Engineer
17a5140c-a227-53b6-bb1b-930c20c4a914 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
b1c8abe8-5e01-5fce-ba7d-ae2080b43e87 | note | Frequency - Prior to commencing any activities
d13eb50d-6a5b-516e-8197-610276251445 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
75185538-73d0-5990-9d9d-4de1b0ad90f3 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
abf06095-7bf1-5c21-bbc7-171952b56fb6 | note | Inspection/Test Method - Verify
f78c7b91-f167-5da4-979c-0d175be305cc | note | Record of conformity - Site and office Inspection
dea835b8-8a32-59f0-beb9-f1d6afb64e7c | note | HP*
492d3161-69b5-5d5c-b5c3-3b0b54bb4fda | note | Responsibility - Project Engineer / Site Supervisor
1a761cb6-1739-5231-a304-1740c04bfc65 | date | Date Completed:
de40263c-b7c8-53dc-ae47-1287cd4a5c25 | checkpoint | 1.3 - Material/equipment approvals
f50cddb5-c152-5829-b45b-46febd125cd2 | note | Frequency - Prior to start
9b9f59a6-e8f0-53ee-84c8-344032349d0a | note | Acceptance Criteria - Materials and equipment that shall be used in the construction of the works as nominated on the Drawings.
d3e7a9b1-4753-514a-acdc-719b7b8baabd | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 2.3
deaae5fc-d4fd-5b67-b374-f50cda576d3e | note | Inspection/Test Method - Verify
60f0ecfc-7eda-5125-9186-7f4484e139e7 | note | Record of conformity - Aconex reference(s)
afb90af9-7b48-57f7-97f4-dfe8a2d92a0c | note | HP*
45e049bc-b21a-55b3-85f9-28c9957fe7d6 | note | Responsibility - Project Engineer
13a07e97-e873-5875-8467-feebff81f3cb | date | Date Completed:
37da4ca4-9059-5f77-8956-6bc7d9cb93e3 | checkpoint | 1.4 - Setting out for airfield luminaires
05c67439-9b8e-527d-aa6f-d013651a46bf | note | Frequency - Each Lot
05e3861b-0b08-51b9-9b46-9486ebf45c5c | note | Acceptance Criteria - HOLD POINT
77631a20-328d-56ae-ac12-a64728a96660 | note | ○ The Contractor shall survey the proposed light locations in conjunction with the new and existing line-marking to set out the proposed lights. A schedule of the proposed lights shall be produced and submitted to the Contract Administrator.
0a596d91-2dfe-5bc6-8fe7-22f2ae1fd00b | note | Reference Documents - ZULU- BECA-001-SPC-00003 cl 5.4
5a1db113-abf6-5054-9267-2175089641f7 | note | Inspection/Test Method - Verify
273ff0cc-a6d6-5d2b-a98f-307add13e94d | note | Record of conformity - Aconex reference
f2c6079f-dc6c-5b72-b54e-628f8ee13d59 | note | HP
126f27ca-e90c-5898-937b-a1d6cec09c28 | note | Responsibility - Project Engineer / Beca
29a46fe9-1a00-5314-8e2a-9ffc79f66e50 | date | Date Completed:
96ed5756-8212-581a-b233-9f7850a3696d | signoff | AUTHORITY HOLDPOINT
8c74635c-11ca-5e3f-b186-c4ce6584e1d4 | section | 2.0 - Removal of Existing Can
2ddc3560-ccc8-54c3-96ec-d2cba7a29714 | checkpoint | 2.1 - Removal of existing AGL can
430c3dec-bc91-534f-a831-530fce96f995 | note | Frequency - Each lot
7a4bcd73-9144-5287-9688-89bdb8158b09 | note | Acceptance Criteria -
09135dc2-cdfa-5033-bc59-d13b78cad3e4 | note | Reference Documents - ZULU-BECA-024-DWG-07513
d45ff866-c0a6-5483-91bf-ae3aeca5db68 | note | Inspection/Test Method - Visual Inspection
a3ae43c8-d83d-5aa1-b568-4ffd04218050 | note | Record of conformity - This ITP signed, Avionics Removal of Existing Can checklist
09d4764e-d758-55da-92a6-c02dd52b601e | note | IP
cf42774b-72d0-56f3-aaac-ec33b6793345 | note | Responsibility - Project Engineer
9753c511-dbf4-5b88-a085-a690b4c87e47 | date | Date Completed:
17b9e06c-4a3e-5c10-a953-5d92439f9591 | section | 3.0 - Installation of Shallow Base Can
8226183b-768c-53b8-93be-03436d29a4a4 | checkpoint | 3.1 - Inset luminaire base can
07f4f2fd-e8ed-5279-8e03-7dc69393e65c | note | Frequency - Each lot
ba6cec38-004d-54e3-81b3-9f937287b7f2 | note | Acceptance Criteria -
756cd43f-e403-5130-92bd-300646fcb8bd | note | Reference Documents - ZULU-BECA-024-DWG-07501, ZULU-BECA-024-DWG-07506-8
4648c9d7-554a-5a50-81a0-f4f9d000642d | note | Inspection/Test Method - Visual Inspection
f49a4d2f-8208-586d-ab8d-d784a61594c7 | note | Record of conformity - This ITP signed, Avionics Shallow Canister Installation checklist
eb7f1abb-7df6-5b5f-af4c-4a31f7d1d498 | note | IP
d81b5b99-8c22-5f87-8dc3-7e2b103720a5 | note | Responsibility - Project Engineer
abf7e728-7c3b-5bc4-93ab-576a1813ccd6 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
59e9a41a-9eca-5958-a226-24d2700db36c | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
e1bf6fce-a9da-5ac8-a650-36374942bd25 | textbox | Print Name:
acbb9cd2-1435-5789-a7ee-fbc848bcf068 | textbox | Position:
24ac43bf-4f9d-5dd1-9a2e-d681c5f24931 | date | Work Completed On:
86ff4a10-6933-5b1a-9f8b-9d3c47bd350b | date | Date:
b1fdc53a-5ffc-4304-888c-9ffc226e0e7d | checklist | FH-ZU2-QU-ITP043 - AGL Deep Base Cans - Rev 0 | itp | ITP043 - AGL Deep Base Cans
e6cc6117-6ed6-4dfc-87ed-ba1cfc18e02c | section | 1.0 - Preliminary Works
a50f456f-91f7-4961-9d53-faa865dbb952 | checkpoint | 1.1 - Check for correct documentation
5074af79-1571-5ec8-8010-37d63cae3c7f | note | Frequency - Prior to commencing any activity
c08ead4f-d9ad-5c73-85bc-dc6bb085aa50 | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
4fb23805-6d69-5c73-aa34-206b158af6f0 | note | Reference Documents - IFC Drawings
2d53516b-c556-5b2f-a16a-c424a8b0ba06 | note | Inspection/Test Method - Verify
f2d4e1b9-2b76-5ed5-8876-05e7fb2144ef | note | Record of conformity - Drawings
3e2d0df8-7f93-5c6c-ba4c-6883f2385680 | note | IP
6a5bc82b-f5d1-5275-8d3f-ddaaf1b48428 | note | Responsibility - Project Engineer
b9a184ed-c40d-584a-afb7-92b701458484 | date | Date Completed:
1cf67ab2-fea9-4a6a-8de5-c244f63269e9 | checkpoint | 1.2 - Implementation of all measures and controls
1519c568-7584-5746-abcf-2e2ac85ad298 | note | Frequency - Prior to commencing any activities
3d2aba6c-6ade-536d-8d53-2e0db144331b | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
64dbe181-56ff-526a-a607-2b0d427ae2b5 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
1f2cbc98-56de-5050-bcd7-42c78796631f | note | Inspection/Test Method - Verify
40190f73-d45c-536b-9b7f-ae4196ab03e9 | note | Record of conformity - Site and office Inspection
be40eae5-84e1-5ea5-bf0a-1d7a44cb1bc2 | note | HP*
76ee91c2-9ba2-5408-8169-c5564cf3dfbd | note | Responsibility - Project Engineer / Site Supervisor
986e0914-1a4e-5c55-b895-68fefc9a6a5d | date | Date Completed:
47eb3408-405f-4ab4-9ff4-92f62840c625 | checkpoint | 1.3 - Material/equipment approvals
4eac630c-59b4-593b-a7e8-fa0956d40e38 | note | Frequency - Prior to start
5f5c0080-c594-5ca4-bb4e-22f72dfa8ea9 | note | Acceptance Criteria - Materials and equipment that shall be used in the construction of the works as nominated on the Drawings.
67fe21ee-290e-58a3-b537-6511d20f09ec | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 2.3
b5cefb43-4b29-52c8-b35f-d856f28a20b5 | note | Inspection/Test Method - Verify
8a2b08da-02e4-5033-b72a-8e4155cee58d | note | Record of conformity - Aconex reference(s)
f4d67820-e7a5-57d4-8606-84cc77c9f6ff | note | HP*
05b11070-956e-5d53-b591-884f55f777c6 | note | Responsibility - Project Engineer
f8ef6f06-1915-5764-bec0-95038c0b9bde | date | Date Completed:
ae597d14-9ea5-4676-8246-bd51e6d3105e | checkpoint | 1.4 - Setting out for airfield luminaires
4ecb2dd0-d6f1-5fe8-ac17-96306aa05e86 | note | Frequency - Each Lot
2a0ba7ba-ce99-5303-bc90-ed5ffb0cc54d | note | Acceptance Criteria - HOLD POINT
2d05ec6b-d338-5f73-a3c3-4410b4316d9d | note | ○ The Contractor shall survey the proposed light locations in conjunction with the new and existing line-marking to set out the proposed lights. A schedule of the proposed lights shall be produced and submitted to the Contract Administrator.
254c23e8-d466-55b7-b73f-9c7c12ad53cc | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 5.4
ea11f233-3f36-56cc-9d6b-6facb8a598ed | note | Inspection/Test Method - Verify
18dd6fd2-57ef-59d4-923d-5d6b20e5a06b | note | Record of conformity - Aconex reference
5b0768e2-c8a9-57a8-aaeb-f7882ac1d8e4 | note | HP
ee8979ef-7d0f-5ace-9c7c-b2cbae159de1 | note | Responsibility - Project Engineer / Beca
72e770f6-622c-55f1-bb54-6ecc73e288e4 | date | Date Completed:
8133b17c-5508-4afb-abea-8df67e051dc9 | signoff | AUTHORITY HOLDPOINT
a75122ca-44f2-4ed7-988c-d39fd75e70c1 | checkpoint | 1.5 - Installation of Initial Light Base
14849f58-2a58-5787-ae50-51668b27dfc7 | note | Frequency - Once
fe4e759e-d670-59c8-8f1d-52f3cb8bb9db | note | Acceptance Criteria - HOLD POINT
4f690bff-f3f5-5081-be85-cea430784fae | note | ○ The initial installation of the light base shall be witnessed by the Contractor Administrator
f3f105b7-3586-5616-a4d3-b9c5df50aee3 | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 5.4
a27a3526-4e65-517c-9f62-d1bf251c55ef | note | Inspection/Test Method - Visual, Inspection
0a75a122-9858-5937-9668-4fbbc8f33a94 | note | Record of conformity - This ITP Signed
00fd9954-2160-5097-b0e3-95199a1d4655 | note | HP
6d118091-c10a-5348-bcdb-ba12ac1878a1 | note | Responsibility - Project Engineer / Beca
3831a8d9-8183-568d-b639-55f6b8f0c159 | date | Date Completed:
568e7e69-ebfe-4a01-9a9b-5fa7bd6d5448 | signoff | AUTHORITY HOLDPOINT
80883239-f8e8-4a50-b726-853a96322501 | section | 2.0 - Installation of Base Canister
93670678-455a-4f17-a58c-8bb2fcdf2eb0 | checkpoint | 2.1 - Steel Reinforcement Mesh and Reo Cage
73e50650-31ec-5fb4-804d-f9fa311d004b | note | Frequency - Each Lot
d82cbaf2-e9e8-53d5-8d55-a773ea8cfdb3 | note | Acceptance Criteria - N12-150 steel mesh installed on both direction with 43.5mm cover.
df54a1af-ad32-58b1-9276-b6733d555337 | note | ○ N12 reinforcement cage to be installed as per AGL details
27433d2e-5a21-51bc-abc3-50ad8f5b3345 | note | Reference Documents - ZULU-BECA-024-DWG-07506
2c281575-5f59-56cf-8dc9-1df83d3e65e2 | note | Inspection/Test Method - Visual Inspection
418cf77f-9c27-58be-8816-b9ec18c2391f | note | Record of conformity - This ITP signed, Avionics Base Canister Installation ITC
a3b734d1-65fc-5423-a41d-8a2aa8e6ac0e | note | IP
f878d91c-00da-5a14-b967-dedbd39214cf | note | Responsibility - Project Engineer
a256e952-b782-52db-b17f-4e3c5f3cf47b | date | Date Completed:
dcb518d8-6c3a-40f1-bb12-b96def728c68 | checkpoint | 2.2 - Base Canister and Conduit Installation
0065f323-13a1-50eb-87ed-437306a2b60a | note | Frequency - Each Lot
d8602f9e-cfdf-5432-8667-5850a9c2e4b0 | note | Acceptance Criteria - Concrete encasement for electrical conduit shall have a minimum cover of 40mm.
048453c5-ffb8-5867-8844-d70ace2c11ae | note | – Ensure bottom of can is 200mm minimum to the bottom of foundation.
30077fec-9c72-5967-a178-01fb8286a7d0 | note | – 700mm x 700mm 40MPa concrete foundation
539e29ef-e4c1-5212-a67d-614716a5ff64 | note | – Compressive Strength Test Sample to be conducted per 50 m3 of concrete
3fffc3a7-8f5c-5462-9bf2-e67dd43469f6 | note | – Install 19mm plywood cover with mud plate (sealed and bolts torqued to 40NM)
28887fa0-a15b-5276-bf47-d90c1879c5fa | note | – Check the elevation (RL) of the bottom canister (top plate) relative to the FSL of PCC concrete.
0cab612c-4ddc-5fd0-b6d7-d05f6aaba59d | note | Reference Documents - ZULU-BECA-024-DWG-07507
114e331b-cb96-5dd7-836c-aa5cfe4846a1 | note | Inspection/Test Method - Visual Inspection
d98c9ced-9dc7-5ee6-9f59-4c26ebf252d7 | note | Record of conformity - This ITP signed, Avionics Base Canister Installation ITC, Concrete Test Results
6d64a834-09e5-50a7-96f2-e90ff797dd3a | note | IP
8c0a43ba-1c92-5777-93cf-1abf5a22f325 | note | Responsibility - Project Engineer
4e62385b-debd-5d73-9a4a-d8e696b977d6 | date | Date Completed:
a4bc4f18-5ef5-4419-85da-5787173044e1 | section | 3.0 - Installation of Top Canister
bb71c0a4-e382-4fb0-8564-aa54aa0e2588 | checkpoint | 3.1 - Top Canister Installation
b51ffc26-d3a4-5bd4-8194-accf3d0dc791 | note | Frequency - Each Lot
bc67bcfe-0872-5d28-8588-2a4c4962174e | note | Acceptance Criteria - Core pilot hole (150mm) down to target ring and establish exact centre.
742aa7df-b625-53bf-9c26-f7201df8f207 | note | – Core diameter of approximately 355mm
913dc5ca-f5dc-5271-bfef-8481053f85c1 | note | – Install top canister with spacer rings and dam rings
e51a8eab-e6ab-506a-aee7-d1d47bd41ce9 | note | Reference Documents - ZULU-BECA-024-DWG
ee4a8ce9-8ef3-5297-b123-71780a04b1c5 | note | Inspection/Test Method - Visual Inspection
529f1d5c-ce3a-55b1-b324-c819a6fcfdd4 | note | Record of conformity - This ITP signed, Avionics Top Canister Installation ITC
87565df3-27c5-560c-a315-2974be6ecb6f | note | IP
0fc7941d-2c87-5273-b62a-d30bbc66a3c6 | note | Responsibility - Project Engineer
84259f21-6b0d-514d-8aee-69203abf4f78 | date | Date Completed:
12e378cc-0816-41ed-9355-e6e2b08e644c | checkpoint | 3.2 - Top Canister Close out
f3600858-01a5-5554-8c82-c64c33317ff1 | note | Frequency - Each Lot
0b06a1e8-7ab6-5100-82e6-0045b918cd19 | note | Acceptance Criteria - Install bolts and tightened to manufacturer’s recommended torque using a calibrated torque wrench.
1c29aa2d-763c-511f-bb3a-cd5725b90449 | note | – Apply Webertec FG epoxy sealant to the void between housing and side of excavation
73e0db55-1628-54b3-8895-2fdca41f54c6 | note | Reference Documents - ZULU-BECA-024-DWG
889221e7-b290-5b62-b302-2f1ca5b279ff | note | Inspection/Test Method - Visual Inspection
f97c2aac-c16f-581b-8462-8252ea09a81f | note | Record of conformity - This ITP signed, Avionics Top Canister Installation ITC
030fa07f-961f-5847-9eac-cdbf2d492c24 | note | IP
e26fe6f0-0717-57c9-9997-5958bfcc2ccb | note | Responsibility - Project Engineer
5dfcc4e9-24ff-5452-8d17-09f6c0a7003a | date | Date Completed:
177e2408-5080-4356-a9de-c059a5fab9b3 | checkpoint | 3.4 - Elevated Luminaire Base
5c844d21-6134-5535-b315-cebaad799520 | note | Frequency - Each Lot
65e1fa80-ca79-5e1f-8713-44d02029cad8 | note | Acceptance Criteria - Installed and backfill in accordance with drawings.
7bb0efa7-3f7c-58ea-9cb8-9547c1f50bd3 | note | – Two piece deep base cans to be installed.
08526876-f80d-5488-b081-9ec6154b2fe1 | note | – Min. 500mm cover from finished surface to top of conduit.
86b3c4c4-d36d-5479-8bf0-7bdc77a089f4 | note | – Can fitted with frangible coupling and FAA type/secondary socket retaining arrangement plug and socket.
86fc4c5f-eb35-52e9-b52a-6c13afc83cfe | note | – Foundation and reinforcement installation to match Deep Can Installation for Rigid Pavement
f81a72f0-f127-5560-bb7c-0dca93952647 | note | Reference Documents - ZULU-BECA-024-DWG-07507
b1f1c133-54f6-59a0-a3a8-4d9706cd4544 | note | Inspection/Test Method - Visual Inspection
8ae34061-289a-5cdf-af17-98cf8de4a14d | note | Record of conformity - This ITP signed, Avionics Base Canister Installation Checklist
4dfa7517-d9e8-5af0-952c-3ccbd11c2ba3 | note | IP
58d199e9-125c-5a7c-83c2-31cd43907d1c | note | Responsibility - Project Engineer/Site Supervisor
c84a9d00-1e76-5e31-90ce-99bd34d40327 | date | Date Completed:
c458edb0-a87a-44ac-b39e-0a4ebe256377 | checkpoint | Final Inspection
3a394ce0-6732-5efc-8f4a-efa6d0cc5ae9 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
59e87fb8-765f-564c-a341-2d8585a02867 | textbox | Print Name:
fbfaeccc-44bd-5a0e-beeb-3d6ddca69a69 | textbox | Position:
203c876e-8d96-5b6f-a8a7-ba4c6abb1831 | date | Work Completed On:
601b9e4d-3f1a-5f75-9efe-76e455372458 | date | Date:
40cf46e7-9eac-49b5-a467-46b8a185e084 | checklist | FH-ZU2-QU-ITP044 - AGL Luminaires - Rev 0 | itp | ITP044 - AGL Luminaires
e5362d3e-440a-4c88-8ffa-301e7d7b852c | section | 1.0 - Preliminary Works
31e7f0a4-c455-4f88-a1ff-98420fc51895 | checkpoint | 1.1 - Check for correct documentation
a6e38f86-3110-5c45-b083-15de92494eb0 | note | Frequency - Prior to commencing any activity
844751bd-ae8e-53c3-ae3d-b6ecacf6334b | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
dd12bf58-1e2f-574b-b398-293c033c6389 | note | Reference Documents - IFC Drawings
41ea9812-c297-5ad4-946b-0f4baea30da3 | note | Inspection/Test Method - Verify
f178b106-5210-5f40-8710-817c32bbde6c | note | Record of conformity - Drawings
4d061b82-05ad-5073-be4c-cc006440bb66 | note | IP
fab5e148-9dbc-5f0d-aad3-b7fb6e1e5b2e | note | Responsibility - Project Engineer
db3fd7f5-4a6b-54c5-ab22-e906f30fae5d | date | Date Completed:
20524f49-2c79-4e24-8df5-549c4e2d321c | checkpoint | 1.2 - Implementation of all measures and controls
4777ae02-73c6-52fa-8d58-5792e59f7ef1 | note | Frequency - Prior to commencing any activities
8487d5b2-a3ab-5267-b4e6-b181ef8a825b | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
034bebef-9f96-557c-831a-03a205998114 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
37b643bc-f822-5372-ba03-e0d57ea4e2f6 | note | Inspection/Test Method - Verify
8e79ae68-abed-5ea5-b836-957597c88a89 | note | Record of conformity - Site and office Inspection
e620c074-111f-57e4-9e99-341e6c1eb91a | note | HP*
c3c4c7a3-3f71-5b78-9733-e8d61ff8d786 | note | Responsibility - Project Engineer / Site Supervisor
3793b7ea-53ec-5e47-a52d-edd67a6accdf | date | Date Completed:
a98ed0a1-0267-4280-b1f2-b450e2ff58d5 | checkpoint | 1.3 - Material/equipment approvals
7ca5155c-68e2-59b4-b653-bd961ec5d417 | note | Frequency - Prior to start
f6f8eb81-3795-5365-afdd-df40efded5e8 | note | Acceptance Criteria - All materials shall be proven to meet contractual requirements prior to acceptance.
dcc589f4-e58c-5383-a871-1a18028d7f74 | note | – MAGS shall be from ATG Airfield guidance signs range
1b4cbea6-022a-5b39-8ab3-8120f28c116c | note | – Taxiway centre lights shall be
fa5df35d-d7f2-520c-b72d-da80e3239a09 | note | – from the ADB Safegate range only
c71627c2-9cd2-521e-ab5f-92dd802a73e0 | note | – Runway guard lights shall be from ADB Safegate only.
5025ee73-399e-5b3d-b8f9-4c7166f8f1a6 | note | – Intermediate hold position lights shall be from the ADB Safegate range only
8cad9a53-ea10-540b-acd7-aecad35af350 | note | – Stop Bar Lights shall be from the ADB Safegate
4ea0c8b3-595b-5f70-b383-2b7a38bec3fb | note | – IWDI shall be from ALS
6a9ed3cf-e8a0-54ec-adfa-b3a75cecca92 | note | ○ Any deviation from the above suppliers shall be submitted to the Contract Administrator for approval prior to ordering.
d9ab9d92-e642-539c-9229-96bac8f37d1b | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 2.3
961ef6ce-e2a6-5863-80c8-a6e4f45c374a | note | Inspection/Test Method - Verify
ef7bcae3-6aad-5ff0-a052-56cda408f893 | note | Record of conformity - Aconex reference(s)
fe236a95-2375-52a9-b348-d0951808a12a | note | HP*
6b23cd21-bf33-52f6-b3d5-d97af1e2be0d | note | Responsibility - Project Engineer
9b18b9e4-9afc-57eb-b25e-4a82ab2f659d | date | Date Completed:
18dd092a-730f-4cf2-a606-b6740af5c3e2 | checkpoint | 1.4 - Setting out for airfield luminaires
83e50014-8881-58cc-8457-e9a9a60ee8c8 | note | Frequency - Each Lot
479dcd7b-9b7a-5074-8332-60ebaeca5ded | note | Acceptance Criteria - HOLD POINT
eac1abfd-9163-55ce-9bac-cffdb8648911 | note | ○ The Contractor shall survey the proposed light locations in conjunction with the new and existing line-marking to set out the proposed lights. A schedule of the proposed lights shall be produced and submitted to the Contract Administrator.
9e739e4d-5103-5378-83c1-09e45c4eb0cc | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 5.4
74715ca1-b763-5113-8d01-877ab6432915 | note | Inspection/Test Method - Verify
707e4dc4-8f3c-5822-9d97-d5a9a87ff51a | note | Record of conformity - Aconex reference
3072a521-95bf-50ce-b0ae-389847bc651b | note | HP
04c1edf1-bda8-56ec-8a63-20496dd11d7e | note | Responsibility - Project Engineer / Beca
3ffb6f28-b7b4-521a-892e-37d033c9ce71 | date | Date Completed:
8923ea71-dce3-4309-8883-7365bb4ad439 | signoff | AUTHORITY HOLDPOINT
d8219702-29a7-4775-85f4-6b20e84138f1 | section | 2.0 - Installation of AGL Luminaires
aa23ac61-fe19-46f4-9f99-7d14b9c6f225 | checkpoint | 2.1 - Elevated Light Installation
c2c0e67b-24fd-5188-8f79-b0c451c5d9be | note | Frequency - Each Lot
5f845435-8070-51d0-99c7-98583a5d8046 | note | Acceptance Criteria - Components of elevated lights shall:
b42999df-f20a-531f-a749-20278d413889 | note | – Be less than 360mm above the pavement level including the frangible coupling.
e58238f3-5ce9-50a4-a042-9a2158404d2a | note | – Be suitable for installation on a threaded connection when installed.
769e7879-72ea-5a30-bf4e-4964cbc80b2a | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 4.4.4.1
1b4b2361-bab6-542f-b9b0-fc6520c0e12b | note | Inspection/Test Method - Verify
4c3444fd-d92c-5e1d-b384-95b75d4fb01c | note | Record of conformity - This ITP signed
4bfa64d3-b32d-529d-90ba-6277adf5837a | note | IP
bbbc11de-e167-5a35-a3b5-573c353e9ddc | note | Responsibility - Project Engineer
8be6ee96-8abe-511b-8c7c-7b1fe5d2605e | date | Date Completed:
29807ad5-0d91-4cb4-8e45-3b45d86004a0 | checkpoint | 2.2 - Inset Light Installation
b8727966-1933-50ad-b986-6b16de0560e5 | note | Frequency - Each Lot
dcec0426-348b-5d54-a53a-740001b9d9ee | note | Acceptance Criteria - Components of inset lights shall:
5a4ebf54-c4bd-5992-9640-b8b845306bb2 | note | – Be less than 13mm height above the surrounding surface.
be85313d-6056-5ac6-927e-583d7345e8e2 | note | – Have a slope of surface of the unit to be less than 20 degrees (not including any recesses).
f7c4e446-4e9d-5766-86d0-0250a57b777b | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 4.4.4.3
2d2df26c-ef50-53c3-b0f2-a39a681aa183 | note | Inspection/Test Method - Verify
beb57f01-7f57-5faa-aea7-b9bd533b6a4e | note | Record of conformity - This ITP signed, ADBSG Installation of Inset Light Fittings checklist
d07ce993-9da5-5eaa-a747-a928edd6d3c0 | note | IP
e409c5ee-92c0-5282-8ac3-69e56bac2f25 | note | Responsibility - Project Engineer
67e52dad-c049-5a33-825d-f4beea4d9493 | date | Date Completed:
32664a1a-4029-4bcb-8706-19d973aafb45 | checkpoint | 2.3 - Series Isolation Transformer (SIT)
4830ae71-e313-5466-b4ae-58031081ff8c | note | Frequency - Each Lot
4dd73a3b-ae96-50b5-8599-e9bd16d15cc5 | note | Acceptance Criteria - SITs shall be installed in specified deep base cans or pits
54395ba7-7d93-538b-8bd6-08bf67f571f7 | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 4.3
6d816e99-b430-54ae-badd-7d0d1b9cb525 | note | Inspection/Test Method - Verify
6bbc2fc8-c1f4-5f15-9517-a64e44bb9bb6 | note | Record of conformity - This ITP signed, ADBSG Installation of Series Isolating Transformer (SIT)
3c398358-16e6-54b0-8604-1d89b220ec28 | note | IP
0dbc49cb-39a1-5f62-bdf3-258b2611cef8 | note | Responsibility - Project Engineer
14c0430c-f05a-5c1c-aa1c-66d0e475e361 | date | Date Completed:
e8d6688e-9dfe-46f0-a1f2-a154c1a16828 | checkpoint | 2.4 - Luminaire Circuit
817cbc8a-5372-54a8-9444-2056fc5d2829 | note | Frequency - Each lot
a0938b02-2819-58b6-b7fb-3187a9b9b4ec | note | Acceptance Criteria - Each luminaire fitting shall be installed on the appropriate circuit as specified in the AGL schedule.
d7399dfb-4e9d-509c-8b4c-7b0c2f59131e | note | Reference Documents - ZULU-BECA-024-DWG-09001-16
a4c88368-9055-5498-bfa5-d1598d91c25b | note | Inspection/Test Method - Verify
9f5cb6b6-f789-5e76-92eb-fca4394666b5 | note | Record of conformity - This ITP signed, As-Built Documentation
c6abf804-b828-57aa-8e39-47f893482815 | note | IP
447f8e9f-5ef3-555e-a519-47046b37d707 | note | Responsibility - Project Engineer
870c302e-4cbd-5067-b169-c229133d4520 | date | Date Completed:
66e139b6-7301-4c10-9c82-8bdee84ac825 | section | 3.0 - Post Construction
2c8cff63-7f20-4ed3-aaf4-143e15e5f2eb | checkpoint | 3.1 - As-Built
1e720d91-6aed-5eaa-8350-faee5f426bdc | note | Frequency - Each lot
d211e718-c1a1-5f04-968a-d3859807c45a | note | Acceptance Criteria - Submission of surveyed luminaire position to superintendent prior to practical completion
bbe1e46d-b474-57f0-8544-4c3801e76f75 | note | Reference Documents - WP-001-09
d6b3bdb9-8642-54a6-99ca-d74a61e9f3eb | note | Inspection/Test Method - Verify
89e30b3d-9c47-5a21-837d-274f9e34532c | note | Record of conformity - SCP
a63a45c5-f437-509b-9644-042653df2cbb | note | SCP
eab90674-47cc-53bf-a91c-8fea1e8a1105 | note | Responsibility - Project Engineer
7afdc925-e9fd-50d8-957e-5b545c4e9029 | date | Date Completed:
d1d73c77-6a47-41c6-ae35-7f78df043d9b | checkpoint | Final Inspection
63e52dc8-6d0c-5a2d-90aa-e6c7e550ff2d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
0b3603ab-6b22-50ee-914d-449c3e5fa5e4 | textbox | Print Name:
23824264-d6c3-59ac-92cc-621bd8f206a7 | textbox | Position:
9516638f-d636-5971-a29f-fc2dfc27fd57 | date | Work Completed On:
7cf975b0-7dce-5e21-972f-4c8f943ffe5f | date | Date:
e303755e-82d8-4a03-b8e4-98bdb2ea10a5 | checklist | FH-ZU2-QU-ITP045 - ALER 3 Fire Services - Rev 0 | itp | ITP045 - ALER 3 Fire Services
60e26547-ace1-4beb-9f95-8589dba7ebc8 | section | 1.0 - Preliminary Activities
5c4c347d-6f09-4f89-b430-8fd0bfa94b3b | checkpoint | 1.1 - Check for correct documentation
9b6fcf92-6968-52f7-b553-ae9953495652 | note | Frequency - Prior to commencing works
9753ecfa-4ce7-5455-9539-6ab41062de92 | note | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
3afd33af-6ea9-5374-a124-ba8efcc39b42 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
3b80d107-b556-5843-af16-06bf7d7926f8 | note | Reference Documents - Current Revisions in Aconex or ACC
e66595ad-7f71-55e2-9898-53f1013b65bc | note | Inspection/Test Method - Verify
37121e5e-8516-547a-842d-8accc60bb983 | note | Record of conformity - This ITP Signed
b8582e3e-5de8-5cf5-83d9-2183aef623d8 | note | HP*
d8135261-bffc-5f41-8543-9db89483f084 | note | Responsibility - Project / Site Engineer
f19e370d-63b9-5037-89d3-e6330ad8b858 | date | Date Completed:
f8bd4cfd-24fe-4507-a1dc-26dd7db34802 | checkpoint | 1.2 - Implementation of all measures and controls
b0c5d5f1-0882-53e9-87a6-35f601618961 | note | Frequency - Prior to commencing works
93474f1c-156a-59b2-bb83-a8a25f48e524 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
b85d3662-8d5a-5de3-a215-16523591591e | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
81cb333c-a13e-56a5-a832-4bfb978dbaa4 | note | Inspection/Test Method - Visual Inspection
dc32eb43-9919-5c4c-81be-31f05a95ae3e | note | Record of conformity - This ITP Signed
976c5247-6130-5190-9094-2aba12804bb1 | note | HP*
699c0ca3-bff6-5555-9d50-d837fc4bcf7b | note | Responsibility - Project / Site Engineer
927653b0-cc4d-5784-9946-d99dc080b1f0 | date | Date Completed:
19c2b03c-cff7-4e9f-bac7-14d661291b52 | checkpoint | 1.3 - Submission & approval of shop drawings
6f97ecbf-69f8-5ef8-a95d-f5c7c708029d | note | Frequency - Prior to commencing works
9c1c06d6-bb04-5f58-bf41-17de859b2ead | note | Acceptance Criteria - HOLD POINT
9b516e32-61ff-5523-b441-33622f09cf15 | note | ○ Submit shop drawings, calculation reports & cause & effect matrix to the principal’s representative for approval prior to fabrication commencement.
d82ce73d-b7d4-53d7-8569-b21434b624ed | note | Reference Documents - ZULU-BECA-001-SPC-00005, Drawing Package 030-32
973e68ed-1ad6-55b8-bb75-a295ed794d06 | note | Inspection/Test Method - Verify
a8abb313-903e-5885-9d62-6234bb6cc7b9 | note | Record of conformity - This ITP Signed, Aconex Ref
ba63c1bb-2ecf-5d42-9dd7-1a6e00410599 | note | HP
142737ed-0e2a-5d09-9c97-00c445109221 | note | Responsibility - Project Engineer / Site Engineer / Principal’s Representative
245316db-df15-5989-b730-57c064951b9d | date | Date Completed:
f98cff53-14f2-4232-bb21-f68391cb74c4 | signoff | AUTHORITY HOLDPOINT
d1eac009-6f21-4fc2-a257-75aa0531f5e1 | checkpoint | 1.4 - Material Submissions
fcdff816-0ce4-57f7-a88a-baac4bd51a3e | note | Frequency - Prior to commencing works
f5e473ea-d5e9-58dc-b3e9-c6350c6f4bbc | note | Acceptance Criteria - Items to include but not limited to:
317d9778-08e2-5b4e-9ff9-8ce5d90191ec | note | ○ Fire Indicator Panel (main & Sub)
d0908d49-532d-5f0f-b6e2-fd33feb68556 | note | ○ VESDA Panel
8bc5a034-4fc1-5181-b7c0-131afe3fcfbd | note | ○ Agent Release Control Panel
6adde347-0d8e-5110-9283-08b9f6a08d87 | note | ○ Manual gas release/aborting switch
1e16b1df-3e56-50e9-bcce-6a2f1af83a18 | note | ○ Alarm Speaker
0be3ab2b-ed9b-5d92-bafc-760fed7ee92a | note | ○ Horn Speaker
eeac9b10-f648-5ee9-9587-803d41844557 | note | ○ Visual Alarms
f07d5c02-0293-59a0-a6ae-734a77af6715 | note | ○ Manual Call Points
fe2056dd-4754-52f5-98ea-a5770b8f6ceb | note | ○ Visual Alarm Devices (Internal & external)
c81b6e9e-e7c0-5f26-8d18-3cabc481ea24 | note | ○ All related signage
a0f225d0-71e7-53bc-b2a0-c5917c6e78d0 | note | ○ Smoke Detectors
29d2ae40-8e82-5428-b033-0ff2eac62d97 | note | ○ Thermal Detectors
3ef0635e-6ceb-58e0-88e3-ac865a4e0736 | note | ○ Gas cylinders
fb8fec8c-b530-50d3-8563-e92fbce8b8bd | note | ○ Pipes, connections, and valves
e9910657-212e-5d1c-b6ea-728bd61cd27a | note | ○ Sampling Points and pipes
81acc9e6-6234-5f93-80a4-cdcba4190ffb | note | ○ Pressure relief vent
b7fdbeeb-b83e-5830-9a88-e17be05f76d8 | note | Reference Documents - ZULU-BECA-001-SPC-00005, C2300.6.1, C2300.6.3
eca1a51b-9c5c-53a9-9b12-9eb7a0fb0cca | note | Inspection/Test Method - Verify
29881bc6-6e6e-5f5d-9d8c-52dc4fac9e8d | note | Record of conformity - This ITP Signed, Aconex Ref
70f46b89-ad93-55d7-ae27-72ccd27de35a | note | HP*
0256315b-9a82-5716-b9dd-6dd759e8b5a6 | note | Responsibility - Project / Site Engineer
40d3777f-b05a-5d53-adc9-6dec1e213553 | date | Date Completed:
5db13df2-da95-4ead-8656-e1befe014399 | checkpoint | 1.5 - Survey Set out
c5eedc35-a3dc-5d7b-ba6d-80e9268e98ab | note | Frequency - Prior to commencing works
b41678f3-b2d9-56fb-bb2c-64eed5b6cd29 | note | Acceptance Criteria - Confirm survey set out has been completed on site prior to commencement of works
a759d6df-ce00-5377-b2c1-3f4713e5e3d2 | note | Reference Documents - Survey Process
f1706f92-2c5a-5387-8fac-e7757e08b70c | note | Inspection/Test Method - Visual Inspection
8f922e1d-7f52-53b4-9427-037dcfe1129c | note | Record of conformity - This ITP Signed
85df511d-2cf6-5386-b5c5-b6038242823d | note | HP*
24a51cee-e66e-57fb-a752-04224103af16 | note | Responsibility - Project / Site Engineer
961e313c-7d83-51e2-949f-00f6825cb1a8 | date | Date Completed:
c801a543-8a31-49b7-befb-382092e85094 | section | 2.0 - Construction
930a8c04-38fd-47bb-a8a1-24e63bdf2939 | checkpoint | 2.1 - Installation of Gaseous Suppression System
9ec5daf4-488f-518a-b938-3c7ab6eebd4b | note | Frequency - Each Lot
f73a5996-d0ac-5d1a-a022-8aafb32bfe45 | note | Acceptance Criteria - Installation of Fire Suppression System as per shop drawings and manufacturer specifications. Check for
7381a916-ef10-5733-9da3-76157b16e150 | note | ○ Correct pipe support spacing
d5309b39-f89d-5e81-8fb3-da2b863cc5d0 | note | ○ Penetrations are fire rated as required
776cd5d9-6973-5cde-8abd-a222c4b10de3 | note | ○ In accordance with approved drawings
1787cc1a-deb3-51cb-bfef-50c9f877b771 | note | ○ Gas cylinders
a7699b94-d239-58bd-880b-6a92cb329e45 | note | ○ Pipes, connections and valves
7376f43c-a93e-5e7a-b0f5-724f1cd58b93 | note | ○ Manual gas release/aborting switch
6b4638f0-675d-5840-b60c-453628a027ec | note | ○ Agent release control panel
f95f7cee-6d51-58c5-a843-1832e1cd3d5b | note | Reference Documents - Drawing Package 030-32, ZULU-BECA-001-SPC-00005, C2300
db57a1be-8477-5eaf-a1fb-c7dbfdad06fc | note | Inspection/Test Method - Visual Inspection
04c0eaef-0bc2-58ef-af4a-57139ddc0d06 | note | Record of conformity - This ITP Signed, BE ITC
1555569e-2f65-59da-ac42-cf9f41595b31 | note | IP
2d57531e-9433-5894-b4e8-e5fa2ea6605f | note | Responsibility - Project / Site Engineer
1b11302e-df8a-519b-a781-e61a75e3622c | date | Date Completed:
176e1132-f9ef-4207-95a8-0dad59845d24 | checkpoint | 2.2 - Installation of VESDA Fire Detection
ff145baf-a723-52d2-b431-07022e6cfd35 | note | Frequency - Each Lot
c8710977-2f4e-521b-8bcc-4203bf42200e | note | Acceptance Criteria - Installation of VESDA fire detection system as per drawings and manufacturer specification. Check installation of:
916907b8-f86c-5d3f-8406-d591d71ad07f | note | ○ VESDA Pipes
ad8d5ff6-9f35-5dd3-acb4-4349026e4d18 | note | ○ VESDA Panel
06e668b8-b995-5f19-b602-e0526f288ce1 | note | ○ End cap with sampling point
2b3cf86e-221f-5176-8ce8-7f08e52bd96d | note | ○ 2 way valves
21810c12-a1a1-5bb5-ae63-cff8835b6071 | note | Reference Documents - Drawing Package 030-32, ZULU-BECA-001-SPC-00005, C2300
e44d21d3-fff6-5dec-a474-2d82d8e301a2 | note | Inspection/Test Method - Visual Inspection
78fa6383-b2b6-5d84-9a2f-70dd7f4155c6 | note | Record of conformity - This ITP Signed, BE ITC
3d782cf5-610f-5cc1-b063-1de88fcee60c | note | IP
4780cb13-b11b-5694-b91b-2eafed0d0708 | note | Responsibility - Project / Site Engineer
5bc5ab95-25eb-58d1-983e-c0982df73435 | date | Date Completed:
1a104816-0161-41f4-b795-f1d2b0aafd2b | checkpoint | 2.3 - Installation of Fire Alarm & Warning System
c17ff4c9-3133-5a4f-9468-8ca7e8dc279c | note | Frequency - Each Lot
f86a05ad-1fba-5421-ac03-068f02527143 | note | Acceptance Criteria - Installation of Fire Alarm & Warning Systems as per drawings & Specifications. Check installation of:
46bc6f94-dc51-534f-a251-ccf2d25f57e4 | note | ○ Alarm Speaker
321a2774-b562-56bc-932e-b53832326bae | note | ○ Horn Speaker
65e07572-0afa-5610-b531-6f73a5caa71e | note | ○ Visual Alarms
8492e257-2d6b-5ed7-aa7f-18248186dcb1 | note | ○ Manual Call Points
b9f8de3b-a0c4-5677-bec6-9ecc4d33c8a8 | note | ○ Visual Alarm Devices (Internal & external)
85f23c94-ca34-58c3-8f5b-95196e008b1d | note | ○ All related signage
324d216c-0342-59a8-a557-357bbb0968c4 | note | ○ Smoke Detectors
7b73f6b9-2096-5263-a6d7-b688207d6f92 | note | ○ Thermal Detectors
d8a7a5bd-cc58-5066-b2c1-280cc0b0cefe | note | Reference Documents - Drawing Package 030-32
108d1a2e-e1f7-5ca0-bb21-6d6c0b9b268c | note | Inspection/Test Method - Visual Inspection
7bd15b32-890e-571c-8d0a-88e0be8a2b5f | note | Record of conformity - This ITP Signed, BE ITC
f8f0c1f7-91cb-5938-b9a7-b23f88f5846a | note | IP
8d2c0ffc-a2fb-5db8-82cf-1e94de6c1987 | note | Responsibility - Project / Site Engineer
e1918229-00ca-54c6-a155-6825d3baeea3 | date | Date Completed:
811abc0a-d46c-47ad-abe5-56b03f4db21d | checkpoint | 2.4 - Installation of FDCIE & SFDCIE
10626257-17e7-594d-b8ff-0800510e2f45 | note | Frequency - Each Lot
d5afea63-eacb-52ef-a9c6-8baae261a442 | note | Acceptance Criteria - Ensure FDCIE installed in correct position as per IFC drawing
4f6976c9-9c75-51e6-be2c-37e348c132c6 | note | ○ Ensure SFDCIE installed in correct position as per IFC drawing
61fb37af-5c34-5b14-99b4-172acddbf6cb | note | Reference Documents - Drawing Package 030-32 ZULU-BECA- 001-SPC-00005 C2300
bd0ca027-d6d0-57c5-bc49-1ba24a8b1eaf | note | Inspection/Test Method - Verify
459f718f-135f-5b78-bd79-032eef64da95 | note | Record of conformity - This ITP Signed, BE ITC
637084af-fa37-5203-b043-8f25386f7d36 | note | WP IP
877dd013-c5d9-5580-9959-f0e97d644dcf | note | Responsibility - Project / Site Engineer
d1d43f80-413d-50c3-8a48-f0e8d7dc2197 | date | Date Completed:
30e33695-8510-4e0a-aa3d-4f4b2ea442af | checkpoint | 2.5 - Installation of Fire Doors
d45015fb-c200-5c57-97de-b2e84b315609 | note | Frequency - Each Lot
bf0abc90-4a88-5ed1-b66e-3c954f302f96 | note | Acceptance Criteria - Ensure the door closers are fitted and adjusted correctly to close shut once opened.
f3745253-02f8-52c8-83e2-949c21631f1d | note | ○ Verify the door is fireproof door.
a8a0d4f1-1b5c-5a06-bd77-f7decc31ea67 | note | — Confirm S/N Tags
b1285819-e4e6-5e8e-bf94-e1b3aecc3611 | note | ○ Certificate proving fire door is compliant to AS/NZS 1905.1
5cd32866-7328-5040-a3a1-f4d5cc627374 | note | ○ Ensure the ‘fire door do not obstruct’ sign is installed.
3abe5f50-38c3-55de-ac28-991756eb93fb | note | Reference Documents - ZULU-BECA-001-SPC-00005 – 0453, AS/NZS 1905.1
be6661f3-5c03-5a2f-842f-a7574162514f | note | Inspection/Test Method - Verify
3ba4a675-71a4-5a05-a5ce-429bd22c706a | note | Record of conformity - This ITP Signed, Fire Door Certificate, BE ITC
81e124b3-89ea-5000-adff-e03d6e184d8b | note | WP IP
6060a1c2-b3ad-526f-b521-62c30e49e17a | note | Responsibility - Project / Site Engineer
04ab22b4-3ad4-5ba3-9696-09ab6180b755 | date | Date Completed:
7af3a466-d47c-47af-9506-5598cba0d710 | checkpoint | 2.6 - Installation of Fire Extinguishers
ffe062e4-c4c2-55a7-998f-96c29f5f0bce | note | Frequency - Each Lot
e2e89586-72d8-578a-9ae9-8f9aa9117180 | note | Acceptance Criteria - All fire extinguishers installed as per approved layout. Check:
205a858b-b66d-5410-b15b-37e72d426f7a | note | ○ Installed with horn, wall bracket and visual indicator
5f81966d-14fd-5040-bfbd-3c26abe875f8 | note | ○ Correct type
0fd0372e-bb18-5066-af8b-f27010564da2 | note | ○ Housed in a lockable enclosed metal cabinet
2e0202b7-51e7-5d55-b9b6-0c28be0de8f7 | note | ○ Key to each cabinet shall be secured in a break glass box
5f474c7e-b796-5a79-a86e-8b24b12fcc86 | note | ○ Fire Extinguisher Signs Installed
0816cc91-8a6e-58fb-9724-7d953048d3df | note | ○ Fire Extinguishers have tags up to date
44196ed8-c037-5840-a23d-95035b0a506d | note | Reference Documents - ZULU-BECA-001-SPC-00005, C2300.2 C2345.1 AS2444 BCA 2022, AS/NZS 2444
4fa6955e-6216-5492-999c-dd58321768a1 | note | Inspection/Test Method - Verify
047ff15c-9859-5d82-9f83-1ce7ecc9e493 | note | Record of conformity - This ITP Signed, BE ITC
752e7535-b83d-5088-9abf-2830eaab224a | note | IP
9d60bba0-5ab7-5271-a15f-6a1eb51346b3 | note | Responsibility - Project / Site Engineer
f7a9f6e9-a988-5cda-9eb5-a47532104335 | date | Date Completed:
d4f4d5a1-2dd7-4f2e-bd1a-0cb1696f97c7 | checkpoint | 2.7 - Air Tightness
c07cc270-e884-5a14-bbeb-59fef1bf6851 | note | Frequency - Each Lot
0def3ca7-76f0-5252-a920-14823c3e7d5a | note | Acceptance Criteria - Ensure protected rooms are adequately sealed for the proper functioning of the gas suppression system. The necessary airtightness measures shall be undertaken
bd8e79fe-8d63-558c-a494-fcdc6990c4b9 | note | ○ Conduct room integrity test to AS1851 and provide certification
5220b551-f4e9-5f95-9791-da68c3a3ec51 | note | Reference Documents - ZULU-BECA-001-SPC-00005, C2300.2.2 (ix), AS1851
5a4e7e16-a3a6-51c3-adce-0974214b15d1 | note | Inspection/Test Method - Verify
956e4cdc-22e0-5c8e-8ad2-c0e0bcf1e995 | note | Record of conformity - This ITP Signed, Certificate, BE ITC
bcb9980f-5db4-5bf6-bf5f-34bac99b9c3d | note | HP*
45388bcc-9c37-56d7-8fbb-906d1920b7a4 | note | Responsibility - Project / Site Engineer
0c0eda76-1f7e-5d6f-a8b4-9b6654d007da | date | Date Completed:
72472b1a-7834-4464-9e16-3d7832e1cda4 | checkpoint | Final Inspection
2e865360-4ba3-55a7-992c-55851c467c9f | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
c479bd5f-452f-5af4-b2db-0c17caa28395 | textbox | Print Name:
7650a9c8-8462-5e12-82f6-6becb1c86c51 | textbox | Position:
f8dd9cd4-f7fa-5067-a750-a5839505039d | date | Work Completed On:
48205720-37bd-5ed1-82a6-1a8a6ebac363 | date | Date:
594b8267-cf6e-4564-8dfa-1d7787aaf0ea | checklist | FH-ZU2-QU-ITP046 - ALER 3 Fuel & Generator install - Rev 0 | itp | ITP046 - ALER 3 Fuel & Generator install
274748d3-ab36-4250-8582-b22dff6480be | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
38cdfd54-217f-40ce-8abf-05263bbe4fc1 | checkpoint | 1.1 - Check for correct documentation
7cc4c535-1fce-5497-8e8a-9371dd085f41 | note | Frequency - Prior to commencing activity
4ca29e13-38be-59d3-a5d1-7597eb5a5d8c | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
a66864ef-389c-5243-a20f-16bebab65596 | note | — using the correct and complete set of drawings.
b38c7d4f-856e-5590-8100-b0aed0c3552a | note | — all drawings are the latest revision.
417ef1bb-f108-5114-b4ef-ae9847d4aa01 | note | Reference Documents - Drawings / Aconex Register
e1245936-c923-5912-a219-e14f04eef6f0 | note | Inspection/Test Method - Verify
1565c877-ed19-538f-800a-819dcedbf1e4 | note | Record of conformity - Drawings and drawing registers
e2400bc5-a1e8-572b-a4fc-3e901670d5f4 | note | HP*
18324518-47b0-562e-b6d5-d27b4c119650 | note | Responsibility - Project Engineer
70614ad3-1e3a-54f0-a20f-1749bdeea141 | date | Date Completed:
0d370cf6-0776-42bb-a2db-e84fa90d5924 | checkpoint | 1.2 - Implementation of all measures and controls
386ee8fb-a5b5-5fd3-b8a5-064ee96f9efb | note | Frequency - Prior to commencing activity
99804ebb-9ad4-533d-95a2-99ae10821a89 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
9d59baab-4fdb-504c-a39c-039a1924e4ca | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
50f38d8f-b0a3-550d-9ec6-f61d4e09d720 | note | Inspection/Test Method - Visual inspection
6cd14edf-ded7-5653-9c0c-cf648abfce01 | note | Record of conformity - This ITP signed
ee804362-5d49-5b5e-bc62-b4733b38d491 | note | HP*
3efeb8f1-00f9-5c48-ba59-ba686acbaa5e | note | Responsibility - Project Engineer
917a1fea-6474-579b-a886-2c4c190520c6 | date | Date Completed:
61ebe3ae-ec94-4c16-b744-e827e214ce58 | checkpoint | 1.3 - Survey Checks
6d0305b0-a11d-598b-9091-a0cfa58166f9 | note | Frequency - Prior to commencing activity
bb9bb778-37cc-575e-a00a-c901d75e0079 | note | Acceptance Criteria - Check survey to be completed of all footing positions prior to placing any of the components.
79f8913d-5029-5a11-9933-86e53c9e0d48 | note | Reference Documents - Drawings
1d519c46-a516-5e5a-8ce5-359db6dd948e | note | Inspection/Test Method - Verify
1d3b69a5-b7c6-5490-895c-5f9a75b875bb | note | Record of conformity - This ITP signed Survey Report
89dcd5b9-c8d2-5c50-b10a-8f25f97fd081 | note | HP*
ba61cec0-1a36-535d-86b8-da6b05bd9f85 | note | Responsibility - Project Engineer / Surveyor
520567ea-230a-5f19-86fd-de531fc3447c | date | Date Completed:
c6b02448-1ee8-4863-8dee-fb7b9b4fc6d1 | checkpoint | 1.4 - Material Submissions and Shop Drawings
78491c5a-0d7f-5ab9-ae85-4ede2d29f594 | note | Frequency - Prior to commencing activity
626ec1ad-b2fa-5b61-ab81-eba8043f1f10 | note | Acceptance Criteria - HOLD POINT
d4bb8622-46cf-5edb-9cd5-03b2c1f80c32 | note | ○ Items to include but not limited to:
d1be2739-bf02-5c13-b21e-4bcb0b3807da | note | — Fuel lines
a7186555-1be5-593a-b8ea-b4af63ac15e1 | note | — Fuel line Connections
7a2165ae-6c3c-5cb9-9e4a-2a55cae61ba4 | note | — Fuel storage materials
28542eac-017d-5dae-a73f-8c9adcef3a9e | note | — 900kV Diesel Generator
a28da975-9b2c-50cf-b16e-6be81cc334a6 | note | — Fuel Tanks
6af4aa29-a763-58cb-af0c-dfd130d4814c | note | Reference Documents - ZULU-BECA-001-SPC-00005-C2100 - ELECTRICAL SERVICES - GENERAL Drawings AS 1692, AS 1940:2017 and AS 1692:2006
c4e6fa2f-8a2b-542a-b67c-4b5ed7cee214 | note | Inspection/Test Method - Verify
f196e5c5-05e2-526c-a670-56cdb4822cc7 | note | Record of conformity - Aconex Reference
b9b25827-4523-52f0-83ce-77781086bcad | note | HP
667ceab0-cbc5-5e9b-b928-3ce454f4b7f1 | note | Responsibility - Project Engineer / Principals Representative
7e4f9b65-0bf1-5f72-9284-c0785561d140 | date | Date Completed:
4180df04-6beb-44de-b83c-819bb37f7bc4 | signoff | AUTHORITY HOLDPOINT
47c9438d-32e7-4d51-8bde-edcaf47dced4 | checkpoint | 1.5 - Temporary Works
dbeb1206-2347-5828-9b3b-d85b562b64f2 | note | Frequency - Prior to commencing activity
58b42c8c-bfa5-52ad-9538-4c646f56f6a2 | note | Acceptance Criteria - Submission and approval of documentation based on the Temporary Design Process Matrix
028b92b9-f526-5b63-91b1-bc9ef76eb7e0 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
e161ac31-d5fa-516c-9fcb-315f678f046e | note | Inspection/Test Method - Verify
c6b0f234-c079-57c1-8845-738cab78f59c | note | Record of conformity - As defined by the Temporary Works Design Process Matrix (where applicable)
d2cef5e8-3560-5a10-b43d-0715586c1dda | note | HP*
947480a8-3b7d-5a7d-b3bb-6d4021a3d88a | note | Responsibility - Project Engineer
c4a7cf97-2bee-5626-8a57-67d1b0b7691c | date | Date Completed:
71dbd425-04ba-4090-9329-f1a94e984508 | checkpoint | 1.6 - Off-site Inspections
c2f7b7d8-343c-5f47-bf43-f5145b8c25f2 | note | Frequency - Each Lot
3a1288ed-5df8-514e-830d-d0aaccad8468 | note | Acceptance Criteria - WITNESS POINT
9e0a2e6e-e968-57d5-a174-eed8c555e738 | note | ○ Inspection and attendance on site for Factory Acceptance Testing for:
5034b04f-4ca3-577b-89d9-101bdcf79745 | note | — Cummins Generator
489f6c31-e249-52b9-88f4-e1d7111a03b3 | note | — Fuel tanks
38eaf72d-3e9f-541d-8712-35f5cc870e90 | note | ○ Following these inspections FAT testing shall be submitted.
e757f58a-b1ac-5f6b-87be-9a86baa66295 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
a4510b4d-2972-5142-9dd1-be823615c7aa | note | Inspection/Test Method - Verify
1ac9a655-89b8-5053-a608-fa4cd767754a | note | Record of conformity - This ITP Signed Factory Acceptance Tests
271d26b9-8c15-59cf-a237-77dd011e7265 | note | WP, TP, IP
bef46d2e-04e9-5174-808a-43b3e55dc20f | note | Responsibility - Project Engineer / Principals Representative
231737c2-55e8-55b0-9163-f94d8ac6afe0 | date | Date Completed:
9b3833e4-f6d1-4703-a974-73e5988ae33e | section | 2.0 - Construction
a13e1837-f350-47b1-bda6-35664c04d6f9 | checkpoint | 2.1 - Delivery of Materials to Site
811cdd10-9c65-5817-845e-45124929da52 | note | Frequency - Each Lot
1a2d88dc-f02a-53c5-9645-d0a22b96a0e5 | note | Acceptance Criteria - Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site.
586ed438-91a0-54a6-acc4-601fc0bffc81 | note | ○ Identify any damage/defects prior to unloading of the material.
2c11ee7e-0e8f-52b0-87f0-03e0bede5a04 | note | Reference Documents - Drawings
d56fddb5-afa6-542e-8d9e-428cf69e40a1 | note | Inspection/Test Method - Visual Inspection
11d206c2-5566-534b-9ce9-24f2dd104fc6 | note | Record of conformity - This ITP Signed, Materials Inspection Checklist on Conqa
b7dfed34-b84c-5c4e-9fe8-bf6b91459c40 | note | IP
eb0018af-ee22-56d6-91d9-ffe2df96b70f | note | Responsibility - Project Engineer / Site Engineer
45411ddc-8342-51d6-807a-944f4a7ad125 | date | Date Completed:
a025980d-171f-4d9a-aa10-7b2ff8e0a76f | checkpoint | 2.2 - Inspection of Pipes, Transition Pits, Pits, Conduits, Slabs, and Structure
11171f79-7fe8-5bdb-aea1-f953d28440fa | note | Frequency - Each Lot
25e1dc89-aeb6-5d9f-ba6d-ebc1c1d5c4e2 | note | Acceptance Criteria - Generator/Fuel Contractor to inspect builder’s trench to confirm suitability and as per design
393af553-eaf8-5df9-a595-da84a6da349d | note | ○ Generator/Fuel Contractor to install pipes, pits and conduits as per approved design.
05e96ab2-bcc5-5862-bede-77e8ca64b23d | note | Reference Documents - Drawings
fb6be0a0-dea4-5346-84c1-cb81471fb717 | note | Inspection/Test Method - Visual Inspection
3c5b75ea-b63d-5b21-927a-53a51244efb8 | note | Record of conformity - This ITP Signed
c4b76b5d-253d-5f37-a9e0-a14a59955ec0 | note | IP
1782aaea-9794-5ff0-91a7-78557f7ea643 | note | Responsibility - Project Engineer / Site Engineer
8d837beb-f58c-5068-98d8-a19d5d4655cc | date | Date Completed:
cbdc754a-c4b2-4ecd-a5d1-60f604cb4550 | checkpoint | 2.2 - Lifting Preparation (900KVA Generator, 1000L Fuel Tank and 20000L Fuel Tank)
bb3f8017-b021-5d95-80d0-d798e2c6cc35 | note | Frequency - Each Lot
b2ce9ee4-49be-5a6c-ad84-7aec4d844e69 | note | Acceptance Criteria - Complete Pre-Lift/s Commencement Checklist prior to each component being lifted.
0e2ba1f5-4e92-5347-994a-cb5508eb9454 | note | ○ Ensure relevant drawings, lifting & fixing plans available to the crew.
60c53ed3-42df-5c52-a101-8c36610c29ba | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings Lifting Plan
9237fbc2-269a-580f-bd07-d649e472dfff | note | Inspection/Test Method - Visual Inspection
64aec56d-9058-5c38-9190-5361dae563d1 | note | Record of conformity - Pre-Lift/s Commencement Checklist This ITP Signed
92c367dd-3d80-5bd7-8b74-06e68afe7d38 | note | IP, SCP
a7916264-ca9a-55d3-a4e1-4c6dc88d66f8 | note | Responsibility - Site Engineer / Foreman / Surveyor
a1488c6a-936b-58a5-95f6-98b9c6852af5 | date | Date Completed:
cb75c05f-a56d-4695-bce5-c3459d71582d | checkpoint | 2.3 - Equipment Placement
b50c9c83-19bd-52eb-80f8-37795da1a213 | note | Frequency - Each Lot
87860a00-41d4-5172-930b-0aa01e2c35bc | note | Acceptance Criteria - Survey to confirm component placement as per the design.
23e9b786-7c06-53dd-b7cb-0396d2659958 | note | ○ Install all fixings as per the drawings & engineers plan and suppliers’ specification.
e20e73a7-c3e4-5218-bc70-4d99d4a1dd38 | note | ○ Ensuring the generator is placed on waffle mats for vibration dampening purposes and aligned properly with the radiator duct & exhaust outlet.
7ccc5034-87de-590a-9724-bff615df3adc | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings Lifting Plan
25ea1efb-8329-5ab3-8d0d-f26deb58d6d3 | note | Inspection/Test Method - Verify
ee7a2f99-0c6a-5a3e-9172-d15e37be8d29 | note | Record of conformity - This ITP Signed Subcontractor ITP
d8a709e0-2a4c-5d7a-a8f3-bfcc1b8a87b0 | note | IP / SCP
c7754fe1-2152-55e1-a7c5-fc3f22d16a6f | note | Responsibility - Site Engineer / Surveyor
e09c08e0-6161-558f-b6ee-07c6481ff382 | date | Date Completed:
60340702-e987-4ff0-b80d-2e572406619b | checkpoint | 2.4 - Generator Installation
c5c52141-98f0-52cc-83fe-bc343d14312f | note | Frequency - Each Lot
6ad9e7f8-ac30-5ba4-a75d-8b459e1f73c3 | note | Acceptance Criteria - WITNESS POINT
c20e3df0-09d0-5135-905b-0c1d0746b8d0 | note | ○ Installation to include but not limited to:
675a878a-4d80-58db-a0e7-21a32b2acdb8 | note | — 900KVA Generator
f58d5a60-27ca-5b51-b3bb-9e2273f8373c | note | — Flashings, trims & weatherproofing
18976aba-22d3-564a-84d4-c20ba254d613 | note | — Exhaust Mounting Bracket
f80745b9-fb45-53ac-a58b-0b39c877d4c6 | note | — Intake Cowl
eca18a1e-66ab-5aff-b49a-c7f169f25006 | note | — Radiator Duct
5629bd28-483c-5409-9d9e-e36e2998fc75 | note | — Exhaust System Installation
8ad9896c-d898-5a60-8227-aca8508ccaf5 | note | — Duct Installation
0c9ce274-8918-5986-84d9-edbcf0287c3c | note | — Control Panels
9b733d19-db29-58b2-a930-626972f8c253 | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings, Manufacturers Specification
7477a2a3-0eb7-5a06-b15b-5adb8fe3f986 | note | Inspection/Test Method - Visual Inspection
4b100199-6679-5dff-8137-24cd15522cba | note | Record of conformity - This ITP Signed Factory Acceptance Tests, Subcontractor ITP
efdcfe58-7635-5e4d-8dbc-85b6ea82984a | note | WP TP
43147000-f1e3-54d2-89d7-ab9217065323 | note | Responsibility - Project Engineer / Principals Representative
f3f4f6d6-938c-525d-9f75-67f28640cd12 | date | Date Completed:
c5174327-83ae-4e9a-83d1-9e553692c9f7 | checkpoint | 2.5 - 20000L & 1000L Fuel Tank Installation
e7f35564-45eb-571a-8f53-ced2527c4966 | note | Frequency - Each Lot
20b8fa7b-7efa-5bc2-a05c-f2b56244d31f | note | Acceptance Criteria - WITNESS POINT
05714bc1-0da1-5528-a644-6d07999a9582 | note | ○ Installation to include but not limited to:
08442d5f-fb91-5633-aa1c-7affc237dbc5 | note | — 20000L Fuel Tank
32334f58-6199-5de4-b2e1-701224e73a16 | note | — 1000L Fuel Tank
8ea6eba1-a581-57db-9864-301b09db975d | note | — Fuel Pump Delivery System
1c8053d0-dea3-5f13-a338-2dfb6525cddf | note | — Fuel Control Panel
d153a316-4b40-5305-82d6-079888c2e1c4 | note | — Earthing system (AS1020 & AS4897)
17ba982d-8f49-5008-849f-41b0404e840a | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings, Manufacturers Specification
3c414108-e3e1-5ea8-a2c1-8a75ffdd96b3 | note | Inspection/Test Method - Visual Inspection
4203822e-7e5a-5d7e-b8c6-765aa5ac14c3 | note | Record of conformity - This ITP Signed Factory Acceptance Tests, Subcontractor ITP
5dee1462-5aff-51ea-98a4-c3b9efcc7b0b | note | WP TP
4379118f-c968-5be5-91b6-0ec1177f6e40 | note | Responsibility - Project Engineer / Principals Representative
1feaea4e-4cc2-5c30-9607-d9c47fc04c95 | date | Date Completed:
9a624977-e1de-4c75-be51-09c889f204d3 | checkpoint | 2.6 - Fuel line Connections
3d9b3d18-c525-5fec-b45c-786a31e4d171 | note | Frequency - Each Lot
ad88de69-a2f2-53e2-916e-908845f6e8f5 | note | Acceptance Criteria - Fuel lines are to be connected between the generator and fuel cell(s) and terminated in their final positions.
18dbf027-1678-5279-80aa-58944bd8f6da | note | ○ Ensure bend radius, connections etc are all as per manufacturers specification.
a8b1d9fc-67f7-5869-ba4f-e7fd1d40a1ea | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
bded7121-bbee-5f78-84e1-a28b9a6764dc | note | Inspection/Test Method - Verify
77ae7db1-e29f-5849-8a03-cfdd323043aa | note | Record of conformity - This ITP Signed Subcontractor ITP
e57bb8f4-1287-557f-9c24-74181b2929a8 | note | IP
3e9096b4-162b-57eb-b00e-aecc53014735 | note | Responsibility - Project Engineer / Site Engineer
6e3d14a2-b15f-562a-8cc9-3526d4eafd71 | date | Date Completed:
2ee6fade-e544-4ea7-9103-a8f3d5abf30a | checkpoint | 2.7 - Testing of Fuel lines
fbaef479-0e06-5ed5-b26e-0b63944c6d15 | note | Frequency - Each Lot
4211174f-109f-5263-aa65-5b8b3875005b | note | Acceptance Criteria - WITNESS POINT
d1b35fc8-793f-5845-981e-26b3e96bf53b | note | ○ Fuel lines are to be pressure tested to ensure there are no leaks or weak points prior to any fuel being introduced into the system.
fdb1cf46-9e5f-5c0b-be77-de7a0aee715e | note | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
5c985b88-5c54-511e-8270-827d7f4d1b5d | note | Inspection/Test Method - Verify
dd1f025d-d6e7-54ec-a082-fbf1609ad3f5 | note | Record of conformity - This ITP Signed Test results, Subcontractor ITP
098e2ad0-365d-5303-9eb5-d4326ce3802c | note | WP TP
2832fec7-e09d-55df-aadd-8e280613cd35 | note | Responsibility - Project Engineer / Principals Representative
3a830ab6-8eab-58da-9b8c-388d88c54f31 | date | Date Completed:
53726579-905d-4060-a014-55d8cb32321f | checkpoint | Final Inspection
49dc1757-f5d2-5cc5-99d7-f1e0d15df10c | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
87451f50-61d4-5993-807f-a7eda54aed46 | textbox | Print Name:
f396786b-4e12-55cb-854d-7c5e3531614d | textbox | Position:
136f52f1-5057-575a-9826-055cabb9d8fa | date | Work Completed On:
19f63779-12f0-576c-979f-baeadcd6827c | date | Date:
40b11548-6b9f-44c6-b303-afc7c3d38166 | checklist | FH-ZU2-QU-ITP047 - ALER 3 HV Installation - Rev 0 | itp | ITP047 - ALER 3 HV Installation
5b6e5afd-a190-443d-8f86-86a5487f8998 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
da5fb46c-f831-47f7-958f-242a712ffa28 | checkpoint | 1.1 - Check for correct documentation
009eb74d-4c9d-544d-bb8a-4a0fb70f66d5 | note | Frequency - Prior to commencin g activity
51f3b21d-cec6-5474-9650-b413e030e322 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
de4f5467-e783-5baf-bada-08a46c9a1390 | note | — using the correct and complete set of drawings.
20d6cae4-c07b-53d9-a34d-ae529a7f8b4c | note | — all drawings are the latest revision.
4777c2ee-e357-548c-9caf-2fda32496738 | note | Reference Documents - Drawings / Aconex Register
9c1119a4-8534-5bee-8649-ee9fed517de6 | note | Inspection/Test Method - Verify
4b9acbe7-12ea-5e29-8a2c-6804c7aa2733 | note | Record of conformity - Drawings and drawing registers
70655d95-17b1-567f-9249-6b0a936d2e2a | note | HP*
c1970bc0-b354-59ab-9d94-47361da19ba3 | note | Responsibility - Project Engineer / Site Engineer
84b11b85-18f5-5f84-98fa-7a6ca5c214c8 | date | Date Completed:
f6fb716b-8057-4061-b5aa-c886a917440f | checkpoint | 1.2 - Implementation of all measures and controls
b5fb97fa-4548-5ebc-876d-b01e3799430f | note | Frequency - Prior to commencin g activity
7fc20643-22cd-564f-b2d3-0231d2b61310 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
0f330cf2-f16a-5d8d-8fad-49ee96f47553 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
6e7d7cac-b7f5-5618-8f51-40bf9ca80e68 | note | Inspection/Test Method - Visual inspection
126a18b9-f416-5c61-927c-09ff19bf80da | note | Record of conformity - This ITP signed
d5f4293a-c080-5710-adc8-ec6d4fa4916b | note | HP*
69a866ec-d87a-553b-99f1-c509cb8f8045 | note | Responsibility - Project Engineer / Site Engineer
0e3f392c-8665-5a52-b99b-1792699f05f6 | date | Date Completed:
a953ce3e-3caa-46e7-af62-c44fc0431bb3 | checkpoint | 1.3 - Survey Checks
f50eb643-4d32-5c99-8e7d-05bfe172353a | note | Frequency - Prior to commencin g activity
caa5abcb-5251-509c-8ced-2046869b9755 | note | Acceptance Criteria - Check survey to be completed of all footing positions prior to placing any of the panels.
54f6127d-e8d8-53ba-9351-02ce1ee99744 | note | Reference Documents - Drawings
51bdf3a5-f734-5912-8b70-e57f5881f029 | note | Inspection/Test Method - Verify
13080363-828a-5aee-837a-ee602fa85e7a | note | Record of conformity - This ITP signed Survey Report
b9386163-4b43-50ee-a179-43901737ab15 | note | HP*
2879ff42-b75a-5ffc-b501-bb13aa0b2875 | note | Responsibility - Project Engineer / Site Engineer / Surveyor
a72b2717-c978-5120-837a-1d46adbcded9 | date | Date Completed:
afcc2ed7-656e-44eb-840e-3860ae45a025 | checkpoint | 1.4 - Submission & approval of shop drawings
0f258020-dbac-5b92-b197-869975226fa6 | note | Frequency - Prior to commencin g activity
6e7f2ccc-b9a2-527e-a2d7-777c5cfb3756 | note | Acceptance Criteria - HOLD POINT
2f8bcac2-0d77-58e1-868a-7c4d3e0c037c | note | ○ Submit shop drawings to the principal’s representative for approval prior to fabrication commencement.
e5d8da74-cdc9-558d-aa31-f5e6437c2cb3 | note | ○ Items to include but not limited to:
394ecac3-eaaa-59ab-8972-e6299030b519 | note | — HV Kiosk
6ef9e1d5-6e3f-5ab9-bc88-7a4547bde908 | note | — ATS
42a308a8-e4b7-5b54-b037-54610af51ca6 | note | — DB-GEN
63b9bb76-d0c0-5eca-b502-f94b88972c10 | note | — 400 KW Load Bank
3406fb1d-7c33-589e-aa1e-5fd2e9df1cb0 | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
0ae5e3d0-946b-5796-8fb2-2dd313e384f9 | note | Inspection/Test Method - Verify
6313ae0a-7015-593e-a04f-e8361000c41e | note | Record of conformity - Aconex Reference
58098be0-6512-5345-96f8-81542e96f539 | note | HP
0f1620e5-b929-5512-b73c-452c91c84f74 | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
fa8152dc-9423-59d3-93ba-ff4cd2657a83 | date | Date Completed:
b0fc6ac4-86ae-4e71-881b-195b90942486 | signoff | AUTHORITY HOLDPOINT
ba803a1b-4c75-4e05-81c5-4e18b0b7ba37 | checkpoint | 1.5 - Material Submissions
99cf8c71-a9a7-5ad0-95f8-6d3ba9820bc3 | note | Frequency - Prior to commencin g activity
2e339517-0d09-5d03-916b-e2012849315a | note | Acceptance Criteria - HOLD POINT
10c68a33-310e-556c-b492-c783faea23b2 | note | ○ Items to include but not limited to:
1effe553-4871-5b74-af3b-e4a4f5503367 | note | — Bonding Conductors
8f40e64c-5a4f-559d-888a-81c98ee3c0c7 | note | — Copper Conductor Connections
1dce8c34-9189-50de-aca4-32a66dbeda9e | note | — Earth Backfill Slurry Mixture
9a09b0a6-3ae5-581a-a739-96dd1f8d624a | note | — Earth Rod Inspection Box
6c17b89c-6f48-52b1-9eb5-7ed6a1362cc9 | note | — Grid Conductor
9dc1ca3e-de3b-528f-9236-ef4c1dcb52d9 | note | — Permanent Earth Cable Elbow Connection
8956d08a-efb9-5288-b9a8-0fe578d14cae | note | — Sub 164 Retention Barrier
ebbd16a4-0445-5ef1-a034-0ec13eeb0c6c | note | — V90 PVC Insulated Un-stranded Class 2 Copper Conductor
a77b0484-4899-5eaf-bf66-f29dd7033f0e | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings AS/NZS 1252.2
f4f95bb0-bbaa-5863-a0f2-39e9fdeea745 | note | Inspection/Test Method - Verify
a8cffcfe-32e3-517e-aa5f-6073709ca3ac | note | Record of conformity - Aconex Reference
52e4f45c-cf9b-514e-95de-223cb635a06c | note | HP
276db7f4-c0dc-54a6-b894-6b4ee44685c5 | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
e509f7f1-3beb-5577-b8d2-002e8ffb3aaf | date | Date Completed:
238def69-dc44-4c4f-9e89-bcf160cd8357 | signoff | AUTHORITY HOLDPOINT
d5c7ea84-906c-4924-9210-66c06af06a9f | checkpoint | 1.6 - Temporary Works
2ab1c6d3-3ac2-5819-a978-06ab114b3351 | note | Frequency - Prior to commencin g activity
b31a5d99-2554-5263-8c79-e3540da8ea6f | note | Acceptance Criteria - Submission and approval of the following documentation based on the Temporary Works Design Process Matrix.
e462d007-6daf-525a-b7ed-278bdd6590e6 | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
8fb23cf5-b1de-5bf0-bb3d-b80ed47c60bd | note | Inspection/Test Method - Verify
60466089-d451-56ef-80d8-448ccf9efc1f | note | Record of conformity - As defined by the Temporary Works Design Process Matrix (where applicable)
995a576e-bfaf-536b-9b70-a9f90574d043 | note | HP*
7d318009-0d4e-5526-b3e3-f76876d1a1ba | note | Responsibility - Project Engineer / Site Engineer
bf9139d3-5cea-564b-b912-8f454b2f1549 | date | Date Completed:
19308983-2d61-4795-828b-2088e036b270 | checkpoint | 1.7 - Off-site Inspections
8c22031f-a5c2-51c2-86cd-084234cd525e | note | Frequency - Each Lot
be6314b3-0b37-507c-9c45-cc004fccb251 | note | Acceptance Criteria - WITNESS POINT
6b74f833-b480-5f81-9f8b-1d9d27f4920e | note | ○ Inspection and attendance on site for Factory Acceptance Testing for:
34488c35-3e32-5c66-9e58-b17bc85ec5bc | note | — HV Kiosk
2149dc3b-9dac-55a8-ac79-b37c7f709183 | note | — ATS
d1380b16-d589-5170-937b-2522aa937b05 | note | — DB-GEN
148ef95e-58cf-5710-8f85-266f03cfd364 | note | ○ Following these inspections FAT testing shall be submitted and associated certificates.
3510da1c-cb5a-5925-b58b-54ed8bd33be7 | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
c159380b-d6fb-5620-b55f-25ff6daa7d8c | note | Inspection/Test Method - Verify
02d7c05a-1ee2-5743-a613-1fc2fda8b09f | note | Record of conformity - This ITP Signed, Factory Acceptance Tests
deaf9972-a930-5319-9afe-0b23e095b2d1 | note | WP TP
f9363b54-4d48-546f-b1e6-a1b62fbaba4c | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
97be9ad1-bd96-5bd3-845f-c311205fb755 | date | Date Completed:
57555599-a096-4b88-9217-1ea1e4095383 | section | 2.0 - Construction
83d4c20b-1fce-45b0-ad8b-70dc8a4b1bf2 | checkpoint | 2.1 - Delivery of Materials to site
80d760ff-e637-5b2e-98d3-7d39231bca11 | note | Frequency - Each item
0a73f756-19b5-55a3-b623-7ffe1d35c6db | note | Acceptance Criteria - Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site.
92f9761a-5776-5106-8659-9499dce61d92 | note | ○ Identify any damage/defects prior to unloading of the material.
b6c0be82-caf4-5f6e-b987-596ab13d8ff7 | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
c8ccd7c7-f626-5ef5-a417-ec12e36732be | note | Inspection/Test Method - Visual Inspection
67deacd9-320f-5196-9597-f3860f17f585 | note | Record of conformity - This ITP Signed, Materials Inspection Checklist on ConQA
a8e4b91d-84a6-540b-8868-23154f0fd037 | note | IP
65ad963a-d578-5a8e-bd51-2218a597fca7 | note | Responsibility - Project Engineer / Site Engineer
052cb17d-a635-5e73-a774-0038730d2613 | date | Date Completed:
f9333ee1-b290-4e23-87d5-82a8fda51893 | checkpoint | 2.2 - Inspection of installed Pits, Conduits, Slabs and Structure
967e3a55-d9fc-500a-9e92-45292c3db410 | note | Frequency - Each Lot
e3fa7266-0510-5039-a4f2-94704e07a29e | note | Acceptance Criteria - HV contractor to inspect the builder’s installation to confirm suitability and as per design
64a1fa81-5c49-52de-9201-d4ef198ca372 | note | Reference Documents - Drawings
2098787d-a4b4-58e3-9f73-e544af4fe21f | note | Inspection/Test Method - Visual Inspection
9a7f8880-e641-5c17-a462-9e0433625028 | note | Record of conformity - This ITP Signed
11811a26-7fea-5e29-a005-0a24b842b150 | note | IP
63d8bba1-7c82-5ae4-833b-a92d2b34a0d6 | note | Responsibility - Project Engineer / Site Engineer
ea43a675-32a5-5c69-8edc-271620e9c4f0 | date | Date Completed:
228a2211-8bc3-4f05-9b31-f0e92d977c57 | checkpoint | 2.3 - Isolation of existing cables
21c8da2d-a4c9-5510-ab73-50a97e72d0a7 | note | Frequency - Each Lot
105d69fa-1e3f-5cba-8cb0-a6898e5c8555 | note | Acceptance Criteria - Cable to be isolated and earthed at both ends. Ensure correct cable is being isolated as per information on hand. Check Isolation by testing at a suitable point.
ad8ce7e2-6a94-5398-acb9-6ab453b630ec | note | ○ HV cable to be disconnected and taken out of cable compartment.
aeba442b-ec18-5e7b-8dd8-10558c507b3b | note | ○ Existing HV Cables shall have Seath IR testing completed prior to modification to the cable to provide a baseline final testing as per MAS- ELC-002
405a6df1-3d59-51ff-bc12-d977a36ef200 | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
829b86d8-d3f0-5bdc-aab2-2584a062614b | note | Inspection/Test Method - Verify
58f738a4-af4b-56de-8ba5-221873c4df7c | note | Record of conformity - This ITP Signed Test results. Nilsen ITC
c8d906e0-27b2-51f5-bf2b-abb9fa897321 | note | IP / TP
c6da8a8f-bc84-516e-b5b2-a27c715a1038 | note | Responsibility - Project Engineer / Site Engineer
5ad32442-3468-5909-a9af-7e988fc9a54a | date | Date Completed:
3f1f23c9-75a5-48a1-af81-1e90df24faf8 | checkpoint | 2.4 - Cabling – Mains, Submains & Earthing
e94b3c1c-6aa4-57f9-82c9-504313a2e37e | note | Frequency - Each Lot
495014d5-acba-56e9-ab09-741e802a2efc | note | Acceptance Criteria - New cables to be pulled through pre-laid conduits using the provided pull strings.
3273707e-fa50-5dac-9c97-496a23d8d21e | note | ○ Cables to be sufficiently secured out of the way prior to component installation.
d2fec0b4-9346-5c5a-a248-2e0b6f49d9d3 | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
902e08e4-7eb7-5753-8dd6-3aedf72e3f40 | note | Inspection/Test Method - Visual Inspection
3f7eeb51-7531-5946-adb2-89c2d410d086 | note | Record of conformity - This ITP Signed Nilsen ITC
79729edb-36f6-5c03-9c05-5f7c1779c5a9 | note | IP
e1d604cc-a01c-5034-a92d-e6928b60545b | note | Responsibility - Project Engineer / Site Engineer
6563e082-e873-54d4-8201-3b2770647e69 | date | Date Completed:
ea2a1e51-a25c-4791-b972-3f1544fb2b7f | checkpoint | 2.5 - Lifting Preparation (Kiosk)
a0a19c28-e1d9-505a-bcb4-175e43b49b37 | note | Frequency - Each Lot
f4c9993b-6707-5fee-91ac-168071836d7e | note | Acceptance Criteria - Lift Study available and approved.
060841c4-9779-55ca-8704-8e1b39d6b1da | note | ○ Temporary Works for Crane Pad approved and constructed.
9a97926f-b50e-56f8-a61d-81f02853c888 | note | ○ Complete Pre-Lift/s Commencement Checklist prior to each component being lifted.
6d7e880b-ff2a-57e7-a8a0-d8f3e9d25bdb | note | ○ Ensure relevant drawings, lifting & fixing plans available to the crew.
0690df0e-1efc-5410-a8de-9397c2c0cf78 | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings Lifting Plan
4cf9a2b2-be60-5665-8bc2-162847092b30 | note | Inspection/Test Method - Visual Inspection
2749dbf9-2da9-5823-bc2d-c9399d92eef1 | note | Record of conformity - Pre-Lift/s Commencement Checklist, This ITP Signed
f14793f5-8cb2-506d-b075-fd7c43f43cee | note | IP, SCP
dc665189-df39-5336-9482-ba65212d7047 | note | Responsibility - Site Engineer / Foreman / Surveyor
be4bd1cc-7a0a-5e5c-9cbc-7889f850fbda | date | Date Completed:
79ab0a8a-f5c8-4e99-b6b2-a13527a0636c | checkpoint | 2.6 - Component Placement (Kiosk)
6618c6f0-688c-5769-b9cb-3e907ee8c478 | note | Frequency - Each Lot
147e0ad7-153b-5459-8ee6-57853a180d01 | note | Acceptance Criteria - Survey to confirm component placement as per the design.
550ba43a-b362-58b2-9b28-43a114ac7f30 | note | ○ Install all fixings as per the drawings & engineers plan and suppliers’ specification.
41dc303a-f797-58ff-a1db-83a0dfcb3f67 | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings Lifting Plan
81d9928f-9099-5e31-9c26-3faf959d92c4 | note | Inspection/Test Method - Verify
2da4b04e-f5a2-57c4-8b12-18e2a8df9728 | note | Record of conformity - This ITP Signed
6282c523-69ae-5831-9edf-ad2c18395ed2 | note | IP / SCP
3757cf0a-a651-595b-b8d8-5b870f877215 | note | Responsibility - Project Engineer / Site Engineer / Surveyor
f04219e3-a302-58ea-8c6d-d5ae2f664d5e | date | Date Completed:
8c0c84ab-e6c2-44b2-aa21-841d7d1fd83e | checkpoint | 2.7 - Installation of Earthing Grid
fa87884e-1e10-5e1c-a839-b1f0291d2519 | note | Frequency - Each Lot
317c7f18-56fb-5296-abfc-8abfefbf960b | note | Acceptance Criteria - Installation of Earth Grid as defined by IFC Drawings and MAS-ELC- 002 (Section 5.7.3).
6078970e-925a-5c16-8230-96cd11ef62bf | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings AS/NZS 3000
2f0d7103-0045-52a0-9022-b47ce46fd00e | note | Inspection/Test Method - Verify
4eaa8331-d901-5208-ad3a-747a7bde2252 | note | Record of conformity - This ITP Signed Nilsen ITC
c6d6ab88-dd6f-5097-9915-b9370ab7aaae | note | WP
3a531369-545a-50ea-90c0-feeeb6a06418 | note | Responsibility - Project Engineer / Site Engineer
2f94bdf5-1b1e-5bd6-a28f-1846c1bcd53f | date | Date Completed:
b30e8048-b775-4957-9bad-f08fc91a3767 | checkpoint | 2.8 - Earthing Grid Testing
9ff5c466-731c-5373-b438-831e4b308f5a | note | Frequency - Each Lot
d26d8ac8-7177-5009-bcb2-eeac016024ff | note | Acceptance Criteria - Earthing system to be tested as per MAS-ELC-002 HV Standard – Appendix B, including:
577076d7-45cf-54ee-a022-2b5f2ee71ba1 | note | — Continuity testing (earthing and bonding conductors)
c15fd46f-3759-5549-8eef-440a86f1296a | note | — Earth resistivity testing
4872a20f-2339-534e-9d21-1c8a59ee9db6 | note | — Earth potential rise measurement
397f25b6-dc70-511e-bac3-873c02ba3a6f | note | — Current distribution measurement
32a14fde-9acb-59a0-a262-e21604eb5983 | note | — Transfer voltage testing
995fa628-fe58-5b52-b23e-64ccc7611462 | note | — Touch voltage testing
09dd4744-2f9f-51d9-a584-35c4205993ef | note | — Step voltage testing
6a80a40e-e2d4-5b39-ae36-adb09d8ecd6f | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings AS 2067, MAS-ELEC-002
c4b29a2d-5d1f-5a01-a0d1-d4d5b89231ed | note | Inspection/Test Method - Verify
2f005f4c-010a-5763-a5e7-24b5571c91da | note | Record of conformity - This ITP is signed Test results
5cff7d10-988f-572a-9dab-30551cf988a2 | note | WP IP
8e261f69-fc2e-5856-a75d-02b3c8cf2567 | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
c6f3f082-4f00-5f57-93dc-0299c58841b4 | date | Date Completed:
44850724-527a-4a09-9e15-de8fc46c2e56 | checkpoint | 2.9 - HV Cable Terminations
354a3f41-1cd6-5705-a040-6609dadd4c90 | note | Frequency - Each Lot
d8a60ddf-9d56-5ce9-81f5-4482f0e5118a | note | Acceptance Criteria - Relevant cabling can be installed into allocated cubicle. Terminate HV cables in the final position.
25d78ea1-9c0f-547f-aa6e-0915e38578e3 | note | ○ Confirm cables are installed into correct cubicles.
106dd3d4-f277-58e8-bcb3-12f2353d3e45 | note | ○ Confirm earth ring cables terminated to relevant earth bar/position.
b899e5a1-1c52-5ccb-ace9-9cbf4b906584 | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings, HV Access Permit
41e6ca46-1e86-54e0-bf19-8bd8e0fd2a00 | note | Inspection/Test Method - Verify
0d9dd3b4-279b-58ff-a6ef-ae00892ec39c | note | Record of conformity - This ITP Signed Test results, HV Access Permit, Nilsen ITC
c43573e0-45eb-51d5-94df-787836463c26 | note | WP TP
0f01eab8-0e8a-56db-a83f-4c6946a7c23b | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
3bb92d80-a3de-5d67-8edf-da36cb0f0e34 | date | Date Completed:
4b8ce082-10ba-49fb-8d67-67386fe3732a | checkpoint | 2.10 - Testing of New HV Cables (Before Energized)
b323ed61-328b-5617-be24-181c2afc75c8 | note | Frequency - Each Lot
01dd94b3-67e0-5a51-9c33-c69a4169639f | note | Acceptance Criteria - HOLD POINT
91a97ffd-3d34-5643-ba52-2eae40bc7ec6 | note | ○ Confirm the following items are constructed in accordance with IFC design and specification.
a1884bb2-45c9-5254-abd4-1bbee8f67371 | note | — Type, size, colour, quantities, location
841facfc-19de-5879-bb55-352e600f451c | note | — Secure
8cf39663-126f-518e-b5b5-6f47632df73f | note | ○ Verify and confirm the following tests as per AS/NZS 3000 (not limited to):
1832275c-1199-5b86-ad07-6a6b865b5eb9 | note | — Polarity Check
dfadcc89-d720-5722-92a5-68e764bdb80a | note | — Cable Loop Resistance (Ohms)
10b311a4-1af0-5ec9-81ae-181d5373c26e | note | — Insulation Resistance (Core-Core& Core to Earth)
0bec14b8-12af-5d16-bfe4-a89b93495c00 | note | ○ Ensure HV cable connected are bolted up at both termination ends. Testing to include all testing required as per MAS-ELC-002, including VLF testing etc
f7343c98-8cd9-5257-87e8-7f3e56770e5c | note | ○ Ensure new earth cable connected and torqued at both ends. Upload and testing of protection settings into HV and LV CBs. Testing of SCADA Points to EMCS.
30733f25-915d-566a-9ed0-d94207edf216 | note | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings, HV Access Permit, AS/NZS 3000 MAS-ELC-002
ef2ff882-6a4e-5209-b091-b6164bd9c679 | note | Inspection/Test Method - Verify
a5dbe641-4147-53f7-b191-24cbf3d85389 | note | Record of conformity - This ITP Signed Test results, HV Access Permit Nilsen ITC
7b01426a-0ede-5e00-a0ae-1ff176b72106 | note | WP TP
fc230f4a-2635-5c05-aaf0-9f3105b64687 | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
154b78d2-63bc-5120-a68d-65ca5d37ff47 | date | Date Completed:
7ad83487-dc9e-4072-a245-81f723afb4b6 | checkpoint | Final Inspection
388bcb28-3d02-53b6-a43e-bc49612c2543 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
b0de278b-fcf7-5a3e-bc36-3acb6bfa635f | textbox | Print Name:
77ea117a-980d-5dc3-b1c3-e3e2919f7997 | textbox | Position:
208a40f7-725b-5dda-afa6-dcad0be3dde8 | date | Work Completed On:
7f5f9190-8d12-5401-98b2-93cfd3d43045 | date | Date:
387b04e8-51e3-4302-8abc-1c71f1ab1815 | checklist | FH-ZU2-QU-ITP048 - ALER 3 General Fitout & Finishes - Rev 1 | itp | ITP048 - ALER 3 General Fitout & Finishes
71765bcc-e035-418c-a522-5c7240d442bd | section | 1.0 - Preliminary Activities
82148329-5883-42a8-8325-d0dbd4a07fb0 | checkpoint | 1.1 - Check for correct documentation
1569920e-2755-574b-8a06-60bf071dc436 | note | Frequency - Prior to commencing works
affb0c67-1f44-5292-ab98-4b7a44e8c3bc | note | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
71107fc7-6663-55e5-b68a-12157c532489 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
0e51160d-a86c-525b-a903-8d59e3472d2e | note | Reference Documents - Current Revisions in Aconex or ACC
988e5233-0430-535f-be0d-6b707a317ffe | note | Inspection/Test Method - Verify
987ec886-fe66-56af-99e4-7c3f0440f920 | note | Record of conformity - This ITP Signed
9222eb23-03bb-526f-a110-bbca88644113 | note | HP*
c65ab3c7-8c17-5283-9f03-7863c9a3797e | note | Responsibility - Project / Site Engineer
46b8d3ca-c2b2-5117-9878-4e69550be08c | date | Date Completed:
00bd31c9-51b6-4065-bb1c-23248f858bcb | checkpoint | 1.2 - Implementation of all measures and controls
2f378e9f-6220-5f4f-af53-aa9da0e06e57 | note | Frequency - Prior to commencing works
08691e97-681a-53fa-a3e9-6a4ed1efe100 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
52184e54-dc99-518b-8ee2-08ef578a956b | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
e5e30699-29ff-5390-838d-b21ef494a819 | note | Inspection/Test Method - Visual Inspection
57af1f02-d0f2-5a82-b4d4-f77173ae357c | note | Record of conformity - This ITP Signed
a43a0dad-828c-5f00-bf86-645cf682a645 | note | HP*
ab5f3394-03e4-5ca2-9985-c69c5dda08d6 | note | Responsibility - Project / Site Engineer
c32c003c-fee6-597d-9299-b2a2b31ec56f | date | Date Completed:
61c81f21-0b85-4692-bf90-050f16a16ef8 | checkpoint | 1.3 - Check all materials & shop drawings have been approved for use
0a7ad73c-35f4-5d85-a02a-2ade80021ebb | note | Frequency - Prior to commencing works
6ee02961-c947-5c42-a3eb-a235bdc9fcaf | note | Acceptance Criteria - Ensure all materials & shop drawings have been reviewed & approved by BECA.
ca44d3f9-6ce7-50e0-a84a-0efe38ef87d6 | note | Reference Documents - Materials Schedule Drawing Package 030
3a62eb20-2d63-50f3-a38d-960457106a3b | note | Inspection/Test Method - Verify
f1c5b363-89d6-5e54-bd96-3c6eaa0a3ceb | note | Record of conformity - Aconex Register
229df714-be81-51cc-aa62-2f7382698309 | note | HP*
b77553e5-2f23-5c2e-938d-5a9692739add | note | Responsibility - Project / Site Engineer
73f9a687-a0fa-5d40-a5d0-99d7e83f7658 | date | Date Completed:
11475bc7-6fc5-42b4-bf59-2bc829b48a8d | checkpoint | 1.4 - Material inspections (off-site)
31395cfb-c027-5b7a-8897-a1df22613fb8 | note | Frequency - Prior to commencing works
456f57d5-aeb7-55af-9172-c3ec988d652e | note | Acceptance Criteria - WITNESS POINT
3c5f7c5e-fd95-57b8-b5ac-1d8f86606c0b | note | ○ Give notice for inspection of fabricated window assemblies at the factory ready for delivery.
92fc7cf0-d690-5652-a308-4f4ee449e244 | note | Reference Documents - ZULU- BECA-001- SPC-00005, 0451
adca769b-ff5e-5e03-b511-43a10b028532 | note | Inspection/Test Method - Visual inspection
2543a1ac-3332-5fe4-ab66-1be8e07f0177 | note | Record of conformity - This ITP Signed, Inspection Report
88bc23fd-18bb-56c7-81ac-ac2ebc4a8719 | note | WP
f91a965d-b6cd-5da8-a348-fd9c98c5e9d6 | note | Responsibility - Project / Site Engineer / Principals Representative
e9f1c215-9994-5de2-97d4-f98b2674dc74 | date | Date Completed:
43569aff-6d15-4771-9687-5e8b774e26d4 | checkpoint | 1.5 - Material inspections (on-site)
3fada14a-0599-5a0f-9c27-71813fb813cc | note | Frequency - Prior to commencing works
e607b5a3-3c18-536f-b8e4-a8dbc7ec20b7 | note | Acceptance Criteria - Complete a material inspection for deliveries of the following items:
b4c49d92-8e7c-53da-ad8d-a15f75d3494c | note | ○ Roofing
674db405-6806-5c07-b8d7-0e3986785c40 | note | ○ Light Steel Framing
4d811c4a-5777-51bd-a2e2-e1d5bdf9b955 | note | ○ Glazing
cd18de37-f729-544e-bf48-5a9f7e079499 | note | ○ Insulation/sarking
4f155bad-adf8-5a0b-989e-155d6e5e3641 | note | Reference Documents - FH Quality Procedures
a70ef51e-dff4-5b7d-a4f8-105d58daef3c | note | Inspection/Test Method - Visual inspection
6291d2d6-75d8-587c-ad09-689fbab7a4f6 | note | Record of conformity - This ITP Signed
b4055b36-af17-500d-b153-5a5f5b24f24b | note | HP*
fa529de5-2aa8-5890-be6a-91d9b2dbfdbe | note | Responsibility - Project / Site Engineer
91feedfd-b5fe-5b36-a53e-9e68131a330c | date | Date Completed:
9143c8d9-8ee2-4557-bcd9-d997b88ea9d8 | checkpoint | 1.6 - Survey Set out
f5e87f8b-3baa-55b0-8790-4255cd32c7a5 | note | Frequency - Each Lot
d7263785-4e98-520c-8d65-f92c2c5feb87 | note | Acceptance Criteria - Confirm survey set out has been completed on site prior to commencement of works
04ab567b-c6ad-5eaf-b20c-36df9422d4b1 | note | Reference Documents - Survey Process
80e80219-027b-51af-9384-72030f58b845 | note | Inspection/Test Method - Visual Inspection
871b29e4-d475-5e5c-b832-04dd8a817ef6 | note | Record of conformity - This ITP Signed
8344e273-9b4a-5d5f-9fda-52bff5d0c789 | note | HP*
78c87179-9954-5d7a-a21a-087bd8b6a9b2 | note | Responsibility - Project / Site Engineer
909a765f-6660-517a-8dc6-bd1c08115003 | date | Date Completed:
8731080e-0b92-47d4-ae7a-72bb32cd6cd5 | section | 2.0 - Construction
e77382a2-a4bf-45cb-97e4-f0023616ae40 | checkpoint | 2.1 - Roofing
3784af9f-5892-5cd1-9455-d459ebe377c4 | note | Frequency - Each Lot
f22ce040-f9e4-5b5f-ab6a-3fa03f5c0636 | note | Acceptance Criteria - WITNESS POINT
fc346737-5241-58d3-91a1-2e8ca5e9829e | note | ○ Check for installation of the following against manufacturers specification, project drawings and AS/NZS standards:
b5b0d7d2-e697-5922-a517-3e3ca882b25b | note | — Roofing battens
40687f3a-c136-5417-91ea-7d23f3d30ad6 | note | — Insulation Blanket
21fc8278-e3fb-5be1-8668-e64478509a3c | note | — Sarking/vapour barrier
129c91e7-0a61-520b-b366-c6db966064f9 | note | — Roofing Sheets
91505c7c-91ce-5a68-b55b-3e3fb78fb359 | note | — Gutter Hail/Leaf Guards
3b259b48-5f9b-5ea0-be94-f7d46b1b904c | note | — Eaves Soffits
1539d4f9-a1ff-5517-8a48-a2f39f046f31 | note | ○ Notice shall be given for inspection of roofing supports prior to covering up or concealing
60261554-21ee-595f-8764-a583906b8732 | note | Reference Documents - Drawing set 030, AS 1562.1, ZULU- BECA-001- SPC-00005, 0423
c0c00af0-98cf-5af3-9e1e-94c4232641bc | note | Inspection/Test Method - Visual Inspection
96e20172-ee0c-5572-b637-a0a04b142c27 | note | Record of conformity - This ITP Signed, BE ITC, Compliance Certificate
c7ab52b9-a4c0-53e8-988a-7ac7209a86a6 | note | WP
e692a7bf-292b-5a9d-92b4-c1ea03f5c0c5 | note | Responsibility - Project / Site Engineer / Principals Representative
fff9f376-f00b-5a4c-a88e-4edae4307def | date | Date Completed:
34e813d4-8b56-48fe-8d8c-7245c3d4af0f | checkpoint | 2.2 - Glazing
9e92b8a8-be91-5a49-ba54-9fe6494e2f05 | note | Frequency - Each Lot
64a4b9f7-45eb-5f4d-a377-aa668ef8e24a | note | Acceptance Criteria - WITNESS POINT
1bc9ed2e-a278-5335-8a57-4e34c382c9a0 | note | ○ Installation of all windows as per the project drawings and manufacturer specifications.
fe39e5d1-7527-5e4c-9bc2-1b402e801208 | note | ○ Check windows are plumb, correctly sealed and securely fixed.
112858cf-968f-5622-b1ce-40e6c9d7863d | note | ○ Give notice for inspection of the following:
0788560b-600f-541e-a156-454f001778fe | note | — Openings prepared to receive Windows in precast walls
fffa979b-da36-50f8-b4e2-6a48f14dc470 | note | — Commencement of Window installation
81ccbf36-1e0a-5186-b219-d6a36235a850 | note | ○ Certification required confirming that window assemblies conform to AS 2047 (2014)
6cf1bde9-0a2f-5d00-bc63-2ab5ada7f616 | note | Reference Documents - Drawing set 030, ZULU- BECA-001- SPC-00005, 0451, AS 2047
0b6f6314-46bf-582b-b2fc-3f7c9d74cf22 | note | Inspection/Test Method - Visual Inspection
027aece3-7ea8-5182-b5e4-00be70b55401 | note | Record of conformity - This ITP Signed, BE ITC, Compliance Certificate
eca327c5-6555-5094-abf4-cf004b4124a5 | note | WP
25c551c9-0a25-5bf2-b68a-9d16f1da537c | note | Responsibility - Project / Site Engineer / Principals Representative
d966bf25-6a52-5a0d-8e8e-ff16e70e584e | date | Date Completed:
39d4c039-3163-466b-bdad-2098d01f1612 | checkpoint | 2.3 - External & Internal Door & Jambs
18cf1767-660d-5e13-a79c-b1fcaa2c0a17 | note | Frequency - Each Lot
721b0717-b3a9-509c-978a-76d816409d28 | note | Acceptance Criteria - WITNESS POINT
bf24d47f-c3a5-59b8-9b22-f0e0a3c0470b | note | ○ Installation of the following
970cdf2b-6462-556b-b717-014af8accd20 | note | — Door frames/jambs
84134c1d-01ba-52d1-aabb-d086ccd5bb25 | note | — Hang doors
3a32ecfe-f375-5384-8e90-7b430a86eaac | note | — Locks, latches & handles
1160613c-63cf-57cc-985a-10f0c2561980 | note | — Fire Doors – as per certifiers requirements
4e5c8e89-6599-5efc-8b6a-0b154dbe733f | note | ○ Check for
7c0c9c66-48a6-56b9-a55e-26186d6a04db | note | — Plumbness
ad291b33-4e87-561c-a03d-10e9cff9fbd7 | note | — Securely affixed
d4d4b501-7792-5e8e-8e75-feb07e58e2e1 | note | — Proper function
d2327fa9-8f0e-521e-8180-b9edad387aa5 | note | — As per drawing sizing & locations
ec0e4646-ab53-5bdf-8379-73c1bfeea38c | note | — Adequate clearance bottom of doors
7ce75aca-f216-57e9-a943-23d2527e7e23 | note | — Sealing installed as required
cd31b31b-070e-5864-8272-c55b0c3f9aa6 | note | ○ Give notice for inspection of door frames in place prior to any joinery/trim being installed.
c266d930-97ba-5916-8fb4-b70ba17c3530 | note | Reference Documents - Drawing Set 030, ZULU- BECA-001- SPC-00005, 0455
e55252f3-d8fd-5cad-b0f2-df82027f27ac | note | Inspection/Test Method - Visual Inspection
fc7b07ae-434e-5800-ade2-68347b4d43f1 | note | Record of conformity - This ITP Signed, BE ITC
8b01f211-8867-524f-aefa-497410184164 | note | WP
3f3ac091-ab9d-5654-9f74-4e97200c7ff8 | note | Responsibility - Project / Site Engineer, Principal’s Representative
013c5497-ac8f-534a-a4ca-56a3321c20ee | date | Date Completed:
2ca43b19-10cf-48a3-9338-20495e33e8c0 | checkpoint | 2.4 - Wall & Partition Framing
5dd59736-20de-51a0-bff1-a0721bfbab49 | note | Frequency - Each Lot
030c7fad-306d-59de-b3de-4860f0f64dee | note | Acceptance Criteria - WITNESS POINT
b401a721-f530-5e46-9ab3-c141662e13a5 | note | ○ Installation of Light Steel Framing to the project drawings and as per manufacturers specification.
fa873e97-f3ad-5127-b9cd-f91033bbe781 | note | — Max Stud Spacing of 600 mm
2599023f-6bbf-55a1-9fe0-9dad2605e120 | note | — Damp Proof Course as required
ec43df72-a124-561d-8113-5b043b9c840a | note | ○ Give notice for inspection of the following
9c570ad4-8b38-54b2-bc1c-aef2a879732d | note | — Set out prior to construction
024ae0b8-c538-50d0-b435-b6e176ee5d3a | note | — Wall & Partition framing prior to plastering/lining
c1e1a46d-cfad-5608-b863-b8f2dd93bba7 | note | — Framed & lines partitions ready to receive framed and glazed components
bf9b863c-5cb2-5399-b08f-0d43d807e73f | note | — Completion of installation Certification required confirming that the erected frame conforms to the documented project requirements.
3015fcc7-bd74-5297-bedd-f4c7f0f7da0a | note | Reference Documents - Drawing set 030, ZULU- BECA-001- SPC-00005, 0342
f4049c9d-c8ae-54e9-b4d2-a4269759aa85 | note | Inspection/Test Method - Visual Inspection
000385d8-12e5-5d4f-b8a4-9eb21bb96f10 | note | Record of conformity - This ITP Signed, BE ITC, Compliance Certificate
89659934-fd18-5fcb-8c67-79d9d35ef8a2 | note | WP
949b0c29-dbfe-585c-a65a-0ef54c9c21fc | note | Responsibility - Project / Site Engineer, Principal’s Representative
c088c7bd-e03e-5974-b3fd-4c0b5050e6e2 | date | Date Completed:
2332eea7-73f3-40b0-9f6b-65345f2320ab | checkpoint | 2.5 - Fireproofing – Fyrchek Panels / Ceilings
8ba034e0-8f90-56b4-acd0-046722b867fa | note | Frequency - Each Lot
bfe80276-41a5-591c-b557-ed327d60a175 | note | Acceptance Criteria - WITNESS POINT
d162ab32-5a59-5c20-86a9-34e3098815d5 | note | ○ Ensure the following during installation:
6867a8f7-6391-55a8-a508-4eac45068f8a | note | — Butt joints flat with no visible gaps
7c5fe17b-c156-554b-964e-92385444bed5 | note | — Junction with floors and ceilings straight and true, and allow for a 10mm fire caulking gap
e50d767f-954c-5e01-9b56-775cd5ac03ba | note | ○ Expansion joints, taped joints and setting per spec and manufacturers requirements
f5b3597a-5999-5fca-a659-a147c16733a6 | note | ○ Give notice for inspections of the following:
87195833-9a36-56dc-a770-fb1fd6b28d75 | note | — Control/construction joints completed and ready for fire- stopping
1fc8bccc-30ce-56ff-921e-f6a2ae3075ba | note | ○ Finished Fire Stopping prior to concealment
79cd0acf-fd1f-5c16-ae28-54617f5497e4 | note | Reference Documents - Drawing set 030, ZULU- BECA-001- SPC-00005, 0511, 0182, Gyprock – The Red Book
c1a3b7b7-b806-5f58-b6a3-4c59f0ea0e64 | note | Inspection/Test Method - Visual Inspection
4760cf3d-5ed5-5c09-907c-b8f91c1b52bc | note | Record of conformity - This ITP Signed, BE ITP, Fireproofing Certificate
b12a4213-678f-5a90-9936-91fd940393ac | note | HP*
8b8dedbb-9d0f-5815-8ff3-296d9881be26 | note | Responsibility - Project / Site Engineer, Principal’s Representative
35d57e4c-f365-5752-8268-cf8e90da5592 | date | Date Completed:
46da049b-e7de-47a9-a3b5-436c6d288baf | checkpoint | 2.6 - Suspended Ceiling
fb7a6e06-5d80-5679-9a60-e62cc4e2066e | note | Frequency - Each Lot
d1bf00df-45bd-5481-96a7-1292069c924f | note | Acceptance Criteria - WITNESS POINT
bde953e0-bc1b-5856-9203-e9f37021f41d | note | ○ Installation of the suspended wall system as per manufacturers specifications and to the project drawings.
4221a44f-6cf8-5361-bfd3-d2836ae3edc1 | note | ○ Ensure ceiling height is correct.
db8e80a3-68ae-5738-a4d7-50905de8adb0 | note | ○ Give notice so that inspections can be made of the following:
eb036aa8-2417-553a-8668-4bd12c6319ba | note | — Suspension system before installation of lining
99c4ec30-c68a-536f-8fa0-3ca1c554410b | note | — Ceiling assembly before installing of fittings and site painting
022dfc29-276a-5246-a8d4-301b4f15dbaa | note | — Completed Ceiling
5ae3d02f-8b8b-5de2-a654-ca7f2e0e63f5 | note | Reference Documents - Drawing set 030, ZULU- BECA-001- SPC-00005, 0532
40323f05-4a39-58d7-b071-81562fdbe213 | note | Inspection/Test Method - Visual Inspection
51e49f46-99f8-5400-88e8-3256701e592d | note | Record of conformity - This ITP Signed, BE ITC
fb6bb127-e6db-5b4f-b6dc-8780944c54e1 | note | WP
4c965696-a7e0-5ce2-ac3c-8e5cbdff017b | note | Responsibility - Project / Site Engineer, Principal’s Representative
d5f8bd3e-fe89-5b8d-a2ce-0f56132d4fba | date | Date Completed:
fa88e38c-0cb5-40dd-8192-dd11a90e0aab | checkpoint | 2.7 - Insulation
8a64bbe0-2986-52d5-b92a-02fc96b3de89 | note | Frequency - Each Lot
5a63f0ee-69b4-5837-86d5-99d907d4622f | note | Acceptance Criteria - Install all wall insulation prior to plastering/wall lining.
1d68cd92-3e62-5459-9a08-1212e02d5783 | note | ○ Ensure adequately placed and secured.
861ad847-538f-58fe-bb26-349d2561b618 | note | Reference Documents - Drawing set 030
1d84f2e8-d3e8-5324-b488-573123ccb7d6 | note | Inspection/Test Method - Visual Inspection
66663c20-0c40-563d-9420-54e912ec3519 | note | Record of conformity - This ITP Signed
ad2fe35f-530b-5310-a75b-c4043434053c | note | IP
29862900-7af1-5c63-a848-8f67d30f01ba | note | Responsibility - Project / Site Engineer
86e017f4-dd4b-5459-abb4-8b87ae8ef570 | date | Date Completed:
d1c436a4-ed38-41ad-a76a-5a6fa1dc90d8 | checkpoint | 2.7 - Plastering & lining
f4f4fb07-14cf-52ec-8c55-fd3951c3129b | note | Frequency - Each Lot
b7949853-7f94-50e4-9700-59616442215d | note | Acceptance Criteria - WITNESS POINT
d6975bbf-2d50-5243-be0c-ace31fffed6b | note | ○ Installation of the following as per manufacturers specification:
eab65a65-b1e3-513c-9bea-ac7fe4cbd20d | note | — Wall Plastering to steel frames
41350e4e-cf0f-5c69-9a10-6c793e53d1bf | note | — Ceiling lining to suspended ceiling
ce25e632-d85a-5408-bc0c-ba98509cdb6f | note | ○ Expansion joints, taped joints and setting per spec and manufacturers requirements
473f1e59-7715-59be-a109-83c8b9a040ba | note | ○ Give notice for inspection of finished surface prior to applying sealer or finish coatings or decorative paper
1288633c-a514-5328-9d28-f88b3dde4057 | note | Reference Documents - Drawing set 030, ZULU- BECA-001- SPC-00005, 0511
88d8b61c-00de-5194-95c5-65b32b4201e1 | note | Inspection/Test Method - Visual Inspection
f4226d54-9efa-58d9-8813-757c68250b97 | note | Record of conformity - This ITP Signed, BE ITC
77b1dffc-b5b7-5e6a-887c-741f26f07ca2 | note | WP
dae4ffd6-4a4a-5c3d-bbb8-215ed5fa2b09 | note | Responsibility - Project / Site Engineer Principal’s Representative
ff3f8bbd-ae72-56c7-8b3f-529297bc1e77 | date | Date Completed:
12b1bb25-f6e5-40e5-a8a0-e1d7093cff99 | checkpoint | 2.8 - Fireproofing – Penetrations
8ad26e3c-5acf-5c92-918a-2b5573710f35 | note | Frequency - Each Lot
24d5c6a9-791a-5b5f-8e87-66e1522a45b6 | note | Acceptance Criteria - Ensure the following for all penetrations in fire rated rooms:
ed4d4d3e-1d9c-5b84-a919-e4eac3a44533 | note | — Penetrations are sealed and approved
b4ab348f-df1d-57a2-9628-b8a7a7a24aad | note | — Fire collars are installed as per manufacturer specs
679749c7-55f5-5616-94b3-a23943797fab | note | — Verify door jambs are filled in or packed
06de94fe-38ee-5895-b508-e06ff2df61fd | note | — 500mm run for junction seals
3035db50-2707-56db-8790-983733d84a6c | note | — 500x500mm area for penetration seals
ff87c433-6896-54a5-824e-39c59ba96cd5 | note | ○ Give notice for inspections of the following:
94649d54-299e-5aef-a55c-bf064e03ccfb | note | — Service penetrations completed and ready for fire-stopping
c04bb1df-536d-5541-88c6-95ce512d0932 | note | — Finished Fire Stopping prior to concealment
76498162-b4e3-5b4b-b430-abab02115681 | note | Reference Documents - Drawing set 030, ZULU- BECA-001- SPC-00005, 0182, Gyprock – The Red Book
a5a35bb1-7186-5688-a0a5-d1aa4b1270be | note | Inspection/Test Method - Visual Inspection
a0427760-b4f3-5593-8597-e96585772b5b | note | Record of conformity - This ITP Signed, BE ITP, Fireproofing Certificate
1eee4887-bfbe-5fb4-9e37-66a6374cf688 | note | WP
25174823-996f-545f-8a6c-e5f210bf4547 | note | Responsibility - Project / Site Engineer, Principal’s Representative
fc36bb30-91e0-511a-9238-aa11788a00ea | date | Date Completed:
acfacc70-7712-4209-820e-f8b5c23e6ef1 | checkpoint | 2.9 - Joinery/Fixing
76f0315a-f5ef-5c8f-8665-c79cf8e2648c | note | Frequency - Each Lot
1ea12d32-277f-5dc1-b044-89b280892cc7 | note | Acceptance Criteria - Installation of the following in accordance with project drawings and as per manufacturers specifications:
ee5d3633-aa74-59fa-bc04-0600e5ff1a04 | note | — Skirting
d86bb272-239d-584b-a17a-8b7d617bb0ae | note | — Architraves
ebc22509-81f3-57ef-8f5b-ad6cf5120f3a | note | — Cabinets (if applicable)
ad0bf5ae-324c-50e6-92f9-5e6f08e6fa7f | note | — Door Handles
c470dad7-0c53-567e-ac37-1255d653f429 | note | — Grabrails
ac9324e5-1f20-59f8-9c9f-d5ebdc933f3a | note | — Toilet fixtures such as soap dispensers, toilet roll holder, paper towel dispenser etc
f7fc5b10-e2bd-5a84-ada4-567c699f23eb | note | — Door close speeds set
11bd4ed5-3408-5fc5-abea-aeea687df34e | note | — Kick plates
9f7dcb54-d87a-5375-882d-40f58bff5857 | note | Reference Documents - Drawing set 030
e437e0f8-5b2b-5cf4-ba79-a95477b6dc13 | note | Inspection/Test Method - Visual Inspection
c064cb27-4ad7-5920-8f39-fefe89b8c0b0 | note | Record of conformity - This ITP Signed, BE ITC
e5c20a80-d8f5-5a4b-83a6-97c9aebfd394 | note | IP
af725d5e-c43d-5e8a-be21-24c1b45544ef | note | Responsibility - Project / Site Engineer
4071eaf7-d842-5bc7-905e-4d668232589e | date | Date Completed:
8f6e8e9b-bb1c-4705-809b-629a98743cda | section | 3.0 - Finishes
9c727057-4a3b-422d-9598-0f0662707cc6 | checkpoint | 3.1 - Painting
ff57b7a2-d770-51bd-a1d9-e919f85acc73 | note | Frequency - Each Lot
f18e087e-b4b7-53bb-bfd8-0113f6a8eaed | note | Acceptance Criteria - WITNESS POINT
1256dd3e-686a-512e-abdd-b259bc7cf236 | note | ○ Painting off required components as per specified colour & paint.
1af8fb98-48b3-5cce-9271-a508993cca8f | note | ○ New unpainted interior surfaces: To AS/NZS 2311 (2017) Table 5.1.
12dc8a22-16da-55ef-b349-9a42127afe4b | note | ○ New unpainted exterior surfaces: To AS/NZS 2311 (2017) Table 5.2
d287fad4-1405-5c40-a92d-2f42853e8c23 | note | ○ Give notice for inspection of: Opaque finishing stages:
deb37eb1-cf43-5bf8-83ec-7be0c271ddcd | note | — Completion of surface preparation.
464878ba-c49c-5ff5-b3f1-90bcfbda49ca | note | — After application of final coat. Clear finishing stages:
8b6db6ab-287f-5c46-9413-9767dfdb3883 | note | — Before surface preparation of timber.
40db2cfb-8d37-544a-92d5-639350f9dc0e | note | — Completion of surface preparation.
783eb65c-e018-595f-8b0f-7954bea2bec6 | note | — After application of final coat.
802fabd9-b5cd-557d-9f24-1601fc9715d3 | note | Reference Documents - Drawing set 030, ZULU- BECA-001- SPC-00005, 0671p
f5265081-2fbe-5ff2-8394-accf12da1d76 | note | Inspection/Test Method - Visual Inspection
dac316f4-de06-556d-a5f9-caabdcc06c54 | note | Record of conformity - This ITP Signed, BE ITC
6ceab4b7-3485-5a47-9aca-20c85e7e9e7b | note | WP
e96c24af-987a-5bd5-90a6-cd074c0643d9 | note | Responsibility - Project / Site Engineer, Principal’s Representative
025ffbe0-938a-5df4-914f-ba06f455c989 | date | Date Completed:
92e5911e-7b85-447c-8069-3fbe025cba91 | checkpoint | 3.2 - Waterproofing
955ed04c-7a13-54c0-86ad-d76ef83a248b | note | Frequency - Each Lot
bbf81ead-08d0-56e5-932b-30e44d4518a5 | note | Acceptance Criteria - WITNESS POINT
427f3422-88de-51d5-b2af-20724f8425dd | note | ○ Installation of approved Waterproof Membrane in strict accordance with manufacturer’s instructions and to the extents covered in Aconex BecaCPL-GCOR-002069.
152909af-4d07-53d7-b789-6cd5f2d8bfb8 | note | ○ Give notice for inspection of:
4e9546dd-0879-5d36-824f-733c3886814f | note | — Substrates prepared and ready prior to waterproofing
4f9cb9b9-4a86-5f60-91c9-4b7ae195afc3 | note | — Secondary Layers prepared and ready for subsequent layers
e4303c1e-0828-587f-ae9c-8a07cac25879 | note | — Membranes after installation and before concealment"
44bce4b5-1777-5f81-abea-a26967f96d0c | note | Reference Documents - ZULU BECA-001-SPC-00005621
4da459b3-d108-55a3-aff5-45c37b1f055e | note | Inspection/Test Method - Visual Inspection
77379b67-6349-5f64-8b5f-0d9917981355 | note | Record of conformity - This ITP Signed, BE ITC
9073e57d-aea4-5d06-b6c3-3bcbdce8428e | note | WP
15ad67fe-8ca0-59d2-a70e-5792f79807ee | note | Responsibility - Project / Site Engineer, Principal’s Representative
4877cd6b-8fab-5d7c-bee7-1a6d0717c572 | date | Date Completed:
d53ac908-b940-432a-8c25-be91fd82c24a | checkpoint | 3.3 - Flooring
8341d306-ea94-5a23-ba03-b423a07f4df1 | note | Frequency - Each Lot
903bfe94-a435-53db-aa58-786149c19d54 | note | Acceptance Criteria - WITNESS POINT
edb9d75d-079e-53fb-b0f0-ced2cc1b9155 | note | ○ Ensure all flooring surface is level and falls to drains have the required grades prior to installation of flooring.
aa4df830-8542-5648-8585-7c1a1547e5d0 | note | ○ Installation of the following strictly according to manufacturer’s specifications and project drawings:
6f6a0541-785f-5e81-8d7e-f4fd8a48a465 | note | — Vinyl Flooring
3a7a9c4f-febe-58a2-a852-5e09a975a0de | note | — Resin Based Flooring Give inspection for the following: Resin based Flooring
32d8f9be-3f6d-5e57-88ed-e3a3e3e6be95 | note | — Completion of substrate preparation
eda86625-9e57-5059-8d71-798855201ae9 | note | — Substrate joints, thresholds and perimeter walls
f27647df-7d95-5188-ae3d-3913d0a89494 | note | — Completed priming of base.
c05ee0d7-aa3e-549a-bb7d-57cfc2cdd9fe | note | — Completion of each coat in the flooring system
17f2a431-d740-57a0-9c2b-696d40a4a2e6 | note | — Completed application Resilient Flooring
fe27741a-01c9-5f36-a009-51d4cf3058b5 | note | — Substrate immediately before fixing resilient finishes or underlay
63d1ce23-2dd0-5b4a-b7c7-47a8c3807d7d | note | — Trial set outs before execution
69ceeab9-25c8-5615-a642-7494c27860e0 | note | — Completed underlay, if any
8f1b7e31-0898-5ca9-aa40-e6248868f882 | note | — Finished surface before applying sealers or polishes, if any
b355c41a-867c-5f40-aac0-95cd6cdeae1b | note | — Completed installation
e6b1f353-3681-5f15-9d14-750d1b34b3e9 | note | Reference Documents - Drawing set 030, Materials Schedule, ZULU- BECA-001- SPC-00005, 0657, 0651
bf733fe2-5d3c-545e-8e3c-13c80d83ccbd | note | Inspection/Test Method - Visual Inspection
153e7d96-2831-5ca1-b18d-0a5c49038282 | note | Record of conformity - This ITP Signed, BE ITC
dfde5c55-f809-5bb2-9ca0-6a27ed1fb467 | note | WP
eac95cb2-adef-56af-96e7-a958f2562bb7 | note | Responsibility - Project / Site Engineer / Principal’s Representative
cbe3ea68-e642-5671-ac9f-cc595a011817 | date | Date Completed:
9f863566-56bf-407f-aa61-81c02cef68dc | checkpoint | 3.4 - Furniture
2e6fd97c-c2d9-57e2-bd95-c04c01766f5a | note | Frequency - Each Lot
603e00ef-70d4-507f-9ab9-2c7126445eae | note | Acceptance Criteria - Delivery and installation of approved furniture.
c2bd93ba-300a-5ddb-a9b1-547b8a8c52df | note | ○ Installed on site as per manufacturers specifications.
54220b00-f621-55b8-b409-c62df598a32e | note | Reference Documents - Drawing Set 030, Aconex DCWC Mgt-GCOR- 010265
c805e58a-b6e8-5f42-8daf-905ec8e6a178 | note | Inspection/Test Method - Visual Inspection
9c9c1fd8-b969-50c0-977b-b17220be318a | note | Record of conformity - This ITP Signed
425fedee-f0f8-5a31-832d-7802fd1930a7 | note | IP
86efff61-d79c-54d6-81fd-d4dffc8af56b | note | Responsibility - Project / Site Engineer
ce89112c-e2d1-5e47-ad92-ea08f0f42bfb | date | Date Completed:
746caf49-7e44-41ef-9964-c1364b207916 | checkpoint | 3.5 - Mirror
7d4f69f3-6ea7-5e7b-8cf3-92e914eea197 | note | Frequency - Each Lot
16b7d95b-99c6-5f7f-a718-08cc484b45ff | note | Acceptance Criteria - Installation of bathroom mirror as per drawings and manufacturer specification.
c8f7e3d3-5c1e-5a89-a8ea-64b5e93e03d9 | note | ○ Correct adhesive used and allowed to cure for minimum period whilst mirror is supported.
6a9c70e9-f4c4-5383-962a-b007f677c50f | note | Reference Documents - Drawing Set 030
bf1af911-5421-5e17-8683-143ed6f2a447 | note | Inspection/Test Method - Visual Inspection
1e9fe04f-88b0-5113-a3f9-deb01c5aaa4b | note | Record of conformity - This ITP Signed
50ab70be-6da4-5705-aa68-f3ca30e8ea72 | note | IP
cc8c337b-826a-528b-b612-fb01b96c6838 | note | Responsibility - Project / Site Engineer
7e9d58a3-0660-5279-bb67-bbadcf000ee2 | date | Date Completed:
3a3e68b2-81d2-4f14-a90f-ebf21b0ccaea | checkpoint | 3.6 - Eye Wash Station
57683cb1-6962-500a-beca-e0190f748687 | note | Frequency - Each Lot
fb84a581-ea5c-591c-b6a9-ea6a4149c51f | note | Acceptance Criteria - Installation of eye wash station as per drawings and manufacturer specification.
690e2236-da3e-5a8b-bd2e-4585c3fd2291 | note | Reference Documents - Drawing Set 030
716f1db8-7969-5185-a916-2fdd0dd1555f | note | Inspection/Test Method - Visual Inspection
2fa434cf-6497-5012-85ad-98b388b4c462 | note | Record of conformity - This ITP Signed
2de2f90c-c4af-5dc5-9ef5-cacce91868da | note | IP
80ad295e-8d25-52cd-9124-451bcda1b524 | note | Responsibility - Project / Site Engineer
da94c9e5-eee1-5f92-b06c-eb903ea95d13 | date | Date Completed:
b953c6f8-9008-4e34-a9b7-b356f7dfb3ce | checkpoint | 3.7 - Installation of Small Kitchenette
ce6327fb-ae34-5802-b817-ea5d690a01a0 | note | Frequency - Each Lot
f1e14dc3-9f97-52db-bf6f-37c3ced7523c | note | Acceptance Criteria - Installation of kitchenette as per drawings and manufacturer specification.
7baf584a-e473-533a-a4ce-b153a7bee292 | note | Reference Documents - Drawing Set 030
c5baf04f-1b9b-5d23-a458-76b41195798a | note | Inspection/Test Method - Visual Inspection
98cb1448-97ad-5041-aebd-5ac387aaaf6b | note | Record of conformity - This ITP Signed
88b70d1d-0856-5a87-a6a9-5a20ef9ffad4 | note | IP
a69f6e7f-fb7b-5224-bf54-f87021ce227c | note | Responsibility - Project / Site Engineer
be66b174-4e54-5e9b-b87d-b4b63c3cf58e | date | Date Completed:
52988a2a-61e3-4a91-854d-af9f80af16e1 | checkpoint | Final Inspection
dc788842-12ad-5863-b0b7-f62ae79cdb1e | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
64a572f6-a790-52d7-a971-05031dbc11d8 | textbox | Print Name:
209881a4-96eb-588b-b59f-07d4ec6944b9 | textbox | Position:
681870ea-d672-5751-9de7-d2bf7fc59cf2 | date | Work Completed On:
c2d66707-357b-516e-b580-15db4d39f0d5 | date | Date:
1ec42277-de86-41b7-85d0-541f2a3da67f | checklist | FH-ZU2-QU-ITP049 - ALER 3 AGL Equipment Installation - Rev 0 | itp | ITP049 - ALER 3 AGL Equipment Installation
502d2287-816c-4300-9f11-2104b6fee3af | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
5f7ba567-389d-439b-b9ae-b533f930eced | checkpoint | 1.1 - Check for correct documentation
60c55b3e-ee25-55fe-9990-e240b67cdb94 | note | Frequency - Prior to commencing activity
ec3d55d9-bfbe-5323-ac76-038e40a98eb0 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
351ed243-d5d4-5141-90a4-c2e4a2cc7d11 | note | — using the correct and complete set of drawings.
b65513c0-f3db-5618-8c33-59d3a19ae0e0 | note | — all drawings are the latest revision.
a7890248-16c9-5a68-96a8-beaeb2cf8b1b | note | Reference Documents - Drawings / Aconex Register
5259d216-19f9-5fc0-bbf3-9b90dbb1e7f6 | note | Inspection/Test Method - Verify
fbef0897-093c-58f6-8d25-92ef8b0eaa58 | note | Record of conformity - Drawings and drawing registers
e1394d2e-7e31-5b78-9ad5-4db20dff11b8 | note | HP*
c968699c-d0a5-5d95-8223-7f74cbc3008f | note | Responsibility - Project Engineer / Site Engineer
a4383817-99b6-5f88-ac89-83bc34c0b8c3 | date | Date Completed:
6a542940-3301-4881-8cad-0b2f7f2006db | checkpoint | 1.2 - Implementation of all measures and controls
2164fca0-6aa9-5bdc-96bd-2a06388964c5 | note | Frequency - Prior to commencing activity
99b9d809-0113-5c17-b0f7-8936a18b0717 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
4369e672-5af0-5e5f-ae1d-35e237d82d02 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
facc2e05-4c3a-565e-b45e-fb5b8461b9b1 | note | Inspection/Test Method - Visual inspection
572a0980-b70e-5767-ac96-841a3be00762 | note | Record of conformity - This ITP signed
47a1bbe5-fddd-5724-aa9c-5b1b8374d3a5 | note | HP*
aed112fb-ebeb-5505-8a59-6e1177acff6d | note | Responsibility - Project Engineer / Site Engineer
d08d1b8d-d742-5e84-9730-7a160cae1dda | date | Date Completed:
7701f083-b8c0-41fa-bc76-05dd92626d0c | checkpoint | 1.3 - Survey Checks
91b2bdba-977d-5e46-82ff-37f8b0a91903 | note | Frequency - Prior to commencing activity
4d0ecbfc-5fb8-58a7-9be7-ef1fa3615778 | note | Acceptance Criteria - Survey set out to be completed for all assets
5b11f5f7-60f6-52bd-aad6-e4b19fc483af | note | Reference Documents - Drawings
ecc50f56-c2a0-5528-b709-473a8495955a | note | Inspection/Test Method - Verify
f6877288-76fa-5abb-8804-ef16267cf696 | note | Record of conformity - This ITP signed
c5707af8-b3e4-5bfc-986b-2ab05c18b6bd | note | HP*
0a005193-7b9b-5496-a4ea-49ba9ce6a6de | note | Responsibility - Project Engineer / Site Engineer
77b17908-8aae-5ae6-b629-d56c0da22b0d | date | Date Completed:
8914e859-1a44-47b4-b3de-2e43c9736b92 | checkpoint | 1.4 - Submission & approval of shop drawings
b3218b8e-5307-5b4d-a7ba-1dcfea8228b2 | note | Frequency - Prior to commencing activity
1bbc7163-9533-52bd-97f9-975b15ef25d8 | note | Acceptance Criteria - HOLD POINT
c7986e74-997c-5cc3-ba50-99d3af3af87c | note | Submit shop drawings to the principal’s representative for approval prior to fabrication commencement. Items to include but not limited to:
a5fddfa8-3b1d-58ed-8220-0396166ba22f | note | ○ DB-AGL1
971fdf2f-44db-5c28-a9a3-59efd56733cb | note | ○ DB-AGL2
388787a3-a75f-5f2f-a027-b11ba4c6f324 | note | ○ CCRs
04848909-89f7-5962-bda9-ed6918033e23 | note | ○ SACs
8df779ee-0ebc-5847-888a-b7f7dd6e7df9 | note | ○ SCOs
804063e7-a952-5e12-a607-4da5a09057a7 | note | ○ ILCMS equipment
089137c1-f817-5749-97d9-d379a0c7e129 | note | Reference Documents - ZULU-BECA-001-SPC-00005 C2100 Page 10 Drawings 030-3100 set Approved Shop drawings
04999c55-758c-5484-ad31-2329decbcea9 | note | Inspection/Test Method - Verify
8ebc5f2e-234e-588c-b12e-264301d3a146 | note | Record of conformity - Aconex Reference
7c7aaf49-fc7d-584f-a4f7-159d9f6df603 | note | HP
f42b55f6-6e8a-568d-8019-0adb5a60a190 | note | Responsibility - Project Engineer / Site Engineer / Principal’s Representative
43de17f7-408a-5a4b-9c57-e1a1da2e33de | date | Date Completed:
9397f984-4bde-4bcc-b94d-f6e98d747b2e | signoff | AUTHORITY HOLDPOINT
372215a3-8640-4954-8ceb-33b4df6e381e | checkpoint | 1.5 - Material Submission
85803757-b45a-5c8a-975a-3a2c5b22ef67 | note | Frequency - Prior to commencing activity
f0937de9-292a-5ca4-abc4-6192fc1449ca | note | Acceptance Criteria - HOLD POINT
dfcee139-0647-5d31-a5cd-531e71f51ecd | note | Items to include but not limited to:
9a1a4c62-c6eb-5648-91c3-436e4a0b48ad | note | ○ Control Systems
6a4a9839-7c45-587a-a570-beb2d89c8169 | note | ○ Power Control
b206b2f1-0ced-5a9d-b3c6-73d560db6b1f | note | ○ Switchgear
209bebe5-98fb-5f5a-a716-2b3dd82cf043 | note | ○ Cables
8ede6215-b0d1-5810-a5b3-ff3eb3d0009b | note | Reference Documents - Drawings / Aconex Register
d2877b73-82c5-5bb9-bef0-314e632b0521 | note | Inspection/Test Method - Verify
4b17ee16-09f6-57f0-a5db-be496719af2f | note | Record of conformity - Aconex Reference
410866e5-03df-594c-a873-ff9174088468 | note | HP
65486f5d-9f9f-5ec2-954d-493446dfaa5b | note | Responsibility - Project Engineer / Site Engineer / Principal’s Representative
481c8d16-66de-5145-9351-65aeffbbd447 | date | Date Completed:
90b3439e-9472-4b26-86a4-b27bd89921d5 | signoff | AUTHORITY HOLDPOINT
8a1db87e-2eda-4dd0-a57e-132ecef1810a | checkpoint | 1.6 - Off-site Inspections
f172f442-9f68-531b-9549-9cec498797e2 | note | Frequency - Each Lot
4fcc7d43-9a2c-5a70-9b24-a4f27b43b709 | note | Acceptance Criteria - WITNESS POINT
5b54b6db-bf50-5d4f-bf80-ae174f2c809f | note | ○ Switchboards shall be fully tested before leaving the manufacturer’s premises. Inspection and attendance on site for Factory Acceptance Testing for:
33303260-2609-50a1-afbc-c65c91ea71b4 | note | — Switchboards
131e97e9-d677-5ee4-9939-ad18151c606a | note | — Distribution Boards
c3c69802-0702-55b9-84f0-41f0343f9689 | note | ○ Following these inspections FAT testing shall be submitted.
cb5ea02a-2643-50f7-9613-2e72089eda90 | note | Reference Documents - ZULU-BECA-001-SPC-00005 C2121.20 Page 58 AS/NZS 3000 Drawings 030-3100 set
38034d95-a03e-5f59-9181-41966271531b | note | Inspection/Test Method - Verify
662ff7cc-f6ed-5f14-8957-9263404bac68 | note | Record of conformity - This ITP Signed, Factory Acceptance Tests
926a8833-6d99-5e1c-84d5-cf4cf19686e2 | note | WP TP
2ad95ff2-792d-5108-854d-547910769344 | note | Responsibility - Project Engineer / Site Engineer / Principal’s Representative
14c63533-d9f3-5652-a708-c290c8e2b07c | date | Date Completed:
2756fb64-d5f8-425e-bd73-9a957501d328 | section | 2.0 - Construction
172ea43e-7c3b-4e66-ac40-d2fa2aab96aa | checkpoint | 2.1 - Delivery of Materials to site
5e31742a-4b39-5af7-ba02-bdaac8d823c8 | note | Frequency - Each Lot
e05f2c4d-844c-5172-a376-472b3757d551 | note | Acceptance Criteria - Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site.
3d281868-0475-51d3-9f34-673f2dc53ac3 | note | ○ Identify any damage/defects prior to unloading of the material.
5e410456-7ffd-5010-be1b-afa4730ba882 | note | Reference Documents - ZULU-BECA-001-SPC-00005 Drawings
ead77a80-622a-54c7-8b54-ad7bf0274baa | note | Inspection/Test Method - Visual Inspection
6fd50910-b0bf-5ac9-827e-230644061c43 | note | Record of conformity - This ITP Signed, Materials Inspection Checklist on ConQA
09bae280-22a4-5473-b89b-8e6b7ae26da2 | note | IP
0f9143b0-1c05-508c-98cd-92cdfd032ee8 | note | Responsibility - Project Engineer / Site Engineer
a234d4c0-eadb-504e-ac37-a2128ed328f5 | date | Date Completed:
c31ca3cc-da2e-413c-9452-557ac5d1e742 | checkpoint | 2.2 - Inspection of installed works
0a69da51-4886-5ff2-8a77-546a3a93c371 | note | Frequency - Each Lot
eeb9d99b-13c8-5df4-8295-d4a60d2885ce | note | Acceptance Criteria - AGL contractor to inspect the installation to confirm suitability and as per design, including but not limited to:
5e42b033-dae1-5dd9-9de9-bb9bb53bfdec | note | ○ Pits
96342990-e710-5fd1-9240-5eb58d75b8d1 | note | ○ Conduits
4268903d-9e31-59cb-a2c1-b24c58ddc5f2 | note | ○ Slabs
bd6e9a9f-bc3d-5f7c-87d1-084a98c5e94a | note | ○ Structure
3220644b-7219-53b4-b570-af13129e98fe | note | ○ Cable trays
eabdb820-3344-5df5-bae7-031a4bb80e6a | note | Reference Documents - Drawings
3c7ba7a7-474d-5e40-bcc4-893b271e8849 | note | Inspection/Test Method - Visual Inspection
7c757b65-f20c-53d3-b6f2-cb52cb54e6cb | note | Record of conformity - This ITP Signed
15f13cf2-81d2-5fda-bdf5-d58a6b942758 | note | IP
144792f1-a64e-5547-ba1d-12f4a073c90d | note | Responsibility - Project Engineer / Site Engineer
cbc76cb7-52b3-5125-a54a-444a330a3f7f | date | Date Completed:
6adbcf80-7405-42a4-a7f9-2a1755edd2d4 | checkpoint | 2.5 - SCO
05d43440-0851-5ad6-ba24-bea67ee1c840 | note | Frequency - Each Lot
1a7fe58c-b991-55bf-92ef-a4672cbf618e | note | Acceptance Criteria - Supply and installation of (Nos.04) SCOs as per drawings and approved shop drawings. Including but not limited to:
05aaa73a-642d-5bee-a090-a82cdf56b2de | note | ○ Cubicle to be plinth mounted
1527d369-7c8d-5b18-88ee-a382630439db | note | ○ Cabling
fbef0b82-1567-59e8-96f5-0aecb876f439 | note | ○ Labelling
3cc493fa-f4b9-5f7b-9488-24525b2c9c81 | note | Reference Documents - AS/NZS 3000 Drawings 030-3100 set Shop Drawings
b5973d6e-2f2f-5be1-82c5-4c6f8e19cf89 | note | Inspection/Test Method - Visual Inspection
0f962111-c612-5666-8e53-5e03b42ee692 | note | Record of conformity - This ITP Signed, ADB Safegate ITC
fce2e959-01cd-5586-a415-c1819994ad91 | note | IP
01f609c3-c664-5129-93ad-7d9673d599c8 | note | Responsibility - Project Engineer / Site Engineer
91c32998-3e93-574f-9d9d-616e9f887368 | date | Date Completed:
e2fe39de-d250-438d-8c78-4dfa647002cc | checkpoint | 2.6 - SAC
2209acad-415a-587d-8cd5-63c063eadb23 | note | Frequency - Each Lot
fb0ddd92-0ead-5116-bd9f-80ddfd8461d0 | note | Acceptance Criteria - Supply and Installation of (Nos 04) SACs (with 36 x SDH-100-2000-PH Surge Diverters per Cubicle) as per drawings and approved shop drawings. Including but not limited to:
56f5303e-33c6-5c29-92a6-03706d46ec80 | note | ○ Cubicle to be plinth mounted
5ea44022-86be-572c-9aff-2c6384da78d4 | note | ○ Conduit hood installed
082cdd79-18ff-5aeb-82a3-3a6d40aa1a04 | note | ○ Cabling
a6f48a93-e0df-5b0f-86d5-0e4c0eaf093f | note | ○ Labelling
2b4ce231-7b16-5c5b-9974-4bbf6a2b494c | note | Reference Documents - AS/NZS 3000 Drawings 030-3100 set Shop Drawings
9b51af97-7c03-566f-bba4-d84990bdae7b | note | Inspection/Test Method - Visual Inspection
58a931f5-2ce2-5e0a-babc-a4bd1f1516f3 | note | Record of conformity - This ITP Signed, ADB Safegate ITC
3474ac67-92d7-5751-b652-601eb7c84f31 | note | IP
b4ae4798-09fd-5b68-85a3-e7d4acda6d7c | note | Responsibility - Project Engineer / Site Engineer
6a3eb3f4-0d64-5f53-84f9-66495156d65c | date | Date Completed:
03f871ec-8b6e-424b-ac44-e39f336229fa | checkpoint | 2.7 - ILCMs
80c2377f-4673-500b-991a-f3f7dc5dbd3e | note | Frequency - Each Lot
06b0801f-f1ef-5ae5-8f24-8a1437435a99 | note | Acceptance Criteria - Supply and Installation of ILCMs equipment (including NCU cabinet, ASP cabinet, and existing SFAL) as per drawings and approved shop drawings. Including but not limited to:
1bbccba1-12f5-5780-b83c-441e3a4de271 | note | ○ TFO 200W NO E 6.6A/6.6A 50/60HZ Installed
4c2abee4-5936-52be-87c2-49dea5855eb7 | note | ○ SCF Complete Capsuled Installed
fdc9ab6a-8416-5ce2-87e3-283d0cd91fb9 | note | ○ Two SCI Series Circuit Inductors Installed
f0b3838d-b63f-517e-ab3e-5fa2395a5058 | note | ○ Cabling
dbc7a67a-3a32-5869-a5e8-2c3055e3b3f3 | note | ○ Labelling
e296782c-b995-58c0-b4d9-73eea8f7e10c | note | Reference Documents - AS/NZS 3000 Drawings 030-3100 set Shop Drawings
67392ffb-0a08-54c2-8332-53c61ed8095a | note | Inspection/Test Method - Visual Inspection
46c41a5c-ef04-52e5-a3a4-87f71a4a23bd | note | Record of conformity - This ITP Signed, ADB Safegate ITC
83ac2297-c200-5319-809f-288df98f9bb8 | note | IP
ef0ecdaf-b31e-5452-99ae-32770a76fd8e | note | Responsibility - Project Engineer / Site Engineer
1cb5db5d-b42a-59e6-9e2b-f74dc98962dc | date | Date Completed:
aa98bc35-b923-4ecb-bf82-41cc3ab655a0 | checkpoint | 2.8 - SCM
21f5c1fc-be5c-517f-857b-e30839ec5e02 | note | Frequency - Each Lot
5d02b38d-ed29-5cb8-ac4c-cff8a50e0641 | note | Acceptance Criteria - Supply and Installation of SCM equipment as per drawings and approved shop drawings. Including but not limited to:
5d8e1e5a-b058-5fbf-b3e6-38f6e1f3301c | note | ○ SCM Cabinet Modems Labelled
2639603a-e896-570f-b6dd-33333f88f2a9 | note | ○ OFLEX CLASSIC 110 CY 2x1.5 installed from CCRs to SCM Cabinet
a0e7c7a9-04e5-5e54-bcb6-ffd8fe438812 | note | ○ OFLEX Cables tied and labelled on the cable tray
d1daa081-cc83-5fd9-9106-14311d8e8d5f | note | ○ OFLEX Cables terminated inside the SCM Cabinet
3674ef3d-2398-5e54-b5fa-50cd30866a7c | note | ○ SCM Cabinet Energised
bed85bb6-fe2c-58ee-9630-ff4164b1b2f0 | note | Reference Documents - AS/NZS 3000 Drawings 030-3100 set
781a5842-0387-50c3-896e-010ef98eb5d0 | note | Inspection/Test Method - Verify
c09caf24-37d4-52df-ad48-abccd2f8fcb4 | note | Record of conformity - This ITP Signed, ADB Safegate ITC
f8c97061-44ef-5774-94fb-40b10e8bbc52 | note | TP
6c5c2dd2-b121-55d5-8503-34db69b11911 | note | Responsibility - Project Engineer / Site Engineer
170c4c43-95a2-5bcc-bffc-835b54b357e7 | date | Date Completed:
5160a9e6-0f57-45cc-b9f4-fdebcf5b848e | checkpoint | 2.9 - CCR
767f36ec-670a-509c-8b11-133db660cae6 | note | Frequency - Each Lot
0743db37-268d-55c8-9c19-626c757aeb0c | note | Acceptance Criteria - Supply and Installation of CCR equipment as per drawings and approved shop drawings. Including but not limited to:
f1b247af-5015-5985-a068-9532b7314ff5 | note | ○ 7.5 kW CRE CCR’s to be installed
c75313e8-d594-558c-b075-827eedee4166 | note | ○ CCR Power supply Cables with 50A Plugs Installed
cc5e2c99-8757-5da3-9da7-445dccb26b51 | note | ○ Cables form CCR SCO to the 2 SCI Series Circuit Inductors with Female Connectors Installed
86428fc8-f112-561d-bb4b-19f2875de235 | note | Reference Documents - AS/NZS 3000 Drawings 030-3100 set
ed25e855-8ba0-5bd7-838c-1884290e1799 | note | Inspection/Test Method - Verify
8b89cbc9-83f5-559c-93f6-bd6c80e86993 | note | Record of conformity - This ITP Signed, ADB Safegate ITC
d5b0d83c-7d64-5f17-ba35-504251ad9a7f | note | TP
9f3eba3b-71bd-5517-bf3a-edefae854249 | note | Responsibility - Project Engineer / Site Engineer
7ef0d889-3c54-556d-898b-9acd17404ee7 | date | Date Completed:
5291cc68-10b1-4cd9-9813-683c57dea830 | checkpoint | 2.11 - DBs
47e95fad-ddfc-52ad-b4cc-2d4c9678d056 | note | Frequency - Each Lot
968523f2-6c1f-54e2-b0b0-95849e59ba5c | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
a0e6bb43-5d40-5d50-95b9-62dae722c074 | note | ○ Size, colour, location
f11e9e38-f5a2-5ce7-9b8c-fe8b7483fb7d | note | ○ Plinth (if required)
a4dad53c-b8f3-5422-9bd1-31e97c593be9 | note | ○ Secure and anchored.
0da82c84-0cc4-518a-b5e6-e038ea057744 | note | ○ Labels
b60c5cd5-aec9-5b3b-84d3-cd6772dd240e | note | ○ Tightness & alignment
20e564d5-4784-5ce2-bf3f-66e78ee6978a | note | ○ All wiring tidy and neat
e405b2f9-bf6d-53bd-b5a1-f39b15ea3d00 | note | Reference Documents - ZULU-BECA-001-SPC-00005 C2100.2 AS/NZS 3000 Drawings 030-3100 set
3c31810a-4bf7-5ead-af4d-c75b3a2c464f | note | Inspection/Test Method - Verify
d29b5448-d9f9-544f-b231-7a4f11789ab9 | note | Record of conformity - This ITP Signed, ADB Safegate ITC
d13fc364-a0b1-5be8-81a8-51d6a6432f59 | note | TP
af0d58f5-da15-57e8-bd0b-f1bbcbe340c9 | note | Responsibility - Project Engineer / Site Engineer
7a9b5f7f-06cc-58a8-893b-389b66902f1d | date | Date Completed:
25581c53-62b4-494f-a7dc-21857f4ce34e | checkpoint | 2.12 - Cabling – Mains, Submains,
241719d0-b204-5c24-bb09-4a8506cd1d30 | note | Frequency - Each Lot
e917a776-b197-5fb3-8af0-b6e446cd318c | note | Acceptance Criteria - Confirm the following items are constructed in accordance with IFC design and specification.
9c3f65b3-fd73-55da-b329-c5a8886b3b0a | note | ○ Type, size, colour, quantities, location
03e8bc7a-7356-529f-98c5-6fd05d28dda8 | note | ○ Secure
d7716a3a-8368-56e5-8a18-55ee318309e9 | note | Verify and confirm the following tests as per AS/NZS 3000 (not limited to):
98bb4618-3f52-52dc-8c79-ea11cff8f4e7 | note | ○ Polarity Check
2bdc01a9-92a7-5ed2-aa67-2b49b54cb8d6 | note | ○ Cable Loop Resistance (Ohms)
0be28d32-870e-5d35-98b9-e6dd65c34234 | note | ○ Insulation Resistance (Core-Core& Core to Earth)
fc66d734-6b8f-5dd5-8f91-afa5d4d775c0 | note | Reference Documents - ZULU-BECA-001-SPC-00005 C2111.5 AS/NZS 3000 Drawings 030-3100 set
77e65aa0-b27a-5381-ae07-1c4abd28d2a6 | note | Inspection/Test Method - Verify
f6308655-9498-5bce-9386-80e827daa519 | note | Record of conformity - This ITP Signed, ADB Safegate ITC
aac88a8d-fab3-5ba8-9e08-df82d492d0df | note | TP
268aaf0a-e1e0-5126-94f2-79e1c1b3c827 | note | Responsibility - Project Engineer / Site Engineer
ed0e5451-f790-590a-a06c-55caebfe45a4 | date | Date Completed:
0a39fe94-544d-42e5-9406-d477c1c43924 | checkpoint | Final Inspection
7c3fabe0-12ef-55a7-af6d-cd2bdc5eb0dc | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
276c855b-6751-55a4-bbbb-5f3d0e4f2c05 | textbox | Print Name:
13866e3e-2140-5eb2-bf37-4bfa1dd74dbe | textbox | Position:
3af36b21-7512-59ce-9923-a6ccf8bbda2a | date | Work Completed On:
a02b0fd5-6a16-5ae6-8c0e-5e3868ebce0b | date | Date:
33de5ee1-28e8-4a52-a461-a233f3a1a4e7 | checklist | FH-ZU2-QU-ITP050 - ALER 3 Communications - Rev 0 | itp | ITP050 - ALER 3 Communications
c2e2c7fe-4678-4501-8466-e97d16ad5a38 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
20eaefe2-8575-49d2-b50e-def55da0ca8f | checkpoint | 1.1 - Check for correct documentation
fd4fcbe2-2670-5daa-b1cf-69f322813036 | note | Frequency - Prior to commencing activity
e788c0ac-1f11-5b9f-9aa9-cf45b6a06ed6 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
85f836ef-6300-51c1-9311-766d9c8b42f8 | note | — using the correct and complete set of drawings.
7423d07f-2648-5636-9a12-9725397287b8 | note | — all drawings are the latest revision.
4d447c55-596b-5d11-b5f9-b9253676c309 | note | Reference Documents - Drawings / Aconex Register
7316cf20-b5e7-57ba-bb6e-23947f6eeda6 | note | Inspection/Test Method - Verify
5a6bbd08-5f19-5d26-a4b2-53ae2cc7a283 | note | Record of conformity - Drawings and drawing registers
fb174b3b-e14e-529f-a4c0-90518f323c79 | note | HP*
9153ffc7-a83a-55eb-8324-36541ffd284f | note | Responsibility - Project Engineer / Site Engineer
ea0d9e24-f8f9-509d-b066-b98f3aedc4ac | date | Date Completed:
3ddea3bb-d5d6-4af6-b337-dd60029a65ba | checkpoint | 1.2 - Implementation of all measures and controls
2a811399-1bb9-5b00-a220-db17853a212d | note | Frequency - Prior to commencing activity
9d47cfc3-95bb-5659-8a98-6eb0670917f0 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
f9cb1e2f-fda3-5edc-8f57-11bef4cec396 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
9fd5c8c2-64e6-57e2-9987-a9942d612647 | note | Inspection/Test Method - Visual inspection
2f7fe6e3-24aa-5d7d-ae1c-b4768b4da837 | note | Record of conformity - This ITP signed
6164d8ef-4ff7-5383-b724-b5af4957bc26 | note | HP*
d44d21a5-29d3-5b60-9025-301b003d4dc3 | note | Responsibility - Project Engineer / Site Engineer
fb47a02c-1a01-5913-9008-e644c30cd92f | date | Date Completed:
62252cac-8abb-4e98-9f4b-75282234dfb0 | checkpoint | 1.3 - Submission & approval of shop drawings
42ba4981-7054-5afc-98bf-aa1038a4c843 | note | Frequency - Prior to commencing activity
3599d01e-5e25-539c-9874-cca4fba330dd | note | Acceptance Criteria - HOLD POINT
d867ec51-8cd7-597a-a2bd-4829061b41fe | note | Submit shop drawings to the principal’s representative for approval prior to fabrication commencement.
2513f204-7c59-5afd-8299-eb5fac9b4410 | note | Items to include but not limited to:
e3803b97-c21e-53e0-9365-46bca46eb562 | note | ○ Netshelter Comms Racks
a981b97d-613e-5afa-80f3-463240d74266 | note | ○ Power Rails
13a2df1b-20c4-5456-8568-600598685c3f | note | ○ UPS
3e18b43e-97d7-5d9b-afd2-9ff0ef18a01e | note | ○ Loaded Patch panels
d44c9c8b-8266-5164-8af0-928ca1dca886 | note | ○ Additional Battery Pack to suit UPS
bf115593-385d-582d-bdca-d858684e8f81 | note | ○ Hard wired input and output for downstream switchboard
569594ca-6fab-58b6-8210-9ea448f37fc2 | note | Reference Documents - ZULU-BECA-001-SPC-00005-C3500.2 Drawings
ac53f6b9-fb8a-512d-9cd8-4eb7a05eeb3a | note | Inspection/Test Method - Verify
98091dd5-7867-5a06-b306-0f635e40bfbb | note | Record of conformity - Aconex Reference
019cc899-9a9f-50bb-a866-565056b55091 | note | HP
3945866b-d4b9-582b-abba-6ead142a472d | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
33749a5b-9d22-530b-8b62-e17d68d6497c | date | Date Completed:
fcdc84eb-fd9e-45f4-ae2b-8f737ec2e283 | signoff | AUTHORITY HOLDPOINT
ff83e376-6acf-46f6-8c56-3114eb096147 | checkpoint | 1.4 - Material Submissions
8a21bfc1-82eb-5257-8b69-9188a8e258cf | note | Frequency - Prior to commencing activity
210f47ab-8b96-5cc0-b935-110615f63451 | note | Acceptance Criteria - HOLD POINT
a6795011-4d0a-5325-9e98-bf264da14738 | note | Provide technical datasheets and compliance certifications for all ICT materials. This includes but not limited to:
22e36411-6259-5f89-a123-7fbc72c69b75 | note | ○ OS2 G.652D fibre optic cable (12-core microblown)
5b730ec3-785f-50fd-9165-d9ab2bddbfb8 | note | ○ TE Connectivity or equivalent FOBOTS and patch cords
06805a50-a8ed-5c6b-91ec-9e141272bad2 | note | ○ Cat6A UTP/FTP cable and modules
deacbf76-d6d5-5a13-a365-8251fe1220dc | note | ○ LC duplex connectors (blue or green coded)
f2e7aa30-a323-5180-8fd9-ee325e5bc057 | note | ○ Critchley label sleeves or heat-shrink tubing
cec49ef5-b2ba-57cc-b878-a74d76857a5e | note | ○ Fibre warning labels, jumper rings, dust caps, cable markers
191da85e-8025-5499-b8b7-9b5b21d374cf | note | ○ Cable trays: pre-galvanised/hot dip (min. 42μm)
578e93cb-b70d-5bf6-9ab1-4ed7a14d26d6 | note | ○ UPS APC Smart-UPS 3 kVA
2e10e41a-3b7e-5459-86f6-0be09f791304 | note | Reference Documents - ZULU-BECA-001-SPC-00005-C3500.2 Drawings AS/NZS 1252.2
72a60a8c-b0d5-52d5-ab88-0eb5a1cf87b3 | note | Inspection/Test Method - Verify
168b1220-da15-5e1b-ab23-6b9818e48af3 | note | Record of conformity - Aconex Reference
cbeb7039-dcdc-5785-b2b0-d80f4809a6e3 | note | HP
8191f5d9-e50a-55bb-9207-b9316931c6c3 | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
3e18acef-00b3-504e-b3cb-9f369de8fe89 | date | Date Completed:
d895309a-cab8-423e-bf2c-a5ebc9f7573a | signoff | AUTHORITY HOLDPOINT
8d531474-eec1-4fd6-a5bd-a8f4d67bbc7e | section | 2.0 - Construction
a15afc51-85fa-4126-9972-8c45f0658305 | checkpoint | 2.1 - Delivery of Materials to site
dc5aa6cb-3da8-596b-a445-452c77870e73 | note | Frequency - Each item
059568fe-3575-5cea-8c3b-1a7ee07b6640 | note | Acceptance Criteria - Verify each cable drum label, cable length, and ID matches the approved submission and cable schedule. Inspect condition of fibre drums and verify ends are sealed with heat- shrink and protected from dust or water ingress. All components shall be stored elevated on insulated racking. Equipment that has been damaged or exposed to moisture must be rejected. All fibre drums shall be colour coded yellow (OS2) and visibly tagged at source and destination.
c7d58cbb-ea91-5128-8d08-c139ce3e85fb | note | Reference Documents - ZULU-BECA-001-SPC-00005-C3500.2 Drawings
bdbcbf92-8e21-5010-bf04-fa8af47d4e3f | note | Inspection/Test Method - Visual Inspection
618feb0f-18ed-5fbd-ae74-7773ec51a3a7 | note | Record of conformity - This ITP Signed, Materials Inspection Checklist on ConQA
5df4c53a-f156-5fe3-b3e4-037a46984733 | note | IP
a8a99de6-e27f-5b2b-8f89-5ab0b8d19a59 | note | Responsibility - Project Engineer / Site Engineer
825ec70b-7ab1-52d2-973a-0009d63ea77a | date | Date Completed:
d1b92d5b-8472-4ee9-a638-5bbabf843e3b | checkpoint | 2.2 - Inspection of installed Pits, Conduits, Slabs and Structure
d89bbbf4-0023-5e28-988a-28bb47800f3c | note | Frequency - Each Lot
00bef96a-8a07-597c-80ca-244a2eb415de | note | Acceptance Criteria - Inspect that all underground conduits are clean, dry, and fitted with compliant drawrope. Duct ends must be bell-mouthed and sealed when not in use. Comms pits must include the following:
14ba1d4f-58c3-5f7e-8aab-8b4e1a6c1812 | note | — Approved pit covers
88742fbd-dea6-5867-95fd-9880bd11125c | note | — Earthing (if metallic)
6afcacc2-92e6-5ab5-8704-1409549cf33b | note | — Cable support brackets,
a667d39c-480a-5e69-b7c1-bc60d7ddec65 | note | — Internal spacers (where applicable)
582540f5-af99-530f-835c-f429c24a16a3 | note | ○ Ensure pit depth and position align with survey setouts and installation tolerances. Check slab penetrations are core-drilled or pre-formed as shown in IFC and sealed post-install.
faf9aa01-ae1d-5773-b9c2-bd4783020ebc | note | Reference Documents - Drawings
f4179672-4efe-5c13-976f-a97af9fc885f | note | Inspection/Test Method - Visual Inspection
41c0b2c6-5e37-57dd-881d-908a20e45e3c | note | Record of conformity - This ITP Signed Stowe ITC
751f2df4-e68e-53db-85b6-79d0a92698fa | note | IP
3fed644e-0c9c-534c-9782-3f7a08e23085 | note | Responsibility - Project Engineer / Site Engineer
6cb4817c-eac1-592f-99e8-9f4f92749709 | date | Date Completed:
92f2fb3b-844c-4640-bde5-33001b8aef79 | checkpoint | 2.4 - Cable Pathway Inspection
61f93b81-d0fc-5686-8741-62135502f7d1 | note | Frequency - Each Lot
9d70d9c4-dc99-58e1-9582-89743e43d44d | note | Acceptance Criteria - Verify cable tray installation matches approved shop drawings. All directional changes must be supported with brackets within 300mm. Maximum tray support spacing is 1.5m. Confirm no tray deformation or sharp edges exist. Earthing continuity must be maintained with bonding links across expansion joints. Segregation dividers must be present where power and ICT cables share a common tray. Firestop penetration seals must be compliant with AS 4072.1 and identifiable by tag number or batch number.
a2e33fb3-cc4f-520c-bc69-670c5c972b31 | note | Reference Documents - ZULU-BECA-001-SPC-00005 Drawings
c813cf7a-f95a-5b74-996b-99546f15c536 | note | Inspection/Test Method - Visual Inspection
e9920e25-d55b-5eb0-a0b6-726dd5239840 | note | Record of conformity - This ITP Signed Stowe ITC
8bf20601-2f7b-56b1-82da-58f931a33518 | note | IP
021a78e5-80f3-56e2-b354-77d916f3345e | note | Responsibility - Project Engineer / Site Engineer
e1e2970e-2059-5baa-b865-092824cedb34 | date | Date Completed:
52b795d5-2af9-4d56-8be5-7ef1e35b79d2 | checkpoint | 2.5 - Fibre Cable Installation
740ca627-9629-5746-ba70-a6fe286d6105 | note | Frequency - Each Lot
39eecf16-d9ce-5eee-aa98-32ce8eb7d001 | note | Acceptance Criteria - Fibre shall be pulled using calibrated tension monitoring equipment to ensure no tension exceeds 270N. Minimum bend radius must be ≥10x cable outer diameter or 80mm for microblown 12-core units. Label each cable at both ends using Critchley sleeves or approved printed heat-shrink tubes. Every 4 metres, apply orange warning labels inside shared containment paths. Route must follow a star topology structure unless otherwise specified. Keep micro ducts free of gel, dust, or moisture during installation.
47d1bc73-9460-55da-9b70-01828489f7e7 | note | Reference Documents - ZULU-BECA-001-SPC-00005 Drawings
2c41a2a9-e933-5031-b03c-cfff3d48d69b | note | Inspection/Test Method - Visual Inspection
62211486-2f47-5d3d-984f-260461407e73 | note | Record of conformity - This ITP Signed Stowe ITC
537fe7b6-192f-571b-84ea-59ee550fd025 | note | IP
17f66ecf-2f3e-50f4-b347-c001828f31aa | note | Responsibility - Project Engineer / Site Engineer
ebdd4296-cefc-580c-a98c-ca7a35e831c2 | date | Date Completed:
3d8f0754-9c9a-4bba-8d0d-cbaa1e448482 | checkpoint | 2.6 - Comms Room Fit-Out and Installation
525ba8b0-4702-5679-b402-c729a3faec67 | note | Frequency - Each Lot
c37d0254-e07f-5ca1-9673-ff10fd9f2174 | note | Acceptance Criteria - Install racks, patch panels, and FOBOTS as per manufacturer’s instructions. All patch modules to be 19” rack mounted, fixed with screws and dust covers. Incorporate jumper rings, labelling strips, and drawer sliders where required. LC connectors shall be installed clean and dry, colour coded (Blue = PC, Green = APC), and secured to minimise bend strain. Verify the presence of cable strain relief and that unused ports are sealed with caps.
3211bb9d-22ba-5b57-9417-c3690b1c8b10 | note | Reference Documents - ZULU-BECA-001-SPC-00005-C3500.2 Drawings
070c9216-0cc9-51e0-8f08-ff07ca3dee18 | note | Inspection/Test Method - Verify
0ba23027-b80e-5dd6-aa4b-0efb0cf9804e | note | Record of conformity - This ITP Signed Stowe ITC
5dd10f19-1bbb-55b7-855a-787b5c3de548 | note | IP
275da5ae-1820-55c1-8af6-767f7e98a22e | note | Responsibility - Project Engineer / Site Engineer
487d3297-8727-596d-8169-915b08c2c789 | date | Date Completed:
b78450c0-a75a-4056-a179-10916cdc305e | checkpoint | 2.7 - Comms Room UPS Installation
f48582b2-3699-5e31-a156-1c7d83971b5f | note | Frequency - Each Lot
dc90c4db-5382-5d8d-9acc-cdc088c0a149 | note | Acceptance Criteria - Confirm UPS installed are as per approved material submission.
fdfcfc6d-8c4d-5469-aac3-53e7955868d6 | note | ○ Verify battery and/or UPS capacity can operate normally for a duration of Eight (8) hours.
4fdac353-8e70-5bb8-863d-61fba28e848c | note | Reference Documents - ZULU-BECA-001-SPC-00005-C3500.2 Drawings
d4a931c8-0a79-5c41-9bb8-57e2209b08a9 | note | Inspection/Test Method - Verify
91aefffd-2a6f-55e5-afb9-d31bf11940e1 | note | Record of conformity - This ITP Signed Stowe ITC
ca55832c-d7d2-532e-8a28-73f6f07c69a3 | note | IP
e99625cd-5658-513f-843e-4f20350ee2d0 | note | Responsibility - Project Engineer / Site Engineer
f033e196-41b8-5a8c-9c55-84f4fbcc9aae | date | Date Completed:
1c355d6c-2015-4b4e-bc39-cd6f4d7ce699 | checkpoint | 2.8 - Control/Data Cable Installation (AGL & ICT)
34132c1d-4133-542f-966c-5d18020d1b41 | note | Frequency - Each Lot
7a5032c0-9bff-5607-b098-274bbe98a63e | note | Acceptance Criteria - Install Cat6A UTP cables in separate containment from power. Maintain ≤90° bend angles and ≤45m run length between active equipment unless boosted. Label within 300mm of each end. Each pair must be colour matched to the patch panel schedule. Testing of all the criteria for compliance with CAT6A, NEXT and ACRF values post-install to validate compliance with ISO/IEC 11801 Category 6A standards. No unapproved joins or patch- throughs allowed inside ceiling space or risers.
e0e8034e-698e-59ac-8be9-5ef8f32bfe70 | note | Reference Documents - ZULU-BECA-001-SPC-00005-C3500.2, C3501.4
6c7023ac-c95a-58a9-9ae8-f115931dacca | note | ○ AS/ACIF 3009:2006
fc9d7904-651c-5989-a1cb-1dc014e60d7f | note | ○ AS/NZS 3080 Drawings
7fe71183-1786-50c9-ba7a-2c29a2ad0bc4 | note | Inspection/Test Method - Verify
8c65324d-5f16-56f5-b5a6-6d24ed8c39a3 | note | Record of conformity - This ITP Signed Stowe ITC
e578d7be-0246-54d0-bf0b-e609f6370312 | note | IP
d6173228-0406-57a1-8ebe-6e58facfde20 | note | Responsibility - Project Engineer / Site Engineer
61565e9e-1503-5939-9bb8-3fa2e585e31a | date | Date Completed:
02a1be3b-a5cc-45e2-90ad-a6147f5bddac | checkpoint | 2.9 - Cat 6A RJ45 Data outlets Installation (AGL & ICT)
aeb00da3-d5cb-5663-b336-52ffb1571f6f | note | Frequency - Each Lot
2544cc58-6915-5493-9fce-ae315ac29779 | note | Acceptance Criteria - Installation of all Cat 6A RJ45 data outlets are as indicated in drawings.
2cecc0ea-ef44-56fa-b963-31480d16acf9 | note | Confirm mounting height of outlets on site with the Superintendent. Generally, and unless otherwise shown on the drawings, outlets shall be mounted at:
1b58b1d3-6653-5b13-bdcf-9eb1aeb01412 | note | ○ 300 mm above floor level or 200mm above benches in commercial areas.
b17319ec-19c7-5710-b044-a558e6e8bf18 | note | ○ 1400 mm above floor level in plant and industrial areas
eed51e73-fb2d-572d-ba5f-4e46998b0d5a | note | Reference Documents - ZULU-BECA-001-SPC-00005-C2141
d155bddf-3afb-57a3-a265-44c56d2469b4 | note | ○ Drawings 030-3100 set
b9c52b85-e959-523d-84e9-4defe37b170b | note | ○ AS/NZS 3000
e717921d-2fa6-5a18-bff3-d329fa2b13f6 | note | ○ AS/ACIF S009:2006
15248d04-a0ee-5967-b324-d390463f28ec | note | Inspection/Test Method - Verify
013fbba9-d7a2-5304-988c-b58303b3c059 | note | Record of conformity - This ITP Signed Stowe ITC
a03cadf7-6d95-51d0-981e-ba6b7291d87f | note | IP
9db0b8a6-3da3-5775-b32f-845bbb15e967 | note | Responsibility - Project Engineer / Site Engineer
26289097-6574-5dc7-93a1-47ce6dc12d3a | date | Date Completed:
d24478b0-17e5-47ec-85cc-3261f7d6ec94 | checkpoint | 2.10 - Fibre Testing (OTDR + IL/ORL)
e52cea86-a097-5001-a6e3-28597f1860b5 | note | Frequency - Each Lot
696793e3-a7a5-5ea6-98c0-f53bbc73b103 | note | Acceptance Criteria - WITNESS POINT
1c233752-ce05-5cba-b76e-4954db429bf1 | note | Verify fibre cable performance through industry-standard testing methods:
d862b3ff-67b5-5f49-ad96-76a1074fc89d | note | — OTDR (Optical Time Domain Reflectometer): used to detect faults, splices, and measure the attenuation along the fibre length.
6fc4363b-c2b1-5f18-ac3c-d53871301d8e | note | — IL (Insertion Loss): the total loss of signal power resulting from the insertion of a device (connector, splice, or cable) into the optical path.
dcf13d6a-8636-52e3-a044-c6249f4bb73f | note | — ORL (Optical Return Loss): the amount of light reflected back toward the source, which must be minimized to avoid interference or data errors.
aacca2aa-0d93-5a7f-920c-a06e88934817 | note | Conduct 100% testing of all fibre cores in accordance with AS/NZS 14763.3:
cad5ff58-74c5-532b-afa3-19ce105cc41a | note | — Use 1-jumper test method to verify Insertion Loss (IL < 0.5 dB per connector)
41594f8f-f598-5f21-afdb-01e490222827 | note | — Conduct OTDR tests bi-directionally (A–B and B–A) for links >150m
ee689356-75d9-5f6a-8838-b14bc4615c2f | note | — Measure Optical Return Loss (ORL > 35 dB per core)
71b548fc-26fc-597e-851f-4536e52eaf8b | note | — Include test at 1310nm and 1550nm wavelengths
d18b420e-0dad-5dbd-81fe-04758844231b | note | ○ Submit OTDR trace files, link loss reports, fibre IDs, test configurations, and calibration certificates of equipment used. All testing must be supervised by the Site QA Representative.
4c6a299b-c12f-5404-af2d-47111bf1ac59 | note | Reference Documents - ZULU-BECA-001-SPC-00005-C3502.5 Drawings AS/ACIF S009:2006
3822e0bf-8bf5-5b17-9e66-107b1ce3bf61 | note | Inspection/Test Method - Verify
3ac7ae18-c529-5c7c-9cce-7248a4d46073 | note | Record of conformity - This ITP Signed Stowe ITC
e8c3004f-c72b-59a5-a618-b73d2285b712 | note | WP
f57f2677-fdc0-578d-bc95-ddd2038b6867 | note | Responsibility - Project Engineer / Site Engineer
ca79f7ab-8662-5185-a9f0-350972a45e57 | date | Date Completed:
4a623a3d-a6f6-44b0-b343-84f3433dcfdf | checkpoint | 2.11 - Tray Earthing Continuity Test
bc2040a7-6bff-5f59-a71f-fd6849883203 | note | Frequency - Each Lot
0ed712ba-03e7-5231-b425-7e6df7415cd1 | note | Acceptance Criteria - Confirm electrical continuity of all metallic cable trays using a calibrated digital multimeter. Bonding between tray segments shall not exceed 1Ω resistance. Ensure earthing tails are installed and terminated using crimped lugs at each fixed support location. Earth point locations must be clearly marked and photographed as part of the QA record.
5c7985c8-ba7b-5d25-9dc8-4191cf845e73 | note | Reference Documents - ZULU-BECA-001-SPC-00005-C1740.6 Drawings
65ebae78-5cbc-5dd2-b186-090a7fe54e85 | note | Inspection/Test Method - Visual Inspection
9579985d-6b2a-5c16-a0cd-f24be5d4dc37 | note | Record of conformity - This ITP Signed Stowe ITC
1f5e873c-b3eb-5f71-a46a-58f39f2aede7 | note | IP
8fb8f3fc-77f9-5023-aeba-4ae494bd28e8 | note | Responsibility - Project Engineer / Site Engineer
61f9afea-cafb-596e-94a2-3ed0afac5eb1 | date | Date Completed:
b7710e52-9296-46c4-8f12-24b9d5ac1c92 | checkpoint | 2.12 - Air Blown Fibre Testing
cdc5f48b-5555-5044-8046-fbb412cd3b9d | note | Frequency - Each Lot
815e8859-8209-5035-8fe9-9aa37bc7344a | note | Acceptance Criteria - All Air Blown Fibre (ABF) testing must be conducted using a calibrated tester with a valid calibration certificate not exceeding 12 months from the test date. New test reference leads shall be used.
313c65cb-73e7-5be0-8202-9e20b3823fe1 | note | Testing shall include ABF Tube Calibration & Testing for each individual primary tube within the tube bundle in the following sequence:
143198ec-d3f2-537e-b97a-0d1afce7f278 | note | 1. Tube Air Flow Testing – confirm a clear airflow path over the full tube length and correct coupling sequence.
51f9b2bf-d4f1-56c3-ae43-feb2ea43dee7 | note | 2. Tube Pressure Testing – confirm no leaks in the tube route or connector fittings by applying and monitoring a test pressure.
f1d7c67a-d5de-5f28-87f5-fc2ef63c5d33 | note | 3. Tube Continuity Testing – verify the bore diameter and concentricity are suitable for blowing the fibre bundle without obstruction.
ca48a1b7-4c7e-5349-9c5d-92f24c21d2d8 | note | Once tube integrity is confirmed, blown fibre shall be tested in accordance with the fibre optic test regime in C3502.5:
db6d3d19-b7c5-5d80-9afb-1ee74cb31ff5 | note | — Link Loss Testing (OLTS, 1-jumper method) to confirm Optical Loss Budget compliance.
4de2b539-378b-54b4-99d9-90b80f3c5072 | note | — Insertion Loss (IL) not exceeding 0.5 dB per connector.
6973f9c0-d9d7-5346-8e05-1c8230ab62b4 | note | — Optical Return Loss (ORL) ≥ 35 dB per core.
08056b18-64f3-58df-b5e8-54e1e3ad3bbf | note | — Bi-Directional testing for each core
4600819d-c04b-52e4-8916-bac84ba2ef98 | note | ○ Results shall be recorded in raw-data and PDF formats, referenced to the tube ID and cable ID, and included in the O&M manual.
44598e62-9701-56fe-8881-421e83e0618f | note | Reference Documents - ZULU-BECA-001-SPC-00005-C3502.5, AS/NZS 14763.3
62f73089-9adf-55c5-86a9-2c580dbb4f03 | date | Date Completed:
40346074-2ef0-4861-a911-e0c9cf95e95d | checkpoint | 2.13 - Testing of the Racks Power Distribution Units
3b617dc0-ec31-5d6e-b133-fed7eeee3ee5 | note | Frequency - Each Lot
8b3c8bcd-accd-525b-9825-6ae0f768a68f | note | Acceptance Criteria - Testing shall confirm:
f72e3dc4-088d-5dab-baaa-2c7b76807e65 | note | ○ Mechanical & Electrical Installation – PDU securely mounted in rack, aligned with cable management hardware, and labelled in accordance with the rack equipment schedule.
83f9a7da-1105-5391-9487-c35f7e44f606 | note | ○ Functional Verification – confirm correct input voltage, output voltage, and phase balance (if applicable). Test each outlet socket for correct operation and power-on indication.
f54ea7ca-7309-5f10-98d5-90ffdf161d6d | note | ○ Load Testing – verify the total connected load does not exceed the PDU rated capacity. If PDUs have integrated circuit protection or surge suppression, confirm correct operation.
0fd912da-44cd-5ace-960e-7b2469fe4e90 | note | ○ Earthing & Bonding – confirm PDU body and mounting rails are bonded to the rack earthing system (max resistance ≤ 1 Ω).
5164feb2-2015-5189-9c8e-b34d2ba87365 | note | ○ Integration with Rack Cabling – ensure PDU installation does not obstruct cable management systems or violate bend radius requirements for adjacent fibre or Cat6A patching. Maintain clearance for fibre patch panels and FOBOTS as per C3502.3(g–j).
78cce450-8fe8-5c0e-a00d-10e3518afbf9 | note | ○ Labelling – each outlet and PDU to be labelled in accordance with the approved IFC and as-built drawings, matching the equipment schedule and port mapping.
5b86e078-6776-5136-b2cd-5a225fcd779f | note | Reference Documents - ZULU-BECA-001-SPC-00005-C3502.3 AS/NZS 3000
1dd88c7e-e62e-5ab2-ab92-33e89e1d4e9f | date | Date Completed:
49b0e5ee-3e25-4caf-bb0b-56e6df359cc8 | checkpoint | 2.14 - Final Labelling Verification
9c39ba5a-6d4b-506a-9f3f-3a0f4cdbe764 | note | Frequency - Each Lot
99fd12b4-75a7-5203-a448-aa3379b8e247 | note | Acceptance Criteria - HOLD POINT
ca1782fc-ef52-5f3c-8947-4bd748971682 | note | Verify that all ICT infrastructure is labelled clearly and permanently in accordance with the approved IFC drawings and the final as- built documentation, Including:
5fa152c5-7f6b-5cd0-94d4-bb20588c7f6e | note | — Cable tags at both ends (heat shrink or engraved)
d52926aa-11be-5277-983d-6705e1a2d110 | note | — Enclosure and tray ID labels
6f91efe9-a309-5111-a431-dd9960b00e3b | note | — Rack/patch panel port label
86dc29f2-4d72-57bb-8d14-8f34f40f73f5 | note | — Floor boxes and comms cabinets
0670f538-9752-5e71-9399-ed1920d917bf | note | ○ Labelling must match the naming conventions and ID numbers in the approved schedules. Any mismatch, missing tags, or unclear labels shall trigger non-conformance and require rework prior to Practical Completion.
e402cec4-fd69-5f21-a68a-057552f919da | note | Reference Documents - ZULU-BECA-001-SPC-00005-C0171- 7.16 Drawings
53dfb9ee-936c-5e94-a84e-8f2a8130b63b | note | Inspection/Test Method - Verify
f8825473-072b-5a03-9b91-3d75b79772ba | note | Record of conformity - This ITP Signed Stowe ITC
890d9b25-987b-5060-8476-b76ff5f2b7cb | note | HP
728b6141-3790-51c3-9f66-cee2b6a43779 | note | Responsibility - Project Engineer / Site Engineer / Principals Representative
cdc88b31-7d1b-581a-9645-2c4f2cad62ef | date | Date Completed:
c46bec93-9bc5-4d06-bd34-5c85c5f0e560 | signoff | AUTHORITY HOLDPOINT
7efd0e3c-35de-414a-96f7-07a2c785c0f1 | checkpoint | 2.135 - Survey As Built
1d0aa11e-a18b-5df8-8f3c-f2d657be6a16 | note | Frequency - Prior to Covering Services
73450966-bbd9-5b23-9bdc-6aab7304e36d | note | Acceptance Criteria - Survey to pick up services prior to covering
ac220b1c-be9f-5b73-b673-2580db820009 | note | Reference Documents - FH QMP
5ebb11d6-3223-5f3c-9353-8fd86a7f00d4 | note | Inspection/Test Method - Verify
527cdf90-ac7d-5616-8fc2-c6b84c950f9b | note | Record of conformity - Survey
1e8cea8a-8e89-56a8-a4bc-d784c0e58cf7 | note | HP*
e4c3ee8e-a6bc-5fce-9d2d-a818686abded | note | Responsibility - Project Engineer / Site Engineer / Surveyor
eefe5b3c-4d34-5dc0-a102-5b3a481b0753 | date | Date Completed:
37a4499c-0644-44bf-8cd3-c4a5c6016bcb | section | 3.0 - Communication Service Migration
4b58dd87-6492-4c92-99c6-ef80b774f904 | checkpoint | 3.1 - Existing Comms Services Migration
3f41c51e-5e78-5cdd-af52-700ffe6beaa0 | note | Frequency - Each Lot
308c9ebf-5a0a-587b-945a-46b8009d7194 | note | Acceptance Criteria - The following existing services have been migrated to the new ALER3 Comms Rack:
0d12299a-a9b2-5d62-8d94-56cfbc22d557 | note | ○ Building 52
9ef33d09-d127-5ef4-86c1-361f682713b9 | note | ○ ALER 2
d60a87e4-f789-546c-ab5f-688c662abf19 | note | ○ Terminal 2
7fe28862-fc97-5a50-8507-6cf53cbbad2a | note | ○ RVR
138c6d96-eb37-517c-955c-03b626661ca9 | note | Reference Documents - ZULU-BECA-001-SPC-00005-C2100.2
9a1fe90a-e144-58ef-8ba2-362db298c285 | note | ○ Drawings 030-3100 set
89a9fa25-b348-579c-95c2-8f667f5034a1 | note | ○ APAM standards AS/NZS 3000
20199c1e-edbe-59ce-bc87-f0e79b188ec3 | note | ○ AS/ACIF S009:2006
565ebb97-664d-5724-9f79-c20781690edb | note | Inspection/Test Method - Verify
f2c64412-2937-59db-ad0b-a586de2e0632 | note | Record of conformity - This ITP Signed Stowe ITC
8bc06783-974e-57bb-aefa-ce1a176a7566 | note | TP
b931f373-6976-5a31-b1a5-b49becd65747 | note | Responsibility - Project Engineer / Site Engineer
3703dc05-b565-5cef-b01d-7e29001b2e57 | date | Date Completed:
7ed7a4f1-4b9b-4dd3-a3c9-bed53a7d8a21 | checkpoint | Final Inspection
3cf4e266-4bd5-5e1e-b286-6caef97e9a5d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
a542e17c-7b1b-5bd2-ba80-275d50725a22 | textbox | Print Name:
3b3f70b3-9cf4-5e05-8e73-ddb16bdbf7fe | textbox | Position:
a6eb59c9-de1c-59c5-b9ce-402bb3870b83 | date | Work Completed On:
dcef7fba-93e5-5310-91f3-8a3a1898ffca | date | Date:
d402d28b-f858-4f79-bb0f-db2ef9295df2 | checklist | FH-ZU2-QU-ITP052 - Temporary Works - General - Rev 0 | itp | ITP052 - Temporary Works - General
57f2608e-8a36-40b2-a4d1-e981a8530745 | section | 1.0 - Temporary Works - Design Phase
b325a07f-edb3-48be-8ecc-4af53e4c942a | checkpoint | 1.1 - Review Temporary Works Design Process Matrix
5ac04f3f-fcde-5eaf-9505-631aa679c20c | note | Frequency - Prior to commencing activity
a528e3a0-83a5-5bcd-89db-9121c0abc793 | note | Acceptance Criteria - Confirm extent of temporary works required by reviewing the Temporary Works Design Process Matrix.
88b5e6ba-5e3f-5de6-85ca-1e989ca9540b | note | Reference Documents - Temporary Works Design Process Matrix
8361ff05-5aae-5abf-960e-816b38ca0990 | note | Inspection/Test Method - Verify
ee5ec4d1-cc97-525d-8676-b36100a4873c | note | Record of conformity - Drawings and drawing registers
6956151d-2cd8-517a-b18c-7e80c13af764 | note | HP*
74824d80-2432-58a6-9ebf-37f37ac6b4f6 | note | Responsibility - Site Engineer/Project Engineer
c8b04174-6d0e-56cb-acba-c558a8dfe97a | date | Date Completed:
5d8516d7-7116-4655-b2a7-f92eebbe3673 | checkpoint | 1.2 - Submission of Risk Assessment for relevant Temporary Works
fa098975-8ca3-546e-9a3e-1104659fc3cb | note | Frequency - Prior to commencing activity
fb240922-da43-53e0-922d-af04f82a592c | note | Acceptance Criteria - Confirm the level of risk assessment documentation required for temporary works
1750efdb-83f6-50cf-a83b-8032ae10b8e2 | note | Reference Documents - Temporary Works Design Process Matrix
0902896b-2373-5c55-a9b3-140e91ec57bf | note | Inspection/Test Method - Verify
8d8d87d2-e0ff-5f35-9ef7-55eeb061d7a1 | note | Record of conformity - Risk Assessment
0759b215-000a-52c3-b4e7-c05854adac88 | note | HP*
2d5496ee-1c29-591c-951f-b3eea2e38e6d | note | Responsibility - Site Engineer/Project Engineer
03adce32-a2f9-5c05-b71d-ac63d16afc7a | date | Date Completed:
567d615f-5477-41ca-a320-9ee11e846d6a | checkpoint | 1.3 - Submission of Temporary Works Brief for Temporary Works Designer
dd5ad3b6-5efd-5f09-92ed-734c57914ca8 | note | Frequency - Prior to commencing activity
49f8a8b4-5bc5-5976-bc56-f02636cab9e2 | note | Acceptance Criteria - Completion of the temporary works design brief to highlight the scope and required design/deliverables for temporary works designer.
f80ad700-12ed-5d5a-a5f9-fac20ac41072 | note | Reference Documents - Temporary Works Design Process Matrix Drawings
4c3afd1f-6f55-58c3-8977-d34ec738586a | note | Inspection/Test Method - Verify
dda65646-ed10-507d-b8d0-5e816a44ff8d | note | Record of conformity - Temporary Works Design Brief
82fd26c5-d47f-5d66-9bf2-763ffcec731d | note | HP*
d4fa1d7c-34ae-5543-9427-3cf2b2b38644 | note | Responsibility - Site Engineer/Project Engineer
d80ddafd-494a-5da7-bbd1-e60386a8e322 | date | Date Completed:
0bd0e178-0bf8-4332-a474-d1a4a2c7adbd | checkpoint | 1.4 - Submission of IFC Temporary Works Design Documentation
122a1519-332d-59bc-a224-70e9bbf6ff1f | note | Frequency - Prior to commencing activity
051fdaa5-ee9d-5779-bc4b-6cba0949f8c0 | note | Acceptance Criteria - Submission of temporary works design documentation. Including but not limited to:
fccebc2a-9fa0-592a-bff3-15a460b778ca | note | ○ Construction methodology
78c09daa-8718-59f8-8f84-d86443ec9b4d | note | ○ Plans and details
599e7d13-36f7-5888-b371-49ee380e975e | note | ○ Calculations
7fd6d899-9f90-5eae-91b0-68205de2eabb | note | ○ Geotechnical reports
982604a4-abb2-5d5e-8b10-3cb99e876691 | note | ○ Lift plans
37f3bf77-014c-5a09-86fc-85fa243fe573 | note | ○ Material specifications
3c575787-24a7-5aa0-8b99-f1a9a77f9203 | note | ○ Testing (as required)
6bdd7d44-f57f-5809-b70f-ca148b71b69a | note | ○ Inspection criteria/plan
4fcdfb41-23ab-5352-8b1f-9b85be11472c | note | Reference Documents - Temporary Works Design Documentation Drawings
3ccdc7fd-09dd-55e3-8fde-aa3b4840934e | note | Inspection/Test Method - Verify
4f88ab2a-2f3b-52df-ad25-57d30bad7097 | note | Record of conformity - Construction Methodology
70e8c5e5-98f3-58d3-9d5d-04a5bf65674f | note | ○ Plans and details
0049bc2b-7587-575c-9de4-99f72aaf1736 | note | ○ Calculations
97f26df5-f8a9-5fb9-832f-468028e3a696 | note | ○ Geotechnical report
e3995c93-71c5-5781-a9a1-3c6a1ff54915 | note | ○ Lift plans Testing
575acc39-6884-5b28-84ad-810893851e34 | note | ○ Sequence Drawings
72a43086-6a98-54bf-9bef-696126eb17f3 | note | HP*
938e6561-79de-58a4-b9ad-4ddf62381ea9 | note | Responsibility - Site Engineer/Project Engineer
38ad1547-92d0-522a-929a-f250b9d23637 | date | Date Completed:
7aa4acd1-6a0b-46ac-b030-704f53a9186b | checkpoint | 1.5 - Review Subcontractor WMS / ITC (if applicable)
650dfcb2-1f7d-50ff-ac8b-6f1bfd1ccd06 | note | Frequency - Prior to commencing activity
d147f899-dec2-5b6a-aa10-141c2dd73618 | note | Acceptance Criteria - Submission and review of subcontractor WMS / ITC and confirm alignment with temporary works design documentation
234989c8-d9a9-5532-8db9-49cafe0b23f1 | note | Reference Documents - Temporary Works Design Documentation
4ecde8e8-1cde-53bf-bfd6-b733c02e14df | note | Inspection/Test Method - Verify
6f353ce1-8de1-53ed-ab43-675cf343f72f | note | Record of conformity - ITC WMS
39f65c42-da6e-55eb-91d8-de9f2bc2bb34 | note | HP*
6b3e4f3a-0b5b-58db-9551-3af8bf084ca2 | note | Responsibility - Site Engineer/Project Engineer
e205e660-55a0-5baf-b874-bc7f7792e652 | date | Date Completed:
bb365070-2596-4121-829f-dbb002000d45 | checkpoint | 1.6 - Designer Certification check as Profession Engineer (NER / RPEV) – as required
eb9f5e73-516c-564b-9f82-ac6b5cc51b05 | note | Frequency - Prior to commencing activity
20bed086-05c6-5955-b0b7-10c9b9d06b8e | note | Acceptance Criteria - Confirmation of Designers credentials on the National Engineering Register (NER) and/or Register of Professional Engineers Victoria (RPEV)
99b4a508-2159-55a9-a509-0afd462246c1 | note | Reference Documents - Temporary Works Design Process Matrix
6d2bdd45-7d86-5b5e-becd-b172e6ca8687 | note | Inspection/Test Method - Verify
a5eef102-04a1-510a-b4c1-fc5fe5591de4 | note | Record of conformity - NER RPEV
10183743-493e-5e1f-b9c8-263445fcdd3f | note | HP*
ca639267-bfea-5afd-b9c1-9a73a9dc55e2 | note | Responsibility - Site Engineer/Project Engineer
7b8766f7-ccc4-5b4f-9de2-66716a14ed33 | date | Date Completed:
8657e77e-8296-4e3d-a993-3b900e416dcc | checkpoint | 1.7 - Designer Validator Certification check as Profession Engineer (NER / RPEV)
946fd528-4b4c-5db1-a2bb-50f9f5fc93e0 | note | Frequency - Prior to commencing activity
d58ad893-a24e-5792-86d8-407b8f43ad2c | note | Acceptance Criteria - Confirmation of Designer Validators credentials on the National Engineering Register (NER) and/or Register of Professional Engineers Victoria (RPEV)
6a902517-544b-5f21-8fa7-ce6a1f832487 | note | Reference Documents - Temporary Works Design Process Matrix
47e7583d-e279-5ce6-9ecb-9d5c02284190 | note | Inspection/Test Method - Verify
b53a0a1c-bce7-5526-9600-b5704be08e3f | note | Record of conformity - NER RPEV
77fa620d-6345-50e5-8afb-467d17729148 | note | HP*
47304034-bbbc-51a9-9c00-3f9c1497ba70 | note | Responsibility - Site Engineer/Project Engineer
0c58f21a-33d5-53d8-90fe-f12b35c5ee83 | date | Date Completed:
b07346bd-57f8-47b7-960d-f0883816826c | checkpoint | 1.8 - Update of relevant Safe Work Method Statement
8edbee2c-1f0e-531a-9d12-971251013a37 | note | Frequency - Prior to commencing activity
dd99174c-d3ce-5ba9-b6bd-a3cd847dbbc1 | note | Acceptance Criteria - Verification of updated SWMs demonstrating relevant safety controls / mitigations to eliminate hazards
5d422dc5-02a2-5b27-a791-215761f7bb3b | note | Reference Documents - Temporary Works Design Process Matrix
a7ee9745-335b-51ba-93dc-c2878de9a15a | note | Inspection/Test Method - Verify
f2ffef1d-635b-58fc-8a07-b3f4105a266f | note | Record of conformity - SWMS
cc6003e2-3d6b-55c5-a5dc-3ec277d3b0c8 | note | HP*
f0d1db1f-c188-56fa-b034-cfd739d8ac52 | note | Responsibility - Site Engineer/Project Engineer
a21dd0d3-0af8-5834-81e4-8765b176c39c | date | Date Completed:
b6da784e-e40d-4097-b301-95ecf551817e | section | 2.0 - Construction / Site Implementation
a9c7b9ae-7bd9-4279-8825-99c4b9fee15d | checkpoint | 2.1 - Check for correct documentation
1f436b8b-453c-564a-974f-15bc9e58f873 | note | Frequency - Prior to commencing activity
348c1e5c-f7c5-5f53-8b96-131a2b4976cd | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
35193a6a-f7e7-5663-8b2d-04202ba3cfd9 | note | – using the correct and complete set of drawings.
86580564-6515-567d-b6ec-77f04cef6237 | note | – all drawings are the latest revision.
c235b0e9-62b2-557a-90f9-f3f705c8f168 | note | Reference Documents - Approved Temporary Works Design Documentation
fc5b7f7d-db48-5165-a95c-458974d6a0ff | note | Inspection/Test Method - Verify
387b4926-4ace-5003-ac00-3531aed915a4 | note | Record of conformity - Drawings and drawing registers
dffa5189-0e20-5042-a3c3-c8498ffdb8ef | note | HP*
844ff3d6-f2e3-5054-8062-aed995ab15e5 | note | Responsibility - Project Engineer
638e67bb-ee3d-5c01-9d1b-e0f10ad6ed3c | date | Date Completed:
748a132a-1d30-45f7-ae9c-933e65363de3 | checkpoint | 2.2 - Procurement of Temporary Works Material
75c94568-4599-5bb0-ad2b-6c4a2287871d | note | Frequency - Each Lot
26bf04d5-3d50-58b4-8172-bb7364feff6a | note | Acceptance Criteria - Ensure all required materials are procured in accordance to approved shop drawing specifications / requirements.
1989dadb-7be6-52f7-be02-a06759d8b193 | note | Reference Documents - Approved Temporary Works Design Shop Drawings
a90f8446-b392-5521-8c3b-c2b6e92788a6 | note | Inspection/Test Method - Verify
d7bd96b8-aadf-58c8-b2c8-d8a6648ba9a8 | note | Record of conformity - This ITP signed
06c3b654-61e6-52b4-8043-a202bdd1f67f | note | WP
f1d84d3f-963b-5121-8176-5e9386ba5004 | note | Responsibility - Site Engineer/Project Engineer
4ac74cd6-3384-5fe9-a962-521388c8aade | date | Date Completed:
ebf6b6dc-df2e-4e06-bfbf-ca90b43b80d1 | checkpoint | 2.3 - Certification of Compliance
d4ef1392-4849-5be9-8933-163831f95d59 | note | Frequency - Each Lot
d55eb3f2-fa41-5525-961a-42a169db07e5 | note | Acceptance Criteria - Provide manufacturer’s Certificate of Compliance against temporary works drawings.
5a744e08-78a3-51ec-a0ab-328f6c0435be | note | Reference Documents - Approved Temporary Works Design Shop Drawings
a80c22fc-9539-581e-bde8-b03edb5083c8 | note | Inspection/Test Method - Verify
4cb544dc-b13c-5758-8a02-2fb477b993aa | note | Record of conformity - Supplier’s Certificate of Compliance
99981ae5-545a-5581-8c5d-f45d058b9c86 | note | HP*
db8b0865-66df-536f-a6a2-54dacb1d4039 | note | Responsibility - Site Engineer/Project Engineer
ca492735-a31a-51c4-944a-21021d34ea0b | date | Date Completed:
e0b2fa12-e6d6-4888-ac1e-e8891590e56b | checkpoint | 2.4 - Implementation of all measures and controls
e68d58b2-e51b-5b7a-b99e-7b0c522dd545 | note | Frequency - Prior to commencing activity
7df7db5a-b7d7-5814-8d31-31580a211a68 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
4b193d93-d74c-5917-aeb6-6619cc3a8379 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
2be41416-4022-5e0f-a625-af49815b625e | note | Inspection/Test Method - Visual Inspection
30cd5a3a-235b-55d5-bc74-503efcd2e30c | note | Record of conformity - This ITP signed
a48ba535-6dae-5746-9dc9-0ff51591f765 | note | WP
92183b14-7ec6-5147-a1cf-9cbbc39d7343 | note | Responsibility - Site Engineer/Project Engineer
e2c93d39-a74f-547e-bf0b-7e7553a792bf | date | Date Completed:
abbba430-af2d-458f-b36c-b58b51b057f9 | checkpoint | 2.5 - Ground support check
601deb59-f6a7-5ff9-90c4-6b39987d1918 | note | Frequency - Prior to commencing activity
de137158-f874-557c-b95c-9a39887dc98f | note | Acceptance Criteria - Confirmation of ground conditions comply with the expected ground conditions as per geotechnical report / structural drawings.
162bfbab-a3b9-575b-a728-98afdf1e3dfe | note | Reference Documents - Approved Temporary Works Design Documentation
4cd5d899-a932-5375-9633-338c72eb843b | note | Inspection/Test Method - Test Report
0141524e-a986-541c-80d9-95b05179b598 | note | Record of conformity - Inspection report, Geotechnical report
208fa1c8-87c5-569d-a932-6a1bfc04be50 | note | HP*
6605fb23-d602-57cc-9d0a-a8e797efa14f | note | Responsibility - Site Engineer/Project Engineer
4016f221-add5-5d88-b1af-c9a226e4d11e | date | Date Completed:
780cebae-9f9e-42e9-87bd-8689ca415e46 | checkpoint | 2.6 - Survey Checks
893cad74-5a39-5c25-b072-40f906ed8c57 | note | Frequency - Prior to commencing activity
f6c681fc-5f6f-50c9-aac2-bfff77033a22 | note | Acceptance Criteria - Survey set out to be completed for all assets
7e5e5f4d-e533-5139-b550-0ee3a2e0e830 | note | Reference Documents - Approved Temporary Works Design Shop Drawings
2531344d-d95a-5812-97b6-22f887e5c2a6 | note | Inspection/Test Method - Verify
62d512eb-de52-5a53-903c-655e32a8a1fb | note | Record of conformity - This ITP signed
d9639908-e4c2-5efe-8b02-d6a4999748a3 | note | HP*
7de4dff0-0113-54f6-a795-43a3c3c67b55 | note | Responsibility - Project Engineer / Surveyor
5abfc7d1-94eb-5a88-9ec7-0cb7727b06d6 | date | Date Completed:
1c92a23c-f23d-4682-b275-2357b730d92f | checkpoint | 2.7 - Permit to Construct Temporary Works
f8fc503b-2e2c-50c9-b119-d6ca507c426d | note | Frequency - Each Lot
99e92316-0167-5492-987e-766255406063 | note | Acceptance Criteria - Verification of work described has been inspected and approval is given to construct in accordance with the temporary works design, detailed construction methodology, inspection and test plans, and risk assessment.
7b32838d-b592-5a3b-a1f7-51b55098bee0 | note | Reference Documents - Construction Methodology, Sequence Drawings
d9475d69-fde5-5233-a257-060a67557137 | note | Inspection/Test Method - Visual Inspection
db40b785-c568-5094-a0ad-3095a3d7e8d7 | note | Record of conformity - Temporary works permit to construct, apply load and remove, Subcontractors ITC
c3827081-c477-52a9-a2f7-284fffd53fb4 | note | HP*
c1477a5e-71e4-56fe-a620-ce86e4c4338b | note | Responsibility - Temporary Works Coordinator, Project Engineer
b89d3da1-182e-55e4-a09c-1dfadbdcf0a4 | date | Date Completed:
559b4c3d-4f94-4d6d-933d-a491f5bc8720 | checkpoint | 2.8 - Permit to Apply Load to Temporary Works
6df1aa50-c0cf-5677-b380-588de75578f3 | note | Frequency - Each Lot
9630ee16-e383-5138-876f-c234af8ec39b | note | Acceptance Criteria - Verification the temporary works described have been constructed in accordance with the temporary works design, detailed construction methodology, inspection and test plans, risk assessment and all required checks carried out.
b1fd2efb-b786-5631-9008-47b28e8c47f5 | note | ○ Any minor non-conformances between construction and design are to be noted.
3952a2a3-0548-5b4f-8deb-13ada5e6f73b | note | Reference Documents - Construction Methodology, Sequence Drawings
a59ca4f5-59be-5781-b61f-0378a70741d4 | note | Inspection/Test Method - Visual Inspection
b8f24701-d7d3-52bd-9c8b-c271898f7cb6 | note | Record of conformity - Temporary works permit to construct, apply load and remove, Subcontractors ITC
870c7e67-c378-5bb7-a8be-7d2b47430881 | note | HP*
1642dd8e-29c5-50f8-a387-47d0c7a32213 | note | Responsibility - Temporary Works Coordinator, Project Engineer
8235fca2-03c2-5383-9d66-6f706793fe16 | date | Date Completed:
c5f7c24d-59ee-4c9a-b478-3568b7b40915 | checkpoint | 2.9 - Routine Inspections (time, weather event, etc.) where applicable
0f27ccb0-3e87-5b06-b336-3d4adc8be26e | note | Frequency - Each Lot
3049dc4c-f575-5cf2-84cb-5c7686929c34 | note | Acceptance Criteria - Evidence that routine inspections as defined by the temporary work are undertaken (where applicable).
fc6f9393-3bff-569d-886e-a1ee2c5a13f5 | note | Reference Documents - Approved Temporary Works Design Documentation
62b9d771-018d-55ac-a957-6fca4d7bd7f8 | note | Inspection/Test Method - Visual Inspection
4586f31a-39a7-5c9f-a2fd-f25d9f5261a5 | note | Record of conformity - Inspection Report, Subcontractors ITC
4edb503b-eb9b-5f6c-89cd-499ee435140c | note | IP
6955ba2d-921f-53b5-887d-bb83a4e9252a | note | Responsibility - Temporary Works Coordinator, Project Engineer
7f8d7cd8-93ed-5216-b970-5789b8979853 | date | Date Completed:
c11222de-09ed-4bef-b3fe-dc82bc442a40 | checkpoint | 2.10 - Permit to Remove Temporary Works
e20b6365-9c49-55f3-9369-ba4d73548be1 | note | Frequency - Each Lot
e8a55e6e-ffd9-54bc-9134-4a8f15a85d37 | note | Acceptance Criteria - All necessary checks have been completed and the temporary works described may be removed in accordance with the detailed construction methodology, risk assessment and inspection and test plans.
275a5c68-a47d-57da-b5b8-54597cbe6c04 | note | Reference Documents - Construction Methodology, Sequence Drawings
e2c21b46-78dc-5959-a4ff-ec1bb36bb92a | note | Inspection/Test Method - Visual Inspection
59cdb282-86f2-5a20-8b0e-6de6a8173790 | note | Record of conformity - Subcontractors ITC
e89e12b2-e1c5-5dc7-8427-a99e1c9cd13a | note | HP*
35046a3b-cdda-5fc9-a9ad-3ed85ce63789 | note | Responsibility - Temporary Works Coordinator, Project Engineer
c8a9715a-76bb-5872-8687-31ac4152ae7d | date | Date Completed:
6594bb63-59e5-4c8d-8130-78f9766829d6 | checkpoint | 2.11 - Demobilisation and tidy
0c9643d8-1390-5e54-8b86-a53fa33964fd | note | Frequency - Each Lot
135f7e6d-0441-54d2-88d2-2a3b86110cf5 | note | Acceptance Criteria - Ensure no remaining material is left behind and housekeeping completed.
88beb2be-f51d-5c1d-88e7-cc2796490a74 | note | Reference Documents - N/A
fde7e1f5-b35a-54e1-95cf-b1c57339d4e4 | note | Inspection/Test Method - Visual Inspection
19745d2f-6f5f-5417-8056-fde68873e842 | note | Record of conformity - Site Inspection
1c6b3b8b-dd22-56f6-9a89-7fd3ab242e9d | note | WP
454b6e18-8aa2-5214-a1f6-4929dd67d9b4 | note | Responsibility - Site Engineer/Project Engineer
624c1f33-7c14-5c44-8bbb-0cb3a89d6eb3 | date | Date Completed:
8233e0cb-065a-459c-b10b-d978ae41bdeb | checkpoint | Final Inspection
a0a124bb-a512-505d-9163-6b3c02ddea79 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
de73e4c3-e087-52a2-aafd-48da14212584 | textbox | Print Name:
3c0b0819-6a65-563c-87d7-c72237d99ecd | textbox | Position:
60664e5d-8b30-58fd-bd51-949885df4c45 | date | Work Completed On:
c1e70ad0-3bdd-59d9-9d16-9642c9138234 | date | Date:
f4ad3654-824f-4b2f-9b44-e8211c7f5b87 | checklist | FH-ZU2-QU-ITP053 - IWDI Install & Commissioning - Rev 0 | itp | ITP053 - IWDI Install & Commissioning
eb7002a2-a7cf-4f67-9eef-b1ff0b3df479 | section | 1.0 - Preliminary Works
80b960ab-644d-4b41-b1cc-9a9beadef341 | checkpoint | 1.1 - Check for Correct Documentation
292df0f7-3cde-5c01-86f8-e307f54f1f86 | note | Frequency - Prior to start
4e6f2443-d415-5ed9-adb2-1d3bdbb10022 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
8fa73ddd-1ce8-5b3f-a615-8149ea370e59 | note | – using the correct and complete set of drawings.
8ffce494-169a-5171-8f2d-2cc1dbd39bc4 | note | – all drawings are the latest revision.
4fe1e597-7fb9-5613-9a89-4907e8cadb44 | note | Reference Documents - Drawings / Aconex Register
90af1f6a-ef7e-521d-8418-8f209bed1131 | note | Inspection/Test Method - Verify
bb81b98c-4659-52d7-afd0-687cbc9bfbb2 | note | Record of conformity - Drawings and drawing registers
333d6f2b-3e26-561e-be24-fe5367009a84 | note | HP*
773b90be-b200-5dd9-8f9c-a2da517235fa | note | Responsibility - Project Engineer / Site Engineer
e9cbd0f2-492c-5ade-8d8b-e371eb39f7bc | date | Date Completed:
22f5f822-4dd6-4538-8388-70fcf7ef5fd7 | checkpoint | 1.2 - Implementation of all measures and controls
1c1f0496-5ea0-5a04-8dad-0795b6e96eac | note | Frequency - Prior to start
1799a1d4-ac57-5365-8fee-ca9243666aeb | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP
5cc7f5c9-fd8f-5ea2-91b3-d7ec1b3183e1 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
e4883355-ce87-5046-8f67-c2cdce86ccc6 | note | Inspection/Test Method - Visual Inspection
05e79a6c-aa86-56fa-a301-7d99f6b3a290 | note | Record of conformity - This ITP signed
8d41c274-b084-5cf6-8a67-b4ba823c18f2 | note | HP*
b4b75778-1392-56ee-a0fb-c5266025226f | note | Responsibility - Project Engineer / Site Engineer
6d25945a-c531-5422-baa9-054e12d00ef9 | date | Date Completed:
b1d6f350-25a1-4d1e-940c-f71243bf5285 | checkpoint | 1.3 - Pre-lift preparation
c8c93eb6-73b3-5ad5-be1e-1301664840ff | note | Frequency - Prior to start
a83b87fc-bb8b-53e5-88a8-d41f58fc2106 | note | Acceptance Criteria - Prior to Franna lift, the below shall be completed:
a5866853-9308-5f71-a5c1-cff4902d0e08 | note | ○ APAM Crane Permit
056a937f-3862-5630-842a-e0e244fff762 | note | ○ Mobile Crane Checklist
dbf28477-41fb-53c2-b691-6b7156e847cf | note | ○ Lift Study (if required)
d74d9be9-7b10-5859-980c-7b0c8ec42246 | note | ○ Certification of any lifting lugs/beams/spreaders (if required)
bad2076a-cdac-5598-bc12-ee02717210d2 | note | ○ Pre lift checklist
805ad97b-9c3d-575f-a92d-0ff464102923 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
6655e475-ca1d-5174-9103-4be2d8a77464 | note | Inspection/Test Method - Verify
27462ab0-64e4-5a76-9448-28f05c4d52fe | note | Record of conformity - This ITP signed
17d2bb7d-0d47-54c7-95ac-c3d009445cda | note | HP*
52878b78-2807-5422-9015-5756dd5aeca7 | note | Responsibility - Project Engineer / Site Engineer
9f33a08d-7f69-563c-89f6-5e9499e4eb68 | date | Date Completed:
3d80a59b-8a92-4cbb-8ba1-c193a233644f | checkpoint | 1.4 - Material Submissions and Shop Drawings
4e86f96e-bc6f-587d-a637-a6f70b38dd43 | note | Frequency - Prior to start
50ab75cc-c11c-57ba-9c11-c756d357e8d0 | note | Acceptance Criteria - Submission and approval of the following:
cce393b4-2dc0-5c76-a174-e882166b43a6 | note | ○ Pole Structure
f0ff1131-26b7-5a82-b7fc-313a5e93a4be | note | ○ Windsock (white)
fd431648-84d2-5a88-bf74-425020fe572f | note | ○ Bird Spikes
fda2ef06-b295-5d7d-8170-2c8b40d663af | note | ○ LED Lamps
98dd44a8-1b39-5fe0-9df9-af8106c798fc | note | ○ Isolating Switch
5039b114-a6a2-5fd6-b784-e76ed3012882 | note | ○ Surge Arrestor
087fd8ea-1d53-5a39-ac84-bfe518f6c6b4 | note | Reference Documents - Drawing 07503
0187800d-7010-53ed-b7a5-db6c52b980c7 | note | Inspection/Test Method - Verify
6f8117e3-112c-5df7-8990-69c852177580 | note | Record of conformity - This ITP signed Aconex Reference
9e6847eb-6d0e-5e72-92f5-4cf7a9fc2640 | note | HP*
a587363f-2d97-5a17-9793-9a064b478ec0 | note | Responsibility - Project Engineer / Site Engineer
35c2afc6-7041-583f-8b45-7ef51e03b1d1 | date | Date Completed:
679da2f0-e146-477b-9906-0e6655c6bde4 | section | 2.0 - Installation
4778854a-482b-4e0b-b49f-887b7c430cf0 | checkpoint | 2.1 - Pole Install
a9036c8e-f615-552d-a5ed-b8d81dce04da | note | Frequency - Each Lot
2c2a4919-e699-5e0c-822b-b49ac3efeb3b | note | Acceptance Criteria - Pole installed level as per manufacturers specification and design drawings.
0888c440-57b8-5f80-b397-d9e989c8c1e8 | note | ○ Rag bolt nuts secured firmly and torqued as per manufacturers specification.
16c4452e-9232-5aa5-966c-529475208d9f | note | Reference Documents - Manufacturers spec Drawing 07503
a43fcce6-e910-5488-9027-7874537b21dd | note | Inspection/Test Method - Visual Inspection
98c879c0-540c-565f-9036-ba436efcc4da | note | Record of conformity - This ITP Signed Avionics Checklist
a34984e1-ff03-588b-b988-08da4e1a9d79 | note | IP
03717371-26d4-5703-bd7a-7d2cf5d020bb | note | Responsibility - Site Engineer / Foreman
0ea0ce52-dabe-5c7f-b04f-8e9083f1b6fe | date | Date Completed:
bc59a827-d6f8-431c-bd80-bdd6cd17f28e | checkpoint | 2.2 - Cabling Works
ad4b0ef9-3b64-548b-8d76-fefed27d38c2 | note | Frequency - Each Lot
c7eacd51-fa48-500e-b736-5c2e2f8db07f | note | Acceptance Criteria - Install cabling, isolating switch, surge arrestor, earthing and termination box
35b516d6-cf3a-52fe-8872-2bc654ce7bf9 | note | Reference Documents - Drawing 07503
be002884-8883-59a2-9143-b813d51f131b | note | Inspection/Test Method - Visual Inspection
b947bb25-a18b-5878-aadc-7f5d551b887e | note | Record of conformity - This ITP Signed Avionics Checklist
1158ac5a-223a-5e4e-befe-e87e481192dd | note | IP
1455e241-3269-57df-9286-161052025d7f | note | Responsibility - Site Engineer / Foreman
903fbe8f-10fd-5fb7-a3ba-f88d1516cd02 | date | Date Completed:
507b084d-8f25-4a87-848e-958879beb543 | checkpoint | 2.3 - Lighting
72eea572-9a20-5839-bd66-7aee64654288 | note | Frequency - Each Lot
6a41cb59-9cd9-5dd4-a4b4-eca47cdcfb03 | note | Acceptance Criteria - Install and connect LED lamps
6d01e797-24b3-5af9-bbdc-fa20532cd6d8 | note | Reference Documents - Drawing 07503
9dea7b07-74ad-5591-a937-da5800f9543e | note | Inspection/Test Method - Visual Inspection
6391ce4b-99e9-576f-8589-40a2a7f4cc5d | note | Record of conformity - This ITP Signed Avionics Checklist
c7b3c61d-64ae-56e4-ac73-8b933e4197e6 | note | IP
70070276-20db-57ea-a567-5b84f9836280 | note | Responsibility - Site Engineer / Foreman
7a69a1b9-eae0-50af-8910-6cede775d612 | date | Date Completed:
96ecb341-7dd9-45ae-96c9-f984d48133a9 | checkpoint | 2.4 - Windsock Barrel & Bird Spikes
29ac6b26-d3ea-5f32-882b-f0fca0662086 | note | Frequency - Each Lot
c27be487-dfca-58c1-a4c6-d0bd069f1a2d | note | Acceptance Criteria - Windsock & Barell installed and secured to pole, ensuring the windsock is installed 6500mm from the ground as per MOS139
fe2147f4-ec84-5679-bbe7-7b209cef788e | note | ○ Stainless steel bird spikes installed to floodlight mounting arms
63710f21-94b5-5bac-9f10-ac8796662880 | note | Reference Documents - Drawing 07503, MOS139
b7c57f41-bc79-5541-a4a1-53edf4149611 | note | Inspection/Test Method - Visual Inspection
13232570-a3fc-54ed-9b4f-7154510ecb07 | note | Record of conformity - This ITP signed
e78fbd16-a985-5d10-b81e-e26595e04754 | note | HP*
a60c3da7-a397-5332-9d36-3f8737ece595 | note | Responsibility - Site Engineer / Foreman
1f24f3ad-6d18-59f4-965e-b46e1e5f2b2c | date | Date Completed:
a38d198a-a8b4-4bda-bb0c-a55952570d3a | checkpoint | 2.5 - Assembly
b8fbd29d-7145-5710-a51d-8252dff9ed8f | note | Frequency - Each Lot
3841ccba-591c-543b-8662-8f2ec3f455f4 | note | Acceptance Criteria - Demonstrate the lowering of pole and making sure the mast assembly isn't damaged when lowering.
1a54277e-4f77-5d4d-a076-18b0ba5e07f9 | note | Reference Documents - Aconex BecaCPL-GCOR- 001356
6f8b1392-85aa-5654-a4c7-ac0cd20d947f | note | Inspection/Test Method - Visual Inspection
0d648d11-80f5-5fa3-b39a-28bc8b2d7bd1 | note | Record of conformity - This ITP signed
73c1dd97-dee8-5018-a665-4d81e2ae8433 | note | IP
8c5dddcb-bdd0-59c6-aa65-a827e9657e0a | note | Responsibility - Site Engineer / Foreman
1b36dd7e-fc66-5ed9-ab6b-8673daec303c | date | Date Completed:
fe07c2da-cf68-428e-8ca0-07c2fb914a75 | section | 3.0 - Testing and Commissioning
10f6f915-0d52-4562-851d-2a471d95e5fb | checkpoint | 3.1 - Energise IWDI
4ad00fb4-db22-5128-9021-306cf7bbcd18 | note | Frequency - Each Lot
dc9df609-732f-51ce-ad38-815f0a8b8ef4 | note | Acceptance Criteria - Perform relevant cable tests prior to energization (not limited to):
7b53357b-4e1e-5a4e-b6ae-aa0a9336cd9a | note | – Polarity Check
1e817573-da08-5400-8613-6124ead3fdc1 | note | – Cable Loop Resistance (Ohms)
a9f1e52f-934e-566c-826d-b452c9ba16cb | note | – Insulation Resistance (Core-Core& Core to Earth)
f07a3512-ec64-5f3d-8ef7-9c7b51ea00ae | note | ○ Confirm all test measurements are within AS3000 tolerances.
9ac88af3-9e43-5a2f-ab84-9dd9ec39b277 | note | Reference Documents - AS3000
2ca34190-5eac-58e1-93d0-7cba43ef3403 | note | Inspection/Test Method - Verify
7e157de0-c2f7-5239-addd-d21fcf856b36 | note | Record of conformity - Certificate of Electrical Safety (Non- Prescribed) (CES), Avionics ITC
1e2c2f36-d965-5703-809e-b21bfcac98a9 | note | TP
40e4804a-8322-59b1-aed1-371c2c583a3a | note | Responsibility - Site Engineer / Foreman
3d4cf911-90f8-5343-9b44-b6fc16f39cb4 | date | Date Completed:
5eb39697-3f14-420f-903c-f4b048dd91e9 | checkpoint | 3.2 - Testing – Lux Measurement Testing Grid
4312c378-281d-588a-881a-be44ccfdf5fa | note | Frequency - Each Lot
599cc5b5-6195-57d5-8361-ccbe79dab81f | note | Acceptance Criteria - WITNESS POINT
7101506b-ddf9-5bdd-8f99-8b0dcf03d87a | note | ○ Provide 7 days notice to Principals Rep to attend
27fafa80-4326-5f1d-8652-a32f3879244a | note | ○ IWDI shall be fully tested by continuous operation for not less than 24 hrs as a completed system prior to acceptance. The IWDI shall illuminate properly during each portion of the test.
3c5e3a3b-50c3-56da-bef1-acc5759ed7bc | note | ○ LED Lamps to be tested as per MOS139, with each reading between 100 to 600 lux within the testing grid.
f59cef5d-957a-5d03-b296-44896657fb82 | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl. 4.6 MOS139
e6bf4283-30c1-5433-8c2c-6fe05e455b67 | note | Inspection/Test Method - Verify
005be2ce-cd67-5af1-9d61-553830ccd54c | note | Record of conformity - This ITP signed Test Results, Letter of Conformity Avionics ITC
f22078a3-96d0-5c00-8a13-27c56cb5c2b0 | note | TP WP
7c7e547e-5cb9-5b64-8cb9-68536d7c8754 | note | Responsibility - Site Engineer / Foreman
fa9b5103-406c-5f5d-bd27-b9905d9f5ebd | date | Date Completed:
765c8ce8-024b-4550-8ff9-ee670edea300 | checkpoint | 3.3 - Testing – Glare/Distraction to Pilots
166ee911-38d6-5e55-b295-aba2899fae31 | note | Frequency - Each Lot
d55c1a67-e302-5b95-af3a-60a517746b74 | note | Acceptance Criteria - From an observer’s standing position on ground that is level with the base of the pole there should be no glare at a range of 25 m or more. The assessment need only be made from those directions likely to be viewed from landing, taking-off or taxiing aircraft.
ad1cb1f9-54e3-5770-9f42-48ef6fec5191 | note | ○ Qualified individual includes an electrical engineer or a licensed electrician
78f18d7f-cbbd-5d14-8a36-ff8e8fd73fe6 | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl. 4.6 MOS139
5a51daa2-5c0b-5eb8-9418-ba15453ccdaf | note | Inspection/Test Method - Verify
ca7e3405-78e3-5f5d-b566-33852afc917b | note | Record of conformity - This ITP Signed Avionics ITC
dbb433bd-8151-59f9-88fd-effa3dc2c082 | note | TP, HP*
e157ef93-0638-51f0-bf99-bcf13c524006 | note | Responsibility - Site Engineer / Foreman
4deee960-c74b-5059-943a-2c3ac407d341 | date | Date Completed:
2be9cdd4-ee30-465c-8f9a-6be98889ff28 | checkpoint | Final Inspection
8aae8cd9-d798-5af3-b1b8-49a94a2075a2 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
7f170f86-9f3e-5e51-9dc2-dd51529bd4df | textbox | Print Name:
11de7e8a-f0bc-5685-acbe-3fe3687b8a09 | textbox | Position:
ef57db54-e161-516a-aab0-6ebc2babecce | date | Work Completed On:
6f2d6757-050b-5f20-b4de-dfedf122a574 | date | Date:
a55a9798-1f89-4739-acb3-6d6490560f53 | checklist | FH-ZU2-QU-ITP054 - ALER 3 Fill Placement - Rev 0 | itp | ITP054 - ALER 3 Fill Placement
c9e93f6f-87bd-4b53-84a9-d0042b781943 | section | 1.0 - Preliminary Activities
4a228689-3cdf-4e06-8397-a34f8acba002 | checkpoint | 1.1 - Check for correct documentation
b77436a7-7efc-5c7b-8ca9-2f8fc9e2a62a | note | Frequency - Prior to works
a71dbf33-cecc-570f-a4d0-04f6a4bc2bca | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
75bbd758-d72a-52d4-a0c6-229ed7102020 | note | ○ Using the correct and complete set of drawings.
c8590b87-127b-550c-96b5-b5cad59d24bd | note | ○ All drawings are the latest revision
02ab51d0-9e02-537c-b2ac-080ae02daa58 | note | Reference Documents - Aconex
c2bdd5d3-01d0-55c0-85d7-9b6610ea5f00 | note | Inspection/Test Method - Verify
b0509ebb-0f0d-535d-81b8-7ab74b154f14 | note | Record of conformity - This ITP signed
269e1cb2-6111-5bb3-818f-df50a3cedcac | note | IP
ef54bc96-30aa-5cf4-bd8d-a8ef077df3c3 | note | Responsibility - Project/Site Engineer
c6ab5916-9435-5cd7-a7af-a148e2029a3c | date | Date Completed:
df2f11f1-f5f8-4d97-a88e-09b541676115 | checkpoint | 1.2 - Implementation of all measures and controls
08e97c9e-7ebd-5018-8b6b-decd10ea2f91 | note | Frequency - Prior to works
13fe5b81-0126-5a69-b52d-248fa351b1fb | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS and WP.
4c9bfc68-b108-5822-91bd-a8b80beb43d0 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
e8a59c9c-17d6-5f3e-ab91-ef6ec6aa5ee3 | note | Inspection/Test Method - Visual inspection
b430bd31-3631-5d09-ab37-023a90807736 | note | Record of conformity - This ITP signed
1b5b0066-a523-5689-ac48-533a43651447 | note | IP
c1a0bab7-add7-5876-9ada-459714aa5b97 | note | Responsibility - Project/Site Engineer
8e79f178-219d-5e66-a38e-fe776ab0288d | date | Date Completed:
48d9b781-350f-4224-bc28-ad92aaec99eb | checkpoint | 1.3 - Survey
6beaf11b-5742-5a7a-b70e-69d06cb21812 | note | Frequency - Prior to works
a2bf2243-7399-57ec-a23a-2c074a19cab6 | note | Acceptance Criteria - Area has been surveyed, highlighting any areas where excavations should not occur (e.g. exclusion zone).
cbf68b55-df42-5f43-8aef-9d3dadb0fad6 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
24aa6009-726a-5295-9870-5b445a0fa848 | note | Inspection/Test Method - Visual inspection
7d53888f-36d5-5c24-8763-7c12f01dc44f | note | Record of conformity - This ITP signed
da92cc5b-e06d-53fd-ba6d-ffb351398b8b | note | IP
a764db1f-1b33-5a71-89ea-fbb4344dd198 | note | Responsibility - Project/Site Engineer, Surveyor
5804e54d-fa7c-55ec-b5e8-775d56e5464e | date | Date Completed:
04932730-58bb-47be-859e-a589cec4b790 | checkpoint | 1.4 - Submission of Capping Layer material
001c8f95-74da-5f91-beff-f32e8a76f47f | note | Frequency - Prior to works
371bdb94-5798-55b2-a504-565fee2950bf | note | Acceptance Criteria - HOLD POINT
e016df7f-ef0e-5b8f-bb1d-c2456257fdf3 | note | ○ Submission of APAM supplied recycled crushed concrete 20MM Class 4 to VicRoads Section 812 and TN107
22d4a101-04ed-53b6-86ad-44ffdb6e7982 | note | Reference Documents - FHPL- GCOR- 006781
bf46210e-acae-5c44-8ea7-894b6b360b1e | note | Inspection/Test Method - Test Report
5cac1302-7335-55a7-9f2a-b73bc0f37d12 | note | Record of conformity - This ITP signed, Aconex Reference
2d2309dd-8c3a-50f9-b1d6-b3ec4f497473 | note | HP
88bdfef0-d436-566e-aba2-6d1845b76b5c | note | Responsibility - Project/Site Engineer, Principles Rep
0f093f8c-13ce-54f8-ad66-8998cc88a2ac | date | Date Completed:
78b9d623-1081-4dd7-bd38-8bf0bd6aaf8e | signoff | AUTHORITY HOLDPOINT
97f54454-8128-420e-97a6-f6442087553a | checkpoint | 1.5 - Plant & Equipment
e8502849-47cc-5f5a-a8cf-b52cce5a7aaa | note | Frequency - Prior to works
9c7ce1bb-6849-517c-ae75-185baa72dde7 | note | Acceptance Criteria - All plant inducted and inspected as per Fulton Hogan’s plant safety guidelines
20b4f6c5-9ba9-5824-ab62-51b934180c39 | note | Reference Documents - FH Safety Policy
9083462c-7c93-547c-83e9-7c9c716481d3 | note | Inspection/Test Method - Verify
36e5b8fb-c652-51a3-bb1f-77090bca4d3e | note | Record of conformity - This ITP Signed
2e2efbd3-33dd-5881-b484-82db73270f56 | note | HP*
2e54a559-7308-542e-bc1b-f85483d460bc | note | Responsibility - Project/Site Engineer
95908205-998f-5452-ac24-e830e773ced7 | date | Date Completed:
9a20d20f-73a2-4849-acc0-8de9b1075a9c | section | 2.0 - Select Fill Works
83037846-f63c-4994-8773-d4f7e704af91 | checkpoint | 2.1 - Select Fill Placement
a2667a9c-42a2-590e-9b18-941b20997929 | note | Frequency - Each Lot
d8687cc2-06ae-59f8-ab90-c71ab7c2e67c | note | Acceptance Criteria - Each Lot of fill must:
f870d9cc-9d86-50cf-afcf-47afb0fbdf2f | note | ○ Not be greater than 300mm in loose layer thickness
002da607-a79e-5e2f-b468-0f15772fe8ac | note | ○ Be placed in manner where handling and spreading does not produce gradation of the material
965d9b35-8e9d-5067-a083-89a3bfc7f556 | note | ○ Surface is always self-draining
79066f18-4fae-5d93-a1d2-ba65b223e6c2 | note | ○ Where constructing Permanent batters, it shall be overfilled, compacted, and cut back to the dimensions, levels and design grades to ensure the final batters have the required compaction
d17e4da6-b265-5217-9336-547c1b2cea01 | note | Reference Documents - Drawing 00201 E27- E34
f64eaf30-689e-51eb-a797-9b67e1d700ba | note | Inspection/Test Method - Verify
4cb83a34-6fc5-5faa-8778-797904b8f685 | note | Record of conformity - This ITP signed
d004237b-3ccf-5528-b641-35118ce771e6 | note | IP
1be24c1e-12c7-5521-81a1-ca0ed900b5db | note | Responsibility - Project/Site Engineer, Foreman
160fa9bf-08e2-51e8-8952-aabfcd45b092 | date | Date Completed:
709e255c-6533-40c9-b6ec-40e42fb2545a | checkpoint | 2.2 - Compaction
40230a8c-a86a-5add-8146-9b70176a51b6 | note | Frequency - Each Lot
bb153dfa-ff40-59ec-ae5a-bfdb23da46d8 | note | Acceptance Criteria - HOLD POINT
2c20782e-bb54-5aea-bceb-2685631e2f63 | note | ○ Engineered fill material shall be compacted by tamping rollers and methods approved by the Superintendent. In areas where access by such plant is not possible, it shall be compacted by a Method approved by a qualified geotechnical engineer.
c03c96fd-04fa-5f7d-ac25-2db4030e0a9b | note | ○ Ensure each fill layer has adequate bonding between layers and is free of laminations and discontinuities
f77333c5-3b02-5cdb-991e-4b0848e537fa | note | Reference Documents - Drawing 00201 Notes E37, E38
a847d0bd-2748-521a-8ef8-06a3eccda363 | note | Inspection/Test Method - Visual Inspection & Verify
6fe89d19-97ab-5b17-855e-8b01f325803b | note | Record of conformity - This ITP signed
b880d4bc-bf1a-56b2-94b8-326b134c40a5 | note | HP
81ff72a9-50a3-5dfe-a654-ee8eff1a43e8 | note | Responsibility - Project/Site Engineer, Principles Rep
27bac015-fcc3-5895-a06b-11511b298f12 | date | Date Completed:
fd66817d-24d3-435f-95af-1d032f4cfd28 | signoff | AUTHORITY HOLDPOINT
7616d9f2-9fb9-4bf0-a3d9-55a651cc9366 | section | 3.0 - Testing
3ba2bf31-75ad-48d3-82da-a4bd0aee27e1 | checkpoint | 3.1 - Compaction Testing
afc94a65-a2f1-5225-821b-3ca7143eabee | note | Frequency - Each Lot
9fec3a83-7490-551b-ba91-6a62b11d6d23 | note | Acceptance Criteria - Compact by rolling to achieve a Dry Density not less than the following:
b05bb29f-f882-5ab5-a830-b388e4525939 | note | — Greater than 300mm below formation level to MIN 95% SMDD
ebfe0824-7160-5d2e-abd3-f4ccd47767ac | note | — Top 300mm below formation level to MIN 98% SMDD (Capping Layer)
85143a75-38fb-5aed-9431-3a670958dfd0 | note | ○ The minimum frequency of field density tests shall be in accordance with AS 3798 TABLE 8.1 and not less than the following:
95b77b61-8d3f-5c3e-b7ea-fad55276fd05 | note | — 1 test for each 500m³ volume of compacted fill distributed evenly (minimum 3)
53c8a4c4-5d1b-563f-ba37-622221978309 | note | ○ Test Certificates to be provided 14 days after completion of each test to the principals representative
4df69f2b-f4db-5ecb-af38-7a29622f81bf | note | Reference Documents - Drawing 00201 Note E33, E40, E43, AS1289 5.8.1
5cbb24a6-0e34-56c5-84a8-65e825c58489 | note | Inspection/Test Method - Verify
ed565e8b-aa80-5706-bd7f-1f331f4b8e8e | note | Record of conformity - Test results & This ITP signed
8a5f20ff-ce09-506a-b7b7-9155ecee3017 | note | HP
886b93b0-61d1-5c6d-92ce-fa077f5e63ff | note | Responsibility - Project/Site Engineer, Principles Rep Foreman
473e3a6b-a4e9-5dc2-893c-6fe1e90742a7 | date | Date Completed:
3684fe4c-c861-4f34-9906-9e52e66134f1 | signoff | AUTHORITY HOLDPOINT
49a75033-999e-4f93-af6e-a8e18e483d62 | checkpoint | 3.2 - Proof Roll
670811b4-f434-5dbe-9bc4-b7d4e24138f2 | note | Frequency - Each Lot
a17c73c4-9ac1-529d-a8b7-8eebb2cfff99 | note | Acceptance Criteria - On Completion of Density Testing, Proof Roll in accordance with AS3798 Section 5.5.
3c47ca8e-74f9-5e89-85f2-e1812382548d | note | Reference Documents - Drawing 00201 Note E41, AS3798
d33a5f5d-3975-5375-b845-700ca2ec7f41 | note | Inspection/Test Method - Visual Inspection
02acc72c-5f12-5c9f-b520-37d64d4fda8d | note | Record of conformity - This ITP Signed
891d509a-6479-5cd7-bfe5-ace54e55e434 | note | HP
54eef390-355c-5d25-9d98-0e00082eedeb | note | Responsibility - Project/Site Engineer, Principles Rep
befdcdce-4464-5c94-9ba9-8db4a56e3607 | date | Date Completed:
f9972851-b905-4bb1-9b9f-9765f18a5863 | signoff | AUTHORITY HOLDPOINT
f7ec1272-0cf0-4b1b-be03-32f5522753b8 | checkpoint | Final Inspection
2725b8eb-a651-5e38-b3cf-12e5101ca5cb | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
e537c19a-00f5-5c8c-855f-a835736029e0 | textbox | Print Name:
249c67c4-a538-5bf8-b591-58c1c72d81c9 | textbox | Position:
fb205ee0-06e4-5aa2-a26c-212351c52042 | date | Work Completed On:
aa41c4e2-6b7e-5401-b720-046124c77200 | date | Date:
00c075d2-c71a-4c07-81f9-f57e536ea2c1 | checklist | FH-ZU2-QU-ITP055 - Grooving - Rev 0 | itp | ITP055 - Grooving
076bebae-832d-4866-bb6e-ade38ab6d164 | section | 1 - Trials
66ecfa98-fc87-44fb-8e36-a55662d69a38 | checkpoint | 1.01 - Trial section of grooving in new asphalt surfacing
86b8d0e4-d69b-53fb-b7fe-dd9e437f0598 | note | Frequency - Prior to the commencement of grooving works.
1a86b9d6-c606-58b5-81d2-99c774aabcfa | note | Acceptance Criteria - Construction of a trial section of grooving that complies with the requirements of Sections 2 and 3 of this ITP.
dba470fb-8b74-5c4c-bd78-8f9dca7a4ebb | note | Reference Documents - GHD-DD-SPC-001 7005, HP7005-1
3989691c-f061-5d7c-90d6-7e83d06fc46b | note | Inspection/Test Method - Inspection
9fd89b6b-50b4-513b-9e1d-617378384429 | note | Record of conformity - ITP
c715f920-16d6-5d53-b59f-3dda5af6463e | note | HP
38e2b4ff-d817-55b7-842d-8b61314131c3 | note | Responsibility - Quality Manager
9d10a483-be51-5c42-ab7a-084059545653 | date | Date Completed:
c906909f-b007-42c7-8e1c-47e92ec3ff36 | signoff | AUTHORITY HOLDPOINT
b165a4c6-31ac-4739-a0a8-e0701fd66769 | section | 2 - Grooving
64411348-348d-4e74-b7dc-4e320c054170 | checkpoint | 2.01 - Commencement of grooving in new asphalt surfacing.
9f70cd3f-9b00-5914-b4aa-33dd2ee5b815 | note | Frequency - Prior to the commencement of grooving works.
be36d0b6-a65d-56e3-87d3-07693e95b9df | note | Acceptance Criteria - Grooving of asphalt surfacing commenced no less than 8 weeks after the completion of the construction of the asphalt surfacing.
cfc231ee-f3f5-5045-8957-7bfb3089bff2 | note | Reference Documents - GHD-DD-SPC-001 7004(a)
4840dc9e-5787-5888-b506-71627ccb133b | note | Inspection/Test Method - Inspection
4ad35e93-fa83-5d01-92c3-e7e311739859 | note | Record of conformity - ITP
f1d18dd6-2471-5860-954d-9aea2c148563 | note | IP
83df2148-74c8-51ac-965f-5b9d3e08a8d9 | note | Responsibility - Site Engineer
b6e650ce-e6d2-5a57-9580-4afb2cc5d67c | date | Date Completed:
a94fc757-69a4-48e2-9856-b32dd0cf5598 | checkpoint | 2.02 - Grooving of new asphalt surfacing as per specified dimensions, length, extent and shape.
117a844f-f218-574c-a8f7-202d0d6efe8f | note | Frequency - During grooving works, on at least 15 randomly selected grooves within a lot. Submission of groove lots to be within 48 hours of completion of a lot.
3889bb11-b0a8-5d18-acb1-f1c678c894d0 | note | Acceptance Criteria - Width, depth and spacing of grooves are as indicated on Drawings. Floor of grooves are parallel to the finished surface of the pavement. Square grooves are square with sides perpendicular to the surface of the runway; trapezoidal grooves are a consistent trapezoidal shape and not round or semi-circle. The deviation from specified groove shape is not more than specified in Note 1. Grooves are cut continuously across the width of the pavement and are cut to extend over the length of the pavement, as shown on the Drawings.
f5459c81-3274-52a6-a1ef-f064263e71a8 | note | Reference Documents - GHD-DD-SPC-001 7004(c)(d)(f)(g), Table 7007-1, WP7007-1
3ff2cf28-8c20-5335-8f32-5d26e961fa87 | note | Inspection/Test Method - Inspection; random selection in accordance with AS 1289.1.4.2
4c94784e-22cc-50d4-bff2-b3cc622c5a19 | note | Record of conformity - Conformance report
34622758-9fd6-5c0a-82b6-ae3be348d61f | note | WP
672bdf7f-f433-500d-b29e-2adf95ef2bcf | note | Responsibility - Site Engineer
a2e53b54-f30b-5fe5-94b6-1903be74f5a5 | date | Date Completed:
5c6478b8-dd77-4da9-82a5-39ac786d702f | checkpoint | 2.03 - Grooving of new asphalt surfacing as per specified alignment.
c376a31f-01b7-50ea-b1e2-f7c58c4db1aa | note | Frequency - During grooving works, on at least 15 randomly selected grooves within a lot. Submission of groove lots to be within 48 hours of completion of a lot.
9ef8ebe2-ad1a-5e6b-8d9e-b293eb87356e | note | Acceptance Criteria - Alignment of grooves reset to truly perpendicular to the runway centreline at 150 m intervals along the runway. Grooves are cut in parallel straight lines perpendicular to the runway centreline and comply with the requirements of Note 1. Grooves on rapid exit taxiways are in straight lines and oriented as indicated on Drawings.
10b8a67c-6477-5312-8627-8b7fa3b94838 | note | Reference Documents - GHD-DD-SPC-001 7004(e), Table 7007-1, WP7007-1
65a0d92c-39c5-5165-b9f2-b67c0def13e4 | note | Inspection/Test Method - Inspection; random selection in accordance with AS 1289.1.4.2
8ba036f1-f5a2-53cc-813d-d4a1a50f15e0 | note | Record of conformity - Conformance report
05064637-5ee1-519d-a630-6a9de7419707 | note | WP
079de454-97c8-53ff-b33b-f5278f14cb04 | note | Responsibility - Site Engineer
e8c81952-0fcd-55d7-a451-c317344213f1 | date | Date Completed:
a6efcc00-5c90-47d7-9ba4-723297cdccb6 | checkpoint | 2.04 - Grooving of new asphalt surfacing near inset light fittings.
8e18b868-f8a3-5702-a174-3dd65d067d33 | note | Frequency - During grooving works adjacent to inset light fittings.
b706152b-304e-5a8b-9a80-472adeef9979 | note | Acceptance Criteria - Grooving is stopped to leave a regular (rectangular or square) ungrooved area symmetrically surrounding the light fitting. Grooves are not sawn closer than 150 mm and not more than 900 mm from the edge of any inset light.
c9e658a0-2e3b-5e58-a8f4-54d7f1876cee | note | Reference Documents - GHD-DD-SPC-001 7004(h)
d6c87f96-2889-5717-9567-19386bd9f632 | note | Inspection/Test Method - Inspection
4c8ea35b-23ad-5f95-8642-f044c050a6c1 | note | Record of conformity - ITP
e421f1fc-1d81-593c-afce-693a3f6d4d55 | note | IP
53f0cee0-9130-56d9-89d4-b1448ea56a87 | note | Responsibility - Site Engineer
ee894fc3-4a5c-54a7-a10b-a467236386e9 | date | Date Completed:
17092f96-6026-448a-a415-a265f62b5287 | checkpoint | 2.05 - Grooving of new asphalt surfacing near cable slots.
906a244e-1a17-507c-9f4f-5e4ce4202542 | note | Frequency - During grooving works adjacent to cable slots.
872f76ce-e5d9-504a-8c76-a59d9dfddfa5 | note | Acceptance Criteria - Grooves are not sawn closer than 150 mm and not more than 900 mm from the edge of any cable slots.
ab647318-9763-57f1-8220-6df685434fca | note | Reference Documents - GHD-DD-SPC-001 7004(i)
14ea33da-13a1-5df5-beb2-c46366851be6 | note | Inspection/Test Method - Inspection
a489d3f5-ad75-59bf-8c9b-eb0070d4802d | note | Record of conformity - ITP
06ac2ca0-1c66-5b5b-ae7e-f57368684cb7 | note | IP
612b9029-b1d7-55d6-8d4f-59e6aec202ae | note | Responsibility - Site Engineer
85791ddc-d5a6-586c-aedf-e5651a15852e | date | Date Completed:
23babc0e-8176-48f4-979b-3df376307e1c | checkpoint | 2.06 - Grooving of new asphalt surfacing near cable arrestors.
4edef976-8165-57e8-953c-b375ad9eed98 | note | Frequency - During grooving works adjacent to cable arrestors.
302b9c6d-f0b0-597c-9426-7ce039c0b07d | note | Acceptance Criteria - Grooves are not sawn closer than 3,000 mm each side of a cable arrestor system.
eff4c155-57a5-55f6-a183-66e1a1b94e53 | note | Reference Documents - GHD-DD-SPC-001 7004(j)
7c2beec9-d52d-548e-b028-864201e4feac | note | Inspection/Test Method - Inspection
ba0e4e55-3698-52be-9a2e-8c56072dd2bc | note | Record of conformity - ITP
00f94a7b-96e9-582a-8f9c-63a15a979451 | note | IP
5b97c4dd-9f12-57d9-a46f-0118983fc03f | note | Responsibility - Site Engineer
b3684367-39af-5aab-a80b-323c8337d802 | date | Date Completed:
ad2e2cba-34bc-416a-8f2c-1fe04c392b4a | section | 3 - Slurry Removal
a7774712-d950-4c3a-8676-f68fcfaa3dd2 | checkpoint | 3.01 - Cleaning of grooved surface.
54414647-1b4a-5b93-b05b-f926ad577b39 | note | Frequency - Progressively during grooving and at the completion of grooving works.
d362ba94-d507-569f-bf49-8cb5b346d01a | note | Acceptance Criteria - Slurry produced by grooving equipment is flushed from grooves as it is produced and removed by suction into a mobile container. Residual slurry is removed to produce a clean pavement free from all material arising from the cutting of grooves.
bb2db637-0118-572d-9609-c5375a03d006 | note | Reference Documents - GHD-DD-SPC-001 7006
48e011a4-3c62-5178-a5d9-abb8e1ee4aac | note | Inspection/Test Method - Inspection
22e9b142-ba39-54ce-a2e8-df74ea15c8d0 | note | Record of conformity - ITP
5790384b-33ca-5ca2-bff1-e8e11b213668 | note | IP
8f0b30d4-3068-512a-9fdd-4c5fb15c18b2 | note | Responsibility - Site Engineer
710d756d-f19e-5408-ad21-984f72862a6a | date | Date Completed:
e6393ae7-9de3-4454-9f32-aef7df6d6ee0 | checkpoint | 3.02 - Notification of completion of cleaning of pavement surface.
08c6da3a-b338-51c5-8b0c-952b13dafbdb | note | Frequency - At the end of each work period in which grooving works have been undertaken.
ec0c0970-2ccf-50c6-babd-23be318272c6 | note | Acceptance Criteria - Contract Administor is notified of completion of cleaning of pavement surface.
7859dde5-ed82-5a63-b894-b9eacdeb1773 | note | Reference Documents - GHD-DD-SPC-001 7006, WP7006-1
daa8bcdb-ced5-5d07-8d28-c0613122deec | note | Inspection/Test Method - Inspection
50ffb2c4-c4bd-5408-acc5-9d683b0e6927 | note | Record of conformity - ITP
532fe7d2-65b5-587e-872d-e5d77540b6af | note | WP
c01beb1c-bfb4-5ffe-a93d-23a70c793604 | note | Responsibility - Site Engineer
1d8a9380-7c8d-5481-84d8-b7aae78d96bd | date | Date Completed:
197eea28-48e4-41d8-a5df-9f32227aa2e6 | checkpoint | Final Inspection
eda6249c-8017-5626-b563-aeeb325387dc | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
1d7cf47b-afe8-5bf4-ad2e-ee0ddde4e940 | textbox | Print Name:
724a0477-03cb-5480-9f5a-27bdb6fb13d6 | textbox | Position:
dcb0dc2b-2863-52e5-9626-c83320db02a4 | date | Work Completed On:
f0a3a46e-543f-5a97-b915-763f8a66bfb9 | date | Date:
8845def4-38cb-503b-93bb-770aeb7e2a71 | checklist | Order Acceptance Certificate |  | Order Acceptance Certificate - Lot:
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
7718e601-4a4a-5c86-9399-63c49d4ed075 | checkpoint | Order Acceptance Certificate -- Details:
12a7c1e5-72a9-5807-befc-b9efc424750a | textbox | Subcontractor (full name of Subcontractor, ABN, Subcontractor's ACN and ABN)
5af93389-f25c-5d80-b77f-39a4818315e4 | textbox | Order No.:
4133d23c-5515-5362-b530-be47a6518f52 | textbox | Delivery Site/Location:
cd8c425f-9f53-5c2d-ad08-4b2c599e8049 | date | Date on which materials delivered:
c0097141-a841-55bf-8ae3-c53f2873beca | dropdown | Inspecting Engineer: | Abdallah Saidan, Abdul Saad, Alex Soo, Angela Julianto, Brad Carroll, Chris Cappelleri, Cristin Swar, Fadi Hanna, Faiyaaz Ahmed, Giuliano Follacchio, Jamal Khodr, Jasman Singh, Jihad Barbar, John Kakoliris, Jonathon Rock, Jordan Nicolaou, Marianne Sales, Michael Natalizio, Owen Tieu, Patrick Croagh, Tirrell Slaney
45e3f212-8d1c-543b-9a35-0358266c0e47 | textbox | Inspecting Engineer (if not included above)
4966c6cb-3e3d-5752-bb82-0a115d0656d6 | textbox | Subcontractor's delivery personnel (full name)
6b811dd6-6dc3-548c-b57f-0364a98d27a7 | textbox | Delivery vehicle registration number
62c93c34-0246-563a-b324-2ca2b6e4a8ae | checkpoint | The Subcontractor has checked all Materials included in this delivery and is satisfied that all of the Materials comply with the Subcontract.
8c958ecf-1640-539b-b8e3-d3a57349e5a2 | section | Packaging Inspection
5e80b1cf-5f85-5eae-9226-9c6c53dea384 | checkpoint | Inspection Result ID:
5af37914-7f8a-57ac-b8eb-af8f32f81e30 | button | Special Storage/ Handling Requirements? | Yes, No, N/A
d472a224-2992-568f-9627-b4deeee5931a | textbox | If yes, provide details
5c6b6948-bc83-52c5-9b75-ea98613e1ad4 | note | The following is for completion by Fulton Hogan
6d4bcd5e-6127-574d-a9b9-fb512def9611 | button | Confirmation of receipt of Units delivered. [Subcontractor does not complete. Contractor will initial on receipt.] | Yes, No, N/A
70fd54d0-3acd-5341-b686-5705578dd7c0 | button | QA/Compliance Docs Delivered? | Yes, No, N/A
49ff98bb-f0fa-5156-a58c-e12bcb2510f0 | button | Defective? | Yes, No, N/A
200f6892-fac1-5fdf-b1aa-f27f539f27ab | checkpoint | 1)
14fbd31c-3ed8-50d5-8bdf-b1544e387fea | textbox | Item ID:
2994839b-a721-5165-ac58-c135d99c2709 | textbox | Item description:
65816c8d-705e-5e01-a0e3-31d06a01fe72 | textbox | Units ordered:
2a8a3e58-1dff-56b1-9a34-9c5d3d05d8c9 | textbox | Units delivered:
d727198e-a11c-508d-b0e2-c3d4c1563815 | textbox | Number Accepted
d0755175-ee3f-501a-a373-48d612f07c5b | textbox | Number Rejected
111ddf99-8375-57e2-92b4-62eb39931b6b | note | Inspection Result ID (select below)
eb186f37-07fd-507f-a68b-4eba6d0d570c | tickbox | OK = Meets all criteria
d18323b2-c7d1-5115-a09c-544c7bdfcd3b | tickbox | QI = Quantity incorrect
0d812c22-f0a3-5d0c-9055-d001df447d3f | tickbox | IN = Item incomplete
bd28b41a-6ae4-5899-b676-258553c470b5 | tickbox | MI = Make or type incorrect
aab47e5e-1a43-5442-b958-df4ebb9be7ee | tickbox | TD = Damaged in transit
98d6ddf2-47e8-59a0-9158-0dbdfaa17086 | tickbox | NI = Not properly Identified
d6144275-4bd2-5780-83d0-a0e828e846d1 | tickbox | CD = Compliance docs not provided
200db96a-bdae-5e06-9fba-d8ee29460a36 | checkpoint | 2)
bcb8a80c-62a2-5601-8016-580bbc87704f | textbox | Item ID:
1b8dc746-448e-5455-895a-f55bcd8ebb83 | textbox | Item description:
4c97d56b-02c8-5d15-b1b2-77fb99e0d5ec | textbox | Units ordered:
a7fc8070-6e1b-5dba-bf70-313ca170f523 | textbox | Units delivered:
932ae001-ff39-554d-9551-288cb472e167 | textbox | Number Accepted
415e27e9-065d-5622-b00d-a2681ed2da3d | textbox | Number Rejected
f9f13e5f-856f-534d-a759-79009afd7c7c | note | Inspection Result ID (select below)
29b66bee-d998-50b8-bc4b-51bcc0a4b891 | tickbox | OK = Meets all criteria
4df1d900-41f1-5892-9255-6196f48f45b2 | tickbox | QI = Quantity incorrect
b6316236-2594-55a7-8f43-05628dd24ba8 | tickbox | IN = Item incomplete
0260be27-5d9c-5126-9cd6-2bdb101cfedc | tickbox | MI = Make or type incorrect
99b072dd-aa0b-5134-90bb-cb8ce550164e | tickbox | TD = Damaged in transit
53310f68-ca19-5463-a84e-fbb01226322e | tickbox | NI = Not properly Identified
3d1740fb-d64a-5717-8671-52a78e10fb91 | tickbox | CD = Compliance docs not provided
b5f9cc86-4177-54ea-a1ac-7dad72d6be28 | checkpoint | 3)
7d0b2e97-16e6-5457-98d3-76cd64b0f7e4 | textbox | Item ID:
eaca7272-0657-5d88-ba36-14ecc6e4f300 | textbox | Item description:
bfcf3a2f-2700-522c-82fe-c8b1bfd41064 | textbox | Units ordered:
c85741be-5e1d-508b-9596-988eabaa0f2a | textbox | Units delivered:
edd2e7e2-63ef-5942-ac19-b879a6054401 | textbox | Number Accepted
ba9cf8c6-51f0-5fea-a9af-e267a9c2954d | textbox | Number Rejected
1a5019de-b026-5684-bb61-9054252a1b79 | note | Inspection Result ID (select below)
18eb4d14-d9f2-5767-bd57-95ef30adb9af | tickbox | OK = Meets all criteria
a5db3abf-a7d9-5d87-ba79-115540460781 | tickbox | QI = Quantity incorrect
e3505139-cebb-5419-a051-7ef94dd7113c | tickbox | IN = Item incomplete
b2ff2970-0289-502b-bad3-211bbc4fd855 | tickbox | MI = Make or type incorrect
592bbd0c-4513-567e-b6bd-330459126e7d | tickbox | TD = Damaged in transit
9f04d024-b4de-5d63-9de0-e34bb90ecf2e | tickbox | NI = Not properly Identified
4278a3d3-eb65-553f-b192-ad44788bbdf1 | tickbox | CD = Compliance docs not provided
06fc7414-b417-521a-b0cf-51877a6d64be | checkpoint | 4)
02030a4a-e9f9-5de5-b134-e3c68ff5647b | textbox | Item ID:
0adef97f-9057-5939-ac0e-36f39d8591bf | textbox | Item description:
f1deff30-74cc-527b-97ac-ca8758e545bb | textbox | Units ordered:
bad31414-c790-55f1-94df-e9b3e7db8d0c | textbox | Units delivered:
6126b4ab-c1a1-5e47-803d-d37b5714cefb | textbox | Number Accepted
2608bb75-8749-5221-b1ae-e7e03b904cf1 | textbox | Number Rejected
cb797cad-1ab2-5fa4-93b8-5639b0145c17 | note | Inspection Result ID (select below)
485a4c56-ea86-5699-a275-6085cba522d1 | tickbox | OK = Meets all criteria
3657c271-31a4-5827-b9be-83ccb17cfea9 | tickbox | QI = Quantity incorrect
aea79501-99ea-5d7c-a344-23456988306a | tickbox | IN = Item incomplete
375a4393-fb27-5712-85d2-a3d39c6bea58 | tickbox | MI = Make or type incorrect
014225a6-fd62-55e4-a7fc-248b025fa0b5 | tickbox | TD = Damaged in transit
9e770ae4-cb01-5510-8737-fa33711c1bfb | tickbox | NI = Not properly Identified
dabc3c4d-271a-52e4-848a-b6f31b0f5dd6 | tickbox | CD = Compliance docs not provided
fe0c543b-2411-5c6d-86bf-c4f032ef97ed | checkpoint | 5)
ee3e5da8-de72-531e-95b5-9d20e807142c | textbox | Item ID:
8e7052af-a398-5e46-92b7-a2e49a4d9b3d | textbox | Item description:
89b51c1b-da9e-5489-8e93-95759094bd01 | textbox | Units ordered:
839dbb10-e1dd-5507-befe-477e8984beed | textbox | Units delivered:
b255ed66-3db3-518b-9402-6788fc4751b1 | textbox | Number Accepted
9ca98e0a-965c-5b4a-931b-555565640b79 | textbox | Number Rejected
2b9365df-3a69-5e77-9670-c4c1643e71dd | note | Inspection Result ID (select below)
83b4e2c3-6d8a-5719-a07a-3f29a40bd4c0 | tickbox | OK = Meets all criteria
0f572fc2-39e3-5ccd-a238-48068a967c0f | tickbox | QI = Quantity incorrect
1b0d93e3-fbf6-56d6-9ebd-234da000b0a4 | tickbox | IN = Item incomplete
9d4ab8e8-64d7-51e9-bceb-3aa3845370a1 | tickbox | MI = Make or type incorrect
b81b70ef-1498-5b95-afa1-955a18d41376 | tickbox | TD = Damaged in transit
880ad6fd-7a04-5537-8145-e9ec30b0af67 | tickbox | NI = Not properly Identified
5947b083-7280-51a0-bbba-ef46a1b46c3d | tickbox | CD = Compliance docs not provided
f3e7f541-2469-54e2-b778-ef8fe4bcac9a | checkpoint | 6)
f5213d94-b80a-58ad-9e02-f4c55d406424 | textbox | Item ID:
edd20faa-cb86-5256-bc0a-01f72d478ff4 | textbox | Item description:
777534c3-f873-5c72-b8bc-84a8652d31c5 | textbox | Units ordered:
c70ed69f-7b0f-51a7-9ebc-8e8780ed4eba | textbox | Units delivered:
bf72f1f5-fd8a-5f81-bfa7-30ec85b2b7b4 | textbox | Number Accepted
c066d4e0-a8b8-55e3-80b1-95163a7f00d9 | textbox | Number Rejected
f4a433b9-bedb-535f-afb2-38b96236e638 | note | Inspection Result ID (select below)
78f4fb22-5dd4-53c8-ae6f-45f0e5bbec26 | tickbox | OK = Meets all criteria
76a89976-b7bb-58ec-9dd9-5273687c8bb7 | tickbox | QI = Quantity incorrect
e3057735-dba9-579a-883b-f54c31d4dda4 | tickbox | IN = Item incomplete
b1e39859-58b0-57c7-a46f-b8dcece44ae6 | tickbox | MI = Make or type incorrect
317c7343-d44b-5e6f-ac4d-14777d996856 | tickbox | TD = Damaged in transit
22d1c960-40b1-5717-a111-2733e94a093b | tickbox | NI = Not properly Identified
5627b1ca-a2cb-569b-b8d7-4b4fdf5390e5 | tickbox | CD = Compliance docs not provided
50256c4d-11e5-54f7-9e72-dfc39a625998 | checkpoint | 7)
24420331-8897-5df8-8e20-28850ce6820b | textbox | Item ID:
050f2298-60e1-597c-ba41-19f372d6f9ea | textbox | Item description:
4aed13e8-5b70-5ac5-b063-27682e4b1e7d | textbox | Units ordered:
a8455a7c-3e34-5fe2-9484-44265dbc6270 | textbox | Units delivered:
c96e5370-3e8a-546d-b3ba-30efbbacacd3 | textbox | Number Accepted
2ef35f51-cea1-59a0-a464-7b59d63adaef | textbox | Number Rejected
8d6998f0-ae2a-550b-9a35-ce9a90bcd907 | note | Inspection Result ID (select below)
38731218-084d-5300-8ed7-2fa488172541 | tickbox | OK = Meets all criteria
f5fab120-e143-55d9-98b3-47b141326437 | tickbox | QI = Quantity incorrect
1bbc596b-6778-5be7-be40-a3679ec04117 | tickbox | IN = Item incomplete
59d81aa0-cf54-5156-96b1-253b1feaf6aa | tickbox | MI = Make or type incorrect
a2040892-0694-53d0-bcd2-55ecc0661f89 | tickbox | TD = Damaged in transit
5ff1772d-def4-5790-807b-814328b8894d | tickbox | NI = Not properly Identified
4aee0408-6d70-5ad6-a317-4bbc96d33a65 | tickbox | CD = Compliance docs not provided
f5eb9f57-0331-5249-85d0-33af4c854139 | checkpoint | 8)
0a389b74-9f90-525d-8b0c-2552b759cf12 | textbox | Item ID:
da5d972b-2633-569a-ac0d-39ab45185063 | textbox | Item description:
5225212b-ed5d-5287-97df-f33b1afb8849 | textbox | Units ordered:
93ccb08d-1a0e-5bbd-b3fe-401d00e9b93f | textbox | Units delivered:
efe49955-ccdf-5024-a811-8666f33136b1 | textbox | Number Accepted
ded9f1eb-3668-56ca-b5a9-a52244bb2ade | textbox | Number Rejected
ae08ee64-0f14-5936-97e7-b66bc37e6886 | note | Inspection Result ID (select below)
369bd422-e8d4-5e79-93e2-fec34f9dcbe0 | tickbox | OK = Meets all criteria
36c62b89-9687-5b3e-8bae-397801b4f57c | tickbox | QI = Quantity incorrect
db8728c7-e9ea-5d6b-b0e6-ebd0d5eb6d8d | tickbox | IN = Item incomplete
ed22784c-94c4-5299-b9ac-d91e57c69287 | tickbox | MI = Make or type incorrect
5a8fff9f-6801-5421-98eb-2215df843cbe | tickbox | TD = Damaged in transit
676893f2-c88c-51b8-80f3-69b2dc890cfc | tickbox | NI = Not properly Identified
67c8e16c-c8f8-588a-9ee8-31eb20893fad | tickbox | CD = Compliance docs not provided
9718bee2-a89a-568e-81da-fd28f3920a98 | checkpoint | 9)
65eae4e7-939c-5ce5-9db2-eece6a4a649f | textbox | Item ID:
974acc2a-4b50-5eee-9e15-9ba65a782a7c | textbox | Item description:
21e915b9-fedf-5b73-a47d-be5243581d53 | textbox | Units ordered:
0cced952-00de-55ce-8584-6be8030a25ee | textbox | Units delivered:
f3a96a9e-67cf-55a6-8f0d-bf09c6d85ef8 | textbox | Number Accepted
d3a1489b-5278-579a-9a15-15c1cea2f994 | textbox | Number Rejected
f383bbb4-9354-50cb-b763-6b692204c157 | note | Inspection Result ID (select below)
05656c8c-a056-5d75-971d-973831c209d5 | tickbox | OK = Meets all criteria
aee89344-f771-5ce8-8c50-075d95882fce | tickbox | QI = Quantity incorrect
377a752a-da2e-5870-83e8-7d570544216a | tickbox | IN = Item incomplete
8158ea5b-dcb3-5a4a-970a-029eebc1a66c | tickbox | MI = Make or type incorrect
9fe0fffb-3708-50b7-a9ce-0792b5913c20 | tickbox | TD = Damaged in transit
f81eae3f-8b92-5308-9e64-456dbeb343cb | tickbox | NI = Not properly Identified
6857182b-1b54-522a-a5d4-8dbdcedde131 | tickbox | CD = Compliance docs not provided
d32e9f98-55c9-5057-9b0a-904c60fdc129 | checkpoint | 10)
f31045c7-1532-5996-9539-a059c44e9143 | textbox | Item ID:
bf14bf6a-0c22-5298-acce-1b1e76efa58b | textbox | Item description:
275633ff-23c0-509e-994c-a32a2affc4d8 | textbox | Units ordered:
f4f913e7-857f-587d-853a-582fc5c6cea6 | textbox | Units delivered:
0ad7f80a-763c-56c2-a5d0-fccc379240e3 | textbox | Number Accepted
728face4-b70a-51ba-9372-5306f854b124 | textbox | Number Rejected
09e54c31-f69e-559c-9836-3041d059feb5 | note | Inspection Result ID (select below)
f83dc770-5925-5f78-8f97-99ada5109ef4 | tickbox | OK = Meets all criteria
24966949-b70a-5c70-8b17-e0f2631cc6df | tickbox | QI = Quantity incorrect
4f31970c-fe9c-5c41-b197-736cf33848ba | tickbox | IN = Item incomplete
26817fea-ad8e-5d03-ab40-a2308c1e1b90 | tickbox | MI = Make or type incorrect
aa968b3c-f799-56e7-b410-ef29880b0530 | tickbox | TD = Damaged in transit
a7e94359-1c7f-51d6-b0c8-688f94b72d28 | tickbox | NI = Not properly Identified
945ea484-67de-5837-a72f-5e3f7a05d714 | tickbox | CD = Compliance docs not provided
3ceadcd6-d779-5c97-8426-53dd865a89c4 | section | Sign Off
2511984d-74dc-51b8-9984-3f4226eae93c | checkpoint | Accepted by Fulton Hogan
afd289e2-65eb-5256-927e-e1c2ccbc0bb3 | signoff | Sign Off
be433d2f-bac8-4938-8bdf-f9a8a323cda4 | checklist | Partial Backfill Inspection and Testing Hold Point Form |  | Partial Backfill Inspection and Testing Hold Point Form - Lot:
f2be53ac-ae60-4017-aae4-4896502908dd | section | Details
deb51cf5-3a42-4588-ac37-351060ec0720 | checkpoint | Partial Backfill Inspection and Testing Hold Point Form -- Details:
b6a411e7-be19-59a3-a961-622168ee0b96 | note | Project / Site: Taxiway Zulu 2.0 - ALER 3 Building (Melbourne Airport)
aa78f90f-dda1-5e53-aef9-77a3a3c526d9 | number | Inspection Number:
37eaebd9-c35a-5757-9384-062df89bf365 | textbox | ITP and Lot:
8c7e39ae-1eda-585c-979d-1afa38f7e124 | dropdown | HP/WP/TP: | HP,TP,WP
e284bfa9-b52a-5260-b70b-dc874dab4cad | dropdown | Inspection Type: | Pre-Backfill,Testing,Pre-Pour,Other
6d51ec70-4446-5f37-94b2-9666975ea6d8 | dropdown | Service Type: | Electrical/Comms,Sanitary (Sewer),Stormwater,Other
0c2d4920-91b1-5fb5-9718-415b16d93072 | date | Date & Time:
be60bf0e-8ce9-5c0b-b5bd-27947beb21a9 | textbox | Engineer Responsible:
b1b11675-41b5-47b0-bc0a-9bffcb27be4a | section | Description
3072ceac-2a56-4473-b917-2ce322c3d06b | checkpoint | Description
6978b95c-4228-5c91-a4b1-747ab37ab222 | textbox | Description:
bc11281f-f5d4-4eac-bff7-4283eabd0e20 | section | Sign Offs
2e413bd3-9347-4f45-b489-9a2dfc431714 | checkpoint | BECA – Signature
b594039f-438c-4e9a-9d96-41d6a1b9cf4b | signoff | Signature
5e7448e0-fdce-43e9-8fd2-0d66232c81e7 | checkpoint | Fulton Hogan – Signature
32f4ad40-ab5e-4eed-8acb-25b52005e027 | signoff | Signature
74639306-11b5-47b8-ba55-a20117fdac56 | checkpoint | Building Engineering – Signature
988284cb-9100-4ade-b5d7-92606b16dcc4 | signoff | Signature
67acbde0-1dfd-558f-bb6b-eb900bac2f6c | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0009 - Unbound Pavements (FCR & RCC) - Rev 1 (3.5 Signed off) | itp | ITP009 - Unbound Pavements (FCR & RCC)
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
22b60133-d07e-5778-afbb-3104cb451e98 | note | Frequency - Prior to commencing works
90628709-661f-5c1d-808d-3f9633505536 | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex
bc77cecb-25db-54e2-a46f-f50316ce64bd | note | Reference Documents - Aconex
248e7c02-a029-5336-9878-3422c829cf56 | note | Inspection/Test Method - Visual inspecti on
505c13d3-3958-55d4-b28a-dbe56fcb6509 | note | Record of conformity - This signed ITP
d9b9a31e-4fc1-55c9-8cf1-e24191b8f35b | note | HP*
577c368a-5703-5a58-b59c-18e92dbc9be8 | note | Responsibility - Project/Site Engineer
0ca55223-b839-58b1-9ea2-63b876b41d8e | date | Date Completed:
0ee48894-54ec-5653-949e-3aecb94d8a6f | checkpoint | 1.2 - Implementation of all measures and controls, weather, and material properties.
d49a7852-f9a9-5121-afd2-663081afa613 | note | Frequency - Prior to commencing works
1e3e4950-6df5-54d8-b002-d4b18ac8c1d9 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
46aa07a5-24fd-5c8d-8bf3-189213104141 | note | ○ Check weather prior to starting any works.
4274f253-54a3-50bd-9ec8-7b1601fe3d02 | note | ○ FCR material used for the works in accordance to VicRoads Class 2 Crushed Rock.
9351f45c-6020-5acc-acdf-0786a7e52f32 | note | ○ RCC material to be used for the Works in accordance with VicRoads Class 3 Crushed Rock.
67de20a2-0256-57b6-850f-aadb800e0d07 | note | ○ Checking underlying layer ITP’s (subgrade ITP008 and select fill ITP004 has been completed)
337e8923-b57f-5282-856b-d3a6b8d18b41 | note | Reference Documents - PSP, EMP, TMP, WP SWMS, Spec Cl 4.19, Spec cl. 4.1, VicRoads Technical Note 107 Spec cl. 4.6
b918f1ef-0da1-5bc1-8bb8-6c02335de461 | note | Inspection/Test Method - Visual inspection
6f531f46-a05a-5c16-b04e-195d1c3f4a93 | note | Record of conformity - This signed ITP
3b7b3517-c997-5002-97c8-f1aa5f1e7cae | note | HP*
2de72f79-4994-57b6-a35f-9b3e18858774 | note | Responsibility - Project/Site Engineer, Foreman
baa8b9fa-f889-5d30-8dea-a71cc722d564 | date | Date Completed:
b55c3da7-c29e-50dc-b5c6-6c3d6d4c85da | checkpoint | 1.3 - Material Report - Fine Crushed Rock (FCR) Material & Recycle Crushed Concrete (RCC)
08f8e815-db8e-5c04-a20e-779ea9c698a3 | note | Frequency - 7 Days - Prior to works
f23fc5f1-f6fb-5435-ad79-c5ecdcd035c6 | note | Acceptance Criteria - Material Report to be submitted 7 days prior to works to include;
1344dbf9-3674-54ba-b047-2f9a512d67de | note | ○ Source and Quarry location
dc8222db-ef8f-5c16-b274-2905dc7a31d3 | note | ○ Quarry material is sourced from.
a8449f49-f55e-5365-8100-695b2068f934 | note | ○ Material rock type and petrographic description
8b784087-184c-59ef-b6b6-040c79a2a485 | note | ○ Historical test results
836aacce-c6f4-5341-b85b-04b293e861dc | note | ○ Method of processing and transportation
52202e1b-799b-57e1-bfb2-b5a8c390d48f | note | ○ Material summary of the results of recent test on samples of the material from the source
e2e34f1e-e0b2-5faa-bb77-6746fc484680 | note | Reference Documents - Spec cl 4.20.1
c4580524-9128-5583-a7bf-4fa86d4a90ec | note | Inspection/Test Method - Verify
6f6417f1-69f8-5ad5-984c-fd198378675f | note | Record of conformity - This ITP signed
c8da58f1-5852-54c6-b606-35386ce293d9 | note | HP
27f7bd55-d87c-5dde-b69a-8a690d4a1c5c | note | Responsibility - Project/Site Engineer, Principles Rep
98351715-983d-55b6-b5e4-29818398c2fb | date | Date Completed:
f90cc78c-5577-584a-bf6f-2baea0a79d8a | note | Principal’s Representative - Aconex Ref: Holcim RCC Class 3 - DCWC Mgt-GCOR-009582
6ed4e75b-7d7c-59d4-860f-84f44b2920d0 | note | ○ Holcim FRC Class 2 - DCWC Mgt-GCOR-009581
f1140fed-3d65-5000-a675-33f0cf450936 | note | ○ Stirling Class 3 - DCWC Mgt-GCOR-009565
8b2d5395-ceb8-53cb-8eb1-c7add6510501 | signoff | AUTHORITY HOLDPOINT
ec34d278-5586-5c2a-99c8-01e2abad83a0 | checkpoint | 1.4 - Reference Samples
525ba691-af22-5b05-b06f-d97f2febed12 | note | Frequency - 5 Days prior to works
d6fbd216-8984-5446-82cf-f06bf7078519 | note | Acceptance Criteria - Reference samples to be submitted 5 days prior to works commencing. Two bags to be taken each weighing 25kg. One bag submitted to Client, one retained by Contractor
393a62fb-dc1a-51af-820d-43d92dcf2ed5 | note | Reference Documents - Spec cl. 4.20.2
81cb4669-886b-5347-b152-1895c2aef53c | note | Inspection/Test Method - Verify
3df23d20-62cf-5417-b4eb-60cb6864ab05 | note | Record of conformity - This ITP signed
afaad2f4-dbb5-5fd8-87e6-401b5bf4febd | note | HP
54753b28-df32-5121-a510-4e413fb619cc | note | Responsibility - Project/Site Engineer, Principles Rep
ee76c1dc-3531-5a2f-8c1f-475d8f250b39 | date | Date Completed:
9ddd2561-c351-5c44-858a-2e4143344a3b | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000825
d95e7d5e-6bf0-5924-b391-1cfea39c7d6c | signoff | AUTHORITY HOLDPOINT
86350ec1-aec3-5802-aaf3-a14a45b6d2ff | checkpoint | 1.5 - Trial Section
65684dbf-f369-509e-a5e8-b314c3fd8819 | note | Frequency - Prior to works
bafdae1c-25bf-5ae2-9cd0-6608d8ef0a98 | note | Acceptance Criteria - Trial section to be completed with Principles Representative approving the use of the spreading machine.
6c6faa28-2c6a-59b8-bc47-3393a4e05f95 | note | Reference Documents - Spec cl. 4.7
af7d6c18-3dcc-50bf-b3f8-53ce25ab318e | note | Inspection/Test Method - Verify
17a066a2-c53c-51e9-a713-f8604f6dba5c | note | Record of conformity - This ITP signed
eeb60278-237d-56da-890e-daecf0bb1cf4 | note | HP
b8253941-a061-5b59-a6f1-8d269d6fe801 | note | Responsibility - Project/Site Engineer, Principles Rep
a035e09f-3c92-5f13-973b-02f96ca5b1ac | date | Date Completed:
50b5aab5-7a04-53ea-a4dd-31d851a2dce3 | signoff | AUTHORITY HOLDPOINT
690716ed-b540-5814-804e-da1a18d341a5 | checkpoint | 1.6 - Compaction Equipment
b945be75-e6e9-57a1-8123-6e8633aab849 | note | Frequency - Prior to works
e74b505a-9f5c-54a0-aeea-6de10bb335eb | note | Acceptance Criteria - Pneumatic tyred rollers having a weight of 27t (min roller weight can be 7t spread across 7 wheels). Tyre inflation pressure to be checked. A 15t to 20t smooth drum roller to be used.
2801421f-e441-58d5-bb6a-16a4d3e6997a | note | Reference Documents - Spec Cl 2.4.3 Item 84 Tender Clarifications
7714caf1-b8f8-5140-a270-f11a742d03c8 | note | Inspection/Test Method - Verify
c68e6fd7-3cf1-58cb-b9e5-ef98680eb80c | note | Record of conformity - This ITP signed
1ca6e76d-4a10-59f8-9af4-a8cfd70ad21c | note | WP
de947921-e38e-5dbb-98de-20d29f6f2cf3 | note | Responsibility - Project/Site Engineer, Principles Rep
780ed8c5-c16d-5d7d-a120-b2874bf1d159 | date | Date Completed:
f1bd1704-9d65-5504-9073-a58e0fb450e7 | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000893
1d9506f5-f6c7-5206-bffc-81f4f4f90212 | signoff | AUTHORITY HOLDPOINT
282695af-0cd0-5fe3-8b64-3dcbc3207e5e | checkpoint | 1.7 - Testing Determinations
435afed8-b133-50ef-9159-3038e4e9ce4f | note | Frequency - Prior to works
36ad8297-35ac-522d-abb9-b2825c174034 | note | Acceptance Criteria - 1. Basecourse and Sub-Basecourse thickness test points selected randomly.
23450c8f-eb32-5958-a1f6-4c1070f0aa49 | note | 2. Field dry density test locations selected in accordance with AS1289.1.4.1.
b46d1e09-9f04-5e91-94c9-e815bb795a73 | note | Reference Documents - Cl 4.21.1
523cd7eb-bebb-5653-b8f3-ced01627075f | note | Inspection/Test Method - Verify
a6984f74-007e-5d32-81f4-43d2d0ae7149 | note | Record of conformity - This ITP signed
9d271944-3ad5-5014-8b38-573d1b5c08db | note | HP
c4dc7eef-31c3-51c3-8336-cd5de23a3ab5 | note | Responsibility - Project/Site Engineer, Principles Rep
4e0c42ad-439e-5855-9604-6d597d69fa7b | date | Date Completed:
466d62da-b64c-5642-9815-ed935f373305 | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000890
83a1d299-f349-508e-bab0-117c246c15aa | signoff | AUTHORITY HOLDPOINT
31f3573f-3cd4-53a2-bab5-d81150ad14d3 | section | 2.0 - Placement of Sub-basecourse and Basecourse
520af3e6-6af9-53b6-9cab-e0a37d5ddeeb | checkpoint | 2.1 - Layer Placement Parameters
aaa3edf8-61eb-55f2-97a1-d0fb08386030 | note | Frequency - Every Lot
16c77b6b-81f0-5b20-ad8d-8506d7ec2d02 | note | Acceptance Criteria - Summary of Parameters for each Lot;
3f87eaec-bfd5-5113-a5dd-c989fed0fec5 | note | ○ A lot is defined as one layer placed in a single days production of uniform material
ba7c17ca-eae9-5ba4-a3ff-214dac3491bc | note | ○ Max Layer is 200mm
322cb297-e6e8-5565-b3fe-48d519767cce | note | ○ Min Layer is 75mm
ce182ba1-c8fb-5c79-9cb4-9e7811cce7b1 | note | ○ Final Surface Level +0mm, -10mm (excluding intermediate layers)
3fcf686c-043f-5d65-9648-ea4b780b560f | note | ○ Shape: every 10m intervals, <7mm deviation over 3.5m straight edge (excluding intermediate layers)
2a7aa885-9c4f-5381-8ece-bb1b9ccba295 | note | ○ Material to be batched within 1% of OMC
2585bc1f-f9ba-51cb-839f-4f8d9b4863dc | note | Reference Documents - Spec Cl4.8, cl 4.21.2, cl 4.13
cced5364-2910-5d18-aa42-577b9981563e | note | Inspection/Test Method - Verify
8100ba46-80fe-5560-aca3-286dd0f42292 | note | Record of conformity - This ITP signed
be2c8188-b893-5606-951c-1d3052e63cd4 | note | IP
6d1c799a-1c5e-5479-95f5-52693cfb267f | note | Responsibility - Project/Site Engineer
c035320a-65e6-5da3-8edd-85233f228189 | date | Date Completed:
ab12b78d-7983-5acd-aa07-c177c46370e6 | checkpoint | 2.2 - Placement Checks
35f1d8ab-6103-59c1-8b59-7dbfdfd5a318 | note | Frequency - Every Lot
d330c613-67e4-5ca5-a41d-034019e87353 | note | Acceptance Criteria - During placement of the material check;
a0897ee6-0317-5245-b2d4-b7319354e90a | note | ○ Deliveries do not disturb underlying layer
c52be776-0b87-5bb4-9639-97923473720f | note | ○ Spreading starts from crown / high side where practical.
6558ad17-534d-5102-861d-33bdf6acdef4 | note | ○ Material does not get contaminated during placement / delivery
da1053c0-3a2a-5ac3-86fd-b3ecc6fd4402 | note | ○ Watercart is present to condition material as required
23130571-9585-5f82-a1bd-667592304329 | note | ○ Edges are cut / removed if dry of not compacted with abutting lots
25bb25f1-45b3-507e-b660-1bdfb628c3bb | note | Reference Documents - Spec Cl 4.8
35f5add3-e162-53d8-9bcf-6f098b9c662c | note | Inspection/Test Method - Verify
b7644ee8-0ce7-5f78-90af-aafeca592397 | note | Record of conformity - This ITP signed
5a905e00-c1e4-512f-9a17-ade2ccd58b44 | note | IP
19652dec-189a-5f21-8896-0766c8cb7a88 | note | Responsibility - Project/Site Engineer
2a0baffe-e984-564d-9c01-dab08964c6d6 | date | Date Completed:
03b653d0-0f2f-5bbe-ba99-60916a24386a | checkpoint | 2.3 - Compaction Check
58e6a7da-0a23-579e-adb3-07ffa5af4807 | note | Frequency - Every Lot
09efdcc0-9ad5-589b-9f7a-29a04ff56202 | note | Acceptance Criteria - During Compaction check;
112f68b3-7620-566d-bcbd-453cf4539fcb | note | ○ Heavy smooth drum roller of 15t to 20t is used for initial compaction
156bec7b-d118-5098-80a4-9f9811800889 | note | ○ Pneumatic roller of 27t will compact material for final consolidation.
63744c10-259a-59ff-aa84-ed5a2ec11330 | note | ○ A heavy smooth drum roller (in static mode) may also be used for final consolidation
1dcab749-3f6d-5dc0-8b70-8e6ccc60521a | note | ○ Watercart Present onsite for conditioning
55bdb2c8-4342-5857-baae-a10bdc7ecac0 | note | ○ Materials are trimmed to required shape and level
d22c4f0e-7900-552c-8a73-ef0db6e4ae0e | note | Reference Documents - Cl 4.10
1993e4bb-389f-5674-aac7-b01ba95c1fb1 | note | Inspection/Test Method - Verify
669b9d6b-f3ad-50de-bde3-67155680d007 | note | Record of conformity - This ITP signed
14eaa2db-1f06-5432-8e0c-27042f49ab02 | note | IP
6cd03551-ea7e-545c-bfad-d40f0419bc20 | note | Responsibility - Project/Site Engineer
045eb3cb-4193-5ec9-b4b2-f7ded14ec478 | date | Date Completed:
56c1eb5a-a610-51e7-86f1-f05ba8e1b5bd | checkpoint | 2.4 - Services & Culverts
cad1544e-6b90-53e9-b346-5cdaec13789b | note | Frequency - Every Lot
6ade1825-13f6-521f-80f3-e6df0e156981 | note | Acceptance Criteria - Check if any culverts or services are with the influence zone for compaction.
f01b9dd3-612c-5a17-a57d-010ef1513183 | note | ○ A general rule, FH will seek advice from the Principles Representative if any culverts, duct banks or RCP pipe are identified closer than 1m from pavement layer surface. If identified, Fulton Hogan will maintain a 1m exclusion zone either side from centre of service for vibrating compaction activities. Hand held DPU’s/whacker plate to be used in lieu of rollers in restricted areas.
67c452e0-d6b9-5f8e-a3da-b3d574687983 | note | Reference Documents - CL4.10
fa8211c9-abd1-57da-b54f-de0c6e5dbe35 | note | Inspection/Test Method - Verify
ffa561c5-3a1c-5b2a-8fdc-90801c716515 | note | Record of conformity - This ITP signed
33423efd-62ae-5c89-b304-dd78ede7b634 | note | IP
54f78c92-1f94-54e5-9290-23165c7f8f9b | note | Responsibility - Project/Site Engineer
d6d1b5b8-e9d7-5583-8a85-3068b4699540 | date | Date Completed:
af9dc4f1-7e43-5752-b5a1-15b8f94cf295 | checkpoint | 2.5 - Protection of Layer
b5def97a-8a82-52be-9c54-498ac337f247 | note | Frequency - Every Lot
f5abe81d-8f4d-510d-8885-fa3cc5fca33b | note | Acceptance Criteria - Protect area from undue deterioration by;
f417fc95-2acf-5b5c-8b72-7fc970c8db29 | note | ○ Section off area for at least 12 to 48 hours to allow material to dry back.
59af82c2-ee2b-55ae-9f1a-84ba3d796d2f | note | ○ If unable to do so, keep traffic to a minimum
7b0a10bc-80ce-5720-b786-07441ed72b4e | note | ○ Or ensure any traffic that has to cross pavement layers, do not follow the same driving line.
98124425-bbe9-54b3-9173-c49ea88147ad | note | Reference Documents - Cl4.17
941d9051-473f-561a-bb5b-246c9d4cf08f | note | Inspection/Test Method - Verify
4ca87943-c62f-5a1b-b82a-fc898998e077 | note | Record of conformity - This ITP signed
fbcb7b46-d64b-5e69-8d4c-558089c333e1 | note | IP
86dbe21d-b474-525d-b7cc-73d45852ecfe | note | Responsibility - Project/Site Engineer
c1acb8c3-0d37-5859-88bb-9dc12a60a61b | date | Date Completed:
ed4dca39-7158-53f5-b80c-2934cf975618 | checkpoint | 2.6 - Proof Rolling
44460523-6468-5e7d-8f76-60c382cfa5cc | note | Frequency - Every Lot
b7f9cddf-e0d6-57dc-b450-1557ea5a71de | note | Acceptance Criteria - Proof rolling will be undertaken at the top layer surface of the imported select fill material for under pavements using a 16T smooth drum roller (minimum), or a 15kL watercart (minimum).
1d13e8cc-aca0-5c16-ade1-a98bb49c050a | note | ○ Principles Representative to be invited to proof roll 24 hours prior to inspection.
2bc6ddb4-edfd-5f91-8fd6-de65508b146e | note | ○ Principles Representative must witness the proof roll.
ebf5a59e-8e44-5291-8371-0f476cc2fda0 | note | ○ Following completion of the successful Proof Roll, Principles Representative will approve Fulton Hogan to place the next layer.
6134a0b9-74fd-5991-9fe4-7f7c835cb261 | note | ○ Placement of next layer can occur once lot is accepted following proof roll. Proof roll inspection will satisfy pre-placement CTB inspection
ed8f929c-5f3c-5d99-9d6c-e9ec5ff8a2c2 | note | Reference Documents - CL 4.11, CL 4.8, CL 4.16, CL 5.9
8853b58d-aa9e-5f04-8604-ca7be2a1e182 | note | Inspection/Test Method - Verify
9166191e-1d47-50c9-a1c2-aa87106416fb | note | Record of conformity - This ITP signed
8d54efd3-12ea-58c5-9db4-1ee9e840e530 | note | IP, HP, WP, HP, HP
b82ae293-b330-51f3-a3dd-5b0af50e15d0 | note | Responsibility - Project/Site Engineer
baa750f2-e49b-504c-a61d-2e359d14fe2f | date | Date Completed:
40f59b4f-71be-5a37-8b06-48355023e0f7 | signoff | AUTHORITY HOLDPOINT
18355098-3bb1-5292-9129-5d9c49ee19cd | checkpoint | 2.7 - Completion of Remedial Works (if required)
a6eea7f7-f90d-5f24-ba42-3cee0d13807c | note | Frequency - As required
10860f22-bd45-5045-b42a-51938225a3eb | note | Acceptance Criteria - Completion of remedial works or nonconforming Sub-Basecourse and/or Basecourse to be approved by Principal’s Representative before proceeding with the next layer of pavement Works.
b60361f7-65c4-5619-aaf9-fb1de60ca685 | note | Reference Documents - Spec cl. 4.21.3
a5be587b-5a31-5d92-87c4-2cf51d5227dc | note | Inspection/Test Method - Verify
ba4d1c10-00f9-5670-bb2c-33ef0baf1f43 | note | Record of conformity - This ITP signed
99acb4ef-c1fe-5a03-89cc-dff4993bedc2 | note | HP
a0e4e81b-9909-57d4-ba10-bc175a31943f | note | Responsibility - Project Engineer, Principal’s Representative
8a219366-a68a-5b60-8cff-5a38571304ec | date | Date Completed:
90a2a886-571d-56de-9a6a-670b0a14580e | note | Principal’s Representative - (if required)
c3655578-698a-581e-b5a5-f09c022177f4 | signoff | AUTHORITY HOLDPOINT
9b0000de-0289-50d5-8923-c7478a283c5e | section | 3.0 - Testing, Lot Size and Compliance
8ba74c27-2d49-528e-b53a-453ab30f277b | checkpoint | 3.1 - Survey Conformance
ce5c29e5-5140-5189-9eb7-e50ab50e5199 | note | Frequency - Every Lot
f272f98a-afa0-55a2-99ab-2926a15cf644 | note | Acceptance Criteria - Final survey level to be checked in a 5mx5m grid to conform with -10mm to +0mm.
df4c2108-63ab-5b10-b7f3-2e9c90d8b439 | note | ○ Survey report not provided for intermediate layers of the same material type (i.e. for PT2 where multiple layers of same material type placed).
12872338-4862-5c8b-9333-33b95e486659 | note | Reference Documents - Cl 4.13
53f1e0a9-3cd8-5987-afac-9955739ce2e2 | note | Inspection/Test Method - Survey Report
cfaa3583-94cb-5b87-a96f-4b0626c0b7ea | note | Record of conformity - This ITP signed
115ef3cc-0237-5ccb-b90f-4e1d03a9a55a | note | SCP
929cefd4-f1a7-5699-a3e6-84e1cfe5d6df | note | Responsibility - Project/Site Engineer
9d93fb88-69f1-59e3-929a-d5c9541b8328 | date | Date Completed:
80ed8158-99a3-513d-9e12-09880383a921 | checkpoint | 3.2 - Surface Smoothness
c0ec5a15-a8a0-51ca-90fd-d266a977ae28 | note | Frequency - Every Lot
d3bb6e9d-cacf-567a-bb05-bb6f85f87f76 | note | Acceptance Criteria - Surface smoothness to be checked every 10m by placing a 3.5m long straight edged on the ground a checking any deviations over 7mm. Complete within 7 days of completion of each section. Document results.
c0794366-a9f1-513e-a322-e27e793bf4c7 | note | ○ Intermediate layers and shoulder pavements are not required to be checked.
428ff593-cbc8-5486-9adf-190d324ee211 | note | Reference Documents - Cl 4.14
916d282e-b4f1-5915-a1c9-84918bf87ad0 | note | Inspection/Test Method - Verify
f13e2c07-1d50-5bc0-b7a8-ec257e7c1c05 | note | Record of conformity - Report
0a56ea0b-1e1d-575f-aaaa-8362bd7334a7 | note | TP, HP
7c42df32-edf4-5349-9cac-0db15597dd49 | note | Responsibility - Project/Site Engineer, Principles Rep
7afe6ac4-7764-512e-b7a2-c8fe830be0cc | date | Date Completed:
ab521b67-11c2-59d8-a3c0-98ec86671180 | signoff | AUTHORITY HOLDPOINT
12ef7ba2-4a80-5164-a247-feedc5d67ff8 | checkpoint | 3.3 - Layer Thickness
c7d134cc-94cd-5822-9a24-cf05412661f1 | note | Frequency - Every Lot
dfdd1cec-5b69-565b-969b-13bfc3125815 | note | Acceptance Criteria - Check thickness of layer using survey at the frequency of field dry density determinations. Thickness shall not be less than what is shown on the design documentation other than allowable construction tolerances.
39ceb27a-a277-5db6-8968-85e5c122043f | note | ○ Total pavement thickness is to be checked. Intermediate layers, no check is required.
02cf8440-e7ce-5019-8d6d-f32d5fb3afbd | note | Reference Documents - CL 4.12, CL4.21.1
018a61a9-d71a-5691-a975-97cdb35c1e0b | note | Inspection/Test Method - Survey
7625b794-097f-518f-90e0-c3cf230ed64d | note | Record of conformity - Survey Report
381236eb-aca7-59e3-a405-b6edd1e665c5 | note | SCP
53f8aeac-1b5e-5448-811f-f523a49ae4ee | note | Responsibility - Project/Site Engineer
b848acb5-3d29-5719-ad16-385a2f8d9cea | note | Aconex Ref: DCWC Mgt-RTRFI-001329
8bc84e71-cdd6-5f5b-afd0-1b535d392c96 | date | Date Completed:
9fdc7f62-f611-5a1d-a6d5-ee615e4ec42e | checkpoint | 3.4 - Degree of Saturation - Sub-Basecourse or Basecourse
88ac18ee-32b3-5465-8cd7-55615a26e84c | note | Frequency - Every Lot
9c74aee7-54c4-5afa-91e6-17f8b6c54a58 | note | Acceptance Criteria -  Degree of Saturation to be tested for information.
7d6d8edb-471d-59a3-84c9-22efe19673c4 | note | ○ Target less than 70% Mean Moisture Ratio.
5267ce29-e9dc-5467-8683-1ff409d3ea82 | note | ○ Test to be taken the shift prior
9ceab416-7620-5e4c-90dd-667de55b8550 | note | ○ If lot gets impacted by significant wet weather, tests to be re-taken
8589b525-694e-5da5-b255-316e9b32bc6b | note | Reference Documents - Cl 4.9
5fc35d50-782c-58c0-a03c-3e2d8632bc41 | note | Inspection/Test Method - Test
36e1d3a5-9404-5501-a43d-8d4439103d9f | note | Record of conformity - Test Report
5b334ed9-a6bc-5b9f-a9a5-188554ebf8fe | note | TP
57654c0f-8304-5154-aabe-6a53ae12880c | note | Responsibility - Project/Site Engineer
2fb7e3e4-a500-5dab-971f-da16c64f635a | date | Date Completed:
93d9ed7b-13bd-571c-b28a-b3e62bf41308 | checkpoint | 3.5 - Field Dry Density
ab290cab-8857-5299-aa93-394c9f7fa1cd | note | Frequency - Every Lot
44b41968-019b-5980-9048-f4b4803f2fa7 | note | Acceptance Criteria - Dry density for basecourse layer has the following acceptance criteria:
14d36e20-9b4e-51c7-b303-4820d35263fe | note | ○ Average of 5 consecutive tests exceeding 100% MMDD.
58de0ee5-78b1-54c6-8224-caf072eeab7c | note | ○ No individual test result less than 98% MMDD.
5d48328e-ac3a-5ad6-b3d1-2406a288f5b8 | note | ○ Principal’s Representative approval based on the results of proof rolling.
f93e1ad9-5cf4-5128-a858-cd7b9bd4cdbb | note | Dry density for sub-basecourse layer has the following acceptance criteria:
e55b6308-f7dc-5856-a542-efcc3c4daea4 | note | ○ Average of 5 consecutive tests exceeding 98% MMDD.
9bf576a0-bf13-5841-ab9a-3afc1935f1b8 | note | ○ No individual test result less than 95% of MMDD.
87da770e-45a7-5e52-8aa1-dda76aa5f24a | note | Principal’s Representative approval based on the results of proof rolling.
44ea133f-24b6-54a9-a30f-f261e13a62f9 | note | Reference Documents - CL4.10 Cl4.21.1
f280a436-de2a-53ef-93ab-b1e3225eeeeb | note | Inspection/Test Method - Test
52cdd929-b842-55ad-8145-5e9812049d33 | note | Record of conformity - Report
407dbe1a-efa0-5213-9bb6-8e6f36cbc3c5 | note | TP, HP
ab5827b3-767d-5dbc-a203-d030deba9967 | note | Responsibility - Project/Site Engineer
e7b37db0-a68e-5a1c-bb23-556cc134f8ee | date | Date Completed:
b4b288d4-a5a3-5645-a157-30ee8075f492 | signoff | AUTHORITY HOLDPOINT
78953ecd-84e7-5c05-ab3e-4b8357499fea | checkpoint | 3.6 - Quality Assurance Records
6006ffa3-1aa2-59bd-83dc-d6b805ff55b4 | note | Frequency - Each Lot
b2f55ca2-6a14-5a7e-82ba-84de49be30a1 | note | Acceptance Criteria - Submit test results on Aconex for every lot of Sub Base and Basecourse. Results to summarise each test (Moisture content, field dry density and layer thickness).
7bd5a9d8-f1f0-515c-9bd2-db15c58c3a89 | note | ○ Aconex ref to be submitted as Hold Point sign off.
37e3ac2e-1f70-5db3-af28-32a669466602 | note | Reference Documents - Cl4.21.2
c4470a88-b0fb-56dc-9525-ae5913364874 | note | Inspection/Test Method - Verify
e77eb85f-0ce5-5a4d-8372-d2a926cf0d3b | note | Record of conformity - Summary of results
425f643f-a056-5010-9038-22100d4cf06c | note | HP
199e0e4e-ff37-594a-a3d2-8836730d58da | note | Responsibility - Project/Site Engineer
76c8b366-beb3-55a7-bfb4-5516b9aae5c1 | date | Date Completed:
9cafd654-8c3b-5d53-b27f-4fd2723098a3 | note | Principal’s Representative - Aconex Ref: FHPL- TRANSMIT- 001750
172816b0-0bf5-52f3-80f0-01074156ae49 | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
ed6b8455-38dd-51af-bd54-3125b5c47d2a | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
df9f428d-9eb7-515a-8ac0-5b3ec3fd6875 | textbox | Print Name:
f06a7fa1-f701-5396-b827-73e4dfa88863 | textbox | Position:
e17ead71-e36c-5c5b-8116-ea40ac9b8e17 | date | Work Completed On:
4f3c133c-1503-54e8-8324-f5dd13700c4c | date | Date:
676a23e6-b816-500c-bd22-fc4a3c2512aa | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0009-LOT-001 - Stage 1 PT1 - Rev 0 | itp | FH-ZU2-QU-ITP009-LOT-001 - Stage 1 PT1
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
22b60133-d07e-5778-afbb-3104cb451e98 | note | Frequency - Prior to commencing works
90628709-661f-5c1d-808d-3f9633505536 | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex
bc77cecb-25db-54e2-a46f-f50316ce64bd | note | Reference Documents - Aconex
248e7c02-a029-5336-9878-3422c829cf56 | note | Inspection/Test Method - Visual inspecti on
505c13d3-3958-55d4-b28a-dbe56fcb6509 | note | Record of conformity - This signed ITP
d9b9a31e-4fc1-55c9-8cf1-e24191b8f35b | note | HP*
577c368a-5703-5a58-b59c-18e92dbc9be8 | note | Responsibility - Project/Site Engineer
0ca55223-b839-58b1-9ea2-63b876b41d8e | date | Date Completed:
0ee48894-54ec-5653-949e-3aecb94d8a6f | checkpoint | 1.2 - Implementation of all measures and controls, weather, and material properties.
d49a7852-f9a9-5121-afd2-663081afa613 | note | Frequency - Prior to commencing works
1e3e4950-6df5-54d8-b002-d4b18ac8c1d9 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
46aa07a5-24fd-5c8d-8bf3-189213104141 | note | ○ Check weather prior to starting any works.
4274f253-54a3-50bd-9ec8-7b1601fe3d02 | note | ○ FCR material used for the works in accordance to VicRoads Class 2 Crushed Rock.
9351f45c-6020-5acc-acdf-0786a7e52f32 | note | ○ RCC material to be used for the Works in accordance with VicRoads Class 3 Crushed Rock.
67de20a2-0256-57b6-850f-aadb800e0d07 | note | ○ Checking underlying layer ITP’s (subgrade ITP008 and select fill ITP004 has been completed)
337e8923-b57f-5282-856b-d3a6b8d18b41 | note | Reference Documents - PSP, EMP, TMP, WP SWMS, Spec Cl 4.19, Spec cl. 4.1, VicRoads Technical Note 107 Spec cl. 4.6
b918f1ef-0da1-5bc1-8bb8-6c02335de461 | note | Inspection/Test Method - Visual inspection
6f531f46-a05a-5c16-b04e-195d1c3f4a93 | note | Record of conformity - This signed ITP
3b7b3517-c997-5002-97c8-f1aa5f1e7cae | note | HP*
2de72f79-4994-57b6-a35f-9b3e18858774 | note | Responsibility - Project/Site Engineer, Foreman
baa8b9fa-f889-5d30-8dea-a71cc722d564 | date | Date Completed:
b55c3da7-c29e-50dc-b5c6-6c3d6d4c85da | checkpoint | 1.3 - Material Report - Fine Crushed Rock (FCR) Material & Recycle Crushed Concrete (RCC)
08f8e815-db8e-5c04-a20e-779ea9c698a3 | note | Frequency - 7 Days - Prior to works
f23fc5f1-f6fb-5435-ad79-c5ecdcd035c6 | note | Acceptance Criteria - Material Report to be submitted 7 days prior to works to include;
1344dbf9-3674-54ba-b047-2f9a512d67de | note | ○ Source and Quarry location
dc8222db-ef8f-5c16-b274-2905dc7a31d3 | note | ○ Quarry material is sourced from.
a8449f49-f55e-5365-8100-695b2068f934 | note | ○ Material rock type and petrographic description
8b784087-184c-59ef-b6b6-040c79a2a485 | note | ○ Historical test results
836aacce-c6f4-5341-b85b-04b293e861dc | note | ○ Method of processing and transportation
52202e1b-799b-57e1-bfb2-b5a8c390d48f | note | ○ Material summary of the results of recent test on samples of the material from the source
e2e34f1e-e0b2-5faa-bb77-6746fc484680 | note | Reference Documents - Spec cl 4.20.1
c4580524-9128-5583-a7bf-4fa86d4a90ec | note | Inspection/Test Method - Verify
6f6417f1-69f8-5ad5-984c-fd198378675f | note | Record of conformity - This ITP signed
c8da58f1-5852-54c6-b606-35386ce293d9 | note | HP
27f7bd55-d87c-5dde-b69a-8a690d4a1c5c | note | Responsibility - Project/Site Engineer, Principles Rep
98351715-983d-55b6-b5e4-29818398c2fb | date | Date Completed:
f90cc78c-5577-584a-bf6f-2baea0a79d8a | note | Principal’s Representative - Aconex Ref: Holcim RCC Class 3 - DCWC Mgt-GCOR-009582
6ed4e75b-7d7c-59d4-860f-84f44b2920d0 | note | ○ Holcim FRC Class 2 - DCWC Mgt-GCOR-009581
f1140fed-3d65-5000-a675-33f0cf450936 | note | ○ Stirling Class 3 - DCWC Mgt-GCOR-009565
8b2d5395-ceb8-53cb-8eb1-c7add6510501 | signoff | AUTHORITY HOLDPOINT
ec34d278-5586-5c2a-99c8-01e2abad83a0 | checkpoint | 1.4 - Reference Samples
525ba691-af22-5b05-b06f-d97f2febed12 | note | Frequency - 5 Days prior to works
d6fbd216-8984-5446-82cf-f06bf7078519 | note | Acceptance Criteria - Reference samples to be submitted 5 days prior to works commencing. Two bags to be taken each weighing 25kg. One bag submitted to Client, one retained by Contractor
393a62fb-dc1a-51af-820d-43d92dcf2ed5 | note | Reference Documents - Spec cl. 4.20.2
81cb4669-886b-5347-b152-1895c2aef53c | note | Inspection/Test Method - Verify
3df23d20-62cf-5417-b4eb-60cb6864ab05 | note | Record of conformity - This ITP signed
afaad2f4-dbb5-5fd8-87e6-401b5bf4febd | note | HP
54753b28-df32-5121-a510-4e413fb619cc | note | Responsibility - Project/Site Engineer, Principles Rep
ee76c1dc-3531-5a2f-8c1f-475d8f250b39 | date | Date Completed:
d95e7d5e-6bf0-5924-b391-1cfea39c7d6c | signoff | AUTHORITY HOLDPOINT
86350ec1-aec3-5802-aaf3-a14a45b6d2ff | checkpoint | 1.5 - Trial Section
65684dbf-f369-509e-a5e8-b314c3fd8819 | note | Frequency - Prior to works
bafdae1c-25bf-5ae2-9cd0-6608d8ef0a98 | note | Acceptance Criteria - Trial section to be completed with Principles Representative approving the use of the spreading machine.
6c6faa28-2c6a-59b8-bc47-3393a4e05f95 | note | Reference Documents - Spec cl. 4.7
af7d6c18-3dcc-50bf-b3f8-53ce25ab318e | note | Inspection/Test Method - Verify
17a066a2-c53c-51e9-a713-f8604f6dba5c | note | Record of conformity - This ITP signed
eeb60278-237d-56da-890e-daecf0bb1cf4 | note | HP
b8253941-a061-5b59-a6f1-8d269d6fe801 | note | Responsibility - Project/Site Engineer, Principles Rep
a035e09f-3c92-5f13-973b-02f96ca5b1ac | date | Date Completed:
50b5aab5-7a04-53ea-a4dd-31d851a2dce3 | signoff | AUTHORITY HOLDPOINT
690716ed-b540-5814-804e-da1a18d341a5 | checkpoint | 1.6 - Compaction Equipment
b945be75-e6e9-57a1-8123-6e8633aab849 | note | Frequency - Prior to works
e74b505a-9f5c-54a0-aeea-6de10bb335eb | note | Acceptance Criteria - Pneumatic tyred rollers having a weight of 27t (min roller weight can be 7t spread across 7 wheels). Tyre inflation pressure to be checked. A 15t to 20t smooth drum roller to be used.
2801421f-e441-58d5-bb6a-16a4d3e6997a | note | Reference Documents - Spec Cl 2.4.3 Item 84 Tender Clarifications
7714caf1-b8f8-5140-a270-f11a742d03c8 | note | Inspection/Test Method - Verify
c68e6fd7-3cf1-58cb-b9e5-ef98680eb80c | note | Record of conformity - This ITP signed
1ca6e76d-4a10-59f8-9af4-a8cfd70ad21c | note | WP
de947921-e38e-5dbb-98de-20d29f6f2cf3 | note | Responsibility - Project/Site Engineer, Principles Rep
780ed8c5-c16d-5d7d-a120-b2874bf1d159 | date | Date Completed:
1d9506f5-f6c7-5206-bffc-81f4f4f90212 | signoff | AUTHORITY HOLDPOINT
31f3573f-3cd4-53a2-bab5-d81150ad14d3 | section | 2.0 - Placement of Sub-basecourse and Basecourse
520af3e6-6af9-53b6-9cab-e0a37d5ddeeb | checkpoint | 2.1 - Layer Placement Parameters
aaa3edf8-61eb-55f2-97a1-d0fb08386030 | note | Frequency - Every Lot
16c77b6b-81f0-5b20-ad8d-8506d7ec2d02 | note | Acceptance Criteria - Summary of Parameters for each Lot;
3f87eaec-bfd5-5113-a5dd-c989fed0fec5 | note | ○ A lot is defined as one layer placed in a single days production of uniform material
ba7c17ca-eae9-5ba4-a3ff-214dac3491bc | note | ○ Max Layer is 200mm
322cb297-e6e8-5565-b3fe-48d519767cce | note | ○ Min Layer is 75mm
ce182ba1-c8fb-5c79-9cb4-9e7811cce7b1 | note | ○ Final Surface Level +0mm, -10mm (excluding intermediate layers)
3fcf686c-043f-5d65-9648-ea4b780b560f | note | ○ Shape: every 10m intervals, <7mm deviation over 3.5m straight edge (excluding intermediate layers)
2a7aa885-9c4f-5381-8ece-bb1b9ccba295 | note | ○ Material to be batched within 1% of OMC
2585bc1f-f9ba-51cb-839f-4f8d9b4863dc | note | Reference Documents - Spec Cl4.8, cl 4.21.2, cl 4.13
cced5364-2910-5d18-aa42-577b9981563e | note | Inspection/Test Method - Verify
8100ba46-80fe-5560-aca3-286dd0f42292 | note | Record of conformity - This ITP signed
be2c8188-b893-5606-951c-1d3052e63cd4 | note | IP
6d1c799a-1c5e-5479-95f5-52693cfb267f | note | Responsibility - Project/Site Engineer
c035320a-65e6-5da3-8edd-85233f228189 | date | Date Completed:
ab12b78d-7983-5acd-aa07-c177c46370e6 | checkpoint | 2.2 - Placement Checks
35f1d8ab-6103-59c1-8b59-7dbfdfd5a318 | note | Frequency - Every Lot
d330c613-67e4-5ca5-a41d-034019e87353 | note | Acceptance Criteria - During placement of the material check;
a0897ee6-0317-5245-b2d4-b7319354e90a | note | ○ Deliveries do not disturb underlying layer
c52be776-0b87-5bb4-9639-97923473720f | note | ○ Spreading starts from crown / high side where practical.
6558ad17-534d-5102-861d-33bdf6acdef4 | note | ○ Material does not get contaminated during placement / delivery
da1053c0-3a2a-5ac3-86fd-b3ecc6fd4402 | note | ○ Watercart is present to condition material as required
23130571-9585-5f82-a1bd-667592304329 | note | ○ Edges are cut / removed if dry of not compacted with abutting lots
25bb25f1-45b3-507e-b660-1bdfb628c3bb | note | Reference Documents - Spec Cl 4.8
35f5add3-e162-53d8-9bcf-6f098b9c662c | note | Inspection/Test Method - Verify
b7644ee8-0ce7-5f78-90af-aafeca592397 | note | Record of conformity - This ITP signed
5a905e00-c1e4-512f-9a17-ade2ccd58b44 | note | IP
19652dec-189a-5f21-8896-0766c8cb7a88 | note | Responsibility - Project/Site Engineer
2a0baffe-e984-564d-9c01-dab08964c6d6 | date | Date Completed:
03b653d0-0f2f-5bbe-ba99-60916a24386a | checkpoint | 2.3 - Compaction Check
58e6a7da-0a23-579e-adb3-07ffa5af4807 | note | Frequency - Every Lot
09efdcc0-9ad5-589b-9f7a-29a04ff56202 | note | Acceptance Criteria - During Compaction check;
112f68b3-7620-566d-bcbd-453cf4539fcb | note | ○ Heavy smooth drum roller of 15t to 20t is used for initial compaction
156bec7b-d118-5098-80a4-9f9811800889 | note | ○ Pneumatic roller of 27t will compact material for final consolidation.
63744c10-259a-59ff-aa84-ed5a2ec11330 | note | ○ A heavy smooth drum roller (in static mode) may also be used for final consolidation
1dcab749-3f6d-5dc0-8b70-8e6ccc60521a | note | ○ Watercart Present onsite for conditioning
55bdb2c8-4342-5857-baae-a10bdc7ecac0 | note | ○ Materials are trimmed to required shape and level
d22c4f0e-7900-552c-8a73-ef0db6e4ae0e | note | Reference Documents - Cl 4.10
1993e4bb-389f-5674-aac7-b01ba95c1fb1 | note | Inspection/Test Method - Verify
669b9d6b-f3ad-50de-bde3-67155680d007 | note | Record of conformity - This ITP signed
14eaa2db-1f06-5432-8e0c-27042f49ab02 | note | IP
6cd03551-ea7e-545c-bfad-d40f0419bc20 | note | Responsibility - Project/Site Engineer
045eb3cb-4193-5ec9-b4b2-f7ded14ec478 | date | Date Completed:
56c1eb5a-a610-51e7-86f1-f05ba8e1b5bd | checkpoint | 2.4 - Services & Culverts
cad1544e-6b90-53e9-b346-5cdaec13789b | note | Frequency - Every Lot
6ade1825-13f6-521f-80f3-e6df0e156981 | note | Acceptance Criteria - Check if any culverts or services are with the influence zone for compaction.
f01b9dd3-612c-5a17-a57d-010ef1513183 | note | ○ A general rule, FH will seek advice from the Principles Representative if any culverts, duct banks or RCP pipe are identified closer than 1m from pavement layer surface. If identified, Fulton Hogan will maintain a 1m exclusion zone either side from centre of service for vibrating compaction activities. Hand held DPU’s/whacker plate to be used in lieu of rollers in restricted areas.
67c452e0-d6b9-5f8e-a3da-b3d574687983 | note | Reference Documents - CL4.10
fa8211c9-abd1-57da-b54f-de0c6e5dbe35 | note | Inspection/Test Method - Verify
ffa561c5-3a1c-5b2a-8fdc-90801c716515 | note | Record of conformity - This ITP signed
33423efd-62ae-5c89-b304-dd78ede7b634 | note | IP
54f78c92-1f94-54e5-9290-23165c7f8f9b | note | Responsibility - Project/Site Engineer
d6d1b5b8-e9d7-5583-8a85-3068b4699540 | date | Date Completed:
af9dc4f1-7e43-5752-b5a1-15b8f94cf295 | checkpoint | 2.5 - Protection of Layer
b5def97a-8a82-52be-9c54-498ac337f247 | note | Frequency - Every Lot
f5abe81d-8f4d-510d-8885-fa3cc5fca33b | note | Acceptance Criteria - Protect area from undue deterioration by;
f417fc95-2acf-5b5c-8b72-7fc970c8db29 | note | ○ Section off area for at least 12 to 48 hours to allow material to dry back.
59af82c2-ee2b-55ae-9f1a-84ba3d796d2f | note | ○ If unable to do so, keep traffic to a minimum
7b0a10bc-80ce-5720-b786-07441ed72b4e | note | ○ Or ensure any traffic that has to cross pavement layers, do not follow the same driving line.
98124425-bbe9-54b3-9173-c49ea88147ad | note | Reference Documents - Cl4.17
941d9051-473f-561a-bb5b-246c9d4cf08f | note | Inspection/Test Method - Verify
4ca87943-c62f-5a1b-b82a-fc898998e077 | note | Record of conformity - This ITP signed
fbcb7b46-d64b-5e69-8d4c-558089c333e1 | note | IP
86dbe21d-b474-525d-b7cc-73d45852ecfe | note | Responsibility - Project/Site Engineer
c1acb8c3-0d37-5859-88bb-9dc12a60a61b | date | Date Completed:
ed4dca39-7158-53f5-b80c-2934cf975618 | checkpoint | 2.6 - Proof Rolling
44460523-6468-5e7d-8f76-60c382cfa5cc | note | Frequency - Every Lot
b7f9cddf-e0d6-57dc-b450-1557ea5a71de | note | Acceptance Criteria - Proof rolling will be undertaken at the top layer surface of the imported select fill material for under pavements using a 16T smooth drum roller (minimum), or a 15kL watercart (minimum).
1d13e8cc-aca0-5c16-ade1-a98bb49c050a | note | ○ Principles Representative to be invited to proof roll 24 hours prior to inspection.
2bc6ddb4-edfd-5f91-8fd6-de65508b146e | note | ○ Principles Representative must witness the proof roll.
ebf5a59e-8e44-5291-8371-0f476cc2fda0 | note | ○ Following completion of the successful Proof Roll, Principles Representative will approve Fulton Hogan to place the next layer.
6134a0b9-74fd-5991-9fe4-7f7c835cb261 | note | ○ Placement of next layer can occur once lot is accepted following proof roll. Proof roll inspection will satisfy pre-placement CTB inspection
ed8f929c-5f3c-5d99-9d6c-e9ec5ff8a2c2 | note | Reference Documents - CL 4.11, CL 4.8, CL 4.16, CL 5.9
8853b58d-aa9e-5f04-8604-ca7be2a1e182 | note | Inspection/Test Method - Verify
9166191e-1d47-50c9-a1c2-aa87106416fb | note | Record of conformity - This ITP signed
8d54efd3-12ea-58c5-9db4-1ee9e840e530 | note | IP, HP, WP, HP, HP
b82ae293-b330-51f3-a3dd-5b0af50e15d0 | note | Responsibility - Project/Site Engineer
baa750f2-e49b-504c-a61d-2e359d14fe2f | date | Date Completed:
40f59b4f-71be-5a37-8b06-48355023e0f7 | signoff | AUTHORITY HOLDPOINT
18355098-3bb1-5292-9129-5d9c49ee19cd | checkpoint | 2.7 - Completion of Remedial Works (if required)
a6eea7f7-f90d-5f24-ba42-3cee0d13807c | note | Frequency - As required
10860f22-bd45-5045-b42a-51938225a3eb | note | Acceptance Criteria - Completion of remedial works or nonconforming Sub-Basecourse and/or Basecourse to be approved by Principal’s Representative before proceeding with the next layer of pavement Works.
b60361f7-65c4-5619-aaf9-fb1de60ca685 | note | Reference Documents - Spec cl. 4.21.3
a5be587b-5a31-5d92-87c4-2cf51d5227dc | note | Inspection/Test Method - Verify
ba4d1c10-00f9-5670-bb2c-33ef0baf1f43 | note | Record of conformity - This ITP signed
99acb4ef-c1fe-5a03-89cc-dff4993bedc2 | note | HP
a0e4e81b-9909-57d4-ba10-bc175a31943f | note | Responsibility - Project Engineer, Principal’s Representative
8a219366-a68a-5b60-8cff-5a38571304ec | date | Date Completed:
90a2a886-571d-56de-9a6a-670b0a14580e | note | Principal’s Representative - (if required)
c3655578-698a-581e-b5a5-f09c022177f4 | signoff | AUTHORITY HOLDPOINT
9b0000de-0289-50d5-8923-c7478a283c5e | section | 3.0 - Testing, Lot Size and Compliance
8ba74c27-2d49-528e-b53a-453ab30f277b | checkpoint | 3.1 - Survey Conformance
ce5c29e5-5140-5189-9eb7-e50ab50e5199 | note | Frequency - Every Lot
f272f98a-afa0-55a2-99ab-2926a15cf644 | note | Acceptance Criteria - Final survey level to be checked in a 5mx5m grid to conform with -10mm to +0mm.
df4c2108-63ab-5b10-b7f3-2e9c90d8b439 | note | ○ Survey report not provided for intermediate layers of the same material type (i.e. for PT2 where multiple layers of same material type placed).
12872338-4862-5c8b-9333-33b95e486659 | note | Reference Documents - Cl 4.13
53f1e0a9-3cd8-5987-afac-9955739ce2e2 | note | Inspection/Test Method - Survey Report
cfaa3583-94cb-5b87-a96f-4b0626c0b7ea | note | Record of conformity - This ITP signed
115ef3cc-0237-5ccb-b90f-4e1d03a9a55a | note | SCP
929cefd4-f1a7-5699-a3e6-84e1cfe5d6df | note | Responsibility - Project/Site Engineer
9d93fb88-69f1-59e3-929a-d5c9541b8328 | date | Date Completed:
80ed8158-99a3-513d-9e12-09880383a921 | checkpoint | 3.2 - Surface Smoothness
c0ec5a15-a8a0-51ca-90fd-d266a977ae28 | note | Frequency - Every Lot
d3bb6e9d-cacf-567a-bb05-bb6f85f87f76 | note | Acceptance Criteria - Surface smoothness to be checked every 10m by placing a 3.5m long straight edged on the ground a checking any deviations over 7mm. Complete within 7 days of completion of each section. Document results.
c0794366-a9f1-513e-a322-e27e793bf4c7 | note | ○ Intermediate layers and shoulder pavements are not required to be checked.
428ff593-cbc8-5486-9adf-190d324ee211 | note | Reference Documents - Cl 4.14
916d282e-b4f1-5915-a1c9-84918bf87ad0 | note | Inspection/Test Method - Verify
f13e2c07-1d50-5bc0-b7a8-ec257e7c1c05 | note | Record of conformity - Report
0a56ea0b-1e1d-575f-aaaa-8362bd7334a7 | note | TP, HP
7c42df32-edf4-5349-9cac-0db15597dd49 | note | Responsibility - Project/Site Engineer, Principles Rep
7afe6ac4-7764-512e-b7a2-c8fe830be0cc | date | Date Completed:
ab521b67-11c2-59d8-a3c0-98ec86671180 | signoff | AUTHORITY HOLDPOINT
12ef7ba2-4a80-5164-a247-feedc5d67ff8 | checkpoint | 3.3 - Layer Thickness
c7d134cc-94cd-5822-9a24-cf05412661f1 | note | Frequency - Every Lot
dfdd1cec-5b69-565b-969b-13bfc3125815 | note | Acceptance Criteria - Check thickness of layer using survey at the frequency of field dry density determinations. Thickness shall not be less than what is shown on the design documentation other than allowable construction tolerances.
39ceb27a-a277-5db6-8968-85e5c122043f | note | ○ Total pavement thickness is to be checked. Intermediate layers, no check is required.
02cf8440-e7ce-5019-8d6d-f32d5fb3afbd | note | Reference Documents - CL 4.12, CL4.21.1
018a61a9-d71a-5691-a975-97cdb35c1e0b | note | Inspection/Test Method - Survey
7625b794-097f-518f-90e0-c3cf230ed64d | note | Record of conformity - Survey Report
381236eb-aca7-59e3-a405-b6edd1e665c5 | note | SCP
53f8aeac-1b5e-5448-811f-f523a49ae4ee | note | Responsibility - Project/Site Engineer
e3d5de64-9d54-52dc-8d45-c0af394a5259 | note | Aconex Ref: DCWC Mgt-RTRFI-001329
8bc84e71-cdd6-5f5b-afd0-1b535d392c96 | date | Date Completed:
9fdc7f62-f611-5a1d-a6d5-ee615e4ec42e | checkpoint | 3.4 - Degree of Saturation - Sub-Basecourse or Basecourse
88ac18ee-32b3-5465-8cd7-55615a26e84c | note | Frequency - Every Lot
9c74aee7-54c4-5afa-91e6-17f8b6c54a58 | note | Acceptance Criteria -  Degree of Saturation to be tested for information.
7d6d8edb-471d-59a3-84c9-22efe19673c4 | note | ○ Target less than 70% Mean Moisture Ratio.
5267ce29-e9dc-5467-8683-1ff409d3ea82 | note | ○ Test to be taken the shift prior
9ceab416-7620-5e4c-90dd-667de55b8550 | note | ○ If lot gets impacted by significant wet weather, tests to be re-taken
8589b525-694e-5da5-b255-316e9b32bc6b | note | Reference Documents - Cl 4.9
5fc35d50-782c-58c0-a03c-3e2d8632bc41 | note | Inspection/Test Method - Test
36e1d3a5-9404-5501-a43d-8d4439103d9f | note | Record of conformity - Test Report
5b334ed9-a6bc-5b9f-a9a5-188554ebf8fe | note | TP
57654c0f-8304-5154-aabe-6a53ae12880c | note | Responsibility - Project/Site Engineer
2fb7e3e4-a500-5dab-971f-da16c64f635a | date | Date Completed:
93d9ed7b-13bd-571c-b28a-b3e62bf41308 | checkpoint | 3.5 - Field Dry Density
ab290cab-8857-5299-aa93-394c9f7fa1cd | note | Frequency - Every Lot
44b41968-019b-5980-9048-f4b4803f2fa7 | note | Acceptance Criteria - Dry density for basecourse layer has the following acceptance criteria:
14d36e20-9b4e-51c7-b303-4820d35263fe | note | ○ Average of 5 consecutive tests exceeding 100% MMDD.
58de0ee5-78b1-54c6-8224-caf072eeab7c | note | ○ No individual test result less than 98% MMDD.
5d48328e-ac3a-5ad6-b3d1-2406a288f5b8 | note | ○ Principal’s Representative approval based on the results of proof rolling.
f93e1ad9-5cf4-5128-a858-cd7b9bd4cdbb | note | Dry density for sub-basecourse layer has the following acceptance criteria:
e55b6308-f7dc-5856-a542-efcc3c4daea4 | note | ○ Average of 5 consecutive tests exceeding 98% MMDD.
9bf576a0-bf13-5841-ab9a-3afc1935f1b8 | note | ○ No individual test result less than 95% of MMDD.
87da770e-45a7-5e52-8aa1-dda76aa5f24a | note | Principal’s Representative approval based on the results of proof rolling.
44ea133f-24b6-54a9-a30f-f261e13a62f9 | note | Reference Documents - CL4.10 Cl4.21.1
f280a436-de2a-53ef-93ab-b1e3225eeeeb | note | Inspection/Test Method - Test
52cdd929-b842-55ad-8145-5e9812049d33 | note | Record of conformity - Report
407dbe1a-efa0-5213-9bb6-8e6f36cbc3c5 | note | TP, HP
ab5827b3-767d-5dbc-a203-d030deba9967 | note | Responsibility - Project/Site Engineer
e7b37db0-a68e-5a1c-bb23-556cc134f8ee | date | Date Completed:
b4b288d4-a5a3-5645-a157-30ee8075f492 | signoff | AUTHORITY HOLDPOINT
78953ecd-84e7-5c05-ab3e-4b8357499fea | checkpoint | 3.6 - Quality Assurance Records
6006ffa3-1aa2-59bd-83dc-d6b805ff55b4 | note | Frequency - Each Lot
b2f55ca2-6a14-5a7e-82ba-84de49be30a1 | note | Acceptance Criteria - Submit test results on Aconex for every lot of Sub Base and Basecourse. Results to summarise each test (Moisture content, field dry density and layer thickness).
7bd5a9d8-f1f0-515c-9bd2-db15c58c3a89 | note | ○ Aconex ref to be submitted as Hold Point sign off.
37e3ac2e-1f70-5db3-af28-32a669466602 | note | Reference Documents - Cl4.21.2
c4470a88-b0fb-56dc-9525-ae5913364874 | note | Inspection/Test Method - Verify
e77eb85f-0ce5-5a4d-8372-d2a926cf0d3b | note | Record of conformity - Summary of results
425f643f-a056-5010-9038-22100d4cf06c | note | HP
199e0e4e-ff37-594a-a3d2-8836730d58da | note | Responsibility - Project/Site Engineer
76c8b366-beb3-55a7-bfb4-5516b9aae5c1 | date | Date Completed:
9cafd654-8c3b-5d53-b27f-4fd2723098a3 | textbox | Aconex Ref:
172816b0-0bf5-52f3-80f0-01074156ae49 | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
ed6b8455-38dd-51af-bd54-3125b5c47d2a | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
df9f428d-9eb7-515a-8ac0-5b3ec3fd6875 | textbox | Print Name:
f06a7fa1-f701-5396-b827-73e4dfa88863 | textbox | Position:
e17ead71-e36c-5c5b-8116-ea40ac9b8e17 | date | Work Completed On:
4f3c133c-1503-54e8-8324-f5dd13700c4c | date | Date:
177eeaad-3082-5a9a-a955-18da21d8a2ca | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0010-LOT-001 - Stage 1 - Pavement Type 1 - Rev 0 | itp | FH-ZU2-QU-ITP010-LOT-001 - Stage 1 - Pavement Type 1
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
8aa88d4b-ee91-5ba0-8457-6ddccc0d3aa5 | note | Frequency - Prior to works
f596a299-9f58-53ca-9c69-525ee7c3cc5c | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex.
e63a70e3-79b5-5073-95c3-410eeed9d6ef | note | Reference Documents - Aconex
66c5096d-0ffa-51b0-b947-f747cf16c41e | note | Inspection/Test Method - Visual inspection
5576b08f-da41-5fb2-928c-3099cdaa6f44 | note | Record of conformity - This signed ITP
bd555431-cb25-5b36-b645-bdbb62cd6733 | note | HP*
3b038d3a-33f6-557b-82bd-e7cd92c4d207 | note | Responsibility - Project/Site Engineer, Superintendent, Foreman
2f246865-c5bc-5edc-9639-3718d72b4815 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
b0b243f7-51c3-55b3-a663-0dc1b1e0b83a | note | Frequency - Prior to works
f696c199-a47f-5990-bd66-7861ff848da2 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
94fa6461-840a-5ed1-8c42-e091c2be9c8f | note | Reference Documents - PSP, EMP, TMP, SWMS & WP
77b7ee44-7821-5616-bd18-d2ce2cac25ba | note | Inspection/Test Method - Visual inspection
63a96ffb-32b4-5e4b-8a97-562a0fa2a122 | note | Record of conformity - This signed ITP
af9cf847-45a8-50a3-a06c-f3aa247d5f84 | note | HP*
1bb9c244-d14a-5e0b-ad9d-5e50f2486391 | note | Responsibility - Project/Site Engineer
20fe73d9-f13f-5d4b-9540-7726d2227e41 | date | Date Completed:
b9437d57-cad2-5d07-86bd-bc4cd9694fa4 | section | 2.0 - Cement Treated Base Documentation & Trial
f713fe9a-9690-5e10-a912-023f37ca0459 | checkpoint | 2.1 - Submission of Mix Design
f84701ba-8df7-56a7-bbf7-fd0108956189 | note | Frequency - 21 days prior to works
4c9630b9-e2f4-5db5-896f-1a0e63df22cf | note | Acceptance Criteria - CTB material and test results to be submitted to the Principal’s Representative for review to ensure that specifications are met and are compliant, prior to the initial placement of the material.
e094d516-039e-569f-9119-c1c7926abfa5 | note | Mix design results will include:
6e374311-1c48-581e-bddc-512318494010 | note | ○ Cement sample should include a CTB material within +/-0.5% of the specified cement content.
7554aa82-ddbf-5f1b-bdd1-acb07d6ad61f | note | ○ Aggregates comply with either Section 4.4 or VicRoads Class 2 or 3 material.
74caf24d-bc49-56b5-a014-a303fa78a0dc | note | ○ Cement shall be Portland Cement Type GP or Type GB complying with AS 3972.
4bd42f13-d34e-5934-acc8-df754cb1cd35 | note | ○ 3% minimum Portland cement content by weight of the dry un-stabilised material.
0998a3e8-f98a-5b9a-be32-e00b897df493 | note | ○ Mean seven-day unconfined compressive strength of CTB to be a minimum of 5MPa and a maximum of 15MPa. No single samples are to be below 5MPa.
42cad487-7e07-5ecf-9580-c34b1c0004d7 | note | ○ Water to be pot
1b7669d0-aaac-57b0-96ea-a1fcdf6df9ca | note | Reference Documents - Spec cl. 5.4, Spec cl. 5.5 AS 3972 VicRoads Class 2, VicRoads Class 3
873572a1-d8cc-565f-94c0-b94eb417573b | note | Inspection/Test Method - Verify
a66909ef-0334-52a2-bb86-0d40152f53e9 | note | Record of conformity - Approved Mix Design Report
2a6c4f49-8b5a-554f-8666-bcb24bd3eb89 | note | HP
5f8594b4-a8be-5f85-bfc9-24cd96c89d3a | note | Responsibility - Project/Site Engineer, Principal’s Representative
6f53238e-be9b-5995-8685-fd629656dbea | note | Principles Rep - Aconex: BecaCPL-GCOR-000790
66263921-7ec1-5447-8330-44ed2cae7d71 | date | Date Completed:
5b68e915-fa91-5491-8e7f-3cf5fa1c57e8 | signoff | AUTHORITY HOLDPOINT
b08682c6-b8e3-5977-9b10-3b486b29efa1 | checkpoint | 2.2 - Supply of Information on Materials Source
72c22c59-df34-5e6a-8aae-a691c8b99d03 | note | Frequency - Prior to works
f06bcd80-cb39-5f6c-b7ee-acc980e2837c | note | Acceptance Criteria - Principle Contractor to supply the Principal’s Representative with supply information regarding the source of the CTB material via Aconex.
8162544f-1551-5f20-8f89-31e412124556 | note | ○ Material information will include the material brand, material type, material supply source, and a supporting test certificate from a laboratory registered by NATA to prove material suitability for the Works.
0fa3973c-f303-515a-83ef-710cdaa6e7b0 | note | Reference Documents - Spec cl. 5.21.1, Spec cl. 5.21.1.1 AS3972
f426f090-b259-5e95-9fe5-efd9491e0e42 | note | Inspection/Test Method - Verify
f4fd7777-24a4-5e24-8f03-2efc20b3adda | note | Record of conformity - Approved Supply of Information Material Source
2c108637-99ea-5b69-8af2-367b81ad171b | note | HP
77f8cbba-a50c-5b3b-980b-bc14c923226d | note | Responsibility - Project/Site Engineer, Principal’s Representative
737f78ca-d449-5e8e-9300-55c08726cd26 | note | Principles Rep - Aconex: BecaCPL-GCOR-000790
2deff7dd-cb7b-5ccf-9592-103910360dfc | date | Date Completed:
2be119e5-29ff-5f1c-b5de-c6aec4a7e549 | signoff | AUTHORITY HOLDPOINT
a3b266d6-20d2-577d-8bcc-cd0d95185e7c | checkpoint | 2.3 - Production and Construction Trial
2237b766-5dba-5d29-821a-e23e772d006b | note | Frequency - Prior to works
3851ad88-0336-50bc-9701-1a660bba0fbb | note | Acceptance Criteria - Construction Trial for CTB mix to be undertaken by Contractor and reviewed by the Principal’s Representative.
a16ae413-4a25-567f-a41e-e6d4836ce8bd | note | ○ Trial of CTB will be based on the first day of placement. Construction procedure to be reviewed and updated if there are any non-conformances associated with the initial trial.
b2ee570e-0077-5e08-a6d7-b9ab0e54b482 | note | ○ The size of the trial area shall be a minimum of 3.5m wide and 50m in length.
92a07a74-804e-50e3-927c-8e7863345b9a | note | ○ The CTB trial area may form part of the completed works.
9c4ed211-657f-57d9-81c5-2446d3c19ac0 | note | Reference Documents - Spec cl. 132, Spec cl. 5.6
717ed14e-d0fa-59c1-bb81-5da36d688f29 | note | Inspection/Test Method - Verify
2dee421f-a4d7-599a-92f8-3f4f57c30792 | note | Record of conformity - Approved Construction trial report
aae278da-12eb-5ac9-aa6e-efefd64eccb1 | note | HP
22a01488-e3ea-50b4-87f1-af2f3639ea98 | note | Responsibility - Project/Site Engineer, Principal’s Representative
05718d70-ae85-54e4-8dac-399b72b5185c | date | Date Completed:
b511eb0c-9811-5b67-89e8-b06a8ab74610 | signoff | AUTHORITY HOLDPOINT
36dd2170-94f3-5210-af3d-9abe62a51461 | checkpoint | 2.4 - Placement of CTB Methodology
8f31af96-a04d-519f-825d-c89d24070a0f | note | Frequency - Prior to works
22af0bf6-e6a7-533b-8b84-023de9149711 | note | Acceptance Criteria - Prior to placement of CTB the Principles Representative shall review this Work Method Statement for proposed methods of placement, compaction and curing
668d3fd8-fac2-52af-8caf-cb2488203135 | note | Reference Documents - Spec cl 5.9
9de3b2f3-7747-5f3c-baa3-785a2747e99a | note | Inspection/Test Method - Verify
c9bf8592-c08d-5316-bb18-160a3df6be87 | note | Record of conformity - Aconex Sign off
86c48c51-5b11-53ec-8c30-3f290786b3b5 | note | HP
da4ae08c-fac7-5e47-93e1-6f347419f540 | note | Responsibility - Project/Site Engineer, Principal’s Representative
7786b41c-8d21-537b-9856-adcc3eb88695 | note | Principles Rep - Aconex: BecaCPL-GCOR-000810
58f6c910-c461-5b65-a59d-decf015fc5c0 | date | Date Completed:
d887b5c3-5f02-5d22-ace4-5123e7694541 | signoff | AUTHORITY HOLDPOINT
ce085ba5-14a6-5251-aa31-3e4c7b381a10 | checkpoint | 2.5 - Provision of Material Samples
f34ea86e-e126-502d-b7d8-799a4d4501b1 | note | Frequency - At Least 5 Days Prior to works
dd7bb70d-a2b5-55c9-94b4-8dfc76fad08d | note | Acceptance Criteria - Principal Contractor to physically handover reference samples to Principal’s Representative of the approved CTB material. To be truly representative, the reference samples will be taken straight from the supplier of the material.
0c874d56-cf4b-5428-a181-0fb5c3e72280 | note | ○ The reference samples shall be divided into two representative portions, with one being held by the Contractor and the second portion by the principal until completion of the Works.
a7eaa790-89eb-560b-bb6a-42b034b9f4b6 | note | Reference Documents - Spec cl. 5.21.1.2
4123a350-addc-57f1-bedd-545a3336c7ad | note | Inspection/Test Method - Verify
e3479ff3-9d0e-5684-8e1e-0bf3b53ff2f0 | note | Record of conformity - Handover of Reference Samples and Aconex sign off
da9049f6-a774-5ab7-b2b1-03431ba9fadc | note | HP
92c0e4db-5ee2-5bbb-a183-8fea440ae72a | note | Responsibility - Project/Site Engineer, Principal’s Representative
ba3782a7-3abb-5d95-b86c-c78ef690149a | date | Date Completed:
ce0e26d2-cdbc-5212-b7b6-711abae7313d | signoff | AUTHORITY HOLDPOINT
3a93befc-813a-54fa-93e6-ed544f594f7e | section | 3.0 - Placement of Cement Treated Base
e6432367-fc0d-5d29-92fc-3e7e2637f723 | checkpoint | 3.1 - Subgrade, Basecourse Preparation
1d26deef-fe2e-5fdb-a424-a3909955245a | note | Frequency - Each lot
90173b31-4a14-50e9-93e3-3fed40bb5797 | note | Acceptance Criteria - Existing surface of subbase is maintained in compliance with tolerances on surface smoothness and level. The subbase is clean and clear of any foreign matter before the placing of the CTB.
c310d359-b226-5439-8830-9bf651637b3d | note | ○ Principal’s Representative will be notified 24 hours prior to the placement of CTB to allow the subbase to be inspected prior to the placement of the CTB. This will be recorded in ITP009 – Unbound Pavements.
65fd1623-8231-5854-aa9f-5cda3e8b9715 | note | ○ Principles Representative to be notified of the intention to place CTB.
b1ae7aca-a8e4-5915-b171-70d23878625f | note | Reference Documents - Spec cl. 5.7, Spec cl 5.9
35910732-4634-5050-a1f3-a7e82e567390 | note | Inspection/Test Method - Visual Inspection
a9a3fb03-d34e-5643-aeab-c7f7c06b097d | note | Record of conformity - This signed ITP
0061e970-f3a6-5f64-861d-4a3562876699 | note | HP*
b5dc517c-d7f8-5f6b-b8b0-6a317bdab769 | note | Responsibility - Foreman, Site Engineer, Principal’s Representative
de55df49-5ade-5de7-908d-27572a37eefb | date | Date Completed:
d5f5265f-9acd-5150-85f4-b8e0fd5c4c1b | checkpoint | 3.2 - Layer Placement Parameters
15d20a59-abb9-5a63-bbbb-ae10c247e7e7 | note | Frequency - Every Lot
a7549654-01da-5468-98c6-45fd6149d6b2 | note | Acceptance Criteria - Summary of Parameters for each Lot;
9b307856-48e1-5148-b00c-36535f9c5285 | note | ○ A lot is defined as one layer placed in a single days production of uniform material
443263a8-e71e-5b88-afb4-8b92e59bb419 | note | ○ Max Layer is 200mm
bed1a5bc-d098-5239-b2e4-030a8525d7c3 | note | ○ Min Layer is 100mm
187f4fc7-665d-5338-8487-8e92b1d07d02 | note | ○ Final Surface Level +0mm, -10mm (excluding intermediate layers)
7171547a-ee6b-53d6-b20f-7d3ad0a0d8c9 | note | ○ Shape: every 10m intervals, <7mm deviation over 3.5m straight edge (excluding intermediate layers)
01ea9862-06c3-54c0-8365-67d7ef6c4f5d | note | ○ Material is batched within 1% of OMC
154ea760-0093-5671-9a15-c4fb065e211a | note | Reference Documents - Spec Clause 5.9
23e30d10-91f9-5caf-bf9a-50c0b7a25197 | note | Inspection/Test Method - Visual Inspection
e3db2985-1629-55b1-86de-615aa90f8bca | note | Record of conformity - This signed ITP
92da49e6-752c-58e5-a3a5-368767d9eadc | note | IP
131f5628-0346-5a4c-830c-ee5d14e15223 | note | Responsibility - Foreman, Site Engineer, Principal’s
cc2418e7-c804-5128-ace2-e40bde4c6554 | date | Date Completed:
a791ad98-de04-56f3-baea-854bfe3fec6e | checkpoint | 3.3 - CTB Placement – Weather
a8945776-a6f4-5b36-b3fe-925c329ce3df | note | Frequency - Each lot
527d722b-c5b1-574b-81b0-1a2b37349e23 | note | Acceptance Criteria - Weather to be check prior to placement, CTB shall not proceed when;
8b6f23cb-bdd6-52db-9b80-19f7c3a85136 | note | ○ Ambient temperature is below 5°C
b5a25fd6-d1a7-555c-a444-784f86bdf94d | note | ○ Temperature is over 35°C
abb0ce29-4364-5f04-86af-c2c1030115d2 | note | ○ Heavy Rain fall is forecasted
e8bd97b5-51ed-58e4-b56f-93694ea86fc5 | note | Reference Documents - Spec cl 5.18
17631fb5-c95b-50f9-96d9-c8cb7cd5a4ae | note | Inspection/Test Method - Visual Inspection
d44b3070-6831-5703-af8f-496e3889538e | note | Record of conformity - This signed ITP
77032644-9c84-5d86-8fa0-8438ebe70d20 | note | HP*
19904e0d-6cd6-551f-af45-e992a7ccbd14 | note | Responsibility - Foreman, Project/Site Engineer
ccba4635-1cdd-5b1f-84fb-6f07cec24b9c | date | Date Completed:
a990dc3f-4e0f-51d5-8138-9ebb78589eff | checkpoint | 3.4 - CTB Placement – Checks
1bb2aa2a-c4ff-561d-a13d-7afbe13bc904 | note | Frequency - Each lot
32f8ef17-8490-50c9-9251-810682a3751a | note | Acceptance Criteria - During CTB placement Activities check;
40f02693-c8d1-535f-a199-ece05f6f73b8 | note | ○ Placement starts on the high side or crown of the layer where practical
048bd7c5-c004-55da-9bc4-93e115f79601 | note | ○ Material is spread in the direction of Taxiway across full width
4f433ccd-ee6c-524f-b818-eae38e7377da | note | ○ Underlying layer is not disturbed during deliveries
d08de34c-ea7f-583a-b415-47e596003fb9 | note | ○ Inspect Material for any contamination through placement activities
a61ff818-105d-5a4e-8680-ff9d042ce44a | note | ○ Adjoining layers are a clean face / vertical
8df5403a-2649-51c2-a3ad-c7303e4bb19d | note | ○ Segregation does not occur
b355b70a-b0ac-5a92-b3ac-1b8a400fe4a1 | note | ○ Placement to be completed within 120 minutes from time of batching and before concrete has obtained its initial set
f4942690-8cd5-558c-9f3a-44274fe159c5 | note | Reference Documents - Spec cl. 5.9 AS1289.5.2.1
b574633f-2bb1-5d4e-950e-ff2484b56389 | note | Inspection/Test Method - Visual Inspection
60226c75-b0de-5c5b-96e9-8673327b422c | note | Record of conformity - This signed ITP
b828ff37-ec7f-50be-94b1-ee32fc7cc07b | note | IP
d1b766ef-1c08-5b21-b039-7f9ab4683bf1 | note | Responsibility - Site Engineer, Foreman
2654885b-329c-5964-89f4-e465307a4a9b | date | Date Completed:
7401f6c4-9bed-5d6f-b4ec-db03b8a866c1 | checkpoint | 3.5 - CTB Compaction – Checks
d318849b-5618-597c-91b3-814e52d4f0e1 | note | Frequency - Each Lot
ae30e580-e65b-59b1-93b6-ceb7450cd2f2 | note | Acceptance Criteria - During Compaction check;
b10036b6-d4c3-53e6-a7dd-623f106280d5 | note | ○ Heavy smooth drum roller of 15t to 20t is used for initial compaction
d1f1c126-533a-5e6a-8dc4-2e235688e671 | note | ○ Pneumatic roller of 27t will compact material for final consolidation.
05876ce7-e80b-5055-948b-92633bd9b857 | note | ○ A heavy smooth drum roller (in static mode) may also be used for final consolidation
8a9f03d1-75fb-512e-bbdb-7318c1488415 | note | ○ Watercart present onsite for conditioning
65490f31-31f1-55fa-ba27-62cb0064acd3 | note | ○ Materials are trimmed to required shape and level
18e147eb-3edb-5867-bda3-b7734942fa05 | note | Reference Documents - Cl 4.10
a5cc52f2-9ea2-51e1-9d76-86f779782816 | note | Inspection/Test Method - Verify
4ed1fdbe-a813-5556-8b34-fa80b91e4a55 | note | Record of conformity - This ITP signed
d2cb62fd-45c5-53ba-a041-c81c964b747c | note | IP
8ca58966-39f3-51c1-9bf7-7cfb7924a9f8 | note | Responsibility - Project/Site Engineer
7d2e2bd3-99ca-5153-891e-45c4cf8e6ee3 | date | Date Completed:
2bddfd15-ae28-5cbe-bfb1-25a7421f7b98 | checkpoint | 3.6 - Curing & Protection
d9202bed-4ccb-5e6c-8eae-441e32bd0d2a | note | Frequency - Each Lot
3d18e78a-fbc1-525b-822e-0dad77056df3 | note | Acceptance Criteria - Curing to commence as soon as CTB has been placed, compacted and trimmed. No plant (other than curing) to track across CTB for minimum 24 hours.
3ff88ce5-7c4d-55c3-8a20-b2077108bb2f | note | Curing to follow one of the below methods;
426e9ca7-487a-5f20-a6ae-ffdc3fd8f5d4 | note | 1. Wet Method: This will involve a watercart lightly spraying the CTB surface for minimum 7 days.
ac0408e5-01eb-511d-bec8-72574746a26a | note | 2. Debonding Coat: The CTB will be covered with a bitumen curing compound. In locations of PCC, will be the C170 seal with 7mm aggregate.
dcc282aa-d774-5d32-a21a-2340833e3a7f | note | Reference Documents - Spec cl. 5.15
c185cb39-41db-5b74-bf4b-58039a1d2486 | note | Inspection/Test Method - Verify
5ed27476-046b-5d4c-91f4-9d6dc280e91b | note | Record of conformity - This ITP signed
4127c5e4-b820-5275-befd-3ba282773570 | note | HP*
90a1f255-e2f6-5258-82f4-a6608d585ead | note | Responsibility - Foreman, Project Engineer, Site Engineer
b29214e6-d20d-57e7-b892-48164a53e9e0 | date | Date Completed:
6e009c69-70d7-514c-b44e-f3bb3867a1e3 | checkpoint | 3.7 - Post Placement CTB Inspection
c133101a-b607-579c-b4f9-2cf71ca93f9b | note | Frequency - Every Lot
a7f09b74-8c7e-5e9c-8c19-390ba5710f6c | note | Acceptance Criteria - Prior to the application of the succeeding layer or installation of the de-bonding coat, CTB final surface is to be inspected with the Principle Representative
3dd631f2-a2a1-571d-a620-d5d946c8b5bb | note | Reference Documents - Spec cl. 5.9
84554310-d991-5d29-82f6-a3c07c5d5599 | note | Inspection/Test Method - Verify
09e8586b-eca6-5d3a-a226-2bcb388209a4 | note | Record of conformity - ITP signed
5ccaaf5a-f383-5dcb-9802-a10733a58443 | note | HP
905e8200-14cf-53ec-a676-f2ddc9f34212 | note | Responsibility - Project/Site Engineer, Principal’s Representative
d7a8daed-5a8c-5363-9fc5-cd375d53fabb | date | Date Completed:
1fbbaaa5-dcbd-58a7-a340-05841913c755 | signoff | AUTHORITY HOLDPOINT
131e830c-80ee-5bfa-ae6d-3cee6331c53a | section | 4.0 - Acceptance, Compliance, Controls and Quality Assurance
99e681f2-8a6c-56a0-be58-12603b6f7477 | checkpoint | 4.1 - Field Dry Density
f03186bd-59c9-5281-b6ef-20321711d5ed | note | Frequency - Each Lot One test every 500m2 (or 250T) or part thereof
102f1ebf-e51b-5ed9-ad43-a0896478ebdd | note | ○ Minimum 4 tests for Lots under 800m2 (or 400t)
f5ceefec-34de-5727-916e-0b288c1aabd4 | note | ○ Minimum 6 tests for Lots over 800m2 (or 400t)
803c9230-1f43-5b08-9bac-c416ef40d10d | note | Acceptance Criteria - Average of Specified Minimum Dry Density Ratio (SMDDR) of 97% of the Maximum Modified Dry Density
0f72bb26-c4ac-5f47-9353-d47361c2c94d | note | – Average Equals or Exceeds 96% with no individual result be less than 93%. The lot will be accepted.
54e288c2-afc9-5831-bdd3-c814dbafdac1 | note | – Average Equals or exceeds 96% with a result being less than 93% - an additional 4 tests will be taken
7422857c-dbf4-5cde-8fcd-7a9eebb01ddf | note | – Average is less than 94%, the lot will be rejected
58937cc4-12d9-5cda-a665-45ab2a8da7e5 | note | – Average is in between 94% and 96% - an additional 4 tests will be taken
a9f58864-2561-54a2-bfa0-dab77c1e7259 | note | Reference Documents - Spec cl. 5.10, Spec cl 5.21.2.5
28029483-eb30-5e34-b3a9-ed80ee976a2f | note | Inspection/Test Method - Verify
71a6959e-311c-5755-aa07-77880c544a37 | note | Record of conformity - This ITP signed, Test Report Attached
16a6d560-db93-5e93-aac4-1ef0e3b58824 | note | TP
4d63e4ce-61af-549e-93cd-88e90439f6fe | note | Responsibility - Foreman, Project Engineer, Site Engineer
d729f33b-569d-5d94-bf25-bde0399b776e | date | Date Completed:
c083058b-dae6-5e3d-a513-cc68f715ae5a | checkpoint | 4.2 - Moisture Tests
48e1392d-43e6-58f5-af5e-7dedfde8269c | note | Frequency - Each Lot One test every 500m2 (or 250T) or part thereof
06c7fffd-057a-5683-a5f7-8a8c381a276e | note | ○ Minimum 4 tests for Lots under 800m2 (or 400t)
2b0ffe7c-a0d8-59f6-bebc-62ca95b1f694 | note | ○ Minimum 6 tests for Lots over 800m2 (or 400t)
ebec3e40-e3e6-5a4b-9711-f0369aaf6a53 | note | Acceptance Criteria - Target Moisture content of +/-1% for information only. Production of CTB to be within 1% of OMC.
b5ab453a-a9ac-5e01-bf8f-b88b1b412688 | note | Reference Documents - Spec cl 5.21.2.5
31eba2f8-121a-5f0a-9bbd-1df0d0fcd5d6 | note | Inspection/Test Method - Verify
1d86b1f4-11bd-5c0c-9580-e4d32aaf98f6 | note | Record of conformity - This ITP signed, Test Report Attached
6a896df5-fbe0-5c11-9572-3ea136c6b665 | note | TP
dd17bd53-ffd2-53b4-ac3a-23be9eb1f240 | note | Responsibility - Foreman, Project Engineer, Site Engineer
da840038-f33d-5214-8629-cc69fb864320 | date | Date Completed:
435a97a0-8348-5acf-b9b1-f34f54f87f6c | checkpoint | 4.3 - Strength Testing
27bc8c7e-95d1-5dcf-88ae-82823e1085d9 | note | Frequency - Each Lot, divided into four approx. equal sub-lots
2fddab20-aeb3-51af-80f7-3033426b797b | note | Acceptance Criteria - A total of 4 sub-lots will be taken as samples, with 2 being used for the 7-day strength testing, and the remaining being used for the 28-day strength testing. 28 day results are for information only.
53e841bf-eed4-57b9-9fbd-fd88b73d2b2a | note | ○ The mean 7-day unconfined compressive strength of the CTB shall be a minimum of 5.0MPa and a maximum of 15.0MPa. No single sample shall be below 5.0 MPa.
2750053b-5e5b-527a-927e-8e87f4aab69a | note | Reference Documents - Spec cl 5.11, Spec cl. 5.21.2.6, AS1012.9, AS5101.4
520a4d5f-8343-5414-af26-941844343fab | note | Inspection/Test Method - Testing
51ba2912-8e23-5929-9c94-7c2fc5b9173a | note | Record of conformity - This ITP signed, Test results
102a9d58-c7cf-58d9-a254-e2b57c059a11 | note | TP
62c9a368-385e-5f8a-a5fd-3173b78cbeb5 | note | Responsibility - Project/Site Engineer
cd63fc81-2748-5204-8c71-1ecdc8d7094d | date | Date Completed:
a63f0532-32bb-5725-9bef-0a20b43e1e13 | checkpoint | 4.4 - Process Control
c610b4ae-a285-5c6e-8fcd-207cb4c478c1 | note | Frequency - Each Lot
139d6cc6-0860-5d37-84ea-5eec2d18cc61 | note | Acceptance Criteria - CTB production and process control test results to be supplied to the Principles Representative
4cf57679-b162-55ad-abc5-71060624730a | note | Reference Documents - Spec cl. 5.21.2.1
a2362452-e6b9-50cc-8ab0-15193aa438e1 | note | Inspection/Test Method - Verify
6b11e16c-b89c-532c-8d84-0dde9b1f6e07 | note | Record of conformity - This ITP signed
f14b3625-4f6b-54d3-86cd-83ac17befadb | note | IP
cbabd8ff-86fb-5ea7-adaf-3d9bcd3a5cc2 | note | Responsibility - Project/Site Engineer
81b3934b-4a7c-5973-9a83-ac3ddb5484e9 | date | Date Completed:
2bcbf63d-6c13-5d63-acf0-f62700f979cb | checkpoint | 4.5 - CTB Layer Thickness
1799115e-1fc2-519a-85de-f01907f95ab3 | note | Frequency - Once Every 30m2
fb01f919-1253-50b5-bafd-444151f02c79 | note | Acceptance Criteria - CTB layer thickness to be measured, recorded, and included in the Quality Assurance records. No CTB layer thickness to be less than that shown on the drawings other than allowable construction tolerances
86aed6fe-a7e1-5bbe-b54d-a6febb6dcee1 | note | Reference Documents - Spec cl. 5.21.5, Spec cl. 5.21.7
1751b0ea-39bf-557f-a987-76db1c978ff5 | note | Inspection/Test Method - Testing & verify
8f655c65-eeac-573b-a41b-ff7a4763d512 | note | Record of conformity - Test results & this ITP signed
1edaa5b4-7fe2-53f7-904d-ef6ccb84713b | note | IP, SCP
440d35fd-e0b5-5913-b784-e8a1609522a6 | note | Responsibility - Project/Site Engineer, Site Engineer
eccb55c7-0a4e-5468-9b53-be60bc785e84 | note | Aconex Ref: DCWC Mgt-RTRFI-001329
8486d6a6-edbe-5b6f-ad1b-e3320c99b948 | date | Date Completed:
a65f8491-197d-5f8d-98e9-df0607f9802b | checkpoint | 4.6 - Quality Assurance Records
e28ad406-42b3-54df-bd45-1d533d8a6992 | note | Frequency - Each Lot
6bff1fb8-fc6a-5245-be5d-b0d34882f2da | note | Acceptance Criteria - Provision of ITP test reports must be submitted within 60 days after the completion of the Works. Principal contractor to supply electronic copy of reports detailing the results of the quality control and testing undertaken.
ff73a1e8-da4b-56d3-b9ad-dd3e0a5b5867 | note | ○ Reports to be transmitted on Aconex and Aconex Reference to be quoted as Hold Point Sign off.
901e3f69-22d4-5dff-a8fb-4777b97224e0 | note | Reference Documents - Spec cl. 5.21.3
dbe748d1-13fc-59a6-b11a-3fde2f3eafe5 | note | Inspection/Test Method - Submission of ITP reports
d186873f-c9c4-57e7-a8a6-10ef7c2b1f91 | note | Record of conformity - This signed ITP
ddbf53ba-4ba6-5162-a876-1db4a0b8cda0 | note | HP
6a8940a0-674a-51b8-a949-c153ebc3521f | note | Responsibility - Project/Site Engineer, Principal’s Representative
d26e1c20-cd8c-5956-8617-743c63ff978f | textbox | Principles Rep - Aconex Ref:
a6b55153-f7f0-5005-ad8c-0083e0fd459c | date | Date Completed:
ad2de4d9-5721-5145-9475-1d1edaefaba1 | signoff | AUTHORITY HOLDPOINT
39c190b7-b116-57f8-a2a7-da1cc234c6f0 | checkpoint | 4.7 - Survey As-Built Report
2275ba0b-0e87-5dba-a66e-9441454b85ae | note | Frequency - Each Lot
dbb59df4-c843-56b6-8c73-5f8a99b22177 | note | Acceptance Criteria - The surface level at the top of the final CTB layer shall not deviate from design level at the specified points by -10mm or +0mm. Contractor to provide Survey Conformance report of completed CTB surface layers per Lot.
61d1d193-4712-5f16-853e-4cf7e99a2d55 | note | Reference Documents - Spec cl. 5.17, Spec cl. 3.14.2
c5212fbd-57c5-5049-9e22-15468fa5c769 | note | Inspection/Test Method - Verify
b30b9298-b275-527f-83c5-0965084bdb9c | note | Record of conformity - Completed drawings, survey report, & this ITP signed
a9cbc0bd-f47a-5f26-81e9-5f5cb769aaf6 | note | IP, SCP
3d2bd58c-980e-593c-8704-511a08c99272 | note | Responsibility - Surveyor, Project Engineer
c5056a76-945c-5f08-b874-d76e1d320dbe | date | Date Completed:
0f7f576e-520a-5643-9fc4-f169fffc004d | checkpoint | 4.8 - Surface Smoothness
5d4acac4-2875-5596-93f5-1a785ba3e054 | note | Frequency - Every Lot
93786c44-4ebd-54d3-aca1-951acc07afb5 | note | Acceptance Criteria - Surface smoothness to be checked every 10m by placing a 3.5m long straight edged on the ground a checking any deviations over 7mm. Complete within 7 days of completion of each section. Document results.
91fb8cd2-d46e-5227-b807-708f1a461489 | note | ○ Intermediate layers and shoulder pavements are not required to be checked.
c01c18c5-37ba-58b4-a6a2-642d82ab94c0 | note | Reference Documents - Cl 5.17
58c12aac-2d98-5ac4-b686-7c9e9cfaa8e0 | note | Inspection/Test Method - Verify
ed18d16e-eb2c-55be-9c34-5b2c4fd34347 | note | Record of conformity - Report
3b7bb992-09a4-5bdd-9c10-fcc45ede27d4 | note | TP
f9ae33fc-2416-5f39-a778-8195e2fb3791 | note | Responsibility - Project/Site Engineer
effa941f-c08e-5def-b3a5-5ecdab676233 | date | Date Completed:
c801c62f-58a1-5837-8f7c-89512b249fce | checkpoint | 4.9 - Correction of Nonconforming Work
9ec784eb-353e-506d-9619-b27d85a09297 | note | Frequency - Each Lot (if required)
369bd2a4-9673-5e6f-b9a7-c89bb20602c2 | note | Acceptance Criteria - All CTB that do not meet all the specified requirements will be rejected by Contract Administrator. Materials to be removed full depth of the layer and reinstated, unless otherwise approved through the NCR process.
ac35cc23-2d07-57ea-aa08-9d3098856e40 | note | Reference Documents - Spec cl. 5.21.4
99ba277c-f48e-501e-89c3-e4675b0c7544 | note | Inspection/Test Method - Verify
55f90695-7572-5a0e-8395-fe465a26db9f | note | Record of conformity - This Signed ITP
db96ea5a-921e-5ed5-8c15-2a19c2d9a5bd | note | HP
6a3f2218-7f09-5a57-b7a7-c49b0d52d177 | note | Responsibility - Project/Site Engineer, Principal’s Representative
dba5f565-ca20-52ba-aca1-c9ea7c152251 | note | Principles Rep - (if required)
e18f55d4-6a0b-5027-bffa-6021233c4d87 | date | Date Completed:
a1f73c0c-47cf-52f8-abb9-28b1f1690f2e | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
f9a7189c-b860-50c9-ac40-38214720411f | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
2ed5916a-4453-538c-a5f9-3dc1b4870a03 | textbox | Print Name:
3b7bd65a-2e57-5fdf-babf-8993d668d7c2 | textbox | Position:
90d84dfb-f506-5b4b-b2a3-b1f9ce2894e4 | date | Work Completed On:
bbf80422-452e-53b5-8e68-f944166304fe | date | Date:
e6b8a30d-eb8a-5bbc-8c38-65aad60ce48a | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0013 - PCC Pavements - Rev 2 | itp | ITP013 - PCC Pavements
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
2907e598-3fa6-573d-bd16-0574524c85dd | note | Frequency - Prior to commencing works
b9918449-71ab-57a3-8fb9-16b7aa22b72c | note | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
e00f65c1-9d2f-5be2-a812-fb0d735c5f0c | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
fcc655b9-fbb7-56a9-a250-a3e6ddfcdac9 | note | Reference Documents - Current Revisions in Aconex or ACC
7c8e2404-1102-5ee8-a17e-bf5965da5090 | note | Inspection/Test Method - Verify
bbf512ae-8c96-50fe-ab8e-041fb46b2033 | note | Record of conformity - This ITP signed
50155e9b-2035-554f-a3b9-dc1292319b1d | note | HP*
c857cb14-757e-552e-a08f-8d2f33488cba | note | Responsibility - Project / Site Engineer
7985f0ba-6f2a-53e3-86b8-8d2bb4b8fa9e | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
f76991b4-2e34-58da-a5a7-07c02f17fe3d | note | Frequency - Prior to commencing works
c651df4c-8e29-5d2d-9375-da49ffe74cdf | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
48b636c8-8a77-5c74-8d2b-2a67f6f57838 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
396ec348-d33a-5b4c-8f22-e1c5c2acb765 | note | Inspection/Test Method - Visual Inspection
7cf37097-e48c-53c0-8bbf-4d645002a09d | note | Record of conformity - This ITP signed
811f2fa4-250a-5ede-9e06-77ba08912d60 | note | HP*
3d378ac4-0b26-56cd-9c2f-4fba1d62a6ed | note | Responsibility - Project / Site Engineer
91cced02-0c77-52ba-9865-19bd3dc69329 | date | Date Completed:
7e28438e-f51f-55d2-9f71-e8c9c5437afc | checkpoint-no-value | 1.3 - Mix Design Report Submission and Approval
4507ccca-25f6-5ce8-996e-f117534195a8 | note | Frequency - Prior to commencing works
5b39bd65-bb88-5915-86f4-2d1b0165bfb7 | note | Acceptance Criteria - Theoretical mix design and preliminary trial mix results submitted in a report to the Contract Administrator for review and acceptance prior to full trial mixing.
98bbfa8e-9bff-5a20-994c-001991a18233 | note | Reference Documents - Beca Spec 002 - 11.5.3
85cbfe58-d6b7-5804-b260-f5c730fa1f47 | note | Inspection/Test Method - Verify
a862afaa-1ec6-58ad-b24c-6eacb2fca986 | note | Record of conformity - Aconex Reference
cb6a07a3-cb1d-5b7a-a016-a5b1ac8a4d5b | note | HP
ab6e881a-aab1-5c9a-9521-b29a5139afc2 | note | Responsibility - Project / Site Engineer, Principal’s Representative
2d313683-5885-50c2-9eb2-66762b61c470 | note | Date Completed: 01/06/2024
3211cacc-9c39-5b9a-9514-0f07b88fe014 | note | Principal's Representative - BecaCPL-GCOR-000846
05fade62-fb69-5838-88b0-d4e2cca8452e | signoff | AUTHORITY HOLDPOINT
1d417a20-1781-524c-8f26-32728ee4d344 | checkpoint-no-value | 1.4 - Job Mix Formula
8b89fdfc-d9d1-527e-8a5a-973029e07bae | note | Frequency - Prior to commencing works
7614f9ac-8801-59ee-a747-c145e86ec76c | note | Acceptance Criteria - The Job Mix Formula must state the mass proportion of all ingredients per cubic metre of concrete. The allowable limits in the Job Mix Formula (when compared to the agreed theoretical concrete mix design) must be in accordance with Table 11-2 of BECA 11.5.4 (see notes section).
57149b72-6f59-5d04-86e7-4525b9b35b55 | note | Reference Documents - Beca Spec 002 - 11.5.4
b51a7841-f170-5d47-8f36-c8cd85564a64 | note | Inspection/Test Method - Verify
503bc281-5ed7-58d1-aa06-fb549f758ad5 | note | Record of conformity - Aconex Reference
93011ee0-68cc-5e96-bafe-17d75aa2198c | note | WP
5375edff-176c-5d66-988f-1c14a5004c0b | note | Responsibility - Project / Site Engineer, Principal’s Representative
71a389be-f505-5ac1-9f06-a680d8c8848e | note | Date Completed: 30/05/2024
e0d8cbf6-790b-5a21-8182-cc284a5187fa | note | Principal's Representative - BecaCPL-GCOR-000839
ea2ed3cc-4240-5302-a62f-08cf18713d1a | checkpoint-no-value | 1.5 - Production and Construction Trials
e5fdbc46-719d-5942-8304-c39bd3e2059a | note | Frequency - Prior to commencing works
19475a37-83f9-5590-bea2-9dc4e0ea4477 | note | Acceptance Criteria - A production and construction trial must be completed as per the requirements in the specification.
1b130452-3c22-5b57-96d2-d425c83968d6 | note | ○ The results, control procedures, construction methods and completed trial pavement will be presented for review and approval by the Contract Administrator.
468ed8d3-72e9-5e5e-9e7c-4cd84000cb62 | note | Reference Documents - Beca Spec 002 - 11.6.1 to 11.6.4
4077b7bd-82bc-5ac9-8abf-482efd9b2c4b | note | Inspection/Test Method - Verify
df708af5-9f11-534c-af7d-32a465b86af9 | note | Record of conformity - Aconex Reference
528f6782-a3f3-5bce-bf62-414e8a0aa3b5 | note | HP
08bcb58d-ea03-5f6c-8d87-068ee9a666c4 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a044b821-045c-516d-806b-4adbf19eae93 | note | Date Completed: 19/08/2024
3f498654-9c27-5215-b0b9-26044de9c986 | note | Principal’s Representative: DCWC Mgt-GCOR-009917
73453e67-147f-57a2-8c4e-a327bf10ac4a | signoff | AUTHORITY HOLDPOINT
e5f4e390-d859-5bb8-8754-88a6610c4a41 | checkpoint-no-value | 1.6 - Curing Compound Material Submission
9b855dfe-dcaf-5780-a60c-3107674b9ed2 | note | Frequency - Prior to use of curing compound
83186ab9-3183-5a0d-8af9-d95cee37cc97 | note | Acceptance Criteria - Membrane curing compounds shall be a white pigmented type confirming to AS 3799, Type 2. Wax based compounds shall not be used.
f420a157-3565-5505-8230-a10228b203ee | note | ○ No compound shall be used without written approval by the Contract Administrator.
25cd7b38-ee48-596d-b07d-17fa9f379210 | note | Reference Documents - Beca Spec 002 - 11.4.11.1
60e9e8c5-b8ed-5bd9-a26e-3382693460cc | note | Inspection/Test Method - Verify
c0fd41e0-1e99-5cb1-b48f-4c618b1231d9 | note | Record of conformity - Aconex Reference
725ec045-95ca-572c-9b4e-9c371e3ec53f | note | HP
f35c5635-fb93-5f33-b60d-c63641ec0278 | note | Responsibility - Project / Site Engineer, Principal’s Representative
696d3ed0-b889-5758-aec5-19902ec4d780 | note | Date Completed: 22/05/2024
a818c49e-eaec-5a25-8530-c20a4d5b18bd | note | Principal's Representative - BecaCPL-GCOR-000791
cae769b2-61e3-5ca9-9808-11d45f78e1b4 | signoff | AUTHORITY HOLDPOINT
ba929a80-28cc-56d4-987f-a6898a2999b4 | checkpoint | 1.7 - Impermeable Blanket Material Submission
761302c5-7075-519c-9d7b-694b9d82823c | note | Frequency - Prior to use of impermeable blanket
b5091c95-16c2-5ef1-a417-df9805b7c0ab | note | Acceptance Criteria - If required to be used, impermeable blankets shall comply with the requirements of ASTM C.171.
db67cc05-0893-5f00-99ff-d92e8f8fca9b | note | ○ The blankets shall have sufficient strength and weight to meet the required conditions of service and shall be approved by the Contract Administrator before use.
46bd5aaf-a712-5584-9956-c7ddf7e3671b | note | Reference Documents - Beca Spec 002 - 11.4.11.2
40d7a594-43f0-57e3-8f8e-430fd5f4061f | note | Inspection/Test Method - Verify
6af78c57-3fbc-5181-a1c9-23ad09bdf0ba | note | Record of conformity - Aconex Reference
bb338aed-f7e8-569f-995d-e97baa3ee2b6 | note | HP
4768e536-db22-57da-8f25-3e8dfeda92eb | note | Responsibility - Project / Site Engineer, Principal’s Representative
fdd17bfc-d0c1-55b5-88b6-5f825b05769a | date | Date Completed:
6c2414bf-bba4-528f-9da8-08464c25f39d | signoff | AUTHORITY HOLDPOINT
5885abc0-a77e-5d54-803d-3fd1515e6818 | section | 2.0 - Pre-Placement Activities
16ee8263-a125-5876-ab26-79db8c104fdd | checkpoint | 2.1 - Formwork Installation
65a8de96-f184-5a0b-af0f-2fd24a991fb5 | note | Frequency - Prior to placing concrete
1f1a7b28-fea3-5aa9-b6c2-a714d1d257f5 | note | Acceptance Criteria - Formwork must rest firmly on the base to eliminate gaps and ensure no leakage of concrete will occur during placement.
a5ca7930-6074-5fd1-9a44-03273fc974f8 | note | ○ Formwork must be secured into position and locked together during placing, spreading and finishing of the concrete.
1e88b2e3-5eaf-5da0-8afd-bc24150e6b21 | note | ○ The top of the form must not deviate by more than 3mm from the required level.
2f868783-cb5a-598f-8cfa-65f1caec0add | note | ○ The form face shall be vertical and not vary more than 6mm from the required alignment.
31c77cba-682b-53dc-87ae-5baea14f37a7 | note | Reference Documents - Beca Spec 002 - 11.8.1.1
6ef34b37-ea17-5ff3-ae4b-e99491dfaaaf | note | Inspection/Test Method - Visual inspection
a9ebca94-422a-50d0-83cf-12869d540e0b | note | Record of conformity - This ITP signed
f249917f-23af-5d15-86c4-a29b6426d2d9 | note | WP
5b8afdc5-c63f-53f0-a861-23a7b328949e | note | Responsibility - Project / Site Engineer, Principal’s Representative
7409513b-e0b7-52ca-8954-8936dd8759d3 | date | Date Completed:
fd1f1b65-94f0-536d-a050-a134453028a2 | checkpoint | 2.2 - Pre-pour checklist
ab32c07d-9a9d-53ce-b9b5-123154b34553 | note | Frequency - Prior to placing concrete
18c8a68c-2470-5f7a-a086-63658f6c6540 | note | Acceptance Criteria - Completion of the pre-pour checklist: CL013A – Pre-Pour Checklist which details various checks required for formwork, reinforcement, joints and the pour area.
b28cd113-7abb-5137-9cf8-2b694ff03494 | note | Reference Documents - Beca Spec 002 - 11.8, 11.10, 11.13
be572c26-123b-5025-998f-2abc96f9640b | note | Inspection/Test Method - Visual inspection
d984894d-908e-5b6f-ad12-8ad9faed8fba | note | Record of conformity - CL013A, This ITP signed
d8b6310c-914c-575c-865b-9033ff0b5181 | note | HP*
7a14446c-e20a-5723-ad87-0f7c48d3e202 | note | Responsibility - Project / Site Engineer
ae723b76-57c3-5197-94af-ab6ad7d4b3a6 | date | Date Completed:
ca0fa0ec-49b6-5c2d-9237-de158062e778 | checkpoint | 2.3 - Pre-pour inspection
0d5d906e-fcbc-570f-9189-0a7d6e0ee14a | note | Frequency - Prior to placing concrete
36f2b982-f113-5f64-af91-09c84a5c2070 | note | Acceptance Criteria - The area in which concrete is proposed to be placed shall be inspected and checked immediately prior to commencement of placing.
95f8d6ff-6ebc-58a5-82a5-cc48c697c8d9 | note | Reference Documents - Beca Spec 002 - 11.9.1
ec12b8e5-7bac-50e6-a482-57ff3e913491 | note | Inspection/Test Method - Visual inspection
4a0db4bd-ded3-57d5-a929-3ed0243e8d0e | note | Record of conformity - This ITP signed
851d29f9-48e1-59c4-915c-64990356ff5b | note | WP
74492460-66c9-548e-ae28-8c4b837302a0 | note | Responsibility - Project / Site Engineer, Principal’s Representative
39c274b1-0ec0-570d-bc94-d540fdbfb401 | date | Date Completed:
d9388486-1250-5ff8-b9ad-8d44105f357b | checkpoint | 2.4 - Weather Forecast Checks
d43c1ab9-5201-5007-b19e-cb14e0ad0be0 | note | Frequency - Prior to placing concrete
0a8b717f-0ec7-5292-8236-466654675c31 | note | Acceptance Criteria - Check the weather forecast for unfavourable conditions (rain, wind, hot weather or cold weather) on the day prior and immediately before confirming
ed0bef5e-c778-5d14-9786-2791f8899413 | note | Reference Documents - Beca Spec 002 - 11.9.5.1
c980c01d-b749-5c67-a48b-015656e8fe01 | note | Inspection/Test Method - Verify
5740e4c3-89c1-5bdd-a073-809a08fe31b8 | note | Record of conformity - This ITP signed
a2371590-dbcb-552a-9f00-aa021e745a5c | note | HP*
20538a2e-8184-5d34-a5e7-dbca391524b0 | note | Responsibility - Project / Site Engineer
10ba42c8-0df4-561f-89da-75552b10f2ca | date | Date Completed:
cd1921f5-0447-55dd-a906-346b6c56d7e0 | section | 3.0 - Placing Concrete
4ce1dbde-921b-5f12-92f2-cb172108eb2c | checkpoint | 3.1 - Place, Spread and Compact Concrete
7665b879-a2be-524d-ac3e-ecf0582e021e | note | Frequency - Each concrete pour
723f9130-2ba8-5f32-8090-706d2a025af7 | note | Acceptance Criteria - Concrete placement must be at a rate appropriate to achieve a consistent high quality resulting pavement.
80257cee-5638-514e-a8ff-24d1c99ba788 | note | ○ During placing, the concrete must not drop freely by more than one metre onto the base of the paving lane.
ede5d52d-6d18-5925-a3b4-ed8eb0fbe3a1 | note | ○ Concrete shall be placed uniformly over the width of the slab and in a way to minimise segregation.
fb7bb21a-0517-5585-8cba-f749e3db01cb | note | ○ Concrete to be adequately compacted by internal mechanical vibration.
47ad46e2-d1bd-59d1-992d-bbe52b4d9cbd | note | Reference Documents - Beca Spec 002 - 11.9.1, 11.9.4, 11.11.2.1
638de61b-8375-576b-9262-504c09b1a131 | note | Inspection/Test Method - Visual inspection
39a74bcb-e849-515c-9206-afe7bbf2cd12 | note | Record of conformity - This ITP signed
73d72013-09b1-5d43-9fe7-bab4cde0554c | note | IP
bc0e21bc-775d-5d51-b0cb-529089e2bd84 | note | Responsibility - Project / Site Engineer
4fad147d-594c-5d20-96cf-f52b3f9b9d35 | date | Date Completed:
01340969-6666-50d8-81f7-9de3ba0476a1 | checkpoint | 3.2 - Concrete Deliveries
8246b40e-a538-5ae2-a7e5-ff27722c2f97 | note | Frequency - Each concrete pour
ff9bb630-b1de-5601-afdb-7766627168d9 | note | Acceptance Criteria - Each concrete delivery to site is to be recorded on CL013B – Concrete Pour Record Sheet.
c719bd61-97e4-5c4c-84ed-af3fe5c02149 | note | ○ Concrete shall be placed within 90 minutes from the time of batching and before the concrete has attained its initial set.
fb71dde1-c897-5894-867b-60edb818ef6e | note | ○ The pour location, direction and order to be recorded on CL013C – Load-Batch Traceability.
04107314-7b34-53c4-8165-e6655e2e25de | note | Reference Documents - Beca Spec 002 - 11.9.1
1ad59df4-04e9-5aaa-acc6-fcecf0a20d1e | note | Inspection/Test Method - Verify
3945ca57-c77b-5137-bdc3-c380e553e0df | note | Record of conformity - CL013B CL013C, This ITP signed
b03e5d32-467f-5422-9751-5cd135c27c28 | note | IP
45e148b9-6d9b-5f88-a000-ad7e6419a0c2 | note | Responsibility - Project / Site Engineer
ba507cfd-70e3-534c-bfd9-36d529c0cfe7 | date | Date Completed:
a8846c82-3dab-5b97-8463-d576a7c411cc | checkpoint | 3.3 - Evaporation Rate
620b32c5-666d-5ac5-9d40-c190badf7dab | note | Frequency - Each concrete pour
65d8d07b-bb3e-5b85-89c1-9dcc1f61a1be | note | Acceptance Criteria - Concrete must not be when the evaporation rate from the surface of unprotected concrete is in excess of one (1) kg/m²/hr.
5245a27c-ae3a-572e-82a2-c0a5168e075d | note | ○ When the evaporation rate exceeds 0.6 kg/m²/hr, precautionary measures to prevent plastic shrinkage shall be taken.
1f0914c8-b9e4-5490-8cb3-4394352605b4 | note | ○ Evaporation rate to be recorded on CL013D – Rate of Evaporation.
a658725f-486e-574f-83ff-b8cc2eb40700 | note | Reference Documents - Beca Spec 002 - 11.9.5.2
1f4e2277-f1ef-5141-bc8f-dd05fc26f7a0 | note | Inspection/Test Method - Verify
f76b01c6-bd98-5ff3-9e87-82bc36a34708 | note | Record of conformity - CL013D, This ITP signed
3e4d1077-a8f0-5a0f-9fa6-30268bc119ef | note | IP
acaccec8-ef2c-51a4-a20c-aef89753f903 | note | Responsibility - Project / Site Engineer
cb08b5a5-0abd-51b0-8c20-fdbdb49bb359 | date | Date Completed:
6bde1751-12a1-5704-bd61-b45ba632ac70 | checkpoint | 3.4 - Hot Weather Concreting
744e946e-f126-5621-9e7e-a4972f3ef9ba | note | Frequency - Each concrete pour
a1e7bd7d-1f73-5185-bd3f-77e0967bec30 | note | Acceptance Criteria - Undertake additional precautions when placing concrete in hot weather.
7d9e13d6-291a-5804-8258-3aaced05a93f | note | ○ Ensure the concrete is placed at the coolest temperature practicable – the concrete temperature should not exceed 32°C.
78f48efa-0ae5-5dc1-8f31-3313b3109889 | note | Reference Documents - Beca Spec 002 - 11.9.5.3
d831f3f8-c332-5686-bda4-38c911c66549 | note | Inspection/Test Method - Verify
10d0b85b-3d61-5194-8f9d-e39d2c381564 | note | Record of conformity - CL013B, This ITP signed
4807115e-733f-50c1-b298-52829bceea88 | note | IP
37c77533-2901-5453-b540-56df0c72adc4 | note | Responsibility - Project / Site Engineer
60155a52-54ab-55ff-9c03-8d923452d239 | date | Date Completed:
0a674bc7-9c0b-59d4-b89b-165fe5156d0a | checkpoint | 3.5 - Cold Weather Concreting
b46d4377-743b-5e2c-9a62-72656b686c51 | note | Frequency - Each concrete pour during ‘cold weather concreting’ conditions
7fe02ad8-3085-5f3a-ad2a-0d86841ffc75 | note | Acceptance Criteria - Cold weather concreting applies when placing concrete when the temperature of the air, aggregates or water is below 10°C.
d01a9e14-2976-5bf7-af7e-f001c89aa7a4 | note | ○ Placement of concrete can only proceed if the ground temperature at the concreting site is greater than 5°C and the temperature of the concrete is not below 10°C.
14bec05b-75b6-5cbd-8313-7107a72b00fb | note | ○ Refer to checklist CL013E – Cold Weather Concreting for ground temperature records.
2c83eea4-ede8-58de-8a96-8fdc2ca50a2d | note | Reference Documents - Beca Spec 002 - 11.9.5.4
5400d6da-e277-5552-934d-295719475b4a | note | Inspection/Test Method - Verify
0cf4e0f5-f7b0-591c-a4bc-a74cc1925e3f | note | Record of conformity - CL013B CL013E, This ITP signed
f7ee5f93-57e9-570b-80b5-7e193fd5587f | note | IP
4121e0e9-6a3c-5dea-90e4-8dea93d0437c | note | Responsibility - Project / Site Engineer
16188178-5de4-56d5-bf57-fb2443ec071b | date | Date Completed:
bce17218-2b32-50e2-99bf-8851b7031e92 | checkpoint | 3.6 - Concrete Surface Finishing
b26ed40c-f7fe-5c69-a471-0ad5980c219a | note | Frequency - Each concrete pour
3dd3cb8a-4d02-5a4b-a302-32045875d4e6 | note | Acceptance Criteria - Finishing operations shall compose transverse finishing, longitudinal straight-edge finishing, floating and broom finishing, in that order.
53be0521-6bdd-50fc-b99c-5d2a91eb7f37 | note | ○ Finishing operations must be started immediately after compaction of the concrete and completed as soon as possible but not later than 90 minutes from the time of batching and prior to the concrete attaining its initial set.
2ba31877-3f8d-5551-bf43-08e177e81c36 | note | Reference Documents - Beca Spec 002 - 11.11.2.2
e09b32d0-416e-5346-9c9b-1220537934c9 | note | Inspection/Test Method - Visual Inspection
6e7e4584-a8b0-595f-a24d-de612f1127a2 | note | Record of conformity - This ITP signed
ad934164-50ae-59cb-98b2-675b58179b25 | note | IP
699e0910-0d47-5413-9c83-c52b19be34c6 | note | Responsibility - Project / Site Engineer
6abdad8c-dc11-55fd-8218-36822687b6ab | date | Date Completed:
d4da5116-30ab-56c9-b1eb-849f5003fc96 | section | 4.0 - Sampling and Testing Concrete
43ff8655-1595-5766-8438-ea3569c93eaf | checkpoint | 4.1 - Slump
e7dc755c-ff25-50ee-96af-ff0dab3dcd19 | note | Frequency - 1 test every 2 trucks
9fbac8e6-40ae-5a64-ae00-e85f95490dd9 | note | Acceptance Criteria - 60mm +/- 10mm
1e1c2738-c8ef-566d-b4ef-c0a06b1b95d1 | note | Reference Documents - Beca Spec 002 - 11.24.17, BecaCPL- GCOR- 000846
631b6b02-f4ee-54f6-aab2-f4606e4be2b8 | note | Inspection/Test Method - AS 1012.3.1
6e0d6122-3d83-517b-9fb4-9810dfb73c77 | note | Record of conformity - NATA Test Certificate
3799165a-793c-5f52-9e99-1bc8e66aa85d | note | TP
f33f7e7f-5c6b-5a6f-90b3-368d440763fa | note | Responsibility - Project / Site Engineer, Laboratory Technician
edc8ffe1-57f1-5325-886e-40e630995883 | date | Date Completed:
df8751f1-b783-5ced-bb43-a84f6efb9e3e | checkpoint | 4.2 - Temperature
0c42cd12-866c-585a-869b-e826adc3da04 | note | Frequency - 1 test every 2 trucks
92d7b2a7-237c-52b8-badd-e661cea05acb | note | Acceptance Criteria - Minimum 15°C (except in cold weather concreting where minimum is 10°C)
1ac66703-6f4b-5503-a481-2cd5bf33c432 | note | ○ Maximum 32°C
065863ac-e20e-5236-a611-2c120f585201 | note | Reference Documents - Beca Spec 002 - 11.24.16
867d37cd-753b-5c5e-baa0-37d9c5934684 | note | Inspection/Test Method - AS 1012.3.1
ecc7394e-9e35-58b5-b477-c08cd31a0447 | note | Record of conformity - NATA Test Certificate
be4204fb-85e0-5c77-a84d-bf595ef132ea | note | TP
0b169908-fbcd-530e-a69b-735905db5c2b | note | Responsibility - Project / Site Engineer, Laboratory Technician
dd04c20d-b5c7-5091-8993-9cb5aee071da | date | Date Completed:
2ffe1a6e-8b66-57f5-bbd8-0c2e46eccdea | checkpoint | 4.3 - Flexural Strength (7 day)
506d83af-a213-50cf-bd4c-086b494c9637 | note | Frequency - First 5 lots: 2 Beams per 75m3 or part thereof.
d1c99a14-cafa-596a-96d4-30a78dab4373 | note | ○ After 5 lots: 1 Beam per 75m3 or part thereof.
4a796ae1-7593-5083-acbc-16b5ce896c8d | note | Acceptance Criteria - Results for information only
f079ae4f-0da6-55dd-8f57-d175df0f1741 | note | Reference Documents - Beca Spec 002 - 11.24.10
6f6c0f31-b5d0-51b0-b720-0309c7e52034 | note | Inspection/Test Method - AS 1012.11
909c13bc-855e-5784-919c-3711ccbebb19 | note | Record of conformity - NATA Test Certificate
85fe830c-74ec-52ff-b129-4a3ed94a9760 | note | TP
0c8466ea-46f8-563c-980b-4ccf33c2a639 | note | Responsibility - Project / Site Engineer, Laboratory Technician
7d92ade6-8787-586c-a9f9-909bcaec1671 | date | Date Completed:
f5e85626-3e87-51d9-b123-8dbe71828123 | checkpoint | 4.4 - Flexural Strength (28 day)
68bc7023-086e-52c4-a527-072e730877c5 | note | Frequency - First 5 lots: 2 Beams per 75m3 or part thereof.
25a96de9-b8aa-5d12-9823-ba69d74ca852 | note | ○ After 5 lots: 2 Beams per 75m3 or part thereof.
dc2be2b2-4f0f-552f-8dcf-b7bab6ae9120 | note | Acceptance Criteria - Mean of the pair of beams > 5.0 MPa Individual beams > 4.8 MPa
6f64e51f-d32c-5c63-8e3a-7d51f1de2841 | note | Reference Documents - Beca Spec 002 - 11.24.10
34161891-b4e6-5856-a5cd-40d95a043493 | note | Inspection/Test Method - AS 1012.11
3af3ca24-1695-54ac-ae7f-fbc32c179aab | note | Record of conformity - NATA Test Certificate
0da54949-117b-58bf-b3cd-c3583c3829b3 | note | TP
a3663f3b-081d-58c3-91a7-c63a62d9874a | note | Responsibility - Project / Site Engineer, Laboratory Technician
7eddf880-425d-5c79-88c0-4b9f42dd923a | date | Date Completed:
9e886210-4b93-5748-a95e-ad183ab45c95 | checkpoint | 4.5 - Air Content
beb5fad9-719b-5f31-9ca2-bbe8fea2632b | note | Frequency - 1 test per Lot
cce2068d-7751-5d08-b115-9c85be983a61 | note | Acceptance Criteria - 3% - 5% ±1%
cce38939-39dd-5930-b456-e385fde10ce4 | note | Reference Documents - Beca Spec 002 - 11.24.8, 11.24.9
4f873026-9a91-58f9-bd7f-32975b9c9630 | note | Inspection/Test Method - AS 1012.4.1 or 1012.4.2
96ae24eb-2d77-5f28-89c2-4f1dc3ced80b | note | Record of conformity - NATA Test Certificate
f0e67256-3950-55e7-a7f5-ff9fb9edfb96 | note | TP
c7616360-f69d-5c7a-a9a4-e385f182e23f | note | Responsibility - Project / Site Engineer, Laboratory Technician
eed76a32-8847-5b9f-bcd9-7ac60e6b2939 | date | Date Completed:
9ad6888c-fa3b-5efb-b8a6-dea67ddcb735 | checkpoint | 4.6 - Mass Per Unit Volume
249ca4b9-5f12-5647-bd16-61bb71132964 | note | Frequency - 1 test per Lot
914a1061-d7db-5862-80b3-2dc51c3bbd66 | note | Acceptance Criteria - Results for information only
d61bce60-4427-5438-a778-ac44dd2b9ac6 | note | Reference Documents - Beca Spec 002 - 11.24.9
56516493-bebe-5e10-94d5-968d50da156a | note | Inspection/Test Method - AS 1012.5
89fec65b-8936-51e1-b966-5a9bc9bb695e | note | Record of conformity - NATA Test Certificate
cea769a3-8529-5654-8e6d-9695b25c878c | note | TP
813e7f85-510e-53fa-b17a-6671485216dc | note | Responsibility - Project / Site Engineer, Laboratory Technician
7655c7ad-d1c4-5ddf-a170-5835f574c71f | date | Date Completed:
784088d9-4c0a-591a-bcd5-f66d2ffb7819 | checkpoint | 4.7 - Wet Analysis
343a3167-cf90-59c7-bf56-10568edf0ef9 | note | Frequency - 1 test per Lot
ed0a84e9-18b8-512b-89eb-0fa090f32c09 | note | Acceptance Criteria - Results for information only
a23c85d7-48fb-5dca-accc-8001ad078bf1 | note | Reference Documents - Beca Spec 002 - 11.24.9
b0493a50-ceb7-5173-b70b-785e23524ab0 | note | Inspection/Test Method - AS 1289.3.6.1
715add53-bd8f-5fd2-a2b2-69d474fbef00 | note | Record of conformity - NATA Test Certificate
79d6b9e1-35e3-5868-a636-e5b774e97e92 | note | TP
d74d9e31-040b-53aa-8098-f3eafa8096f7 | note | Responsibility - Project / Site Engineer, Laboratory Technician
c49d4dd6-001e-5b3d-acf4-c27d4f3d7767 | date | Date Completed:
21046b26-0f7a-50ea-a8d4-20fcdb40c85b | checkpoint | 4.8 - Concrete Core Analysis (Density & Compressive Strength)
44ef0abf-113d-5a24-b205-4a368131b77d | note | Frequency - First 10 lots: 6 cores per Lot
8dda6e55-4e3f-5481-a80c-36712dd44c50 | note | ○ After 10 lots: 1 core per 75m3 or part thereof
f698075e-11c4-5bff-b6a4-f3df2e4eb701 | note | Acceptance Criteria - Cores must be not less than 120mm diameter.
f121d421-0622-5526-b970-29ddf62c3769 | note | ○ Calculate the degree of compaction by comparing the density of individual cores with the average density of flexural test beams (exclude beams whose density is less than 97.5% of maximum theoretical density). Refer to notes section for acceptance requirements.
93ff3a2a-1e34-5537-a2c0-92305264f999 | note | ○ On third of the cores taken shall not be tested for density but shall be tested for compressive strength and results submitted for information purposes only.
8998f956-5b2b-5eba-abc6-3cc8f555afbd | note | Reference Documents - Beca Spec 002 - 11.24.12
81946f43-f32b-5770-847b-fca603623b71 | note | Inspection/Test Method - AS 1012.12, AS 1012.9
c579b5f9-7653-5159-950f-b218a132b5a9 | note | Record of conformity - NATA Test Certificate
d065c9e2-e7de-5724-81b2-3ff5c52b422c | note | TP
9d2eceff-0e85-554e-8aa1-6229bdbf671a | note | Responsibility - Project / Site Engineer, Laboratory Technician
59c3b69c-68da-5505-8ce0-3f8a9ece2c03 | date | Date Completed:
782b8ec4-e2e7-589a-bdec-0fe6bc056628 | section | 5.0 - Post-Placement
cf47b8f0-f88a-54c2-b407-91f44e2a654f | checkpoint | 5.1 - Curing
d935de30-5a7e-5f55-8a4c-05bb1a5194a1 | note | Frequency - Each concrete pour
0b1553ac-4ec0-5a8e-8d8f-f4260aefd946 | note | Acceptance Criteria - Concrete shall be cured by protection against loss of moisture and rapid temperature changes for a period of not less than seven (7) days from completion of the finishing operations.
40e0f672-c0b1-5de3-939a-86d62221b715 | note | ○ Curing of the concrete shall comprise an initial mist curing followed as soon as possible with continuous wet curing with hessian matting for the duration of curing period.
a2c4a646-91dd-5a03-97cb-f09b867f8363 | note | Reference Documents - Beca Spec 002 - 11.12.4
8441d7a4-4ca1-5d1d-b5a9-8246823633f8 | note | Inspection/Test Method - Visual Inspection
5ecbc6a7-bdf6-5d88-b7fb-dfe592caf6cd | note | Record of conformity - This ITP signed
da2577af-fbbe-5cc3-836f-f2db59d57582 | note | IP
d887255a-6945-5b74-8988-38edbf9405af | note | Responsibility - Project / Site Engineer
586a76b4-cd49-5ad5-9eb3-335564e3ab27 | date | Date Completed:
aa609089-ea6f-521a-b2a7-7cd41a2d5d49 | checkpoint | 5.2 - Cold Weather Concreting Concrete Protection
b72a3ea0-9cf3-54a7-beec-14b61b7a485d | note | Frequency - Each concrete pour during ‘cold weather concreting’ conditions
bf428b0e-8c96-580d-9b28-a5f2c3a1450c | note | Acceptance Criteria - The surface of the concrete must be maintained at a temperature of at least 10°C, for not less than 72 hours after placing and at a surface temperature above freezing (0°C) for the remainder of the curing period.
f9469610-5e96-5a78-922e-b7dee55d8e29 | note | ○ Concrete surface temperatures post-pour to be recorded on checklist CL013E – Cold Weather Concreting.
a429a458-d908-5b2c-ac3a-8f1ba931df5e | note | Reference Documents - Beca Spec 002 - 11.9.5.4
4f84e7fa-b264-5dfe-bca2-9a95248c0896 | note | Inspection/Test Method - Verify
410a28c0-f2e4-5be6-9d42-669ddbe29548 | note | Record of conformity - CL013E
71518393-0ca3-58de-b30c-7e807bd704e0 | note | IP
148e7960-cfe8-5c7b-a158-389cc3f3c208 | note | Responsibility - Project / Site Engineer
bc31c826-5b56-59c5-9460-f2f09b4366fc | date | Date Completed:
82b7f08a-ab9e-5a58-be5c-738ceda7b9f1 | checkpoint | 5.3 - Inducement Saw Cutting
ba74ad63-a217-5659-8789-4213c2ef4104 | note | Frequency - Each concrete pour
9d64d094-2296-50a1-b47e-7ab9a78b0e8b | note | Acceptance Criteria - An initial 3-5mm wide saw cut to a depth of T/4 to T/3 where ‘T’ is the concrete thickness (generally 150mm) is performed along transverse contraction joints as early as possible post pour.
125b6f42-2b3a-58fe-b46a-92a76549fb7a | note | ○ The concrete must harden sufficiently to permit cutting the concrete without excessive chipping, spalling, or tearing.
1a776220-10f0-5a53-b868-97fef033431d | note | Reference Documents - Beca Spec 002 - 11.13.5.2
30288578-007f-585f-a161-4929011df0c2 | note | Inspection/Test Method - Visual Inspection
377ff993-cbe6-50a7-aa30-10d2d23a7839 | note | Record of conformity - This ITP signed
2b2e9676-0d95-5bfb-9060-7ae0fcc14764 | note | IP
ac9e5c42-5d54-51f0-92a6-47743e8b6671 | note | Responsibility - Project / Site Engineer
ec669d6c-1236-5ce8-b376-bbfb38d60b30 | date | Date Completed:
1415f254-48b2-52a5-8aea-2df0d8845449 | checkpoint | 5.4 - Formwork Removal
4c9f9ded-2540-5aa1-a9b7-1549da9de3ad | note | Frequency - Each concrete pour
c89af9fa-9c3c-5b89-9507-b7f0b4112f66 | note | Acceptance Criteria - Forms must remain in place at least 12 hours after the concrete has been placed (but no longer than 48 hours).
28e65d8a-e481-5fae-b3c1-156e31999afd | note | Reference Documents - Beca Spec 002 - 11.8.1.3
a1b1af8d-5887-5e45-80c8-c711f63c9273 | note | Inspection/Test Method - Verify
f4445baf-2265-5b77-9a96-a3717922e231 | note | Record of conformity - This ITP signed
5d0613f6-7e0b-5386-9b7c-f4e76151a0d6 | note | IP
6d4b2aac-9612-5e27-a9cf-153d627386ae | note | Responsibility - Project / Site Engineer
18f2ef5c-d133-5162-88cf-ce695de1233a | date | Date Completed:
69489b9b-1e23-57b3-b09f-8b123c4734fd | section | 6.0 - Completion
8fa0b7c0-e1be-5bfb-a603-8cd013fc6298 | checkpoint | 6.1 - Surface Smoothness Testing
55e7de99-3c61-538a-a173-cbdebe5c1754 | note | Frequency - Per Lot
0c6efdae-61ee-505e-af82-1add84557269 | note | Acceptance Criteria - The finished surfaces of the concrete pavements shall not deviate from the testing edge of an approved 3.5m straight-edge more than 5mm longitudinally and 5mm transversely. No ponding of water is permitted.
32222931-7dbf-5c57-a8be-fb36823b71be | note | ○ Points exceeding tolerances and any observed areas of ponding water will be recorded on ArcGIS.
8789dc0b-3a2a-58b2-89a8-c6643a4d1cac | note | Reference Documents - Beca Spec 002 - 11.14.3
9d59607b-536c-51a3-b9b8-f275e3994b93 | note | Inspection/Test Method - Visual Inspection
d920b062-aab2-5cc1-8472-ec4909ccab24 | note | Record of conformity - ArcGIS, This ITP Signed
2d893d27-0cfb-5e97-acd3-5a846b45f93c | note | IP
168e7066-b2f9-5912-8c30-42b0df934b3f | note | Responsibility - Project / Site Engineer
4799c1ed-759e-577d-acbc-1c9e9a389eb2 | date | Date Completed:
91cbcdd4-c964-5ba9-81ea-9199af3ff529 | checkpoint | 6.2 - Pavement Surface Levels
f7b31f9b-21d2-5bd8-8aca-6bac5928cc2c | note | Frequency - Per Lot
445217a3-704d-54d0-91f1-f47b50e14278 | note | Acceptance Criteria - The Contractor shall take levels on the finished pavement surface at the corner of each slab.
986af59c-af1b-54e1-b235-cc9960654cdb | note | ○ The finished surface levels taken shall be within ±5mm of the design levels shown on the Drawings.
54cd0821-1456-58c9-9edb-34ea1dfb4396 | note | ○ The levels shall be measured to an accuracy of 2mm.
2479533d-2d5a-5645-94a5-2f3915c91011 | note | Reference Documents - Beca Spec 002 - 11.14.2
7d131307-0cf5-5fb5-a872-6605679b0156 | note | Inspection/Test Method - Verify
30637c20-3975-54ca-b8e5-98e5838a8c78 | note | Record of conformity - Conformance Report
91934272-5c06-53f9-bced-b8f5a45c58a2 | note | SCP
942d3878-1a64-50ba-9f33-700d3f5365a2 | note | Responsibility - Project / Site Engineer, Surveyor
c89333bd-fc10-5caf-a06a-0387ff3ec9a7 | date | Date Completed:
4ea2f5f4-1037-54b8-98fd-5a7f56de6983 | checkpoint | 6.3 - Protection of Slabs
e0a272cc-8031-5c13-94e7-2c52940c54d6 | note | Frequency - Per Lot
ca4200e7-3811-542f-9623-95ab15582db2 | note | Acceptance Criteria - Concrete pavement must not be trafficked until 7 days old or early strength results are obtained. Steel tracked or steel wheeled equipment is not to be used.
d0d67642-8c06-5e46-8e83-6af9a4ec16ed | note | Reference Documents - Beca Spec 002 - 11.17
1981dabb-a7d4-56cc-a815-bb0ec0aac791 | note | Inspection/Test Method - Verify
d9f99ce0-fd9f-523d-b3b0-028767f2b5d5 | note | Record of conformity - This ITP signed
536c33e3-9e33-5297-a415-b849c3716a6b | note | IP
a9977ffb-173a-5f9c-a3fc-11de956a432f | note | Responsibility - Project / Site Engineer
5f06486e-2a73-588f-a366-13292ebceedf | date | Date Completed:
2c5ed52b-149f-5ba6-86ad-1a18b9ce8a73 | checkpoint | 6.4 - Defects to Slabs
3f516d19-5afa-50e8-8656-411903a8c112 | note | Frequency - Per Lot
150631ea-1856-53df-a83c-9a9317be8056 | note | Acceptance Criteria - Check for any nonconforming defects (cracks) in the concrete slabs.
94aceb5c-6f5d-54f3-bdd1-ca5bc232a8a3 | note | Reference Documents - Beca Spec 002 - 11.19
ec7e76c9-dc53-5142-98bd-3df83042df78 | note | Inspection/Test Method - Verify
ff40cd6d-cd44-56b9-a6a1-b07d689665dd | note | Record of conformity - This ITP signed
d109b0da-565c-5772-9e5b-2c8a5ff335e3 | note | IP
36bc9767-f10d-5220-8856-df85756fe6b7 | note | Responsibility - Project / Site Engineer
c9833f31-e161-56f7-9594-e08d707687aa | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
6ec667d0-0f8f-5ddb-9183-5e7d582c3f27 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality/System Procedures and verifies lot compliance with specifications.
d2e6550e-c607-57f6-87e4-4aa671b9d4d2 | textbox | Print Name:
870a6224-29d1-5697-b7e0-a4aee1ba336c | textbox | Position:
3b5d58b4-9d81-5add-bb5f-d6993954ebd6 | date | Work Completed On:
94480ab5-0fac-571f-9c29-dad8053606d3 | date | Date:
a204c3fc-4ad8-422a-8cee-b6abca267a66 | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0013 - PCC Pavements - Rev 2 (1.6 Checkpoint) | itp | ITP013 - PCC Pavements
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
2907e598-3fa6-573d-bd16-0574524c85dd | note | Frequency - Prior to commencing works
b9918449-71ab-57a3-8fb9-16b7aa22b72c | note | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
e00f65c1-9d2f-5be2-a812-fb0d735c5f0c | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
fcc655b9-fbb7-56a9-a250-a3e6ddfcdac9 | note | Reference Documents - Current Revisions in Aconex or ACC
7c8e2404-1102-5ee8-a17e-bf5965da5090 | note | Inspection/Test Method - Verify
bbf512ae-8c96-50fe-ab8e-041fb46b2033 | note | Record of conformity - This ITP signed
50155e9b-2035-554f-a3b9-dc1292319b1d | note | HP*
c857cb14-757e-552e-a08f-8d2f33488cba | note | Responsibility - Project / Site Engineer
7985f0ba-6f2a-53e3-86b8-8d2bb4b8fa9e | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
f76991b4-2e34-58da-a5a7-07c02f17fe3d | note | Frequency - Prior to commencing works
c651df4c-8e29-5d2d-9375-da49ffe74cdf | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
48b636c8-8a77-5c74-8d2b-2a67f6f57838 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
396ec348-d33a-5b4c-8f22-e1c5c2acb765 | note | Inspection/Test Method - Visual Inspection
7cf37097-e48c-53c0-8bbf-4d645002a09d | note | Record of conformity - This ITP signed
811f2fa4-250a-5ede-9e06-77ba08912d60 | note | HP*
3d378ac4-0b26-56cd-9c2f-4fba1d62a6ed | note | Responsibility - Project / Site Engineer
91cced02-0c77-52ba-9865-19bd3dc69329 | date | Date Completed:
7e28438e-f51f-55d2-9f71-e8c9c5437afc | checkpoint-no-value | 1.3 - Mix Design Report Submission and Approval
4507ccca-25f6-5ce8-996e-f117534195a8 | note | Frequency - Prior to commencing works
5b39bd65-bb88-5915-86f4-2d1b0165bfb7 | note | Acceptance Criteria - Theoretical mix design and preliminary trial mix results submitted in a report to the Contract Administrator for review and acceptance prior to full trial mixing.
98bbfa8e-9bff-5a20-994c-001991a18233 | note | Reference Documents - Beca Spec 002 - 11.5.3
85cbfe58-d6b7-5804-b260-f5c730fa1f47 | note | Inspection/Test Method - Verify
a862afaa-1ec6-58ad-b24c-6eacb2fca986 | note | Record of conformity - Aconex Reference
cb6a07a3-cb1d-5b7a-a016-a5b1ac8a4d5b | note | HP
ab6e881a-aab1-5c9a-9521-b29a5139afc2 | note | Responsibility - Project / Site Engineer, Principal’s Representative
2d313683-5885-50c2-9eb2-66762b61c470 | note | Date Completed: 01/06/2024
3211cacc-9c39-5b9a-9514-0f07b88fe014 | note | Principal's Representative - 40mm mix (VF509BW45):
4de8b9d7-8a9e-56b6-ab0e-97e16a9542c5 | note | ○ BecaCPL-GCOR-000846
9bfb2b0d-ee4d-5d09-8f3a-d73592ce630a | note | ○ 01/06/2024
b36ccdb8-21a7-5d8f-b493-28ebc1ebbb4c | note | 20mm mix (VF502BW45):
02fbd96e-add1-53bd-8fe5-4ad3ebfae557 | note | ○ BecaCPL-GCOR-001287
29325ff7-5d1d-512c-a119-dcc624cde04f | note | ○ 08/11/2024
1d417a20-1781-524c-8f26-32728ee4d344 | checkpoint-no-value | 1.4 - Job Mix Formula
8b89fdfc-d9d1-527e-8a5a-973029e07bae | note | Frequency - Prior to commencing works
7614f9ac-8801-59ee-a747-c145e86ec76c | note | Acceptance Criteria - The Job Mix Formula must state the mass proportion of all ingredients per cubic metre of concrete. The allowable limits in the Job Mix Formula (when compared to the agreed theoretical concrete mix design) must be in accordance with Table 11-2 of BECA 11.5.4 (see notes section).
57149b72-6f59-5d04-86e7-4525b9b35b55 | note | Reference Documents - Beca Spec 002 - 11.5.4
b51a7841-f170-5d47-8f36-c8cd85564a64 | note | Inspection/Test Method - Verify
503bc281-5ed7-58d1-aa06-fb549f758ad5 | note | Record of conformity - Aconex Reference
93011ee0-68cc-5e96-bafe-17d75aa2198c | note | WP
5375edff-176c-5d66-988f-1c14a5004c0b | note | Responsibility - Project / Site Engineer, Principal’s Representative
71a389be-f505-5ac1-9f06-a680d8c8848e | note | Date Completed: 30/05/2024
e0d8cbf6-790b-5a21-8182-cc284a5187fa | note | Principal's Representative - 40mm mix (VF509BW45):
97dbaacd-89ff-522e-9186-769e59f17b9f | note | ○ BecaCPL-GCOR-000839
4a21ce11-d18b-5f6d-a29d-0665e8bf4d71 | note | ○ 30/05/2024
9441d817-8cf2-51d4-aa71-29ea2f9c69e8 | note | 20mm mix (VF502BW45):
92bfda34-2b87-59b7-8f99-c5d1dcba2c9b | note | ○ BecaCPL-GCOR-001287
60967fed-10b5-5d10-9b31-c82faa272db7 | note | ○ 08/11/2024
ea2ed3cc-4240-5302-a62f-08cf18713d1a | checkpoint-no-value | 1.5 - Production and Construction Trials
e5fdbc46-719d-5942-8304-c39bd3e2059a | note | Frequency - Prior to commencing works
19475a37-83f9-5590-bea2-9dc4e0ea4477 | note | Acceptance Criteria - A production and construction trial must be completed as per the requirements in the specification.
1b130452-3c22-5b57-96d2-d425c83968d6 | note | ○ The results, control procedures, construction methods and completed trial pavement will be presented for review and approval by the Contract Administrator.
468ed8d3-72e9-5e5e-9e7c-4cd84000cb62 | note | Reference Documents - Beca Spec 002 - 11.6.1 to 11.6.4
4077b7bd-82bc-5ac9-8abf-482efd9b2c4b | note | Inspection/Test Method - Verify
df708af5-9f11-534c-af7d-32a465b86af9 | note | Record of conformity - Aconex Reference
528f6782-a3f3-5bce-bf62-414e8a0aa3b5 | note | HP
08bcb58d-ea03-5f6c-8d87-068ee9a666c4 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a044b821-045c-516d-806b-4adbf19eae93 | note | Date Completed: 19/08/2024
3f498654-9c27-5215-b0b9-26044de9c986 | note | Principal’s Representative: 40mm mix (VF509BW45):
513327b9-ee48-5bb6-aa2f-f43a31e65b89 | note | ○ DCWC Mgt-GCOR-009917
80f1a148-d7e3-5061-ae9a-4e7bea017c92 | note | ○ 19/08/2024
2594963a-406b-5b50-b7d8-7ce87a745935 | note | 20mm mix (VF502BW45):
c5189654-3944-5828-928b-f5408e54e5bc | note | ○ BecaCPL-GCOR-001287
b8131940-bed2-5474-957b-e9597b721743 | note | ○ 08/11/2024
e5f4e390-d859-5bb8-8754-88a6610c4a41 | checkpoint | 1.6 - Curing Compound Material Submission
9b855dfe-dcaf-5780-a60c-3107674b9ed2 | note | Frequency - Prior to use of curing compound
83186ab9-3183-5a0d-8af9-d95cee37cc97 | note | Acceptance Criteria - Membrane curing compounds shall be a white pigmented type confirming to AS 3799, Type 2. Wax based compounds shall not be used.
f420a157-3565-5505-8230-a10228b203ee | note | ○ No compound shall be used without written approval by the Contract Administrator.
25cd7b38-ee48-596d-b07d-17fa9f379210 | note | Reference Documents - Beca Spec 002 - 11.4.11.1
60e9e8c5-b8ed-5bd9-a26e-3382693460cc | note | Inspection/Test Method - Verify
c0fd41e0-1e99-5cb1-b48f-4c618b1231d9 | note | Record of conformity - Aconex Reference
725ec045-95ca-572c-9b4e-9c371e3ec53f | note | HP
f35c5635-fb93-5f33-b60d-c63641ec0278 | note | Responsibility - Project / Site Engineer, Principal’s Representative
696d3ed0-b889-5758-aec5-19902ec4d780 | note | Date Completed: 22/05/2024
a818c49e-eaec-5a25-8530-c20a4d5b18bd | note | Principal's Representative - BecaCPL-GCOR-000791
ba929a80-28cc-56d4-987f-a6898a2999b4 | checkpoint | 1.7 - Impermeable Blanket Material Submission
761302c5-7075-519c-9d7b-694b9d82823c | note | Frequency - Prior to use of impermeable blanket
b5091c95-16c2-5ef1-a417-df9805b7c0ab | note | Acceptance Criteria - If required to be used, impermeable blankets shall comply with the requirements of ASTM C.171.
db67cc05-0893-5f00-99ff-d92e8f8fca9b | note | ○ The blankets shall have sufficient strength and weight to meet the required conditions of service and shall be approved by the Contract Administrator before use.
46bd5aaf-a712-5584-9956-c7ddf7e3671b | note | Reference Documents - Beca Spec 002 - 11.4.11.2
40d7a594-43f0-57e3-8f8e-430fd5f4061f | note | Inspection/Test Method - Verify
6af78c57-3fbc-5181-a1c9-23ad09bdf0ba | note | Record of conformity - Aconex Reference
bb338aed-f7e8-569f-995d-e97baa3ee2b6 | note | HP
4768e536-db22-57da-8f25-3e8dfeda92eb | note | Responsibility - Project / Site Engineer, Principal’s Representative
fdd17bfc-d0c1-55b5-88b6-5f825b05769a | date | Date Completed:
5885abc0-a77e-5d54-803d-3fd1515e6818 | section | 2.0 - Pre-Placement Activities
16ee8263-a125-5876-ab26-79db8c104fdd | checkpoint | 2.1 - Formwork Installation & Pre-pour Inspection
65a8de96-f184-5a0b-af0f-2fd24a991fb5 | note | Frequency - Prior to placing concrete
1f1a7b28-fea3-5aa9-b6c2-a714d1d257f5 | note | Acceptance Criteria - Formwork must rest firmly on the base to eliminate gaps and ensure no leakage of concrete will occur during placement.
a5ca7930-6074-5fd1-9a44-03273fc974f8 | note | ○ Formwork must be secured into position and locked together during placing, spreading and finishing of the concrete.
1e88b2e3-5eaf-5da0-8afd-bc24150e6b21 | note | ○ The top of the form must not deviate by more than 3mm from the required level.
2f868783-cb5a-598f-8cfa-65f1caec0add | note | ○ The form face shall be vertical and not vary more than 6mm from the required alignment.
9c162418-572b-54f0-a012-ec365748db1f | note | ○ The area in which concrete is proposed to be placed shall be inspected and checked immediately prior to commencement of placing.
31c77cba-682b-53dc-87ae-5baea14f37a7 | note | Reference Documents - Beca Spec 002 - 11.8.1.1, 11.9.1
6ef34b37-ea17-5ff3-ae4b-e99491dfaaaf | note | Inspection/Test Method - Visual inspection
a9ebca94-422a-50d0-83cf-12869d540e0b | note | Record of conformity - This ITP signed
f249917f-23af-5d15-86c4-a29b6426d2d9 | note | WP
5b8afdc5-c63f-53f0-a861-23a7b328949e | note | Responsibility - Project / Site Engineer, Principal’s Representative
7409513b-e0b7-52ca-8954-8936dd8759d3 | date | Date Completed:
fd1f1b65-94f0-536d-a050-a134453028a2 | checkpoint | 2.2 - Pre-pour checklist
ab32c07d-9a9d-53ce-b9b5-123154b34553 | note | Frequency - Prior to placing concrete
18c8a68c-2470-5f7a-a086-63658f6c6540 | note | Acceptance Criteria - Completion of the pre-pour checklist: CL013A – Pre-Pour Checklist which details various checks required for formwork, reinforcement, joints and the pour area.
b28cd113-7abb-5137-9cf8-2b694ff03494 | note | Reference Documents - Beca Spec 002 - 11.8, 11.10, 11.13
be572c26-123b-5025-998f-2abc96f9640b | note | Inspection/Test Method - Visual inspection
d984894d-908e-5b6f-ad12-8ad9faed8fba | note | Record of conformity - CL013A, This ITP signed
d8b6310c-914c-575c-865b-9033ff0b5181 | note | HP*
7a14446c-e20a-5723-ad87-0f7c48d3e202 | note | Responsibility - Project / Site Engineer
ae723b76-57c3-5197-94af-ab6ad7d4b3a6 | date | Date Completed:
d9388486-1250-5ff8-b9ad-8d44105f357b | checkpoint | 2.3 - Weather Forecast Checks
d43c1ab9-5201-5007-b19e-cb14e0ad0be0 | note | Frequency - Prior to placing concrete
0a8b717f-0ec7-5292-8236-466654675c31 | note | Acceptance Criteria - Check the weather forecast for unfavourable conditions (rain, wind, hot weather or cold weather) on the day prior and immediately before confirming
ed0bef5e-c778-5d14-9786-2791f8899413 | note | Reference Documents - Beca Spec 002 - 11.9.5.1
c980c01d-b749-5c67-a48b-015656e8fe01 | note | Inspection/Test Method - Verify
5740e4c3-89c1-5bdd-a073-809a08fe31b8 | note | Record of conformity - This ITP signed
a2371590-dbcb-552a-9f00-aa021e745a5c | note | HP*
20538a2e-8184-5d34-a5e7-dbca391524b0 | note | Responsibility - Project / Site Engineer
10ba42c8-0df4-561f-89da-75552b10f2ca | date | Date Completed:
cd1921f5-0447-55dd-a906-346b6c56d7e0 | section | 3.0 - Placing Concrete
4ce1dbde-921b-5f12-92f2-cb172108eb2c | checkpoint | 3.1 - Place, Spread and Compact Concrete
7665b879-a2be-524d-ac3e-ecf0582e021e | note | Frequency - Each concrete pour
723f9130-2ba8-5f32-8090-706d2a025af7 | note | Acceptance Criteria - Concrete placement must be at a rate appropriate to achieve a consistent high quality resulting pavement.
80257cee-5638-514e-a8ff-24d1c99ba788 | note | ○ During placing, the concrete must not drop freely by more than one metre onto the base of the paving lane.
ede5d52d-6d18-5925-a3b4-ed8eb0fbe3a1 | note | ○ Concrete shall be placed uniformly over the width of the slab and in a way to minimise segregation.
fb7bb21a-0517-5585-8cba-f749e3db01cb | note | ○ Concrete to be adequately compacted by internal mechanical vibration.
47ad46e2-d1bd-59d1-992d-bbe52b4d9cbd | note | Reference Documents - Beca Spec 002 - 11.9.1, 11.9.4, 11.11.2.1
638de61b-8375-576b-9262-504c09b1a131 | note | Inspection/Test Method - Visual inspection
39a74bcb-e849-515c-9206-afe7bbf2cd12 | note | Record of conformity - This ITP signed
73d72013-09b1-5d43-9fe7-bab4cde0554c | note | IP
bc0e21bc-775d-5d51-b0cb-529089e2bd84 | note | Responsibility - Project / Site Engineer
4fad147d-594c-5d20-96cf-f52b3f9b9d35 | date | Date Completed:
01340969-6666-50d8-81f7-9de3ba0476a1 | checkpoint | 3.2 - Concrete Deliveries
8246b40e-a538-5ae2-a7e5-ff27722c2f97 | note | Frequency - Each concrete pour
ff9bb630-b1de-5601-afdb-7766627168d9 | note | Acceptance Criteria - Each concrete delivery to site is to be recorded on CL013B – Concrete Pour Record Sheet.
c719bd61-97e4-5c4c-84ed-af3fe5c02149 | note | ○ Concrete shall be placed within 90 minutes from the time of batching and before the concrete has attained its initial set.
fb71dde1-c897-5894-867b-60edb818ef6e | note | ○ The pour location, direction and order to be recorded on CL013C – Load-Batch Traceability.
04107314-7b34-53c4-8165-e6655e2e25de | note | Reference Documents - Beca Spec 002 - 11.9.1
1ad59df4-04e9-5aaa-acc6-fcecf0a20d1e | note | Inspection/Test Method - Verify
3945ca57-c77b-5137-bdc3-c380e553e0df | note | Record of conformity - CL013B CL013C, This ITP signed
b03e5d32-467f-5422-9751-5cd135c27c28 | note | IP
45e148b9-6d9b-5f88-a000-ad7e6419a0c2 | note | Responsibility - Project / Site Engineer
ba507cfd-70e3-534c-bfd9-36d529c0cfe7 | date | Date Completed:
a8846c82-3dab-5b97-8463-d576a7c411cc | checkpoint | 3.3 - Evaporation Rate
620b32c5-666d-5ac5-9d40-c190badf7dab | note | Frequency - Each concrete pour
65d8d07b-bb3e-5b85-89c1-9dcc1f61a1be | note | Acceptance Criteria - Concrete must not be when the evaporation rate from the surface of unprotected concrete is in excess of one (1) kg/m²/hr.
5245a27c-ae3a-572e-82a2-c0a5168e075d | note | ○ When the evaporation rate exceeds 0.6 kg/m²/hr, precautionary measures to prevent plastic shrinkage shall be taken.
1f0914c8-b9e4-5490-8cb3-4394352605b4 | note | ○ Evaporation rate to be recorded on CL013D – Rate of Evaporation.
a658725f-486e-574f-83ff-b8cc2eb40700 | note | Reference Documents - Beca Spec 002 - 11.9.5.2
1f4e2277-f1ef-5141-bc8f-dd05fc26f7a0 | note | Inspection/Test Method - Verify
f76b01c6-bd98-5ff3-9e87-82bc36a34708 | note | Record of conformity - CL013D, This ITP signed
3e4d1077-a8f0-5a0f-9fa6-30268bc119ef | note | IP
acaccec8-ef2c-51a4-a20c-aef89753f903 | note | Responsibility - Project / Site Engineer
cb08b5a5-0abd-51b0-8c20-fdbdb49bb359 | date | Date Completed:
6bde1751-12a1-5704-bd61-b45ba632ac70 | checkpoint | 3.4 - Hot Weather Concreting
744e946e-f126-5621-9e7e-a4972f3ef9ba | note | Frequency - Each concrete pour
a1e7bd7d-1f73-5185-bd3f-77e0967bec30 | note | Acceptance Criteria - Undertake additional precautions when placing concrete in hot weather.
7d9e13d6-291a-5804-8258-3aaced05a93f | note | ○ Ensure the concrete is placed at the coolest temperature practicable – the concrete temperature should not exceed 32°C.
78f48efa-0ae5-5dc1-8f31-3313b3109889 | note | Reference Documents - Beca Spec 002 - 11.9.5.3
d831f3f8-c332-5686-bda4-38c911c66549 | note | Inspection/Test Method - Verify
10d0b85b-3d61-5194-8f9d-e39d2c381564 | note | Record of conformity - CL013B, This ITP signed
4807115e-733f-50c1-b298-52829bceea88 | note | IP
37c77533-2901-5453-b540-56df0c72adc4 | note | Responsibility - Project / Site Engineer
60155a52-54ab-55ff-9c03-8d923452d239 | date | Date Completed:
0a674bc7-9c0b-59d4-b89b-165fe5156d0a | checkpoint | 3.5 - Cold Weather Concreting
b46d4377-743b-5e2c-9a62-72656b686c51 | note | Frequency - Each concrete pour during ‘cold weather concreting’ conditions
7fe02ad8-3085-5f3a-ad2a-0d86841ffc75 | note | Acceptance Criteria - Cold weather concreting applies when placing concrete when the temperature of the air, aggregates or water is below 10°C.
d01a9e14-2976-5bf7-af7e-f001c89aa7a4 | note | ○ Placement of concrete can only proceed if the ground temperature at the concreting site is greater than 5°C and the temperature of the concrete is not below 10°C.
14bec05b-75b6-5cbd-8313-7107a72b00fb | note | ○ Refer to checklist CL013E – Cold Weather Concreting for ground temperature records.
2c83eea4-ede8-58de-8a96-8fdc2ca50a2d | note | Reference Documents - Beca Spec 002 - 11.9.5.4
5400d6da-e277-5552-934d-295719475b4a | note | Inspection/Test Method - Verify
0cf4e0f5-f7b0-591c-a4bc-a74cc1925e3f | note | Record of conformity - CL013B CL013E, This ITP signed
f7ee5f93-57e9-570b-80b5-7e193fd5587f | note | IP
4121e0e9-6a3c-5dea-90e4-8dea93d0437c | note | Responsibility - Project / Site Engineer
16188178-5de4-56d5-bf57-fb2443ec071b | date | Date Completed:
bce17218-2b32-50e2-99bf-8851b7031e92 | checkpoint | 3.6 - Concrete Surface Finishing
b26ed40c-f7fe-5c69-a471-0ad5980c219a | note | Frequency - Each concrete pour
3dd3cb8a-4d02-5a4b-a302-32045875d4e6 | note | Acceptance Criteria - Finishing operations shall compose transverse finishing, longitudinal straight-edge finishing, floating and broom finishing, in that order.
53be0521-6bdd-50fc-b99c-5d2a91eb7f37 | note | ○ Finishing operations must be started immediately after compaction of the concrete and completed as soon as possible but not later than 90 minutes from the time of batching and prior to the concrete attaining its initial set.
2ba31877-3f8d-5551-bf43-08e177e81c36 | note | Reference Documents - Beca Spec 002 - 11.11.2.2
e09b32d0-416e-5346-9c9b-1220537934c9 | note | Inspection/Test Method - Visual Inspection
6e7e4584-a8b0-595f-a24d-de612f1127a2 | note | Record of conformity - This ITP signed
ad934164-50ae-59cb-98b2-675b58179b25 | note | IP
699e0910-0d47-5413-9c83-c52b19be34c6 | note | Responsibility - Project / Site Engineer
6abdad8c-dc11-55fd-8218-36822687b6ab | date | Date Completed:
d4da5116-30ab-56c9-b1eb-849f5003fc96 | section | 4.0 - Sampling and Testing Concrete
43ff8655-1595-5766-8438-ea3569c93eaf | checkpoint | 4.1 - Slump
e7dc755c-ff25-50ee-96af-ff0dab3dcd19 | note | Frequency - 1 test every 2 trucks
9fbac8e6-40ae-5a64-ae00-e85f95490dd9 | note | Acceptance Criteria - 60mm +/- 10mm
1e1c2738-c8ef-566d-b4ef-c0a06b1b95d1 | note | Reference Documents - Beca Spec 002 - 11.24.17, BecaCPL- GCOR- 000846
631b6b02-f4ee-54f6-aab2-f4606e4be2b8 | note | Inspection/Test Method - AS 1012.3.1
6e0d6122-3d83-517b-9fb4-9810dfb73c77 | note | Record of conformity - NATA Test Certificate
3799165a-793c-5f52-9e99-1bc8e66aa85d | note | TP
f33f7e7f-5c6b-5a6f-90b3-368d440763fa | note | Responsibility - Project / Site Engineer, Laboratory Technician
edc8ffe1-57f1-5325-886e-40e630995883 | date | Date Completed:
df8751f1-b783-5ced-bb43-a84f6efb9e3e | checkpoint | 4.2 - Temperature
0c42cd12-866c-585a-869b-e826adc3da04 | note | Frequency - 1 test every 2 trucks
92d7b2a7-237c-52b8-badd-e661cea05acb | note | Acceptance Criteria - Minimum 15°C (except in cold weather concreting where minimum is 10°C)
1ac66703-6f4b-5503-a481-2cd5bf33c432 | note | ○ Maximum 32°C
065863ac-e20e-5236-a611-2c120f585201 | note | Reference Documents - Beca Spec 002 - 11.24.16
867d37cd-753b-5c5e-baa0-37d9c5934684 | note | Inspection/Test Method - AS 1012.3.1
ecc7394e-9e35-58b5-b477-c08cd31a0447 | note | Record of conformity - NATA Test Certificate
be4204fb-85e0-5c77-a84d-bf595ef132ea | note | TP
0b169908-fbcd-530e-a69b-735905db5c2b | note | Responsibility - Project / Site Engineer, Laboratory Technician
dd04c20d-b5c7-5091-8993-9cb5aee071da | date | Date Completed:
2ffe1a6e-8b66-57f5-bbd8-0c2e46eccdea | checkpoint | 4.3 - Flexural Strength (7 day)
506d83af-a213-50cf-bd4c-086b494c9637 | note | Frequency - First 5 lots: 2 Beams per 75m3 or part thereof.
d1c99a14-cafa-596a-96d4-30a78dab4373 | note | ○ After 5 lots: 1 Beam per 75m3 or part thereof.
4a796ae1-7593-5083-acbc-16b5ce896c8d | note | Acceptance Criteria - Results for information only
f079ae4f-0da6-55dd-8f57-d175df0f1741 | note | Reference Documents - Beca Spec 002 - 11.24.10
6f6c0f31-b5d0-51b0-b720-0309c7e52034 | note | Inspection/Test Method - AS 1012.11
909c13bc-855e-5784-919c-3711ccbebb19 | note | Record of conformity - NATA Test Certificate
85fe830c-74ec-52ff-b129-4a3ed94a9760 | note | TP
0c8466ea-46f8-563c-980b-4ccf33c2a639 | note | Responsibility - Project / Site Engineer, Laboratory Technician
7d92ade6-8787-586c-a9f9-909bcaec1671 | date | Date Completed:
f5e85626-3e87-51d9-b123-8dbe71828123 | checkpoint | 4.4 - Flexural Strength (28 day)
68bc7023-086e-52c4-a527-072e730877c5 | note | Frequency - First 5 lots: 2 Beams per 75m3 or part thereof.
25a96de9-b8aa-5d12-9823-ba69d74ca852 | note | ○ After 5 lots: 2 Beams per 75m3 or part thereof.
dc2be2b2-4f0f-552f-8dcf-b7bab6ae9120 | note | Acceptance Criteria - Mean of the pair of beams > 5.0 MPa Individual beams > 4.8 MPa
6f64e51f-d32c-5c63-8e3a-7d51f1de2841 | note | Reference Documents - Beca Spec 002 - 11.24.10
34161891-b4e6-5856-a5cd-40d95a043493 | note | Inspection/Test Method - AS 1012.11
3af3ca24-1695-54ac-ae7f-fbc32c179aab | note | Record of conformity - NATA Test Certificate
0da54949-117b-58bf-b3cd-c3583c3829b3 | note | TP
a3663f3b-081d-58c3-91a7-c63a62d9874a | note | Responsibility - Project / Site Engineer, Laboratory Technician
7eddf880-425d-5c79-88c0-4b9f42dd923a | date | Date Completed:
9e886210-4b93-5748-a95e-ad183ab45c95 | checkpoint | 4.5 - Air Content
beb5fad9-719b-5f31-9ca2-bbe8fea2632b | note | Frequency - 1 test per Lot
cce2068d-7751-5d08-b115-9c85be983a61 | note | Acceptance Criteria - 3% - 5% ±1%
cce38939-39dd-5930-b456-e385fde10ce4 | note | Reference Documents - Beca Spec 002 - 11.24.8, 11.24.9
4f873026-9a91-58f9-bd7f-32975b9c9630 | note | Inspection/Test Method - AS 1012.4.1 or 1012.4.2
96ae24eb-2d77-5f28-89c2-4f1dc3ced80b | note | Record of conformity - NATA Test Certificate
f0e67256-3950-55e7-a7f5-ff9fb9edfb96 | note | TP
c7616360-f69d-5c7a-a9a4-e385f182e23f | note | Responsibility - Project / Site Engineer, Laboratory Technician
eed76a32-8847-5b9f-bcd9-7ac60e6b2939 | date | Date Completed:
9ad6888c-fa3b-5efb-b8a6-dea67ddcb735 | checkpoint | 4.6 - Mass Per Unit Volume
249ca4b9-5f12-5647-bd16-61bb71132964 | note | Frequency - 1 test per Lot
914a1061-d7db-5862-80b3-2dc51c3bbd66 | note | Acceptance Criteria - Results for information only
d61bce60-4427-5438-a778-ac44dd2b9ac6 | note | Reference Documents - Beca Spec 002 - 11.24.9
56516493-bebe-5e10-94d5-968d50da156a | note | Inspection/Test Method - AS 1012.5
89fec65b-8936-51e1-b966-5a9bc9bb695e | note | Record of conformity - NATA Test Certificate
cea769a3-8529-5654-8e6d-9695b25c878c | note | TP
813e7f85-510e-53fa-b17a-6671485216dc | note | Responsibility - Project / Site Engineer, Laboratory Technician
7655c7ad-d1c4-5ddf-a170-5835f574c71f | date | Date Completed:
784088d9-4c0a-591a-bcd5-f66d2ffb7819 | checkpoint | 4.7 - Wet Analysis
343a3167-cf90-59c7-bf56-10568edf0ef9 | note | Frequency - 1 test per Lot
ed0a84e9-18b8-512b-89eb-0fa090f32c09 | note | Acceptance Criteria - Results for information only
a23c85d7-48fb-5dca-accc-8001ad078bf1 | note | Reference Documents - Beca Spec 002 - 11.24.9
b0493a50-ceb7-5173-b70b-785e23524ab0 | note | Inspection/Test Method - AS 1289.3.6.1
715add53-bd8f-5fd2-a2b2-69d474fbef00 | note | Record of conformity - NATA Test Certificate
79d6b9e1-35e3-5868-a636-e5b774e97e92 | note | TP
d74d9e31-040b-53aa-8098-f3eafa8096f7 | note | Responsibility - Project / Site Engineer, Laboratory Technician
c49d4dd6-001e-5b3d-acf4-c27d4f3d7767 | date | Date Completed:
21046b26-0f7a-50ea-a8d4-20fcdb40c85b | checkpoint | 4.8 - Concrete Core Analysis (Density & Compressive Strength)
44ef0abf-113d-5a24-b205-4a368131b77d | note | Frequency - First 10 lots: 6 cores per Lot
8dda6e55-4e3f-5481-a80c-36712dd44c50 | note | ○ After 10 lots: 1 core per 75m3 or part thereof
f698075e-11c4-5bff-b6a4-f3df2e4eb701 | note | Acceptance Criteria - Cores must be not less than 120mm diameter.
f121d421-0622-5526-b970-29ddf62c3769 | note | ○ Calculate the degree of compaction by comparing the density of individual cores with the average density of flexural test beams (exclude beams whose density is less than 97.5% of maximum theoretical density). Refer to notes section for acceptance requirements.
93ff3a2a-1e34-5537-a2c0-92305264f999 | note | ○ If a lot requires 3 or more cores, one third of the cores taken shall not be tested for density but shall be tested for compressive strength and results submitted for information purposes only.
100d7a77-1402-5478-91dd-ac73722a5a83 | note | ○ Refer Aconex: DCWC Mgt-RTRFI-001244
8998f956-5b2b-5eba-abc6-3cc8f555afbd | note | Reference Documents - Beca Spec 002 - 11.24.12
81946f43-f32b-5770-847b-fca603623b71 | note | Inspection/Test Method - AS 1012.12, AS 1012.9
c579b5f9-7653-5159-950f-b218a132b5a9 | note | Record of conformity - NATA Test Certificate
d065c9e2-e7de-5724-81b2-3ff5c52b422c | note | TP
9d2eceff-0e85-554e-8aa1-6229bdbf671a | note | Responsibility - Project / Site Engineer, Laboratory Technician
59c3b69c-68da-5505-8ce0-3f8a9ece2c03 | date | Date Completed:
782b8ec4-e2e7-589a-bdec-0fe6bc056628 | section | 5.0 - Post-Placement
cf47b8f0-f88a-54c2-b407-91f44e2a654f | checkpoint | 5.1 - Curing
d935de30-5a7e-5f55-8a4c-05bb1a5194a1 | note | Frequency - Each concrete pour
0b1553ac-4ec0-5a8e-8d8f-f4260aefd946 | note | Acceptance Criteria - Concrete shall be cured by protection against loss of moisture and rapid temperature changes for a period of not less than seven (7) days from completion of the finishing operations.
40e0f672-c0b1-5de3-939a-86d62221b715 | note | ○ Curing of the concrete shall comprise an initial mist curing followed as soon as possible with continuous wet curing with hessian matting for the duration of curing period.
a2c4a646-91dd-5a03-97cb-f09b867f8363 | note | Reference Documents - Beca Spec 002 - 11.12.4
8441d7a4-4ca1-5d1d-b5a9-8246823633f8 | note | Inspection/Test Method - Visual Inspection
5ecbc6a7-bdf6-5d88-b7fb-dfe592caf6cd | note | Record of conformity - This ITP signed
da2577af-fbbe-5cc3-836f-f2db59d57582 | note | IP
d887255a-6945-5b74-8988-38edbf9405af | note | Responsibility - Project / Site Engineer
586a76b4-cd49-5ad5-9eb3-335564e3ab27 | date | Date Completed:
aa609089-ea6f-521a-b2a7-7cd41a2d5d49 | checkpoint | 5.2 - Cold Weather Concreting Concrete Protection
b72a3ea0-9cf3-54a7-beec-14b61b7a485d | note | Frequency - Each concrete pour during ‘cold weather concreting’ conditions
bf428b0e-8c96-580d-9b28-a5f2c3a1450c | note | Acceptance Criteria - The surface of the concrete must be maintained at a temperature of at least 10°C, for not less than 72 hours after placing and at a surface temperature above freezing (0°C) for the remainder of the curing period.
f9469610-5e96-5a78-922e-b7dee55d8e29 | note | ○ Concrete surface temperatures post-pour to be recorded on checklist CL013E – Cold Weather Concreting.
a429a458-d908-5b2c-ac3a-8f1ba931df5e | note | Reference Documents - Beca Spec 002 - 11.9.5.4
4f84e7fa-b264-5dfe-bca2-9a95248c0896 | note | Inspection/Test Method - Verify
410a28c0-f2e4-5be6-9d42-669ddbe29548 | note | Record of conformity - CL013E
71518393-0ca3-58de-b30c-7e807bd704e0 | note | IP
148e7960-cfe8-5c7b-a158-389cc3f3c208 | note | Responsibility - Project / Site Engineer
bc31c826-5b56-59c5-9460-f2f09b4366fc | date | Date Completed:
82b7f08a-ab9e-5a58-be5c-738ceda7b9f1 | checkpoint | 5.3 - Inducement Saw Cutting
ba74ad63-a217-5659-8789-4213c2ef4104 | note | Frequency - Each concrete pour
9d64d094-2296-50a1-b47e-7ab9a78b0e8b | note | Acceptance Criteria - An initial 3-5mm wide saw cut to a depth of T/4 to T/3 where ‘T’ is the concrete thickness (generally 150mm) is performed along transverse contraction joints as early as possible post pour.
125b6f42-2b3a-58fe-b46a-92a76549fb7a | note | ○ The concrete must harden sufficiently to permit cutting the concrete without excessive chipping, spalling, or tearing.
1a776220-10f0-5a53-b868-97fef033431d | note | Reference Documents - Beca Spec 002 - 11.13.5.2
30288578-007f-585f-a161-4929011df0c2 | note | Inspection/Test Method - Visual Inspection
377ff993-cbe6-50a7-aa30-10d2d23a7839 | note | Record of conformity - This ITP signed
2b2e9676-0d95-5bfb-9060-7ae0fcc14764 | note | IP
ac9e5c42-5d54-51f0-92a6-47743e8b6671 | note | Responsibility - Project / Site Engineer
ec669d6c-1236-5ce8-b376-bbfb38d60b30 | date | Date Completed:
1415f254-48b2-52a5-8aea-2df0d8845449 | checkpoint | 5.4 - Formwork Removal
4c9f9ded-2540-5aa1-a9b7-1549da9de3ad | note | Frequency - Each concrete pour
c89af9fa-9c3c-5b89-9507-b7f0b4112f66 | note | Acceptance Criteria - Forms must remain in place at least 12 hours after the concrete has been placed (but no longer than 48 hours).
28e65d8a-e481-5fae-b3c1-156e31999afd | note | Reference Documents - Beca Spec 002 - 11.8.1.3
a1b1af8d-5887-5e45-80c8-c711f63c9273 | note | Inspection/Test Method - Verify
f4445baf-2265-5b77-9a96-a3717922e231 | note | Record of conformity - This ITP signed
5d0613f6-7e0b-5386-9b7c-f4e76151a0d6 | note | IP
6d4b2aac-9612-5e27-a9cf-153d627386ae | note | Responsibility - Project / Site Engineer
18f2ef5c-d133-5162-88cf-ce695de1233a | date | Date Completed:
69489b9b-1e23-57b3-b09f-8b123c4734fd | section | 6.0 - Completion
8fa0b7c0-e1be-5bfb-a603-8cd013fc6298 | checkpoint | 6.1 - Surface Smoothness Testing
55e7de99-3c61-538a-a173-cbdebe5c1754 | note | Frequency - Per Lot
0c6efdae-61ee-505e-af82-1add84557269 | note | Acceptance Criteria - The finished surfaces of the concrete pavements shall not deviate from the testing edge of an approved 3.5m straight-edge more than 5mm longitudinally and 5mm transversely. No ponding of water is permitted.
32222931-7dbf-5c57-a8be-fb36823b71be | note | ○ Points exceeding tolerances and any observed areas of ponding water will be recorded on ArcGIS.
8789dc0b-3a2a-58b2-89a8-c6643a4d1cac | note | Reference Documents - Beca Spec 002 - 11.14.3
9d59607b-536c-51a3-b9b8-f275e3994b93 | note | Inspection/Test Method - Visual Inspection
d920b062-aab2-5cc1-8472-ec4909ccab24 | note | Record of conformity - ArcGIS, This ITP Signed
2d893d27-0cfb-5e97-acd3-5a846b45f93c | note | IP
168e7066-b2f9-5912-8c30-42b0df934b3f | note | Responsibility - Project / Site Engineer
4799c1ed-759e-577d-acbc-1c9e9a389eb2 | date | Date Completed:
91cbcdd4-c964-5ba9-81ea-9199af3ff529 | checkpoint | 6.2 - Pavement Surface Levels
f7b31f9b-21d2-5bd8-8aca-6bac5928cc2c | note | Frequency - Per Lot
445217a3-704d-54d0-91f1-f47b50e14278 | note | Acceptance Criteria - The Contractor shall take levels on the finished pavement surface at the corner of each slab.
986af59c-af1b-54e1-b235-cc9960654cdb | note | ○ The finished surface levels taken shall be within ±5mm of the design levels shown on the Drawings.
54cd0821-1456-58c9-9edb-34ea1dfb4396 | note | ○ The levels shall be measured to an accuracy of 2mm.
2479533d-2d5a-5645-94a5-2f3915c91011 | note | Reference Documents - Beca Spec 002 - 11.14.2
7d131307-0cf5-5fb5-a872-6605679b0156 | note | Inspection/Test Method - Verify
30637c20-3975-54ca-b8e5-98e5838a8c78 | note | Record of conformity - Conformance Report
91934272-5c06-53f9-bced-b8f5a45c58a2 | note | SCP
942d3878-1a64-50ba-9f33-700d3f5365a2 | note | Responsibility - Project / Site Engineer, Surveyor
c89333bd-fc10-5caf-a06a-0387ff3ec9a7 | date | Date Completed:
4ea2f5f4-1037-54b8-98fd-5a7f56de6983 | checkpoint | 6.3 - Protection of Slabs
e0a272cc-8031-5c13-94e7-2c52940c54d6 | note | Frequency - Per Lot
ca4200e7-3811-542f-9623-95ab15582db2 | note | Acceptance Criteria - Concrete pavement must not be trafficked until 7 days old or early strength results are obtained. Steel tracked or steel wheeled equipment is not to be used.
d0d67642-8c06-5e46-8e83-6af9a4ec16ed | note | Reference Documents - Beca Spec 002 - 11.17
1981dabb-a7d4-56cc-a815-bb0ec0aac791 | note | Inspection/Test Method - Verify
d9f99ce0-fd9f-523d-b3b0-028767f2b5d5 | note | Record of conformity - This ITP signed
536c33e3-9e33-5297-a415-b849c3716a6b | note | IP
a9977ffb-173a-5f9c-a3fc-11de956a432f | note | Responsibility - Project / Site Engineer
5f06486e-2a73-588f-a366-13292ebceedf | date | Date Completed:
2c5ed52b-149f-5ba6-86ad-1a18b9ce8a73 | checkpoint | 6.4 - Defects to Slabs
3f516d19-5afa-50e8-8656-411903a8c112 | note | Frequency - Per Lot
150631ea-1856-53df-a83c-9a9317be8056 | note | Acceptance Criteria - Check for any nonconforming defects (cracks) in the concrete slabs.
94aceb5c-6f5d-54f3-bdd1-ca5bc232a8a3 | note | Reference Documents - Beca Spec 002 - 11.19
ec7e76c9-dc53-5142-98bd-3df83042df78 | note | Inspection/Test Method - Verify
ff40cd6d-cd44-56b9-a6a1-b07d689665dd | note | Record of conformity - This ITP signed
d109b0da-565c-5772-9e5b-2c8a5ff335e3 | note | IP
36bc9767-f10d-5220-8856-df85756fe6b7 | note | Responsibility - Project / Site Engineer
c9833f31-e161-56f7-9594-e08d707687aa | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
6ec667d0-0f8f-5ddb-9183-5e7d582c3f27 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality/System Procedures and verifies lot compliance with specifications.
d2e6550e-c607-57f6-87e4-4aa671b9d4d2 | textbox | Print Name:
870a6224-29d1-5697-b7e0-a4aee1ba336c | textbox | Position:
3b5d58b4-9d81-5add-bb5f-d6993954ebd6 | date | Work Completed On:
94480ab5-0fac-571f-9c29-dad8053606d3 | date | Date:
ad2d1791-ffd6-5f4a-81da-08ea1abbcf2a | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0014 - Sawcutting & Joint Sealing - Rev 0 | itp | ITP014 - Sawcutting & Joint Sealing
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
fbd6ef58-7046-5030-bc38-d0da69c3974d | checkpoint | 1.1 - Check for Correct Documentation
79bd05d0-9a65-5949-b1aa-d4a42fc4e829 | note | Frequency - Prior to commencing works
31adfb6e-d09a-5768-8b5b-c2053849fb88 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
5d8b007b-08f3-5787-8929-bf98bc3e325d | note | ○ Current revisions of these documents to be obtained via Aconex or ACC
fee07b74-ed1e-5be5-bf5f-59b71136dd74 | note | Reference Documents - Current revisions in Aconex or ACC
da8dd3cc-19e3-5726-b492-cba5176eab7e | note | Inspection/Test Method - Verify
b231cc0c-dad8-53ec-b88f-e9c0bc8f723f | note | Record of conformity - This ITP signed
7235dad4-6d0b-59a9-8eed-fbebbba2a3c3 | note | HP*
5c7ff4ef-cb14-595e-b46d-97dfd87a16cd | note | Responsibility - Project / Site Engineer
3e94d70a-74f0-5061-98da-8624cc10e016 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
3303edab-5b66-5af1-b8d1-22ab8495cee9 | note | Frequency - Prior to commencing works
be859a16-d2c6-53c3-9eda-012f04d455a3 | note | Acceptance Criteria - All necessary measures and controls are being implemented in accordance with PSP, EMP, TMP, JSEA, SWMS & WP
dbcba871-bf73-5749-8b4e-72cae0e93402 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
a0786763-a24a-554c-b4b4-6fc9d456cccb | note | Inspection/Test Method - Verify
d3393572-6931-512b-8426-8ac8490b3c40 | note | Record of conformity - This ITP signed
18970737-ee7c-5380-85c4-295e20dbdb59 | note | HP*
ac463377-a89f-5219-a70a-255e42583d57 | note | Responsibility - Project / Site Engineer
1e1c368b-64cd-5b5b-a437-b6e79ffd73ad | date | Date Completed:
6388a249-3345-585a-b094-a82a42091183 | checkpoint-no-value | 1.3 - Materials
104cfd90-1f66-5422-ba65-37d3da17529b | note | Frequency - Prior to commencing Works
04426826-43e9-5e13-9ab8-c8fd7051ae59 | note | Acceptance Criteria - Joint sealer shall be Dowsil 888 silicone joint sealant or approved equivalent.
d6909b33-132b-5a99-9c4d-9d6f19d6a2c7 | note | ○ Manufacturer’s instructions shall be provided to the Principal’s Representative prior to works commencing.
196df762-12b9-59fd-a43e-07f70198a115 | note | Reference Documents - Beca Spec 002 - 11.4.15 & 11.13.7
ec797054-95f2-4c19-80dd-7f72509b3664 | note | Aconex reference: FHPL-TRANSMIT-001667
8015b1e2-15af-5303-b7fc-371f61f1f555 | note | Inspection/Test Method - Verify
36243bbf-6174-5952-8558-8d07c07db877 | note | Record of conformity - This ITP signed
1c190af6-c392-51f3-a584-d381a85854fd | note | WP
1c777fe5-4e59-5b43-9ad5-8a5f0e3b41e7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
14fd5d8e-7b7b-5cf8-8ac8-3bceaaaa5b46 | note | Date Completed: 13/05/2024
62cb0e25-66ef-5565-83f6-0dac7af7e013 | section | 2.0 - Installation
80fb73ed-9148-5be9-84ce-96314adc85d5 | checkpoint | 2.1 - Define Area of Works
295d7320-011a-559c-a972-4aed72dd5c8d | note | Frequency - Prior to commencing works
c1de4dee-b4bc-55c7-90e3-f8968bd9f205 | note | Acceptance Criteria - All joints shall conform to the details and shall be constructed in the locations shown on the Drawings.
5939cd03-4fd1-5d3d-82f6-15ba24074494 | note | Reference Documents - Beca Spec 002 - 11.13.1 to 11.13.5
722d964b-67c3-5d03-ad10-f925c6693338 | note | Inspection/Test Method - Verify
63562468-3c10-533c-bd0c-8b100a446611 | note | Record of conformity - This ITP signed
c1528537-18cf-598f-b010-d783ae5d9fb6 | note | IP
0a85ca7f-f949-53e8-8449-464fb9998035 | note | Responsibility - Project / Site Engineer
8ceb191f-f8d6-5a46-8a48-8d31b0754533 | date | Date Completed:
9ad22714-45c3-594f-bafc-69cb92633a96 | checkpoint | 2.2 - PCC Curing
31744c6d-8b9e-5970-ba1d-a84974b2d5c0 | note | Frequency - Each Lot
230244ca-7f00-5c06-964a-22aed6882ccb | note | Acceptance Criteria - In areas where sealing works are planned, confirm PCC has been cured for a minimum of 7 days prior to sealing.
f93d14d2-c38d-5953-8a9c-76b4355bcc0c | note | Reference Documents - Beca Spec 002 - 11.13.7
3e1be03d-3f7e-59a2-8fc5-5da68d188d6e | note | Inspection/Test Method - Visual Inspection
d4439ab2-6542-58e0-aa12-6ef6c03afed2 | note | Record of conformity - This ITP signed
ed398638-07e7-5a6e-b3d2-236d2382808d | note | HP*
f36e53b7-aa1e-5d8b-840b-da3b6b51c409 | note | Responsibility - Project / Site Engineer
d18e00cc-bf4f-59b3-be8c-05e630d9b96b | date | Date Completed:
f9a30c12-b07c-5b7a-a70a-74c6dc3b696e | checkpoint | 2.3 - Cleaning of Joints
54a84945-1e69-597f-b3da-e8f0613d560c | note | Frequency - Each Lot
8d1e99cf-2220-5158-a456-6350bb440f3a | note | Acceptance Criteria - Joint faces shall be thoroughly cleaned and dry prior to sealing. This shall be approved by the Principal’s Representative.
76b748eb-a640-5b9f-abff-577239a7e83d | note | Reference Documents - Beca Spec 002 - 11.13.7
3f303229-fda5-55cd-80a2-1ec9c63f5bc3 | note | Inspection/Test Method - Visual Inspection
5029e114-3f54-5c3a-957a-b36a2e35ad46 | note | Record of conformity - This ITP Signed
a4970c7c-ab86-5b24-b946-10cfe343ba20 | note | HP
dd3d86b2-47be-5f2e-bb01-be9bb380d7c0 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a3590dfe-3c4f-5768-b7ae-73cb1bc9d759 | date | Date Completed:
ba83cded-4d09-50d7-a949-2a60a3a7c8c2 | signoff | AUTHORITY HOLDPOINT
9a279428-8bb3-5f72-acd3-3d377212d952 | checkpoint | 2.4 - Backing Rod Install
825ca411-5727-5ec3-ab0c-19d7c3092ad8 | note | Frequency - Each Lot
7905221d-1424-5c4b-b9c7-3761007aa3b9 | note | Acceptance Criteria - Backing rod to be installed to depth shown on the drawings.
4c33455f-d134-56b9-bd91-914522f6aaa4 | note | Reference Documents - Beca Spec 002 – 11.13.7
d2303ef6-434e-5eb4-a00e-a4ee33374713 | note | Inspection/Test Method - Visual Inspection
64a37ad5-f09b-52f9-b76b-c67f1920410f | note | Record of conformity - This ITP Signed
847a7d15-8584-5e8d-ada6-d4c079607b83 | note | IP
be167dd5-d048-5341-927a-74ada804837a | note | Responsibility - Project / Site Engineer
da094bf1-5076-5913-93c2-aaf21e393771 | date | Date Completed:
0439dd16-c209-52bc-9c79-8b4362871d01 | checkpoint | 2.5 - Sealant Install
5e294b05-1fc6-567f-850a-edc8fc6ef83d | note | Frequency - Each Lot
9e69eab8-128a-5236-9b3c-14420c4b12dc | note | Acceptance Criteria - Sealant to be tooled off to correct recess. Excess sealant to be removed from the surface of the concrete.
5318b95d-2c17-5177-be5b-77c7e07c7f66 | note | Reference Documents - Beca Spec 002 – 11.13.7
66de4527-e36e-5cf2-8bbb-f15f283e02da | note | Inspection/Test Method - Visual Inspection
165c9f15-ca4b-5e66-a171-a5fa68fd6053 | note | Record of conformity - This ITP signed
723c8b20-6353-5b5a-b67f-425d9e2bc5d0 | note | IP
873f9e41-1b9d-5139-aede-4a5e8a601dc0 | note | Responsibility - Project / Site Engineer
99785c1a-a191-5411-9d83-66073b0d8f49 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
2032242e-37a0-5afc-b658-cf9d20792b14 | note | This is to verify that the final inspection has been carried out in accordance with the Fulton Hogan’s Quality Procedures and Project Quality Strategy and the product is hereby certified to confirm with the contract specifications:
86eb545f-008f-5daf-9ba8-17e663686c8b | textbox | Print Name:
98c0cebe-8793-50d3-959c-8570dee248eb | textbox | Position:
6d2a49ff-3315-51d0-aca3-72cedec50543 | date | Work Completed On:
7347a2ab-2fd0-59f3-ba1f-0f8ea233c1f7 | date | Date:
3e319325-9222-45dd-a810-5c248b1c1af8 | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0015 - High Early Strength Lean Concrete Placement - Rev 0 | itp | ITP015 - High Early Strength Lean Concrete Placement
dfbc0e0a-0cb2-49ec-94fc-753028b5d0c2 | section | 1.0 - Preliminary Activities
6712e7e7-b913-4cad-a29c-d541f7808afb | checkpoint | 1.1 - Check for correct documentation
7944f4f4-2a7a-5b80-aa50-6767d0d2a5e8 | note | Frequency - Prior to commencing works
f78851a2-a7c1-5009-8726-89dff85b0b83 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
bd0154f6-5203-5aee-9602-24cd92746f32 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
737d535a-d507-5293-aee6-e96722b043f8 | note | Reference Documents - Current Revisions in Aconex, ACC
2a9991a1-400e-52d2-a532-7c07c7c0f57f | note | Inspection/Test Method - Verify
6c4719c8-cfd5-5c14-8b15-4824ff243cd5 | note | Record of conformity - This ITP signed
019d1d84-5721-5b7f-a59b-8509ce6e90b9 | note | HP*
e6cf1f99-cbf2-58eb-9268-b1748e0f9127 | note | Responsibility - Project / Site Engineer
8349b8d3-a86f-5134-93be-469508f9ce73 | date | Date Completed:
c2beb12b-988d-46c5-99a1-f440f3242bf0 | checkpoint | 1.2 - Implementation of all measures and controls
432a4e6e-49ef-58ed-a8a7-792bf669b352 | note | Frequency - Prior to commencing works
77347a37-aaa7-50b9-b751-d3da9b490b48 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
48b83619-aa46-5c5d-8f2c-cbd47ffd2b35 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
9ee7ac61-d46f-5209-9d46-a57bee5b6b9b | note | Inspection/Test Method - Visual Inspection
f2e279a5-f5d7-512a-9af9-61084ae4e1a0 | note | Record of conformity - This ITP signed
3b4c2eb5-4c7b-537e-a5a1-d528932c95b8 | note | HP*
ef2e5bba-dce8-51f0-a266-d8cb8d4e8862 | note | Responsibility - Project / Site Engineer, Site Supervisor
368187d3-5373-5a5b-9483-ec1d6809aa93 | date | Date Completed:
3d6b455e-7ff5-4469-bd24-cc6f221f9106 | checkpoint | 1.3 - Plant & Equipment Check
c131f583-5e95-53f8-8e87-f799b68dcd9b | note | Frequency - Prior to commencing works
c87e5796-f7d5-5b43-a828-389c557654eb | note | Acceptance Criteria - Plant and equipment items used in the Works shall be appropriate for the intended purpose and shall be maintained in good and serviceable condition at all times during which they are operating.
2508810e-4f7a-5111-9299-e2166eb1baad | note | Reference Documents - Beca Spec 002 13.3
2acf9b97-26ae-50ab-b157-0579f2313003 | note | Inspection/Test Method - Verify
40d5b898-284e-598a-9d79-7f6d5ec8ecbb | note | Record of conformity - This ITP signed
dba5bad5-efb6-5bd2-82a4-a771a148fb1b | note | HP*
477374f2-efd5-54d6-9b29-5f492eb70a16 | note | Responsibility - Project / Site Engineer, Site Supervisor
61d9259b-8795-5c12-b319-472fe87b587f | date | Date Completed:
2b718a27-b6f1-4b3d-b17c-ca03606fe914 | section | 2.0 - Production and Construction Trials
682b747b-5a82-4c22-81d8-df8c9c975ef7 | checkpoint-no-value | 2.1 - Mix Design
690fb887-aaf5-5226-9877-6b127492e350 | note | Frequency - Prior to works
a9f9ff38-7b55-5999-a385-0e900bf245c5 | note | Acceptance Criteria - Theoretical mix design and preliminary trial mix results to be submitted to the Principal’s Representative for review and acceptance prior to full trial mixing.
ef34d970-9ec5-569b-b469-92d280482227 | note | Reference Documents - Beca Spec 002 13.5.1
dbc726aa-9b61-50e0-9236-cf4018222388 | note | Inspection/Test Method - Verify
7ec50637-b5d7-5df8-b9b8-e5ea03059f97 | note | Record of conformity - This ITP Signed / test reports
2082d925-a5e5-5f6d-aed5-63a4acdf504f | note | HP
fe96dc1b-a0de-5c7e-844b-aa56582e1472 | note | Responsibility - Project / Site Engineer, Principal’s Representative
e2f09bb8-e62f-5e1b-a563-1758942f5573 | note | Date Completed: 13/09/2024
58ea452f-e285-5a95-9e6e-51546848526b | note | Principal's Representative - BecaCPL-GCOR-001171
6cc29a56-28fd-41df-82bf-5caacf9a0054 | signoff | AUTHORITY HOLDPOINT
d5308491-7824-4983-88a3-fe3bc5cf80e8 | checkpoint-no-value | 2.2 - Mix Design Report
1902e885-fe4b-5de8-bb33-b97d18928d62 | note | Frequency - Prior to works
99825237-1513-5b47-a4f9-14cdb6fbd36d | note | Acceptance Criteria - The theoretical mix design and preliminary trial mix results to be submitted not less than seven (7) working days prior to full trial mixing.
fefed4a2-c7a1-5821-9d41-c085c23a9c29 | note | Reference Documents - Beca Spec 002 13.5.2
c7a78384-dfc8-51f5-9036-0840ca99f8f9 | note | Inspection/Test Method - Verify
86e01fb3-8fa8-5538-8987-f640cec437ed | note | Record of conformity - This ITP Signed / test reports
7bdda105-e475-52a5-9ffe-6e50afbeffd8 | note | HP
67104860-a283-5f86-bd09-b8b1e3ec176f | note | Responsibility - Project / Site Engineer, Principal’s Representative
155e5b71-3c9c-57d3-a4b8-b5b060abd230 | note | Date Completed: 13/09/2024
52723341-65e8-5ae5-870c-17371d770fef | note | Principal's Representative - BecaCPL-GCOR-001171
fa88cff8-8569-4928-81b7-80bd21d6cd80 | signoff | AUTHORITY HOLDPOINT
9d264ec7-add2-4523-9072-8300d10e3b7b | checkpoint | 2.3 - Mixer Uniformity Test
39fbdbd6-5d06-5d8e-ad5a-d02c35330554 | note | Frequency - Prior to works
2feafff9-77db-59b5-ac91-4f22dd3efc47 | note | Acceptance Criteria - Mixer uniformity tests shall be undertaken on the fully operational mixing plant at least seven (7) days prior to undertaking production trial and submitted to the Principal’s Representative.
c16eb7fd-72c0-5540-ba90-0ea9e0f0c32d | note | Reference Documents - Beca Spec 002 13.6.1
264b4f9e-78d2-549a-8abe-4a07fc9c04da | note | Inspection/Test Method - Verify
e0edec82-428d-5bc1-a745-56f0bc2ba6c9 | note | Record of conformity - This ITP Signed
b3680153-cce4-58fe-b2e3-f758c7903ae3 | note | WP
35194a59-3a43-5c36-842d-5c56cd2b61aa | note | Responsibility - Project / Site Engineer, Principal’s Representative
63e223d4-8c2c-5ce1-97e4-5c41c3794a37 | date | Date Completed:
1de4b53c-11e2-48b5-9a89-4d47793e3511 | checkpoint | 2.4 - Production Trial
d25a798d-8df3-5b3a-b5c9-c5cf88574f2d | note | Frequency - Prior to works
c52d8fae-5752-57cc-92c3-f68a7a6b7be9 | note | Acceptance Criteria - A production trial must be completed as per the requirements in the specification.
fb197d40-b81c-5a53-9f40-7a0848d671dd | note | ○ The results and control procedures to be presented for review and approval by the Principal’s Representative.
5b529e85-01fd-5471-85a3-cc7e0065022e | note | Reference Documents - Beca Spec 002 13.6.1
563c748f-2c3e-57c6-b5f2-f00ee0a1b924 | note | Inspection/Test Method - Verify
be1949fb-49bb-5210-b8de-d94a7d613739 | note | Record of conformity - This ITP Signed
415d955e-e8e5-54ec-ae80-2ddbd50e9806 | note | HP
2f9850dd-98ac-526d-8d4e-d21e020f7fa8 | note | Responsibility - Project / Site Engineer, Principal’s Representative
4755571d-c41f-544b-97b4-80e8972d5ec0 | date | Date Completed:
41999afb-0e79-4922-a9bc-679bb1454545 | signoff | AUTHORITY HOLDPOINT
7e751069-aa7a-4226-9427-79d195756c82 | checkpoint-no-value | 2.5 - Compliance
1aaea2fb-0862-5079-ad10-7925bdd82753 | note | Frequency - Prior to works
0c8dbc77-ecc3-5b9e-b0f2-008c10230ada | note | Acceptance Criteria - Provide evidence to Principal’s Representative of concrete supplier demonstrating compliance to AS 1379 or is a third party accredited to AS 1379.
d84f4476-71ff-56cf-a3c4-4fef572eba5b | note | Reference Documents - Beca Spec 002 13.7
7101cd85-203e-5797-8cb6-5d817d1f2179 | note | Inspection/Test Method - Verify
c001f072-6adb-5fd8-9486-4e1925866f82 | note | Record of conformity - This ITP signed / evidence documents
f6694ee0-d210-5607-9700-c4e65ea9a4a0 | note | HP
50edde23-2933-56b0-b478-d16c475f2595 | note | Responsibility - Project / Site Engineer, Principal’s Representative
ed00a9df-0ce8-57ec-8ac4-acf65c95455d | note | Date Completed: 13/09/2024
cf51fd12-128c-538b-bde5-9e64cbf7c0ce | note | Principal's Representative - BecaCPL-GCOR-001171
e4318980-a89a-498d-ac9a-9280f991a23b | signoff | AUTHORITY HOLDPOINT
b4e29d90-5665-43d5-998a-f0fff578eb70 | section | 3.0 - Pre-Placement Activities
3809d3b0-56fd-4685-b8b4-1e09ae8a3836 | checkpoint | 3.3 - Surface preparation
9d5e19e6-7aa0-5a95-8111-4e454dd24bec | note | Frequency - Prior to works
e3bd3171-cd44-5af5-9a7e-d1d1cccfb054 | note | Acceptance Criteria - The surface must be clean and inspected by the Principal’s Representative prior to placing.
169928af-7fe9-5337-b889-23f4ba40159c | note | Reference Documents - Beca Spec 002 13.8.1.5
0c8ab2dd-d061-527c-847a-f6b344f10af4 | note | Inspection/Test Method - Verify
94d79d16-dfb7-58d5-bf0d-f4214fc52a30 | note | Record of conformity - This ITP signed
01ea45ac-e65d-5f54-affe-9e98b567dfda | note | HP
e349923d-b6f3-5ab3-a104-2b91a2c06302 | note | Responsibility - Project / Site Engineer, Principal’s Representative
cd097b79-d737-5421-b4e2-334bdf0dfbc5 | date | Date Completed:
74e2efbd-a79c-4ce3-b24d-e90583b74c08 | signoff | AUTHORITY HOLDPOINT
5262d2f8-2f71-489b-b857-ca06cb282b87 | checkpoint | 3.4 - Weather Conditions
6caf6fec-cfa2-56aa-a829-c287a6af9ba6 | note | Frequency - Prior to commencing works
45ba7fd4-3722-5daa-b9bf-55c6f4468e68 | note | Acceptance Criteria - HESLC shall not be placed when the shade temperature is below 5°C or above 35°C.
8a5364ea-2313-5bac-9a1f-9b293dcb7b95 | note | Reference Documents - Beca Spec 002 13.15
49c4d3f1-eae2-508d-b3f1-9d3296c9d2f0 | note | Inspection/Test Method - Verify
06f3d9a4-1c58-5464-8272-ec125f9b63d9 | note | Record of conformity - This ITP signed
b0297096-a032-5d1e-b7f2-fd073dfa4e21 | note | HP*
54f874d9-6831-5c9f-a6e4-7eedd5a12ce2 | note | Responsibility - Project / Site Engineer, Site Supervisor
97547145-88dd-5914-aa8a-56cbbd362bdd | date | Date Completed:
a1407878-971c-458b-9a7e-de1ab5605e91 | section | 4.0 - Placing Concrete
0507a2ed-1c43-4e70-890a-8f1142b40462 | checkpoint | 4.1 - Place, Spread and Compact Concrete
198a3453-4bf6-5ca5-b68f-444692cf8198 | note | Frequency - After completion of works
7680b5f8-0138-5407-8a54-42d62336f866 | note | Acceptance Criteria - Compaction of HESLC shall commence immediately after placing and shall be by internal vibration.
97aa61b3-6a5d-5c15-a4dd-875663f53968 | note | Reference Documents - Beca Spec 002 13.10
b4162197-ce02-56b8-8c14-c8d61ad0a7ec | note | Inspection/Test Method - Verify
a8b66a92-9486-5c8c-a5c7-3d825ce53d43 | note | Record of conformity - This ITP signed
94e3dd4a-c354-55d2-913f-91cb96ebf710 | note | IP
b2e5153c-0b85-5df3-9590-26439120c522 | note | Responsibility - Project / Site Engineer
be46e53f-2abd-5b7f-bbcd-0cb4f0d7ae63 | date | Date Completed:
3922c64b-5eb2-409d-b3b7-b403d2905d30 | checkpoint | 4.2 - Slump
e268e261-039f-583e-a796-c3c0bf173246 | note | Frequency - 1 test every 2 trucks
8d013726-3126-5a3a-95fa-5cfb8364b328 | note | Acceptance Criteria - 100mm +/- 20mm
be6c938b-6766-5da8-8a53-2be35de8289e | note | Reference Documents - Beca Spec 002
1779ad00-433b-5aec-b466-6a6f45219e24 | note | Inspection/Test Method - AS 1012.3.1
7a9d68bd-236f-5fb9-8b9f-8e5476f56534 | note | Record of conformity - NATA Test Certificate
babc4247-da89-53f6-8be8-c40801383605 | note | TP
bbd92bf4-d2fd-55eb-85ed-1fe463b3414f | note | Responsibility - Project / Site Engineer, Laboratory Technician
f761a99a-8c40-58fc-99c2-693dd338ce9e | date | Date Completed:
f4f6a52e-67cc-420f-b926-0e4b3d172c8d | checkpoint | 4.3 - Temperature
14c5c469-01dc-578b-aaf1-d632d8466bc6 | note | Frequency - 1 test every 2 trucks
0b5ee5cb-be0d-56ac-9466-d13a1e639996 | note | Acceptance Criteria - Minimum 10°C Maximum 30°C
6fd17808-4107-5121-8e61-0190ae37fedc | note | Reference Documents - Beca Spec 002 13.15
414c748b-c490-59e4-82aa-499c77e8ecfb | note | Inspection/Test Method - AS 1012.3.1
eb8c0ad9-0dc6-5995-9dfe-a3b79a59b855 | note | Record of conformity - NATA Test Certificate
1c3ce3f0-279e-5678-95cc-b61bb6b94424 | note | TP
13107dce-39a0-51d2-bc57-88e0fa901d33 | note | Responsibility - Project / Site Engineer, Laboratory Technician
9eee4560-09ce-57b6-98d8-dd5ac6709ee5 | date | Date Completed:
66240731-3b85-4826-8867-0188c1b6708b | checkpoint | 4.4 - Density of Cylinders
1dcad014-72b0-580c-896d-cad6cdd3b8ca | note | Frequency - 6 cylinders per Lot (same cylinders used for compressive strength)
b4d23261-a7e5-5e93-9668-f23a3aacedf6 | note | Acceptance Criteria - Results for information only. To be used to determine density of cores.
a9a32d5a-2cf4-54be-8603-320e9a2699f3 | note | Reference Documents - Beca Spec 002 13.17.3.6
08f6dbdb-93ec-5a8f-8ba0-6da359bf7d1d | note | Inspection/Test Method - AS
c80d4005-469d-5dc2-8e83-3a0b5846f89d | note | Record of conformity - NATA Test Certificate
9e4aa837-c55a-5e6e-b38b-55177c77dd50 | note | TP
4e697d4c-5c94-59fa-b889-6a2ad547bb54 | note | Responsibility - Project / Site Engineer, Laboratory Technician
3780cf11-63bb-5b7c-82ca-b48480d3dd2c | date | Date Completed:
16cfd622-7461-4109-b108-e0f0ef57be08 | checkpoint | 4.4 - Compressive Strength (7-day)
d7318c78-b9c2-5888-9999-e7d6257abcf2 | note | Frequency - 4 cylinders per Lot (same cylinders used for Density)
86980492-a652-5124-8380-c1b078c46f6a | note | Acceptance Criteria - Mean of the 4 cylinders to be minimum 10MPa and maximum 15MPa.
d079095e-5bd2-5047-b991-83f0460c0502 | note | Reference Documents - Beca Spec 002 13.5.1, 13.17.3.6
c2e00e97-b9a7-5c6e-ae69-55eca92b6446 | note | Inspection/Test Method - AS 1012.1, AS 1012.8, AS 1012.9
ed217bc4-1326-53d5-bf1a-2259e992356b | note | Record of conformity - NATA Test Certificate
04c09162-9be2-59c0-a507-2d76bf9194c4 | note | TP
3146a27d-074f-5de3-afa6-704c297ef0c3 | note | Responsibility - Project / Site Engineer, Principal’s Representative
d3ab9044-ef99-5639-9017-2712987f9d54 | date | Date Completed:
cbe4abae-ff1e-478d-b434-3d0fe258f8b0 | checkpoint | 4.5 - Compressive Strength (28-day)
14d20435-e543-5925-b31d-61c96e0754e5 | note | Frequency - 2 cylinders per Lot (same cylinders used for Density)
c4f7131a-fd02-500b-89df-74d7c4827700 | note | Acceptance Criteria - Each sample to be minimum 20MPa.
111b6e38-baf1-5917-9948-a981684b25b2 | note | Reference Documents - Beca Spec 002 13.17.3.6
3b7af89a-2fd2-5582-acc9-75f4d6356f5d | note | Inspection/Test Method - AS 1012.1, AS 1012.8, AS 1012.9
21b83c28-2f3e-578d-bb60-d738036d51e7 | note | Record of conformity - NATA Test Certificate
55d40b35-fd58-5994-8633-3b1846c3e7de | note | TP
0958e6a3-2480-5148-9acc-2707aa8a3eac | note | Responsibility - Project / Site Engineer, Principal’s Representative
322f68d4-95cd-513c-828a-8a12e623888e | date | Date Completed:
b55478d7-beb0-4753-bf39-36b977686a22 | section | 5.0 - Post-Placement
e1ecbfa8-be77-447c-b41f-91a19770aa03 | checkpoint | 5.1 - Construction Joints
f5716e6a-c228-5890-b1fc-6f41bf60ed17 | note | Frequency - Each Concrete Pour
822e004a-cfc8-5701-80c2-b38124bbbd4f | note | Acceptance Criteria - At the end of the day’s works, the HESLC to be feathered out and cut back before work restarts to give a straight, vertical face for full depth of layer.
991e214b-a324-5a1d-8826-35595e7047ce | note | ○ Edges of construction joints shall be painted or sprayed with bituminous emulsion.
9b5838f4-e83f-5d78-a095-9153083db635 | note | Reference Documents - Beca Spec 002 13.11.1
71a40074-8816-5dbb-b8b9-74e7e39b2fb3 | note | Inspection/Test Method - Verify
4ece3e36-a3f0-5e1d-a5f2-d7cef8123b47 | note | Record of conformity - This ITP Signed
38eb2330-8653-515c-9658-2ef5bf5bbc69 | note | IP
b47ea37e-416a-52f4-aaa0-3f28030725a1 | note | Responsibility - Project / Site Engineer
2ad772d0-d82a-544b-b176-7c8f8cd09edf | date | Date Completed:
22888a47-37bf-439a-aa02-1d55dcedade4 | checkpoint | 5.2 - Saw Cut Joints
d844226a-0d5e-5911-ba9a-9f573347673c | note | Frequency - Each Concrete Pour
c1d75f63-edfe-5dc4-a80a-df9412220ffd | note | Acceptance Criteria - HESLC to be sawcut into maximum slab spacing of 5m x 5m. Where pavement width is less than 5m the spacing shall be reduced to obtain slab dimension ratio of maximum 1:1.25.
0274fc1d-a0a1-5c41-b3a1-e58cc2d31cf4 | note | ○ Sawcut to be approximately one third of the layer depth.
a3a692db-5ed4-555c-9df7-2fbfbc1cb6fa | note | Reference Documents - Beca Spec 002 13.11.2
d81f8a7c-3cce-50fb-b821-afe2351f9aba | note | Inspection/Test Method - Verify
0cfdc788-f9ed-5373-9584-c0df96e6f26b | note | Record of conformity - This ITP Signed
9fa58922-7e05-5e5d-8dd9-78ada9d6e23e | note | IP
d562e3e3-50e8-59b5-913e-b8d3ab586c46 | note | Responsibility - Project / Site Engineer
389162fe-6238-54d5-ad14-e21bbe7f3f34 | date | Date Completed:
95953ac6-73b9-49dd-9d69-0640ad1e9571 | checkpoint | 5.3 - Layer Thickness
cea64afc-f762-5e98-9681-6e015b522cb6 | note | Frequency - Each Concrete Pour
b4148477-3aa8-5151-a5de-cf735bb73aaa | note | Acceptance Criteria - Finished surface of the HESLC to be picked up by a surveyor to determine the thickness of the layer.
83c7ed0d-1cdc-5db7-a534-8dbafa9d7d5d | note | Reference Documents - Beca Spec 002 13.17.3.4
a0ad0340-a950-5d9c-be86-bc34d632d744 | note | Inspection/Test Method - Verify
b8e3e630-4b57-5cc8-a59b-1ddec90966ed | note | Record of conformity - Survey Report
0e9c8a07-3c0b-53e7-8f93-fe4d7efaa67f | note | HP
9d171493-7d25-5ee3-a152-aa5861210ad6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
91943864-c9ac-5d94-b206-486c43219ac1 | date | Date Completed:
68f9d247-c764-41be-a855-17a6e87826f0 | signoff | AUTHORITY HOLDPOINT
31e8d669-82ee-4911-acf0-3f5040c60faa | checkpoint | 5.4 - Core Analysis – Density
8a32859c-6326-5a94-bfad-3c1b77f0c7bf | note | Frequency - Refer to markup in notes section
93b111bc-6750-536d-b57a-b167d9a3e7ed | note | ○ Aconex: BecaCPL- GCOR- 001038
3cc692e1-73c5-527a-885d-2c57b23acba5 | note | Acceptance Criteria - Cores shall be 120mm diameter.
f644fa61-c994-5fc2-8df1-492456b372fe | note | ○ Calculate the field density by comparing the density of individual cores with the average density of four (4) compressive strength cylinders taken.
b1eddd99-d299-58fc-9453-d33aaefaaf2f | note | ○ Field density to be not less than 98%. If the density is less than 98% then a Hold Point to be raised for the nonconforming Lot.
9676ae89-d884-5414-b875-8640a92ab949 | note | Reference Documents - Beca Spec 002 13.10.1, 13.17.3.6
8c142d85-2d87-5fba-bcaf-b81cf7214dbc | note | Inspection/Test Method - AS 1012.12
699297c0-a312-5aaf-8494-759917f169c4 | note | Record of conformity - NATA Test Certificate
96dab2b9-b40c-59ca-a412-382d18e893d8 | note | HP
360145fd-647c-5054-9656-c4ba6b553063 | note | Responsibility - Project / Site Engineer, Principal’s Representative
666d2443-3749-5d7a-9a1c-0e472a7d14bb | date | Date Completed:
ece3e311-0c3f-4fba-8f66-ecb2ca20e876 | signoff | AUTHORITY HOLDPOINT
19706174-acba-4f32-a556-9d706fc7e282 | checkpoint | 5.5 - Testing Records
063e25ab-0b06-5f4b-aada-48c43a54a028 | note | Frequency - During works
920f3643-3897-547a-9edc-a08af95f34f2 | note | Acceptance Criteria - Within three (3) weeks of completion of the Works, the Contractor shall supply two (2) copies of a report detailing the results of all quality control and testing undertaken.
d9ef0c7f-0d58-516c-8678-ca24c8756a61 | note | Reference Documents - Beca Spec 002 13.17.4
6c35228b-0aa6-54e5-94c2-f2e8784f97f0 | note | Inspection/Test Method - Verify
4c883190-17eb-5617-8001-1c778157c280 | note | Record of conformity - This ITP Signed
e68bc714-671d-5ed5-a051-d8179d95a353 | note | HP
8b8e84ca-616c-59fc-a610-56eeb0503ed9 | note | Responsibility - Project / Site Engineer, Principal’s Representative
1895af9d-ad24-553e-b0e3-93a6ef5f869c | date | Date Completed:
4a36c140-21b2-4a2b-a784-0bc385adbb65 | signoff | AUTHORITY HOLDPOINT
d711f7e7-c7d5-479f-be7c-4355519473d9 | checkpoint | 5.6 - Protection of Layer
24b8d90e-66b7-58b0-9f36-b3ae516dbb09 | note | Frequency - Prior to placing subsequent layer
485c7c4a-6d49-5efc-b6db-01b933afb611 | note | Acceptance Criteria - The Contractor shall protect the HESLC from damage until surface layers are placed. The layer shall not be covered by any further pavement layers under it has been accepted by the Principal’s Representative.
79615dd0-439e-585a-809f-a38198c4a0ff | note | Reference Documents - Beca Spec 002 13.16
297329e7-d81f-56b8-86c1-51f357a9bb22 | note | Inspection/Test Method - Verify
17eade7b-1b04-5cb6-984c-a27b2470e231 | note | Record of conformity - This ITP signed
75dae2b9-d1bf-5796-8a8e-dede46d87257 | note | HP
68d21345-fb7c-5b5f-bc54-aba360ab5f9d | note | Responsibility - Project / Site Engineer, Principal’s Representative
da4a7eb1-e932-5eac-ae88-e84ab23f68f1 | date | Date Completed:
22ceabd1-017f-4aa0-8cea-6d27a135d9eb | signoff | AUTHORITY HOLDPOINT
363ad996-7d75-43a6-aaf5-3344a19cc577 | checkpoint | 5.7 - Removal and Replacement of Defective Pavement Areas
3d0d5f43-8940-51d8-a952-03bed5b29970 | note | Frequency - After completion of works
bdce08f2-e264-5753-8632-35a84e07a7a1 | note | Acceptance Criteria - If required, defective pavement areas shall be removed and replaced as specified herein with pavements of thickness and quality required by the specifications.
5fe8f3a8-d4f6-5512-98d4-d9d20c24efd4 | note | Reference Documents - Beca Spec 002 13.13
bf2d7e60-a9a4-5b2a-8fba-714f41a1b796 | note | Inspection/Test Method - Verify
fe6a6ce0-8a8c-5a7b-ab9b-619775918fbf | note | Record of conformity - This ITP signed
db99968f-a872-5fd5-92bc-a381d79af903 | note | HP
76f382d2-7b39-544d-9219-e8db84c0c486 | note | Responsibility - Project / Site Engineer, Principal’s Representative
7c4db7a6-e8d3-516d-ab5b-f2c780fe2e77 | date | Date Completed:
a9bb2736-b53f-4e46-a4d2-82b7952032ca | signoff | AUTHORITY HOLDPOINT
d4b3bc14-209d-4ad8-a59b-994cf644c80a | checkpoint | Final Inspection
fb09fa88-8452-58fe-9547-4a9286c54640 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
c968d22d-31b1-58c7-bbdd-ee3958476419 | textbox | Print Name:
77552f1a-bb76-5cf3-a1fd-d5ec1f4d22fb | textbox | Position:
70826dfb-3325-56fe-b490-9de374be0465 | date | Work Completed On:
253be1d8-576f-5155-a005-1f7e75432430 | date | Date:
5acea7fd-33b5-4033-8602-aa75bb681f9c | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0016 - Asphalt Production - Airport Mix - Rev 0 | itp | ITP016 - Asphalt Production (Airport Mix)
b41961d5-4119-4626-b3fc-679d1745872b | section | 1.0 - General
213a28e7-7ceb-47e1-8bd3-6d8b4a54334c | checkpoint | 1.1 - Submission of ITP
bdb86153-7552-500e-8f93-f680066d86a0 | note | Frequency - Prior to commencing works
fc00ea1a-bdb0-535e-96d9-d1d31af385b1 | note | Acceptance Criteria - All relevant ITPs to be submitted to the Principal’s Representative.
de394c33-05bc-56eb-b400-797193b958f6 | note | Reference Documents - AfPA Sec 4.3 Cl 14-18
3e8e4dc0-efa5-5a4f-949b-73676461d3fa | note | Inspection/Test Method - Verify
107a0054-60a9-5b95-b574-dc4a1b8e6037 | note | Record of conformity - Aconex Correspondence
618aa47f-38a3-581c-9ddf-46f3bd9d4de7 | note | HP
0928a277-eb96-5151-9126-d20f482b2bd6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
8cf1fee8-4ef3-557f-8b06-e87675881549 | date | Date Completed:
cddbe3b0-a07b-4642-ab55-41a1af347dc2 | signoff | AUTHORITY HOLDPOINT
5e1b307b-9f93-42bc-8656-f2bc5f0a1a88 | checkpoint | 1.2 - Change in Mix Design
e0b10024-a57f-595c-92fc-6f472f6baf9f | note | Frequency - During the works
ec91254c-1b34-50a6-b95f-ffb034761db0 | note | Acceptance Criteria - Any change in the constituent materials or mixture design must be immediately reported to the Principal’s Representative. The Contractor must detail the proposed mixture design verification testing to ensure that the performance of the asphalt has not been adversely impacted by the change.
e82de9c5-6859-505d-b24c-def456c82a7e | note | Reference Documents - AfPA Sec 6.2 Cl 75-77
96f2221c-f401-564d-b7ea-637f3a01a5a5 | note | Inspection/Test Method - Test Method and Results
88837a84-5897-5cbe-bbd8-233af8d90d14 | note | Record of conformity - Hold Point Release Form
9cc8679a-a8f4-5e6b-adc4-24c1c650aae4 | note | HP
1213d8f5-3664-56cb-a4ca-c27548a507f9 | note | Responsibility - Project / Site Engineer, Principal’s Representative
d9dae5ca-98f6-5bb8-b964-5dbe4744915d | date | Date Completed:
e5c6366a-eea3-42d9-81e3-89b1aa01192a | signoff | AUTHORITY HOLDPOINT
14f868aa-5be4-4a6f-ae49-8b593c5881e2 | section | 2.0 - Manufacture of Asphalt
5cffe477-9835-40f4-833b-d716ad63ccd3 | checkpoint | 2.1 - Monitor and Control Asphalt Manufacture
1d2ab844-92d2-551b-979d-377b158615e8 | note | Frequency - During the works
588c88cd-202e-502d-aab3-be6702e9080a | note | Acceptance Criteria - The Contractor must produce asphalt to be consistent and uniform in temperature, and composition, consistent with the approved Construction Procedure.
7b52b539-ae14-51f8-a6f0-92142028951e | note | Reference Documents - AfPA Sec 9.1 Cl 138 - 142
01bb9c2a-1212-587a-8ace-2151d55c75c2 | note | Inspection/Test Method - Plant Process Controls
845fa0bd-025a-5dc3-a636-57f73d7a3890 | note | Record of conformity - Process Control Records
6534fbfc-a7fe-54a4-bde2-9b45bd3c5cc0 | note | TP
4c1df650-8e8f-5e9f-990e-52b6fa0c6846 | note | Responsibility - Laboratory manager
3cabcf51-1b16-5945-857e-4cd8d85a29f4 | date | Date Completed:
511eb577-fa50-42cc-b3a8-d197a255adab | checkpoint | 2.2 - Conformance of manufactured asphalt
edd20ad6-d43e-5830-8382-3a5c95ded1bb | note | Frequency - For each truck load of Asphalt
fd7ce31d-4a67-5830-a029-de1dea6cf910 | note | Acceptance Criteria - Segregated or not fully coated asphalt must not be used in the works. If required, the Principal’s Representative is to be advised of steps to be taken to remedy the non- conformance.
484d2af3-cfb0-5440-8294-2492c5b66ce1 | note | Reference Documents - AfPA Sec 9.1 Cl 142
a30ed5bc-78e8-5e2b-a59c-cdb36be3f79e | note | Inspection/Test Method - Visual
d91deb6b-787a-51e6-bfa0-97cfad63e1df | note | Record of conformity - Delivery Docket
850c1bda-5498-5ec3-9b5f-5242a738cb05 | note | HP
29139b30-193e-52cf-8c06-58f204891791 | note | Responsibility - Quality manager
b1c4df93-e48c-5001-a2ec-19ee9eaa9f91 | date | Date Completed:
ba1a3238-cda9-4991-9356-545f961e6fe1 | signoff | AUTHORITY HOLDPOINT
3b597e55-788b-442f-8b0a-52853d6ca78d | section | 3.0 - Sampling and Testing during Asphalt Production
23ccaa9d-a2a0-4bc0-b95c-995f35d929ee | checkpoint | 3.1 - Coarse Aggregate Testing
a589ffa6-3941-5878-81a1-9c3e11de7ecd | note | Frequency - During the works at prescribed frequency
278d875f-47d6-5154-a150-a69d627c22ba | note | Acceptance Criteria -
ed80d4a3-3ed5-5dc7-8320-d5fde476417b | note | – – – – – – – – –
02e8c6ae-1ce7-5ac3-b686-f17a00e63c38 | note | Test property ¦¦ Test method ¦¦ Test frequency
bd30ab7c-fd80-532a-8650-e77f51cb143b | note | – – – – – – – – –
5a6ff7b8-a14b-55e8-a820-b41edf1676ec | note | Particle size distribution (grading) ¦¦ AS 1141.11.1 ¦¦ 1 test per 500 tonnes aggregate
f3373b76-1de8-53eb-ab7f-140e9f5e7925 | note | Material Finer than 0.075 mm in Aggregates (by washing) ¦¦ AS 1141.11.1 ¦¦ 1 test per 500 tonnes aggregate
8def2738-96b2-5c0b-908e-c0c4a82729ee | note | Flakiness Index ¦¦ AS 1141.15 ¦¦ 1 test per 1000 tonnes aggregate
4585bbe8-3fc7-5b68-b719-fc803f891366 | note | Weak particles (including clay lumps, soft and friable particles) in coarse aggregate ¦¦ AS 1141.32 ¦¦ 1 test per 1000 tonnes aggregate
90fdd0c6-802a-5fa3-8db6-bb24d2371ebd | note | Particle density ¦¦ AS 1141.6.1 or AS 1141.6.2 ¦¦ 1 test per 2000 tonnes aggregate
5ae59ed8-0955-5e80-887a-3d5192b95415 | note | Water absorption ¦¦ AS 1141.6.1 or AS 1141.6.2 ¦¦ 1 test per 2000 tonnes aggregate
7a522877-0447-5986-95e1-4127f3c85984 | note | – – – – – – – – –
10128205-fe76-5770-a3e3-1b69eaf63b66 | note | Reference Documents - AfPA Sec 11.2.1 Cl 187 - 190
22ad8606-c742-51d8-989f-083af10caed0 | note | Inspection/Test Method - Test Method and Results
4da7247d-04bf-532a-82f2-6b3ca73c6f26 | note | Record of conformity - NATA Test Report
7dc3e140-2984-5312-8b1d-c4635d723512 | note | TP
f4aa7687-ab12-5718-82ee-824f34ce1a89 | note | Responsibility - Laboratory Manager
b380921e-6cc1-5dd4-b6f4-a949f56f6ef5 | date | Date Completed:
6eb9dd08-65e0-4eb0-aebc-e2750aab3017 | checkpoint | 3.2 - Fine Aggregate Testing
c6ed84fb-d0dc-5b5c-b7b2-50640acfa70a | note | Frequency - During the works at prescribed frequency
380f506a-f8ef-5887-bbe3-6fa922809534 | note | Acceptance Criteria -
0ac214ed-4103-5c42-9c7e-cea4cba6b163 | note | – – – – – – – – –
a3fac0a9-418a-5f2a-beff-5dc638a04395 | note | Test property ¦¦ Test method ¦¦ Test frequency
31505897-1742-57e8-9cd7-5a6a6546ab1c | note | – – – – – – – – –
7b01bf2f-7f4c-546a-9579-49fb4c964e28 | note | Particle size distribution (grading) ¦¦ AS 1141.11.1 ¦¦ 1 test per 500 tonnes aggregate
f2fd70b1-48a4-575a-a434-edd443668121 | note | Particle density ¦¦ AS 1141.5 ¦¦ 1 test per 2000 tonnes aggregate
5f189cf0-5ea0-5134-9622-cf4d4f1f49f6 | note | Water absorption ¦¦ AS 1141.5 ¦¦ 1 test per 2000 tonnes aggregate
421ede66-372b-5958-b960-7c97ea60a58b | note | – – – – – – – – –
2a8304d3-b91c-5f6d-8e11-c8e70d1bf852 | note | Test property ¦¦ Test method ¦¦ Test frequency
43cd3dc0-a854-555b-8a3c-5519754a65b1 | note | – – – – – – – – –
30ad53a0-d68a-5791-aabe-b01e7c757620 | note | Plasticity index ¦¦ AS 1289.3.3.1 ¦¦ 1 test per 2000 tonnes aggregate
d10de4e5-121e-5b87-be74-86104cc76a15 | note | – – – – – – – – –
7e0de98a-14c5-5b0f-a8b5-8aaf55f975ef | note | Reference Documents - AfPA Sec 11.2.2 Cl 192 - 196
a3f40e26-1053-5c1f-8c11-0aa7b4538e66 | note | Inspection/Test Method - Test Method and Results
60812e7c-09a0-543a-92b8-89ccf51aa220 | note | Record of conformity - NATA Test Report
7461fcd1-5fcc-560f-9166-10876c624148 | note | TP
22e1719d-8c71-5334-96a6-3aeca69cd5d6 | note | Responsibility - Laboratory Manager
8c63fffa-2dc6-5c74-a4ee-023c06a75be6 | date | Date Completed:
4033ea5a-2881-4b8a-a312-b6775b38ad27 | checkpoint | 3.3 - Binder Compliance Certificate
bebb093f-d2cf-57d0-ba1b-981fcb1628ff | note | Frequency - Every Delivery to Production Plant
0b00c7ab-15be-59e2-a39b-d3c9a7b27cef | note | Acceptance Criteria - A test certificate to be supplied for every delivery to the asphalt mixing plant.
b9d9ab14-df05-56cc-b48c-4d8a0eb8f4b0 | note | Reference Documents - AfPA Sec 11.2.4.1 Cl 200 - 201
0bdec986-d568-5350-98ce-bb7f458fbabe | note | Inspection/Test Method - Test Method and Results
09395b7d-1508-5b87-b5c6-318c9dcd70bb | note | Record of conformity - NATA Test Report
189a8f28-347a-5c9d-b8eb-ab4825164002 | note | TP
093d02dc-2d76-504b-ac94-593a4d60e15f | note | Responsibility - Laboratory Manager
753ebc6e-4fdb-50d6-812f-c7595c68bd22 | date | Date Completed:
dc8b5b2f-13b0-43b3-bb6a-4f7577c41a70 | checkpoint | 3.4 - Binder – Binder Consistency Testing or Confirmation
6fec9a16-ad29-5e15-9623-6e3c2cd92aca | note | Frequency - Every Delivery to Production Plant
30593879-397b-5bf5-afa3-65fd3cc173ba | note | Acceptance Criteria - For every batch of polymer modified binder production either:
9103259f-5c4d-54e5-a2e1-dbbca6a44ce6 | note | a. Provide written confirmation that the raw ingredients are consistent with the modified binder used to produce the asphalt mixture.
fa8306b5-0ed0-5994-9020-65c4d10f1c44 | note | b. Sample and test the binder according to Clause Cl 204.
10911447-8029-53b5-8bbf-d2d3e5d1330b | note | Reference Documents - AfPA Sec 11.2.4.1 Cl 202 - 206
72ee71a7-d799-5a3d-b3ef-9fece61cda14 | note | Inspection/Test Method - Written Confirmation/ Test Method and Results
04be4585-2cac-5d25-b9bf-3520fb6692c1 | note | Record of conformity - NATA Test Report
a2fdac23-cb4c-5a44-a0c8-a9832dd987c4 | note | TP
2973c3d1-6a8e-5465-9348-104299c4bfe5 | note | Responsibility - Laboratory Manager
b384c805-b2f4-58a3-a5a2-0555779d1e61 | date | Date Completed:
59c3cdd1-cd11-40e8-854d-857a37b065c2 | checkpoint | 3.5 - Binder – Point of Production Testing
bfabd134-3db0-55fa-94e2-ce9f9c34e71c | note | Frequency - Every Production Batch
26eb3474-e3cc-5363-b5e1-0b7267e44a66 | note | Acceptance Criteria - Every production batch of binder must be sampled at the point of production and tested by the Contractor, for:
28667a45-5b11-5a1d-9a66-d424e1d39fa3 | note | a. Viscosity at 165°C according to ATM-111.
a399fc40-20aa-5af1-8bb0-84136c627ecd | note | b. Torsional recovery at 25°C, 30 s according to ATM-122.
ec012d61-e469-5539-919b-4f74843b87c6 | note | c. Softening point according to AG: PT/T131.
b05dbcff-c507-57fe-9a85-aba99b79d539 | note | Reference Documents - AfPA sec 11.2.4.1 Cl 207 - 208
91bed82c-b871-5b74-a566-7ae06895b1ac | note | Inspection/Test Method - Test Method and Results
c7de522e-f3a1-5d53-af75-fdf7f0c97d3d | note | Record of conformity - NATA Test Report
c92ec59c-90be-5674-986a-e85278bfc01f | note | TP
05230d3b-6692-5df0-ae61-47bac645a28d | note | Responsibility - Laboratory Manager
2c1f15e6-476f-5584-b029-c28fef3dcc28 | date | Date Completed:
c699d2da-112f-422a-a713-5b7b435d4d55 | checkpoint | 3.6 - Binder – Addition Production Testing
2e8318e4-8141-523e-893d-46d1635ac860 | note | Frequency - Every Ten modified production batches
a3b2d33c-5853-5f24-931a-762beaf467e8 | note | Acceptance Criteria - Additional production testing must be performed at least once every ten modified binder production batches, or once every 250 tonnes of modified binder production, whichever is more often.
5f167e36-559e-50e9-bf04-0c11d11ab8c4 | note | Reference Documents - AfPA sec 11.2.4.1 Cl 209 - 212
e87de267-89c7-5062-b388-14afc99aeb05 | note | Inspection/Test Method - Test Method and Results
c355b42e-2334-589b-be88-a77530fbbbac | note | Record of conformity - NATA Test Report
8c623087-ca89-569e-b052-bd8261fa86fc | note | TP
c95c3355-3bf4-54fa-b96f-a4e51c90e54f | note | Responsibility - Laboratory Manager
55f7f0ef-447d-5c5d-aedd-063b9ece7136 | date | Date Completed:
6df675b8-46ab-48da-ade5-9575b3b8d1ca | checkpoint | 3.7 - Binder – Point of Delivery Sampling
18bbc93f-ef11-5d51-9db0-4b33cba1ddba | note | Frequency - Prior to the commencement of asphalt production
0b8178b9-e58b-5149-a803-5461b414f811 | note | Acceptance Criteria - Binder must be sampled for each delivery vessel/tank, not more than four hours prior to the commencement of asphalt production or transfer of binder to the asphalt product plant binder storage tank.
32360183-99a3-5b0d-8608-190fabf75db3 | note | ○ A minimum of two samples, each not less than 0.5 L in volume, must be obtained in accordance with ATM-101.
8021f184-afbd-57c5-8ac2-0934eddbf017 | note | Reference Documents - AfPA Sec 11.2.4.5 Cl. 213 - 219
f3d07810-5a00-51e4-9435-25503bfd7619 | note | Inspection/Test Method - Test Method and Results
1ba73a66-9465-5cc7-8693-cbf9f861638b | note | Record of conformity - Sampling Process Control Charts
91316cb1-3e3a-54b1-a7a9-0f379a71da1b | note | WP
2a2045d7-e46a-5745-93dc-2e1c6801b2c0 | note | Responsibility - Laboratory Manager
23bed54d-7d7a-5cb8-a933-3109a2d53563 | date | Date Completed:
ad006504-9776-4bb9-af98-ae8d634ec43a | checkpoint | 3.8 - Point of Delivery Binder Testing
2c481049-9b18-5ea1-93f9-25926ef860b1 | note | Frequency - Before each production shift
ec345c81-bc09-5647-9a49-362d59da0bbb | note | Acceptance Criteria - The point of delivery sample, to be retained for point of delivery testing, must be tested by the Contractor, prior to the commencement of asphalt production for the work period, for:
a0179994-a9d1-5485-b5f3-f085cb918142 | note | a. Viscosity at 165°C according to ATM-111.
5adc816b-ad8b-5114-a7b1-2014f1a7d6a2 | note | b. Torsional recovery at 25°C, 30 s according to ATM-122.
b7d1fc02-9b70-59d6-a283-89ef40c92066 | note | c. Softening point according to AG:PT/T131.
0756f038-4269-54cf-84e7-cca22efd4bba | note | Reference Documents - AfPA Sec 11.2.4.6 Cl 220 - 221, Sec 12.2.4. Cl 275
c0755e9e-7bd1-59a2-952f-e511cd0011cb | note | Inspection/Test Method - Test Method and Results
57947390-eb09-5b86-8f4e-ba5a1a96541e | note | Record of conformity - NATA Test Report
a154cded-a9cc-551c-a000-e10bc90c566a | note | HP
d809409a-ea71-5ba8-9fd9-1301e7cfce56 | note | Responsibility - Laboratory Manager
f9dc76d4-084d-5928-b723-c75872d3cd2a | date | Date Completed:
f101fb55-9014-4442-b49e-d709cb525aec | signoff | AUTHORITY HOLDPOINT
8c8f4048-3830-4521-8212-baacf0bc7a37 | checkpoint | 3.9 - Point of Delivery Binder Testing
dbf1b64a-429e-5988-93b8-4f7fb3f07ace | note | Frequency - If binder test results nonconforming
d026923b-cb3c-565f-a179-78dd41a82950 | note | Acceptance Criteria - If required, the Contractor must prepare and submit a disposition regarding the binder point of delivery test result for approval by the Principal’s Representative.
f8f9e935-37e6-528c-8642-930dbf3beb34 | note | Reference Documents - AfPA Sec 12.2.4.6 Cl 220
3a6fc9c6-d9b2-5bdb-95dd-b90daee15515 | note | Inspection/Test Method - Test Method and Results
b29f90e5-38b4-5367-ad4f-9f3bafe0e921 | note | Record of conformity - NATA Test Report
6daceb26-ed63-5010-b6cd-20b47aba59bc | note | HP
e8975e6d-8ed6-587b-b772-b303da3efae0 | note | Responsibility - Laboratory Manager
c4a30661-a1be-5324-85ff-efcd3cbe1721 | date | Date Completed:
a7411e21-30a6-4bcb-b471-2825cd91a494 | signoff | AUTHORITY HOLDPOINT
257a3c60-7c42-46ae-8e04-7956a9eff190 | checkpoint | 3.10 - Tack Coat Testing
1a4ad729-36ee-51c6-ae73-bae92326454b | note | Frequency - Every Delivery to Site
8c6e8380-eadd-591a-9eb0-3cec33dedf9d | note | Acceptance Criteria - A test certificate which demonstrates that the tack coat complies with AS 1160 or approved modified tack coat production properties, must be supplied for every delivery to site
5e000a3f-e3d8-567c-bc44-dcb03e02b32f | note | Reference Documents - AfPA Sec 11.2.5 Cl 222
19e722d2-5038-514a-a51d-893baed51deb | note | Inspection/Test Method - Test Method and Results
c1b8d57c-8a01-5186-a49d-904ecd63bd2f | note | Record of conformity - NATA Test Report
9f89b204-d8c9-586c-862f-1fafca77c1fc | note | TP
46478128-8323-5fb6-b96a-d99f22ca1deb | note | Responsibility - Laboratory Manager
0b8bac05-3628-5471-a51b-abbcdda5d3a2 | date | Date Completed:
da8f8b5c-2011-4d4a-8168-a2611612fb53 | checkpoint | 3.11 - Asphalt Production Testing
6d0c45b3-1fdd-590a-ab81-96201165568c | note | Frequency - During each production shift as prescribed by Table 16
74559471-b76c-52c9-96e3-486587055b7c | note | Acceptance Criteria -
9e8a9a21-f829-590e-bc3b-784ee8a02205 | note | – – – – – – – – –
fa40e1d4-6611-51d0-b793-05a1ed5bbe39 | note | Tonnes of Asphalt in the Lot ¦¦ Number of test sets
03423c16-0592-5b0a-9f07-5f1b9ae5ac8c | note | – – – – – – – – –
3b5af6e6-edff-5f8a-87a2-14888f2dba2c | note | Not greater than 300 tonnes ¦¦ 2
09f194a9-40f2-5453-a377-91cf8d4036c3 | note | 300 to 600 tonnes ¦¦ 3
0b1c640a-bc2d-56bc-8871-cb9f3f3ff083 | note | 600 to 1,000 tonnes ¦¦ 4
c791ee2f-e7c4-5d5e-ab4f-349cae9f5e41 | note | Greater than 1,000 tonnes ¦¦ 5
cbe5cff0-25e7-583f-9bcc-4499dc85e068 | note | – – – – – – – – –
ed4837bc-1654-5cca-85ea-a383853347d3 | note | Reference Documents - AfPA Sec 11.3 Cl. 222 - 223
2f4a9018-277e-51f7-940d-b48eb4c5194e | note | Inspection/Test Method - Test Method and Results
544dff85-7e8e-5eeb-b052-a2ac149f2350 | note | Record of conformity - NATA Test Report
4e629fe5-85c1-5a40-9ac5-afe0e13cbd8f | note | TP
5c0fe24c-e79b-58d2-9c0f-30063f210cc8 | note | Responsibility - Laboratory Manager
28ead5a8-bd0f-5af9-8aaa-f97965b9c592 | date | Date Completed:
764137e8-9d81-4d10-8dc9-0ea4dc20ad92 | checkpoint | 3.12 - Shift Usage Calculations
faaf521b-92a6-50df-8535-ec736841d65a | note | Frequency - For each Production Shift
24e7f157-c004-532f-a3ab-7507c5741919 | note | Acceptance Criteria - For each production Lot calculate; bitumen usage, mass of asphalt produced & average bitumen content
f5ac51c1-f9e3-5d01-a45d-4f2d89392e1a | note | Reference Documents - AfPA Sec 11.3 Cl. 231
3b0a2aee-502a-5ef3-8950-a639eceab280 | note | Inspection/Test Method - Test Method and Results
2af0204a-8661-5666-b8f9-cdb8cc23aa95 | note | Record of conformity -
d4a1286d-976f-55f0-ae4c-2cf06b4bfd7c | note | TP
e218ab39-4df2-5c12-9dcd-893f9f6c4899 | note | Responsibility - Quality Manager
8730c74a-c1b2-5223-9292-cac37675767c | date | Date Completed:
9c429be7-1d6e-4cd7-89c2-88c6e935d0dc | checkpoint | Final Inspection
446f4f0d-6b42-57b4-9d71-8605f0ad6a62 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality/System Procedures and verifies lot compliance with specifications.
c4ccd037-d93b-5d43-bc88-6900cdd0f281 | textbox | Print Name:
4d872769-1e8f-57df-8f5e-dff23968f387 | textbox | Position:
c6caefae-8487-5714-b3b5-0f639054a1ca | date | Work Completed On:
0fb1d074-49ad-5ce7-aa18-408c0e89bee0 | date | Date:
02f54b75-6d21-4c45-bcc5-2740fdfbccb8 | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0017 - Asphalt Production - 14H Mix - Rev 0 | itp | ITP017 - Asphalt Production - 14H Mix
f86777f9-a770-4934-a24b-541bc96183de | section | 1.0 - Production of Asphalt
eaaec954-116d-4024-87db-232a2a30ee5f | checkpoint | 1.1 - Temperature
2136a98f-0f15-5f52-85c7-06d7028892b8 | note | Frequency - Every loaded truck or at intervals of 15 minutes if more than one truck is dispatched in 15 minutes.
e26f2526-7f2a-5df3-9364-36f41f40718b | note | Acceptance Criteria - ≤175°C
68626ca3-b1c7-5a27-a698-395cb41050cb | note | Reference Documents - Section 407.11(a), 407.15
2abcfc10-e37c-5778-b206-1113eefbbd80 | note | Method - Thermometer
0251ebb7-b7fc-5bc0-98fc-7c23769607e9 | note | Record - Load inspection sheet / docket
d036dbfb-a5e3-5dd5-8486-2e3efa8d4ddd | note | Responsibility - Plant Operator / Technician
88336bbf-a546-5acd-bd41-83c71158ad15 | date | Date Completed:
02b6066e-899d-439a-949b-bf2d3ec2a824 | checkpoint | 1.2 - Temperature
79a510f0-dd9b-58d2-8556-dfe630b98371 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
920a332e-20c5-532e-beb8-53a249d0da72 | note | Acceptance Criteria - ≤175°C
716ca1ed-929b-5061-80ff-5b1fa73e56d6 | note | Reference Documents - Internal
fce07e83-4571-51fd-9a57-b44fc79d50f5 | note | Method - Thermometer
5a440112-749a-586a-888b-be44fb68dd59 | note | Record - Load inspection sheet / test report
e2987813-6e2f-5985-a6ac-262145909a8f | note | Responsibility - Technician
59387d15-698d-5b0d-a743-e95deca5b8a0 | date | Date Completed:
743a8212-06f3-426a-a48f-e99cdecb310e | checkpoint | 1.3 - Visual inspection for segregation, uncoated particles, separated binder, excess binder or overheating
1018d5ac-5d5f-59ff-9719-9e106c2ca447 | note | Frequency - Every loaded truck
2ae6731c-f507-5d24-bdcf-a9be66dd32f1 | note | Acceptance Criteria - >95% coarse aggregate coated with binder, no obvious separated binder or uncoated particles
0c1149d4-90aa-5652-801f-03844b21b09f | note | Reference Documents - Section 407.11 (b)
adfe9b46-8eea-5c12-9109-db5859473831 | note | Method - Visual check
10402f32-95fa-5554-883b-a881b5bf552d | note | Record - Load inspection sheet
d2106aff-5e01-584a-9213-6f8f39e37029 | note | Responsibility - Plant Operator
cfd97c38-5421-5620-b1e4-4c96a69d1469 | date | Date Completed:
040d8861-3f13-47d8-ab6f-7de1efd2e105 | checkpoint | 1.4 - Visual inspection for segregation, uncoated particles, separated binder, excess binder or overheating
a0a3cd7a-8969-57f0-b6a6-f2afa58ca70d | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
58a1b18f-43b5-5782-8950-822e412047b2 | note | Acceptance Criteria - >95% coarse aggregate coated with binder, no obvious separated binder or uncoated particles
2ecac746-9770-52be-957c-2856fe99250e | note | Reference Documents - Internal
1a4c19c5-e9c1-502f-aea6-81c810e62c27 | note | Method - Visual check
250ca365-f8fe-5c62-b2d1-01a23e1baae4 | note | Record - Load inspection sheet
4e8a0022-37b3-5eab-9bf5-e441ce13cc92 | note | Responsibility - Technician
767bcba7-e694-574e-9bb2-33ee214d854c | date | Date Completed:
d78471cf-c969-4471-928b-c942877fdcee | checkpoint | 1.5 - Maximum density
02444fba-2830-54bb-a705-ab1583a61bc7 | note | Frequency - On every production day
74334de1-e815-5bfb-ba81-3b67c6d6ca11 | note | Acceptance Criteria - ± 35 kg/m3 of its 6-point rolling average
65f1c12f-22c0-507b-bfb8-0bb6ac8f984b | note | Reference Documents - Section 407.11(e), 407.15
a123ccd7-18f7-5523-aa3b-7c9103a7fc6f | note | Method - AS2891.7.1
9ef899f2-fffa-5675-89dd-74a9925b4bc0 | note | Record - NATA-endorsed test report
aa50b84a-8988-5a34-b4a3-e914bc380ae0 | note | Responsibility - Technician
27d00282-d869-5768-a3a1-3cb441453f77 | date | Date Completed:
9530b9eb-8080-49ad-9361-898907e44dbb | checkpoint | 1.6 - Binder content
d5c44728-de7b-56e1-855e-7132303988d9 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
4093e520-9d53-5a08-a182-7516042f0d97 | note | Acceptance Criteria - ±0.3% of mix design specification
b00a84b8-7aa1-5e4b-b901-b5a198eaa074 | note | Reference Documents - Section 407.10, 407.15, 407.11
dd8ab117-c9a8-524c-81e9-d173e9ff402e | note | Method - AS2891.3.3 or AGPT/T234
8b6ffe09-c588-5b80-b826-7a1bbfd2b339 | note | Record - NATA-endorsed test report
6d97f0fd-6496-5194-9a83-17f5d888cca0 | note | Responsibility - Technician
df8027cf-71ed-57f1-9f23-ac47475ea03f | date | Date Completed:
b29a3f10-60ef-48ca-a517-26fc00581ffc | checkpoint | 1.7 - Full sieve analysis
f0673b06-a08c-5b88-9219-306a17a575b2 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
1c0c29a2-9aa6-55d5-8694-2f7c3d001351 | note | Acceptance Criteria - See Table 1 of this document
b62f08c9-2498-58db-b7ff-6c1c4882336d | note | – – – – – – – – –
ad595973-74f5-559f-8826-1c783fafd1f9 | note | Table 1: Production tolerances for mix grading (Table 407.101 in DTP Section 407)
1986e833-45bb-5d3d-bfb7-0734c5f003d5 | note | Sieve size AS (mm) ¦¦ Size 7 ¦¦ Size 10 ¦¦ Size 14 ¦¦ Size 20
a562349c-9085-51b6-97aa-5c2969948449 | note | – – – – – – – – –
750b82b3-32bf-5faf-91b5-d1a2f4954f90 | note | 37.5 ¦¦ Nil ¦¦ Nil ¦¦ Nil ¦¦ Nil
63bbcf48-8dc4-5e00-9708-fe1412642bf7 | note | 26.5 ¦¦ Nil ¦¦ Nil ¦¦ Nil ¦¦ Nil
feff2b7e-4e12-5cdf-a6ba-579ab2e97326 | note | 19 ¦¦ Nil ¦¦ Nil ¦¦ Nil ¦¦ ± 6
309ca4e4-d840-5f85-b6fe-28aecd1ccad3 | note | 13.2 ¦¦ Nil ¦¦ Nil ¦¦ ± 6 ¦¦ ± 6
4e5e2d66-ef24-5631-929a-709514186e50 | note | 9.5 ¦¦ Nil ¦¦ ± 6 ¦¦ ± 6 ¦¦ ± 6
61f2e34a-5c7a-5b05-9751-9c286908d8ac | note | 6.70 - 4.75 ¦¦ ± 6 ¦¦ ± 6 ¦¦ ± 6 ¦¦ ± 6
d5026ce2-fc7c-5121-88f8-cad462df8a5e | note | 2.36 – 0.600 ¦¦ ± 5 ¦¦ ± 5 ¦¦ ± 5 ¦¦ ± 5
4d6a97d1-0796-5cc4-a5e9-8e2ba8104595 | note | 0.300 – 0.150 ¦¦ ± 3 ¦¦ ± 3 ¦¦ ± 3 ¦¦ ± 3
f99a305b-efb0-53e1-92c0-1f24f9fe98c1 | note | 0.075 ¦¦ ± 1.0 ¦¦ ± 1.0 ¦¦ ± 1.0 ¦¦ ± 1.0
5a9d41f4-d17e-5767-b2c9-da52f87f5a97 | note | – – – – – – – – –
b57ad8a8-eee3-5246-8447-20280811450f | note | Reference Documents - Section 407.10, 407.15, 407.11
646a96cf-e543-562d-9a24-918a99a87666 | note | Method - AS2891.3.3 or AGPT/T234
c6a0205c-ae02-5244-82e2-8f57d4b75a7c | note | Record - NATA-endorsed test report
29eeeffa-264f-51d2-b315-51044e0fd4ff | note | Responsibility - Technician
3d932bf7-07d0-54d7-87ae-45508e749800 | date | Date Completed:
763b54f1-29b7-4eaa-bac1-52b4bc08f122 | checkpoint | 1.8 - Moisture content
863688e9-5ca2-5f3a-9a41-3585e2198bb7 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
5bd2c25d-e131-50c2-a5c1-637769a96ab7 | note | Acceptance Criteria - ≤0.5% moisture
2645a2de-a383-5afc-8501-45b50203adf6 | note | Reference Documents - Section 407.11 (b)
f3fb828c-12b7-546e-9438-2a91b5723f9d | note | Method - RC 211.01
5a4cf3ae-3975-59bf-8852-70fe1e08e5c2 | note | Record - NATA-endorsed test report
286f3db1-4a4b-5d83-9a79-524eb1cb5792 | note | Responsibility - Technician
a68a7adb-9b0c-55d8-870a-5ca2bc037fab | date | Date Completed:
1090299c-4a54-4d52-b60f-93012ebb2b05 | section | 2.0 - RAP Testing - RAP Level 1 and 2 (as per Table 407.121 Section 407)
2671db02-eef4-4e14-89d7-ec6052cca18e | checkpoint | 2.1 - Moisture content of RAP
fa4b27d3-15c6-506c-a591-d59718edc1a1 | note | Frequency - One test per 500 tonnes of RAP
569097ff-6fed-5066-b163-48d6b1d87dfc | note | Acceptance Criteria - Not exceeding the maximum moisture content acceptable for the asphalt plant nominated in the RAP Management Plan – Fulton Hogan Infrastructure Services. Any materials with moisture content greater than the nominated moisture content should be allowed to drain before being utilised
4d99a431-c908-5185-b14a-6bc6df2aa691 | note | Reference Documents - Section 407.13(c), FH RAP, Management Plan Section 3.2
2aca144f-9ec3-57d1-a4c4-7ce0f939f963 | note | Method - AS2891.10
b4f62afa-b0ac-5586-ab28-431dc27f1d12 | note | Record - NATA-endorsed test report
d1c25ef9-c694-5a0a-b1db-d5c3b7f9f616 | note | Responsibility - Technician / RAP Yard Supervisor
c7d86439-f754-5e47-af6c-b941c93dc36c | date | Date Completed:
6f582191-4b15-445c-a3ac-b0a7071367d4 | checkpoint | 2.2 - Binder content of RAP
31ba157a-abad-5cf8-9799-db4b3b34fd2a | note | Frequency - One test per 500 tonnes of RAP
7622cb69-d19a-50f2-953f-a94324340172 | note | Acceptance Criteria - ± 0.5 of target binder content
f27ecee2-29b3-5371-a504-1932adef6c00 | note | ○ 1 out of 10 consecutive results is allowed outside tolerance
edfb08bf-fce3-5257-afe0-62d8a94c7708 | note | Reference Documents - Section 407.13(c), 407.11
d82a0091-a207-54f1-be61-9d791adf5d16 | note | Method - AS2891.3.3
a345f482-d7b1-543f-9b56-8c2f19432367 | note | Record - NATA-endorsed test report
ae4ced9e-da1b-5cf9-b76b-df1790026fb0 | note | Responsibility - Technician/ RAP Yard Supervisor
9f1500ff-b0fe-57bb-95ad-2c2ac811d418 | date | Date Completed:
0b835721-220f-4456-a337-c8ec984de7c2 | checkpoint | 2.3 - Sieve analysis of RAP
62e86c66-0fe2-5ded-a7e2-b67de9c29e39 | note | Frequency - One test per 500 tonnes of RAP
b95bc3aa-cc43-5446-86cc-bc51c5570192 | note | Acceptance Criteria - See Table 2 of this document
bac122dd-9df9-57c0-afe8-1515bb54f248 | note | – – – – – – – – –
7efaf993-0f42-5347-b4c1-5a3f5d57311b | note | Table 2: RAP grading tolerances (Table 407.131 in DTP Section 407)
2e960692-6314-51c8-b9f7-68854cead5ec | note | Description ¦¦ Tolerance (from target grading) ¦¦ Allowable number of results outside of tolerance
8d77efa3-47d6-5346-9f34-f86b3093bfc8 | note | – – – – – – – – –
015e08a4-383d-5476-9d79-a6aaaa04dc01 | note | Passing 26.5 mm sieve and larger ¦¦ ± 10 ¦¦ 1 out of 5 consecutive results
96e479ac-1008-570a-99a3-ed582b426d6f | note | Passing 4.75 mm to 19.0 mm sieve ¦¦ ± 8 ¦¦ 1 out of 5 consecutive results
c02f4821-aa32-5c9f-a7b6-fbe8d7242eff | note | Passing 1.18 mm and 2.36 mm ¦¦ ± 6 ¦¦ 1 out of 5 consecutive results
75f728e5-4a9a-55e0-9007-ce97ab775d89 | note | Passing 0.300 mm and 0.600 mm ¦¦ ± 5 ¦¦ 1 out of 5 consecutive results
cd8d2ed2-5fc0-59b3-91a5-17264ce1ed7c | note | Passing 0.150 mm ¦¦ ± 3 ¦¦ 1 out of 5 consecutive results
9d255828-626a-56ff-810b-8ca4f640b4d5 | note | Passing 0.075 mm ¦¦ ± 2 ¦¦ 1 out of 10 consecutive results
4f29aa99-6ce8-590e-b1b0-895c58a2fe7b | note | – – – – – – – – –
1e3611a3-90df-594f-8bf4-8394902af3bf | note | Reference Documents - Section 407.13(c)
0a914e54-db27-5b23-9713-dc16c30e2673 | note | Method - AS2891.3.3
9b5e61aa-9fe1-5b70-bc66-4b2be2389863 | note | Record - NATA-endorsed test report
5682ed41-dfdc-5f26-8a7a-29957d686185 | note | Responsibility - Technician/ RAP Yard Supervisor
9ea1785d-de8f-5d23-8fcb-3f6e4d31e9e7 | date | Date Completed:
9021a7a2-e8e4-4164-a22e-154398838c07 | section | 3.0 - RAP Testing - RAP Level 2 (as per Table 407.121 Section 407)
a70a1afc-6796-4f98-a60c-b1322b06c88a | checkpoint | 3.1 - Binder viscosity
c9b859f2-2f52-526e-b046-dfd87f11dff2 | note | Frequency - One test per 1000 tonnes lot of RAP used for Level 2 mixes as per Table 407.121
638e570c-ad4d-51cb-9036-cce9b4bc8d16 | note | Acceptance Criteria - Viscosity of the blend of virgin and RAP binder shall fall within the range in table
57787fb8-7372-531d-abdf-3e0e09d1b881 | note | – – – – – – – – –
0b8c88ac-b440-5647-a9ba-da4a4e6ccc73 | note | Specified Binder Class ¦¦ Binder Blend Viscosity Range (Pa.s @ 60°C)
b2e34c0d-c16e-5e62-b89b-4ec57bc22a0d | note | – – – – – – – – –
a8c51968-b615-5b12-a5ea-5a9cbf3ba3d1 | note | C170 ¦¦ 170 – 240
ea70d51e-d6bc-5d05-8821-6ff2b17b71d8 | note | C320 ¦¦ 320 – 500
ef9cbafd-cd29-5ab5-b40f-f967279f213c | note | C600 ¦¦ 600 – 880
099695d9-d773-5540-9ee9-4cdb0b41adf3 | note | – – – – – – – – –
e9422418-3469-5762-a057-29d7ca81f80e | note | Reference Documents - Section 407.13(e)
dcab2c91-298e-5731-9c9e-3858ffc3c7af | note | Method - AGPT/T192 or AS 2341.2, AGPT/T193
d3aa5934-9e09-546f-9635-9462a80030ef | note | Record - NATA-endorsed test report
a8a5d9f8-2092-59bf-9ca1-4ea03e650e0a | note | Responsibility - RAP Yard Supervisor / Laboratory supervisor
3ee7ecb4-1890-539b-9896-1db869c75f4f | date | Date Completed:
7a651e5a-b4a3-4d04-9949-cff44d93eb3c | checkpoint | Final Inspection
2d1d16f5-5a8f-5846-878d-ffe1d9a36f89 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
3bd77594-0b9a-56f2-9d5f-cf6a79df486f | textbox | Print Name:
527695d8-93f9-50a2-abf0-56dc7bfce049 | textbox | Position:
1adf7434-14bc-5860-92a1-759173af3782 | date | Work Completed On:
095a949d-a150-58f5-8b0c-171799497afb | date | Date:
5214819d-f3e5-42f9-9366-0a431b043e3f | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0018 - Asphalt Placement - Rev 1 | itp | ITP018 - Asphalt Placement
9f2884d8-204c-4a8d-8a71-c6e6449c515b | section | 1.0 - Preliminary Activities
f9f9bade-be5c-4e37-9b6f-87558c7464d8 | checkpoint | 1.1 - Check for correct documentation
a5f9aed7-8e63-5dda-9f83-59b1caf55907 | note | Frequency - Prior to commencing works
62caa993-c7b0-5913-ac1d-d31314032ddf | note | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
57a4295e-8bd6-5c03-92d4-379b93c11fa3 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
fb9ae8ff-8531-572c-9794-d1245faeae5e | note | Reference Documents - Current Revisions in Aconex or ACC
d3ea8f0f-7f2e-5f67-ae22-0da0e0523b54 | note | Inspection/Test Method - Verify
3aa525f1-e8c3-5b2b-beb4-fe2bd8f50e49 | note | Record of conformity - This ITP signed
11bb45cb-f28b-524c-b7f4-105132e67009 | note | HP*
78324ebd-00a9-5887-bd39-689ae15436c2 | note | Responsibility - Project / Site Engineer
c71ae7c0-25e9-5c3c-80c3-9f3aa604f96e | date | Date Completed:
1b0d1945-ba45-49a1-bc53-a2c6293444f9 | checkpoint | 1.2 - Implementation of all measures and controls
b68c1335-9ce2-5ac6-94fc-a2752ff12ea9 | note | Frequency - Prior to commencing works
1b6eb168-ef14-543d-8908-f5a6d134139e | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
df3f696c-f4c5-5025-ab6c-982cf912fcef | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
da5647da-699b-5876-b8fe-f39669d4cab8 | note | Inspection/Test Method - Visual Inspection
0548f38b-76c7-5d93-8856-121e4f8636cd | note | Record of conformity - This ITP signed
0c394852-2286-5f12-ad60-a4d52ee11dd6 | note | HP*
b1024191-3b75-5777-9b53-075e00e18054 | note | Responsibility - Project / Site Engineer, Site Supervisor
516afb68-8bdf-5654-8b8d-23388ae689e3 | date | Date Completed:
108cd8a0-6efd-4313-89c5-c1008ebeb015 | checkpoint | 1.3 - Plant & Equipment Check
b042bd38-3294-597e-92f2-cc1403ca2c8e | note | Frequency - Prior to commencing works
051f61f5-5ff2-5606-ba22-ca18522f21ef | note | Acceptance Criteria - Asphalt plant & equipment meeting the requirements of Project Specification.
48f08a81-f61a-50d0-bab9-26102264dde4 | note | ○ Pre-Start checks completed by operators of plant and equipment. All plant and equipment are acceptable for use. Any faults are reported. Standby equipment in place where required.
74d44a80-c7a4-55b3-a0b5-3c32b28ba157 | note | Reference Documents - AfPA Sec 7.1 Cl 91-100
2a1ccd91-733c-5faf-a811-4f132cb811b1 | note | Inspection/Test Method - Verify
022476df-5970-565f-b0a6-0aead13c9076 | note | Record of conformity - This ITP signed
b6103524-bb1a-51cc-9f50-7222fc0f4327 | note | HP*
8283dd86-33c8-5e69-b1dc-a1990bba54b3 | note | Responsibility - Project / Site Engineer, Site Supervisor
db4cb085-a78d-5ed0-86ca-f8c0812b85d6 | date | Date Completed:
0c3e6d21-8357-46e2-848b-15fe6a08b1fb | checkpoint | 1.4 - Tack Coat Material Submission
bf603bbc-8b9a-5609-9c31-24241ba39f7c | note | Frequency - Prior to commencing works
7542c7a2-bac8-55d2-a2b4-12fa0c17b7b3 | note | Acceptance Criteria - Details of the proposed tack coat and test certificates shall be submitted to the Contract administrator for review.
c1d6a3c7-51ff-5df8-b763-4eaa8513b64d | note | Reference Documents - Beca Spec 002, 9.4.1, 9.9.1
3f504c9b-03e6-5e29-8d1e-dd15d83572d3 | note | Inspection/Test Method - Verify
fd0ab66c-99df-5d4d-bcca-df381b2a263c | note | Record of conformity - Aconex Correspond ence
035dfd60-95c4-5688-8116-afff433c2dd0 | note | HP
4fff7910-1b74-5a0a-a10a-8af5a3f88971 | note | Responsibility - Project / Site Engineer, Principal’s Representative
3f20c2e4-acd6-5c46-b2cf-8274b8debc4a | date | Date Completed:
0e5a3f03-50e9-48ac-9206-8bd253c7af2f | signoff | AUTHORITY HOLDPOINT
4953225d-5ded-4192-97fc-21a96922a99b | section | 2.0 - Tack Coat
84bc005b-5e84-4d02-90ec-b11c2423a625 | checkpoint | 2.1 - Surface Preparation
47766e02-13e2-5cf9-949f-d9989cb75713 | note | Frequency - Prior to applying tack coat
b69269c7-9b38-5d4d-9f9d-fdd746b6e0eb | note | Acceptance Criteria - Immediately before applying the tack coat and following all cold planning activities, all loose and foreign materials shall be removed from the surfaces to approximately 150mm beyond the edge of the area to be coated.
8598bb11-aa76-558e-8ec4-469626fea4c4 | note | ○ Tack coat must not be applied on a wet surface, or when the surface temperature is below 5 degrees Celsius.
8e5f6818-1379-5010-a8da-54b575cf5f73 | note | Reference Documents - Beca Spec 002, 8.5 & 9.5
a9f35569-5ae8-5b49-8339-88f474b7086f | note | Inspection/Test Method - Visual Inspection
c7adcae1-e616-5408-b0d5-cba668ad0083 | note | Record of conformity - This ITP signed
ff7d2081-f834-5ba8-970d-795e4aa5f8dc | note | HP
6801e94d-4647-5de5-b39e-d6451b1f9b61 | note | Responsibility - Project / Site Engineer Principal’s Representative
87c9411f-3137-5c10-8215-53bd51008a0c | date | Date Completed:
2a78a280-0174-461e-81e8-0f3926f5db41 | signoff | AUTHORITY HOLDPOINT
3fd7c619-20bf-40f9-9f01-fd2fb7595208 | checkpoint | 2.2 - Weather Limitations
c2a26f77-89f6-5fbb-b122-d418d308c7ba | note | Frequency - Prior to works
eadca574-9ef9-5a8f-bc24-1120ee28f823 | note | Acceptance Criteria - Tack coat shall not be applied on a wet surface, or when the surface temperature is below 5°C, or when the weather conditions would prevent the proper application or adhesion of the tack coat.
fec2bef3-c907-522c-b743-69fc7f4347b4 | note | Reference Documents - Beca Spec 002, 9.7
f901a7c3-7b05-5fc2-92a9-a008f77bd9e9 | note | Inspection/Test Method - Verify
671c43c2-4458-5f70-b0b8-852e1915d8fb | note | Record of conformity - This ITP signed
9370743f-41d9-5cc9-97b9-1ab0fc841db8 | note | HP*
e7f22c4b-8163-5d1a-96c8-4b11dcd4d120 | note | Responsibility - Project / Site Engineer, Site Supervisor
65ee4d3f-d779-580d-a277-bb8b8776c26e | date | Date Completed:
e46bd571-7112-4706-b2b3-2d357f0f9db2 | checkpoint | 2.3 - Application of Tack Coat
ef0cfcc9-1da0-50b0-b3f4-7b4274abe427 | note | Frequency - During Works
6a3523b1-20ec-55cf-b2ad-3f6b38afc9a0 | note | Acceptance Criteria - Tack coat must be applied to the prepared surface at a rate of 0.2-0.3 L/m2 of residual bituminous material, calculated at 25°C.
d869ee84-c759-57c5-a131-73ea86fff1cc | note | ○ Vertical faces of milled and excavated existing pavement must be thoroughly tack coated by hand lance or other method.
7d2587a3-26cd-58b1-b82c-36ed591a89a3 | note | ○ Tack coated surfaces must be protected from construction equipment trafficking to the extent reasonably achievable.
6d4dfb3e-ccc2-50a8-a987-933bc740eebd | note | ○ Asphalt paving must not commence until emulsified tack coat is substantially broken over more than 80% of the surface of the paving run.
53ad700b-f6d1-5d22-9382-331bbdb8c1dd | note | Reference Documents - Beca Spec 002, 9.9.3, 9.6, AfPA Sec 10.3 Cl153-156
a2538ff4-291c-58ba-a121-5252afaa2ad0 | note | Inspection/Test Method - Verify
4f2d60a1-00a6-5951-8702-849c76a20b49 | note | Record of conformity - Spray Rate Record Sheet, This ITP signed
679563c0-0697-519c-81fe-754fa5acc007 | note | WP
5cc1ec7a-434b-5737-82c9-b7243c0f60b6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
e2d25fa6-6833-5d61-a723-54a4e5a00bb9 | date | Date Completed:
64658685-fe27-4cdd-ac2b-4549a7330c9a | checkpoint | 2.4 - Test Certificates
a9a27fd4-abdd-55e4-b628-8556a7264c61 | note | Frequency - During works
ea3f92ac-7f6d-5770-b520-e1f4082498fa | note | Acceptance Criteria - If during the progress of the work the Contractor desires to use other materials or materials from other sources or materials produced from the same source using method of production different from those originally agreed, new samples shall be taken and tested and the results shall be submitted to the Contract Administrator.
810325e0-6ac2-5c81-872c-2b59960d405d | note | Reference Documents - Beca Spec 002, 9.9.1
2bf44c31-b1c7-53bc-9d70-80f6a53d8372 | note | Inspection/Test Method - Verify
de741aeb-88bd-5092-a94d-c31c91b612c5 | note | Record of conformity - This ITP signed, Test Reports
b8c777fc-0cc4-5934-ac6c-ffa5b957dc28 | note | HP
c84bbd9e-5aaa-5cb0-a7ec-460b5d7bef4b | note | Responsibility - Project / Site Engineer, Principal’s Representative
c42c3400-4221-5ffc-8501-61cf1d41b774 | date | Date Completed:
31f66bbc-f152-4adf-a435-516b83d5180f | signoff | AUTHORITY HOLDPOINT
e2542c4c-923f-4bc0-9f2a-f62375759b49 | section | 3.0 - Hot Mix Asphalt Placement
4ba75adf-7760-45bb-bb6f-355827c08a53 | checkpoint | 3.1 - Construction Trial
b84d28a8-9929-5d70-97ff-0e53d10f2b2c | note | Frequency - Prior to commencing works
4a17730b-d2bf-5cad-8d96-683cf8140c42 | note | Acceptance Criteria - A construction trial must be completed as per the requirements in the specification.
c5772dad-ba86-5906-8dc2-e89e0a85ca84 | note | Reference Documents - AfPA Sec, 8.3 & 8.4
e6511b96-c544-5242-bf12-12564331e895 | note | Inspection/Test Method - Verify
c465d417-fa23-5b16-9644-7448e5707044 | note | Record of conformity - Aconex Reference
5ebc8428-cf20-5234-8445-d1c3b84bb012 | note | HP
2d827f24-bba3-54dc-89ea-c194c2cd0ae7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
b8e798a4-b66e-5aae-a948-b342729a707b | date | Date Completed:
37ee13db-6271-4db5-96fb-a829a16ee48d | signoff | AUTHORITY HOLDPOINT
5df4a6be-d7f6-4f8e-9d1b-509eca6c9074 | checkpoint | 3.2 - Ambient Conditions for Placing
79839c47-2778-51bc-86d9-fd04a46d1e58 | note | Frequency - Prior to placement
c2838b20-7eb8-5a2b-b2d9-e61b4457693d | note | Acceptance Criteria - Asphalt must not be produced and constructed during weather, or expected weather, that may be detrimental to the quality of the finished asphalt surface layer(s).
bc654fdd-f7b9-5290-8c58-718e4fedb8b3 | note | ○ If required, where the existing surface temperature is below 15°C, the Contractor must develop and submit cold weather construction procedures for the Contract Administrator approval.
d73b971c-0d21-59af-9adf-0dbe751cc05b | note | Reference Documents - AfPA Sec 10.1 Cl 145-146
09f2a1d3-41d7-547a-85ca-7e75c1d9869a | note | Inspection/Test Method - Infrared Thermometer
55b086f1-c840-5443-b5be-c5b98739870c | note | Record of conformity - This ITP signed
73f0e451-f488-5e78-8bd8-07f9e6e6cbfc | note | HP
14286aa6-2b9a-5dcf-802f-e0b1f5365bae | note | Responsibility - Project / Site Engineer Principal’s Representative
5b5620cd-5938-5f07-986d-05d56fbd3ce7 | date | Date Completed:
d34b09a5-878a-41bc-899d-f558efdff5ab | signoff | AUTHORITY HOLDPOINT
15e52648-fbe7-4534-b4b4-46fe42c3932e | checkpoint | 3.3 - Surface Preparation
79e3704d-42f4-5643-8fb8-729e37e6326d | note | Frequency - Prior to placement
3ce9eecb-71b2-5e1a-8f8e-1c7d03133187 | note | Acceptance Criteria - The surface on which the asphalt is to be placed has been jointly inspected by the Contract Administrator and the Contractor, and it is agreed to be suitable.
fd35128b-8025-5291-88b5-5a87bb4468f4 | note | Reference Documents - AfPA Sec 10.2 Cl 147
84e8b29c-c59b-51a3-9526-afa88ef46280 | note | Inspection/Test Method - Visual Inspection
4983c872-056d-5676-a87b-609a7b4f0aa0 | note | Record of conformity - This ITP signed
1f503468-09a6-5523-b76f-27db8e2f5976 | note | HP
d41d03ea-96de-552d-9569-834480f7b52b | note | Responsibility - Project / Site Engineer, Principal’s Representative
9232169d-ad2c-574a-935c-862b37671421 | date | Date Completed:
5a4d6fa6-eff8-4908-aeec-2541fc0bd6ee | signoff | AUTHORITY HOLDPOINT
142b296d-56a3-4576-9c5c-0b29f6f3bbfa | checkpoint | 3.4 - Asphalt Placement
0f3da3cd-bc5d-5689-aa59-8652039ec1dc | note | Frequency - During Paving
76ec15fc-338e-541d-b5a2-5821ed495eb9 | note | Acceptance Criteria - The following processes to be monitored with the Contract Administrator to confirm consistency with Construction Trial:
6e637df4-83cd-5d3e-ab89-19ece676732f | note | – Roller patterns
0a89e57f-8c51-580f-8e00-935758dde67d | note | – Surface texture within paving lanes
71c92926-13dd-5961-8478-373fe002cb12 | note | – Surface texture at the joints
134582bb-dff3-587c-94b9-7575c09e6eff | note | Reference Documents - AfPA Sec 11.4.1
cb4e5f95-4459-54f8-a91f-0ee027ab93c3 | note | Inspection/Test Method - Verify
82daf4a7-2650-5b15-8fd6-5a714933d924 | note | Record of conformity - This ITP signed
85015cef-7985-54f2-9768-8b468e2cc983 | note | WP
5094bbd6-ac4a-5586-8670-9b177d36c2b7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
870b5305-8aa7-5028-9197-2a9d4405b024 | date | Date Completed:
5a7a5f30-cd93-45ca-a0a3-4fd0ba23f096 | checkpoint | 3.5 - Longitudinal Joints
619d9178-dc5d-52cb-bf6b-859e782302fa | note | Frequency - During Paving
0925c409-735c-560d-a580-ebd41d244628 | note | Acceptance Criteria - All longitudinal joints shall be constructed as hot joints (exceeding 125°C upon placement of the adjacent paving run) unless restricted by staging constraints or in constrained working areas.
0e2ef384-b47f-517e-8f79-387d9bbd0b0a | note | ○ Gas fuelled infrared joint heaters may be used to reheat the joint and create a hot joint where the measured temperature has not fallen below 90°C.
c9d82ab5-3da3-5f24-82f0-df129a7af676 | note | Reference Documents - Beca Spec 002 10.5, AfPA Sec 10.4.4
39df120d-2163-5a39-a86c-214aedbd31ae | note | Inspection/Test Method - Verify, Infrared Thermometer
171bf6f6-35cb-557a-8111-8fab28ad0d77 | note | Record of conformity - This ITP signed
4adb2a41-7300-5dcf-ac31-251a81331fa4 | note | HP*
60547fd5-58c6-535d-a8a3-c9436bb0bd51 | note | Responsibility - Project / Site Engineer, Site Supervisor
934ed53a-3fa4-54ea-a96c-11ef015fef21 | date | Date Completed:
9d1b5089-fbca-4929-acef-8c10a2267407 | checkpoint | 3.6 - Surface Finish of Wearing Course
21fcb48b-1259-5831-ab67-4ea5876059c7 | note | Frequency - During paving and after final roll
5596fd42-29d0-5d18-bd3e-850dfbe73e60 | note | Acceptance Criteria - The finished surface of the asphalt must be a tightly bonded, closed textured, surface of uniform appearance, free of dragged areas, cracks, segregation and open textured patches. Joints must be tightly closed. Surface finish must be consistent with the asphalt construction trial.
c5ba9a73-63fd-5815-b26f-6871758a4b4f | note | Reference Documents - AfPA Sec 12.4.1 Cl 288-291
a35847a5-a752-5894-a474-1d74a5aeda7e | note | Inspection/Test Method - Visual Inspection
8845183d-ac15-504f-9673-cc51e4e2a444 | note | Record of conformity - This ITP signed
d8d46058-0cd3-562d-abc1-6baaf6ef4c00 | note | HP*
0824a6e9-4325-5c3b-a8fa-dd30a620d63f | note | Responsibility - Project / Site Engineer
fdd7b257-b107-5384-826e-f90f5e6565d0 | date | Date Completed:
8cb930ae-52c9-4e44-8e8d-2eba25935a42 | section | 4.0 - Compaction Testing
65918363-6123-4bbf-a500-09863b051283 | checkpoint | 4.1 - Compaction Testing (AfPA Mix)
5b5e0720-9ba9-5ca8-b6b1-e76d0a53d518 | note | Frequency - See Note 1.
990733fb-00d8-55f6-bd8e-d1af740d4de1 | note | Acceptance Criteria - The in-situ air voids content to be determined using calibration between the nuclear density gauge (NDG) and the asphalt cores developed during the Construction Trial.
07cb5bd2-2c4f-5f50-8bf4-1b8e14c1e604 | note | For test locations away from joints:
bf682df4-a28a-50ae-a8fc-dbe8587a2967 | note | ○ Individual Air Voids: Minimum 2% and Maximum 8%
c9a25a06-f594-55c1-93a2-cd84bb394fd7 | note | ○ Average Air Voids: Minimum 3% and Maximum 6.5%
65758bb4-6d1e-560e-b938-2478bee7b78c | note | For test locations on longitudinal joints:
16e1d95b-6321-5b92-a5e3-dce46f78dfdd | note | ○ Individual Air Voids: Minimum 2% and Maximum 9%
b077ab9a-869d-5b8a-9681-137185741295 | note | ○ Average Air Voids: Minimum 3% and Maximum 7.5%
5c99acb6-bb52-51bf-917c-2492ca5d594c | note | Reference Documents - AfPA Sec 12.4.2 Table 22
c075ad1d-7fa5-53b7-b9a3-b57a30a0c645 | note | Inspection/Test Method - Verify
f20839b2-94d2-5d01-a79b-734c6462b437 | note | Record of conformity - NATA accredited test certificate
c4571efc-9490-5578-a62b-cfe0cebe1985 | note | TP
bef2ed99-72f7-5036-835a-9f27ea19b464 | note | Responsibility - Project / Site Engineer, Laboratory Technician
fc5f5a58-40dc-5d7c-9c3a-8ca819ada0e0 | date | Date Completed:
099bf5a9-42e3-4058-8cfb-a636699af661 | checkpoint | 4.2 - Compaction Testing (Type H Shoulder Mix)
9b48356e-602d-559e-8a70-19606954c66f | note | Frequency - See Note 2.
a8551a37-bdba-521c-80f9-474ba6a6831d | note | Acceptance Criteria - The in-situ air voids content to be determined using calibration between the nuclear density gauge (NDG) and the asphalt cores developed during the Construction Trial.
0c7e4376-0e2c-5857-924b-0120a7ed0450 | note | For test locations away from joints:
107aea62-354c-53e3-9115-eb9771885bcb | note | ○ Individual Air Voids: Minimum 2% and Maximum 8%
473a830d-3b43-58bd-9e47-4a383d38304e | note | ○ Average Air Voids: Minimum 3% and Maximum 8%
2ba06b15-8b0b-5278-9835-4f90f88aa04c | note | For test locations on longitudinal joints:
5afbb6a7-a4a1-560e-b022-82e9bad1ac09 | note | ○ Individual Air Voids: Minimum 2% and Maximum 9%
6d90001c-c503-5e9b-8633-69a430cf8c68 | note | ○ Average Air Voids: Minimum 3% and Maximum 9%
cc46bb88-056d-53d7-82ce-d6c48ca4ae8f | note | Reference Documents - AfPA Sec 12.4.2 Table 22
b0191cb8-548b-5422-bde2-f41df3842d66 | note | Inspection/Test Method - Verify
d1b883be-5e5f-5ed4-b140-3befcf9b1ad2 | note | Record of conformity - NATA accredited test certificate
3fbdf891-67af-5c38-ab0c-79f738d20de3 | note | TP
6be359d7-c79a-5104-bb58-32105d588c66 | note | Responsibility - Project / Site Engineer, Laboratory Technician
285591af-2d8b-5f00-927a-b4fc49ea144c | date | Date Completed:
18252a39-32ab-442a-9d38-6c7bfe17dd9d | section | 5.0 - Completion
f135dadf-31b5-4ee1-8ff7-5a5dd8677e8c | checkpoint | 5.1 - Surface Smoothness Testing
c5b297c9-1eaa-5d22-b991-d7370db8f6b4 | note | Frequency - After completion of pneumatic tyred rolling
b8ef7f30-9a88-58b1-a959-233eb3238049 | note | Acceptance Criteria - The finished surface of the surface layer must not deviate from a 3.5 m straight edge by:
1c97bc8e-013f-5cc6-9051-95b3b7691b8f | note | – Full Strength Pavement (AfPa Mix)
a52d80a4-e60a-5e0c-a30a-08ce049272a0 | note | o Longitudinally: Max 4mm
2667ae6b-1201-57c3-910f-80419cb48b72 | note | o Transversely: Max 6mm
76e76f41-9bd0-57f9-a873-544c2cbc3215 | note | – Shoulder Pavement (14H Mix)
cd9cc2e5-680b-5aa0-94d7-a143aab8c022 | note | o Longitudinally: Max 6mm
b8766bfd-c89f-5557-8d40-dce12e9795bc | note | o Transversely: Max 7mm
b15d9a54-5ff8-57ac-973a-23ba0bcb77c5 | note | Reference Documents - AfPA Sec 12.4.3 Cl 293.
45da2edb-bcd3-5f1f-82f4-b03962d62b13 | note | Inspection/Test Method - Visual Inspection
cfe9e470-6d0b-5f2b-88ac-6e6d1c58af01 | note | Record of conformity - This ITP signed
61c443ad-591f-5ec9-a841-8ded3f0ddbe6 | note | HP*
624295ee-5c1c-5bf9-a4e3-eaf1381950f9 | note | Responsibility - Project / Site Engineer
a264105a-ffcc-579a-9d8b-8c89d1dae253 | date | Date Completed:
43fe13a2-0a84-4e51-82f6-ca67366a4941 | checkpoint | 5.2 - Finished Surface Levels
66876240-1348-5152-ac6d-41ce6367c2df | note | Frequency - Per Lot & Per Asphalt Layer
4cefae3a-08a3-5f96-80cf-af2c2804403e | note | Acceptance Criteria - Surface level must be as per following:
3c26b3ae-1fd7-5f3d-bee0-61edba6d1384 | note | – Full Strength Pavement (AfPa Mix)
c9ad5d4a-fd55-5803-8cfa-519b19ad020b | note | o ≥95% of the deviations between design surface level and finished surface level must be maximum 7mm.
2ad96614-1c2b-5c2c-b8cf-fdaa3b4d1095 | note | o ≥95% of the finished surface deviations between design surface cross fall and finished surface cross fall must be maximum 0.3%.
914f0b94-6f35-5076-9c01-9f1643c1286e | note | – Shoulder Pavement (14H Mix) (14H Mix)
ffaa615c-26b4-5a2f-a2d0-a1ed3a8c9fee | note | o ≥90% of the deviations between design surface level and finished surface level must be maximum 7mm.
59bb3e47-78dc-596d-932a-d61366e367c5 | note | o ≥95% of the finished surface deviations between design surface cross fall and finished surface cross fall must be maximum 0.3%.
9c5be199-f41d-51ef-a6b0-5b574c0a900c | note | Reference Documents - AfPA Sec 11.5.1, Sec 12.4.5 Cl 298-299
22178bd7-0fcf-5c93-a8ab-c2723d84fd25 | note | Inspection/Test Method - Verify
7e22766e-22e3-56d7-9c4c-e9df49aa9a3d | note | Record of conformity - This ITP signed, Survey Reports
e7c89dad-45b0-551d-8de5-254576255443 | note | SCP
988132d4-0915-57d6-bde2-14bab73e2dcd | note | Responsibility - Project / Site Engineer, Principal’s Representative
5d806959-75fa-5932-be18-d1cb9f89ec36 | date | Date Completed:
b253de93-fa93-48b5-a4e2-0c9980e58583 | checkpoint | 5.3 - Surveyed Average Layer Thicknesses
63e6e4f7-0a51-5e46-9448-c0f8df6a6857 | note | Frequency - Per Lot & Per Asphalt Layer
405b7330-f7cf-56e1-9351-f2a60f83585d | note | Acceptance Criteria - Average layer thickness must not vary by ± 4mm from nominal thickness.
f9a244f1-abe1-50a7-9fb4-8eb14124edde | note | Reference Documents - AfPA Sec 11.4.5 Cl 247-248, Sec 12.4.4 Cl 294-295
1d83e7a2-aaea-5045-9c0d-22d3430eec75 | note | Inspection/Test Method - Verify
578da9fa-c510-5aad-ac01-c3e36ce4ee63 | note | Record of conformity - This ITP signed, Survey Reports
d48ca06e-97df-596d-918b-21331cd7c500 | note | SCP
de4108f9-392a-53d2-9ef1-b3a49aa27687 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a770faed-91f7-5d62-b114-4a6ef6765ce8 | date | Date Completed:
a5eb0caa-ec90-4ffb-a402-1b1c3a0c235c | checkpoint | Final Inspection
a2ac3a83-86a1-5bf8-b2ff-78c908b1a89d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality\System Procedures and verifies lot compliance with specifications.
594d0e9b-0456-5ab9-ae14-07100c0e9d21 | textbox | Print Name:
248be112-e257-515d-be95-4a4ca261c02a | textbox | Position:
42c4f1e7-3c8c-538f-acb9-b809dabca7df | date | Work Completed On:
ff9187ca-a632-5f3b-8c55-892c5854bac5 | date | Date:
cf51d2f2-2033-5b12-9a4c-aaa56a5e7f9f | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0019 - Spray Seal Placement - Rev 0 | itp | ITP019 - Spray Seal Placement
6607cab9-33c5-558e-bbf8-f1706ae449f8 | section | 1.0 - Preliminary Works
fbd6ef58-7046-5030-bc38-d0da69c3974d | checkpoint | 1.1 - Check for Correct Documentation
0338091b-6849-5e91-ab24-288d05799d5a | note | Frequency - Prior to commencing works
f1c4bcfa-15fd-5082-b518-2f6bfe1a3c25 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors. Current revisions of these documents to be obtained via Aconex or ACC.
56761984-8b52-53a8-8822-50c863d43498 | note | Reference Documents - Current Revisions in Aconex or ACC
099c6cc3-ecd8-5d83-943e-4562fd5208bb | note | Inspection/Test Method - Verify
ade0a277-7020-5d2a-94b7-a292ef5478ea | note | Record of conformity - This ITP signed
341e8386-6719-57f2-9a54-37739b8f945d | note | HP*
19df1e36-01d3-55c7-becc-a83a2fa2c7cd | note | Responsibility - Project / Site Engineer
9349017d-0618-575c-bdb4-e285fd401f19 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
d1bf2877-da5f-5876-b9fc-c31847f95bea | note | Frequency - Prior to commencing works
4e20f32d-dc92-5a56-b3c1-2592d032165b | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
f0514b64-ef11-5406-929d-d307acb2e68d | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
c5f9c362-259a-5a8a-bbd2-7ebdb8121eac | note | Inspection/Test Method - Visual Inspection
33394019-6e12-5d23-b044-82b76ee325ec | note | Record of conformity - This ITP signed
8b086da5-1a28-55e3-9f11-214f144f4571 | note | HP*
07c91057-9fde-53ba-8f80-73b73e39e6df | note | Responsibility - Project / Site Engineer
da1eeaf7-6b98-5193-a3b1-5f6458c1cc1d | date | Date Completed:
01fe0f38-b21a-52fb-bc33-d24ffdce9887 | checkpoint | 1.3 - Plant & Equipment Check
52451bc8-8fa5-5227-98c8-d3d0deb939fb | note | Frequency - Prior to commencing works
24b5ade8-68a9-5ac8-8c5c-b3ad20d181d6 | note | Acceptance Criteria - All equipment shall comply with VicRoads Section 408 and VicRoads Bituminous Sprayed Surfacing Manual.
83e8ea0d-fb35-5495-bcd6-9dca4a47221c | note | Reference Documents - Beca Spec 002 - 12.3
89d0dc0a-2ecd-5b17-a449-754396782cf9 | note | Inspection/Test Method - Verify
cb9e460a-9837-53ce-8921-e8afd339d828 | note | Record of conformity - This ITP signed
62f23a0d-83b7-5f21-9d28-1247cadf1ffe | note | HP*
0383f368-68bb-55dd-bbec-c764949d16a5 | note | Responsibility - Project / Site Engineer
db217685-0cc4-532c-8d74-629561e88330 | date | Date Completed:
378e9cc1-cd99-5625-8321-b480ee1a80c6 | section | 2.0 - Materials
7f7d3002-dbbd-5bba-8b90-ca19482036fa | checkpoint | 2.3 - Material Approval
36048218-ebba-5b75-bc93-16bd0d21a04b | note | Frequency - Prior to Works
9588d36e-1d96-5a41-8af8-fd13ad0ea4f6 | note | Acceptance Criteria - The binder used shall be class 170 residual bitumen complying with AS 2008.
9938bcd9-e8ca-5533-953c-1bc2616e5baa | note | ○ All aggregates used shall comply with VicRoads section 801 and 831. Material and Test Reports to be submitted to the Principal’s Representative prior to commencement of works.
c3abd480-94e4-5797-ab62-34fda3bddc67 | note | Reference Documents - Beca Spec 002 - 12.6.1.1 to 12.6.1.3
03b20b15-37cb-53e4-96e6-3c6595c4898c | note | Inspection/Test Method - Verify
6ad33181-3bc4-5705-a55a-b1b9497ff0a0 | note | Record of conformity - Test Reports, This ITP signed
cf0e6f2b-dc71-5d10-a3eb-9f65f11eeb28 | note | HP
53ae5648-9273-5cc6-ac92-b31bb6c24af3 | note | Responsibility - Project / Site Engineer, Principal’s Representative
6440aab1-856c-57ff-bc25-7f7131fba383 | date | Date Completed:
c0fb703d-700a-51c3-aa97-5c9392cf120d | signoff | AUTHORITY HOLDPOINT
d7be73a1-96ee-543f-9d6a-da9f3eb56961 | section | 3.0 - Construction
84b31f08-968f-52e4-a569-422bde1a1ac6 | checkpoint | 3.1 - Underlying Surface
3eebee34-1fbe-5403-8c42-4d4010c12a81 | note | Frequency - Prior to works
c419e70b-0b7b-5980-bce7-7cf2a80ae7fa | note | Acceptance Criteria - The pavement surface should be cleaned to remove all mud, carried on material, dirt and dust.
12e9e198-9b63-5054-8528-6b47f4eeeb04 | note | ○ After cleaning the surface should be swept with a suction sweeper, supplemented by hand brooms where required. Seal coat should only be applied to a sound clean dry surface.
35b9ca1f-8b6b-5878-9d6f-9221cb439ce7 | note | ○ Preparation of the underlying surface shall be approved by the Principal’s Representative.
0ac039db-423e-5f23-9e6f-c0268094e410 | note | Reference Documents - Beca Spec 002 - 12.4.1 to 12.4.5
3f8554d4-dc75-5643-8404-1463684c4e6c | note | Inspection/Test Method - Verify
f0ceec3a-c604-532f-871e-a530b25eb790 | note | Record of conformity - This ITP signed
c1d1704e-a365-5d2e-b5db-817215969479 | note | HP
416e0906-13a6-5ba4-b20b-b4087b73c12d | note | Responsibility - Project / Site Engineer, Principal’s Representative
f8a2683b-6a39-5341-9d92-90c14da8a1d5 | date | Date Completed:
486e988a-6d15-52f1-be0b-9d2371ced570 | signoff | AUTHORITY HOLDPOINT
d0b185fe-eb3f-560c-94a2-ac66313efd10 | checkpoint | 3.3 - Binder and Aggregate Application
46d85ea1-c304-5100-9c87-246ff6a83c14 | note | Frequency - During works
6a161514-f2d1-5174-9d98-2c10b3b48112 | note | Acceptance Criteria - Application rates shall be:
fe593034-64be-54d4-90d4-5c3eaaf31146 | note | ○ Binder: 0.8 – 1.0 L/m2
9d2c2fa6-d5e5-5f58-ae4b-3ff7166eb06f | note | ○ Aggregate: 8 – 10 kg/m2
a9f893e6-e430-59e5-8f3d-4782d9c75631 | note | Reference Documents - Beca Spec 002 - 12.6.2
e608d166-4c9c-5617-8ef6-8875835087e6 | note | Inspection/Test Method - Verify
c53d96b2-ca83-5b49-8488-179c251e1ddf | note | Record of conformity - This ITP signed
80c1be45-e4cd-5346-88de-53cd36ff02be | note | IP
087e4ab6-8a1e-5869-bdab-146f2b456660 | note | Responsibility - Project / Site Engineer
2c140901-e263-550e-8106-6da5f1b5b88f | date | Date Completed:
b202e282-3595-59ac-b16a-e799c765ba53 | checkpoint | 3.4 - Aggregate Spreading
360de500-a0c3-58ae-9e44-5cf64aec2ab6 | note | Frequency - During works
da6cba42-dc9a-5cc3-9313-f781c145627d | note | Acceptance Criteria - All aggregate spreading shall be undertaken using forward aggregate spreading and discharge plant.
361fa8c1-eba4-54dd-a451-62c80444a098 | note | Reference Documents - VicRoads Section 408 – 408.13(e) to 408.13(f)
19f40917-c682-5fb4-9902-726e9cfce912 | note | Inspection/Test Method - Verify
010672fc-b6b3-55d1-b9b5-768da0e2f368 | note | Record of conformity - This ITP signed
66a42d9e-9912-5e72-9f9f-47009903b973 | note | IP
6215b40e-1dbd-5998-b4df-ae2088f5401c | note | Responsibility - Project / Site Engineer
aa9fb1ce-a68d-5e5f-a943-677b79c35632 | date | Date Completed:
946d5fda-a1a1-5f46-9863-44dae4f5dd1a | checkpoint | 3.4 - Rolling of Aggregate
a43d4bb9-7058-5eea-ac7b-e5e628da8ef4 | note | Frequency - During Works
4518b789-9bf4-5581-beaa-0a0d4b093079 | note | Acceptance Criteria - Rolling of aggregate shall be undertaken over the full width of the pavement being sealed. Works to be undertaken by static rubber tyred rollers or otherwise approved by the Principal’s Representative.
7c58c4b2-29ab-5815-beca-47873a10793e | note | Reference Documents - VicRoads Section 408 – 408.13(g)
45fabd6d-a208-5ad3-8128-0653884c352b | note | Inspection/Test Method - Verify
8c9decdd-5dac-55ef-848f-12c23e105859 | note | Record of conformity - This ITP signed
9cea5468-74c7-5703-8b8e-8c1e4381a91e | note | IP
e6d83783-27c5-5256-8396-4ffbb37c539d | note | Responsibility - Project / Site Engineer
c3225380-19dd-5012-9895-f56263b181d2 | date | Date Completed:
26d067c2-aa89-5a54-bc39-3ef8a5d9d14d | checkpoint | 3.5 - Removal of Loose Aggregate
df14e7ab-bcbd-5004-af25-98c10d4ea0bf | note | Frequency - During Works
2a630df0-8c56-5d37-b998-cda5d3b73777 | note | Acceptance Criteria - At completion of sprayed seal treatment, the Contractor shall remove and dispose of all loose aggregate.
5abe8ced-7041-5092-9364-153adfb962f6 | note | Reference Documents - VicRoads Section 408 – 408.14
3cf93853-d5c7-5a59-9fb3-9c10d57b585d | note | Inspection/Test Method - Verify
a991d669-89b6-58dd-8128-79458c7a112b | note | Record of conformity - This ITP signed
c943f80d-44fc-5e60-b513-0646f5af80fd | note | IP
ce475f64-84c9-5d22-8531-52ebc44d3971 | note | Responsibility - Project / Site Engineer
ce7b8f6e-0579-5c75-980b-5f694f011b25 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
32497480-f3b1-5c2f-8a18-88a7a7a743b6 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
7628e703-c3b0-571d-b220-426fddfe55fc | textbox | Print Name:
90716a2d-8ead-50b9-91c7-b9f6ab0813d3 | textbox | Position:
d8ed759e-5f16-58e0-9e77-a58513e6c30d | date | Work Completed On:
bcae2680-09f7-5058-abb3-53df76875256 | date | Date:
f8615df5-4fd1-4e1a-957a-48b320d5cd93 | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0019 - Spray Seal Placement - Rev 1 (2.1 Checkpoint) | itp | ITP019 - Spray Seal Placement
e8bcd4ad-4c6e-425f-9433-981140c4ac85 | section | 1.0 - Preliminary Activities
57149455-e3a9-4ad5-b430-af51d0a24901 | checkpoint | 1.1 - Check for Correct Documentation
99d26f55-d53b-5be9-919d-f74e244ca72b | note | Frequency - Prior to commencing works
f44b925b-8ef3-5cbf-9564-c18048cf1da7 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
fd728d1f-dbca-598f-9a99-380ce33e6d02 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
385bde3c-18ea-5756-af9a-b177f4adb1f1 | note | Reference Documents - Current Revisions in Aconex or ACC
a1ce4557-03f4-56fb-b37d-e20fd3a97e9a | note | Inspection/Test Method - Verify
9ae40c17-71da-5e69-bf13-bed52a2dcc8a | note | Record of conformity - This ITP signed
ea1bf8a7-8bcf-5839-b274-32d5f5d551e0 | note | HP*
4970d0c4-183e-511b-91e6-99185641679a | note | Responsibility - Project / Site Engineer
cf668b44-5796-50eb-b82c-3a3544c86e42 | date | Date Completed:
e6fe80b7-4f90-4fdd-8026-1a074f6808cc | checkpoint | 1.2 - Implementation of all measures and controls
515120e3-76b8-51ab-b2b7-8575773312c4 | note | Frequency - Prior to commencing works
e4195976-f45f-5f6c-9bff-330c716b3ef3 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
946ef10d-cc61-510c-810b-1c33215ca0e5 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
6407e481-51ff-5c31-bdeb-c4bd3b171a2e | note | Inspection/Test Method - Visual Inspection
68c2ba93-d343-5ef3-b7a2-03296d418963 | note | Record of conformity - This ITP signed
1f5e4321-6d40-55ba-b88f-4d8a837ad394 | note | HP*
e99d7166-ace9-52a2-b86a-1b8473160663 | note | Responsibility - Project / Site Engineer
19946092-3c09-5298-9e35-05f392ce81f1 | date | Date Completed:
d23305ae-bacf-43fa-b4b5-d08430aa855b | checkpoint | 1.3 - Plant & Equipment Check
9a2b3deb-4d64-50b5-85a9-039b86918458 | note | Frequency - Prior to commencing works
279b0fe8-bad9-5bab-8b28-1a4cef298b56 | note | Acceptance Criteria - All equipment shall comply with VicRoads Section 408 and VicRoads Bituminous Sprayed Surfacing Manual.
b0a61a36-6acb-55d1-aef5-93a93bf4ad11 | note | Reference Documents - Beca Spec 002 - 12.3
4e9e834e-f65f-50b1-80e9-176cc7e50741 | note | Inspection/Test Method - Verify
305535f9-f829-5f08-a2f4-f9b183621e3e | note | Record of conformity - This ITP signed
c4287885-cd53-5223-b23d-ebd5531c6f3f | note | HP*
401e6ef2-678d-5abb-9c2e-fe54abe0e62f | note | Responsibility - Project / Site Engineer
f76a6910-fd36-5143-b7cb-7c09734ff325 | date | Date Completed:
86e65bcb-0044-42c5-800f-41bbe5723b10 | section | 2.0 - Materials
51c9704a-2a0c-4520-9081-782837612c4a | checkpoint | 2.1 - Material Approval
0180bf66-82fe-5bdf-b75d-a5a3a494916a | note | Frequency - Prior to Works
b7f612c1-825d-5eca-82ac-c5078adca858 | note | Acceptance Criteria - The binder used shall be class 170 residual bitumen complying with AS 2008.
ad3c639b-e0c7-5c6c-9468-955e077988f7 | note | ○ All aggregates used shall comply with VicRoads section 801 and 831. Material and Test Reports to be submitted to the Principal’s Representative prior to commencement of works.
4b76e043-3a96-5d84-9078-cf3a5e38d0fb | note | Reference Documents - Beca Spec 002 - 12.6.1.1 to 12.6.1.3
1c829db9-cd91-555c-9bf6-2690806079dd | note | Inspection/Test Method - Verify
026372fd-6f92-5df9-85e1-172497381ef3 | note | Record of conformity - Test Reports, This ITP signed
306957d8-b06d-52b1-a97f-0cb06468180b | note | HP
5960453d-3adb-5f5c-aa48-22864a93455a | note | Responsibility - Project / Site Engineer, Principal’s Representative
4a2f89ba-db0c-5606-92d1-5c6c6f1f3ea3 | date | Date Completed:
6b43d63c-ba7a-5475-83d2-8e8eb4441002 | note | Principal’s Representative - DCWC Mgt-GCOR-009596
a44762f8-fe22-4af4-9ad6-f40ced12d155 | signoff | AUTHORITY HOLDPOINT
8a2cad47-c623-4226-a99f-55e64477505a | section | 3.0 - Construction
0336702c-135e-4a8b-ad26-5e786bff34ef | checkpoint | 3.1 - Underlying Surface
b55c9220-1218-5b6b-9965-d5a620d7c5c5 | note | Frequency - Prior to works
8a6942f8-87cf-5f67-93a5-19f8b664c1bb | note | Acceptance Criteria - The pavement surface should be cleaned to remove all mud, carried on material, dirt and dust.
a1905cf2-aa5d-5c68-a05d-e3ea0e2adf5b | note | ○ After cleaning the surface should be swept with a suction sweeper, supplemented by hand brooms where required. Seal coat should only be applied to a sound clean dry surface.
c4b95760-ee66-5f4b-967e-ae1bd2dbbe9e | note | ○ Preparation of the underlying surface shall be approved by the Principal’s Representative.
da482898-a99b-564f-bf91-ea0730671827 | note | Reference Documents - Beca Spec 002 - 12.4.1 to 12.4.5
907dac99-ae2e-5ab5-ba6b-e820b1135a56 | note | Inspection/Test Method - Verify
6b71389b-b533-5318-bf2b-2369ac003a3a | note | Record of conformity - This ITP signed
e732b59b-9a25-55a6-a246-675f1888c65c | note | HP
dec31d14-7e78-5705-981d-5900356a0d60 | note | Responsibility - Project / Site Engineer, Principal’s Representative
4a94e1b2-3c5a-554b-83fa-72558f4fe7f0 | date | Date Completed:
389b6e60-5f91-4cee-8bac-b00d91a6eb23 | signoff | AUTHORITY HOLDPOINT
bc827790-c421-43a3-b33a-9c4c2631347f | checkpoint | 3.2 - Binder and Aggregate Application
460ff129-e91b-5d1c-8557-f539998c1c2a | note | Frequency - During works
e9108c97-6a3c-5c77-9af1-b4d273309262 | note | Acceptance Criteria - Application rates shall be:
e5dc51ac-c7a5-53f0-a742-63910cb561d0 | note | ○ Binder: 0.8 – 1.2 L/m2
55f29abb-e7ad-5805-bcf6-8c98d32ca74b | note | Refer Aconex: DCWC Mgt-RTRFI- 001272
10bcf56c-1534-59b1-a1b9-5cb997b62e67 | note | ○ Aggregate: 8 – 10 kg/m2
17fc8aaf-1094-56d0-9a29-213c3b45e032 | note | Reference Documents - Beca Spec 002 - 12.6.2
91bd4695-dbc1-5301-83a8-d81418984ff4 | note | Inspection/Test Method - Verify
afeecce6-979e-5a3f-b14e-964698b0d649 | note | Record of conformity - This ITP signed
22069dc3-6f08-5b8a-a768-17492cc4da03 | note | IP
f1650274-2108-54b7-9557-c47b13242630 | note | Responsibility - Project / Site Engineer
caa491e8-6357-53b2-9b3f-896606b18a58 | date | Date Completed:
3558efa7-7cce-4cc8-a9b7-c5c80dddb2a0 | checkpoint | 3.3 - Aggregate Spreading
5aaaeec4-daca-5031-82ff-6f3d20e0dace | note | Frequency - During works
90f2b260-756d-598a-b1d5-115f70a2538d | note | Acceptance Criteria - All aggregate spreading shall be undertaken using forward aggregate spreading and discharge plant.
e9df92de-0853-5fdd-9e67-e76b4b0e2b1d | note | Reference Documents - VicRoads Section 408 – 408.13(e) to 408.13(f)
91deb454-fb48-5ee9-9a00-d53385df6b64 | note | Inspection/Test Method - Verify
376bbbbc-c41f-5c66-b4b4-251f3de0f271 | note | Record of conformity - This ITP signed
3e762456-f42d-5369-96e4-1f2d7569ccfb | note | IP
3b210cfd-cb73-54cb-90ce-9757b15569b8 | note | Responsibility - Project / Site Engineer
b95944c8-e12b-577c-825d-a7fc3c9a1fff | date | Date Completed:
ecb510a8-5206-4b93-9181-49dc76567198 | checkpoint | 3.4 - Rolling of Aggregate
a7fce128-f8e8-5077-bf89-7a3c37aa1b55 | note | Frequency - During Works
d22150a9-200e-5a7f-8cdd-186dba96b56f | note | Acceptance Criteria - Rolling of aggregate shall be undertaken over the full width of the pavement being sealed. Works to be undertaken by static rubber tyred rollers or otherwise approved by the Principal’s Representative.
e464d500-9632-55b9-b873-6bd8740f7323 | note | Reference Documents - VicRoads Section 408 – 408.13(g)
7f6376ab-8124-5c2d-84c6-2bb3a7bd4e99 | note | Inspection/Test Method - Verify
2049228d-37a6-5e50-b5f9-90730444ff19 | note | Record of conformity - This ITP signed
123b39ab-4d8b-5fda-846f-2b4fa2145053 | note | IP
93355f4f-e6ed-5e20-b491-da8d2e372b00 | note | Responsibility - Project / Site Engineer
8672d42b-ebe7-550d-a954-d270e4c03e8a | date | Date Completed:
f94df72a-e1c3-4079-b178-e65baa3d3c27 | checkpoint | 3.5 - Removal of Loose Aggregate
086d6c37-30fc-500b-bd7b-dac102a3cd08 | note | Frequency - During Works
0f19303d-5fc5-5200-b707-0294471d0d79 | note | Acceptance Criteria - At completion of sprayed seal treatment, the Contractor shall remove and dispose of all loose aggregate.
18eef251-bc87-5480-ae5b-f73eab77b998 | note | Reference Documents - VicRoads Section 408 – 408.14
cc9ae318-b7a0-5772-bddf-62c993fee511 | note | Inspection/Test Method - Verify
8a30db57-cb6a-558c-b399-f5afba5e132f | note | Record of conformity - This ITP signed
0af44172-96bd-5bed-a873-9c16b72fdd11 | note | IP
e96c6382-4a04-500f-91bf-2d846f2d2fe3 | note | Responsibility - Project / Site Engineer
eb44069f-d261-5957-951c-6b9cb9c899f7 | date | Date Completed:
ee618c11-52bb-4dd3-9c47-0be815c7da71 | checkpoint | Final Inspection
093a37ab-ed53-55a4-8356-00f47ef65b7d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
7d02be77-d93e-5a61-8cb6-2a7e1eb9340a | textbox | Print Name:
b229b7f5-c9f1-5ed5-9d70-14a8e2cdcc0a | textbox | Position:
4e1a7de0-332c-5b3b-9cb1-37894f0e6a5b | date | Work Completed On:
e70f894e-7cbb-5c5b-8ee6-58631cf99e2c | date | Date:
e4d66131-e842-4969-8dac-30df36d96f43 | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0020 - Prime Coat - Rev 0 | itp | ITP020 - Prime Coat
77c2a549-4048-4187-bf5a-cbd0237f6494 | section | 1.0 - Preliminary Activities
e6bd9291-ce69-4466-949c-d6d0d8063f8f | checkpoint | 1.1 - Check for correct documentation
3e28b716-2665-587d-86de-d28fb8b9dd9c | note | Frequency - Prior to commencing works
a2878d92-55b9-5fd4-9074-645b7059c720 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
72ffe1c9-9473-5a0f-acbf-9a9d3323b8df | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
83384688-a514-596b-9db7-8593f4d907f0 | note | Reference Documents - Current Revisions in Aconex or ACC
8c846aa3-c5cd-5a1c-a1eb-b0a775b09dc2 | note | Inspection/Test Method - Verify
15d02e57-f78c-514c-a965-2d6609a0fd06 | note | Record of conformity - This ITP signed
8ecf7fdf-6570-5673-9944-8f69427ae829 | note | HP*
601ab77e-f898-5cfd-a19d-b7aeeb9d630b | note | Responsibility - Project / Site Engineer
f8d67e0d-eef7-5796-9ba1-b0cd158e5a8f | date | Date Completed:
fac1c1be-542b-48df-a8fc-412903db3db8 | checkpoint | 1.2 - Implementation of all measures and controls
fd61bdef-3dc4-5478-950d-3f3ed5dd4fb4 | note | Frequency - Prior to commencing works
57674075-8edb-5562-8973-ef097f089d48 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
8ae25de7-7141-520b-9a1b-68cd7ba42fa5 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
5956918e-348e-50e5-bae8-f6815a3cf00a | note | Inspection/Test Method - Visual Inspection
0c1cd28d-dfe7-5e74-af2c-35d58ef875c7 | note | Record of conformity - This ITP signed
3f65063a-8271-54bb-b412-d7f9668ad4cd | note | HP*
2c79d54a-6138-5731-b689-a14b68a4757f | note | Responsibility - Project / Site Engineer
bb0613ac-6d91-53a0-98a4-a15813d1100d | date | Date Completed:
c4372892-3c33-410f-a10e-314c6c8a4356 | checkpoint | 1.3 - Plant & Equipment Check
48b03e0f-1dfe-5a8b-bf87-ccaaeb4ea185 | note | Frequency - Prior to commencing works
dfe82327-01d7-5d90-b3af-65fd48c877b1 | note | Acceptance Criteria - The Contractor shall provide equipment for heating and uniformly applying the bituminous material and blotter material.
6c8b4d08-3b6f-5ca8-be4a-8fbe09eb8ffd | note | ○ The bitumen distributor shall comply with the requirements of NAS 70: ‘Bitumen Sprayers’
2024fdb5-2ab0-57c0-a846-3b6a65326676 | note | Reference Documents - Beca Spec 002 - 7.3
c82f184b-0e79-5f30-b0d5-c7f02464dda5 | note | Inspection/Test Method - Verify
c19e226c-977c-5c19-a6ac-a5c3bdc5dd70 | note | Record of conformity - This ITP signed
b0685503-e401-5ec2-beaa-424566373517 | note | HP*
98ee50b1-ed5d-58ec-a07e-e21c10fe35dd | note | Responsibility - Project / Site Engineer
9c9243c6-38aa-5049-831f-68b0369f2464 | date | Date Completed:
3bb99724-153a-4e53-8f17-f377c9ccd3bd | checkpoint | 1.4 - Weather Conditions
1757d7c8-7b9e-5f63-9e18-8a3b9f2894da | note | Frequency - Prior to commencing works
258c24fd-de63-5eb1-8b11-e788b3a15630 | note | Acceptance Criteria - Prime coat shall not be applied on a wet surface, or when the surface temperature is below 10°C, or when the weather conditions would prevent the proper application or adhesion of the prime coat
69bae7e7-0f2a-52d6-bb8b-44f360d5e261 | note | Reference Documents - Beca Spec 002 - 7.9
e1355026-7302-5287-a4b7-3ca26eca4c53 | note | Inspection/Test Method - Verify
1d8b15b2-1c86-5b18-9574-0a3eb8861fc0 | note | Record of conformity - This ITP signed
de46e4ac-35a1-56fe-9b90-80059a3153ac | note | HP*
c78e9ec0-1cb2-533b-b850-689ed4c43fc3 | note | Responsibility - Project / Site Engineer
bef7f574-7a99-5578-88ca-b7edc2392955 | date | Date Completed:
de348b1d-773f-463c-b540-9e82ba8a75e9 | section | 2.0 - Materials
bbe3702a-1de0-49d5-ba53-b1f9667b6c01 | checkpoint | 2.1 - Cut-back Bitumen
5a845578-274c-5c5d-9778-c478b66ec5d9 | note | Frequency - Prior to commencing works
47fdd202-1cce-5ca0-9d9f-61da5ea5f6d3 | note | Acceptance Criteria - Cut-back bitumen for prime coat shall comply with AS 2157 and shall be class AMC0, AMC00 or AMC1.
6e034720-761e-57c8-b234-a4ae2197469a | note | Reference Documents - Beca Spec 002 – 7.4.1
5afb3c07-8877-5d88-8d35-f5be1c4f9663 | note | Inspection/Test Method - Verify
02b3f534-0085-573d-ac1e-d7231d0232ed | note | Record of conformity - This ITP signed
83c4f1f6-251a-5fd6-8549-eed1d892a7ae | note | HP*
b9bae47a-9ff8-589f-b53e-9b539feb5010 | note | Responsibility - Project / Site Engineer
e5218776-941b-5734-95c8-d541afe46f53 | date | Date Completed:
3a26611d-32f8-45e1-85a9-9f5df9cf0941 | checkpoint | 2.2 - Cutter
2ec749d3-e4c0-5ba0-9b7f-e97cda92030f | note | Frequency - Prior to commencing works
44191fc2-4976-5bb0-9822-b17594bb3f68 | note | Acceptance Criteria - The cutter for use in cutback bitumen shall be a suitable petroleum-based material complying with the requirement of AS 3569.
a048271a-b023-5219-87da-15e93e767746 | note | Reference Documents - Beca Spec 002 – 7.4.4
280e28a3-c46a-5488-a7a8-0763ff10c1d4 | note | Inspection/Test Method - Verify
caf54b2d-b844-5db2-91f7-c4e3bf8449d2 | note | Record of conformity - This ITP signed
75a46fae-6394-55b4-9d9f-b48aa94b7896 | note | HP*
ed25d063-39c6-54bf-b5a0-207b05fa5bcc | note | Responsibility - Project / Site Engineer
bb370798-8dc3-5d38-ad79-e105606c7519 | date | Date Completed:
bcc1e27e-aff6-4b94-8d29-95ccd17bb3c1 | checkpoint | 2.3 - Bitumen Emulsion
76d445f1-48af-58b0-88f0-e6fcb925a7ae | note | Frequency - Prior to commencing works
9d0874b1-5782-561b-a5c7-c594ebdb1ad8 | note | Acceptance Criteria - If directed by the Principal’s Representative, bitumen emulsion complying to AS 1160 shall be used as a prime coat.
205fb309-6c13-5686-b85a-f192804d7535 | note | Reference Documents - Beca Spec 002 – 7.4.2
8c81b12e-747f-53a4-91e2-6838e33fd7ec | note | Inspection/Test Method - Verify
5ea3bb67-1b3b-5129-a2b5-d7383c64cfcb | note | Record of conformity - This ITP signed
4946ca3b-3790-5ce7-b9e4-f5561af79a99 | note | HP*
71e952ee-dce8-53b9-9eef-ec190898e94d | note | Responsibility - Project / Site Engineer
b0eedbc5-aadc-5c89-a5fd-eca364354b49 | date | Date Completed:
f576d954-49a0-42e9-ac80-bbfe9b7186db | checkpoint | 2.4 - Blinding Sand
0c428cd8-ee5e-5efd-81a0-76b1d574d74c | note | Frequency - Prior to commencing works
dd81b60a-4a4c-50b8-9e79-a4c147533df3 | note | Acceptance Criteria - If required, blinding sand to be used for absorbing excess primer shall comply with the following PSD.
c2fd285d-2476-5e8b-ad68-eb65fa989f70 | note | – – – – – – – – –
7f3456da-1847-5c0e-b994-a63ac1a5d4c1 | note | AS Sieve Size (mm) ¦¦ Percent Passing Sieve by Mass
7373b608-2a20-5b28-a2dc-45c227098ca8 | note | – – – – – – – – –
dee58195-b56a-5086-9c21-3317909095b5 | note | 6.7 ¦¦ 100
c89fb368-084b-5ccd-a25c-5e6648dfa48f | note | 4.75 ¦¦ 85-100
8c2ca609-efc1-53ee-bef9-a9baec78a423 | note | 1.18 ¦¦ 40-100
112cda15-adec-5d68-bff4-e7e054049ba3 | note | 0.425 ¦¦ 10-50
09f921e7-9bcc-5145-9e5f-241a1ca1d9bf | note | 0.075 ¦¦ 0-5
e39f3f4f-c1ab-5469-915e-991bb4a90a25 | note | – – – – – – – – –
f991a567-1f3c-5f5a-aa8b-40188453ed3c | note | Reference Documents - Beca Spec 002 – 7.4.5
ea483d90-6c58-50d4-beb8-598538458b7b | note | Inspection/Test Method - Verify
4c2327f9-2861-5eb8-9f41-a0eb74b66bb7 | note | Record of conformity - Test Report
9a2a6ca8-a9a0-5d22-8aa7-46a50e3c8322 | note | TP
e783442a-53e7-53dd-8c06-fd1c7f314069 | note | Responsibility - Project / Site Engineer
e71aa016-769f-5825-8d9f-f1865a9e7af9 | date | Date Completed:
961be67c-bf5f-4e52-aab6-63c629df32e8 | checkpoint | 2.5 - Test Certificates
5951c134-99c4-5126-8903-18c8840bcec0 | note | Frequency - Prior to commencing works
e47d554e-a415-542d-9de3-d4d9a63d5553 | note | Acceptance Criteria - The Contractor shall submit a Test Certificate for each material proposed for use in the Works indicating compliance of those materials with the properties or requirements specified.
a7ead04a-5e2c-5935-9172-8844bba2f9c0 | note | Reference Documents - Beca Spec 002 – 7.11.2
1abbacd2-a0e4-59ca-b212-ee89c8953f2d | note | Inspection/Test Method - Verify
55eca4bf-e875-560f-b9f7-bd51a6f27140 | note | Record of conformity - This ITP Signed
8efc5107-d167-5eb4-bb1a-743e8e548db4 | note | HP
f37718ef-72d6-5ce3-acef-3e893adb4fe1 | note | Responsibility - Project / Site Engineer, Principal’s Representative
00e893b5-b03d-5bf0-82df-d73eb0ca623e | date | Date Completed:
c26b8cc6-3c39-45a3-b7f0-5e383ad951a5 | signoff | AUTHORITY HOLDPOINT
57b41481-d68c-4391-90b7-9f9d89a45349 | section | 3.0 - Construction
491114b2-bb94-4739-831b-3c181b620eea | checkpoint | 3.1 - Trial Application
c19b6e36-1556-5662-8e3b-f4c52c9e0755 | note | Frequency - Prior to commencing works
e66b1bdb-6f64-52fe-af14-cbfafc9854ba | note | Acceptance Criteria - A trial application, to be conducted as part of permanent works, shall be conducted on an area of the Works agreed and witnessed by the Principal’s Representative
af5b48aa-c2a6-5e1c-8f10-f3370cb0889d | note | Reference Documents - Beca Spec 002 – 7.5
7f1ef474-79ff-5de1-b406-54b608a4495f | note | Inspection/Test Method - Visual inspection
9c0b55f7-61c9-5684-bde1-8f885847c0f7 | note | Record of conformity - This ITP signed
b42bd78c-ad4e-57fe-8ea4-61f146d837fe | note | WP
b82a8cb5-2d38-5273-8ae1-403740c26d57 | note | Responsibility - Project / Site Engineer, Principal’s Representative
406d6ea4-31b7-58b1-a3f7-6c745a8da018 | date | Date Completed:
bdb6f786-9d14-4d15-990f-6b639b120d4c | checkpoint | 3.2 - Surface Preparation
773a9aa3-ff5c-5944-bccb-01be5c87e0da | note | Frequency - Prior to commencing works
598d64e6-ead0-515d-b29f-964c310c4c60 | note | Acceptance Criteria - Immediately before applying the prime coat, the full width of the surface to be primed shall be swept to removal all loose dirt and material. The prepared surface is to be inspected by the Principal’s Representative.
203147b0-7dc0-5aa9-9b11-f9be67189f19 | note | Reference Documents - Beca Spec 002 – 7.6
4588eeaa-da56-565d-8276-ecafa72e65b3 | note | Inspection/Test Method - Visual inspection
52f14954-865d-59b4-b737-81399518cca1 | note | Record of conformity - This ITP signed
b9599d19-5082-5bc3-9cc4-0386357d50a9 | note | HP
ad28aeba-8d64-5dfc-a5d3-fdc10776ea72 | note | Responsibility - Project / Site Engineer, Principal’s Representative
845b96ba-b45e-5e50-95c4-e86b955bf003 | date | Date Completed:
14b307ab-29c0-4f6d-affe-50c8e32766b7 | signoff | AUTHORITY HOLDPOINT
6b746c0c-f9f3-4314-b90d-936949285f61 | checkpoint | 3.3 - Application of Bituminous Material
5927ef10-05c0-5e30-b878-a0cf84ce60ba | note | Frequency - During works
6ef9b667-a035-5d62-a551-6efb39d2dd23 | note | Acceptance Criteria - The prime coat shall be applied at a uniform rate and shall be between 1.0 and 1.4 litres/m². The depth of penetration shall be a minimum of 6mm and maximum of 10mm
8552218b-5cb9-5e9c-8c60-c99ac0d16523 | note | Reference Documents - Beca Spec 002 - 7.7.1
dd2df51c-e5b4-5695-8529-0eba36c4ef7b | note | Inspection/Test Method - Visual inspection
f137d25f-23b3-5538-9e5c-8fd12bd00229 | note | Record of conformity - This ITP signed
89c050ed-eefb-5ca1-a945-d100eccc7d99 | note | WP
5ed4fc47-a56e-5a55-9e45-3c7ecd1836a7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
4a9b897e-27c8-5c6b-a81e-22e0b85583ed | date | Date Completed:
8d4009bf-128b-4ba8-9c2f-f59a6b63c4f0 | checkpoint | 3.5 - Job Samples
a25b296e-7122-59c1-965b-5dbbd425f1f6 | note | Frequency - During works
e1247717-fdc6-5cd4-ab4b-c7284f49c6f4 | note | Acceptance Criteria - Samples of each bituminous material shall be obtained from the delivery vehicle at not less than one sample per 10,000 litres of bituminous material sprayed.
499e39c3-8cf3-507d-8f7e-86373ba32d2c | note | Reference Documents - Beca Spec 002 – 7.11.3
c4c8f6a5-b97f-5568-883f-d5a6f587b46d | note | Inspection/Test Method - Verify
593b9d22-2eed-5a0c-89f4-3d58ec10c487 | note | Record of conformity - This ITP signed
e2673f27-73ac-52c8-8656-0bb7484901ea | note | WP
3d3107ee-41da-5a2a-add6-b44331834c17 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a61fc26e-0007-587a-a63b-9eeddb53199c | date | Date Completed:
3111ef1e-8067-4611-9b62-cc6907b81677 | checkpoint | 3.6 - Spray Rates
5293682c-172a-58fc-950d-21b77a8a012f | note | Frequency - During works
b650fea7-6531-52ad-98b5-0390b0fc3213 | note | Acceptance Criteria - The Contractor shall submit records of spray application rates at completion of each mobilisation
48c810e2-deeb-56db-8d38-8ac4d78c4fbd | note | Reference Documents - Beca Spec 002 - 7.11.4
9f9951cc-7314-586f-b814-06dbc24e42bc | note | Inspection/Test Method - Verify
e673b04d-668e-5ba2-8fa3-e193efd1cd4c | note | Record of conformity - This ITP Signed
e2bb34f8-7a03-5b63-b023-62fa95a3cd26 | note | HP
7f2eaaed-6852-58d3-809f-d4764c71b679 | note | Responsibility - Project / Site Engineer, Principal’s Representative
bc0e6561-5eeb-583d-9fbe-03ff94d22535 | date | Date Completed:
b07a4c7a-0883-4cd9-993a-7cc53f321ead | signoff | AUTHORITY HOLDPOINT
e7911909-0654-4de0-888c-21d32b274fb8 | checkpoint | Final Inspection
4c2faa46-c70c-5661-924e-86e232994310 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality\System Procedures and verifies lot compliance with specifications.
45b29829-d6fe-58e8-8eec-d07a28ddadfb | textbox | Print Name:
500536a7-e1bf-50d2-8c1a-760159d5e869 | textbox | Position:
c33e2fde-3cdd-5305-8e64-d94760ac2606 | date | Work Completed On:
9f863073-35d4-5e36-8dc1-19fa91b6d652 | date | Date:
b8376c32-7bdf-4fda-aac9-ba46ae4e16bc | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0020 - Prime Coat - Rev 1 | itp | ITP020 - Prime Coat
a1e0cb8c-28cc-424c-a78f-7fe526521fc2 | section | 1.0 - Preliminary Activities
1c0bdf25-0790-4f04-9077-28744eba5206 | checkpoint | 1.1 - Check for correct documentation
80e5f155-88d5-5bcd-ad99-df4b0aa779bf | note | Frequency - Prior to commencing works
fa088635-6c35-5834-bf44-3c991561f76b | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
cf1d362b-a3f0-57b5-b609-b432a06fce79 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
64334896-b042-5621-9ccf-8c4ea78a093e | note | Reference Documents - Current Revisions in Aconex or ACC
60d86afc-e4e5-5400-910d-b781e2c1d2f8 | note | Inspection/Test Method - Verify
38f6b59d-c829-5bca-9a30-6991bd840622 | note | Record of conformity - This ITP signed
090a4366-69ed-5b45-b3fe-28db780f2220 | note | HP*
4b1083bc-f58e-5105-9dca-8cb800f274fb | note | Responsibility - Project / Site Engineer
ef660620-3032-56b3-9d60-7fd7b4e39609 | date | Date Completed:
6c32f2ec-3e86-4bbf-8f8c-f2f619a03918 | checkpoint | 1.2 - Implementation of all measures and controls
d195e0c3-5608-569b-8fb1-e9a47e8db907 | note | Frequency - Prior to commencing works
9781b6d1-2003-5001-a1b2-ef0efc3311f0 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
ab7d6a29-018a-5822-9d9f-e2a713da4961 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
fcaee547-ed53-5cc0-8382-af25d76b5701 | note | Inspection/Test Method - Visual Inspection
083c25b2-2d46-500a-9a4f-c0ef5c2be2a9 | note | Record of conformity - This ITP signed
552fa7c7-a655-5b9c-bb10-711a3e743a9b | note | HP*
a58521ca-b4e7-5e86-b970-de24b28d6237 | note | Responsibility - Project / Site Engineer
1dbf899d-f489-5014-99f0-1b3c7b6d278b | date | Date Completed:
0a8af407-f3e0-4db0-a9a0-b4e782f6cd47 | checkpoint | 1.3 - Plant & Equipment Check
81e69d9a-5b44-5a8f-97f9-ce234fc7934f | note | Frequency - Prior to commencing works
de60ea39-2dc1-537a-8055-1bbcd19fdb31 | note | Acceptance Criteria - The Contractor shall provide equipment for heating and uniformly applying the bituminous material and blotter material.
1d90ffca-4aeb-5243-bd6e-4a3fc9a5f562 | note | ○ The bitumen distributor shall comply with the requirements of NAS 70: ‘Bitumen Sprayers’
e9e12f20-535b-54d5-83bb-156ac23d53b8 | note | Reference Documents - Beca Spec 002 - 7.3
42cd1320-3e39-55fc-a72a-00de41869e8a | note | Inspection/Test Method - Verify
680136a9-700a-5c42-96fe-f6a727c2a548 | note | Record of conformity - This ITP signed
72d6fd55-3c22-557a-b5e6-70b7c1db44a0 | note | HP*
3d9c33c4-db18-594b-a41c-b41ea185598b | note | Responsibility - Project / Site Engineer
88ffee46-8ff3-53f4-8227-30547653838b | date | Date Completed:
bbf324f0-fc6b-4983-8b48-4014871db62e | checkpoint | 1.4 - Weather Conditions
0f3982b2-bce5-5f5e-a2bb-71b976f8ecef | note | Frequency - Prior to commencing works
4805e412-0a30-55d6-af8b-97c13f793f9d | note | Acceptance Criteria - Prime coat shall not be applied on a wet surface, or when the surface temperature is below 10°C, or when the weather conditions would prevent the proper application or adhesion of the prime coat
d5f38335-254e-5f61-87c6-2ade1cc6f1dc | note | Reference Documents - Beca Spec 002 - 7.9
b67973ed-5400-544b-abcc-eb581fb36be3 | note | Inspection/Test Method - Verify
3c9d6a8f-19cb-58ca-a6df-7fe4ab9e183e | note | Record of conformity - This ITP signed
30700ce1-4ee6-5f7e-9317-366c06df8d7f | note | HP*
21402070-1d8e-57f4-b7fb-812c8ea5873a | note | Responsibility - Project / Site Engineer
68cbdc38-a1f4-5bdf-a13a-8e82d1885305 | date | Date Completed:
8a688cd1-e3a9-4ec0-adbc-05fc02ee376e | section | 2.0 - Materials
0d86362b-32ea-4f97-acbe-04e1e519108a | checkpoint | 2.1 - Cut-back Bitumen
edfce6ca-9860-547f-b246-713a7eef731d | note | Frequency - Prior to commencing works
be71cd22-df92-56a8-a2e5-572e4559b377 | note | Acceptance Criteria - Cut-back bitumen for prime coat shall comply with AS 2157 and shall be class AMC0, AMC00 or AMC1.
750cf271-f13e-5f7a-a9c3-d9bb75f66257 | note | Reference Documents - Beca Spec 002 – 7.4.1
9c39bdf3-7644-5b4c-b564-a2012325bb97 | note | Inspection/Test Method - Verify
0b57be03-5f65-5306-a59e-51d4ff1e5c2d | note | Record of conformity - This ITP signed
bdd0e7ae-f106-5d5b-9327-0bf3ba56a034 | note | HP*
fbc590d7-2ec0-58f4-93cf-1133ed77e60d | note | Responsibility - Project / Site Engineer
76913f32-d7b9-5876-859d-ce0afeaaea0b | date | Date Completed:
fdca09e4-1270-418f-9fab-dd36cbb42333 | checkpoint | 2.2 - Cutter
eefb8dcd-9b67-57f7-8363-a117e2ae0719 | note | Frequency - Prior to commencing works
0c87aad9-c9fb-5cb6-b412-a955c0a5f327 | note | Acceptance Criteria - The cutter for use in cutback bitumen shall be a suitable petroleum-based material complying with the requirement of AS 3569.
f9b606b3-73e7-5a30-8537-07106222a4de | note | Reference Documents - Beca Spec 002 – 7.4.4
19f8b060-d4d5-59a8-99b6-bcbcd0125ae2 | note | Inspection/Test Method - Verify
39148fc5-a21d-5962-bc1a-3eba6e10b7e7 | note | Record of conformity - This ITP signed
efbfb421-afa6-5e3f-9a8c-37445c679a72 | note | HP*
4e5fabdf-7445-5200-bf77-3fbfc79fb308 | note | Responsibility - Project / Site Engineer
458994b8-8aa5-5452-ba83-20c89d7b158f | date | Date Completed:
4fe7170e-50f9-4a44-90f1-4455616e3c1c | checkpoint | 2.3 - Bitumen Emulsion
aca34ed8-1ba0-515c-8116-163da6ad041d | note | Frequency - Prior to commencing works
b5f24114-5738-56ca-8e0d-242c3cdad483 | note | Acceptance Criteria - If directed by the Principal’s Representative, bitumen emulsion complying to AS 1160 shall be used as a prime coat.
e54f8d7b-5b04-5f97-8118-c33fa28654e1 | note | Reference Documents - Beca Spec 002 – 7.4.2
e9292f53-667e-5ec0-be49-cf0a66a59fb6 | note | Inspection/Test Method - Verify
c6f17cb2-f3e2-5c15-a49c-a878cbeef3b7 | note | Record of conformity - This ITP signed
68d8c2db-1067-5ad8-9eb2-23934fa25f48 | note | HP*
b2f87684-4113-5683-8389-21850ac419e4 | note | Responsibility - Project / Site Engineer
4e13904f-923c-5def-9741-ca93c6b29373 | date | Date Completed:
fc81c373-2332-5513-bf5c-ec962a3bbeb3 | note | Principal’s Representative - BecaCPL-GCOR-001036
361bc83d-b2d6-4456-8522-651de250b869 | checkpoint | 2.4 - Blinding Sand
011dff3c-cf11-513d-9e0b-a424ee1aaf96 | note | Frequency - Prior to commencing works
15385523-4d24-5e1a-a3ad-c811ca137a74 | note | Acceptance Criteria - If required, blinding sand to be used for absorbing excess primer shall comply with the following PSD.
2282c032-deb0-5f5f-be2e-a9476b4bac43 | note | – – – – – – – – –
4b68975f-d3bd-5155-b43f-58df01d6a150 | note | AS Sieve Size (mm) ¦¦ Percent Passing Sieve by Mass
0b774250-d152-5c76-bb81-e385511f2370 | note | – – – – – – – – –
8b212033-13e5-5f5b-b3c4-0a228318e308 | note | 6.7 ¦¦ 100
1e7a34d6-2f1a-56c0-95a9-b152ed54bdf0 | note | 4.75 ¦¦ 85-100
56e98935-3c6a-5607-839b-71da3f382d77 | note | 1.18 ¦¦ 40-100
978f3888-ceb9-57d4-98f4-bd102d4c6340 | note | 0.425 ¦¦ 10-50
acc5274b-bdb6-5588-858b-a1e12aef68a7 | note | 0.075 ¦¦ 0-5
03e9d942-3ff4-5260-9013-9efe247af5d7 | note | – – – – – – – – –
0c7ad2b4-7b69-5f37-ac63-73811b15fc0b | note | Reference Documents - Beca Spec 002 – 7.4.5
3339a759-c873-5713-8a9d-cde03860859c | note | Inspection/Test Method - Verify
a7f6daed-3c94-56df-b417-fe5fc0a37d68 | note | Record of conformity - Test Report
101888bf-2192-59ba-9475-afa6361e60c1 | note | TP
57de1639-c4d6-5695-94db-3a8287d54203 | note | Responsibility - Project / Site Engineer
a039e763-d319-59ef-95b2-b5c4f884abaf | date | Date Completed:
ca3eedf5-d89c-4186-9ffc-98f3e42542cc | checkpoint | 2.5 - Test Certificates
bd78bbfc-6b47-5001-8f1e-fb689f3a301e | note | Frequency - Prior to commencing works
4c5eedd5-396d-53fc-9749-55b6260bb7f2 | note | Acceptance Criteria - The Contractor shall submit a Test Certificate for each material proposed for use in the Works indicating compliance of those materials with the properties or requirements specified.
1e833167-31a8-56b8-a943-a3ddce13cc07 | note | Reference Documents - Beca Spec 002 – 7.11.2
967d1733-74ed-5952-9e01-b5a7366a283b | note | Inspection/Test Method - Verify
638b1d31-d5fb-5015-8bc6-07ff05209404 | note | Record of conformity - This ITP Signed
d16d41fc-ad72-5d5f-b5f4-75e6f8a908a1 | note | HP
1a8d1b10-7809-5069-81f0-f47131eb4e06 | note | Responsibility - Project / Site Engineer, Principal’s Representative
58b5c9bb-8669-519a-987c-6d73cb25fa82 | date | Date Completed:
55db0188-58d2-529b-8bd6-4460bdcd3764 | note | Principal’s Representative - BecaCPL-GCOR-000967
f8b41986-295f-4794-bf41-8dbda066fba5 | signoff | AUTHORITY HOLDPOINT
ecb49382-18fc-4eed-901a-408364f65541 | section | 3.0 - Construction
299089d7-10a2-4393-8a92-efe8d2b2848c | checkpoint | 3.1 - Trial Application
d144b3dc-64ed-5441-9b7f-c21dcb62a4b4 | note | Frequency - Prior to commencing works
bf4aa8bc-c909-54eb-a3b8-96e6fd37be54 | note | Acceptance Criteria - A trial application, to be conducted as part of permanent works, shall be conducted on an area of the Works agreed and witnessed by the Principal’s Representative
8fb97ab8-eaf8-5049-9422-386843d03e93 | note | Reference Documents - Beca Spec 002 – 7.5
cfe67c4c-15c1-59a5-9f39-9b382c8a83b3 | note | Inspection/Test Method - Visual inspection
1352953f-e4ac-59e1-ba7b-fcaf05f8dccb | note | Record of conformity - This ITP signed
3ff84b75-5407-539d-b851-f5cecf0b7b54 | note | WP
1c433402-1cda-5e93-a5b2-d0ef2fa1eb6d | note | Responsibility - Project / Site Engineer, Principal’s Representative
510ad5fe-5493-5a6d-9c53-b2d58b5f811f | date | Date Completed:
fd86f1c1-1d8c-4f6a-ba0d-e2961e358854 | checkpoint | 3.2 - Surface Preparation
5235856a-71f1-5bef-ad2d-647a8243a109 | note | Frequency - Prior to commencing works
b1d7c351-0622-5a32-a8ac-e793dc2fc850 | note | Acceptance Criteria - Immediately before applying the prime coat, the full width of the surface to be primed shall be swept to removal all loose dirt and material. The prepared surface is to be inspected by the Principal’s Representative.
5cc7f860-8c1a-5be2-8dc5-e550b89bfcb8 | note | Reference Documents - Beca Spec 002 – 7.6
901c69c8-d778-54e3-8215-5c43ff811247 | note | Inspection/Test Method - Visual inspection
2ef648d3-937e-538f-b17d-b13eaf318e1d | note | Record of conformity - This ITP signed
603fa105-9807-58ba-9a7e-1d644d6785f6 | note | HP
0450a84b-92ad-5df4-a3c5-4bb3999f537a | note | Responsibility - Project / Site Engineer, Principal’s Representative
5d17e978-e38c-5df7-ba97-6b2eee630565 | date | Date Completed:
812d3bc8-5983-4d8b-a284-7d3e9bfba958 | signoff | AUTHORITY HOLDPOINT
39ef0bc9-5453-4150-afd4-7ad1ceac2d05 | checkpoint | 3.3 - Application of Bituminous Material
07d3d7c5-b8ba-55f9-b5c0-58764fb49c6e | note | Frequency - During works
5baa220f-ed69-5830-989b-75b3b6736363 | note | Acceptance Criteria - The prime coat shall be applied at a uniform rate and shall be between 1.0 and 1.4 litres/m². The depth of penetration shall be a minimum of 6mm and maximum of 10mm
b03d062c-7d38-51c8-ba8c-45d9794ae3f9 | note | Reference Documents - Beca Spec 002 - 7.7.1
52be890b-5661-506d-b696-c3a1726b2fe7 | note | Inspection/Test Method - Visual inspection
492c42ab-98a7-5688-a2ac-94d8d5c7355b | note | Record of conformity - This ITP signed
3efbcb93-5f7b-512f-b49a-b1fd230fbd7e | note | WP
1ad3a74a-ad26-5172-9180-c0a4a9d90e17 | note | Responsibility - Project / Site Engineer, Principal’s Representative
68355d5c-0c4d-5e60-810f-135a9636b53c | date | Date Completed:
b5be9366-9f29-4c85-b275-a3adc09d7414 | checkpoint | 3.4 - Job Samples
3b9a3b34-f253-5b54-8edc-845f9c40e66a | note | Frequency - During works
f6bb36ca-d851-5d00-aa04-7377f9b443d9 | note | Acceptance Criteria - Samples of each bituminous material shall be obtained from the delivery vehicle at not less than one sample per 10,000 litres of bituminous material sprayed.
974acb5d-d74f-5838-9e5d-b517b0b9ba3e | note | Reference Documents - Beca Spec 002 – 7.11.3
c5aaf87e-97d8-545d-b640-bf8e0c18d9e2 | note | Inspection/Test Method - Verify
6eb4f2f3-2f56-55dd-afae-4ae1de94d265 | note | Record of conformity - This ITP signed
454a022a-e3a8-5dde-bc65-68d29eff10d9 | note | WP
3a0f3209-dd41-562f-9762-1de6531f5db1 | note | Responsibility - Project / Site Engineer, Principal’s Representative
b242dd58-a2c4-5650-8498-a39b2073ee5b | date | Date Completed:
380b9c8c-4f81-4e01-a1b2-58fb404f6199 | checkpoint | 3.5 - Spray Rates
868ac34f-59cc-5b7d-a286-1adcc0c9e3a3 | note | Frequency - During works
bd2a5f0a-7689-5183-a3a1-8d43ffb60014 | note | Acceptance Criteria - The Contractor shall submit records of spray application rates at completion of each mobilisation
e6ba7726-410c-5af3-8b3f-143425285d6b | note | Reference Documents - Beca Spec 002 - 7.11.4
49ec4345-619c-509f-9ce5-ff4fdef9d760 | note | Inspection/Test Method - Verify
c8c8a3a4-4b14-536f-9c64-55c31f1a51ae | note | Record of conformity - This ITP Signed
aeef1bda-d3be-562a-8ea9-5a8985d0f1b4 | note | HP
6c0f3a68-b9da-5565-8b34-a91678c98257 | note | Responsibility - Project / Site Engineer, Principal’s Representative
8f57e5ff-a979-5812-aa1a-2c606dc62777 | date | Date Completed:
986974b7-9e9a-4beb-b57b-cda2b791ee73 | signoff | AUTHORITY HOLDPOINT
b406b5cd-d6ad-4c01-9333-64cebc0a3a17 | checkpoint | Final Inspection
c0962a4a-b69c-5e1b-88c9-9f018ec5c44f | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
92af86fd-5fe0-53a2-8875-03fde9ada4de | textbox | Print Name:
2be8e558-029f-5e73-af51-f5ff22bbd11c | textbox | Position:
852864a7-7c13-5d8b-864f-8b2460177ef6 | date | Work Completed On:
1cbb886e-5c23-579a-970a-252094c725e6 | date | Date:
4c88f19a-2e80-407b-9781-ef977af6d0c7 | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0022 - Hatelit Install - Rev 0 | itp | ITP022 - Hatelit Install
6bc8eb5b-477b-4042-babb-3146a6873793 | section | 1.0 - Preliminary Activities
0d347d33-2891-4382-9c28-6a6f35594b21 | checkpoint | 1.1 - Check for correct documentation
fe8ec0d2-1652-5981-a4f0-535d6de7b482 | note | Frequency - Prior to commencing works
fab6a839-e954-5ff7-80d9-ab5b3a1e48a1 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
a4f2392d-8f1e-57ff-8b7a-5aff62d805fd | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
9c710b9b-74a3-5ed7-8eef-5d2733d62035 | note | Reference Documents - Current Revisions in Aconex, ACC
4982040e-3988-5e94-8294-ff3faf0f4577 | note | Inspection/Test Method - Verify
8245a88e-f653-5775-a1d0-234e6fc4ba4c | note | Record of conformity - This ITP signed
459f7d5c-0ba6-5b9a-baa6-e5c810116ae5 | note | HP*
795dfdfa-7874-59e0-984f-287a48aaed7b | note | Responsibility - Project / Site Engineer
cf716e5f-76f7-5aee-9735-0288986f3092 | date | Date Completed:
bbaa98b3-bae0-4735-abdf-9e22130c368b | checkpoint | 1.2 - Implementation of all measures and controls
bc148166-d093-5c81-9388-1cfd64b2ba6f | note | Frequency - Prior to commencing works
8fa509c0-ee5d-5e65-b46b-553cb5cccd46 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
c32b3392-7d90-562a-99ec-c4bd3d9fb812 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
477aa62e-c5f1-5949-b9b9-6c284825a576 | note | Inspection/Test Method - Visual Inspection
e53b282d-6654-5abd-8855-9cd14fa4a1a9 | note | Record of conformity - This ITP signed
a4faf0ac-25ca-535a-a761-8200c18d958c | note | HP*
f3d028cd-6ee3-5a89-b3bf-4076c5e0c8a1 | note | Responsibility - Project / Site Engineer, Site Supervisor
09c16e9a-861c-5f6e-9246-db315f42905e | date | Date Completed:
4fa1d1e6-5777-4f0a-aa29-8e84bb3359ee | checkpoint | 1.3 - Equipment
272633c6-1fc7-5cf2-a8e2-dd4e72feef16 | note | Frequency - Prior to Commencing works
35d5d63a-5c2d-5c2b-a512-c722589e74f8 | note | Acceptance Criteria - All plant and equipment to be used in the constructed of the works must be deemed acceptable to use by the Principal’s Representative.
cda47b3e-1add-5037-921f-a664579c3a53 | note | Reference Documents - Huesker HaTelit C Specifications 1.4.1
139ac96f-d512-5273-988f-74d2c4a4c8f4 | note | Inspection/Test Method - Site Inspection
c93c7c50-505c-5973-b7d4-9b27958670c9 | note | Record of conformity - This ITP signed
9042bb6d-5a32-5c61-a3c9-dd1e44f8fbf7 | note | HP
b28982af-f8b7-57da-a97d-a5ec782fb95c | note | Responsibility - Project / Site Engineer, Site Supervisor, Principal’s Representative
83cb149f-6216-5f32-9be7-f86a2d9afe21 | date | Date Completed:
8b376bbb-a1e6-4f91-9655-461cf0f1876c | signoff | AUTHORITY HOLDPOINT
b4d9b665-6961-4e3d-85f1-bc904b77a984 | section | 2.0 - Materials
52866c82-e5fb-4b1a-a69a-901250eb4b8a | checkpoint | 2.1 - Tack Coat Material Acceptance
7e0d55c8-462f-54de-be33-477f787e7886 | note | Frequency - Prior to commencing works, not less than 10 days prior to commencement of delivery
3344c660-6a5e-52f7-8ca5-4031ae8fb73e | note | Acceptance Criteria - Proposed tack coat material and test certificates shall be submitted to the Principal’s Representative for review.
9226a2e1-7a0a-5e0f-a8ba-079522b5e11f | note | Reference Documents - Huesker HaTelit C Specifications 1.10.1
6a0c7f57-2012-54c1-be1e-7c99c7f46125 | note | Inspection/Test Method - Verify
b021f3a4-2a6f-5bf6-8b9d-504f7d874287 | note | Record of conformity - Aconex Corresponde nce
801e8926-5318-594f-ae97-185cb10f18f8 | note | HP
68a456bb-1658-54cc-8097-8178cfacc3fc | note | Responsibility - Project / Site Engineer, Principal’s Representative
0db0a516-4559-57e3-a199-2e162a1e745a | date | Date Completed:
f0a28a39-fd50-4fdb-9ab4-3224fa3e3a05 | signoff | AUTHORITY HOLDPOINT
ccb715f6-6da2-4866-82fa-b307ece78b6d | checkpoint | 2.2 - HaTelit C Material Acceptance
e2aaf721-7970-5676-b31e-2be913b2382e | note | Frequency - Prior to commencing works, not less than 20 days prior to scheduled commencement of application
1f487632-ff56-58df-ac6e-f75c7ba9fa40 | note | Acceptance Criteria - Information on proposed HaTelit C manufacturer and test certificates to be submitted to the Principal’s Representative.
4a8b75fd-8d24-55f3-b4a2-2cf21262a4fa | note | Reference Documents - Huesker HaTelit C Specifications 1.10.2
2b303032-c2a7-53a6-b52b-8d613a77d637 | note | Inspection/Test Method - Verify
45859df7-4fdb-535f-868a-c091c3c30506 | note | Record of conformity - Aconex Corresponde nce
d43c360a-5efd-5477-a08f-4056aa9246bd | note | HP
6b961f63-6a0d-5696-a738-2b00e9ace95b | note | Responsibility - Project / Site Engineer, Principal’s Representative
24b16133-02c4-5a16-80a7-814ba4c2f469 | date | Date Completed:
7cebd87c-8e30-46ce-800a-dd198f4e1775 | signoff | AUTHORITY HOLDPOINT
57cf3a97-43ba-4c6b-acbf-db85a9ad33ff | section | 3.0 - Surface Preparation & Tack Coat
6849b183-cbe8-4337-b9d3-edd40420caf5 | checkpoint | 3.1 - Surface Preparation
32a77ac6-f3c0-587c-b794-aa9341294367 | note | Frequency - Prior to Works
ae612268-10c6-5bc8-9f8b-0aa82321a613 | note | Acceptance Criteria - All loose and foreign materials must be removed from the surfaces to a distance not less than 150 mm beyond the edge of the area to be tack-coated
a53f0137-f67b-56d3-977f-37006ee75fbf | note | ○ All treatments within area to be tack coated to be inspected by the Principal’s Representative.
4831e874-8d2a-511f-9e48-28d24b622af6 | note | Reference Documents - Huesker HaTelit C Specifications 1.6.1
ff9f51df-3dc0-5304-ac07-6686e39fa7c7 | note | Inspection/Test Method - Site Inspection
c34a2050-f5c1-522f-9248-a37bb78ebdf2 | note | Record of conformity - This ITP signed
e410af66-4d28-58e1-a032-7aff3a168130 | note | HP
e49985fb-4326-5b7e-a025-9afa3d51dbc6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
b21de6dc-93f6-5e2a-979a-3182886244b7 | date | Date Completed:
7320c9a6-5add-4862-bbef-78dc8ad9426d | signoff | AUTHORITY HOLDPOINT
a7d10a46-ea30-4ecc-b03f-7dfeec3ac83c | checkpoint | 3.2 - Spraying of Tack Coat
afa2c015-45a6-5fd4-97da-71d113c3ff7c | note | Frequency - Each Shift
74f3f3d7-ad7b-566c-ac28-a8c6ba67475e | note | Acceptance Criteria - The tack coat shall be sprayed evenly at the required spray rate of 0.4 - 0.55 L/m2 to achieve target residual bitumen as per guide.
3a7a394f-a247-5187-bbdd-437168194be5 | note | ○ Rate may be adjusted based on site-specific conditions ensuring HaTelit C is bonded to underlying surface.
1a591022-abe6-55c6-81e6-f24ca0c07b0f | note | Reference Documents - Huesker HaTelit C Specifications 1.6.2
ccac4f47-2d35-540a-818b-a9a3ba729487 | note | Inspection/Test Method - Visual Inspection
c90db9dc-c712-5992-a7a4-67cf4369d2ae | note | Record of conformity - This ITP signed
d310d4fc-96b9-515f-bd07-c778e831d795 | note | IP
1790a5b6-13c6-5819-958f-365e4b0976e5 | note | Responsibility - Project / Site Engineer, Site Supervisor
8857be56-ddfc-51e4-b1f2-cff21571ab05 | date | Date Completed:
8ff253e8-234a-426e-945a-13cc3c8692ff | section | 4.0 - Placement
905319cb-332c-4583-aa0e-b3e286218653 | checkpoint | 4.1 - Prior to placing HaTelit
b4265550-c3bf-5b4f-8f06-d4a282b84b63 | note | Frequency - Each Shift
f5915ba1-db42-56ba-b8f2-08fc23571495 | note | Acceptance Criteria - A minimum of 48 hours’ notice shall be given to the Principal’s Representative prior to the commencement of placing the HaTelit.
c52d0313-603d-5036-aaa1-e61947832a1b | note | Reference Documents - Huesker HaTelit C Specifications 1.7.3
008db338-5c67-5bd1-adcb-e530b059d1f8 | note | Inspection/Test Method - Visual Inspection
23093d03-0a3f-5dbb-a0a4-795ef7fc7f83 | note | Record of conformity - This ITP signed
e6960f47-ef78-5994-96a3-f33762b2b033 | note | WP
15a869d1-d930-598a-9b3b-7c69a1fee506 | note | Responsibility - Project / Site Engineer, Principal’s Representative
859b2eaf-0a36-5df2-95d3-2dafb773b9e8 | date | Date Completed:
0c3531ae-3754-405a-9ea7-52ab36cd3aa7 | checkpoint | 4.2 - HaTelit installation
25491cdb-51a5-5b49-9c2e-22a961328a5f | note | Frequency - Each Shift
9245fff0-348b-560b-8436-3e7222976d59 | note | Acceptance Criteria - HaTelit to be installed to Manufacturers Specification. Where placing multiple rolls, an overlap of 250mm transversely and 150mm longitudinally is required. The overlaps shall be treated with tack coat and rolled to bond to one another. For small areas, manual installation is acceptable provided a fully flat and crease free installation is achieved.
4c324ba5-83cf-5cac-9d93-4f18a1ca7b02 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.2
08bd3837-8272-5c7d-af67-86ea640b873c | note | Inspection/Test Method - Visual Inspection
cc24844b-86a0-5eae-b19d-0423130cd4ff | note | Record of conformity - This ITP signed
4cc2a9ab-7593-5326-abc1-c63253b40466 | note | HP*
102bbd1b-e63a-5497-84d0-fbcc8becc5a4 | note | Responsibility - Project / Site Engineer, Principal’s Representative
978c385c-eab7-5749-bbc6-ad058bafeb03 | date | Date Completed:
5566f46b-1958-405e-bddb-579f6890be4a | checkpoint | 4.3 - HaTelit Rolling
979ae15e-de2a-56fe-b5cc-9b1b42d5ae1d | note | Frequency - Each Run
af49bb2b-99eb-5c95-a365-5b63d2135780 | note | Acceptance Criteria - Rolls applied to tack coated surface without wrinkles, creases and folds. HaTelit to be rolled with 2 passes using pneumatic tyred rollers following application.
e76b356f-6c2d-57c2-9584-63bf1dbe5581 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.3
5481f69d-3a75-55cc-9e32-bed7b3817204 | note | Inspection/Test Method - Verify
70def9b9-a338-54a0-964d-493f31264e65 | note | Record of conformity - This ITP signed
4599d628-a39f-5cd0-84c5-b9541a59f97f | note | HP*
1ec9fdee-3fba-5bbc-91df-8e5bf469b19a | note | Responsibility - Project / Site Engineer, Site Supervisor
66de617c-698f-54bc-94e9-5fbb6d89e4d9 | date | Date Completed:
b77fe150-eaee-432f-8f81-fa7b94680fdd | checkpoint | 4.4 - Surface Finish Inspection
1828e8a6-0e11-5554-ae7c-07625c4e931b | note | Frequency - Each Shift
6cc26bc3-694a-5014-88a7-c75c356a7534 | note | Acceptance Criteria - Installed HaTelit surface to be inspected and areas recorded where required for flatness and saturation.
62e91eb3-bb8c-5335-bf92-533c6c9b0787 | note | ○ Surface to be free from any loose or deleterious material.
094b8f7f-f4c0-5218-89d1-1c7a863ed108 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.3
186f480c-5404-527e-8c9c-f1c7141f1022 | note | Inspection/Test Method - Visual Inspection
7df486d6-2118-5d81-bdeb-1d15587811b3 | note | Record of conformity - This ITP signed
bcf895da-238c-5d8d-88e1-9c37f6ac5049 | note | WP
cb496516-171a-5bd1-9507-a50b59222499 | note | Responsibility - Project / Site Engineer, Principal’s Representative
f3049765-5ece-52ca-98fc-c84b9ee6d654 | date | Date Completed:
08348277-ec6f-4c95-9dfb-f225c5eb239d | checkpoint | 4.5 - Spring Balance Adhesion Testing
bf3a9662-78c4-5774-a483-e0b9d2e55bbd | note | Frequency - 1 every 50 to 150m2
e080bfca-23d5-5051-bc13-9a490953d3b3 | note | Acceptance Criteria - Test locations to show adequate bond between HaTelit and tack coated surface.
7dd62148-0c53-50d4-b3ff-fee5855fba59 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.4
c0e76782-aacb-5d02-ba11-2648a44cef57 | note | Inspection/Test Method - Test Point
536a00b3-43ae-5ee8-b903-a03f8dd73190 | note | Record of conformity - This ITP signed
e1c8dbcf-db55-52a0-b938-3d6380baa1c9 | note | WP
50ee9d3a-2266-5752-b9db-2033d405a278 | note | Responsibility - Project / Site Engineer, Principal’s Representative
91898df6-2d34-5c79-9046-1c055b1f35cf | date | Date Completed:
a406d039-6ebe-4cba-b395-9e7ec98e7d10 | checkpoint | 4.6 - Asphalt paving over HaTelit
cea011ed-3dba-57d8-8670-e9b0fe1fd275 | note | Frequency - Each Shift
a3d59164-7e33-55cd-a69b-4a90064960e3 | note | Acceptance Criteria - Ensure that the surface of the installed HaTelit and the underlying asphalt layer is dry, clean, undamaged and free from loose material until the completion of paving over the installed HaTelit.
1f27c1e0-76e0-52c6-9edf-38387e05e15d | note | Reference Documents - Huesker HaTelit C Specifications 1.7.5
b5386e15-c8dd-5d4a-921e-6bdfb6bf111f | note | Inspection/Test Method - Visual Inspection
a0c8e412-a38c-5766-9472-25f18c4316d8 | note | Record of conformity - This ITP signed
f05e026a-276d-5e0e-90b4-f58f5ca70c97 | note | IP
d48bc467-ef2b-5a70-9d5e-02fec495a012 | note | Responsibility - Project / Site Engineer, Site Supervisor
7c4c1939-313d-5e55-b683-d22464184d3d | date | Date Completed:
b6db0038-bb2f-439e-9f37-af756f09e6e3 | section | 5.0 - Quality Assurance
8b6bdac1-8694-4698-9d49-3209be89fdcb | checkpoint | 5.1 - HaTelit Surface Conformance
20c67dec-9398-5456-8e61-a2ec224ed04f | note | Frequency - Each Lot
956a2fba-cc72-5356-bb16-b6d35517ee67 | note | Acceptance Criteria - The Contractor shall assess the conformance of the surface flatness and saturation of the installed HaTelit surface
4a200501-bd0e-50a1-8e3b-a7cc6316a7d1 | note | Reference Documents - Huesker HaTelit C Specifications 1.12.1
c14e827b-6ef4-51c2-bd6c-bbe5a77c4961 | note | Inspection/Test Method - Survey Report & Visual Inspection
43d53241-1fb7-5087-a6c3-fe4a887a5cc5 | note | Record of conformity - This ITP signed
68e22f3a-0ddb-58f1-ae0c-94b555197b70 | note | HP
9b84d4fd-5492-516d-832d-373d4dc519d5 | note | Responsibility - Project / Site Engineer, Principal’s Representative
4fc0e46b-780c-548b-a2f7-d098d369a1dd | date | Date Completed:
2914a338-9bc7-4878-ac1d-44c51d437206 | signoff | AUTHORITY HOLDPOINT
c510222d-7d53-409f-babb-145b8f045d5e | checkpoint | 5.2 - Nonconforming HaTelit Lot areas
e90312d1-0277-5893-9eb9-7a73142177f2 | note | Frequency - Each Lot
ac5147ee-d2cf-5942-9748-337340752818 | note | Acceptance Criteria - If required, any sections deemed nonconforming shall be removed and replaced according to Manufacturer’s Specifications - FH NCR Procedure to be adopted when lot area is deemed nonconforming.
9e04a652-662a-5ee2-a8cd-6251d87df491 | note | Reference Documents - Huesker HaTelit C Specifications 1.13.1
3d6f2628-3913-57d9-8f68-2b5c1c37917a | note | Inspection/Test Method - Visual Inspection
c409c60e-a456-519f-b0fd-cde38fd8a1f8 | note | Record of conformity - Nonconform ance Report
58d9cb3b-1b7d-543a-9ef7-9a37c5c184ec | note | HP
e5c153ea-14cf-598d-aa8a-53e828231c3a | note | Responsibility - Project / Site Engineer, Principal’s Representative
115d9055-3e44-5308-a2a4-13496030db40 | date | Date Completed:
f02561f4-f59f-4692-96ed-a5877fc14740 | signoff | AUTHORITY HOLDPOINT
50e79eb9-6ce9-45ac-83f7-92e11a3f7043 | checkpoint | Final Inspection
173b0058-bb77-5e89-bd98-2e79ba84542b | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
934f17bb-c4dd-5150-b8d8-e299a363d351 | textbox | Print Name:
66cb06fd-c54e-51d3-88ad-6d43e3a33b94 | textbox | Position:
b1d141aa-a90f-5146-8be8-f61e957ac211 | date | Work Completed On:
602f60e6-bc64-5dfa-98f3-3fcd848960c7 | date | Date:
48e2b06e-08d3-437c-aae8-49c61c1e0e9e | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0023 - RBB Install - Rev 0 | itp | ITP023 - RBB Install
d6b5c7ae-8d09-47fb-a3b1-3e55cc75e2bf | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
186676e5-7449-43fc-a1f3-1a01a8078414 | checkpoint | 1.1 - Check for correct documentation
2c95854c-7da0-5c61-9835-cece79e27c3b | note | Frequency - Prior to commencing works
61543c2b-40ac-517a-8104-fde5a363d1a0 | note | Acceptance Criteria - Current revision drawing is being used including the Subcontractor’s copy.
6f3997bd-ffbd-5b78-ae4f-6d82339efa46 | note | ○ Current revision to be obtained via Aconex.
0cc38b36-4bc2-5fc4-908c-ee6a83dab520 | note | Reference Documents - Current Revisions in Aconex or ACC
15c33c0b-e1b8-532e-a9d4-79f89e788aea | note | Inspection/Test Method - Visual inspection
03bd8099-2eba-5dba-a19e-e6ed65036f92 | note | Record of conformity - This ITP signed
cd19e67e-cb71-5841-8f20-01ee56fb076b | note | HP*
56f2d637-2f15-59e6-950e-52c69bcdf343 | note | Responsibility - Project / Site Engineer
46e90f62-3664-521f-8aa4-66a9b2fa436d | date | Date Completed:
201b6ccc-8d3a-496f-881e-b6221146a2c6 | checkpoint | 1.2 - Implementation of all measures and controls
7f728bcf-3978-5ba5-86d6-b9956acdf930 | note | Frequency - Prior to commencing works
c123ac80-ac46-5d2e-8df4-0c827fd340d3 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
ad5ace02-6ea0-5bc6-b35b-0f876d1c3e6d | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
e1d8dc7c-b8f7-5a09-8b88-9b596a8136da | note | Inspection/Test Method - Visual Inspection
83e1c9d9-2673-56b9-aca7-c792d5081731 | note | Record of conformity - This ITP signed
ead37f11-4ab3-569c-956c-d4d80be278d2 | note | HP*
6a719f23-11cc-513e-b11b-d453eba39fc3 | note | Responsibility - Project / Site Engineer
29e4158d-3355-5a02-b84d-5b225d392793 | date | Date Completed:
41e2ff4d-b15b-4a60-955c-8c17150ab031 | checkpoint | 1.3 - Definition of the work area
041f6814-a957-5767-b30b-2c397636ca14 | note | Frequency - Prior to commencing works
ff013046-beb0-5682-a098-5262c867a6a8 | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of work clearly defined.
580612dc-259c-5832-a13f-8703d05822a2 | note | Reference Documents - Drawings
7a7682a9-60ed-5efb-a925-4971a8e3a68a | note | Inspection/Test Method - Visual Inspection
95b4c713-5890-5fc6-bf8c-938ea8696cf5 | note | Record of conformity - This ITP signed
1750b9fd-8ea6-5f1d-999c-36a434bb6b74 | note | HP*
4b695982-94f9-52a3-a7b1-63121010aed3 | note | Responsibility - Project / Site Engineer
8b7d0b79-8ba6-5f97-b2e4-4bb059c65907 | date | Date Completed:
0cfe9cd4-5e91-4417-a535-4a27e4bc5c8c | section | 2.0 - Materials
d160ed2e-6847-41fb-ba24-e6ed3f7bdbdc | checkpoint | 2.1 - Rubberised Bituminous Sealant
fbd11730-afb4-56a9-9d6f-f890317f7be9 | note | Frequency - Prior to commencing any activity
2c9803dc-4f5a-5f78-a092-e4afea3512b4 | note | Acceptance Criteria - RBB must be a proprietary polymer modified bitumen (PMB) crack and joint bandage product and have the following properties:
03eed60d-ce28-55ac-b813-837e24d89e14 | note | – Minimum softening point to be 95°C
e342c0c3-1015-596f-95d0-7cc86a0516a3 | note | – Penetration at 25°C between 20 and 50
8e51ecc6-b845-51df-bdf6-079955508c9b | note | – Flow at 60°C at 5 hours to be maximum 5mm
9ee93e50-6207-509a-9ae3-0b26209ca80e | note | – Viscosity at 180°C to be maximum 3Pa.s
abdb09e9-354f-50ac-843e-6c417397a30a | note | Reference Documents - Beca Spec 002 – 10.7
fb46036d-fe3d-5318-acf9-6209c2225260 | note | Inspection/Test Method - Verify
e92a81c8-f380-582a-b9f7-552758d21cb7 | note | Record of conformity - Manufacturer’s Datasheet
4e973bea-b492-5cc0-bd28-5664a2c1c28c | note | HP*
a549832f-ad4b-524b-bb0c-c6c777cae0da | note | Responsibility - Project / Site Engineer
02fa45ba-d4b0-5331-96d2-453816ef42c5 | date | Date Completed:
9c3c15e1-04bf-4aa9-82d6-1e10f5cb6aea | checkpoint | 2.2 - Material Sources – Conformance Test Certificates/Reports
4244069d-59ec-58bf-9493-92bed312287f | note | Frequency - Prior to commencing works
c4eaac12-e3c2-5a6b-a2d9-4ffb336f47ec | note | Acceptance Criteria - Test certificates and matching production batch numbers are to be provided for each product used
4a9bdc17-a242-5966-a84d-e1677290c17c | note | Reference Documents - Beca Spec 002 – 10.7
2c6477c0-f0e0-55b0-8fcd-1cdd1014623b | note | Inspection/Test Method - Test Certificates
ae515e79-805f-5df8-bb65-7d051c84c64a | note | Record of conformity - Aconex Reference
ffc645a4-c81d-564d-8708-87cbae1b8233 | note | HP*
8bbd01a0-2e65-5ddc-ac85-a8b586138f82 | note | Responsibility - Project / Site Engineer
8fc12915-5ac4-53d1-9737-26f7a72467c4 | date | Date Completed:
2b78505f-4709-4e31-8b3c-61a3c9ece50f | section | 3.0 - Sealing
e9ba9f88-6c0d-48c6-86ab-f3716397a7de | checkpoint | 3.1 - Applying Sealant
861841e9-49c8-58a0-8426-caedab89037e | note | Frequency - During joint sealing works
8620914e-564f-56e4-975d-dcc24212dd58 | note | Acceptance Criteria - Sealant bandage is to be between 50mm and 75mm wide or as per drawings.
dc9f1072-3067-5bf7-97e1-78546ae8e8e4 | note | Reference Documents - Beca Spec 002 – 10.7
021932c7-7087-59e2-829f-f2c2b0df5f26 | note | Inspection/Test Method - Visual Inspection
cb413dcc-fda2-5e9a-a417-f14e87aecc0a | note | Record of conformity - This ITP signed
ceeeb223-8dc3-5c7c-94df-f44fb1ff3af3 | note | IP
2fac2c4f-ad4c-5196-9678-0c4aced13b1a | note | Responsibility - Project / Site Engineer
ba64cb88-7b63-5a78-a6c0-2601761bb935 | date | Date Completed:
7b89067c-ada2-4eb4-b4c4-ec1368559b41 | checkpoint | 3.2 - Protection of Applied Sealant
16494742-a6f6-5687-86a1-e05a964bd9ac | note | Frequency - During joint sealing works
f22346f2-9dd3-5a42-a7c9-162a247afc16 | note | Acceptance Criteria - Installed sealant must be protected from damage by traffic (and possible pick up on construction vehicles and aircraft tyres) until it has cooled to ambient temperature.
6f57a268-4b60-5f3c-85a6-16360a2afe91 | note | Reference Documents - Beca Spec 002 – 10.7
95f97a53-6263-5acb-bbb9-bdc1f3d784e1 | note | Inspection/Test Method - Visual Inspection
1d978172-71fc-530a-b78d-141d26a22a51 | note | Record of conformity - This ITP signed
7e410a98-6a8c-539a-b8e8-97af0cb70c00 | note | IP
793967b4-3968-51ea-8551-d53d4399ce63 | note | Responsibility - Project / Site Engineer
c30eda83-441d-59e5-8150-a3e62c6ee6d6 | date | Date Completed:
7142072f-8e6a-45e0-b5f6-10766bcde79a | checkpoint | 3.3 - Cleaning up
7ea2d8cb-875c-52c9-a92a-7386fca8926a | note | Frequency - After sealing works
20e1a690-efd5-58f9-abfd-912b712fd967 | note | Acceptance Criteria - Any sealant split on surface of pavements must be cleaned off immediately.
9ee8fd9e-5e71-5539-b571-7870e15ef959 | note | Reference Documents - Beca Spec 002 – 10.7
e0beba91-6ab2-5ff7-af81-3a591484e883 | note | Inspection/Test Method - Visual Inspection
dbecbf8e-d8d6-561a-bdf1-5777e0dd6896 | note | Record of conformity - This ITP signed
f52db4fa-7f90-5943-882d-7583591fd0fa | note | IP
bd5be3ef-182a-5b88-bf86-4f0b5efede10 | note | Responsibility - Project / Site Engineer
8af468f6-b16c-5017-ad32-330faa3db0c4 | date | Date Completed:
ff4c9e47-c7bf-4391-ad81-c8151ab4336e | checkpoint | Final Inspection
fe3a4b26-40e0-5abc-b2f7-b9b43ef0bba3 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
fe5a825e-c3aa-5431-b490-13d79dec5cc6 | textbox | Print Name:
53ce214a-06c1-5e68-ac23-9fb7d1fe59ca | textbox | Position:
649d83bc-792d-505e-9b40-61c34cb55df6 | date | Work Completed On:
85940907-b8d7-5644-9893-d51e93fdbd77 | date | Date:
2e52f8ff-f039-508a-a53c-edd8cbc34cf3 | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0024 - Line Marking - Rev 0 | itp | ITP024 - Line Marking
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
3dd0ff50-fb8b-5323-a5f4-174235db3bb0 | note | Frequency - Prior to commencing works
be6ca003-eacb-5536-9502-4129ac55e0b6 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
570d0344-ab6f-5cba-adbc-bde76755f574 | note | ○ Current revisions of these documents to be obtained via Aconex.
c431b101-0de6-59ab-8118-51c68a8a6dab | note | Reference Documents - Current revisions in Aconex
5575fbe7-6bd3-5b47-9484-d67ebca9a673 | note | Inspection/Test Method - Visual inspection
fb4ad021-737e-577d-93fd-1ad92991ec07 | note | Record of conformity - This ITP Signed
58ca559a-49a6-5f2f-821a-ca46bcc68042 | note | IP
d484f66d-bebf-5686-b013-3d3e948efaf8 | note | Responsibility - Project / Site Engineer
6ad6dba9-f8be-5a8b-bc3d-882f42f8e80b | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
0a017651-706d-54c3-85fb-702e8e5c945c | note | Frequency - Prior to commencing works
0106cef8-fb07-52f8-9d0b-233e8ef0f3d4 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
f58b93c3-403e-5d79-ab72-e34a033eac3c | note | Reference Documents - PSP, EMP, TMP, WMS, SWMS
1f09cf1c-9444-5f88-a031-ba84e76b04f2 | note | Inspection/Test Method - Visual Inspection
d7e6d134-341b-5d02-9a40-0380783982a8 | note | Record of conformity - This ITP Signed
68d00306-27e9-5052-b4d2-6a1210117b22 | note | IP
84d48667-eb48-5eb7-afae-2f88167e3235 | note | Responsibility - Project / Site Engineer
fcdc119e-9234-54a5-a446-d7e82e5bdb52 | date | Date Completed:
8e1d15a0-80f2-5559-9761-6b1391fc9e6a | checkpoint | 1.3 - Plant and Equipment
23478d3f-8c15-5af2-995f-bbc053c914e7 | note | Frequency - Prior to commencing works
69b71fac-fa43-5c98-ad82-6a2ed8531a3e | note | Acceptance Criteria - Plant and equipment used in the works are appropriate to achieve specification requirements.
c5ca853a-957f-5094-972c-3521e8655124 | note | Reference Documents - BECA 15.3
99119ef4-7428-51ff-ac9b-31cd7d180bfd | note | Inspection/Test Method - Verify
1244ceca-96fd-5036-9f91-a4b83546731a | note | Record of conformity - This ITP Signed
f873376a-fa8a-524e-aeac-b362e3eaf3ca | note | IP
6f99f2b5-daa8-5308-b16d-6c10228094b3 | note | Responsibility - Project / Site Engineer
57f8b51b-7585-5199-95a2-a1dda2a6ec41 | date | Date Completed:
3d6e7a74-8a4b-569d-a3c2-e0d24e5279ac | checkpoint | 1.4 - Materials
11e6049f-9282-599b-8fcb-dc11a80f43da | note | Frequency - Prior to commencing works
6b583343-7806-5826-822f-f886d472e47a | note | Acceptance Criteria - The paint to be used shall be a premixed synthetic latex-based paint (such as WATTYL AIRPAVE or approved equivalent).
23e4def6-2144-530f-9067-8eb87b76f67d | note | Reference Documents - BECA 15.4.1
849ce26d-f900-51e9-b9ab-21ff7a41d281 | note | Inspection/Test Method - Verify
1d78b532-1208-5f9e-b15d-a6fae4f54452 | note | Record of conformity - Material Reports / This ITP Signed
ecc46e2a-e3c4-5a42-bf21-ab6823f96a58 | note | HP
96744f4c-965e-5c80-be1f-96add9453d56 | note | Responsibility - Project Engineer, Principal’s Representative
05d53222-c990-50eb-9cc3-8770814cd045 | date | Date Completed:
0119ba62-9ab5-5c8c-bf06-711caae1fe15 | signoff | AUTHORITY HOLDPOINT
da39e7d4-ce7e-5bb2-9638-ef2f50abb8a7 | checkpoint | 1.5 - Material Handling
c3d6276f-066a-52a9-9000-ef5282e2e88c | note | Frequency - Prior / During works
2d82c0ea-8f85-595a-a7cf-90869432ba81 | note | Acceptance Criteria - The paint Is to be packaged in 20 litre containers that are of durable construction without sharp edges. Paint containers are to be clearly labelled “Airport Pavement Marking Paint” as well as being labelled with the following: Manufacturer’s name, Colour, Batch number and Date.
2c1660b3-f58e-5825-ae91-5655d2f8ce13 | note | Reference Documents - BECA 15.4.2
1dd3cc97-d546-56df-adb9-054971e0be0c | note | Inspection/Test Method - Visual Inspection
b8b1013b-2633-57f4-a0b9-1a8a5c0cb19b | note | Record of conformity - This ITP signed
8a6cf72d-6148-5f62-ac49-1cd72a02075b | note | IP
8fb203db-286c-5914-b0dd-97105b755bfb | note | Responsibility - Project / Site Engineer
3a10c983-588f-5609-afab-b5dbc4b19711 | date | Date Completed:
c871658f-3e9a-5e49-b084-2962c09d6aee | checkpoint | 1.6 - Survey and setting out
01f9edc2-85ae-5270-81d6-345693e57f30 | note | Frequency - Prior to commencing works
6a4e6821-b71c-532a-af20-36f243b84fcf | note | Acceptance Criteria - The Contractor shall carry out the setting out of the pavement Markings as shown on the drawings. This shall be approved by the Principal’s Representative.
54e07015-df2e-5be5-b2b2-49c296fb3488 | note | Reference Documents - BECA 15.7
15737500-c913-50a7-bd25-063724ab7b7a | note | Inspection/Test Method - Verify
9fd85844-0a9a-5631-909a-9c3d9dad2f4c | note | Record of conformity - This ITP Signed
40d1cdd5-d2ea-5735-99bb-a2562c034cf6 | note | HP
9aee3244-b56b-556c-bfa0-5c4043c5657e | note | Responsibility - Project Engineer Principal’s Representative
8c36297f-486c-568f-a61a-a65ff6307389 | date | Date Completed:
e0c31cab-119d-5382-b56f-d6078cebdc06 | signoff | AUTHORITY HOLDPOINT
648931ca-ea92-5007-b762-3e625bbef167 | section | 2.0 - Construction
681ade3f-e48c-5564-9edf-5b16cbc3d45b | checkpoint | 2.1 - Removal of Existing Line Marking
764ec3ec-870c-57a0-87f4-8159a07872d4 | note | Frequency - Each Lot
3ac85a29-e707-5e70-97ee-fd25e2b8d166 | note | Acceptance Criteria - Existing pavement markings, at the locations shown on the Drawings, shall be removed by water blasting or other approved means that is non-destructive to the existing pavement surface.
a20704dd-3752-517f-a098-c5e79b7192bb | note | Reference Documents - BECA 15.5
efedbbca-ee60-5ba5-8a07-b130fc8b4f3e | note | Inspection/Test Method - Verify
ebdb1d2a-b6d0-531f-b042-e2a69b4db626 | note | Record of conformity - This ITP Signed
68fa665a-82e1-547c-bad6-7356ac5d833c | note | HP
8d9993ac-df7b-5f07-8d20-5a34c339c90a | note | Responsibility - Project / Site Engineer Principal’s Representative
559431fd-bcaa-51ae-bf61-6f39dba60262 | date | Date Completed:
eef8f178-0072-5287-9af2-7a4ca27e92f2 | signoff | AUTHORITY HOLDPOINT
14088100-2192-5bdc-81da-ec742c09fb6c | checkpoint | 2.2 - Surface preparation
e2c8b966-0ac1-5f47-8638-ee0d2152fff2 | note | Frequency - Each Lot
76c75673-a826-597c-b900-f03b90f44781 | note | Acceptance Criteria - The surface of the asphalt or concrete pavement in the areas to be painted shall be thoroughly cleaned prior to the application of the pavement marking paint. This shall be approved by the Principal’s Representative.
0a20df0c-3926-58a9-bbf0-3ce181017df8 | note | Reference Documents - BECA 15.6
5bbade8c-02b7-54a8-b284-1888a7264a16 | note | Inspection/Test Method - Visual Inspection
57424184-ac24-531d-9aca-1d36f6c32426 | note | Record of conformity - This ITP Signed
864c3c6f-408b-570b-af65-2cee519aabcf | note | HP
b326933c-558c-5185-a248-36d2b855bb39 | note | Responsibility - Project / Site Engineer Principal’s Representative
0be80a0a-60a2-5ade-a6e7-333e0e25db80 | date | Date Completed:
53600c54-7994-55d7-94b2-5f0976e97edd | signoff | AUTHORITY HOLDPOINT
5ebec58b-474a-5be8-8f64-e19e13ed9304 | checkpoint | 2.3 - Weather Conditions
9549e51a-6f94-58bc-8d48-fca26969af2a | note | Frequency - Each Lot
6dafaa30-d289-5b1e-b8c8-3b0007c8de14 | note | Acceptance Criteria - Pavement marking shall not proceed during wet weather or when the pavement surface is wet or when rain is likely or during high winds.
ebc917bf-fd7c-5078-b024-249d2e48f67f | note | Reference Documents - BECA 15.10
6737025b-0d8b-5d4a-9a22-8435e396f8b5 | note | Inspection/Test Method - Verify & Visual Inspection
9664c81b-3037-50b0-89d2-58344186894b | note | Record of conformity - This ITP Signed
87604978-b18d-589d-aa84-162f4868fc54 | note | IP
e4a2e562-4cf0-5a52-997f-da44b4c5d8b7 | note | Responsibility - Project / Site Engineer
31a0d07e-546e-5c07-ac93-fa15e582e689 | date | Date Completed:
a5154039-7580-5563-baf9-1bf6f8ffe4d1 | checkpoint | 2.4 - Application
3d301684-6259-5233-b2eb-7321d10d1906 | note | Frequency - Each Lot
ab07e7f6-d46e-53a2-8beb-1c2407fc97fc | note | Acceptance Criteria - The paint must be applied in two even coats to provide the required minimum total dry film thickness as specified by the manufacturer. The second coat is to be applied no less than three days following the initial coat.
82c65602-9fdf-5025-9dc6-f31c48c4c3e9 | note | Reference Documents - BECA 15.8
7856548a-50a2-5b31-816a-2122d0e018dd | note | Inspection/Test Method - Visual Inspection
06cc89a2-f42b-53a9-8ba6-8b47cf98f081 | note | Record of conformity - This ITP Signed
d47c620d-2137-5eea-9e1f-7aa1c65c68d8 | note | IP
5fa78e4a-7ccc-5d95-a9ab-6a81411db053 | note | Responsibility - Project / Site Engineer
cfc11233-6da3-50cc-9239-dcc92dab8c34 | date | Date Completed:
e81d07e9-bb2e-5c81-bddd-4d004625d48d | checkpoint | 2.5 - Application Rate and Conformity of Application
563b61c1-ce07-5b57-b773-f41581ee0fac | note | Frequency - Each Lot
98200636-45d2-5279-b3ed-9c18ff03b166 | note | Acceptance Criteria - Daily records of paint usage and the area covered shall be maintained by the Contractor.
c1b68d07-31e8-5e09-9c3e-9d37dbf15bab | note | Reference Documents - BECA 15.12
7fec02aa-b67a-5afd-9382-76c469161716 | note | Inspection/Test Method - Daily Records
16591429-06b7-5f37-9377-a7cfe44792ea | note | Record of conformity - This ITP Signed
98ea938a-a873-5359-b179-b853ee519235 | note | IP
64bb29e1-5afd-5cc4-b6b8-4fb265e2f13c | note | Responsibility - Project / Site Engineer
d3b740af-f020-5400-a732-468d6ab5fb0b | date | Date Completed:
3da33369-6e9d-5056-b7b3-713e5e79cd00 | section | 3.0 - Post Construction
bbff472a-32f2-504e-b36c-c68825e037b4 | checkpoint | 3.1 - Records
162b4d84-3404-5e60-9bb5-b03d95ff3c65 | note | Frequency - Each Lot
2cdbf4f6-160a-5604-adea-5b385854df4c | note | Acceptance Criteria - Finished pavement markings shall conform to the following tolerances:
bbf7bbd5-8abb-5779-b60d-646b662381b9 | note | ○ Location of pavement markings ±10mm
f689dfa8-e020-5ef4-a77f-3247e0d5b38c | note | ○ Width of any line or line forming an alpha/numeric symbol ±5mm
eb6dca9a-7994-5705-a50c-2c2f9c6f092b | note | ○ Length of any line and the spacing of broken lines ±50mm
be1d940b-5121-5c10-9be7-cb9f8d85600c | note | ○ Dimensions of any alpha/numeric symbol ±10mm
cf5961b2-a636-54fc-a693-400e4009ff29 | note | Reference Documents - BECA 15.9
6b03534f-1808-5f6d-90be-e674587b5f75 | note | Inspection/Test Method - Verify
df3bfed5-d7f5-516f-9f0d-3ac8de9a4400 | note | Record of conformity - Survey
923afd04-5dea-5669-b301-2cae53158290 | note | SCP
c9b17de7-b8e0-56d3-8f36-4f87e091d88c | note | Responsibility - Project / Site Engineer
7ac1f5cd-621f-5399-a338-8e054ec6a8d4 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
9f6a4cf4-dc9b-5660-b654-f7197f44fbde | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
4354d4b2-71d7-5b11-8246-5ec50a7b1b78 | textbox | Print Name:
fe9538f7-73ad-5156-a05e-cae731d3d5a6 | textbox | Position:
ef4e302c-689d-5b40-a0eb-3681aee031ea | date | Work Completed On:
d36e0338-74d7-585c-bf57-6c855923465a | date | Date:
78f3a578-0ae0-499c-a1c1-d44847bfa722 | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0031 - ALER 3 Onsite Concrete - Rev 0 | itp | ITP031 - ALER 3 Onsite Concrete
4806a8d1-4a93-4552-9d4b-2a6d0cd0f000 | section | 1.0 - Preliminaries
9aaad686-3236-4d35-b6bf-343a953d9e58 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
593c5a38-426b-5717-9241-90bd62442824 | note | Frequency - Prior to Start
513cddc9-ee02-599d-a375-e626545875bb | note | Acceptance Criteria - Current revision drawing is being used (including the subcontractors copy). Current revision to be obtained via Aconex or ACC
4861f6b8-797c-537d-87d5-0309fb7637fd | note | Reference Documents - Drawings and drawing registers
b020b443-7d50-5ae9-ac17-f2369bd80b1d | note | Inspection/Test Method - Verify
29eb2591-60f7-57a2-bfe3-2c192907d497 | note | Record of conformity - Up to date drawing sets and this ITP signed
38021303-5164-5cee-9b31-5502da7ad7ef | note | HP*
885f4745-6ba3-535f-ad80-f31fdc8821c1 | note | Responsibility - FH Engineer
d9039991-c1cc-528b-9063-e93709387960 | date | Date Completed:
55926751-db0f-4167-b625-50a915ef3efc | checkpoint | 1.2 - Implementation of all measures and controls
1394aa06-238d-55f9-bb45-f7c49af2e97e | note | Frequency - Prior to Start
fd7be0a8-28f3-556c-a7a8-70003d980b28 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is CEMP, TMP, SWMS, & WP
cd82d0da-964c-50b2-bd83-431c562e7eb5 | note | Reference Documents - CEMP, TMP, SWMS, & WP
78f75249-1aa6-5409-841e-9cd3a6b91467 | note | Inspection/Test Method - Verify
918215a5-d66c-542e-a8ee-0294badb95f5 | note | Record of conformity - Site and office Inspection
2f3f663f-09ce-5544-8b15-beb8bb6dc163 | note | HP*
2acfc95b-5c0f-5367-a43a-afd8aab0be9d | note | Responsibility - FH Engineer
e61a8d1f-5401-592b-8925-345a541b18f7 | date | Date Completed:
2e508e9c-3fb3-4fb4-ab18-a9aaf749ef4f | checkpoint | 1.3 - Excavation Permit
cd8e4a7c-a5ba-5384-8e1c-bb22b771f3e4 | note | Frequency - Prior to Start
2b89a651-5b93-59dc-872b-84eb070111f6 | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
acd3b0d4-d906-5e2c-bb5f-3184a7b4023d | note | Reference Documents - APAM, Excavation Permit
0b1ebb3c-398d-5826-80f8-129e4a855e3e | note | Inspection/Test Method - Verify
45615be5-d292-5ac9-ac14-41d5074452f8 | note | Record of conformity - Proof of & permit ITP sign
1810de76-77c6-5566-86f8-29cea9af8d73 | note | HP*
5298e48c-cbc4-501d-9281-5748949787eb | note | Responsibility - FH Engineer
fb8b9574-3915-58c3-8a13-7eee556690e1 | date | Date Completed:
2d746ca0-6332-4896-9116-72ed7fd8c09b | section | 2.0 - Supply of Materials
1de86f1f-307b-4ab2-ba50-3b96b5f94306 | checkpoint | 2.1 - Reinforcement
05f1a8bd-05a4-5ca4-b59b-ac76542fcfd0 | note | Frequency - Pre-commencement
83755d2a-0cee-5b0f-a1ca-aeab0d0fde47 | note | Acceptance Criteria - HOLD POINT
841c1010-7b73-5d6a-a4e2-200996575b0a | note | ○ Test Certificates demonstrating compliance of the reinforcement with the requirements of AS 3600
cb965aff-4e5e-57aa-87f6-370eaf4ee24e | note | Reference Documents - Drawings and Specification
4c481164-1a51-53cb-8829-c02650e1df38 | note | Inspection/Test Method - Verify
1a6a32e2-6135-5f69-ad65-3972deb28a8c | note | Record of conformity - Aconex Reference
fb7c0b70-93b3-56e8-bbf9-63aa3c7818c2 | note | HP
8170380e-bf19-52a9-99d5-a89c5dc7fd0e | note | Responsibility - FH Engineer / Principals Representative
034cda63-7117-5d45-bb1d-268b25cecd72 | date | Date Completed:
f5b740ac-ddd5-4f26-bda1-1e4955e3587d | signoff | AUTHORITY HOLDPOINT
6dc03d6a-2bb9-4065-9bec-5a1d34b6666e | checkpoint | 2.2 - Concrete Mix Designs
10ec17a5-a9f7-5e57-9d0f-98f614ac998d | note | Frequency - Each Lot
0e0a528a-21ec-5f07-bdf2-49407e425013 | note | Acceptance Criteria - HOLD POINT
77309343-c1ad-5025-a274-3c92b164b3cd | note | ○ Mix design to be submitted to contract administrator for review and acceptance.
498355fa-71e3-55be-ba72-bd13dcbfa45a | note | Reference Documents - Drawings ZULU-BECA-014-DWG-00201, ZULU-BECA-030-DWG-20001
4c935984-0a71-5fa6-b998-911ccb074f9b | note | Inspection/Test Method - Verify
abf29593-f63e-573d-b42a-7c139f06631d | note | Record of conformity - Aconex Reference
fc5b9380-9773-5ada-bf67-e0b657128073 | note | HP
583a9303-80c9-5139-94a9-e9bec06e4e30 | note | Responsibility - FH Engineer / Principals Representative
93c113c3-2534-5875-bc37-f0d59fdc9cee | date | Date Completed:
8b93dc62-3fef-4ae4-a957-00444ae0de43 | signoff | AUTHORITY HOLDPOINT
9eedabf8-824e-4627-9b17-80d8cf759065 | checkpoint | 2.3 - Review of Curing Regime
f17f448f-9685-5668-9d7b-e6540d02efe3 | note | Frequency - Each Lot
5feea68c-0b08-54a6-b1e0-65bcd511c716 | note | Acceptance Criteria - HOLD POINT
0fcfde67-ecb3-5eef-9e77-fe37059c8451 | note | ○ Concrete curing regime to be reviewed and approved by the contract administrator prior to use
29264901-190f-5f18-801e-5c6db226e100 | note | Reference Documents - ZULU-BECA-030-DWG-20001
3d812be6-1846-5dad-8475-8942de11286b | note | Inspection/Test Method - Verify
ca222c9f-083e-5893-a99c-fbcaf5a6b3b0 | note | Record of conformity - Aconex Reference
becc2851-4768-5324-84f2-a1e6cf307089 | note | HP
bad26777-1dea-5a1c-b2fa-36f0746bf7f1 | note | Responsibility - FH Engineer / Principals Representative
1a9e5a18-b346-5b42-8ec8-2307f82cb58a | date | Date Completed:
92034d8d-5b54-45df-bae9-e0a3de6225a0 | signoff | AUTHORITY HOLDPOINT
e2600f7f-92ae-44d5-8edf-261e60436a1c | section | 3.0 - Construction\Erection of Formwork
57369f24-309a-46cc-bf55-c55169dec4f2 | checkpoint | 3.1 - Setout
3d9f956e-c178-55f5-b928-edca4d2ce53f | note | Frequency - Each Lot
768f1b93-7705-5e81-aa90-eea53acf17ec | note | Acceptance Criteria - Setout completed and conformance with Beca IFC Drawings.
db1bb157-7607-52e1-8c2a-439806f04dc3 | note | Reference Documents - Drawings
27cf5a9b-e1ba-541e-8bf9-b9c510292e3c | note | Inspection/Test Method - Verify
8a7b673a-7821-5dff-aded-1dd9d04ef99c | note | Record of conformity - Survey Report
3769ed35-6293-5c76-997d-c48015222d0c | note | SCP
379171d7-0d97-5ed9-9d75-4d0274c8cd49 | note | Responsibility - FH Engineer Surveyor
889ec5a0-93d5-5a93-aa31-214eccde22e3 | date | Date Completed:
89c8f157-185a-443f-bb3f-8937f949a68f | checkpoint | 3.2 - Excavate
d52945b5-6b48-5102-91e4-a1a66eb686af | note | Frequency - Each Lot
67feda27-92c2-571d-9ccc-35ad09f64318 | note | Acceptance Criteria - WITNESS POINT
e9994449-9af4-5cb0-8576-16ad30493c60 | note | ○ Excavation depth shall be as per specified or as shown on Drawings to accommodate structures.
34efc662-99d2-5511-9f18-e9a2bfa5ed93 | note | ○ Principals representative to be notified for at the completion of excavations for inspection prior to any blinding being poured.
49e9b8d2-2eb5-5121-b32c-a1c829e6ab51 | note | Reference Documents - Specifications as per Drawings
15cc5f51-a815-50e4-a48c-94f3d90a6ce4 | note | Inspection/Test Method - Verify
0a7f07d0-2296-5616-bd01-b2c79ad318c4 | note | Record of conformity - This ITP signed
ecd87402-cd0c-5428-ba14-f76d6e8f9c11 | note | WP
f7125fc4-202c-5d4c-9b22-4273ab22014f | note | Responsibility - FH Engineer
9089d956-5a6d-574f-a940-3a47e656339a | date | Date Completed:
8938c8a4-5180-4b48-adc1-e60f8a9ca0f8 | checkpoint | 3.3 - Confirm Ground
3dd63fa5-ad6b-5688-b515-f3e1612f68d1 | note | Frequency - Each lot
c70e63ac-a984-59d6-8445-51b90ad8e4a5 | note | Acceptance Criteria - HOLD POINT
0c44630b-f00a-58fc-9cf3-05f1d2cd2772 | note | ○ Completion of excavation and inspection of subgrade materials.
0d2a4fc5-8e7b-5bb8-b3af-3bfa14e0ddfd | note | ○ No soft spots, unsuitable material. Confirm ground bearing pressure
aa63bd56-b4d4-5af3-a581-1db2a23506ff | note | Reference Documents - Specifications as per Drawings
e1575ea7-e6cd-53b0-8d56-0e007c57cedd | note | Inspection/Test Method - Verify
a9b15620-d57d-5a77-b4a6-c53d4eeffd9d | note | Record of conformity - DCP Test Results (if required)
8a320a93-26cd-51ba-9c15-60ac46f7e417 | note | HP
e6f1a752-4514-5093-aa44-25379b479608 | note | Responsibility - FH Engineer
c654970a-1784-5703-a52d-ec34af9fe655 | date | Date Completed:
cac20eae-f595-44c3-9a85-aa069acaab3e | signoff | AUTHORITY HOLDPOINT
d3e15cbd-5fb5-434c-bafe-e9bc50f31989 | checkpoint | 3.4 - Concrete Sub-Base
333642ae-ad67-5cbb-b0af-4a29edab0d53 | note | Frequency - Each Lot
733f9691-41d9-5a5b-9200-cf0c6531c5ea | note | Acceptance Criteria - Blinding layer is installed as per drawings
a51be099-4258-5e2a-8e1c-962f9720cf72 | note | Reference Documents - Drawings
bf126300-f350-5ed1-83d0-54106bd53bb4 | note | Inspection/Test Method - Visual Inspecti on
2bc0597d-87f0-54cf-968e-bc81b58bc64f | note | Record of conformity - This ITP Signed
5fbeb9dd-9149-536c-96ee-28387db39694 | note | HP*
3de35f9e-40d6-52e4-90eb-d5fadd4a53a1 | note | Responsibility - Site Engineer / Foreman
40d85e62-3c18-53f0-be2f-979dd30bc024 | date | Date Completed:
862690ea-34c7-4693-b90f-f6e60eb19b4c | checkpoint | 3.5 - Formwork
b85e6bc8-2bbf-5e8b-82f1-9a0d3ddfca1f | note | Frequency - Each Lot
e0b4da40-edce-5c8f-a8ed-521f8823da49 | note | Acceptance Criteria - Formwork / Reverse Shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
67993a53-0716-596c-93e9-c3e849552e03 | note | Reference Documents - Specifications as per Drawings
14df37c1-979b-5416-970b-ae909c7bc23b | note | Inspection/Test Method - Verify
b85a05b4-fdc5-5141-a977-dbc48fabe626 | note | Record of conformity - This ITP Signed
024aaba1-dd7e-54ac-9dae-b9c86188aa91 | note | IP
e0fbfcb9-9915-5b45-81f7-0a2499084485 | note | Responsibility - FH Engineer Surveyor
3cdf28e6-3b0f-5d9c-bb74-ee00cc9049c3 | date | Date Completed:
6040ee44-eea6-4c83-897d-06c4d8b0eee3 | checkpoint | 3.6 - Penetrations/Cast in items
edd8576d-21ab-55de-8551-ef88dfa1fe4b | note | Frequency - Each Lot
7b9289ba-c769-5440-9dae-bc084df94827 | note | Acceptance Criteria - Penetrations/cast in items are present in the formwork.
76e5ecd7-aa1d-56b7-a60b-0d33f9060345 | note | Reference Documents - Drawings
a0981070-0e97-58a9-9b2a-5841d160d353 | note | Inspection/Test Method - Verify
dd3c51b0-76ea-588a-9076-25e06e67e83b | note | Record of conformity - This ITP Signed
ea5c4aeb-e8b5-567f-9bdd-34300b1189a9 | note | IP
c2881c58-9366-5189-89f7-418e8bfc47fe | note | Responsibility - FH Engineer Surveyor
25c808d3-d177-5d60-92b9-758855e794bb | date | Date Completed:
21ca0bdc-e051-4ca6-9e50-3191217714bc | section | 4.0 - Reinforcement
900f1841-0268-49b5-ad94-801c251af620 | checkpoint | 4.1 - Reinforcement installation
65a1acfd-120c-5e18-8ffb-b3b58affeec7 | note | Frequency - Prior to concrete pour
d1b28e11-ef9a-545f-815f-0a52af862eb5 | note | Acceptance Criteria - Pre-Pour Checklist Completed:
034d6501-3d4a-57d5-b4eb-f3e1d08d2277 | note | ○ Position and spacing check and recorded.
bd7f9b32-b17f-59e4-8b41-8a3aae6c523f | note | ○ Cover checked and recorded.
663d2fd6-e8e4-5b67-940b-70afa61b9614 | note | ○ Reinforcing supports checked and recorded.
263e712c-19d6-5912-ac6c-e3ce3d77571b | note | ○ Laps at required length.
1ba38d02-76ab-5ad7-bfbd-7aac838f17c2 | note | ○ Penetrations/cast in items
baf64cba-b413-5086-971d-2dd6d76f2cc2 | note | Reference Documents - Specifications and drawings
bdbfa960-8795-5803-bc38-13b139c24d0c | note | Inspection/Test Method - Verify
da5bcdb6-7fa3-59cf-a9fa-16411d91b373 | note | Record of conformity - Pre-pour inspection List CLA31A
004bd874-164f-56d3-926a-c7cc6361e5c6 | note | IP, HP*
b6cc567b-25b0-5848-8311-bd1a51c20c98 | note | Responsibility - FH Engineer
1f25c989-8ef6-5d1b-b3e4-43b02f8b9193 | date | Date Completed:
df776c21-f4e2-434f-b3f9-d5dd593c7376 | section | 5.0 - Pre-pour Planning and Inspections and Placement (1st Pour)
46837ed5-19b4-45c2-ac47-ce54900b0454 | checkpoint | 5.1 - Pre-pour Inspection
f2484763-c290-5dcd-b7e0-41e37190b4f0 | note | Frequency - Prior to concrete pour
798f39f2-4283-5c08-b874-cf01455fae39 | note | Acceptance Criteria - HOLD POINT
f30d8907-3313-5a1c-862e-44797b5ff120 | note | ○ Superintendent or Engineer to conduct pre-pour inspection prior to concrete pour
88a8ff74-fb25-555c-9283-f96befd4facb | note | ○ Principals representative to inspect formwork and steel fixing
6c33b81c-701e-5c3a-a0a9-d3c948e67b52 | note | Reference Documents - Specifications and Drawings
4c723954-0940-5f7f-a18d-7b4463756b82 | note | Inspection/Test Method - Verify
8977e1b5-be57-5ed2-8ce2-afe50576fcb4 | note | Record of conformity - Pre-pour inspection List CLA31A
cb49e9f2-2aa3-5ad9-aaaf-4abf42a64262 | note | HP
1ddcceb3-24c7-5223-b2e4-5f0cf3b3c46b | note | Responsibility - FH Engineer / Principals Representative
1b3f5005-c94e-5160-bb0d-8013aa90f3c8 | date | Date Completed:
7d311d22-2b93-487e-820b-3ba46aa1860a | signoff | AUTHORITY HOLDPOINT
52b0c5d7-9cdd-4285-9c5f-670134a2bc39 | checkpoint | 5.2 - Pour in-situ
1355c2a6-f9f9-5d29-b489-93888e8eca43 | note | Frequency - Each Lot
44650c60-1e99-5776-94a2-cb5254a7634e | note | Acceptance Criteria - Concrete shall be placed within 90mins from batching.
41328840-a70b-55ff-bf0b-341b947b3ec5 | note | ○ All concrete supplied for concrete structures shall be subject to project control testing in accordance with AS 1379.
dca01f05-3d92-5be9-9e60-728b60234a9a | note | Reference Documents - Specifications and drawings
1bf9746f-adf8-5761-93b8-d8719fdd0404 | note | Inspection/Test Method - Verify
52c56be2-572e-5b70-af79-2255dc77f1f4 | note | Record of conformity - This ITP signed
1d280934-b113-57c0-bd80-b4d709da2e06 | note | IP
3ccb3dcc-6f2f-51ae-8eca-696bdded5bf7 | note | Responsibility - FH Engineer
b6855962-b612-5e2f-ac62-0792e3382943 | date | Date Completed:
ef223fce-4bc6-4cf5-a6c8-34369be90716 | checkpoint | 5.3 - Concrete Testing – Compressive Tests
2b2da260-e8c3-539d-acab-06aec9adac39 | note | Frequency - Each Lot
4f0cd608-4203-5abd-9f26-02f0a1ff2d9f | note | Acceptance Criteria - Composite samples to be taken in accordance with AS 1012.1.
04135baf-7c04-5b6b-92e8-ae071c9ef777 | note | ○ 2 – 7 Day cylinder and 2 – 28 day cylinders to be taken.
ee88fb3b-9bbb-5f72-b305-de24744bcba0 | note | ○ Frequency of testing shall be one sample taken either every 50m3 or once per day, whichever yields a higher frequency.
76688140-0f49-5295-ae2d-2f4b26ad4e81 | note | Reference Documents - Drawing 00201 Note 51. AS 1012.1, AS 1012.9
81553101-d989-57dc-882d-40dca61730a0 | note | Inspection/Test Method - Verify
ab7d9920-1518-59c9-b750-46725835d9e6 | note | Record of conformity - Concrete Testers Sheet/Results
64d51404-86fd-5c9c-a650-b9561369055d | note | TP
22755a03-b0b0-56b2-89ed-0ed5440810aa | note | Responsibility - FH Engineer
4d03af45-e324-52be-933e-bc7fce181b5c | date | Date Completed:
021074c3-c80c-4451-871f-2bca8c9bb742 | checkpoint | 5.4 - Concrete Slump
546ad19e-0901-5b02-aa4f-edf49e4de4cd | note | Frequency - Each Truck
219371ab-7d4f-53b3-8b1a-0d0308f1d00e | note | Acceptance Criteria - Slump test is required for each load per day
16aae70c-4f25-5bfe-b0f2-a3f7ca368f50 | note | Reference Documents - Drawing 00201 Note 51.
7e531048-33a2-5f85-b765-96ff83b1c226 | note | Inspection/Test Method - Verify
6fddce3e-7a2a-5dc3-9000-cba71e339f98 | note | Record of conformity - Concrete Testers Sheet/Results
8f31734b-d655-504e-91c8-8000602939a5 | note | TP
6352f4df-8f5c-563b-8d0d-0d9be71467fa | note | Responsibility - FH Engineer
2430b4d7-6b9b-5ba8-a306-bdce1a03243a | date | Date Completed:
67d1361a-cc99-40bc-93a0-07a5df6d9ef7 | checkpoint | 5.5 - Finishing & Curing
c24f2ac9-d78b-573c-ad80-dc535831a7a3 | note | Frequency - Each Lot
4871d693-5351-5386-a466-101673c62ed8 | note | Acceptance Criteria - Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces.
7b3b5df0-514b-52ca-a5de-853c5b693753 | note | ○ Concrete shall be moist cured or coated by an approved curing compound for a period not less than seven days unless approved by the Superintendent.
1a36f9ee-6c0e-5e9f-bce3-ae4c15162a77 | note | Reference Documents - Specifications and drawings
1199e1ed-5672-52fd-ab9e-e3a83c54cc27 | note | Inspection/Test Method - Verify
2275fa00-f625-5236-8644-ba856b319c5b | note | Record of conformity - This Signed ITP
5072debe-3441-5fcf-ab2c-a8c8ccd3256d | note | IP
317b6eca-e9e4-5f9d-a3cf-896cf284bf6d | note | Responsibility - FH Engineer
ab931e65-f7cd-5000-9f52-9b870d0c8269 | date | Date Completed:
a01c7bf6-e18d-40e0-9f9c-8799d3c07943 | section | 6.0 - Post Pour Details and Inspections
66ef8174-3edc-4865-808b-d32e19cb1105 | checkpoint | 6.1 - Removal of Formwork
d09619f5-38aa-547b-9041-d5217c72cb4a | note | Frequency - Each Lot
797c875a-a8c6-5bd2-8910-2f4dec91f34e | note | Acceptance Criteria - Forms shall remain and be maintained firmly in place until the concrete has attained the necessary strength to support its own weight.
74e28718-0735-5b34-a704-663c6881f656 | note | Inspection/Test Method - Verify
60d87059-94eb-590f-8010-9081ab051bd5 | note | Record of conformity - This ITP signed
8ee67a73-43a1-59cd-bc9f-4d4eb5667495 | note | IP
51908bc0-feb5-589a-be5b-bbc84231a20e | note | Responsibility - FH Engineer
9691fb1e-4f6a-572e-bdc6-61cf8e71e020 | date | Date Completed:
f1f85ffe-295f-4ce1-b97c-78924a648e04 | checkpoint | 6.2 - Review of Test Results
fa19499d-e61f-5869-a329-6437768b662b | note | Frequency - Each Lot
0a88f1c5-2904-5042-9d0a-9f0f0ffce3bd | note | Acceptance Criteria - Review of 7 day and 28 day test certificates
09069dd9-2cb8-5d75-a448-e7ae0191cbaa | note | Reference Documents - Drawing 00201 Note 52.
4d98e580-684a-5a59-a056-569edcf09a5f | note | Inspection/Test Method - Verify
975aede2-7fca-52aa-bbe8-2cdbbea33708 | note | Record of conformity - Aconex Reference
6ff8f7bc-0634-5853-84d0-4f218b179c7e | note | HP
a9fcec03-e1c0-50bd-aca1-b9c08e947c32 | note | Responsibility - FH Engineer / Principals Representative
358e8acf-cf8c-576c-bbfb-8470365a75be | date | Date Completed:
aa97b35e-c297-421d-851f-e1ce1aee5c04 | signoff | AUTHORITY HOLDPOINT
2a71d77b-014b-48ea-a24e-a897a0dd164e | checkpoint | Final Inspection
a4252b10-1ad9-54bc-9f8a-2f58d5ad4032 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
a4d90686-2265-53ce-be56-6258a6b65dfc | textbox | Print Name:
0ca7aec1-4bcf-5407-8bb2-0b6eae124eaa | textbox | Position:
9671ae28-3e49-53a3-8d88-e55ec7881294 | date | Work Completed On:
abfc9a03-9285-59ab-9102-0ccf35a6c79b | date | Date: