## Resources
type | name | values | prefix | postfix | Usage Count | User Addable | Template Name
checklist-flat | FORM-001 Tool Box Talks |  |  |  |  | Yes | FORM-001 Tool Box Talks
checkpoint | Tool Box Talk
note | Project: TPCH
textbox | Tool Box conducted by:
date | Date:
textbox | Attendees:
checkpoint | Electrical tools Tagged & Tested
note | ACCEPTANCE CRITERIA: Completed Onsite
date | DATE:
checkpoint | Tools checked for wear & tear
note | ACCEPTANCE CRITERIA: Completed Onsite
date | DATE:
textbox | Items for Discussion:
textbox | Items for Review and discuss at next meeting:
signoff | Signatures
checklist | REPORT-006 Incident Investigation |  |  |  |  | Yes | REPORT-006 Incident Investigation
section | Details
checkpoint-no-status | Incident Investigation Report
note | GM Fire shall complete an Incident Investigation Report in the event of any injury involving medical attention or off site treatment or in the event of any incidents involving a near miss, property/plant damage or injury to the public or the environment.
note | The principal contractor will be informed immediately in the event of the above. Following discussions with the principal contractor, a decision will be made as to who will conduct the incident investigation. The principal contractor will be provided with a copy of the completed Incident Investigation Report.
checkpoint | Class of Incident
tickbox | Injury
tickbox | Property/Plant Damage
tickbox | Near Miss
tickbox | Environmental
tickbox | Other
textbox | If Other - Please explain
button | Reported to Princpal Contractor | Yes,No
textbox | Details:
button | Further Action Required | Report to Authorities,Other
textbox | If Other - Please explain
checkpoint | Details of Incident
date | Date of Incident
textbox | Time of Incident
button | am/pm | am,pm
textbox | Witness Name
textbox | Witness Contact
textbox | Nature of Incident
textbox | Location of Incident
textbox | Description of Incident
textbox | Details of damage to equipment/property?
checkpoint | Injured Person/s (if applicable)
textbox | Name
textbox | Address
date | Date of Birth
textbox | Occupation
textbox | Employer
textbox | Referred/transferred to
section | What factors contributed to the incident?
checkpoint | Environment:
tickbox | Noise
tickbox | Layout / design
tickbox | Lighting
tickbox | Dust / fume
tickbox | Vibration
tickbox | Slip / trip hazard
tickbox | Damaged / unstable floor
tickbox | Other
textbox | Other (if applicable):
checkpoint | Equipment/materials:
tickbox | Wrong equipment for the job
tickbox | Equipment failure
tickbox | Inadequate maintenance
tickbox | Material / equipment too heavy / awkward
tickbox | Inadequate guarding
tickbox | Inadequate training provided
tickbox | Other
textbox | Other (if applicable):
checkpoint | Work systems:
tickbox | Hazard not identified
tickbox | No / inadequate risk assessment conducted
tickbox | No / inadequate safe work procedure
tickbox | No / inadequate controls implemented
tickbox | Hazard not reported
tickbox | Inadequate training / supervision
tickbox | Other
textbox | Other (if applicable):
checkpoint | People:
tickbox | Procedure not followed / no procedure exists
tickbox | Drugs / alcohol
tickbox | Fatigue
tickbox | Time / production pressures
tickbox | Change of routine
tickbox | Distraction / personal issues / stress
tickbox | Lack of communication
tickbox | Other
textbox | Other (if applicable):
section | Corrective actions:
checkpoint | Contributing factor
textbox | (from above list)
textbox | What are we going to do to fix the problem?
textbox | Who
textbox | When
date | Completion date
checkpoint | Completed By
textbox | Name
textbox | Position
date | Date
signoff | Signature
checklist | ITPS-003 Fire Alarm and EWIS Installation | itp |  |  |  | Yes | ITPS-003 Fire Alarm and EWIS Installation
section | Details
checkpoint | 1 - CABLE TYPE & SIZE TO DESIGN CRITERIA - AS1670.1-2018 Have a cross sectional area of no less than 0.75mm2 AS3000
button | C5.4.0 Wiring | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - CABLE HEIGHTS & LOCATION ADEQUATE FOR FIT OFF - AS1670.1-2018: internal domestic and office situations where cabling is mounted on walls at heights above 1.5m AS3000
button | C5.2.5 Control Loops | Pass
button | C5.4.0 Wiring | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - CABLE FIXED TO SPECIFIED REQUIREMENTS - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
button | C5.2.5 Control Loops | Pass
button | C5.4.0 Wiring | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - DETECTOR BASES FITTED OFF - AS1670, AS1668: Detectors that can be contaminated by construction works should not be fitted unless suitably protected until the construction works are completed.
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - DETECTOR HEADS INSTALLED & TYPE CHECKED - Detector type to appropriate location. Installed to Latest RCP
button | C5.6.0 Sensors/Detectors | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6 - MANUAL CALL POINTS INSTALLED - AS1670.1-2018: An MCP shall be mounted between 750 mm and 1100 mm above floor level and a clear space of 600 mm shall be provided in a semi-circle in front of the MCP.
button | C5.10.0 Manual Call Points | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - STROBES FITTED OFF - AS1670.1-2018: Check with Design Drawing and/or RCP
button | C5.2.2 Set Points | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 8 - SPEAKERS INSTALLED - AS1670: Check with Design Drawing and/or RCP
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 9 - WARDEN INTERCOM PHONES - AS1670.4-2018: The WIP handset shall be mounted at a height of not less than 1200 mm and not more than 1800 mm above finished floor level.
button | C6.2.8 Warden Intercom Phones | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 10 - SPRINKLER INTERFACES FITTED OFF - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
button | C5.2.2 Set Points | Pass
button | C5.8.0 Modules Input/Output | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 11 - FIRE RATING TO PENETRATIONS CORRECT - AS4072.1-2018: Ensure correct Test Report is used – refer to FRL requirements on wall selection
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 12 - LABELS AFFIXED - AS4072.1-2018: The label should be positioned close to the service penetration
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 13 - ACOUSTIC PENETRATION SEALING - AS4072.1-2018: Sound proofing sealant may be used depending on dB Level requirements
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 14 - CABLE TRAY BRACKET SPACING - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 15 - INSTALLED IN ACCORDANCE APPROVED WORKING DRAWING AND LATEST ARCHITECTURAL - In House QA, Up to Date drawing register, Drawings updated with MPX approved references
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | ITPS-014 Diesel Fire Pumpset Installation and Commissioning | itp |  |  |  | Yes | ITPS-014 Diesel Fire Pumpset Installation and Commissioning
section | Details
checkpoint | 1 - Check location of pumpset - in a position that is protected from falling debris, and vehicular and mechanical damage - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - Check clearance of pumpsets - For ongoing inspection and testing, a clearance of not less than 1.0 m shall be provided around the perimeter of a complete pump assembly; - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - Check clearence of pumpset - for multiple pumpset installations, a clearance of not less than 600 mm between each of the installed pumps shall be provided - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - Check elevations - Multiple pumpsets shall be installed with the centre-line of all suction pipes at the same elevation. If the pumps are to be installed at different elevations, the elevated pump shall be installed on a properly constructed mezzanine floor with head clearance of minimum 2.1 m to the underside on both levels - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - Check Plinth - Pumpset baseplates shall be mounted on concrete plinths with a height not less than 150 mm above the floor. For fixing purposes, the concrete plinth shall extend 150 mm past the edge of the baseplate on all four sides. - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
section | PRE COMMISSIONING CHECK LIST
checkpoint | 6a - Check the cooling supply system - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6b - Check engine fuel supply - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6c - Check the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6d - Check the direction of rotation. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6e - Check – Engine lubricating oil is at the correct level. Check – the battery electrolyte level and the battery leads and connections. Check – exhaust system is intact - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6f - Ensure – pump is primed and that lines are clear, valves correctly set (open, closed, or adjusted to required pressure), and that water is available. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6g - Isolate – all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
section | PUMP COMMISSIONING CHECKLIST
checkpoint | 7a - Record – For automatic starting pumpsets, record the pressure in the system at which the pump starts automatically. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7b - Record – Engine Oil Pressure - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7c - Check – Coolant Flow is correct - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7d - Check – That the fan is rotating and all fan belts are intact - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7e - Record – pump shut-off pressure. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7f - Isolate – the flow meter, partially open the test valve, and flush to remove any debris or foreign matter; open any meter-isolating valves, open the test valve, and record pump delivery gauge pressure when approximately full load flow is indicated on the flow meter. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 8 - Run the pump for 30 min at maximum flow and record the following: (i) Suction and delivery pressures. (ii) Engine running temperature, which shall be within the engine manufacturer’s recommended limits. (iii) Engine oil pressure, which shall be within the engine manufacturer’s limits. (iv) Air temperature at pumpset. (v) Discharge pressure at three other flow rates between shut-off and maximum flow, one of which shall be at the duty flow rate. (vi) Check that the requirements of Clause 9.3.6.2 are complied with by holding the engine shutdown mechanism closed and simulating an automatic start signal until the engine has attempted to start for five automatic starting cycles. On the sixth starting cycle, return the engine shutdown mechanism to its normal starting position and check if the engine starts immediately. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 8a - During the operations in Item (h)— (A) periodically check temperature of the bearings and stuffing box leakage and note any abnormality; (B) check that all alarms and indicators, both visual and aural, have been activated; and (C) check that alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped. If the pump failed to start alarms that are fitted on the pump fire pump controller and at the remote station, check that these alarms operate both aurally and visually. (j) Shut down and restore starting mechanism to stand-by status. (k) Restore power supply to the electric pumps and check correct status of indicators. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | CHECK-002 Site Inspection |  |  |  |  | Yes | CHECK-002 Site Inspection
section | 1. Administrative, training and risk management requirements
checkpoint | 1.1 - So far as reasonably practicable, all workers carrying out construction work on the project have been made aware of the content of the WHS management plan, including any updates, and their right to inspect the plan.
checkpoint | 1.2 - All workers carrying out construction work have received the general construction induction training.
checkpoint | 1.3 - Workers have been informed of the site-specific health and safety rules.
checkpoint | 1.4 - Suitable and adequate information, training, and instruction has been provided to workers in relation to work they are carrying out.
checkpoint | 1.5 - Personal protective equipment (PPE) is being worn in accordance with the projects requirements.
section | 2. Safe work method statements
checkpoint | 2.1 - A safe work method statement (SWMS) has been prepared for each high risk construction work activity that is underway or about to commence.
checkpoint | 2.2 - Workers have reviewed and signed off on the relevant SWMS
checkpoint | 2.3 - High risk construction work activities are being carried out in accordance with the relevant SWMS.
section | 3. The work environment
checkpoint | 3.1 - The work environment has been maintained such that it is clean and in a safe condition.
checkpoint | 3.2 - Work areas are clearly identified and separated as necessary so that work can be undertaken safely.
checkpoint | 3.3 - Lighting at the workplace is sufficient to allow:
note | ○ Each worker to carry out work without risk to health and safety.
note | ○ People to move within the workplace without risk to health and safety.
note | ○ Safe evacuation in an emergency.
checkpoint | 3.4 - The workplace has sufficient ventilation to enable workers to carry out work without risk to health and safety.
checkpoint | 3.5 - The entries, exits, and access ways in the workplace are kept clean and clear of materials and waste.
checkpoint | 3.6 - A safe system has been implemented for the collection, storage, and disposal of excess or waste materials.
checkpoint | 3.7 - Sufficient area has been allocated to safely store materials or plant for the construction work.
checkpoint | 3.8 - Protruding objects that are a hazard have been made safe (e.g. exposed nails, vertical reinforcing steel).
checkpoint | 3.9 - Adequate facilities have been provided for workers, including toilets, drinking water, washing facilities, and eating facilities.
checkpoint | 3.10 - First aid equipment has been provided for the workplace and is accessible to each worker.
section | 4. Confined spaces
checkpoint | 4.1 - For each hazard associated with a confined space, a competent person completed ASSES-05 Confined Spaces Risk.
checkpoint | 4.2 - Prior to commencing the works, FORM-003 Entry Permit Confined Spaces has been completed and approved.
checkpoint | 4.3 - Appropriate signage has been erected for all confined spaces.
checkpoint | 4.4 - First aid procedures and rescue procedures to be followed in accordance with POLICY-006 Confined Spaces Rescue in the event of an emergency in a confined space have been developed and practiced to ensure they are efficient and effective.
checkpoint | 4.5 - Workers required to work in or around a confined space have been provided with information, instruction, and training in relation to the:
note | ○ Nature of all hazards relating to a confined space
note | ○ Need for, and the appropriate use of, control measures associated with those hazards
note | ○ Selection, fit, use, wearing, testing, storage, and maintenance of any personal protective equipment
note | ○ Contents of any confined space entry permits that may be issued
note | ○ Emergency procedures.
section | 5. Working at heights
checkpoint | 5.1 - A SWMS is available for all high risk construction work that involves a risk of a person falling more than 2m that has commenced or is about to commence.
checkpoint | 5.2 - Where a risk of fall of less than 2m exists:
note | ○ Each hazard that may result in a fall or cause death or injury if a person were to fall has been identified
note | ○ The risk of death or injury that may result because of the hazard has been assessed
note | ○ Any control measures necessary to prevent, or minimise the level of, exposure to the risk is used.
checkpoint | 5.3 - Where a risk of fall of at least 2m exists, control measures have been used which:
note | ○ Prevent a person falling any distance
note | ○ If prevention is not practicable:
note | – arrest a person’s fall
note | – prevent or minimise the risk of death or injury to a person when the fall is arrested.
checkpoint | 5.4 - Ladders are not used to support a weight greater than that for which they have been designed.
checkpoint | 5.5 - Ladders are used where the:
note | ○ Bottom of the ladder is on a stable surface
note | ○ Rungs of the ladder are approximately level.
checkpoint | 5.6 - Scaffolding has been erected by appropriately licensed workers.
checkpoint | 5.7 - Scaffolding is or has been erected and/or dismantled so as to eliminate or minimise the risk of falling at least 2m to people carrying out the work, in accordance with the regulations
checkpoint | 5.8 - Safe access to and egress from scaffold has been provided during erection, use, and dismantling.
checkpoint | 5.9 - Written confirmation from a competent person stating that the construction of a particular scaffold has been completed, has been obtained prior to the use of that particular scaffold.
checkpoint | 5.10 - REGISTER-007 Plant and Equipment is up to date and includes all mobile plant in use.
checkpoint | 5.11 - CHECK-004 Pre-Start Plant and Equipment has been completed for all mobile plant in use on delivery to site.
checkpoint | 5.12 - CHECK-005 Regular Plant and Equipment has been completed for all mobile plant prior to commencing operation of the plant that day.
checkpoint | 5.13 - Mobile plant operators hold the appropriate high risk work licence.
checkpoint | 5.14 - Where there is a possibility of powered mobile plant colliding with pedestrians or other powered mobile plant, a warning device has been fitted.
section | 6. Electrical
checkpoint | 6.1 - Electrical leads are arranged to avoid damage.
checkpoint | 6.2 - Electrical equipment has been inspected, testing, and tagged in accordance with AS/NZS 3012 Electrical installations – Construction and demolition sites.
section | 7. Hazardous substances and dangerous goods
checkpoint | 7.1 - All hazardous chemicals that are used, handled, or stored at the workplace are correctly labelled.
checkpoint | 7.2 - A safety data sheet (SDS) exists and is available for inspection for each hazardous chemical used, handled, or stored at the workplace.
checkpoint | 7.3 - A register of hazardous chemicals used, handled, or stored at the workplace has been prepared in accordance with the regulations and is kept at the workplace.
checkpoint | 7.4 - A spill containment system has been implemented in each part of the workplace where there is a risk from a spill or leak of a hazardous chemical.
section | 8. Corrective actions
checkpoint | Corrective actions
section | 9. Inspection sign off
checkpoint | This workplace inspection checklist has been completed by;
textbox | Name:
date | Date:
signoff | Signature
checkpoint | I hereby certify that all corrective actions as identified in the above checklist have been completed;
textbox | Name:
date | Date:
signoff | Signature
checklist | ITPS-012 In Slab Conduit Installation | itp |  |  |  | Yes | ITPS-012 In Slab Conduit Installation
section | Details
checkpoint | 1 - CHECK CONDUITS ARE CORRECT TYPE, SIZE AND QUANTITY TO CRITERIA - In-house QA
textbox | Drawing Reference Number:
date | DATE:
checkpoint | 2 - CHECK CONDUIT ROUTE IS AS SPECIFIED IN LAYOUT/ DESIGN CRITERIA - Shop drawings (certified by an RPEQ engineer) are to be provided for each and every item required within 1170.4 Structural design actions – Earthquake actions in Australia.
textbox | Drawing Reference Number:
date | DATE:
checkpoint | 3 - INSTALLATION, CONDUIT IS JOINED CORRECTLY - Installation is in compliance with AS 1170.4 Structural design actions – Earthquake actions in Australia.
textbox | Drawing Reference Number:
date | DATE:
checkpoint | 4 - CONDUIT IS TIED IN
date | DATE:
checkpoint | 5 - CONCRETE COVER IS IN PLACE - General Technical Requirements – Services Ripley Sub-Acute Facility (RSAF) 2.2.3 - 9. All Fire services penetrations post concrete pours are to be immediately sealed with sheet metal cover plates (mastic or similar) to prevent water ingress. Plates to be fixed by use of nylon anchors or similar. Plates to remain in place and maintained until directed by Hutchinson Builders to remove.
textbox | Drawing Reference Number:
textbox | Construction Issued Drawings Number:
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | ITPS-015 GM Tank Installation | itp |  |  |  | Yes | ITPS-015 GM Tank Installation
section | Details
checkpoint | 1 - Confirm – Structural Elements as per AS2304 – Section 3 - AS2304 – Water storage tanks
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - Confirm - Correct Installation drawing, onsite. - AS2304 – Water storage tanks
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - Confirm – Ladder selection and orientation to submitted design drawings, Confirm – Nozzle selection as per submitted design drawings - AS2304 – Water storage tanks
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - Confirm – Position of tanks with principle contractor onsite - AS2304 – Water storage tanks
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - Confirm – Competencies and Authority to work of subcontractor - AS2304 – Water storage tanks
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6a - Commissioning – Structural inspection prior to filling - AS2304 – Water storage tanks
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6b - Commissioning – Inspect all ladders for conformance and clearances and position of tank accessories - AS2304 – Water storage tanks
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6c - Commissioning – Hydrostatic inspection after tank is filled to maximum capacity - AS2304 – Water storage tanks
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6d - Commissioning – Record any defects - AS2304 – Water storage tanks
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6e - Commissioning – Submit certificates and warranty periods - AS2304 – Water storage tanks
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | ITPS-013 Electric Fire Pumpset Installation and Commissioning | itp |  |  |  | Yes | ITPS-013 Electric Fire Pumpset Installation and Commissioning
section | Details
checkpoint | 1 - Check location of pumpset - in a position that is protected from falling debris, and vehicular and mechanical damage - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - Check clearence of pumpset - For ongoing inspection and testing, a clearance of not less than 1.0 m shall be provided around the perimeter of a complete pump assembly; - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - Check clearence of pumpset - for multiple pumpset installations, a clearance of not less than 600 mm between each of the installed pumps shall be provided - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - Check elevations - Multiple pumpsets shall be installed with the centre-line of all suction pipes at the same elevation. If the pumps are to be installed at different elevations, the elevated pump shall be installed on a properly constructed mezzanine floor with head clearance of minimum 2.1 m to the underside on both levels - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - Check Plinth - Pumpset baseplates shall be mounted on concrete plinths with a height not less than 150 mm above the floor. For fixing purposes, the concrete plinth shall extend 150 mm past the edge of the baseplate on all four sides. - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
section | Electric Pumpsets
checkpoint | 6a - Check the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance. - AS2941.1-2013 – Section 11 and 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6b - Check the direction of rotation - AS2941.1-2013 – Section 11 and 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6c - Ensure that the delivery from the pump under test is the only supply to the measuring device and that all flow from the pump passes through the device. - AS2941.1-2013 – Section 11 and 12
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6d - Ensure that the pump is primed and that lines are clear, valves correctly set (open, closed or adjusted to required pressure), and that water is available. - AS2941.1-2013 – Section 11 and 12
button | Hold Point Required: | Yes
button | W5.4 System Filling and Venting | Pass
button | W5.4.1 Pressure Testing | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
signoff | HOLD POINT
checkpoint | 6e - Isolate all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and compression-ignition engine driven pumps - AS2941.1-2013 – Section 11 Installation
button | W5.2 State of the System | Pass
button | W5.4 System Filling and Venting | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7a - The following shall be reported – Pump plate details / photo - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7b - Record - the pressure in the system at which the pump starts automatically. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7c - Record - Pump shut-off pressure on delivery gauge - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7d - Record - Motor current at shut-off pressure. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7e - Record - Delivery pressure at maximum flow - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7f - Record - Pressure on discharge gauge and motor current at three other flow rates between shutoff and maximum flow, one of which should be at the duty flow rate - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7g - Check – (i) periodically check the temperature of the bearings and stuffing box leakage and note any abnormality; (ii) check that all alarms and indicators, both visual and aural, have been activated; and (iii) check that alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 8 - Whether the electric pumpset, together with its associated control gear and ancillary equipment, functioned correctly. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 9 - Whether the pumpset satisfies the intended performance conditions (e.g. flow rate and head). - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 10 - Whether there is operational abnormality. - AS2941.1-2013 – Section 12
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | ITPS-009 Sprinkler System Commissioning | itp |  |  |  | Yes | ITPS-009 Sprinkler System Commissioning
section | Details
checkpoint | 1 - CHECK SPRINKLER HEADS ARE INSTALLED IN AN ENVIRONMENT IN WHICH THEY ARE SUITED - AS2118.1-2017 – Section 2.2 – heads installed to correct classification and spacing
button | W5.2 State of the System | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - CHECK HYDRANTS ARE INSTALLED TO CODE AND HAVE REQUIRED CLEARENCES - AS2419.1-2005 – Section 3.2 – Clearances differ when related to internal or external hydrants, ensure correct standards are implemented
button | W5.2 State of the System | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - AIR TEST INSTALLATION BEFORE WATER FILL - AS2118.1-2017 – Section 7.9.4 – hold 300 kPa for 30 minutes without a 10% loss.
button | Hold Point Required: | Yes
button | W5.4 System Filling and Venting | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
signoff | HOLD POINT
checkpoint | 4 - STATIC TEST INSTALLATION WITH WATER TO 1600KPA - AS2118.1-2017 – Section 7 (7.9.3) – system tested to 1.6MPa and holds pressure for 2 hours
button | Hold Point Required: | Yes
button | W5.4 System Filling and Venting | Pass
button | W5.4.1 Pressure Testing | Pass
button | W5.5.2 Flushing Procedure | Pass
button | W5.7 Static Completion Records | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - CHECK & TEST WATER SUPPLY CAPACITY TO MEET SYSTEM DEMAND - AS2118.1-2017 - section 4.2.2.1 – capable of supplying the flow and pressure requirements of the sprinkler system.
button | W7.2 Flow Rate Measurement Tolerances | Pass
button | W7.5 Preliminary Flow Rate Check | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6 - CHECK OPERATION OF PRESSURE SWITCHES TO DBS - AS2118.1-2017 - Appendix H4 – Test via 15mm test valve and record time taken to operate. Confirm with ASE monitoring service that alarm was received.
button | W5.6 System Checks | Pass
button | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6 - CHECK OPERATION OF PRESSURE SWITCHES FOR PUMP START - AS2118.1-2017 – Appendix H5.4 – P/Sw to be tested via dropping system pressure via test valve or remote test point.
button | W5.6 System Checks | Pass
button | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - CONDUCT 100% TESTING OF PRESSURE SWITCH, FLOW SWITCH & VALVE MONITOR - AS2118.1-2017 Appendix H6 – equipment to be tested to procedure set out in standard and in conjunction with Fire alarm workers.
button | W5.6 System Checks | Pass
button | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 8 - CHECK PUMP PRESSURE AND FLOW REQUIREMENTS - AS2118.1-2017 - Section 14.9 – shall be capable of satisfying the flow and pressure requirements of the design +50kPa.
button | W7.2 Flow Rate Measurement Tolerances | Pass
button | W7.5 Preliminary Flow Rate Check | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 9 - WITNESS TEST HOLD POINTS - PIPE TESTING PROCEDURE
button | Hold Point Required: | Yes
button | W5.7 Static Completion Records | Pass
textbox | Test performed by: Please print name and company of all involved parties
textbox | Witnessed by: Please print name and company of all involved parties
date | DATE:
signoff | HOLD POINT
checkpoint | 10 - HYDROSTATIC SPRINKLER PIPE TEST - AS2118.1-2017 Appendix H & Section 7.9.3; All new installations, trunk mains and water supply connections shall be capable of withstanding for a period of 2 h, without loss of pressure, a hydrostatic test pressure of 1600 kPa.
button | Hold Point Required: | Yes
button | W5.7 Static Completion Records | Pass
note | ○ As per GM Fire ITPS-013 Sprinkler Pipe Testing.
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
signoff | HOLD POINT
checkpoint | 11 - COMPLETE FORM 71 SPRINKLERS - NCC 2019, AS2118
button | W7.10 Commissioning Certification | Pass
textbox | Certificate: Please print name and company of all involved parties
date | DATE:
checkpoint | 12 - COMPLETE FORM 71 HYDRANTS - NCC 2019, AS2419
button | W7.10 Commissioning Certification | Pass
textbox | Certificate: Please print name and company of all involved parties
date | DATE:
checkpoint | 13 - OPERATORS MANUAL, INSTALLERS STATEMENT, AS- INSTALLED DRAWINGS, LOGBOOK AVAILABLE TO SPECIFICATION REQUIREMENTS - In House QA
textbox | Certificate: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | ITPS-002 Purchasing and Procurement | itp |  |  |  | Yes | ITPS-002 Purchasing and Procurement
section | Details
checkpoint | 1 - EQUIPMENT PURCHASES TO SPECIFICATION - In House QA Samples approved by PC/ CL
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - CHECK SPECIFICATION SAMPLES HAVE BEEN APPROVED. - Approval by PC/ CL
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - MATERIALS APPROVED FOR INSTALLATION - CL Specification
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - PURCHASE ORDERS SPECIFIC AND PRICED - Orders from approved suppliers; In House QA – Equipment ordered > Equipment Supplied; POs referenced and invoices approved
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - FIRE PANEL DELIVERED – AS ORDERED - In House QA Reference Design Invoice from Supplier
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6 - FIRE PANEL Q.A. CERTIFIED - In House QA To system Design requirements Supplier QA referenced
textbox | Certificate: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - SMOKE DETECTORS DELIVERED AS ORDERED - Samples approved by PC/ CL. Quantities as required. Invoices checked.
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 8 - FABRICATED PIPE & VALVES DELIVERED AS ORDERED - SPRINKLERS: AS2118.1-2017 – Section 7.1; All pipes, valves and fittings shall be supplied new. HYDRANTS: AS2419.2-2005 – Section 8.1.1; Pipe, valve and fittings provided shall be new and comply with fitting specification. In House QA.
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 9 - SPRINKLER HEADS DELIVERED AS ORDERED - AS2118.1-2017 – Section 9 & 10; Shall be new and meet the demands of the system they are installed on (Light/Ordinary Hazard) - In House QA
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist-flat | 010SAF_08 SWMS |  |  |  |  | Yes | 010SAF_08 SWMS
checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
signoff | By signing I confirm I have completed the Principal Contractors induction.
checkpoint | 2. ALL STAFF
note | 003G Using Platform Ladders
note | 004G Inhalation of Respirable Crystalline Silica
note | 005G Working at Heights
note | 006G Working at Heights Rescue Plan
signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
checkpoint | 3. WET FIRE TECHNICIANS
note | 019T Pressure Testing of Pipework
note | 020T Sprinkler System and Associated Pump Test
note | 021T Hydrostatic and Flow Testing of Pipework
note | 022T Fire Rating
note | 023T Fire Alarm and Emergency Warning Systems Testing
note | 024T Commissioning and Testing of Hydrant System and Booster Area
signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
note | 008I Removal of Existing Fire Alarm Systems and Devices
note | 009I Removal of Pipework Fittings
note | 010I Fire Alarm and Warning System Rough-in
note | 011I Fire Alarm and Warning System Fit-off and Installation
note | 012I Installation of Fire Alarm and Warning System Cabling
note | 013I Installation of Pipework and Fittings
note | 014I Installation of Fire Control Panel & Emergency Warning Systems
signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
checklist | ITPS-004 Fire Alarm and EWIS Commissioning | itp |  |  |  | Yes | ITPS-004 Fire Alarm and EWIS Commissioning
section | Details
checkpoint | 1 - CONDUCT 100% TESTING OF ZONING - AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCIE
button | GMF-COMDRY-001 - Fire Detection Zone Commissioning | Pass
button | C5.2.6 Sequencing | Pass
button | C5.2.9 Alarm Functions | Pass
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - CONDUCT 100% TESTING OF SMOKE AND THERMALS - AS1670.1-2018: Aspirating detectors measure and record the transport time (TT) from the most disadvantaged sampling point for each sampling pipe or branch.
button | GMF-COMDRY-002 - Fire Detection and Alarms (Smokes, Thermals, Duct Probes) | Pass
button | C5.6.0 Sensors/Detectors | Pass
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - CONDUCT 100% TESTING OF MCPS - AS1670.1-2018: (i) the correct operation of each manual call point; (ii) that the activation of manual call points on the same circuit as other actuating devices does not cause existing detector alarm indications to be extinguished; and (iii) that manual call points are not subjected to alarm dependency.
button | GMF-COMDRY-003 - Manual Call Points | Pass
button | C5.10.0 Manual Call Points | Pass
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - CONDUCT 100% TESTING OF DOOR DEVICES - AS1670.1-2018: Check the operation of each device/door release once installed
button | GMF-COMDRY-004 - M.D.H / Auto Door Commissioning | Pass
button | C5.8.0 Modules Input/Output | Pass
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - CONDUCT 100% TESTING CASCADE AND EWIS ZONING - AS1670.4-2018: Audible signals, visual and tactile signals to be checked – automatic operation.
button | GMF-COMDRY-005 - Emergency Warning Cascade and Matrix | Pass
button | C6.2.5 Cascade Sequence | Pass
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6 - CONDUCT 100% TESTING SPEAKERS AND ZONES - AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCIE
button | C5.6.0 Sensors/Detectors | Pass
button | GMF-COMDRY-006 - Emergency Warning Commissioning | Pass
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - CONDUCT 100% TESTING WARDEN INTERCOM PHONES - AS1670.4-2018: The WIP audible call signal shall have a SPL of not less than 80 dB(A) when measured at a distance of 1 m from the WIP. The SPL of the WIP handset audible call signal shall also be met when the WIP handset is mounted within a security enclosure.
button | C6.2.8 Warden Intercom Phones | Pass
button | GMF-COMDRY-007 - Warden Intercom Point | Pass
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 8 - CONDUCT FIRE MATRIX TESTING - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix
button | C5.2.2 Set Points | Pass
button | GMF-COMDRY-005 - Emergency Warning Cascade and Matrix | Pass
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 9 - CONDUCT FIRE FAN CONTROL PANEL AND BRIGADE INTERFACE TESTING - AS1670.1-2018: The FFCP shall be incorporated into or located adjacent to the FBP and constructed in accordance with the FDCIE requirements in Clause 2.1
button | C6.6.0 Brigade Interface – FFCP | Pass
button | GMF-COMDRY-001 Fire Detection Zone Commissioning | Pass
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 11 - CONDUCT FULL FUCNTIONAL FIRE TESTING AND WITNESSING - AS1670.4-2018 – 100% test of installed devices, Interface testing to Trades: Mech Shutdowns, Security trips
button | C7.0.0 Full Function Fire Test – Witnessing | Pass
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
textbox | Witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 12 - SPRINKLER INTERFACES FITTED OFF - AS1670.1-2015: Systems interface testing Prior to any interface testing check that all systems listed in the system interface schedule are complete and operable. This will involve checking that all systems interfaces to the FDAS
button | C5.2.2 Set Points | Pass
button | C5.8.0 Modules Input/Output | Pass
button | GMF-COMWET-001 - Sprinkler Zone Commissioning | Pass
button | GMF-COMWET-002 - Flow Switch, Valve, Pump and Tank Indication | Pass
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 13 - OPERATORS MANUAL, INSTALLERS STATEMENTS, AS- INSTALLED DRAWINGS, LOGBOOK AVAILABLE TO SPECIFICATION REQUIREMENTS - In House QA, Correct documentation, Referenced and submitted to PC
textbox | Drawing Reference Number:
textbox | Test performed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | ITPS-008 Sprinkler Installation | itp |  |  |  | Yes | ITPS-008 Sprinkler Installation
section | Details
checkpoint | 1 - PIPING, DRAWING & CUTTING SHEETS CROSS CHECKED - IN HOUSE
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - UNDERGROUND PIPING TO PUMP HOUSE FROM BOOSTER TO APPROVED LAYOUT & DETAIL - IN HOUSE QA
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - PIPING & SIZE TO DESIGN CRITERIA - SPRINKLERS: AS2118.1-2017 – Section 7.1; All pipes shall be supplied new and conform to the standards and relevant requirements. Latest Design Drawings
button | W5.5 Pre – Commissioning | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - MANUFACTURED FITTINGS TO DESIGN DETAILS - AS2118-2017 – Section 7.1; All fittings shall be supplied new and conform to the standards and relevant requirements.
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - PIPEWORK SUPPORTED BY SEISMIC BRACING - AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
textbox | Drawing Reference Number:
note | ○ Construction Issued Drawings Number:
textbox | Approval by: Please print name and company of all involved parties
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6 - PIPING FIXED TO SPECIFIED REQUIREMENTS - AS2118.1-2017 - Section 7.8; Sprinkler supports shall be of the correct type installed in the correct locations and meet required load ratings for the pipe they are supporting.
button | W5.5 Pre – Commissioning | Pass
button | W5.6 System Checks | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - VALVES TO DESIGN DETAILS - AS2118.1-2017 – Section 8.2 – each installation shall have a main stop valve fitted, have clear identification and be shown on the Block plan.
button | W5.5 Pre – Commissioning | Pass
button | W5.6 System Checks | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 8 - SPRINKLER INTERFACES FITTED OFF - AS2118.1-2017 – Appendix H – check to ensure alarm interfaces are fit off and tested prior to sign off
button | W5.5 Pre – Commissioning | Pass
button | W5.6 System Checks | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 9 - WITNESS DRY FIRE TESTING OF VALVE SETS AND MONITORING EQUIPMENT - AS1670.1-2018, AS2118.1-2017 – Appendix H6 – system tested in accordance to the standard prior to witness testing with client or QFES.
button | W8.2.2 Witness Requirements | Pass
textbox | Witnessed by: Please print name and company of all involved parties
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 10 - SPRINKLER HEADS FITTED OFF - AS2118.1-2017 – Section 5 Approved and up to date Reflected Ceiling Plan (RCP)
button | W5.6 System Checks | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 11 - OMISSION OF SPRINKLERS - Fire Engineers Report (FER)
button | W5.6 System Checks | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 12 - SPARE SPRINKLERS & KEY INSTALLED & TYPE CHECKED - AS2118.1-2017 – Section 6.7 – spare sprinklers of each type used in the installation shall be provided and located in a spares box.
button | W5.6 System Checks | Pass
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 13a - LABELS & BLOCK PLAN INSTALLED - AS2118.1-2017 – Section 8.3 – Block plans shall be provided, be of permanent design, water and fade resistant
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 13a - CONTROL ASSEMBLIES - AS2118.1-2017 - Section 8.1 – shall be located in a secure location and readily accessible to the fire brigade.
button | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
textbox | Performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 13b - LABELING OF CONTROL EQUIPMENT - AS2118.1-2017 - Section 3 (3.3.4) – shall be permanently affixed fade- resistant and water resistant
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 14 - FIRE RATING TO PENETRATIONS CORRECT AND LABELS AFFIXED - BCA
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 15 - ACOUSTIC PENETRATION SEALED - AS4072
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist-flat | CHECK-006 Daily Prestart |  |  |  |  | Yes | CHECK-006 Daily Prestart
checkpoint | Details:
date | DATE:
textbox | TIME:
textbox | SUPERVISOR NAME:
checkpoint | Issues
button | Are there any issues arriving from yesterday? If YES, detail in comments below. | Yes,No
note | NOTE: If this requires a change to the SWMS then please ensure this is captured and relevant personnel inducted.
checkpoint | PLANNED WORK ACTIVITIES / TASKS
textbox | ACTIVITY / TASK |  | Specify the daily work task/s:
note | SWMS that relate to today's task/s
tickbox | 001 – Working with elevated work platforms
tickbox | 002 – Wiring Rough In Minor
tickbox | 003 – Fit off fire alarm system
tickbox | 006 – Installation of pipe and fittings
tickbox | 007 – Manual handling
tickbox | 009 – Pressure testing of pipework
tickbox | 051 – Using platform ladders
tickbox | 060 – Inhalation of Respirable Crystalline Silica
tickbox | 061 – Working in Major Area of Concern
tickbox | Task-specific Safe Work Procedure
checkpoint | Is a SWMS in place for ALL high-risk construction work and work procedures in place for all other works?
note | IF NO, STOP AND DEVELOP!
checkpoint | Are you subcontracting out any works today and will you be interacting with other trades?
textbox | If YES, please list
checkpoint | Permits
button | Isolation Permit | Yes, No
button | Have conditions changed since permit approval? If YES, please note changes below. | Yes, No
button | Hot Works | Yes,No
button | Permit to cut or drill | Yes,No
button | MAC Permit | Yes,No
note | Please list Permit numbers with description below, and upload photo/ attach file if available.
checkpoint | Environmental Risk
note | What controls are in place to manage environmental risk on site, specific for today; e.g. Wash out areas, maintenance of sediment fences and drains, monitoring of dust?
tickbox | Clean up the general area
tickbox | M-Class vacuum
tickbox | Fit test and appropriate fit mask
tickbox | Spill kit onsite
tickbox | Other - detail below
checkpoint | Checklist for Activities
number | Number of people in your Work Group
button | Daily Risk Assessment Completed | Yes,No
button | Qualifications/training of staff adequate for work activities | Yes,No
button | Plant and Equipment on/off site | Yes,No
button | Equipment safe to use | Yes,No
button | Work area inspected and safe for staff to enter and work in today | Yes,No
button | Appropriate and adequate PPE supplied to work teams (SWMS/SDS) | Yes,No
button | Weather conditions for work to be conducted assessed | Yes,No
number | How many workers have been allocated for today’s clean up?
button | Pre-start communicated to all work teams including all trades & subcontractors | Yes,No
checkpoint | Builders Briefing Notes
note | Attach a photo of the builders brief
checkpoint | General Notes
checkpoint | Signoff
note | Remember to clock in and out of your shift.
signoff | By signing I confirm I have have partipicated in this Prestart and I understand my roles and responsibilities today.
checklist | ITPS-007 Sprinkler and Hydrant Design | itp |  |  |  | Yes | ITPS-007 Sprinkler and Hydrant Design
section | Details
checkpoint | 1 - REVIEW CLIENTS DRAWING REGISTER
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - REVIEW TENDER/CONSTRUCTION DRAWINGS
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - REVIEW SPECIFICATION
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - PREPARE SHOP DRAWINGS/LAYOUTS TO LATEST ARCHITECTURAL DRAWINGS
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - DESIGNING PIPING LAYOUT - SPRINKLERS: AS2118.1-2017 – Section 2; All new sprinkler systems shall be hydraulically designed in accordance with the requirements of Section 14 (hydraulic calculation of Sprinkler Systems). HYDRANTS: AS2419.1-2005 – Section 2; Fire Hydrant systems shall be compatible with the equipment and procedures employed by the attending Fire Brigade
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6 - PREPARE SPRINKLER VALVE DRAWINGS - AS2118.1-2017 – Section 8.2.3(b); All sprinkler stop valves shall be clearly labelled on this Sprinkler Block Plan
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - SUBMIT SHOP DRAWINGS FOR APPROVAL - Clients Specifications In House QA
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 8 - REVIEW RETURNED SHOP DRAWINGS - In House QA
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 9 - DISTRIBUTE "FOR CONSTRUCTION" DRAWINGS - Per clients Specification
textbox | General: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | CHECK-003 Site Establishment |  |  |  |  | Yes | CHECK-003 Site Establishment
section | Details
checkpoint-no-status | Details:
textbox | Project Number:
textbox | Project Name:
textbox | Project Manager (PM):
textbox | Project Address:
textbox | QA Platforms used:
checkpoint | In house, FER & Specification Numbers
date | DATE:
checkpoint | Site visit & survey
date | DATE:
checkpoint | Review Drawings & print for site
date | DATE:
checkpoint | Review Fire Engineering Report
date | DATE:
checkpoint | Allocate labour
date | DATE:
checkpoint | Review Principle Contractors (PC) proposed baseline program
date | DATE:
checkpoint | Create Fire Services Proposed Programme
date | DATE:
checkpoint | Upload to ALL necessary QA platforms
date | DATE:
checkpoint | Save softcopy in GM Dropbox
date | DATE:
checkpoint | All employees have attended Induction
date | DATE:
checkpoint | All SWMS soft copies signed & hard copy printed & filed in the ‘on site’ paper folder
date | DATE:
checkpoint | PM Signature:
date | DATE:
signoff | PM Signature
checklist | ITPS-016 Fire and EWIS Panel Installation | itp |  |  |  | Yes | ITPS-016 Fire and EWIS Panel Installation
section | FIRE INDICATOR PANEL
checkpoint | Check – Location - (i) Installed in a location protected by the FDAS (expect where external to building) (ii) Operation of FIP shall not affect evacuation of building (iii) Located in an area which presents low risk of damage to equipment and persons (iv) Not mounted in any rooms containing sprinkler, pumps or motors
textbox | Performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Check – Particulars (i) Have controls and indicators not less than 750mm and not more than 1850mm above floor level. (ii) Have unobstructed access to controls and indicators (iii) Be mounted above ground level to protect batteries/on a plinth
textbox | Performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Check – Where the FIP is obscured by a door ensure the words “FIRE PANEL” in letters not less than 50mm high. There SHALL be no other lettering on the door.
textbox | Performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Check – Clearance. 1000mm in front of FIP and 500mm to each side shall be maintained.
textbox | Performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Zone Block Plan – Installation shall be securely mounted and easily accessible.
textbox | Performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Manual Call point – Manual call point must be installed at the entry point to site if the FIP is not located close to that point.
textbox | Performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Check – Power cabling is installed at FIP location
textbox | Performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Check – Location strobe on front of building is installed and operational.
textbox | Performed and witnessed by: Please print name and company of all involved parties
date | DATE:
section | EWIS PANEL
checkpoint | 1 - CABLE TYPE & SIZE TO DESIGN CRITERIA - AS1670.1-2018 Have a cross sectional area of no less than 0.75mm2 AS3000
button | C5.4.0 Wiring | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - CABLE HEIGHTS & LOCATION ADEQUATE FOR FIT OFF - AS1670.1-2018: internal domestic and office situations where cabling is mounted on walls at heights above 1.5m AS3000
button | C5.2.5 Control Loops | Pass
button | C5.4.0 Wiring | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - CABLE FIXED TO SPECIFIED REQUIREMENTS - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
button | C5.2.5 Control Loops | Pass
button | C5.4.0 Wiring | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - DETECTOR BASES FITTED OFF - AS1670, AS1668: Detectors that can be contaminated by construction works should not be fitted unless suitably protected until the construction works are completed.
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - DETECTOR HEADS INSTALLED & TYPE CHECKED - Detector type to appropriate location. Installed to Latest RCP
button | C5.6.0 Sensors/Detectors | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6 - MANUAL CALL POINTS INSTALLED - AS1670.1-2018: An MCP shall be mounted between 750 mm and 1100 mm above floor level and a clear space of 600 mm shall be provided in a semi-circle in front of the MCP.
button | C5.10.0 Manual Call Points | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - STROBES FITTED OFF - AS1670.1-2018: Check with Design Drawing and/or RCP
button | C5.2.2 Set Points | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 8 - SPEAKERS INSTALLED - AS1670: Check with Design Drawing and/or RCP
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 9 - WARDEN INTERCOM PHONES - AS1670.4-2018: The WIP handset shall be mounted at a height of not less than 1200 mm and not more than 1800 mm above finished floor level.
button | C6.2.8 Warden Intercom Phones | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 10 - SPRINKLER INTERFACES FITTED OFF - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
button | C5.2.2 Set Points | Pass
button | C5.8.0 Modules Input/Output | Pass
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 11 - FIRE RATING TO PENETRATIONS CORRECT - AS4072.1-2018: Ensure correct Test Report is used – refer to FRL requirements on wall selection
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 12 - LABELS AFFIXED - AS4072.1-2018: The label should be positioned close to the service penetration
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 13 - ACOUSTIC PENETRATION SEALING - AS4072.1-2018: Sound proofing sealant may be used depending on dB Level requirements
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 14 - CABLE TRAY BRACKET SPACING - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 15 - INSTALLED IN ACCORDANCE APPROVED WORKING DRAWING AND LATEST ARCHITECTURAL - In House QA. Up to Date drawing register. Drawings updated with MPX approved references.
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | ITPS-010 Brigade Inspection Sprinklers and Hydrants | itp |  |  |  | Yes | ITPS-010 Brigade Inspection Sprinklers and Hydrants
section | Details
checkpoint | 1 - CHECK SPRINKLER HEADS ARE INSTALLED IN AN ENVIRONMENT IN WHICH THEY ARE SUITED - AS2118.1-2017 – Section 2.2 – heads installed to correct classification and spacing
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - CHECK HYDRANTS ARE INSTALLED TO CODE AND HAVE REQUIRED CLEARENCES - AS2419.1-2005 – Section 3.2 – Clearances differ when related to internal or external hydrants, ensure correct standards are implemented
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - CHECK & TEST WATER SUPPLY CAPACITY TO MEET SYSTEM DEMAND - AS2118.1-2017 - section 4.2.2.1 – capable of supplying the flow and pressure requirements of the sprinkler system.
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - CHECK OPERATION OF PRESSURE SWITCHES TO DBS - AS2118.1-2017 - Appendix H4 – Test via 15mm test valve and record time taken to operate. Confirm with ASE monitoring service that alarm was received.
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - CHECK OPERATION OF PRESSURE SWITCHES FOR PUMP START - AS2118.1-2017 – Appendix H5.4 – P/Sw to be tested via dropping system pressure via test valve or remote test point.
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | ITPS-011 Pipework Pressure Testing |  |  |  |  | Yes | ITPS-011 Pipework Pressure Testing
section | Details
checkpoint | Test Information
textbox | Maximum System design pressure:
textbox | Required test pressure:
note | STOP TEST IMMEDIATELY IF PRESSURE GAUGE REACHES 1650 kPa
button | Hold Point Required: | Yes
textbox | Holding time:
textbox | Description of test configuration (attach sketch or piping and instrument diagram):
textbox | Test fluid:
textbox | Test Fluid Volume:
checkpoint | Test Equipment
textbox | Pressure Gauge:
textbox | Pressure Relief Valve:
textbox | Bleed valve:
checkpoint | Safety/Environmental Controls
textbox | SWMS Name:
button | Have all workers reviewed and signed off on SWMS prior to commencing work? | Yes,No (do not commence works)
textbox | Safe disposal of test fluid:
textbox | Test area controls (barricades, signage, etc.):
textbox | Inspection requirements (before, during, and after the test):
button | Is test equipment rated for test pressure: | Yes,No (do not commence works)
button | Are end caps sufficiently tightened: | Yes,No (do not commence works)
textbox | Pressure Gauge reading at completion of test:
textbox | Any visible water leaks?:
textbox | Test Date and Time Commenced:
textbox | Test Date and Time Completed:
checkpoint | Approvals
textbox | Supervisor in charge of test:
textbox | Person conducting test:
date | Date:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | ITPS-005 Fire Brigade Inspection | itp |  |  |  | Yes | ITPS-005 Fire Brigade Inspection
section | Details
checkpoint | 1 - FIRE INDICATOR PANEL LOCATION ACCEPTABLE - AS1670.1-2018 Section 3.9 – FDCIE to be installed with .5m clearance either side of panel and 1.0m clearance in front of Panel.
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - HEAT DETECTORS TESTED - 100% Test of installed devices. Correct location and spacings. Correct zoning and description at FDCIE. Correct interfaces triggered.
button | GMF-ITP-005 | Pass,Reviewed
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - SMOKE DETECTORS TESTED - 100% Test of installed devices. Correct location and spacings. Correct zoning and description at FDCIE. Correct interfaces triggered.
button | GMF-ITP-005 | Pass,Reviewed
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - A / C INTERFACE TESTED - GFAs triggered from correct zones/devices. Interface Matrix referenced.
button | GMF-ITP-005 | Pass,Reviewed
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - MANUAL CALL POINTS TESTED - 100% Test of installed devices. Correct location and spacings. Correct zoning and description at FDCIE. Correct interfaces triggered.
button | GMF-ITP-005 | Pass,Reviewed
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6 - DOOR INTERFACES. BMS INDICATION - GFAs triggered from correct zones/devices. BMS correct to descriptions provided from trades.
button | GMF-ITP-005 | Pass,Reviewed
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - CERTIFICATES PROVIDED - GMF-COMDOC-001, GMF-COMDOC-002, GMF-COMDOC-003, GMF-COMDOC-004
textbox | Drawing Reference Number:
textbox | Certificate: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | ITPS-006 Warranty Period | itp |  |  |  | Yes | ITPS-006 Warranty Period
section | Details
checkpoint | 1 - PROVIDE CLIENT OPERATOR INSTRUCTIONS - As and when required
textbox | General: Please print name and company of all involved parties
textbox | Witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - TRAINING - As and when required
textbox | General: Please print name and company of all involved parties
textbox | Witnessed by: Please print name and company of all involved parties
textbox | Held: : Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - MAINTENANCE PLAN - As per spec. and quoted offer.
textbox | General: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist | Lendlease Contractor Schedule H Checklist |  |  |  |  | Yes | Lendlease Contractor Schedule H Checklist
section | Incident Reporting
checkpoint | Incident Reporting
button | Any incidents were immediately verbally communicated to Lendlease | Yes,No
button | A copy of Incident Notification Form was submitted within 4 hours | Yes,No
note | Detail any incidents from the past month below and attach relevant forms below.
section | Workers compensation first, progress and final medical certificates and Return to Work Plans
checkpoint | Injuries and Illnesses
note | The following have been provided;
button | First Medical | Yes,No
button | Progress Medical | Yes,No
button | Final Medical Certificate | Yes,No
button | Return to Work Plans | Yes,No
button | I have submitted any necessary Injuries and Illness forms within 2 hours. | Yes,No
section | Reporting
checkpoint | A copy of any regulatory notices has been submitted to Lendlease via email immediately following receipt from regulator.
checkpoint | Daily Pre-Starts have been delivered to the office by 9am each morning.
checkpoint | I have submitted a copy of Toolbox Talks to Lendlease weekly, including records of attendance.
checkpoint | I have conducted a miniumum of 1 EHS inspection per day and a copy of EHS inspections for the month have been submitted.
checkpoint | Labour Statistics and Man Hours
note | Contractor Labour Statistics:
button | Has been completed weekly? | Yes,No
button | Has been submitted before the 26th day of each month? | Yes,No
button | Is attached below? | Yes,No
checkpoint | SWMS
button | Copies of updated SWMS have been submitted to Lendlease | Yes,No
button | Contractor SWMS review register has been submitted to Lendlease | Yes,No
button | Updated copies of signed SWMS have been submitted after onboarding each worker | Yes,No
checkpoint | Workers are trained and competent
button | Copy of current training register has been submitted | Yes,No
button | Copies of licences, qualifications, training records for any courses attended during the month | Yes,No
button | VOC (Lendlease Template) for concrete saw/angle grinders and Plant to be submitted for all workers before operation | Yes,No
checkpoint | I have submitted copies of daily pre-start inspection records for the month
checkpoint | I have attached a copy of the up-to-date Plant & Equipment Register
checkpoint | Copy of current and up to date Electrical Register has been submitted ( 3 monthly unless new tools added)
checkpoint | I have attached a copy of the Fall Prevention Register
checkpoint | Lifting gear to be inspected, tested and tagged
button | I have submitted to Lendlease and attached below a copy of lifting equipment quaretly testing register | Yes,No
button | I have submitted annual inspection certificates to Lendlease | Yes,No
button | Monthly inspection register has been sent to Lendlease as per Lendlease Lifting and Slinging Guideline | Yes,No
checkpoint | I have attached copy of Hazardous Substances Register highlighting any chemicals brought on site this reporting period.
note | NOTE: Subcontractors are required to use Chemwatch to log all chemicals utilised
checkpoint | A copy of the Ladder register has been submitted this month
checkpoint | I have attached a copy of Safety Data sheets for chemicals brought onto site within this reporting period (this month)
checkpoint | Temporary Works Design Register
note | NOTE Temporary Works Design Register must be submitted prior to mobilisation capturing of all Temporary works to be implemented by the trade
button | I have attached the updated Temporary Works Design Register | Yes,No
button | I have attached Evidence of Engineering Certification | Yes,No
button | I have attached Evidence of 3rd Party review of engineering | Yes,No
signoff | Signatures
checklist | ITPS-001 Fire Alarm and EWIS Design | itp |  |  |  | Yes | ITPS-001 Fire Alarm and EWIS Design
section | Details
checkpoint | 1 - REVIEW CLIENTS DRAWING REGISTER - IN HOUSE
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 2 - NOTATE INTERNAL DRAWING REGISTER - IN HOUSE
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 3 - REVIEW TENDER/CONSTRUCTION DRAWINGS - IN HOUSE
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 4 - REVIEW SPECIFICATION - NCC2019 FIRE SPECIFICATION
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 5 - PREPARE SHOP DRAWINGS/ LAYOUTS - IN HOUSE NCC2019 FIRE SPECIFICATION
textbox | Approval by: Please print name and company of all involved parties
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 6 - REVIEW SUPPLIERS SHOP DRAWINGS - NCC2019
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - DESIGNING FIRE ALARM SCHEMATIC - In House Design 1670.1-2018 – Must specify size/type of cable to be installed, transmission paths, type of devices to be installed and End of Line Devices
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - PREPARE SCHEMATIC DRAWINGS - Prepared to as installed drawings.
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 7 - SUBMIT SHOP DRAWINGS FOR APPROVAL - In house design Referenced to PC specifications
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 10 - REVIEW RETURNED SHOP DRAWINGS - In House QA
textbox | Drawing Reference Number:
textbox | Witnessed by: Please print name and company of all involved parties
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | 11 - DISTRIBUTE "FOR CONSTRUCTION" DRAWINGS - Referenced to PC specifications. Updated and superseded as needed
textbox | Drawing Reference Number:
textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
signoff | Signatures
checklist-flat | FORM-002 Tool Box Talk Platform Ladders |  |  |  |  | Yes | FORM-002 Tool Box Talk Platform Ladders
checkpoint | Tool Box Talk - Platform Ladders
note | DO NOT use platform ladder unless you are familiar in its safe use and operation.
note | Always complete as much work as possible at ground level before using the ladder.
note | Make sure the platform ladder is stable before climbing.
note | Project: TPCH
textbox | Tool Box conducted by:
textbox | Attendees:
date | Date:
checkpoint | Potential Hazards
note | The folllowing potential safety hazards and risks have been explained to attendees:
tickbox | Falls from height
tickbox | Falling objects
tickbox | Awkward posture
tickbox | Duration of task
tickbox | Repetition of movement
tickbox | Sprains/strains
tickbox | Over-balancing
tickbox | Slip/trip/fall
tickbox | Electrical hazards
tickbox | Climbing with loads
checkpoint | Pre-Operational Safety Checks
note | 1. Familiarise yourself with the safety instructions on the ladder.
note | 2. Wear slip-resistant footwear. Never wear sandals, high heels or flip-flops. Wear appropriate clothing (e.g. no loose or flapping clothing, or clothing that restricts movement when climbing
note | 3. Do not use if affected by a medical condition or medication.
note | 4. Keep ladder clear of live wires, electrical hazards and ceiling fans.
note | 5. When transporting your ladder check for overhead power lines, live wires, service cabling or electrical hazards.
note | 6. Carefully inspect your ladder to ensure there are no worn parts or damage before climbing:
note | • joints between steps and side rails tight, all fittings secure, moving parts operate freely
note | • rungs and platform are free of paint splatter, grit, oil and grease, welds are intact, and
note | • all components of ladder intact including side rails, rungs, platform, feet, hand grip.
note | If any component is found to be worn or damaged, rectify any faults before use.
checkpoint | Operational Safety Checks
note | 1. Complete as much of the task at ground level as possible.
note | 2. Ensure the ladder is placed on dry, firm, level ground/floor. Uneven footing may cause the ladder to rock. If this occurs re-position the ladder until all feet have firm contact with the floor. Always check there is no rocking movement before climbing the ladder.
note | 3. If castors are fitted to the ladder, ensure rubber feet have firm contact with the floor when the springs are depressed.
note | 4. Ensure the ladder is fully opened and the spreader bar is locked into position. Check for overhead obstructions before climbing.
note | 5. Only light work is to be undertaken on the ladder. Always face towards the ladder when climbing, and always maintain three points of contact with the ladder. Use a tool bag or tool belt to help to keep hands free.
note | 6. Only one person is permitted on the ladder at any time. A second person may stand alongside the ladder and help to steady it, or pass materials/tools up if required. Do not lift heavy weights that unbalance the ladder.
note | 7. Never stand or sit on the top cap or use the rails around the top as a step. It is not designed to be used as a tread/seat or step. Always stand in the centre of the platform.
note | 8. Do not over reach whilst using the ladder. Maintain the majority of your body weight inside the perimeter of the platform.
note | 9. Do not ‘walk’ the ladder while on it. Always get off to shift position.
note | 10. Before moving a ladder, take care to ensure that all tools and other items have been removed.
note | 11. Be mindful of your concentration and fatigue level. Avoid becoming overconfident when using ladders during repetitive tasks.
checkpoint | Housekeeping
textbox | Items for Discussion
textbox | Items for Review and discuss at next meeting:
note | All attendees have been made aware they should:
tickbox | Return ladders to secure storage in a clean and in safe working order
tickbox | Regularly check ladder feet for excessive wear.
tickbox | Enter any maintenance in an equipment maintenance record
signoff | By signing I confirm I atteneded this ToolBox Talk.