## Sheet1
ConQA Team Notes:
Document Title: |  | ITP-091-CIV-PSDS-Conduit & Pits-MTM
ITP Description: |  | PSDS-Conduit & Pits-MTM
Discipline (e.g. CIV/STR/RAIL: |  | 091-CIV
Revision Number: |  | 0
Revision Date: |  | 2023-01-13
ITP created by: |  | Shubham Bajaj (Sammy)
ITP approved for use by: |  | Jon De Castro
Special Notes to ConQA Team : |  | ITP for Progress Street
Inspection & Test Plan - Conduit & Pits - MTM
[9 empty] | Revision: | 0
[9 empty] | Date: | 2023-01-13
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Non Dependent | IFC Drawings L1-CHE-STD-043 (VRIOGS 012.2.1) L1-CHE-SPE-070 Australian Standards MRPA Standards | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminaries - Materials
2.1 | Conduits | HV Conduit: AS 2053 HV Conduit (boring): AS 4130 Comms Conduit: AS/ACIF S008:2006 LV Conduit: AS/ NZS 3000 - 2000. L1-CHE-STD-043 L1-CHE-SPE-070 | LV & Signalling: 100Ø (114mm OD), orange electrical heavy duty 5.9mm wall thickness LV & COMMS CONDUITS TO HAVE A MIN 600mm BENDING RADIUS Inspect materials upon delivery and attached delivery dockets. | Visual Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs Attach delivery dockets
2.2 | Pits and Pit Lids | IFC Drawings VRIOGS 012.2.1 Section 6.15-16 VRIOGS 012.2.1 Section 6.9 VRIOGS 012.2.1 Cl. 6.7 (c) L1-CHE-SPE-070 Cl. 10 AS1289 | Pits: Pits located within 1.5m of nearest rail, pit to be 300LA Railway loading Pits 900x900mm or greater, multipart pits lids to be used. Pit Lids: Pit Covers shall comply with AS3996-2006 Pit lids in trafficable areas to be Class D, non-trafficable areas to be Class C. LV, Comms Cover: pit covers shall be labelled with the words “RAILWAYS SIGNALS & COMMUNICATIONS” (L1-CHE-STD-043 14.6) Inspect materials upon delivery and attached delivery dockets. | Visual Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs Attach delivery dockets
2.3 | Warning/Marker Tape | IFC Drawings AS/NZ 2648.1 TS-SP-013 L1-CHE-STD-043 6.4 | Warning/Marker Tape: Above LV: 150mm minimum wide orange coloured PVC ‘DANGER RAILWAY SIGNALLING CONDUITS’ Above Comms: 75mm minimum wide white coloured PVC ‘WARNING COMMUNICATIONS CABLES’ with an embedded stainless steel trace wire to be laid directly above trenched VicTrack assets Above HV: 300mm minium width orange coloured PVC 'Danger - Electrical Cable Below' Inspect materials upon delivery and attached delivery dockets. | Visual Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs Attach delivery dockets
2.4 | Protection Barriers | IFC Drawings L1-CHE-STD-070 10.3.3 AS4702 | Protection barriers shall be polymeric cable protection covers complying with AS4702 OR a min. 40mm thick concrete barriers (pavers) not less than 15MPa at 28 days Inspect materials upon delivery and attached delivery dockets. | Visual Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs Attach delivery dockets
2.5 | Backfill Material (stabilised sand) | IFC Drawings L1-CHE-STD-043 Section 2 Table 1 | Material free of rocks that will not pass a 30mm sieve. The material shall be free or organic matter or anything that could dmanage the conduits. Inspect backfill material. Attached delivery dockets (if applicable). | Visual Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs Attach delivery dockets
2.6 | Bedding Sand | IFC Drawings AS2758.1 | Bedding Sand shall be a clean sand that is an uncrushed fine aggregate to AS2758.1 and shall have a thermal resistivity ≤ 1.2 °Cm/W at 5% moisture content. | Visual Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs Attach delivery dockets
2.7 | Draw Wires | TS-SP-013 AS 4142 | 6 mm diameter polypropylene blue/yellow | Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs Attach delivery dockets
2.8 | Concrete Mix - Trench | L1-CHE-STD-043 | Concrete strength at 28 days shall be not less than 25MPa. Chemical admixtures or fly ash shall not be used | Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs Attach delivery dockets
3 | Prelimnaries - Procedures & Documentation
3.1 | Services | Services CAD file | All services within 5m of Excavation location have been identified and appropriate control in place (refer to MRPA Excavation Permit). Survey to mark out existing services. | Visual | Prior to commencement of works | IP | SE/Site Supervisor | This ITP
3.2 | CSR Works Procedure | WAP_BRU_201 | WAP to be reviewed and signed by all relevant stakeholders along with Rail Safety highlighting works proedure with in the Rail Corridor | Document Review | Prior to commencement of works | HP* | SE/Site Supervisor | This ITP
4 | Pre-Construction Activities
4.1 | Survey Set-out | IFC Drawings | Survey to set out trench alignment and pits, and establish construction control (alignment and level). | Measure Visual | Each element | IP | Surveyor SE/Site Supervisor | This ITP
4.2 | IFC Drawings | IFC Drawings | Check the revision of the IFC drawings are current as per the drawing register (on Teambinder) | Document Review | Prior to commencement of works and at regualr intervals | IP | SE/Site Supervisor | This ITP
5 | Construction Activities
5.1 | Trench Excavation | IFC Drawings L1-CHE-SPE-070 7.3 Table 2 L1-CHE-STD-043 L1-CHE-STD-070 7.1c | Trench profile and depth as per IFC drawings. Edge of trenching to be a min. 2m from strucutres/pile foundation (unless it is mounting the structure) and a min. 4m from the rail for HV and 3m from the rail for LV & Comms The bottom of the cable trench shall be level across its width and free from any protrusions and rubble that could cause damage to the conduits. The width of the trench shall be not less than 200 mm (chain or bucket excavation) or 300 mm (backhoe and other). | Measure, Visual | Each lot | IP | SE/Site Supervisor | This ITP
5.2 | Trench Stability | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings MRPA Standards | Trench stability check: - Shoring, - benching - geotech signoff Attached Geotech Report | Visual, Document Review | Each lot | IP | SE/Site Supervisor | This ITP
5.3 | Placement of Bedding Sand for Conduits | IFC Drawings L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 | 100mm of bedding sand/crusher dust to be places at the base of trench. | Measure, Visual | Each lot | IP | SE/Site Supervisor | This ITP
5.4 | Conduit Placement & Configuration | IFC Drawings L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 L1-CHE-STD-077 | Conduits are configured in accordance with IFC drawings and meet cable separation requirements. Min Cover - HV: 1000mm - VicTrack: 650mm - Signalling: 800mm - LV: 800mm - Electrolysis: 800mm - SCADA: 800mm - MTM Comms: 600mm - 800mm below water coarses (stab sand encasement) - 1200mm Under VicRoads Roads & top of Rail - 900mm below council roads | Measure, Visual | Each lot | IP | SE/Site Supervisor | This ITP
5.5 | Separation of Services | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 L1-CHE-STD-077 IFC Drawings | Separation of services - HV: Min. seperation distance between HV conduits at least 50mm - VicTrack: fiber 300mm from HV - Utility: 300mm to utilities - Rail: When conduits are within 2.1m of edge of sleeper they must be encased in stab sand or cover is to be increase to 1.2m | Measure, Visual | Each lot | IP | SE/Site Supervisor | This ITP
5.6 | Joints | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | All conduit joints shall be made by utilising the spigot and socket ends. Ends to be joined shall be thoroughly cleaned using a solvent approved by the conduit manufacturer. The joint shall be impervious to water and shall be glued with an adhesive approved by the conduit manufacturer. Socket ends to be placed firmly into the spigots then hit with a mallet to ensure a sound connection | Visual | Each Joint in each trench | IP | SE/Site Supervisor | This ITP
5.7 | Conduit Inspection | L1-CHE-STD-070 16 | Provision shall be made for inspection of cable routes by NA, MTM/VicTrack representatives prior to backfilling. | Visual | Each lot | HP* | SE/PE MTM / VicTrack Rep. | This Itp
5.8 | Bedding Sand Installation | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 CL13.1 IFC Drawings | Bedding sand/crusher dust extends 50mm past edge of conduits. Bedding sand/crusher dust extends 100mm above conduits. Attach Delivery Dockets | Visual | Each lot | IP | SE/Site Supervisor | This ITP
5.9 | Marker Tape | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-SPE-070 Cl10.3.3 | Warning Tape installed a min. 300mm above top conduit or a min. 300mm above HV protection barrers. Tape to be one continuous length. VicTrack to inspect the Marker Tape placement.. | Visual | Each lot | HP* | SE/PE MTM / VicTrack Rep | This ITP
5.1 | Backfill Installation for Conduits | IFC Drawings L1-CHE-STD-043 clauses 6.15 and 6.16 | Backfill per trench profile - 150mm layers of 3% stabe sand - conduits under water ways to have 800mm cover from base of water way and backfilled with 3% stab sand The trench shall be finished with a slight mound, height equal to approximately 25% of trench width, to provide for further settlement. Trenches under road pavement - backfill to be same material as the road formation material. Trenches immediately adjacent to footing shall be 3% stab sand. To be thoroughly placed to fill all voids without placing undue strain on or cause displacement of conduits. When conduits are within 2.1m of edge of sleeper they must be encased in stab sand or cover is to be increase to 1.2m VicTrack to be notified and witness the first layer of backfilling. Attached Delivery Dockets | Visual | Each lot | HP* | SE/PE MTM / VicTrack Rep | This ITP
5.11 | Signalling Pits LV Pits Electrolysis Pits SCADA Pits MTM Comms Pits | L1-CHE-STD-043 Cl7.14.o, Cl7.14.g | - intervals no greater than 400m (electrolysis 190m) - 3m from rail - Access Roads, Class D lids - Footpaths and non traffiacl areas, Class C Lids | Visual, Measure | Each Pit | IP | SE/Site Supervisor | This ITP
5.12 | Additional Considerations | IFC Drawings | Access tracks to pits Safe access and egress (i.e. lid doesn't open up with workers back to the rail) Hand rail & retaining wall installed as required | Viual | Each Pit | IP | SE/Site Supervisor | This ITP
5.13 | Bedding for Pit Installation | L1-CHE-STD-070 Cl 7.21.u L1-CHE-STD-043 | 150mm of crushed rock under pit extending 500mm past the pit Drainage arrangements shall be provided at the base of each pit. Attach Delivery Dockets | Viual, Measure | Each Pit | IP | SE/Site Supervisor | This ITP
5.14 | Pit Orientation | IFC Drawings | Pit to be parallel to track and parallel to conduit route. | Viual | Each Pit | IP | SE/Site Supervisor | This ITP
5.15 | Pit Installation | IFC Drawings | Pit installed to design specifications Pit chamber floor to be 100mm lower than the underside of the lowest conduit. | Viual | Each Pit | IP | SE/Site Supervisor | This ITP
5.16 | Conduit Entry onto Pits | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | Lowest conduit 100mm from the pit chamber floor. | Visual, Measure | Each Pit | IP | SE/Site Supervisor | This ITP
5.17 | Tracer Wire | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | Warrning tracer wire for Vic Track routes to be drilled into pits and crimped off. If tracer wire broken needs to Crimped | Visual | Each VicTrack Pit | HP* | SE/PE, MTM / Vic Track Rep | This ITP
5.18 | Spigots and Bell Mouths | L1-CHE-SPE-070_9.3.4 | All conduit ends in pits are to be correctly fitted with spigots to ensure that there are no sharp edges on the conduit; they are to be mounted flush with the pit wall and not touching any other spigots. HV Conduit entering the pit shall extend a minimum of 150mm beyond the edge of the excavation and be fitted with Bell Mouths. | Visual, Measure | Each Pit | IP | SE/Site Supervisor | This ITP
5.19 | Draw Ropes | VRIOGS 012.2.1 | The draw wire shall be continuous for the complete length of the conduit run. The draw wire shall have a minimum of 2 metres of slack within every pit. | Visual | Each Pit | IP | SE/Site Supervisor | This ITP
5.2 | Backfill and Compaction Testing (if applicable) arouns Pits | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | Backfill used around pit & pit lid to achieve 95% standard compaction in layers no more than 150mm layers Sand within sand pits to be compacted in layers no more than 250mm layers Backfill shall be compacted and level with the collar and surrounds for Trafficable Pits. Attach Test Report | Document Review, Visual | Each Pit | IP | SE/Site Supervisor | This ITP
5.21 | Spare Conduits | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | Spare conduits to be sealed and to be included on survey report. | Visual | Each Pit | IP | SE/Site Supervisor | This ITP
5.22 | Pit Lables | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | Pit labels Brass Label (30mm x 150mm) - HV: DANGER - Railway High Voltage - VicTrack: Victrack Comms - Signalling: Rail Sign Comms - LV Pits: Electrical - Electrolysis: Electrolysis - SCADA: Rail Sign Comms - MTM Comms: Rail Sign Comms | Visual | Each Pit Lid | IP | SE/Site Supervisor | This ITP
5.23 | Pit Numbers | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | Pit Number Brass Label (30mm x 150mm) - HV (22kVV Feeders): ###HV - DC (HV Feeders for OHLE): ###DC - VicTrack: ###C - Signalling LV: ###SL - Signalling HV (2.2 or 3.3kv): ###SH - LV Pits: ###L - Electrolysis: ###E - SCADA: ###MS - MTM Comms: ###M | Visual | Each Pit Lid | IP | SE/Site Supervisor | This ITP
5.24 | Cable Route Markers | L1-CHE-SPE-070_13.2 STD_E0169 and STD_E0170 AS 4799 STD G0003 and STD G0004 | Cable Route Markers - points entering & leaving the rail corridor - no greater than 100m spacing - Change of direction (more than 5 degrees) - White posts with marker plates for conduit runs | Visual | Per Cable Route | IP | SE/Site Supervisor | This ITP
5.25 | Cable Pulling | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | Cable pulling to be witnessed by MTM/Vic Track and to be signed off. | Visual | Per Cable | HP* | PE, MTM/VicTrack Rep | This ITP
5.26 | Cable Labels | L1-CHE-SPE-070 Section 13.3 | All installed High Voltage Cables shall be legibly and indelibly marked with an appropriate identifying label at each end of the cable, and at any cable joints. The label shall state the destination points of the cable and the name of the cable relevant to appropriate drawings | Visual | Per Cable | HP* | PE, MTM/VicTrack Rep | This ITP
5.27 | Cable Joints | L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings | Cable joints are installed correctly, with sufficient fault loops lengths & supported correctly in pits. | Visual | Per Joint / Termination | HP* | PE, MTM/VicTrack Rep | This ITP
6 | Post-construction / Post-installation Activities
6.1 | As-built Survey | IFC Drwings L1-CHE-SPE-070 Section 13.1 | Survey report to include but not limited to: - Cable joint locations. - Cable pit locations (Corners) - Pit dimensions & pit lid type - Under line crossings - Under road crossings - Changes of direction - Spare Conduits - Conduits labelled as per trench profile - every 10m - Other significant points of the cable route Attached Survey Report | Document Review | Each Lot | IP | SE/PE | This ITP
6.2 | Handover Check | IFC Drawings | Handover check completed for Testing and Commisioning. Attach MTM/Vic Track Check Sheet (Signed-off) | Document Review | Each Lot | HP* | PE, MTM/VicTrack Rep | This ITP
6.3 | Testing and Commissioning | IFC Drawings | Testing and Comminsiong to be completed Attach Testing and Comminsiong Report | Document Review | Each Lot | HP* | PE, MTM/VicTrack Rep | This ITP
6.4 | Non-conformance Report (NCR) Closure | MRPA Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed. | Document Review | Once, prior to closure of this lot / element / Work area | HP* | SE/PE/SPE | This ITP
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /