## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
80dfb780-035d-5666-9f26-1e3fd33cf5fd | checklist | DN1210-0003 - Stormwater Drainage Line Record | itp | DN1210-0003 - Stormwater Drainage Line Record
d1c4b54a-b4c4-539e-9691-c0d96368dc14 | section | SET OUT
c5d6f50a-ccb6-53db-bb19-e28206919615 | checkpoint | 1 - Confirm Stormwater alignment is as per latest Drawing revision and does not clash with other Services.
a4065fb7-47d2-51b3-8490-491671bfbe94 | note | Comments: Design Engineer to approve if the location needs to be moved.
27872ba7-cfde-54f2-b0b3-7b5d9f6503cf | textbox | NCR/OFI/RFI No:
274a37be-f134-5256-8964-164983e5d09a | checkpoint | 2 - Check Survey Set out and mark out completed.
3125fab0-e6d9-5e66-8bdd-a0deb9806432 | note | Comments: Max. 10m interval
8ac7e125-0b01-530b-adbc-7c83d866cc8e | checkpoint | 3 - Confirm correct location of Manholes or Chambers, Catchpits.
d08aedaa-d3c4-534b-93e0-a8b3f97ae182 | textbox | Comments: Refer to Dwg:
250e19d1-e2cb-5fbb-b958-1502f46075be | section | TRENCH EXCAVATION
a97a1b49-0483-5c2a-aeff-5b999d064122 | checkpoint | 4 - Ensure permits are in place.
c4f9efec-88e3-5916-8886-90616352200c | checkpoint | 5 - Pothole existing services data in place.
a88916c6-f006-5573-8093-21c6e2687901 | checkpoint | 6 - Confined Space Permit required?
1ce99c41-985e-5ed5-8590-6256ee7c23d6 | note | Comments: Trench depth > 1.5m must be shored or battered.
d0547d1e-a8b7-5c80-b83d-cd2c32bdda0c | checkpoint | 7 - Foundation test conducted.
452644e1-e467-5193-9154-2a774c1233b8 | note | Granular Material: Scala 3 blows/100mm 5% CBR
1e418d7c-dc6c-5e26-aa25-6358e957c892 | note | Cohesive Material: Shear Vane Strength 70kPa
fe505ecd-66c2-5d92-97f3-03de78b849b1 | checkpoint | 8 - Undercut required?
82e249bc-038f-574c-b7df-489b09b5f54a | note | Comments:
e957ffca-6498-5936-9eff-b596c5779659 | textbox | Undercut depth:
a3e6936b-8b42-55e4-b322-93da889abab3 | textbox | Metal:
366236e9-d9d4-5404-9128-b2d28615f3e4 | section | STORMWATER PIPE INSTALLATION, BACKFILL AND TESTING
31d5f8ad-f5a7-5de8-b074-5818082d2a1f | checkpoint | 9 - Check actual horizontal and vertical alignment achieved
8c616601-5035-5ce0-9364-a7b6cf83728a | checkpoint | 10 - Ensure pipe is checked & cleaned before being laid into the trench.
7337a6cc-1af5-5a5f-9107-c0f023787fdb | note | Comments: No vandalism, surface damage or deterioration. No install if found defective.
856ead07-9789-5994-9bcc-73fdb1d2732b | checkpoint | 11 - Line, level, and grade conformance checked
e84812bd-8c2d-5281-a984-59b5181bd154 | checkpoint | 12 - Ensure Bedding, surround & backfill materials are well-compacted and tested.
e9f4ee5a-ea12-5e98-b07b-d0f785a5d524 | note | GAP20 - NDM- minimum 95%
d2d34806-3576-5342-8847-b6be96f78380 | note | LRAP65 - NDM- minimum 95%
0d1bfd0d-b01a-562d-a2dc-f55be211f7e4 | note | Comments: At every 200mm compacted lift
e75614fe-2c0c-5b12-9fa9-4b0f2b88bdab | checkpoint | 13 - Ensure installed pipeline has CCTV completed
2601f2b1-185c-5ffa-824a-9f0fefb7305d | note | Comments: No internal surface cracks. Clean from debris and contaminants.
3df15f87-6988-5d80-a0b5-df40e70b3938 | section | ACCEPTANCE
955faf87-29fa-529e-a42f-37e0ac363031 | checkpoint | Inspection By: Downer
9cfcbcb4-0357-5e51-b5a4-fb2be1210189 | textbox | Name:
8663f0dc-3ff4-54d0-8b86-4ffda6e49df8 | date | Date:
32b75610-717e-5075-a935-2468bbb9ba63 | signoff | Signature
26510945-d224-4c04-b6b5-0fbecfb28301 | checklist | DN1210-003 ITP Earthworks - Berm Backfill Rev 0 | itp | DN1210-003 ITP Earthworks - Berm Backfill
b567e37b-305b-4691-ab94-997e3525e2b6 | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS (MATERIAL TESTING & APPROVALS)
ae751a62-077f-4903-8007-09eabdd22652 | checkpoint | 1.1.1 - Weathering Resistance
170d24d6-9aaa-5a61-9714-6d3639b3fdd5 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
512865cd-9a30-59f2-b1c6-17dece2c767f | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
219a3981-3a3a-55bd-b780-74ab0986caad | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
f25d1e77-f126-5a80-af63-e918627bf828 | note | Verifying Document - IANZ Accredited Report
89c43b3a-8d27-5262-bbd0-f584e6beedda | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
d97eb3b9-672a-56bc-91c9-d66ab3b0160f | note | ○ Results to Engineer 2 wks before importing
f9597cbb-85fd-510f-852b-7a2ac6faf220 | note | Verification Activity: Activity - HP
e423c072-3524-5539-a79c-65fe85db3243 | note | Verification Activity: By - ENG
3a53d180-37da-4794-96f1-2c57191058d6 | signoff | AUTHORITY HOLDPOINT
4621ae14-9d3f-4092-8bdc-fb91a7d23106 | checkpoint | 1.1.2 - Los Angeles Abrasion Test
5459d323-a895-5181-8dd2-a5a78f7b1dd2 | note | Detail - NZS4407:2015, Test 3.12 - The Abrasion Resistance of Aggregate by use of the Los Angeles Machine
3b7a0f7d-79e4-5b1b-b7a0-c3f124c211a0 | note | Acceptance / Conformance Criteria - 0.5
0ddf40e4-ab58-5b23-a819-0d492f361e48 | note | Standard / Specification - PS 16.5.5, Appendix V
a56fe015-436d-58c3-860d-c80232f81fa9 | note | Verifying Document - IANZ Accredited Report
d72445bf-ad35-5f36-9523-021cf4c08d4c | note | Testing Quantity Required (based from schedule qtys) - 1 Test Required
ed4b7968-8888-5eb7-a02e-c08d10663fc9 | note | ○ Results to Engineer 2 wks before importing
f33b5661-1301-54dd-a6b5-01710a39df56 | note | Verification Activity: Activity - HP
62db03b1-767b-510f-84b1-dcffa41b7b55 | note | Verification Activity: By - ENG
0b6b78a6-31f1-4901-9607-f42fa97fa179 | signoff | AUTHORITY HOLDPOINT
ec0f526f-6a69-4bcc-bc78-077bd42de97e | checkpoint | 1.1.3 - Particle Size Distribution
834aff6f-f08b-579a-8bd1-cede2f04c2fd | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
8c0bf74e-0e20-5cca-bfb9-7db89783479f | note | Acceptance / Conformance Criteria - No Particles >200mm
cbbeee61-7095-5cc1-ac91-aeb41afe45d7 | note | ○ Maximum fines 10% passing 75micron sieve
55eddd53-3f67-5c5b-bbf1-1ca4d0ca3dff | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
ce403317-715f-5224-a0eb-2a4e21a9d974 | note | Verifying Document - IANZ Accredited Report
8ac422ba-606e-582a-a37b-de668b26fd02 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
c4575f95-29c0-5072-aa90-cf28a1dc5343 | note | ○ 0-400 - 2 tests
1faf988a-add7-5d72-a88b-3c1f71e64b60 | note | ○ 400-1,500 - 3 tests
866b8657-e118-5221-a273-57d7cb135a58 | note | ○ 1,500-4,000 - 4 tests
dfcaf6e4-305a-5955-9cca-45aec79ac805 | note | ○ >4,000 - 1 test for each additional 1,000m3
748b1587-859b-52de-912f-d63aff835bfa | note | – Results to Engineer 2 wks before importing
26711431-b97d-512d-bca6-bc51a82062e4 | note | Verification Activity: Activity - HP
8a1e80a2-5e9e-50d7-96bd-ebea22ee0c6e | note | Verification Activity: By - ENG
1f9e51cb-ecfe-4e36-a665-8117c203dfcb | signoff | AUTHORITY HOLDPOINT
b9c36af9-cacf-4685-9849-b5b3cce9a8fe | checkpoint | 1.1.4 - Maximum Dry Density and Optimum Water Content
77dc297a-b0d2-5fec-ab26-f7a374aaa011 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
774c6f36-018c-5319-a837-7596092ad73a | note | Acceptance / Conformance Criteria - Report Value Only
7aa77f23-5fa0-50c9-bed5-72b1b05dc4bc | note | Standard / Specification - Appendix XVIII, Appendix V
964cd6ca-b827-5bc5-9873-14f2591f0801 | note | Verifying Document - IANZ Accredited Report
14813e4f-e19a-51ed-b6ef-ccd0a296613d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
eb869f09-6a1c-5cab-be26-45194aa2b622 | note | ○ Results to Engineer 2 wks before importing
bab267a8-a813-5045-b8a9-37f18d17a4d1 | note | Verification Activity: Activity - HP
9c1d7416-706e-57f1-b3a7-033045f150eb | note | Verification Activity: By - ENG
87730b18-0c88-4532-968b-4c16a64cbb39 | signoff | AUTHORITY HOLDPOINT
313869ad-e4d9-4ce7-a906-54a77553c69d | checkpoint | 1.1.5 - Soaked CBR
b87e76ea-1e79-59ed-88a6-d487054ed8a2 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
66c07f5e-e6c7-5738-8837-53615c535a16 | note | Acceptance / Conformance Criteria - >25%
852d6290-9082-5256-a910-8fde398d9e5c | note | Standard / Specification - PS 16.5.5, Appendix V
46b18c6f-cbdf-5b99-9606-1a5bfcb50b5d | note | Verifying Document - IANZ Accredited Report
96aa03dd-6d33-517b-be25-b9c32644e019 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
1758c525-e975-592e-a7b3-914b9f092788 | note | ○ Results to Engineer 2 wks before importing
dd1adc3b-47ae-576f-a191-48fb85156421 | note | Verification Activity: Activity - HP
6ed9aa3a-b493-5ffc-9e0c-e3b96b7ad94e | note | Verification Activity: By - ENG
2baa5519-d187-4e8d-aef1-96d204ab3928 | signoff | AUTHORITY HOLDPOINT
0cce9f39-1fe9-4cb7-84a0-1347889a24bf | checkpoint | 1.1.6 - Solid Density
9c9be7ce-a4ed-5593-bddc-204edaac5bd9 | note | Detail - NZS4407:2015, Test 3.7.1 - The Solid Density of Aggregate Particles
0e1d6109-85c8-5dbb-adae-26b462d0f52b | note | Acceptance / Conformance Criteria - Report Value Only
4e3a1109-c507-5ac6-b181-a34c1204ee91 | note | Standard / Specification - Appendix XVIII, Appendix V
7c46fb2d-3b2e-5a72-adf2-52668ed6141e | note | Verifying Document - IANZ Accredited Report
f7705853-d6d8-55ce-9e48-1503adda94bc | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
ccc3ce36-6a79-59c8-9659-716ac1366231 | note | ○ Results to Engineer 2 wks before importing
1a1872d4-ffab-5795-9840-d6f6ac460aff | note | Verification Activity: Activity - HP
f1351d8f-4411-5f37-ac20-8ba4d499f16e | note | Verification Activity: By - ENG
9c032d01-4a60-4715-9580-0367e8722237 | signoff | AUTHORITY HOLDPOINT
9785d001-7bf6-4b2d-8e8f-ddc9322fc6d5 | checkpoint | 1.1.7 - Crushing Resistance
f8da953e-df9e-587f-8c0d-c8921c062455 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
7d890827-de77-5e6f-9f0a-68dde121faa4 | note | Acceptance / Conformance Criteria - >100KN
629ba928-8e42-5014-9037-51e19f1f69b8 | note | Standard / Specification - Appendix XVIII, Appendix V
b07c9dee-9e38-562e-8a2b-bd18421d659a | note | Verifying Document - IANZ Accredited Report
41987e16-5327-5b19-a5e1-9b9f516a2c90 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
54286504-b1e6-503b-aaa4-a4069e1d5d47 | note | ○ Results to Engineer 2 wks before importing
24adba30-fbd5-5c97-bdfb-bc6005ea0014 | note | Verification Activity: Activity - HP
c4e32125-e677-5994-8b23-b1b70a0a1052 | note | Verification Activity: By - ENG
4b425774-86b8-497d-b2d2-6bcd40a72d7e | signoff | AUTHORITY HOLDPOINT
8a26f54e-e6b9-4e37-a364-c24ae4b7703a | checkpoint | 1.1.8 - Geotextile -Only Under Strutual Fill
ed34fa9d-ea58-5764-903a-61aea8490f01 | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation.
55b7212b-8605-5a6e-b6d3-08fea246cf6d | note | Acceptance / Conformance Criteria - Engineers Approval
db20c58a-3d32-5945-b9e3-c61e2a5bce5d | note | Standard / Specification - PS 16.5.7, Appendix V
addf8051-6cfe-509a-ad18-2cfe2f82a5b4 | note | Verifying Document - Data Sheets
0c8190f7-6f91-5a96-b755-7ed564e383b8 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
282ccef2-904b-5a19-9c7b-1a56bec90019 | note | Verification Activity: Activity - HP
99d9d6ae-1258-5499-b7e4-12efc9088624 | note | Verification Activity: By - ENG
0b07cb24-1dc5-4366-b336-4241081bba50 | signoff | AUTHORITY HOLDPOINT
8c64aa70-7d69-4b88-acb1-7b54840e23dd | checkpoint | 1.1.9 - Laboratory Testing for Soil Suitability
58c2b8c9-9287-5d7d-956f-47a3bb0c0f85 | note | Detail - Soil Test Results from Hill Laboratories to confirm that topsoil suitable to for reuse
33f06718-b1ec-510b-b56e-8d831f07f1e4 | note | ○ Soil Reaction
664bbeb1-140e-578c-99a5-1a6d7ee79c93 | note | ○ Electrical Conductivity
4c0cb2b2-93b2-5cc4-83c7-ef4d0c7002bf | note | ○ Mechanical Analysis (texture)
a2f2662e-0706-569e-9c2c-a9a07881a482 | note | ○ Stone Content
550829dc-1225-5a80-afbe-cb7579a4da3d | note | ○ Nutrient Levels of nitrogen, available phosphorus, available potassium and available magnesium
9e615e84-63e4-5625-a015-f388525c6f7f | note | ○ Organic Matter Content
41b89eca-e1aa-5caa-bbfa-6dd1fd937e4b | note | ○ Check for Toxic or Hazardous substances
61950528-1621-5792-aa14-d12e960b70e4 | note | Acceptance / Conformance Criteria - Engineers Approval
bd4a2f79-8e39-50c2-af05-49b16ab1f38e | note | Standard / Specification - NZTA P39:2013 3.1
34ef85cc-c7d0-5565-b46d-0978a305be5d | note | Verifying Document - Hill Laboratories Test Report
7aef608a-586d-5f47-bb9c-1e8f0274bf2e | note | Testing Quantity Required (based from schedule qtys) - 10 equal samples taken from site, mixed together, then 1kg of soil sealed into a plastic bag and sent to lab for sampling
92fc6694-157e-5d62-a1d2-aa3d69efdfb0 | note | Verification Activity: Activity - I
b0f4265a-f627-5607-aee6-728315986084 | note | Verification Activity: By - SE
b3289ac5-b9ad-4084-89c1-bf5603717c12 | section | SECTION 2 – CONSTRUCTION - STRUCTURAL FILL ON BERM AREA
37ad755a-9095-4037-927e-b926371a854d | checkpoint | 2.1.1 - Compaction -Clegg Hammer
5e328567-d191-5a23-af52-78be541c04f9 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
9267bc8b-fd00-561d-9c4b-2b4ebb08037c | note | Acceptance / Conformance Criteria - Structural Fill
9667dfdc-9e21-5142-acf4-6ea9e9c7d7d2 | note | – Min CIV 18
62d08faa-61b8-5d38-8113-bba54b286091 | note | – Ave CIV 20
0a56712a-c6ef-5ac8-83f0-3993dbc1f117 | note | ○ Non-Structural Fill
8777bf59-fd9a-5878-a9f8-2d34a7457fa2 | note | – Min CIV 10
3b623987-3d65-5ea5-8698-bbb7c7eb3160 | note | – Max CIV 12
8e426650-b5de-5e57-92dc-bbc832eebad6 | note | Standard / Specification - Appendix XVIII
0958c8ec-0a9f-5776-8e3e-d2aaa916bb3c | note | Verifying Document - Clegg Hammer Report
b42fa6b7-12bb-583d-bc64-0fbcb27ac8ac | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
fafe8632-2fa0-541c-9c89-3bb6091719f8 | note | Verification Activity: Activity - I
e1ae69a9-943c-53f2-9871-82e4cb23c00d | note | Verification Activity: By - SE
7626dd1d-1b0a-4c69-a009-ddab4adbff12 | checkpoint | 2.1.2 - Compaction-NDM
7beb85a9-ef6f-594b-a5ab-766a5d338a51 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
c7a7531e-ae45-5c65-b65e-8f122e02ad18 | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
a8c61459-cda2-560f-a158-796bc659e919 | note | ○ Non Granular Material
729ac588-2525-5c18-8492-6353269039f4 | note | –Max Air Voids 8%
9b197cf0-ee03-5ba3-ae3f-cbdbcf9f50da | note | Standard / Specification - Appendix XVIII
b47c213a-3c33-59f1-bfa5-12cd7415225f | note | Verifying Document - IANZ Accredited Report
1be65343-0039-5e4a-a4cb-12ef661bc825 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
4122a55a-5c4b-5ebf-be12-e9de4f20070e | note | Verification Activity: Activity - I
d1847105-e1b8-5285-8dcd-a4b816c5e6fb | note | Verification Activity: By - SE
62151bee-e9c8-486a-bb5e-a3721c9fb835 | section | SECTION 3 – CONSTRUCTION - SITE WON LANDSCAPING FILL
aa275cff-9a3a-4d4f-8dc2-5b79d62faac4 | checkpoint | 3.1.1 - On Site track-able Testing
31a18122-4dc9-5abc-9e77-81cac707f0ee | note | Detail - Fine grained Type A3 site won materials may be considered suitable for use as landscape fill providing that it is ‘track-able’ by the contractor’s plant.
682f3a6b-0a2d-54b4-a9ae-9c6ac148180e | note | Acceptance / Conformance Criteria - Trackable by Contractors Plant
cfe28071-1c42-5a3f-926c-af452fbb9fbd | note | Standard / Specification - PS 16.5.5
0ca63b01-d21a-5e89-829c-61846109642a | note | Verifying Document - Site Engineer Site Record
e95b9f7e-556d-5897-960e-6706ae58ee9b | note | Testing Quantity Required (based from schedule qtys) - Before placing any fill each day for each area worked.
932d499e-2f5f-5de7-8c85-69926bd2baf0 | note | Verification Activity: Activity - R
86614c1b-a96c-5e77-8218-5ef3f1dcead4 | note | Verification Activity: By - SE
d3ff9700-c046-4bb0-aa1a-206c1c9ff540 | checkpoint | 3.1.2 - Shear Vane
eb8d7a86-c7c4-5c00-b8cd-9ce7a00c7549 | note | Detail - NZ Geotechnical Society 2001 - Guideline for Hand Held Shear Vane Test. Fine grained Type A3 site won materials may be considered suitable for use as landscape fill providing that it meets minimum shear vane strength of 30kPa.
fc47615d-3eae-5151-98ac-c4413e5e2e1e | note | Acceptance / Conformance Criteria - Min >30KPA
109ce713-b887-5fbd-a09e-c86b3bc46615 | note | Standard / Specification - PS16.5.5
42995995-62cb-5aab-8e2c-346ef7311632 | note | Verifying Document - Shear Vane Report
c8d3e686-b50a-52ef-8222-1b1c5136ea56 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed fill per 200mm vertical ‘lift’.
4788c8aa-2f17-5a86-adc9-40a109b291cb | note | Verification Activity: Activity - R
36b9c113-480a-5762-9067-9ae6a4f8a5a6 | note | Verification Activity: By - SE
04aeec45-6acf-40d4-ac1a-aef0adc7f266 | checkpoint | 3.1.3 - Proof Roll
ef2b91af-b75f-58bf-8260-dbcae5988862 | note | Detail - Visual Inspection of Proof Roll
615dd5d6-e020-52d5-a08d-8f4c3aa8802e | note | Acceptance / Conformance Criteria - Visual Inspection
1a0d17ac-c730-5b7c-990e-e8303c69b509 | note | Standard / Specification - Appendix XVIII
d4bdaf0a-2e0e-5d01-b23f-51c8ecf9f748 | note | Verifying Document - Visual Site Record
a08850e6-08de-5ce9-bd9f-df22f4c4e6b4 | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
bdd7aa09-9e72-5ae6-95f8-fcf28af7531e | note | Verification Activity: Activity - I
e9b5e678-7b74-58a8-8f2c-121046110d49 | note | Verification Activity: By - ENG
e71c0795-e8c0-4e24-bcfe-9363c22f4806 | section | SECTION 4 – CONSTRUCTION - TOPSOIL PLACEMENT
a92b39d0-e9d3-459e-a1af-8deba1750c1a | checkpoint | 4.1.1 - Topsoil Placement on cut and fill embankments
176d7427-5e00-5955-9be9-644f2f5fd3ef | note | Detail - Confirmation of thickness and material suitability
985e9bda-f7f6-519d-b619-b4219c0d352e | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
39d89a24-94a3-5e2b-a857-b2c69092f1b2 | note | Standard / Specification - PS 16.6.3 b)
208a124b-128b-5678-8332-a67b9850d5c5 | note | Verifying Document - Visual Observation
d7bdad61-f850-5ee5-b3ca-4c01dec9c18f | note | Testing Quantity Required (based from schedule qtys) - Once per lot after topsoil re-spread
9dec7009-fe0c-5007-9cd3-1a27aa0f23d6 | note | Verification Activity: Activity - I
9f1d53be-bd27-519a-90a3-80b8c922e570 | note | Verification Activity: By - SE
b8532d23-cfbe-4812-bac6-5c6e480ab014 | section | SECTION 5 – AS-BUILTS
27cb25e4-9be1-4694-9bc8-14ea687588df | checkpoint | 5.1.1 - As-Builts
ec1b2587-20e7-5fa4-ac50-5ac630699408 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
bfe00ec1-02dc-5b18-8b0c-543ee3bdf9f9 | note | Acceptance / Conformance Criteria -
818401b3-0d18-596c-b13e-a634beb2ff38 | note | Standard / Specification - PS 16.7.6
30cb67ff-b755-5db4-a87c-fe94c02d411d | note | Verifying Document - Survey Records / Redpen markups
4f67fd81-d5a4-563d-a650-6775c82d0045 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
bcedf0cd-96f7-5ff1-be78-c407b1d3e10d | note | Verification Activity: Activity - D
43ced653-744f-5b41-885d-4346e13e247f | note | Verification Activity: By - SE
67764006-38ab-4e1b-b2e3-b5efe59f2171 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
43f340f1-c8c5-5d92-a5c2-30d25ce9a4f8 | textbox | Contractor's Rep Name:
020fe78c-de8f-5639-9a0d-ea64537ae1e4 | textbox | Engineer's Rep. Name:
7ce4bd3b-9108-54da-af53-1d5e16435c90 | date | Date:
6c3b4162-ec2b-42ac-ade4-b412cfd97dbb | signoff | Add Signature
e065a17d-81db-479d-9e6e-0454bfdc957d | checklist | DN1210-003 ITP Earthworks - Settlement Installation & Monitoring Rev 0 | itp | DN1210-003 ITP Earthworks - Settlement Installation & Monitoring
fad5ec38-f156-4a66-99cc-56afb17012c6 | section | SECTION 3 – SETTLEMENT INSTALLATION & MONITORING
4325c26c-80c8-4d4a-832b-19115f29d959 | checkpoint | 3.1.1 - Instrument Reading Notice
8c88e885-d079-56fe-8534-8a197fff1990 | note | Detail - The Contractor shall inform the Engineer two days in advance of planned instrument readings so that the Engineer may observe the work.
d03406c5-31b3-5060-a4de-f36c65dd0891 | note | Acceptance / Conformance Criteria - 2 days notice to Eng
6eca6dbd-c82d-506c-a616-43e4ceaae748 | note | Standard / Specification - PS 16.8.2
96909bf5-d670-5530-bbb4-44779f893f48 | note | Verifying Document - Site Records
0c734e60-b3ae-51b7-a0ce-fa13c209ace2 | note | Testing Quantity Required (based from schedule qtys) - Every Time
1422055b-e2a6-5068-aa83-584675f6dceb | note | Verification Activity: Activity - I
18803931-4b9b-5ee6-b7ac-0f4e0519f3f3 | note | Verification Activity: By - SE
25d05582-2766-4d3e-84ec-87f6666206ae | checkpoint | 3.1.2 - Results Submitted to Engineer
7280cb77-04ca-5925-9e1c-e9741b07226e | note | Detail - Results will be submitted to the Engineer within 1 day of reading the instruments
eaadb0e3-faac-523b-ae07-890586c144bd | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
c787a454-90af-5e3d-a494-dbc37b1988b3 | note | Standard / Specification - PS 16.8.2
32c71a89-a793-544b-8620-dfa7ed5da42c | note | Verifying Document - Site Records
833777af-a12c-5bee-8cdd-c4e02232faf0 | note | Testing Quantity Required (based from schedule qtys) - Every Time
409be5f9-136e-5d7b-ad34-f8b707ba7519 | note | Verification Activity: Activity - I
6b005556-5efc-5051-8ccd-07eb8e524412 | note | Verification Activity: By - SE
1a6ddd3e-e5cc-463a-b5e9-7c789fff5870 | checkpoint | 3.1.3 - Baseline Readings
074ea846-917a-5878-ae6c-eed5465be46b | note | Detail - The Contractor shall take 3 sets of baselines readings from all instruments at 2 day intervals
5a878dcc-b07d-5544-b00f-dc2f844aa9a2 | note | Acceptance / Conformance Criteria - Engineers Approval
9353c49e-7db4-54d3-be36-edd712367d81 | note | Standard / Specification - PS 16.8.2
a7d940fe-8995-5783-9807-25f56c50ac3b | note | Verifying Document - Site Records
ac333fb5-690f-532f-8c25-8ec5d4640e5f | note | Testing Quantity Required (based from schedule qtys) - Every 2 days
9201b6dc-5587-52c6-b250-cf10c6597944 | note | Verification Activity: Activity - I
1d3e0eb3-7487-59a2-ad53-ac06ed6bdddb | note | Verification Activity: By - SE
3575e7a3-cc2a-4906-abbb-37cea3216b7d | checkpoint | 3.1.4 - Readings During Active Fill Placement
f68e66f8-595e-592d-a748-66e2b3fc5857 | note | Detail - During active fill placement, the Contractor shall read all monitoring plates twice a week or every 1 metre of fill whichever is more frequent
755f509b-f243-52af-b5d3-b26b5b3d1be7 | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
d8f008dd-2abc-5463-a613-733698ac9367 | note | Standard / Specification - PS 16.8.2
af758653-9fbe-5a8b-b619-91b17587cfeb | note | Verifying Document - Site Records
63b514b7-7068-518e-ad80-b71c06ab6942 | note | Testing Quantity Required (based from schedule qtys) - Twice a week
915bda8a-a9a1-52e5-904f-d5f1bc444a2e | note | Verification Activity: Activity - R
6ee5c505-f87d-50a6-b696-75d7a6057951 | note | Verification Activity: By - SV
6f3e8292-276a-446a-98d4-cb5f12bdb82e | checkpoint | 3.1.5 - Readings During No Active Earthworks in Area
e6f30a42-f97d-55dd-ba7c-5322e9304237 | note | Detail - The Contractor shall read all monitoring plates weekly if there is no active earthworks taking place in the area
4ebce20d-e3a7-572d-b471-30cf96c1997d | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
3a092fb8-12ee-576d-9a78-b4ceec795cb1 | note | Standard / Specification - PS 16.8.2
f8f744d1-f6e0-5586-ae62-10fb092fc1eb | note | Verifying Document - Site Records
82f9294f-5e97-5c0d-96bd-239e7b17e694 | note | Testing Quantity Required (based from schedule qtys) - Weekly
5ab80245-646f-5cc7-b8fe-d704899e4ac0 | note | Verification Activity: Activity - R
151c5a7a-84b7-5896-99fc-740a168a8dfd | note | Verification Activity: By - SV
9b389a66-c0c8-4bde-a9f7-cb310ff7518e | checkpoint | 3.1.6 - Settlement Monitoring Termination
706d668d-86ae-5758-b976-96a0cbef5541 | note | Detail - The criteria for terminating the embankment preload are either: Three consecutive measurements indicating the t90 settlement value has been achieved, A rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed. The settlement readings shall be evaluated by the Engineer to assess the need to extend the monitoring.
af7aca07-bd9c-5b63-a39d-7957b503fe19 | note | Acceptance / Conformance Criteria - Either:
b7fe0a61-4234-55c0-8c64-21b8cb2ceef8 | note | ○ 3 Consecutive Measurements showing T90 settlement value achieved
8dc8a5fd-0159-54e1-b52d-8be00ca27ca0 | note | Or
bf452f69-8553-57d7-af73-abe62f7be910 | note | ○ Rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed
8ff71d6e-9a66-5535-85a0-314783171c9d | note | Standard / Specification - PS 16.8.5
31757f56-c6df-572d-8f76-286259498fe5 | note | Verifying Document - Site Records
2ec99de1-edcf-5b23-85ca-39924bbd94ad | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
e28f3159-1acd-5c68-893a-a5ccaebb44dd | note | Verification Activity: Activity - HP
c8ddf84e-12ee-564a-b836-66dc6a8fb2b1 | note | Verification Activity: By - ENG
186a46a9-fa61-4352-8124-f491956fa16e | signoff | AUTHORITY HOLDPOINT
3e91e37f-7a0a-42bb-ad9c-ad4818fee5cf | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
1bbbd3ff-7896-52fc-86dd-2fad382450ec | textbox | Contractor's Rep Name:
8b9685d4-de7a-5c77-b2aa-3a27feadb32f | textbox | Engineer's Rep. Name:
34c68be1-431d-52a5-a76e-90328604858e | date | Date:
1ea57cc6-cfbf-44c0-ade0-502a5af4b2f8 | signoff | Add Signature
5c175e72-73d4-4b90-8947-518f9d50e046 | checklist | DN1210-003 ITP Earthworks Rev 7 | itp | DN1210-003 ITP Earthworks
303056fd-4628-4f15-b71f-dd6773c8f7b7 | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS (MATERIAL TESTING & APPROVALS)
d2b3bff5-f06b-4fce-9f05-326e50333af4 | checkpoint | 1.1.1 - Earthworks Methodology
b54321a1-ba3d-5299-8b17-46f3fe2de711 | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points for review and approval prior to works.
3ecb78fa-ecee-50b4-b42d-8c0ee2e0bec1 | note | Acceptance / Conformance Criteria - Engineers Approval
36085e54-fa35-5052-8a25-39e2fa5faed4 | note | Standard / Specification - Appendix V
23de603c-c47a-520f-af72-8353684128b4 | note | Verifying Document - Approved Methodology
58b41e61-fda2-533c-9756-71ea7c47ec24 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
54f222d8-f404-5d04-ab3a-d711a768afa7 | note | Verification Activity: Activity - HP
71a56ecc-e5a9-5010-b833-3327f3fa0022 | note | Verification Activity: By - ENG
fac27750-aac3-4c8f-900e-4499eece46bf | signoff | AUTHORITY HOLDPOINT
fdca8724-5a24-4428-966a-2048ffaa3bee | checkpoint | 1.1.2 - Ecology Sign Off
de7cc084-8a7e-5062-8885-4beac2238b18 | note | Detail - Confirmation from Ecology that earthworks can proceed
ac74a2e1-ad78-5e1d-935f-c8b0da4460c1 | note | Acceptance / Conformance Criteria - Email
6d10bfbc-9fd6-5742-9840-91d9dfddf372 | note | Standard / Specification - Internal Hold Point
b597ccc1-b99e-5f2e-8b9c-75ff3d9cbe8d | note | Verifying Document - Email from Ecology NZ
5406859a-4cd0-501c-b631-9480c9166f4a | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
baf4db9f-241d-5d1b-ad87-0bea2c6070d0 | note | Verification Activity: Activity - H
bbe336d6-2093-5ee2-bf3d-57793b7f8984 | note | Verification Activity: By - QM
08284768-1309-487e-add9-77155722f850 | checkpoint | 1.1.3 - Erosion & Sedimentation Controls
6318f672-1100-520b-9d61-e99c9e9e2fef | note | Detail - Confirm that Erosion and Sedimentation Controls are in place prior to earthworks proceeding
9968e49b-02f7-570a-9914-a285687c8160 | note | Acceptance / Conformance Criteria - As-built Completed
4699fa64-737e-5131-a123-68bdaf5da5a8 | note | Standard / Specification - Internal Hold Point
c9a32c2a-7fd5-5fa7-85fa-660037f379b2 | note | Verifying Document - ESC As-built
a0f0541e-f9c0-53a3-90e7-f436f0b036da | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
908cb5d9-ffb9-56ca-8a17-aa18d67ead87 | note | Verification Activity: Activity - H
f1a90b54-11ef-58ca-8bbe-5ff33f2a0201 | note | Verification Activity: By - QM
731f64c5-3239-4097-b5bb-6c62a50b6ea7 | checkpoint | 1.2.1 - Weathering Resistance
9323e9fa-411b-564a-ba98-cf2381f32b2c | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
64660634-199a-5b28-81a6-c33c118708cc | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
7beeb14e-b964-5787-8301-ec00078a6856 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
78f3a799-d019-5a08-94b7-32e24708ea98 | note | Verifying Document - IANZ Accredited Report
2d49902e-aaac-51a7-8ef1-c414d16ac8d3 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
b5d9229e-0c48-5719-a2d5-406a900a5ded | note | ○ Results to Engineer 2 wks before importing
343eb87f-30de-5e46-9864-09aef9015747 | note | Verification Activity: Activity - HP
f5c08cb6-1492-5264-8582-51ed7f060d25 | note | Verification Activity: By - ENG
4586777f-85ff-4c10-b96b-316acb2c3025 | signoff | AUTHORITY HOLDPOINT
3447d2a8-001a-4182-bd12-c7ac443e36b7 | checkpoint | 1.2.2 - Los Angeles Abrasion Test
4a29c643-08f3-5082-9622-692d26bee30e | note | Detail - NZS4407:2015, Test 3.12 - The Abrasion Resistance of Aggregate by use of the Los Angeles Machine
138d02b4-aa1e-55d5-b234-5b3834189d19 | note | Acceptance / Conformance Criteria - 0.5
b55ed5f7-9d7a-5e31-b58f-1a290f3d401e | note | Standard / Specification - PS 16.5.5, Appendix V
f065e9b9-4e2c-53a6-9e3f-f78ad23a631d | note | Verifying Document - IANZ Accredited Report
5804356a-2dda-5e0d-b0b1-12580016799a | note | Testing Quantity Required (based from schedule qtys) - 1 Test Required
426ab0eb-7d43-5b24-8b31-ac4ffa1e6d3a | note | ○ Results to Engineer 2 wks before importing
2da53da6-474c-524e-9bc2-4a5cd43bb1f0 | note | Verification Activity: Activity - HP
faaa5c90-c6c6-5a9e-b5e8-943b87c8cfa6 | note | Verification Activity: By - ENG
850433b6-6282-4cb6-b5ef-63f3203853c0 | signoff | AUTHORITY HOLDPOINT
efda3374-67ed-4c3d-aab6-287f314217f4 | checkpoint | 1.2.3 - Particle Size Distribution
e5a4aaf0-cd15-5c0c-8907-01833dff0445 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
05474fc5-9854-5a7d-87b9-ec4c102492bc | note | Acceptance / Conformance Criteria - No Particles >200mm
783a80bd-3e6e-5fb5-b9a8-13fc553256a4 | note | ○ Maximum fines 10% passing 75micron sieve
3d384da6-c6b1-5fb5-bd30-9c9863950995 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
01f7afe2-fb81-52e0-ab83-b6352c6237e6 | note | Verifying Document - IANZ Accredited Report
62945f89-c600-5943-8e2d-6ac9e8f794d3 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
bc699431-960f-5400-a10a-f9792dc7848b | note | ○ 0-400 - 2 tests
54af8373-d8d8-508c-85b1-b596bbc4ad2b | note | ○ 400-1,500 - 3 tests
97bc0605-d4e5-5786-aa60-90eeb080079a | note | ○ 1,500-4,000 - 4 tests
be292f7e-3d13-5482-92d1-7ea77e965b46 | note | ○ >4,000 - 1 test for each additional 1,000m3
76edf664-22fe-5829-babf-0b0fa99faea3 | note | – Results to Engineer 2 wks before importing
94a4d334-1a17-52cf-8802-0eaad037977f | note | Verification Activity: Activity - HP
7c1439fc-45f6-5868-99e8-c9e27a8e53c1 | note | Verification Activity: By - ENG
f8037966-ccc5-4ebd-946f-55a33132a8b4 | signoff | AUTHORITY HOLDPOINT
ffdf51e2-099b-4bc3-8aa9-8eb24dc5a439 | checkpoint | 1.2.4 - Maximum Dry Density and Optimum Water Content
6a80a402-fed1-5ab4-8735-891b9b3f259a | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
3c82990a-2966-527b-a0c8-e215b8da8432 | note | Acceptance / Conformance Criteria - Report Value Only
39b6effd-914b-514b-90b9-9b378772267c | note | Standard / Specification - Appendix XVIII, Appendix V
fd9c603e-27e1-5be0-907a-846ff1715f29 | note | Verifying Document - IANZ Accredited Report
b945f03a-5a13-5655-9cc4-da40dc8b5601 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
63627248-d4a1-5770-b0d3-9292755c2945 | note | ○ Results to Engineer 2 wks before importing
e3210932-db56-5d6e-b884-b313c9a8ebc6 | note | Verification Activity: Activity - HP
6fa0668e-5f19-518e-8084-f050c0f1c71f | note | Verification Activity: By - ENG
bb65aacd-3b82-4a3e-be21-88c061eb3bba | signoff | AUTHORITY HOLDPOINT
24f31b94-c55b-4494-babc-ce41090c9bc5 | checkpoint | 1.2.5 - Soaked CBR
b0cf16ce-74ed-59f7-9550-397fcf350dfe | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
e47d4ff4-32b9-5826-8626-c7d6fe067700 | note | Acceptance / Conformance Criteria - >25%
15007102-f284-54c6-a07c-f6eeabe117a6 | note | Standard / Specification - PS 16.5.5, Appendix V
3d2d6dc5-3ea6-56be-904b-2cb62c33028e | note | Verifying Document - IANZ Accredited Report
b9e8388c-1782-56db-b8c4-4033476f45ab | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
1e27e463-22e1-5ca8-853f-0a717139d760 | note | ○ Results to Engineer 2 wks before importing
ea9cb904-fdb1-5764-84ca-226a10a2ec8d | note | Verification Activity: Activity - HP
87f00616-eed4-5200-97d1-43595bb3534d | note | Verification Activity: By - ENG
f4470fd9-abc1-446f-ad3e-fef78f8f8536 | signoff | AUTHORITY HOLDPOINT
c2d6c7c2-5225-4612-8dff-382c60b87aef | checkpoint | 1.2.6 - Solid Density
a211f159-81a4-5f16-9749-05dae1a64c2f | note | Detail - NZS4407:2015, Test 3.7.1 - The Solid Density of Aggregate Particles
c2c62408-4f26-54f7-9a9b-bfbccf0b12b1 | note | Acceptance / Conformance Criteria - Report Value Only
c7d59b1a-ee60-5807-a359-9a0417c7577d | note | Standard / Specification - Appendix XVIII, Appendix V
f984006f-54f7-5f9b-931a-bcab79f5f55c | note | Verifying Document - IANZ Accredited Report
bdb7c925-c24d-59a9-86bc-486b31c5450e | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
b76cf549-485d-531d-b3ea-293cb8c1a658 | note | ○ Results to Engineer 2 wks before importing
b05ce438-0af2-59f8-b3b9-759f7160b5ef | note | Verification Activity: Activity - HP
ad494320-e326-5fba-a3ac-cb5c0cf72424 | note | Verification Activity: By - ENG
c3fe690d-7235-47be-a001-99480fca0400 | signoff | AUTHORITY HOLDPOINT
55f6818e-9cb2-4849-9221-98695d647053 | checkpoint | 1.2.7 - Crushing Resistance
69631f1d-b15a-5123-83ef-54f9862b5520 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
f2e11580-7622-54b4-9ac8-783a08101e34 | note | Acceptance / Conformance Criteria - >100KN
90175253-7b17-5bc5-b131-5c4e93693a03 | note | Standard / Specification - Appendix XVIII, Appendix V
b674f20b-6e99-5271-a41c-09d102fd25c7 | note | Verifying Document - IANZ Accredited Report
8b64aba2-e772-546c-b5c9-cb013e73430d | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
4bd9d97e-c29b-5aa2-965b-6eb6435f984f | note | ○ Results to Engineer 2 wks before importing
4348b55b-233c-50ed-ac7e-e7f45f3d4a65 | note | Verification Activity: Activity - HP
6793ecce-2d95-52e7-b71f-365337eb94e1 | note | Verification Activity: By - ENG
8ec5394a-aad2-4dfc-8b36-587c27d32e20 | signoff | AUTHORITY HOLDPOINT
e0ff3f8b-86e6-4a82-890e-a55973b66460 | checkpoint | 1.3.1 - Geotextile
499eb3e7-03e0-5062-b030-62be8dd116da | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation.
28458302-2a22-5df8-a90f-7b56779e6e47 | note | Acceptance / Conformance Criteria - Engineers Approval
7d0ae580-4982-5307-b233-3b00ca03d6b5 | note | Standard / Specification - PS 16.5.7, Appendix V
8fcb4c15-fc6c-5141-ab20-333712a65209 | note | Verifying Document - Data Sheets
37989989-ddbf-5768-a256-7701d8dd15c6 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
b2191c4b-7492-5113-b5d3-d6f5fd86b975 | note | Verification Activity: Activity - HP
3c8026be-9dd4-5b81-a99f-4d1f23e68c42 | note | Verification Activity: By - ENG
8f593ffe-d9da-4344-ba7e-b837cefbdeda | signoff | AUTHORITY HOLDPOINT
ed62092c-d549-47b0-b12e-c3310fa876f9 | checkpoint | 1.3.2 - Field Moisture Content – NDM
87fe575f-97eb-59c6-bd14-5d18a3491384 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
c35fea20-a7fa-5896-a475-fc44cdc28c9e | note | Acceptance / Conformance Criteria - (+/-)10% of OMC
dc188f8b-6d99-56ab-a734-69762a36ac4f | note | Standard / Specification - Appendix XVIII
045f70f6-3e8b-556e-8885-dc512ebd035f | note | Verifying Document - IANZ Accredited Report
66d81f25-eedf-563f-bb0d-7988dfd0ac62 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed.
1dce2b58-a619-580e-907d-1b4a8026576b | note | Verification Activity: Activity - I
e070298b-448b-5eda-817a-b77cfa824938 | note | Verification Activity: By - SE
8479a4bd-6711-484a-b09d-c6642e6fc75b | checkpoint | 1.4.1 - Compaction - Clegg Hammer
ba185bfe-34d6-5e79-b291-84a70f101ff8 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
7d5caeb2-41dd-507c-a6a0-d68c133c07f0 | note | Acceptance / Conformance Criteria - 9 CIV
e70e7165-c595-5fda-940a-885b0634107e | note | Standard / Specification - Appendix XVIII
38dd833a-4402-535c-aff8-e7586a73f87c | note | Verifying Document - Clegg Hammer Report
35d1dedb-960b-5cde-8bf0-621462a992dd | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
6e67567b-12c7-5b09-8a45-79f9c52e1d22 | note | Verification Activity: Activity - I
b0456465-c2ed-51f7-aad0-78a59606d908 | note | Verification Activity: By - SE
b0fe2bc5-d461-454d-aab8-1ad0e2365f5f | section | SECTION 2 – CONSTRUCTION - CUT SUBGRADE TESTING
b25aad17-9f95-41bf-886b-f1c0da0f6856 | checkpoint | 2.1.1 - Proof Roll
7c44a610-aac9-546d-ad1c-92b090bfb06c | note | Detail - Visual Inspection of Proof Roll
14edfdfc-b43b-58ac-b98b-4a0dbefc535a | note | Acceptance / Conformance Criteria - Displacement <15mm
7d22d071-4a56-597d-9e7a-73d23c4d9f1f | note | Standard / Specification - Appendix XVIII
c809b721-04d8-5c18-8779-eae27b69c8c6 | note | Verifying Document - Visual Observation
4d52eab4-57ac-5952-af21-2c737a39a7c0 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
3542baac-de0f-5880-a6bc-6c9cd50d10ab | note | Verification Activity: Activity - V
b86e7420-ad3a-5f1f-91b0-491a22f9d83c | note | Verification Activity: By - SE
e548dcc7-8a77-4900-a139-c6b40bfe6799 | checkpoint | 2.1.2 - Cut Subgrade Inspection
802a779b-af0d-54a2-84c7-df8db746028c | note | Detail - Engineer to inspect all foundation surface inspections
59bc9c3e-c476-574b-a13d-fb02db0b9022 | note | Acceptance / Conformance Criteria - Engineers Approval
50105bc2-5dfe-5ddb-bab9-57eb53375e71 | note | Standard / Specification - Appendix V
09824e2e-bbe9-588d-adb9-9a78fbcc493b | note | Verifying Document - Visual Observation
1beb47c1-9206-50bb-bc42-30cb96dd8ebb | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
0a1ba364-f39a-5993-ba89-ceaefb54e321 | note | Verification Activity: Activity - HP
a67e8c7b-d622-567a-aab3-465ab576124b | note | Verification Activity: By - ENG
5d70dadb-e012-4470-98dc-e990aca6af52 | signoff | AUTHORITY HOLDPOINT
16fbda90-0633-4e65-8c39-d95196b98b3c | checkpoint | 2.2.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
b6d525d4-48c5-56c2-8b06-d1cfc55e8539 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
80053b84-2254-5a40-b848-fb77ea349b2f | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
54e9ea4c-42aa-56c7-8228-1adc3dbd732d | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
26af992f-0610-50a0-a1ff-8ba57e20ac3b | note | ○ Single Test Min SU: >50kPa
cb98c106-fb9b-52a2-bf12-ada31844efee | note | Standard / Specification - Appendix XVIII
4f61b6a4-0af1-5c10-b6a5-efe4e3223dda | note | Verifying Document - Shear Vane Report
7c8085b3-7634-5963-8c16-494660f3d2fa | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
58c9409b-a1cd-5e42-bd91-d3e150c74afb | note | Verification Activity: Activity - I
89272bcf-2ca0-512d-bf75-8d0d8c1b6aaf | note | Verification Activity: By - SE
6910f6a0-c2dd-4113-a6c4-e95816430985 | checkpoint | 2.2.2 - Cut Subgrade Testing - Cohesive Soil Scala Penetrometer
e3ef30b6-a7de-5b34-a02d-a60a9963f587 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
74681f98-af2f-595d-a145-d13ce4419e4e | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
129ddc91-515f-5059-b0cd-a2d429f67152 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
68437886-55c8-57c2-97a0-d3952a4dacf6 | note | Standard / Specification - Appendix XVIII
f2fca783-effc-562c-aff3-defa848c9c84 | note | Verifying Document - Scala Report
58f2c4ad-f5b7-57c0-aab0-990fa4c8d4e2 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
810a7b4d-1286-55a7-9455-de997a57a99d | note | Verification Activity: Activity - I
87578ed1-1259-5fdc-b531-946549b10ce6 | note | Verification Activity: By - SE
98a2275d-c6d3-4203-8622-932b785521e4 | checkpoint | 2.3.1 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
c57673b3-36aa-5aaa-a4f5-96145f5f0cb3 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
bf00692b-91c0-5550-bd48-6050455e9fdd | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
4e96809e-9c8c-5432-914e-57919538b785 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
c277027a-5318-5fa7-a324-144c992734f0 | note | Standard / Specification - Appendix XVIII
a08fb907-2794-51f2-8887-7591d38635a0 | note | Verifying Document - Scala Report
eccddbc4-f52c-51c6-ade8-0833303a51b6 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
56de6bfc-dbf2-588e-8b96-ca27b62ae385 | note | Verification Activity: Activity - I
9ff0ec38-0d65-5b1a-a3ce-9fb6739d584b | note | Verification Activity: By - SE
bb46cd09-db95-453e-933f-b090c7275d3d | checkpoint | 2.4.1 - Release of Hold Point
e2c35c78-2572-5521-9864-319a0fa57169 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade complies with the requirements of the project specification - PS 16.6
57256ee3-f62e-5996-861e-07a80056b2a1 | note | Acceptance / Conformance Criteria - Engineers Approval
de5a3679-a3e1-5f0b-a46f-3ae6793bec5b | note | Standard / Specification - PS 16.9.3
33f62c93-07fa-5df1-b596-b57b15d65057 | note | Verifying Document - Hold point released
2471ecb1-5291-569e-aa26-45e0a1a80c0c | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
ad7d1533-d40c-5d0e-99ce-647fae8cf9db | note | Verification Activity: Activity - HP
5401b672-9f9f-55fd-95af-2c6cedeaab0e | note | Verification Activity: By - ENG
f90214b3-18db-4a00-a736-e1a8bb82993a | signoff | AUTHORITY HOLDPOINT
90e576d8-cc5c-4fd7-92e3-2960aa6506bb | checkpoint | 2.5.1 - Subgrade Level Confirmation
31751713-e6ca-5720-b0d4-8f516b9f7b38 | note | Detail - Confirm subgrade is 735mm from finished height
dd204690-627f-5eb2-86f9-782fe2d570fc | note | Acceptance / Conformance Criteria - String lines - or equivalent are 735mm +0mm/-30mm
09351d8e-7d11-5e71-98c5-9513c4c6528c | note | Standard / Specification - PS 20.14.5
cb0c4664-0fd2-582b-9fac-1095cc5641c2 | note | Verifying Document - String Sheet
5e3b7a11-2f6c-5b0e-adfe-302686547bce | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage
5bcc0761-2a2d-5bdc-afa4-a45f5f706abd | note | Verification Activity: Activity - I
07544134-ee67-5742-aa15-ecff47c57209 | note | Verification Activity: By - SE
bd03d26c-f49b-42a6-b5df-049394ab4049 | checkpoint | 2.5.2 - Subgrade CBR Testing
eb2abe03-3b62-59ce-b773-f65d8d0cb364 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
18345c87-655b-591c-96fd-55b5f89d9f8d | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
233be916-a020-580e-bdef-15039726e1b5 | note | Acceptance / Conformance Criteria - Pavement Type 1
cf7071d8-6519-5dd4-9ab2-f17eadeb4f09 | note | – CBR >6
4ee83d8e-5f05-557c-bd90-73bfd7018c27 | note | – Min 3 blows / 100mm
97c0d418-8b27-5c24-97c2-d6aa124028c2 | note | ○ Pavement Type 2, 6, 7
2a30d082-745e-5208-815b-aad55a904971 | note | – CBR >2.5
fc6a4d4d-fab9-5c41-b97b-f65484234045 | note | – Min 2 blows / 100mm
70b4c641-9cd1-5976-b2bd-66a824d21548 | note | ○ Pavement Type 3, 4, 5, 8
04cd5ab5-a2c7-5aed-b5d7-c07a6e2498ca | note | – CBR >3
1af515a7-e2df-524a-be8a-321faa83c230 | note | – Min 2 blows / 100mm
df511d36-8c75-53da-851a-f6a25cd35646 | note | Standard / Specification - PS 20.4.1
035298bf-e34f-5501-a5cb-961fc581cfda | note | Verifying Document - Scala Report
890bc04d-8045-5eda-abc6-f47351870744 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100M2
f2616a21-4e62-55ec-92ce-1fb6748ffe13 | note | Verification Activity: Activity - I
6cad3431-aecb-5574-81f3-c268475e72d7 | note | Verification Activity: By - SE
69b4c20b-b692-414f-9292-fd600c88bad6 | checkpoint | 2.5.3 - Release of Hold Point
8ddd67c6-ace5-5871-affc-505da18d001c | note | Detail - To release the subgrade hold point and be able to start placing pavement layers, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
2634c5bc-2fa9-50cc-a0c1-24a7412ebbb0 | note | Acceptance / Conformance Criteria - Engineers Approval
57f5350b-d90a-5c16-b167-e0b82030a2c4 | note | Standard / Specification - PS 16.9.3
e3489ad1-dc7a-5654-924b-1520fabca738 | note | Verifying Document - Hold point released
41b6c4a2-875e-5fe5-93ec-34e4fd28b080 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
03743c6b-1193-50e0-b283-c10b6f9c0f12 | note | Verification Activity: Activity - HP
ab30ef15-d65e-5e96-833e-816d96620267 | note | Verification Activity: By - ENG
4b3a292c-5e2c-4592-bf22-ecf0a17bc575 | signoff | AUTHORITY HOLDPOINT
e3838121-13aa-456e-ab15-cb42ae242859 | checkpoint | 2.6.1 - Release of Hold Point
a9272ade-1f15-5893-8405-61ba1b7e1507 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
170c4c56-6bfd-5526-8829-62c778c5919c | note | Acceptance / Conformance Criteria - Engineers Approval
25b59fca-5824-55ea-8831-7c8883b27644 | note | Standard / Specification - PS 16.9.3
6e5e0851-dc28-5001-8b66-def9acb6068b | note | Verifying Document - Hold point released
d17ce4fd-6858-586d-a868-2c409a653898 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
3321fb00-22af-52ab-ae26-64f76d924342 | note | Verification Activity: Activity - HP
96126ca6-f571-5b96-a0c8-f00856c79af2 | note | Verification Activity: By - ENG
d6d021b3-b559-489b-b10d-9dc88d525c9d | signoff | AUTHORITY HOLDPOINT
b85c944c-29db-45cf-98aa-18d7c5d46f27 | section | SECTION 3 – CONSTRUCTION - UNDERCUT TO WASTE & BACKFILL
d85b9ad6-dbe5-42ce-bfea-135c90bc50c1 | checkpoint | 3.1.1 - Undercut Surface Inspection
cd33c94b-cfcc-5375-ac11-a5424f1b1d06 | note | Detail - Engineer to inspect undercut surface
55db45b7-85f1-5ffb-94b2-ba0f73ea8c2d | note | Acceptance / Conformance Criteria - Engineers Approval
b77a59b3-041a-5b1f-a967-68165ce41cbe | note | Standard / Specification - Appendix V
d743ad26-3a6d-533c-86e2-8878d5b16570 | note | Verifying Document - Engineers Approval
1a9fa6f3-91c6-55dc-88d9-419eb2abd59f | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
d8f9c1f1-b971-54d4-b0eb-6cf46bef6595 | note | Verification Activity: Activity - WP
492085f2-dba0-5904-9245-a9f1260ad2c8 | note | Verification Activity: By - ENG
dd4d6de1-af98-486e-8ccc-9e9d980df449 | checkpoint | 3.1.2 - Placement of Geotextile on Undercut
401d021e-fc97-512f-af2f-085193ffc4f1 | note | Detail - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
c0ed44c6-777d-56ae-a8f8-f5558d16a49f | note | Acceptance / Conformance Criteria - Engineers Approval
72ae6244-2dd7-5c94-80f2-2d25a8ec3ba0 | note | Standard / Specification - PS 16.6.4, TNZ F/7: 2003 8.3
d37b9680-c0ba-530c-9c7e-8e36543956a2 | note | Verifying Document - Photos
3c5918f8-cf4a-52de-9a2c-442afda763d4 | note | Testing Quantity Required (based from schedule qtys) -
85fc08b7-6e40-5d73-b346-26f5a64b5f32 | note | Verification Activity: Activity - WP
ac469fa2-0bcf-5ab9-873e-3eb4dc5de405 | note | Verification Activity: By - ENG
72f8681a-a3da-440c-bae2-b07d39be9e4d | checkpoint | 3.1.3 - Subsoil Drain inspection
4413dc54-09ed-58bb-9b6d-af26a609b767 | note | Detail - Subsoils to be placed at base of cuts where directed by the Engineer
d8767c0f-6b70-5a97-93a5-105495d9cc72 | note | Acceptance / Conformance Criteria - Engineers Approval
9ba6c479-87af-5157-a341-ac8fcf3015be | note | Standard / Specification - PS 16.6.4
4eaa83af-1112-5e89-ab2d-8ac1c45c7769 | note | Verifying Document - Photos
39ffe601-51f0-5b23-a77d-044b3d051ecf | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
27c5b002-4dd5-57a5-a14f-7d5f6c496170 | note | Verification Activity: Activity - WP
91741e7b-81eb-572f-a343-e872ff509c2b | note | Verification Activity: By - ENG
501ba117-3dad-478f-84d0-648246f93493 | checkpoint | 3.2.1 - Release of Hold Point
bfa29bb4-58da-5d2c-a3f7-295303333eba | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
e2720518-6484-5917-add2-4c765cc25618 | note | Acceptance / Conformance Criteria - Engineers Approval
344b9972-a7de-537c-b292-2dae112896d9 | note | Standard / Specification - PS 16.9.3
4049e86b-b61c-597d-8d5d-ed21edbffb5f | note | Verifying Document - Hold point released
c105c5cc-629a-5f68-838e-af983d196363 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
d3e715cc-f759-523e-a3e1-b788374aa11b | note | Verification Activity: Activity - HP
026a6091-33bc-543d-8d0c-07d2d35af0a6 | note | Verification Activity: By - ENG
25543144-e012-4919-8f7a-ddc6e33036e9 | signoff | AUTHORITY HOLDPOINT
05f763ae-27dd-4b10-92b7-f2447437a290 | section | SECTION 4 – CONSTRUCTION - COMPACTION OF IMPORTED FILL
1a477d7f-bb1b-46a9-b7a1-860a2a9e22dc | checkpoint | 4.1.1 - Placement of Geotextile
509b6537-0099-555a-b2da-737ff8bc4097 | note | Detail - A layer of Class B Geotextile Fabric to be placed between cut surface and imported A1 Structural Fill with 500mm overlaps
6acd658d-028c-5fbb-97d0-ba3aea8a65d7 | note | Acceptance / Conformance Criteria - Visual Inspection
a05a9376-7bfe-525d-bb25-382152137661 | note | Standard / Specification - NTC084
de7feb83-e69e-5a24-8362-626ee0358e04 | note | Verifying Document - Visual Observation
6ec7b33b-2a07-518f-b44f-b8b30ae86dbe | note | Testing Quantity Required (based from schedule qtys) - As Required
1badb84d-979c-55cb-aa73-2f640f763d31 | note | Verification Activity: Activity - I
5a96edd8-3047-5ac3-a92f-bc23c02f8424 | note | Verification Activity: By - SE
6c38888a-71d0-481f-ac4c-cb0ab1a3ab2b | checkpoint | 4.2.1 - Compaction - Clegg Hammer
738f7f59-087d-50ef-ab2f-8a547c87943f | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
dd0978f6-bcac-5122-aaf9-4e487b4d4339 | note | Acceptance / Conformance Criteria - Structural Fill
052f008a-2922-5eec-ba5f-a788adc8d4ff | note | – Min CIV 18
1138f60e-6b87-5eb1-9b09-feb617c07f4e | note | – Ave CIV 20
7b793600-6db1-59f5-ba6b-a7902e72004c | note | ○ Non-Structural Fill
dab79e9a-7aa5-5591-b2e9-7e763b03e92d | note | – Min CIV 10
c33b7681-e3fe-5df9-8674-70e1b61ad771 | note | – Max CIV 12
bd04d59a-d4a4-566c-b7f1-755d8b16d681 | note | Standard / Specification - Appendix XVIII
e0c01415-20a1-5157-b360-321a750c66c8 | note | Verifying Document - Clegg Hammer Report
298cc7ca-0e6d-5bc8-b3f0-20a801d63ce4 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
6ec4df28-6db8-546b-8ae9-dfb41a4249c0 | note | Verification Activity: Activity - I
f3ae9792-731d-5782-ab5e-1a15e4ddeb81 | note | Verification Activity: By - SE
3fe4601e-c0aa-4383-8ce6-88d90bb98957 | checkpoint | 4.2.2 - Compaction - NDM
4ebf5a77-d909-5f7f-b8eb-e001765a459d | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
2bf190d6-4993-5e6b-8dfe-733c53f1bd0d | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
31c663b8-86b3-5063-9ce4-500a0924bc82 | note | ○ Non Granular Material
a01b40fe-d860-5f8d-879c-bcb2c60788bd | note | – Max Air Voids 8%
863d9c7f-cdf4-51cb-a834-cd27b3b4326a | note | Standard / Specification - Appendix XVIII
4a1c1302-07b3-53dc-8495-b9e09b23448e | note | Verifying Document - IANZ Accredited Report
2cd10ec3-273e-5366-b5cd-6f326eaf7c43 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
4903f512-9540-5764-adbf-0535c70de76e | note | Verification Activity: Activity - I
20faa1bf-d90f-5f5f-90ca-e59b02087600 | note | Verification Activity: By - SE
41b823e2-1640-43b3-a1a9-ac174fbb8289 | checkpoint | 4.2.3 - Compaction Trials
436f8cf1-ffff-5577-8c1b-1b119bff09ee | note | Detail - The Contractor shall carry out compaction trials of the various soil types and combinations on site, and any imported fill materials, using different layer thicknesses, types of rollers and conditioning plant (ie construction discs and scarifiers). The trials shall be conducted over the duration of the earthworks operation with the objective of determining the most suitable and efficient techniques to meet the compaction requirements. The trial details, test data and conclusions shall be reported and copied to the Engineer within five days of completion of each trial.
05a703ae-00d4-502d-9bdb-9801d8149c75 | note | Acceptance / Conformance Criteria - Engineers Approval
a2cb9619-9ca3-5760-91e7-d42e0a5b898c | note | Standard / Specification - PS 16.6.5
8b2f1700-277a-5199-9e39-bd99117960cc | note | Verifying Document - Trial Results
707538c8-e68a-514a-a62d-63af7aee88f3 | note | Testing Quantity Required (based from schedule qtys) -
63b41250-9606-5605-b4f9-56ef41123643 | note | Verification Activity: Activity - R
3815bfc3-a198-5f87-8c8a-7e95d182f36c | note | Verification Activity: By - ENG
64908577-c580-4600-9123-29a2f7c55f35 | checkpoint | 4.3.1 - Compaction - Structural Fill Scala Penetrometer
5dfac380-27a7-54ed-b302-72cfc94b7580 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
eb02f41c-b099-587b-b555-dacced7fec8c | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
2b803d1b-466f-5b9c-98e1-49925e2df4a8 | note | Acceptance / Conformance Criteria - Minimum 5 blows per 100mm penetration
c93696e8-ffb0-51ab-93d3-013cba0b4a4e | note | Standard / Specification - PS 16.5.12
7662651f-bf37-56cc-b262-47d16110be7a | note | Verifying Document - Scala Report
16225484-c0d2-521a-9d47-c4da947e66f8 | note | Testing Quantity Required (based from schedule qtys) - Minimum 1 test per 500m3 of filling evenly distributed over the extent and depth of the filling. A minimum of 1 test per 500mm lift or part thereof to be completed through the full lift thickness.
c5e187bb-4939-5046-b8a3-de1db913c0c4 | note | Verification Activity: Activity - I
941a690d-888c-5135-b282-7f40fc897295 | note | Verification Activity: By - SE
16da8ce6-3eb3-4aa2-9c0f-cb5326e9ccb1 | checkpoint | 4.3.2 - Compaction - Structural Fill NDM
1ea87b41-922e-51f7-bbac-f5ac49ba7823 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
726ca3dd-365c-5aab-b1ed-f9d261e569f7 | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
d8cd8c27-2381-539a-a3aa-8c7b795c7a2b | note | Standard / Specification - PS 16.5.12
3b0d2f79-2139-5eb2-bd30-a1c43ce71b18 | note | Verifying Document - IANZ Accredited Report
f244003d-f71c-5484-badf-ae6e7db3eb92 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
f00e77b8-6f2b-5583-bc9a-d678ccbee5cb | note | Verification Activity: Activity - I
d24709ba-b704-57e7-90a2-470f066486ad | note | Verification Activity: By - SE
8a61aab7-dfc3-44ca-a986-6dcb1bad7ec4 | checkpoint | 4.3.3 - Pumice Sand Fill
a860a83b-830f-5cb4-920e-424879252086 | note | Detail - Pumice Sand Material shall be contained with an outer layer of fill with a minimum thickness of 600mm. Must be Hardfill and/or imported Type A1 material and/or Type A2 material and/or Type A3 material
818594b2-876e-5de4-9378-cb53c10acb54 | note | Acceptance / Conformance Criteria -
f433b870-5d84-5f10-834a-6cf43350b69c | note | Standard / Specification - PS 16.5.12
4c164150-3d89-5b28-b719-3f3727bfa48b | note | Verifying Document - Site Records
f0074700-70d9-548e-af59-3a8651186146 | note | Testing Quantity Required (based from schedule qtys) -
cb959169-fbdf-51ac-b2b6-a7a29ee4b133 | note | Verification Activity: Activity - E
d8b0615b-e718-5a4d-a4c1-d25cd6f35b6d | note | Verification Activity: By - SE
de6ca4ae-557b-4d21-a6bf-aff6d3c9aada | section | SECTION 5 – AS-BUILTS
82f88d2c-afa4-4b25-a0cb-97c4f1ceed3d | checkpoint | 5.1.1 - As-Builts
e953a216-b3c8-56bb-a727-4feee46a2dd0 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
f0cfb15a-dfdf-5596-a741-16283765dcb6 | note | Acceptance / Conformance Criteria -
907821e5-8148-5e0a-9a11-3d58d3ba82f5 | note | Standard / Specification - PS 16.7.6
54bf521d-ef3a-57c9-b5f2-bb3a645e8d34 | note | Verifying Document - Survey Records / Redpen markups
d7286cc2-32ae-5d9f-8935-f2877bb578f6 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
6ecb3006-2660-5a36-a033-a58c1ad4de38 | note | Verification Activity: Activity - D
80702710-d31b-5c91-9d3c-e823087a4ab7 | note | Verification Activity: By - SV
bb3b2017-5215-4a2d-af74-4df7b9be66d1 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
1476d4ad-8734-592d-a70a-9630d7e1cf97 | textbox | Contractor's Rep Name:
ccdcf735-5e01-571e-af47-f4a0514e45c8 | textbox | Engineer's Rep. Name:
45799344-c8bb-5d8c-a127-4eeca12894d5 | date | Date:
77d64376-76f5-4734-b1b4-312475957ff7 | signoff | Add Signature
e8a51180-e519-5178-a260-808bdd591ab6 | checklist | DN1210-003 ITP Earthworks Rev IFC5 | itp | EAR-DN1210-003-LOT-001-Zone 1 North-A
8508ff53-5f3a-5f4c-8d26-a8afd00d3eae | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS
fa40f6b3-5282-5e90-aaa6-c7c2328827d1 | checkpoint | 1.1.1 - Earthworks Methodology
0d104855-89f4-593a-85bd-a50e0fe9215f | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points for review and approval prior to works.
25a842ae-f368-56bf-896b-35fc18939be2 | note | Acceptance / Conformance Criteria - Engineers Approval
bcf47cec-4f3a-530c-9d04-d1129bd3fe6a | note | Standard / Specification - Appendix V
37a6a238-f616-5b99-a3c7-9f3188b36a68 | note | Verifying Document - Approved Methodology
39b5f231-e8ac-5ae7-ae5b-1d3a6d1a3e2c | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
7fc060d6-a7d5-5929-b685-00c4c82f5444 | note | Verification Activity: Activity - HP
de17480b-9985-509f-b3bc-3d9282f4410e | note | Verification Activity: By - ENG
0810d078-72c3-5cc9-b875-7cd778a6935d | signoff | AUTHORITY HOLDPOINT
f4cd2823-6ed1-52de-8392-a796d0472357 | checkpoint | 1.1.2 - Ecology Sign Off
cab789a8-b93b-5ae2-8087-75845ee54abf | note | Detail - Confirmation from Ecology that earthworks can proceed
56e8fc5e-abb4-53f4-95cd-424f70f8dea3 | note | Acceptance / Conformance Criteria - Email
54b8b3a8-a4b8-5826-84b2-0394718c82c0 | note | Standard / Specification - Internal Hold Point
5b86395a-bf45-5246-af35-80455d218425 | note | Verifying Document - Email from Ecology NZ
c89c534e-0044-576a-bc67-1065b357bdfd | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
2ea624cd-7e2b-5a5c-8310-b435b1f9d82d | note | Verification Activity: Activity - H
4714b52a-304b-57fd-a3c9-afe336ad757b | note | Verification Activity: By - QM
efd14769-e8c6-51fc-8d27-f504bf699318 | checkpoint | 1.1.3 - Erosion & Sedimentation Controls
90189df5-862e-578d-ac66-0cec0908d406 | note | Detail - Confirm that Erosion and Sedimentation Controls are in place prior to earthworks proceeding
60bf084c-2ef1-5d5d-bb11-3730f8061b1c | note | Acceptance / Conformance Criteria - As-built Completed
e50e3322-03bc-5b50-a82f-b1b5726dfa72 | note | Standard / Specification - Internal Hold Point
a6624630-2f33-5e2f-9195-8980356dc0db | note | Verifying Document - ESC As-built
eccc1421-408d-5927-9abf-dafa4be2987d | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
98deee31-b439-56dd-bbc4-ce083ff8680d | note | Verification Activity: Activity - H
54de11cd-f76c-5415-91b9-aecf8d005251 | note | Verification Activity: By - QM
0d87e467-4cb2-552a-ac73-f66d3a3d9150 | checkpoint | 1.2.1 - Weathering Resistance
455b43de-ffc1-5af2-a1de-cf40fa18ea41 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
f8552aff-4b9f-5d2c-a904-d6da94d55840 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
303ebd44-48a4-571f-842c-465066d59d51 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
f35bdac5-7335-562e-a47e-19736f7337b6 | note | Verifying Document - IANZ Accredited Report
f5d5ff0f-2b7c-5113-b628-c021affab5ff | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
8fe01f64-c7b3-59ce-8bdb-e04d432f27e1 | note | Verification Activity: Activity - HP
27b4c96d-f6f1-577e-832e-aca2fad4548c | note | Verification Activity: By - ENG
b743bb5e-1c16-53b6-b8bc-16628422b606 | signoff | AUTHORITY HOLDPOINT
084e82bd-1f23-51d2-8dc8-d681090cbe21 | checkpoint | 1.2.2 - Los Angeles Abrasion Test
6d44388d-ed58-540b-ba94-b9114a6f53d0 | note | Detail - NZS4407:2015, Test 3.12 - The Abrasion Resistance of Aggregate by use of the Los Angeles Machine
6af9c5f7-9082-58c6-a445-b02aea78da9a | note | Acceptance / Conformance Criteria - 0.5
81f1e4c6-0496-593b-aaf7-2460f9b0bc05 | note | Standard / Specification - PS 16.5.5, Appendix V
83bdb4ff-97b9-5efb-bb6b-0afeb201ad98 | note | Verifying Document - IANZ Accredited Report
2233790e-3df5-58d8-950c-3a824e566622 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Required, Results to Engineer 2 wks before importing
4e604921-3ac9-5f94-aa82-22b57f94de55 | note | Verification Activity: Activity - HP
147b59c3-fe37-534c-9bbb-5d24fd9d31a4 | note | Verification Activity: By - ENG
8bc26f80-2039-56bd-bb37-e46ffc1c9fe7 | signoff | AUTHORITY HOLDPOINT
d93131df-e262-5431-b317-9d9d9006e3ee | checkpoint | 1.2.3 - Particle Size Distribution
a247f6ea-c2f1-5c89-a542-e6c3b691162b | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
a5ae7ee5-97af-5ab1-a4a9-f34f0615fc4a | note | Acceptance / Conformance Criteria - No Particles >200mm, Maximum fines 10% passing 75micron sieve
30c42a9c-5468-5ddc-8294-ee4b44b237fe | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
af373d42-19f1-5ebe-9a47-dee81487a830 | note | Verifying Document - IANZ Accredited Report
1107cdc3-faec-5731-a82c-a43b17dd3fb0 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
a1e0c85f-e622-50ce-9b8b-a2a1ff24b887 | note | ○ 0-400 - 2 tests
77c7929e-be41-5f74-9c23-69d4baa66048 | note | ○ 400-1,500 - 3 tests
81c9e55d-68ec-593b-955c-8cfe75a66d11 | note | ○ 1,500-4,000 - 4 tests
c8a6f68a-17d0-57ec-873e-fdf59f3bd15f | note | ○ >4,000 - 1 test for each additional 1,000m3
e8a86c27-404e-5dcf-ad75-7093fad8fc25 | note | – Results to Engineer 2 wks before importing
cea069ba-656a-5d8b-a896-3a16bc7a2650 | note | Verification Activity: Activity - HP
7fddd767-f5a6-5c7c-b124-9737d1789702 | note | Verification Activity: By - ENG
cfc336bd-ca9a-5b9e-abd3-a9fa9f2c427e | signoff | AUTHORITY HOLDPOINT
2291f8cc-7920-56fb-b158-84bfdf300c25 | checkpoint | 1.2.4 - Maximum Dry Density and Optimum Water Content
e3bb3786-dfb5-5944-80d0-3bca0eae2690 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
c9c03eee-c3c6-5b8f-bf85-9c8cc2963a5a | note | Acceptance / Conformance Criteria - Report Value Only
735a4b90-cf66-5701-b2ec-83c51d897255 | note | Standard / Specification - Appendix XVIII, Appendix V
b6933e85-9e77-5e0d-ac53-02b2bb6ed28a | note | Verifying Document - IANZ Accredited Report
c90cab11-e5f8-5e38-af10-b817d24bac03 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
e92c2404-f896-5eb7-96ad-0389257f7de1 | note | Verification Activity: Activity - HP
ddbd66dd-516f-5c64-9c78-5a56b46248bd | note | Verification Activity: By - ENG
575e78dd-342d-5a92-8d82-7739e63face1 | signoff | AUTHORITY HOLDPOINT
f1395031-71d6-5468-bf80-c760a6ab6370 | checkpoint | 1.2.5 - Soaked CBR
405d3666-c324-5372-8944-f29095b45593 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
8b3db5d7-2af7-5ece-82a4-c56b78a1e74d | note | Acceptance / Conformance Criteria - >25%
b9dea11c-5f41-58bc-ac45-51cb9785a966 | note | Standard / Specification - PS 16.5.5, Appendix V
a0188409-65e1-5017-ae63-28794e961176 | note | Verifying Document - IANZ Accredited Report
5d8ecde9-fa21-58ca-b177-86a352aeb58b | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
4568dd7f-8d2f-5e6f-b936-479b8a1f7dee | note | Verification Activity: Activity - HP
a85d81f3-c063-51ca-8606-a7cf85fcdc13 | note | Verification Activity: By - ENG
931a1aa8-1380-5a21-bb4d-7282459c2c4a | signoff | AUTHORITY HOLDPOINT
51757bfb-8689-56b5-85cc-9ee5c479f783 | checkpoint | 1.2.6 - Solid Density
86feadec-2cf4-54f2-92ca-451a5718cf11 | note | Detail - NZS4407:2015, Test 3.7.1 - The Solid Density of Aggregate Particles
c0c95f97-4b89-571b-9b8a-3eb659c2137c | note | Acceptance / Conformance Criteria - Report Value Only
4b795ca1-e4f8-5e95-b7aa-b41b5ce72d32 | note | Standard / Specification - Appendix XVIII, Appendix V
6af41c27-9d65-5220-96d6-422dfba7bede | note | Verifying Document - IANZ Accredited Report
0e33c057-1ab0-59b0-aa65-0d9e4596204e | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
e70b4675-8a59-557b-bc32-7e541f2bcb2c | note | Verification Activity: Activity - HP
4c5917fd-dd41-5f03-8fb8-0d49e52f5baf | note | Verification Activity: By - ENG
4ff72493-ec09-5550-980d-b8ce9f81958c | signoff | AUTHORITY HOLDPOINT
f3c7ffc2-519c-5933-8152-8d50f951f298 | checkpoint | 1.2.7 - Crushing Resistance
e3895585-b89f-5ff3-a848-8bd602992717 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
7c707ea0-5bf2-515e-851d-5a872650e550 | note | Acceptance / Conformance Criteria - >100KN
a86e42bb-c961-58ca-8d7d-2f2810d541fe | note | Standard / Specification - Appendix XVIII, Appendix V
789dae34-e3d8-59c1-baea-43317b01c78d | note | Verifying Document - IANZ Accredited Report
9a719381-f8b5-5c9c-a7d3-f70743da7f1d | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
c8ea3b12-2b63-57ab-8fb2-bdc4261830b1 | note | Verification Activity: Activity - HP
37d17fc2-2563-5cf7-885a-aaded160a990 | note | Verification Activity: By - ENG
18198a09-45c8-58df-b28e-13ce7c3dc8f8 | signoff | AUTHORITY HOLDPOINT
d14ec928-f5ca-5c95-8a07-42e01557e8ce | checkpoint | 1.3.1 - Particle Size Distribution
5500a823-de90-5fae-b654-46fac739d405 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
fb118fa7-7067-5703-a701-3521776172af | note | Acceptance / Conformance Criteria - Report Value Only
c0c1507c-ef34-5ff8-b5f2-2d67df5faa81 | note | Standard / Specification - PS 16.5.12
f629e6c6-6c58-5b68-b3c7-f663ac7e7ecd | note | Verifying Document - IANZ Accredited Report
3f63d8cf-77d4-5e1f-898e-de00f21d5404 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required?
e989a096-c208-544e-b3d3-79a5413d7251 | note | Stockpile size:
b2fc4c02-b88c-5191-860a-8fd102257e24 | note | ○ 0 to 400m3 – 2 tests
b9c060e1-3635-5a39-abe6-32c06bcaaf86 | note | ○ 400 to 1500m3 – 3 tests
2bf659e3-f2c6-5582-9b7a-6b45dc6096c5 | note | ○ 1500 to 4000m3 – 4 tests
77c86e10-7365-56fd-b6e4-4d3cd7293646 | note | ○ >4000m3 – 1 test for each additional 1,000m3
2e4a7d5c-6504-5210-b630-49aee01502f6 | note | – Results to Engineer 2wks before importing
98a632fe-7838-5415-83bf-bcdbcd57418d | note | Verification Activity: Activity - HP
40ab8af6-15c9-56b6-9825-58a59e44fc21 | note | Verification Activity: By - ENG
3e090f90-6d14-5042-ae03-d0f85981b5d0 | signoff | AUTHORITY HOLDPOINT
33862698-337a-599f-92ba-d701669d85d9 | checkpoint | 1.3.2 - Maximum Dry Density and Optimum Water Content
56d35ba2-765a-58eb-847e-ecb2a74da5e3 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
ac589409-3515-5145-898d-cce30efe5571 | note | Acceptance / Conformance Criteria - Report Value Only
e434a1b1-a134-552e-87c8-633a2375f5fc | note | Standard / Specification - PS 16.5.12
c30be714-03f2-52c1-b30d-506b1280e513 | note | Verifying Document - IANZ Accredited Report
9d9e5a1f-8a0b-550a-b5eb-12e72cf9c410 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
05cd823d-e183-52a6-9e4f-fe4022db5aaa | note | Verification Activity: Activity - HP
1136acd7-a8da-533f-8fdf-30e0d8cd75b9 | note | Verification Activity: By - ENG
a211f4ec-e2a7-5d58-86a4-27239dd6b739 | signoff | AUTHORITY HOLDPOINT
b6a22ad6-5fc9-58a1-a864-f178b18a9095 | checkpoint | 1.4.1 - Crushing Resistance
16c2530f-9a49-54de-8328-b7d6d3aa0ffd | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
aa510cf1-5dec-5617-8513-48cf38aa40c0 | note | Acceptance / Conformance Criteria - >100KN
b3e554f2-3531-538b-be07-66f41752baf6 | note | Standard / Specification - Appendix XVIII
e05b8394-37d9-5b43-970a-2b3f5a2d638c | note | Verifying Document - IANZ Accredited Report
8830ac9f-4dbe-5315-ad7f-39f34c3d3407 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
9dfbdb6f-bc40-5bdf-ad5b-3ccf30f3ffee | note | Verification Activity: Activity - HP
d65ba4d4-1351-57c0-ade1-641d6be463ea | note | Verification Activity: By - ENG
a398b73d-efa3-5256-ae85-9411c1e2ca37 | signoff | AUTHORITY HOLDPOINT
3f788f51-4f7d-5c69-b850-f5390fcb2c2e | checkpoint | 1.4.2 - Particle Size Distribution
7c63cec1-d77f-571c-82f5-f04a3fe85bd3 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
e257efc7-a9b0-583a-927c-7cc989ea73ff | note | Acceptance / Conformance Criteria - Max Particle Size 53mm, Max 10% passing 13.2mm sieve
080b8c60-2510-5f1d-a9bc-62fd78e805d6 | note | Standard / Specification - Appendix XVIII
20af941c-9c90-5052-83f2-a997a07fd26a | note | Verifying Document - IANZ Accredited Report
3d076029-5037-5ffe-b7b7-a4d803a2cbd1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3, Results to Engineer 2wks before importing
f3cc4b76-e86e-5cd5-b78b-2cb413dedc6e | note | Verification Activity: Activity - HP
aa4e1f07-9947-5ccc-9368-37ecdbc742e1 | note | Verification Activity: By - ENG
ad8b4c0a-d700-5a74-8728-bbff13e996d3 | signoff | AUTHORITY HOLDPOINT
3356783d-4613-55b3-837d-756350b0e3a3 | checkpoint | 1.4.3 - Weathering Resistance
ea32fa72-b426-5fce-8499-e60b73cb0cc0 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
d53186d9-99b3-50e1-ad38-3116af32fdb1 | note | Acceptance / Conformance Criteria - CA or better
43cc3027-84d8-5f0a-968c-6a110e28fc24 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
56a7ef2d-1538-5382-ab04-2a5d78ce4f43 | note | Verifying Document - IANZ Accredited Report
45a931e4-c16b-5b2d-a219-99b82043c1a7 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
4f11e08b-a428-5496-9f61-7f9fefa86fee | note | Verification Activity: Activity - HP
8cd1c7e3-2ff9-5744-aeff-4108c6661726 | note | Verification Activity: By - ENG
ead9a554-7f33-5535-8618-d239ca258e84 | signoff | AUTHORITY HOLDPOINT
cfa973b9-821b-5366-9e96-aef5debe1f37 | checkpoint | 1.5.1 - Geotextile
3a88df61-3f1a-550c-94d9-b7af2c87bf57 | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation.
f32ac2fc-585f-5298-ad31-f1bf364ebe5f | note | Acceptance / Conformance Criteria - Engineers Approval
e40b5f84-336c-54fd-acce-915b13a43f8b | note | Standard / Specification - PS 16.5.7, Appendix V
a7859f63-d29a-5e59-b2c7-0459b955ea14 | note | Verifying Document - Data Sheets
43e247ac-a68e-5bc6-8e38-943217724484 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
981ea3d0-0edc-552d-b40f-7a710ccf5c87 | note | Verification Activity: Activity - HP
5ecb55bf-6dd3-5a7e-8b3a-5a025ad69587 | note | Verification Activity: By - ENG
c9f84dd4-62d1-5a68-a153-52aa059ba6e2 | signoff | AUTHORITY HOLDPOINT
a870b3cc-abd4-5d52-8269-fe725225c68d | checkpoint | 1.6.1 - Laboratory Testing for Soil Suitability
010d3206-ba9e-55a2-96ba-898263e8f9ac | note | Detail - Soil Test Results from Hill Laboratories to confirm that topsoil suitable to for reuse
a40d8b74-816d-5384-858a-37018196f028 | note | ○ Soil Reaction
8a17c5bb-8886-5ba2-b97f-dd797a8bf017 | note | ○ Electrical Conductivity
ac7eb074-bf3e-5c77-b56d-1d9e06434a0d | note | ○ Mechanical Analysis (texture)
501fa943-68c2-57b5-8881-80661b33f270 | note | ○ Stone Content
cdd2f9e9-e38f-57da-a77b-76810a24894c | note | ○ Nutrient Levels of nitrogen, available phosphorus, available potassium and available magnesium
228916c7-3c91-52ec-9095-02bc4182f6ff | note | ○ Organic Matter Content
d3ae7535-eeb1-5748-8d1f-40ad3e815a0f | note | ○ Check for Toxic or Hazardous substances
599b7b46-d953-52ac-9a14-61415586f08d | note | Acceptance / Conformance Criteria - Engineers Approval
580f54ed-bd7f-5fa6-9e96-4f1eee364204 | note | Standard / Specification - NZTA P39:2013 3.1
e58a48e4-074e-5419-b8f4-c5115d268738 | note | Verifying Document - Hill Laboratories Test Report
bca7e7ce-8f0c-5c46-bbe7-9c9b00e3649c | note | Testing Quantity Required (based from schedule qtys) - 10 equal samples taken from site, mixed together, then 1kg of soil sealed into a plastic bag and sent to lab for sampling
4caf85c5-b3d1-51f2-ae8a-4eacde45cd51 | note | Verification Activity: Activity - I
5fdd1e21-9457-50e5-a7b9-3ccd39339507 | note | Verification Activity: By - SE
4df8d327-6e97-5620-a77a-66465636c9d2 | checkpoint | 1.7.1 - Crushing Resistance
bb0e2a6c-a45b-5db4-b8d7-08d582b8ac57 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
ba712546-75dd-559d-b99e-74a050d1816a | note | Acceptance / Conformance Criteria - >100KN
52bea34c-e074-5e00-a0c4-110c2fd14b0a | note | Standard / Specification - PS 16.5.15
e0276c72-f5d1-5a5a-b2ed-30cec3d27c7c | note | Verifying Document - IANZ Accredited Report
a1e15caf-d908-521b-b7e3-116ea85c296e | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
648a71f2-1a92-5393-9276-44c978ca5c2c | note | Verification Activity: Activity - HP
c2f15038-3c58-5879-a074-69089a4d70a3 | note | Verification Activity: By - ENG
0d7c8bd5-7fac-5d51-bc8b-91194e4b4abb | signoff | AUTHORITY HOLDPOINT
621ec4b2-6500-5108-af41-38730533fa09 | checkpoint | 1.7.2 - Particle Size Distribution
e3453d2b-0f0e-5943-9abe-cc046e755504 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
85fce51a-65df-581a-babc-225b335772c3 | note | Acceptance / Conformance Criteria - Max Particle Size 130mm, Max 5% passing 19mm sieve
c257f09e-5315-521b-8cbc-041c26fb48b6 | note | Grading:
c099953a-e37d-57fe-96b4-3f59410c70f3 | note | Sieve Size ¦¦ % Passing
09d74a72-95fc-5e21-a00d-26ffd88a0617 | note | 130mm ¦¦ 100
04df46af-e4ee-52c2-9dc5-7b4002ab8a19 | note | 100mm ¦¦ 70-80
a94322fc-9d15-5144-aae2-4c3bf59e08c8 | note | 63mm ¦¦ 0-50
28b131f0-aff3-59c9-97b0-28e2661b5215 | note | 37.5mm ¦¦ 20-25
11068d5c-8ed9-587c-a6bf-1502dffde10a | note | 19mm ¦¦ 0-5
e5788552-54a4-52b4-8b57-1b0349f98c2e | note | Standard / Specification - PS16.5.15
bc4a4fda-5277-5c68-b952-c532c651c723 | note | Verifying Document - IANZ Accredited Report
1d53f9e0-ed2b-5d55-9549-abab5654a418 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
223c2905-6dda-55e8-9d4d-7f716e02477f | note | Verification Activity: Activity - HP
a825d26f-eab0-5dfe-b8bc-f8375b209886 | note | Verification Activity: By - ENG
2c0f8c29-ad41-5a2a-b635-0a0aff717668 | signoff | AUTHORITY HOLDPOINT
37e76f2f-26c4-42ce-82a2-cdc5007ac58c | checkpoint | 1.8.1 - Maximum Dry Density and Optimum Water Content
07a0a6d7-28b0-54cf-9b02-7634c86a9eb7 | note | Detail - NZS4402:1986, Test 4.1.2 - Standard Compaction Test
c7cb3026-3ee0-5aa2-b0b5-c7273980332b | note | Acceptance / Conformance Criteria - Results to Engineer for Approval
da7f72a5-80f7-5f05-a89a-81afc4889f96 | note | Standard / Specification - Appendix XVIII
18a30af1-bd29-5090-a98e-5ddbdd85539e | note | Verifying Document - IANZ Accredited Report
787ba455-3085-5b0e-bb72-b2200a32b9e1 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per source
20002216-97bc-56ef-928b-63449f19a710 | note | Verification Activity: Activity - HP
2d762234-fa6d-506e-8739-259f54918c65 | note | Verification Activity: By - ENG
c4476e83-179a-4066-b48b-38c709c473a6 | signoff | AUTHORITY HOLDPOINT
28a9939c-3398-5e1c-b9f3-fc35b3f555e1 | section | SECTION 2 – SITE WON LANDSCAPING FILL
01aef69a-6763-59ca-9c8d-736ee53b831a | checkpoint | 2.1.1 - On Site track-able Testing
3f42d642-f175-542b-82b1-b5985457f28f | note | Detail - Fine grained Type A3 site won materials may be considered suitable for use as landscape fill providing that it is ‘track-able’ by the contractor’s plant.
7fff358b-d85f-5211-aeca-a69e18d3e5bb | note | Acceptance / Conformance Criteria - Trackable by Contractors Plant
a197c149-fbfd-5ba1-8b7f-8b20882dc8c2 | note | Standard / Specification - PS 16.5.5
4f8645a9-3bfc-5a34-b967-f66786a89908 | note | Verifying Document - Site Engineer, Site Record
75d1d38d-26b7-5102-b1ff-f76a43a42a76 | note | Testing Quantity Required (based from schedule qtys) - Before placing any fill each day for each area worked.
74103d69-a1be-5ff9-86a8-29373f64ed06 | note | Verification Activity: Activity - R
93001987-c82a-50b0-a687-c7bf697943d7 | note | Verification Activity: By - SE
cea9f37d-9fcc-59d5-a86b-752d34abb6de | checkpoint | 2.1.2 - Shear Vane
e26b7ef8-d97c-53fd-98d6-bd056ebb8715 | note | Detail - NZ Geotechnical Society 2001 - Guideline for Hand Held Shear Vane Test. Fine grained Type A3 site won materials may be considered suitable for use as landscape fill providing that it meets minimum shear vane strength of 30kPa.
dd7408db-f9e9-5c49-a395-0b757e41b7eb | note | Acceptance / Conformance Criteria - Min >30KPA
8967e5c2-9ac2-5a5e-a527-f835a8f34437 | note | Standard / Specification - PS 16.5.5
82c157b0-e50a-5f86-a528-dfb1cca45419 | note | Verifying Document - Shear Vane Report
226b4377-b9bc-53ee-90bf-2d4a82840a3b | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed fill per 200mm vertical ‘lift’.
580e74ff-fe93-5045-83c9-aa7c7882396a | note | Verification Activity: Activity - R
9776a4e5-9649-571d-a52c-cfd171f98003 | note | Verification Activity: By - SE
6d1d7126-1928-59ff-a877-462c509c0a9e | checkpoint | 2.1.3 - Proof Roll
bd66fb71-ae1b-5640-b1f8-904acfcf4caf | note | Detail - Proof Roll
3a58ea8b-4e5e-56ec-a645-4316abdd9086 | note | Acceptance / Conformance Criteria - Visual Inspection
beb4eb0e-ca18-56a8-8abb-ef2a25f558ab | note | Standard / Specification - Appendix XVIII
f8e8deaf-c24b-52ec-bbc5-dd57761b1134 | note | Verifying Document - Visual Site Record
d7d3c93d-c661-51d9-96fa-2886ab91ae83 | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
4800964a-2e44-58dd-8ae5-6cfefab59414 | note | Verification Activity: Activity - I
95fe8f2d-d11b-5ad8-9773-a44dc77da221 | note | Verification Activity: By - ENG
39d605b8-01ec-570b-b293-b6919dc2d8c2 | section | SECTION 3 – CUT SUBGRADE TESTING
0fcfb85c-2785-506a-902a-ef8862f376ed | checkpoint | 3.1.1 - Proof Roll
9b8ee6b6-c1d8-5143-a084-b27a5d279ae0 | note | Detail - Visual Inspection of Proof Roll
6f3952ff-2a7a-5418-ab3f-a84b218867af | note | Acceptance / Conformance Criteria - Displacement <15mm
b2a0f6ea-38ff-504e-8302-4c02f4902b36 | note | Standard / Specification - Appendix XVIII
0cfbc095-713f-50b2-b962-1709167fda88 | note | Verifying Document - Visual Observation
6de84e34-6b3b-5965-ad4a-b91f06ab0ce5 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
12589d38-c993-5bb1-81fa-7b4ba2669742 | note | Verification Activity: Activity - V
fe3486b0-6cc4-5d9b-a6e9-154171770e1c | note | Verification Activity: By - SE
93b11d4a-04e4-5cfd-8dab-0a37521cebb5 | checkpoint | 3.1.2 - Cut Subgrade Inspection
1ad4f939-cb75-5ff9-9543-62cea2bb10fb | note | Detail - Engineer to inspect all foundation surface inspections
7e8b5e53-75e3-5e68-998b-905d79354b01 | note | Acceptance / Conformance Criteria - Engineers Approval
70e6c899-f866-57d8-8fdb-aac02ae513c1 | note | Standard / Specification - Appendix V
3397ab39-8b75-56fd-be39-bd2c305125cb | note | Verifying Document - Visual Observation
f9f254a0-753e-5be3-9750-266085fb3728 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
e9f36af9-e15c-5a9e-af0f-738b50136eb1 | note | Verification Activity: Activity - HP
dc69b9db-23b1-5a06-8db4-abefd628ef4e | note | Verification Activity: By - ENG
963aa0be-3122-5fa7-9edb-c9242f2cacf8 | signoff | AUTHORITY HOLDPOINT
1c232ad4-ca6f-5352-879b-6dc0de1ab807 | checkpoint | 3.2.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
e7163e68-b0e3-5f2f-96a5-ce33320c1c53 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
45014ec0-1f8c-5270-b530-7f36a1ee06ac | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
58bfd0b1-7958-5993-a896-e3e22028cf3c | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
ffe515da-ee85-5ede-9fbf-b3c85024cae4 | note | ○ Single Test Min SU: >50kPa
af1d3197-a6e5-5b8f-8b21-ad8da62ca655 | note | Standard / Specification - Appendix XVIII
d8f50f3c-cc10-5a51-a094-69f7d2654f34 | note | Verifying Document - Shear Vane Report
15f00dfd-9baa-5595-b893-bc90b866bd83 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
739cd2cf-8354-588f-910e-bdad0829c121 | note | Verification Activity: Activity - I
847bef16-6e0a-527a-8e2f-63bb3d5f7e61 | note | Verification Activity: By - SE
90e0aec2-fe18-571c-ab93-111c98467327 | checkpoint | 3.2.2 - Cut Subgrade Testing - Cohesive Soil Scala Penetrometer
b5d7ad09-54d7-5e1f-b147-e713fc784924 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
7e769fe4-3a85-5663-8597-cce49df0563e | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
c701c9ae-eb66-55ac-a955-752cb3f99dc5 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
1cfb59e9-e301-58d7-b234-ec9b84187ba8 | note | Standard / Specification - Appendix XVIII
dc550f5d-09c6-57fa-a9de-3afe17fe3ff6 | note | Verifying Document - Scala Report
d87efcc5-a697-588f-b1e9-d5a654ad196d | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
ff7ce86c-a7b2-50c1-9745-dd2b9d4105fb | note | Verification Activity: Activity - I
4a5b9405-45dc-5570-976c-7e17d705d1db | note | Verification Activity: By - SE
b5bc1a9e-ce3c-5ab7-9191-e1d4655e8d28 | checkpoint | 3.3.1 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
099ba27f-0aa3-5787-b331-288eca947e13 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
37b6532e-c53c-5014-8b83-16a87e3980b3 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
4842107b-db4e-51fc-be72-d50f5651a07d | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
a851bc90-faa8-5ded-a6b2-6d85e2e71932 | note | Standard / Specification - Appendix XVIII
df52a6eb-a78c-5b0b-8224-d27e7dfe1e35 | note | Verifying Document - Scala Report
d99347d2-cfb0-5075-b6f9-15124550728f | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
c7722149-203e-5f1e-9298-257ba8192655 | note | Verification Activity: Activity - I
243c1c30-7a47-5092-a5e5-8ca7fc0e922d | note | Verification Activity: By - SE
e30f05d0-ec2c-5e4b-a54a-d592b64bb134 | checkpoint | 3.4.1 - Release of Hold Point
9c8ca8ca-c3ff-5943-95c9-08571de46e16 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
b47056ce-32ca-584b-b801-937b80fcb179 | note | Acceptance / Conformance Criteria - Engineers Approval
190bbdb6-7726-574c-b85d-8f227be9e743 | note | Standard / Specification - PS 16.9.3
af2bc54a-add3-5907-9179-35f1b262589c | note | Verifying Document - Written Certification
6cc1ee2b-ab37-5006-80a2-362747077ea2 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
3ae6586d-f990-52a3-aea5-9767d20674ab | note | Verification Activity: Activity - HP
0480d17f-a566-54d9-836c-af9c3b82637b | note | Verification Activity: By - ENG
b785ceee-e615-5a5f-b0ef-f5834a2e49e4 | signoff | AUTHORITY HOLDPOINT
839606ac-0bf2-5c84-9972-67e9133f6bc2 | checkpoint | 3.5.1 - Subgrade Level Confirmation
5b1ee707-e641-5e41-9f82-01c7339af913 | note | Detail - Confirm subgrade is 735mm from finished height
f8acf895-08fb-5d6a-9df3-ae46998181f2 | note | Acceptance / Conformance Criteria - String lines - or equivalent are 735mm +0mm/-30mm
5a940419-9a05-569d-877c-84fd3a38bdaa | note | Standard / Specification - PS 20.14.5
14a675cd-e791-50fa-8907-42ad9b0d9518 | note | Verifying Document - String Sheet
dec9c9a2-e516-5c97-896f-06ea24f80b97 | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage
df5c4d78-8ba2-528d-8713-a359de273af9 | note | Verification Activity: Activity - I
473ff51d-3dff-59b1-8fea-b9093f074bc8 | note | Verification Activity: By - SE
4c2880cb-6b19-5352-afc6-0af4ec16bf79 | checkpoint | 3.5.2 - Subgrade CBR Testing
9ca2adba-5d8d-5dc1-b774-1c01f427537d | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
ef3e9759-440a-5d30-accb-f608039c6584 | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
413c7606-9deb-5791-8045-219bf3b5639b | note | Acceptance / Conformance Criteria - Pavement Type 1: CBR >6, Min 3 blows / 100mm
fcc1c763-3684-5936-bb03-cc49bb839751 | note | ○ Pavement Type 2, 6, 7: CBR >2.5, Min 2 blows / 100mm
4dd10b43-71a1-5056-b0ec-c9395db70abf | note | ○ Pavement Type 3, 4, 5, 8: CBR >3, Min 2 blows / 100mm
03481636-9962-5510-bc10-bc410b962eb6 | note | Standard / Specification - PS 20.4.1
1eaac8e5-1e60-55ee-bf47-075dcfa3326c | note | Verifying Document - Scala Report
cd9bc73e-313f-5da3-8b2c-60d448857ce2 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100M2
9eede4ac-42fd-59bf-a294-befab2d2c9f3 | note | Verification Activity: Activity - I
a4c82a62-8b1c-55b1-b1ce-fa9fec3223ed | note | Verification Activity: By - SE
efd6bce0-9436-5a8a-8e4d-3b3dfcc3122c | checkpoint | 3.5.3 - Release of Hold Point
e475e1c5-a240-5723-908b-52369cf8c165 | note | Detail - To release the subgrade hold point and be able to start placing pavement layers, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
0bcc3327-3c68-5d53-a953-398933445973 | note | Acceptance / Conformance Criteria - Engineers Approval
e0a1bb27-639e-577b-b592-4ad81e2f14da | note | Standard / Specification - PS 16.9.3
50a81bc8-d86a-5883-afc1-bc0c5af0b02c | note | Verifying Document - Written Certification
717f4e33-a87d-5781-9f0d-32815dc7150a | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
441f4220-c389-573b-9551-3c1e828d4aa5 | note | Verification Activity: Activity - HP
0c0f8dcc-cd0d-5220-9466-b3c8d4d984a6 | note | Verification Activity: By - ENG
fa6a9276-7859-5e26-9e07-5da5d76a8c15 | signoff | AUTHORITY HOLDPOINT
fcd783e9-5837-58e1-a505-866715da12e7 | section | SECTION 4 – CUT SLOPE INSPECTIONS
65f19254-c0e0-5cee-bd75-e32db1abf131 | checkpoint | 4.1.1 - Cut Side Slope Inspection
eafb8a5a-c8d7-568a-a4da-a4044af9fde7 | note | Detail - Inspection records to include photographs, logged soils (to NZ Geotechnical Guidelines) and shear vane testing
59b61895-d03a-524f-9906-0bab0c512fae | note | Acceptance / Conformance Criteria - Engineers Approval
332d06ad-16bf-5aca-b370-c5a9bc5b2ce6 | note | Standard / Specification - PS 16.6.4
02068a19-61ba-5c61-9eea-0ab28547c7d8 | note | Verifying Document - Site Records
3bd18812-56b9-5747-a8f3-19c7b1be802a | note | Testing Quantity Required (based from schedule qtys) - As per Engineer
8d9f33b2-ec66-5b3c-a304-18eefd5ee936 | note | Verification Activity: Activity - WP
1d2eba01-d547-5a5c-92e1-b224ce415b25 | note | Verification Activity: By - ENG
778e9838-7b8c-5e69-b413-633633b57f38 | checkpoint | 4.1.2 - Cut Slope - Soil Log
c04a919e-c3f7-5310-82a5-6b0fab022ab9 | note | Detail - Soils to be logged to NZ Geotechnical Guidelines
98ac6f09-aeb2-5fba-ac8a-b5a07c7cf703 | note | Standard / Specification - PS 16.6.4
17949f10-fbe3-5c39-a253-67d116933f92 | note | Verifying Document - Soil Log
c4091482-ed12-5378-86ad-800c128c3b79 | note | Verification Activity: Activity - I
b49bef8e-cbd1-5bb3-a6b0-dd65950a5a8f | note | Verification Activity: By - SE
a9f13abe-59e6-5a91-872b-201daf1550be | checkpoint | 4.1.3 - Cut Slope - Shear Vane Test
f8f335cf-3f36-5edf-a43b-76b204e464f3 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
ebca4ad6-34af-5360-96a7-2623ea7582fe | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
fccd3323-eab8-5990-8196-1a8cab2d2b22 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
bf61c6d8-7def-56c8-aadf-0dc8ba0f3866 | note | ○ Single Test Min SU: >50kPa
f0b03302-2718-5660-9e96-a23051f8f0a7 | note | Standard / Specification - PS 16.6.4
161edf4e-7dec-5d2d-81b1-e869e63b344b | note | Verifying Document - Shear Vane Report
e4a94a26-48e1-5152-97d6-7945234ff646 | note | Verification Activity: Activity - I
6abadc46-ca3d-5b6d-bf59-eef1c4f35e1f | note | Verification Activity: By - SE
eb0520ee-76a0-5f5b-8ab0-028f5cd672d6 | checkpoint | 4.1.4 - Drainage Measures if Seepage Encountered
df6a0f47-131d-5150-b664-3e2398ea95bd | note | Detail - Borehole Drains or ballasting may be required, to be directed by Engineer
19ac0b9a-87bd-5144-b9fb-134e403d3d9a | note | Acceptance / Conformance Criteria - Engineers Approval
e59e8ee8-111e-53aa-9e73-d14afd7e90cd | note | Standard / Specification - PS 16.6.4
5e2d2b7f-51c3-57b0-ab11-e99bf1b733c6 | note | Verifying Document - Engineer approval
1233e552-20a2-5624-a4b6-4473dd62d5e0 | note | Testing Quantity Required (based from schedule qtys) - As per Engineer
78e176d2-830b-592f-815a-f533b10fd2ce | note | Verification Activity: Activity - I
b12fbd0d-43d9-5b7c-85cf-2c14f962f961 | note | Verification Activity: By - ENG
b76f45ae-9c1b-51f2-b20c-9ff3446f93b4 | checkpoint | 4.1.5 - Design and Grade Check
d719a61e-92cb-5e04-a1be-67e6cc3b5d2c | note | Detail - Confirm cut slopes have been correctly excavated to design and grade
7ee5a497-9330-50c0-addb-17edd94fe61d | note | Standard / Specification - PS 16.7.1
a08bc602-6e70-59ce-aa28-f1a0ccacb0c3 | note | Verifying Document - Survey Records
66361d3e-45e1-580e-a089-e35463605c13 | note | Verification Activity: Activity - D
0b86cd24-d47e-536d-989e-374847218eaa | note | Verification Activity: By - SV
e04bc573-50a3-54df-8ec4-f2c2fee33603 | checkpoint | 4.1.6 - Stabilisation of Cut Slope Surface
93e98976-6385-56c4-b2d9-349860fcabb3 | note | Detail - Cut slope surfaces to be topsoiled and grass seeded or planted as soon as possible
c916b7dd-a5b1-5dff-90e8-7a56abd81c49 | note | Standard / Specification - PS 16.6.4
5ee42616-31e2-5674-8247-0e6757e2ec47 | note | Verifying Document - Site Records
10ef3a43-e9c7-5964-9a27-cd58df1bd030 | note | Verification Activity: Activity - C
8d4b2d50-9b81-5dd1-9d74-3e40d5f922ed | note | Verification Activity: By - SE
d332b165-be98-57b1-ae8f-c8df339988ac | checkpoint | 4.2.1 - Release of Hold Point
975dc4ff-47f3-5f6e-a731-5b7c043b0a8f | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
85c880c7-d82d-59e8-bf83-e56b043e6a6c | note | Acceptance / Conformance Criteria - Engineers Approval
52598269-cb1d-5ef3-82c7-10df60d04119 | note | Standard / Specification - PS 16.9.3
8c918a19-dd3b-5fa3-b3ac-92294c75f309 | note | Verifying Document - Written Certification
16e9480e-295f-5c45-b8b2-2a9314f1aa63 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
a9f9dc2b-f96f-5aff-83b8-5a9bd212cbb1 | note | Verification Activity: Activity - HP
88c6a9e1-47af-540e-806c-68cde2824c9c | note | Verification Activity: By - ENG
8ab96904-8ef4-591a-ae23-4d319981dd1d | signoff | AUTHORITY HOLDPOINT
d8949eb3-2a58-53de-a569-51450984c878 | section | SECTION 5 – UNDERCUT TO WASTE & BACKFILL
03329000-37e3-5dad-9c5f-fc644c03e0c8 | checkpoint | 5.1.1 - Undercut Surface Inspection
256db5c3-1fdd-5a71-85eb-078779522eb6 | note | Detail - Engineer to inspect undercut surface
4f0a304a-13ed-5f07-8d40-20244ff6ff4d | note | Acceptance / Conformance Criteria - Engineers Approval
c73ff527-8e22-5569-a18b-7840e24e53d8 | note | Standard / Specification - Appendix V
1c058744-4d82-5867-bfc0-c5300dc33d61 | note | Verifying Document - Engineers Approval
339e749c-f490-539c-8c6a-74df1480e8d2 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
84cdccf5-8b1d-5cf9-b7b9-0481b6737256 | note | Verification Activity: Activity - WP
4729c983-c925-5f73-b89a-6b1c52193b49 | note | Verification Activity: By - ENG
4063604d-63cd-5791-a2a5-9f4966e1ea3a | checkpoint | 5.1.2 - Placement of Geotextile on Undercut
5b33c92d-043e-5403-808c-d48497af90f3 | note | Detail - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
e54f28cb-9f6e-5015-90c6-d723332121e1 | note | Acceptance / Conformance Criteria - Engineers Approval
bda4a583-1021-5daf-8d37-7911b23579fb | note | Standard / Specification - PS 16.6.4, TNZ F/7: 2003 8.3
d649f041-1fdd-5aca-b4f7-2ff276e9ac5c | note | Verification Activity: Activity - WP
dd3c4e48-bee9-51f9-8e85-4f2dc9eac914 | note | Verification Activity: By - ENG
0baec06e-bca7-5764-b694-c995a1192578 | checkpoint | 5.1.3 - Subsoil Drain inspection
2d0fd9b7-688e-5f3d-82b3-d58e0a3ef953 | note | Detail - Subsoils to be placed at base of cuts where directed by the Engineer
982df744-6067-5c7e-98fd-3961f3c508e0 | note | Acceptance / Conformance Criteria - Engineers Approval
6da8b5af-6c4d-5267-8841-accb283d54c9 | note | Standard / Specification - PS 16.6.4
5afd4a8d-a2ca-5131-9bd7-f5e260b93cb1 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
38840069-bfa3-5364-bbc0-2bd7c1144c91 | note | Verification Activity: Activity - WP
3ab6db38-4e76-5e78-8fdd-3e93a3812b55 | note | Verification Activity: By - ENG
2b5c3c35-e44a-5fba-9f5b-5f34c6490527 | checkpoint | 5.2.1 - Release of Hold Point
edd45759-2e74-5acd-b50e-431368d9a029 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
45a44b68-29f9-503a-a771-b808ad16301d | note | Acceptance / Conformance Criteria - Engineers Approval
1fa0514e-4bcf-5990-906f-c570a3ce781b | note | Standard / Specification - PS 16.9.3
207fa720-d016-5723-914d-bf51f2305824 | note | Verifying Document - Written Certification
86d88f28-47d0-5253-b632-5fe62c626db2 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
17df2965-bb15-5c5f-8049-a05afca06b8c | note | Verification Activity: Activity - HP
9fd18c9d-d502-54fe-a461-d72145cac5f0 | note | Verification Activity: By - ENG
9b33e9a0-b387-5cd5-a9ff-916d70c37976 | signoff | AUTHORITY HOLDPOINT
48724bee-4e03-5805-b57e-bbb948c422e4 | section | SECTION 6 – COMPACTION OF IMPORTED FILL
d03f7fd2-b98b-5017-b443-b66ce56e2a47 | checkpoint | 6.1.1 - Placement of Geotextile
c57c4551-aaa4-5098-9046-dc7d23f1ca0e | note | Detail - A layer of Class B Geotextile Fabric to be placed between cut surface and imported A1 Structural Fill with 500mm overlaps
37271b8a-817a-51c3-bbb2-d5d76e057393 | note | Acceptance / Conformance Criteria - Visual Inspection
4fb6212e-baa8-5eff-a2d5-03c6d4e2558d | note | Standard / Specification - NTC084
2e01a5a2-2afe-5bc3-8a9f-4e1a52fe8fb9 | note | Verifying Document - Visual Observation
ca6b7040-f14a-5848-86e7-4d95f44a0433 | note | Testing Quantity Required (based from schedule qtys) - As Required
e746025b-3f23-52a5-be29-352a14f73322 | note | Verification Activity: Activity - I
4e1b258e-ef24-5986-8e5b-6ba6f754acd1 | note | Verification Activity: By - SE
36a35987-56f2-51a2-91ba-2c48bca739e3 | checkpoint | 6.2.1 - Compaction - Clegg Hammer
0f2983b7-0568-5f98-bf54-760e89e688dc | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
8b60bda0-eda7-5390-9c06-55463cbb2483 | note | Acceptance / Conformance Criteria - Structural Fill: Min CIV 18, Ave CIV 20
a63a7a49-961d-5112-8522-5443d908eb4c | note | ○ Non-Structural Fill: Min CIV 10, Max CIV 12
e0d6243e-271d-51bf-9c25-8ebf8af78bd9 | note | Standard / Specification - Appendix XVIII
9efe89ee-da3f-5938-a7ae-ec3d36454d92 | note | Verifying Document - Clegg Hammer Report
63b9977d-c247-56d7-9957-540db297f44b | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
da53d111-535f-5332-9db3-53fa60557f5d | note | Verification Activity: Activity - I
c2e31214-2a6b-5bef-a595-9e52c9d2c119 | note | Verification Activity: By - SE
cdac7ed8-dfb2-526c-8f48-c0fe5bf13a94 | checkpoint | 6.2.2 - Compaction - NDM
2c4ccefe-38da-5fc2-8bb2-c6945688099c | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
3724cddd-6f8d-5ace-809e-68271568c1c6 | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
a19928ce-c7ec-5942-8017-5d3627ba5b15 | note | ○ Non Granular Material: Max Air Voids 8%
d47982e4-4647-5723-bfdc-11c2198d30db | note | Standard / Specification - Appendix XVIII
791913a0-97cd-5b7a-8f96-9a0d77c59f7b | note | Verifying Document - IANZ Accredited Report
e0a1361f-ecca-52ad-a951-76b7a3156784 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
2d1f61eb-9a2f-5829-aab5-26186d7d5c05 | note | Verification Activity: Activity - I
a70f7328-fca2-57e8-9a83-3f7f38cce54c | note | Verification Activity: By - SE
8c46c409-8ae9-5510-81ae-2409a0dcb7a5 | checkpoint | 6.2.3 - Compaction Trials
9fb0a691-7ac5-5dca-8c58-d0e9c3d76f5b | note | Detail - The Contractor shall carry out compaction trials of the various soil types and combinations on site, and any imported fill materials, using different layer thicknesses, types of rollers and conditioning plant (ie construction discs and scarifiers). The trials shall be conducted over the duration of the earthworks operation with the objective of determining the most suitable and efficient techniques to meet the compaction requirements. The trial details, test data and conclusions shall be reported and copied to the Engineer within five days of completion of each trial.
3715385f-a561-5dd7-b387-5c2817e306af | note | Acceptance / Conformance Criteria - Engineers Approval
28fa0445-6822-5c24-8724-bf30bf57c3be | note | Standard / Specification - PS 16.6.5
02e21e85-d46b-5b2f-92ae-37890408c2b8 | note | Verifying Document - Trial Results
d8d8c67a-d433-5868-9b91-98d9f5538656 | note | Verification Activity: Activity - R
34f9dfbc-e9c4-5c59-bf71-dfaac063b803 | note | Verification Activity: By - ENG
fbe3407d-cb28-52a0-a9de-c1bce268da67 | checkpoint | 6.3.1 - Compaction - Structural Fill Scala Penetrometer
7a8230f3-b188-52e8-aa73-d5f2d0b3e33a | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
34d9409d-c083-52a0-9e7b-f7e27ac8f8af | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
54a7f7f0-b056-540b-a7af-b20795be7efd | note | Acceptance / Conformance Criteria - Minimum 5 blows per 100mm penetration
832e7712-9da7-5535-a5e3-0eb2027e1332 | note | Standard / Specification - PS 16.5.12
832ab02a-47ae-5c44-977b-7199f6f02552 | note | Verifying Document - Scala Report
9ecc2a3e-80a0-5277-afdc-ef68ad121dd1 | note | Testing Quantity Required (based from schedule qtys) - Minimum 1 test per 500m3 of filling evenly distributed over the extent and depth of the filling. A minimum of 1 test per 500mm lift or part thereof to be completed through the full lift thickness.
5d3a0d63-003c-558d-bc43-947c1fd61c82 | note | Verification Activity: Activity - I
85cb4824-3b4e-509d-8ee7-77ff323494df | note | Verification Activity: By - SE
6241f96b-6fc2-50ef-b732-f04924079f36 | checkpoint | 6.3.2 - Compaction - Structural Fill NDM
457c1a4a-0d41-588f-8702-c1c4a51c4d9c | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
c05456f7-d00a-50d5-803f-ea928a114d3e | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
287a7df2-dd75-5da1-bcec-82fbdd445e4b | note | Standard / Specification - PS 16.5.12
907be105-d2bc-5ef8-9187-cbfb4713d2ea | note | Verifying Document - IANZ Accredited Report
6e64e8f1-6ee5-5b54-992c-73f9536ae0db | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
74fd0876-618e-5c8c-8f44-246e7956aa20 | note | Verification Activity: Activity - I
5bf1ae9e-7c5d-57ec-bc85-47db527cb0d1 | note | Verification Activity: By - SE
662ad010-253b-5a12-a529-7441614b3b64 | checkpoint | 6.3.3 - Pumice Sand Fill
daf880a4-f3be-5c2b-a7ea-53ce71075fac | note | Detail - Pumice Sand Material shall be contained with an outer layer of fill with a minimum thickness of 600mm. Must be Hardfill and/or imported Type A1 material and/or Type A2 material and/or Type A3 material
40545462-e55a-5c89-9da8-15ad69319790 | note | Standard / Specification - PS 16.5.12
3c76e7cd-c115-50e1-9d7c-a1a308ba9d33 | note | Verifying Document - Site Records
cc9db91d-3c94-5e65-9d7d-6b02cada1074 | note | Verification Activity: Activity - E
6c9f6c43-0716-55c1-a18c-b2d004bb9431 | note | Verification Activity: By - SE
6a73a8a8-7989-5156-8499-c39920491575 | section | SECTION 7 – TOPSOIL PLACEMENT
01cae0f9-1947-5325-aa64-e60f3c87d461 | checkpoint | 7.1.2 - Topsoil Placement on cut and fill embankments
2474dbde-e949-5825-9b4b-c6df21ad6318 | note | Detail - Confirmation of thickness and material suitability
efdd939b-0b67-51ff-9c20-e9a31679142d | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
9f0d6b38-9cb1-5f20-8d1b-46eeacaa7afe | note | Standard / Specification - PS 16.6.3 b)
ff47695f-9562-5a11-8a20-fb3b61c78347 | note | Verifying Document - Visual Observation
b85c747e-a11d-51f6-86b7-3c2b2be7644a | note | Testing Quantity Required (based from schedule qtys) - Once per lot after topsoil re-spread
496ce2b8-6b30-5794-949b-4a9acf650e0c | note | Verification Activity: Activity - I
3843524f-0169-5361-a158-82aaeea0e21b | note | Verification Activity: By - SE
a3330d98-78c7-560f-9006-8e2f8e055412 | section | SECTION 8 – SETTLEMENT INSTALLATION & MONITORING
bc29cfd2-ded1-5198-97c7-6d976446c060 | checkpoint | 8.1.1 - Instrument Reading Notice
9138d2a5-833b-5d74-bc27-4fb87fa471e1 | note | Detail - The Contractor shall inform the Engineer two days in advance of planned instrument readings so that the Engineer may observe the work.
1e74c7bd-cbb9-57f6-a3fc-41e86ab88902 | note | Acceptance / Conformance Criteria - 2 days notice to Eng
32e603b1-d51a-555a-9b5b-3ae1fba7f11a | note | Standard / Specification - PS 16.8.2
81db03e5-3ca8-5ed3-8ded-74b94252a0e8 | note | Verifying Document - Site Records
59a2d2b4-d219-5b31-8aca-a96c70384634 | note | Testing Quantity Required (based from schedule qtys) - Every Time
66cda388-c788-521b-9da5-06a0dac81c62 | note | Verification Activity: Activity - I
bf5d7d6e-ff88-5976-aefe-afe83d1a306c | note | Verification Activity: By - SE
1ebb286f-cdd7-51fb-9b19-9386a0211bf8 | checkpoint | 8.1.2 - Results Submitted to Engineer
c14766cc-5b05-5e9e-8968-a8f891dde82a | note | Detail - Results will be submitted to the Engineer within 1 day of reading the instruments
5335b5b4-a095-50ff-8d86-02475f1c74f7 | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
d77f647a-7ef6-5995-9898-0abf6db1436d | note | Standard / Specification - PS 16.8.2
cd195672-6e20-5687-8a8a-5486969f3faa | note | Verifying Document - Site Records
8f444ee1-3401-5e8c-92a1-9e2b05cb1bdd | note | Testing Quantity Required (based from schedule qtys) - Every Time
aa36d35b-ea46-5784-89b2-b02175228e69 | note | Verification Activity: Activity - I
22e987e2-931a-5270-9981-b956d623df17 | note | Verification Activity: By - SE
3d3ae3dd-ace9-5090-92fc-553517c39048 | checkpoint | 8.1.3 - Baseline Readings
dfca4c58-fdd4-5702-9323-368c136a86a0 | note | Detail - The Contractor shall take 3 sets of baselines readings from all instruments at 2 day intervals
7d7dde4a-8e18-5e2b-bc02-3f856da9833e | note | Acceptance / Conformance Criteria - Engineers Approval
6c77cae2-2305-5f56-ad2f-78a74f336c0d | note | Standard / Specification - PS 16.8.2
6d9a1bd9-92a3-5ef2-ae83-bff9e90cd391 | note | Verifying Document - Site Records
e256acef-02eb-5bb1-8dc4-855e82f54d50 | note | Testing Quantity Required (based from schedule qtys) - Every 2 days
bc0afed1-86b2-57d1-b82d-6e51bbf0cdcd | note | Verification Activity: Activity - I
c6189f79-8669-53bd-8a75-f954d309a934 | note | Verification Activity: By - SE
e7a7f3e9-840e-5da4-93a5-63a071074afc | checkpoint | 8.1.4 - Readings During Active Fill Placement
e44330d5-ed03-599e-a3a7-d98a1d807dc1 | note | Detail - During active fill placement, the Contractor shall read all monitoring plates twice a week or every 1 metre of fill whichever is more frequent
29ad938d-fe00-5843-81d2-04a1d04c717b | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
78a29925-300c-55bf-a802-7c47ead2c5b9 | note | Standard / Specification - PS 16.8.2
4f00d42e-75e9-53dc-81f5-3b0677f631a3 | note | Verifying Document - Site Records
92842721-614a-5dde-8394-5f4167684317 | note | Testing Quantity Required (based from schedule qtys) - Twice a week
c217781a-8dad-5447-9963-264f19054387 | note | Verification Activity: Activity - R
1add7908-816a-5f48-8d57-c988710064bc | note | Verification Activity: By - SV
292e3aee-3636-5d32-b777-37a5679b000d | checkpoint | 8.1.5 - Readings During No Active Earthworks in Area
4f95a597-dd8a-5d92-b90f-6e4fd48f41f0 | note | Detail - The Contractor shall read all monitoring plates weekly if there is no active earthworks taking place in the area
c50dcb36-a678-56c8-a2f3-e136fd02c974 | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
c0d929ff-b2b6-51f3-bd86-fe245d3f7164 | note | Standard / Specification - PS 16.8.2
0a3146b3-4fd6-5afc-acd1-d62a2c160f7d | note | Verifying Document - Site Records
c24b8e98-91db-5bac-a829-810e5b768020 | note | Testing Quantity Required (based from schedule qtys) - Weekly
56cd2f44-d76d-5f0b-858b-9d87e4a66efa | note | Verification Activity: Activity - R
4ccef1a1-0513-534b-a6da-01e3f8933e81 | note | Verification Activity: By - SV
3200ddaa-39d0-5fe0-9db2-2ecb08f5e205 | checkpoint | 8.1.6 - Settlement Monitoring Termination
41909bd1-c111-50ef-9ea0-d20a274f7c8c | note | Detail - The criteria for terminating the embankment preload are either: Three consecutive measurements indicating the t90 settlement value has been achieved, A rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed. The settlement readings shall be evaluated by the Engineer to assess the need to extend the monitoring.
04d71d13-3552-5c80-8c41-dd528492d383 | note | Acceptance / Conformance Criteria - Either:
893459fb-3c53-5781-9524-5c7b643d954f | note | ○ 3 Consecutive Measurements showing T90 settlement value achieved
35e75f1b-655f-58d6-bcc9-4333b68485d0 | note | Or
70dd8156-ed59-54c2-a968-6d6090f5d9bb | note | ○ Rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed
53bf25f9-7e2b-5d23-8304-d9057582f22b | note | Standard / Specification - PS 16.8.5
29d23c9c-69f8-5d17-a7ca-1cefeb89b766 | note | Verifying Document - Site Records
2c1e3aca-5656-59a9-9771-9c4c0025318e | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
235ec686-c02a-504b-8871-5000f1a4acc7 | note | Verification Activity: Activity - HP
68bc82d5-caeb-5c67-a0e7-45bb554ab3b1 | note | Verification Activity: By - ENG
3b7e976e-ce37-508c-81a6-0d741734da4e | signoff | AUTHORITY HOLDPOINT
c2ecee3d-6862-5c26-a56d-8a8fd80e012c | section | SECTION 9 – AS-BUILTS
87d570ee-8f54-5bac-a996-aebcb3a25e28 | checkpoint | 9.1.1 - As-Builts
9c194c9a-20c1-554d-aed9-1682811ad650 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
8fdc0114-4e8f-5d6c-b3bb-e38f552a7dcf | note | Standard / Specification - PS 16.7.6
40b6e49a-8eed-58df-9985-66114f70dcaa | note | Verifying Document - Survey Records
50dce19e-a7e6-5fe2-94f5-ec7a3d724fb3 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
8f937779-f78c-5919-b1d6-1d1713891f4d | note | Verification Activity: Activity - D
cadde33f-dce0-57f2-9ff3-6800d7cf10a0 | note | Verification Activity: By - SV
bc936585-a3d5-4d37-b676-71b44bc44bca | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
65e3e954-9a74-59b4-b341-57e0db4a8462 | textbox | Contractor's Rep Name:
ce03386e-128f-52f4-b6e5-b8924a9da172 | textbox | Engineer's Rep. Name:
959ed28e-b26b-57af-b422-57dec9d22799 | date | Date:
5c21dece-c4c2-4e20-a595-9ebaca22ba99 | signoff | Add Signature
79b9d58a-1aa2-5eea-bfd9-318b1d6e9f9b | checklist | DN1210-0004 - Manhole and Catchpit Record | itp | DN1210-0004 - Manhole and Catchpit Record
d1c4b54a-b4c4-539e-9691-c0d96368dc14 | section | SET OUT
c5d6f50a-ccb6-53db-bb19-e28206919615 | checkpoint | 1 - Confirm Stormwater alignment is as per latest Drawing revision and does not clash with other Services.
71262383-01c1-5613-ad46-bff2bab3c896 | note | Comments: Design Engineer to approve if the location needs to be moved.
d2def37c-d86f-54ce-b45c-d3024d8835bd | textbox | NCR/OFI/RFI No:
274a37be-f134-5256-8964-164983e5d09a | checkpoint | 2 - Check Survey Set out and mark out completed.
0b503a68-1b97-50a8-a97a-bc702fb52c75 | note | Comments: Centre point of MH
8ac7e125-0b01-530b-adbc-7c83d866cc8e | checkpoint | 3 - Confirm correct location of Manholes or Chambers, Catchpits.
0a2a6f02-603b-5660-abe7-d20ea331dbbd | textbox | Comments: Refer to Dwg:
250e19d1-e2cb-5fbb-b958-1502f46075be | section | TRENCH EXCAVATION
a97a1b49-0483-5c2a-aeff-5b999d064122 | checkpoint | 4 - Ensure permits are in place.
c4f9efec-88e3-5916-8886-90616352200c | checkpoint | 5 - Pothole existing services data in place.
a88916c6-f006-5573-8093-21c6e2687901 | checkpoint | 6 - Confined Space Permit required?
3de7c1f9-e10b-55e6-b358-b4b95cf017e8 | note | Comments: Trench depth > 1.5m must be shored or battered.
d0547d1e-a8b7-5c80-b83d-cd2c32bdda0c | checkpoint | 7 - Foundation test conducted.
204ee721-a86e-5bfc-920e-789193837958 | note | Granular Material: Scala 3 blows/100mm 5% CBR
f1e92492-cd35-5b56-bdb7-58b5e99c2ec3 | note | Cohesive Material: Shear Vane Strength 70kPa
fe505ecd-66c2-5d92-97f3-03de78b849b1 | checkpoint | 8 - Undercut required?
3cf705f8-3b73-57a8-9c73-5c846dd6bcff | note | Comments:
2667e1cc-5437-510d-ab2f-3ea8cca1a95f | textbox | Undercut depth:
0b44c423-6b70-5fd1-90d1-a764b513787b | textbox | Metal:
4d6c7d1f-d51c-5cd4-97ac-d770a5fad3c1 | section | STRUCTURE INSTALLATION, BACKFILL AND TESTING
23cbe7bd-59d2-5b80-bafa-bf0b49b2cd60 | checkpoint | 9 - Installation of Precast Base Unit on Bedding
d3ffa4bb-d69e-5c00-a5a7-31c0e2fe014a | checkpoint | 10 - Installation of Precast Risers to Lid Level
a515fd04-1c2d-594f-a1de-9a6f419cb951 | checkpoint | 11 - Installation of Manhole/Catchpit Furniture, Steps / clamps
461dbaa5-adaa-5114-960c-83cc8ba2cd05 | textbox | Comments: If N/A- why?
b2499e8b-1ba2-5efb-9386-1005dc876b0d | checkpoint | 12 - Haunching around pipe connection and benching of MH base.
4490b37f-ad0b-5071-a217-8ed8cd47f48e | checkpoint | 13 - Installation of Precast Lid
f6ab9e4b-bec3-5876-b593-f4bc2ae87edb | note | Comments: 300mm above pipe or per IFC drawing
56f4f4ca-29f8-5b3b-b138-ce05266a7562 | checkpoint | 14 - Epoxy- Joints exterior and Interior.
bfdcd0db-a8da-56fd-8b05-8096da758035 | checkpoint | 15 - Backfill around Manhole/Catchpit – testing as per below:
88145006-0079-5875-ac9d-20b186233e9f | note | GAP20 - NDM – minimum - 95%
399e53a4-5218-52f1-a739-9526c860fc0d | note | LRAP65 - NDM – minimum - 95%
8bf87f7c-5a78-5031-8553-dc01677f3080 | checkpoint | 16 - Installation of Cast Iron Frame A Cover Lid Level – set with contour
3df15f87-6988-5d80-a0b5-df40e70b3938 | section | ACCEPTANCE
1f07076b-0076-5f85-b701-97b80c9dd552 | checkpoint | Inspection By: Downer Engineer
3ed9f10d-d7e5-5cab-b036-1ba6c52c1d81 | textbox | Name:
52d07045-b101-5db4-a0c7-f5df59879a7c | date | Date:
a877c709-a54c-5683-8723-668e3595d3f3 | signoff | Signature
284281b0-d493-5cc0-97d7-48c49655d6b7 | checklist | DN1210-006 ITP Pavement - Type 2 - Rev 2 | itp | DN1210-006 ITP Pavements Rev 2
8508ff53-5f3a-5f4c-8d26-a8afd00d3eae | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS
93f30d2d-3e56-50c9-9bd3-5beffe13a132 | checkpoint | 1.1.1 - Geogrid
6ac3edcd-a18c-5733-aec7-06c3a3fd497e | note | Detail - The Contractor shall submit the full details of the geogrid they propose to use to the Engineer for approval prior to installation.
e1465fc9-f1aa-5057-ac0f-5003b12d12a6 | note | Acceptance / Conformance Criteria - Engineers Approval
b46f5045-f195-581a-88d6-16abb80390ea | note | Standard / Specification - PS 20.5.2, PS 16.5.13
79e82902-7c33-5eb1-9ef3-9aca4eee9adb | note | Verifying Document - Data Sheets
ed7871b9-575b-5299-8436-447deb7c2e11 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
cee074c5-40f1-5c02-85d7-a78442c3c9f1 | note | Verification Activity: Activity - HP
77f0f7ed-2077-59b8-b7db-4980558ee76e | note | Verification Activity: By - ENG
84031b1b-c029-5fd2-a7d7-e24c84fe30af | signoff | AUTHORITY HOLDPOINT
3a027d9d-66e5-5b0f-9721-a8c1d3b87fcc | checkpoint | 1.1.2 - Geotextile Fabric
c532d749-a5ef-5c38-ab1d-3d265b7611ce | note | Detail - The Contractor shall submit the full details of the geotextile fabric they propose to use to the Engineer for approval prior to installation.
be535660-8d85-5846-8d57-50f0172cbb73 | note | Acceptance / Conformance Criteria - Engineers Approval
1cd09b83-7c92-5c4e-b0d8-903380c2613f | note | Standard / Specification - PS 20.5.2, PS 16.5.14
587c2b92-cba0-559e-ad03-6314fbef71ed | note | Verifying Document - Data Sheets
c2321eef-3e3a-5095-b50e-a234b11e1833 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
1d3e9db8-a5ea-532c-9e77-817b2d9b4dea | note | Verification Activity: Activity - HP
b6a9b042-e1f5-58a4-8008-fd4adde3cc3e | note | Verification Activity: By - ENG
26b7265b-d3f4-5735-83f1-9fe60d84cd62 | signoff | AUTHORITY HOLDPOINT
ed84c0c4-748e-5387-895f-ad74a2ec012c | checkpoint | 1.2.1 - Crushing Resistance
1517bcfb-bb12-5e2b-92f1-b96e227a2eda | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
7dad6ced-f56d-5b2e-87ab-f65bfcb0c7bc | note | Acceptance / Conformance Criteria - >100KN
a2c2031e-09d3-5e0f-af13-e520f20baa0c | note | Standard / Specification - Appendix XVIII
bb174a8d-7ed9-5040-8249-b66aee897132 | note | Verifying Document - IANZ Accredited Report
66c5c54b-1076-53cc-892c-16fd040dfda3 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
54bb250d-1164-5d06-b952-caa8a16e2924 | note | ○ Results to Engineer 2 wks before importing
f4715e37-7564-538a-b6bc-487264603d64 | note | Verification Activity: Activity - HP
87ba601d-f22f-517e-b051-e6aa3e1317a4 | note | Verification Activity: By - ENG
adcc761f-5e53-5005-86f3-480d4f123fd3 | signoff | AUTHORITY HOLDPOINT
4c2e10ea-a175-5501-8be0-7d21ee763da0 | checkpoint | 1.2.2 - Particle Size Distribution
3f78be19-5dc0-5a94-856e-16319da0c146 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
55384137-ebc9-5d31-b8cf-193274234304 | note | Acceptance / Conformance Criteria - Max Particle Size 53mm
bd879df8-6647-535b-92d3-71c355e11970 | note | ○ Max 10% passing 13.2mm sieve
33befdab-e8cc-53bd-86f4-3e1fe7a022b3 | note | Standard / Specification - Appendix XVIII
48a6b8c6-5784-56f1-bf51-9720e4dbafac | note | Verifying Document - IANZ Accredited Report
e173c21b-cf0c-563c-a3ae-8fa2d28dbbb3 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3
943b5235-da03-5c2b-a373-33983d6f6a4c | note | ○ Results to Engineer 2wks before importing
4bb95a93-2be2-53d3-93ec-fd0353562eef | note | Verification Activity: Activity - HP
e68bc3d5-f9c9-5a6b-bb96-686566b9fec6 | note | Verification Activity: By - ENG
cee16103-a60f-5369-a9e2-e6254b70928e | signoff | AUTHORITY HOLDPOINT
0db13832-0d7b-5811-9f2b-9036b5e2af35 | checkpoint | 1.2.3 - Weathering Resistance
948550e4-3ec5-595c-a387-9ae2f109058f | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
be81eb03-fb6e-5c51-8c0c-eba179bd0121 | note | Acceptance / Conformance Criteria - CA or better
4a67f625-1073-5180-8062-f598d42bbec9 | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
b5f62c44-a545-5811-a235-f0150daced0b | note | Verifying Document - IANZ Accredited Report
cd72ab1b-0e87-57ca-8fdb-e7767554a5ef | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
06b19ba1-6f34-5a8a-943e-e9bf4068b8e7 | note | ○ Results to Engineer 2 wks before importing
134fffe0-bb95-5474-acff-4a0b80d25681 | note | Verification Activity: Activity - HP
3580e4fd-7fea-50c9-b73b-1d753f2ebcb4 | note | Verification Activity: By - ENG
f8ad0c43-4aea-5958-8a75-98ef19bda0d6 | signoff | AUTHORITY HOLDPOINT
5f985f9c-dd22-577d-8c94-898c7067297e | checkpoint | 1.3.1 - Crushing Resistance
7d88ae8f-aacb-5ba1-a9dd-37055c7c23bd | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
3a031fb5-ace4-54b7-b252-460cb31ce1b6 | note | Acceptance / Conformance Criteria - >100KN
f13071fb-691a-5c0c-bca7-10798e7568d5 | note | Standard / Specification - NZS4407:2015 Test 3.10
42024e8d-9dd2-5725-9f08-4ca5ee761e3d | note | Verifying Document - IANZ Accredited Report
675f19af-3f03-5ad3-9a88-86c2a2a6163b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
1ea7cb42-aff4-527d-8938-d60909eed40e | note | ○ Results to Engineer 2 wks before importing
98ebac46-eddd-5a3f-9636-73e72d829ab2 | note | Verification Activity: Activity - HP
9024e84e-5bb7-5456-943b-72dfc7f76479 | note | Verification Activity: By - ENG
e1cc8513-47de-563e-b2e1-210990b82f31 | signoff | AUTHORITY HOLDPOINT
679d1cf7-1c37-591d-ade8-40e0077a84fa | checkpoint | 1.3.2 - Soaked CBR
b17195be-2350-537e-a4f1-c686c9597816 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
41a6630f-929c-5520-af0d-c4d419268605 | note | Acceptance / Conformance Criteria - >25%
e7eee3f0-beb3-5fb6-87d0-fe4ea1a7ae74 | note | Standard / Specification - NZS4407:2015 Test 3.15
63e32444-6124-5d0b-9b01-2bf96924ad2b | note | Verifying Document - IANZ Accredited Report
b8a06ec3-447a-5a39-9abc-a7b864014a51 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e76faaf1-fe0c-5c37-9516-d8a9bac6924a | note | ○ Results to Engineer 2 wks before importing
e63c1d29-1a59-5bc0-8852-a4b89c27d701 | note | Verification Activity: Activity - HP
0bf3c9eb-ca20-524c-995e-6d89f61b796c | note | Verification Activity: By - ENG
22329d2a-5eb0-5d2f-a227-929669dd0fd5 | signoff | AUTHORITY HOLDPOINT
4ed8e59c-467c-5ed9-acf7-1b572e5a503d | checkpoint | 1.3.3 - Weathering Resistance
34bc591f-30c4-5f4b-b481-f749d39a491b | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
072767ee-0561-5a26-9ef8-64c69049d9ee | note | Acceptance / Conformance Criteria - CA or better
feedd065-2f88-54e7-8635-ebe561ed2ee7 | note | Standard / Specification - NZS4407:2015 Test 3.11
6d135723-edf7-55e4-b16d-59a27ac38342 | note | Verifying Document - IANZ Accredited Report
4a18710c-fdb7-545d-bf88-8d83d6544412 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
01c71aa5-4e8f-5d97-bef0-809cf3781743 | note | ○ Results to Engineer 2 wks before importing
475aa73a-9a71-5372-b0cc-560306eadffc | note | Verification Activity: Activity - HP
0ced78a5-267e-5b1b-834c-4e17421f1aa5 | note | Verification Activity: By - ENG
258e872d-a211-5144-a411-e1eacd40a379 | signoff | AUTHORITY HOLDPOINT
8cf048f8-1300-5e8e-a662-95d0f261ac5f | checkpoint | 1.4.1 - Particle Size Distribution
e5fa3848-73e3-523d-9284-2545c0d5fd87 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
44fcb242-d1f3-5d8f-92dc-8b0f10b6cff7 | note | Acceptance / Conformance Criteria - Fitting within standard AP65 grading curve
a3c7aaf0-6404-5902-867a-804015eb596c | note | Standard / Specification - NZS4407:2015 Test 3.8.1
4bc54ea8-a896-5fd2-b6ff-f9015d32b433 | note | Verifying Document - IANZ Accredited Report
f4909142-1a5c-58b7-8333-7b8b6d085886 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
ac296b3c-0da4-551c-8922-98e75b0094c8 | note | ○ 0-400 - 2 tests
b58ff792-a573-5c7f-a938-085f3316b50d | note | ○ 400-1,500 - 3 tests
4746ccc3-3f06-534b-b2eb-db8a12c27607 | note | ○ 1,500-4,000 - 4 tests
c66bc070-6799-5bb2-8636-cb3fb4b6edc1 | note | ○ >4,000 - 1 test for each additional 1,000m3
93883602-1fbc-55f4-896c-67067d7eb706 | note | – Results to Engineer 2 wks before importing
f0e7814c-c9ee-5263-add3-e23f07a7b09c | note | Verification Activity: Activity - HP
90d665bf-f40a-59a0-af98-b2880beaf127 | note | Verification Activity: By - ENG
f922a06d-cac3-5c61-8fcc-c4925e79effc | signoff | AUTHORITY HOLDPOINT
47abf264-56bd-59c4-a276-c61dae763677 | checkpoint | 1.4.2 - Maximum Dry Density and Optimum Water Content
4499f4ad-f72c-5f73-8230-68caed1cb4cb | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
e3759e13-1749-5c96-a2f4-94d15751df05 | note | Acceptance / Conformance Criteria - Report Value Only
85f030b9-0f34-564e-8ed6-4fac153ef291 | note | Standard / Specification - NZS4402:1986 Test 4.1.2
f2510355-2e29-54de-a9cb-66e844e25e36 | note | Verifying Document - IANZ Accredited Report
83646c8e-f4b7-595c-ab2b-76e89287b8c8 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
e666ed9c-a803-5724-97e9-8f6209591bdb | note | ○ Results to Engineer 2 wks before importing
e44d8f7e-e7e6-5752-9d97-68d459847a91 | note | Verification Activity: Activity - HP
11bc04c8-46da-5fcf-80ca-298bc5c2c362 | note | Verification Activity: By - ENG
1221a0cb-dfc4-5d49-965e-bb9d0085ffae | signoff | AUTHORITY HOLDPOINT
b2938728-cc53-58e7-9f1b-0baf459daaae | checkpoint | 1.4.3 - Plasticity Index
67fc375f-8de5-539d-ba76-5a0a1638c85c | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
782e2c95-0e1a-5478-ab4a-58b458395351 | note | ○ NZS4407:2015, Test 3.3 Plastic Limit
70e469cb-9e03-5e51-b3ee-b68ba0cf856e | note | ○ NZS4407:2015, Test 3.4 Plasticity Index
2e4c8fcb-5bb6-5dd1-b454-ebbad6d874a0 | note | Acceptance / Conformance Criteria - NP
8c944f3e-aac8-50aa-9931-e15ed0170446 | note | Standard / Specification - NZS4407:2015 Test 3.2 NZS4407:2015 Test 3.3 NZS4407:2015 Test 3.4
b207f059-6a83-5f03-b3bf-fb16a437186d | note | Verifying Document - IANZ Accredited Report
0c1b8321-ed56-565b-b159-9894c9cec91b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
b0e0af85-d46a-5e28-b08c-502a847308bb | note | ○ Results to Engineer 2 wks before importing
737b6779-90a8-5acb-92f8-a5def5c3d85b | note | Verification Activity: Activity - HP
f0f15341-5f32-5df7-9b82-bf2fbdbab5b1 | note | Verification Activity: By - ENG
2130d6d8-a12e-56f9-b162-c0c07b0bb707 | signoff | AUTHORITY HOLDPOINT
eda8ae89-4166-5dcf-b5c1-0555f7e90d29 | checkpoint | 1.4.4 - Sand Equivalent
48443824-0139-55f2-a533-12054bc550a0 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
9297c6c1-a4fb-5783-8180-20eb7a73824b | note | Acceptance / Conformance Criteria - >25
8c1daf38-8a05-5acd-8b8d-8694a9a9ea77 | note | Standard / Specification - NZS4407:2015 Test 3.6
78bd499e-8a65-5b60-a872-7542e50ee79f | note | Verifying Document - IANZ Accredited Report
f5f856c0-165b-59b9-bcc8-0878e288a7c9 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
0ef4d92e-8673-5ef5-81d5-091f65cad3cc | note | ○ Results to Engineer 2 wks before importing
dbd73ed9-3c6b-58be-946b-193f01e5e124 | note | Verification Activity: Activity - HP
c5314346-dcd4-59a4-99a2-2f788de14d47 | note | Verification Activity: By - ENG
a4e028df-2c24-5c0b-b955-97ddb96388d8 | signoff | AUTHORITY HOLDPOINT
f674adf9-4247-5a76-b2e9-b3657e6ced65 | checkpoint | 1.4.5 - Clay Index
20acd18c-e04f-5a9e-9f71-2413af2e804e | note | Detail - NZS4407:2015, Test 3.5 - Clay Index Test Report
148661c4-7060-5082-bcb3-b2aba5208283 | note | Acceptance / Conformance Criteria - Report Value Only
2e708397-9b23-5d86-9c08-5436428c26a5 | note | Standard / Specification - NZS4407:2015 Test 3.5
cbf291b1-265c-5231-816c-3a4f1f08f704 | note | Verifying Document - IANZ Accredited Report
98d4c346-268c-50f2-8b33-f7ff9d44415d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
c06c540c-002a-5391-9285-c47efeec67dc | note | ○ Results to Engineer 2 wks before importing
e0134cbd-67f2-56b2-8b90-c8e4563c387e | note | Verification Activity: Activity - HP
383f7aee-61b1-5a1d-9fa0-e70f63b07ba9 | note | Verification Activity: By - ENG
85b694a7-1d1f-5216-b70c-8ab4eadd76df | signoff | AUTHORITY HOLDPOINT
c8b1d175-5f5d-5f00-9439-4d640014e228 | checkpoint | 1.5.1 - Crushing Resistance
01438abd-a7b8-5b30-9852-092688c76841 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
94841520-5752-56e5-8276-7094df24d800 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
33acede1-53b8-5ed6-a06e-54de2b7c5e7c | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
258f09ab-3e03-5e2c-9436-42b64a80f462 | note | Verifying Document - IANZ Accredited Report
75a2b696-b288-5e67-88f9-0f237b2f0d83 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
72a5b06b-398b-5018-9f6f-9c08f64cf1c1 | note | ○ Results to Engineer 2 wks before importing
98ba8984-a319-519d-9ef3-2058ca901299 | note | Verification Activity: Activity - HP
5eb4a7f6-748a-59c6-bbdc-937afdd0a7c6 | note | Verification Activity: By - ENG
c7885017-b248-587f-9d80-5265c567d250 | signoff | AUTHORITY HOLDPOINT
34e08bfa-b1e5-5a8e-952f-d8363084b498 | checkpoint | 1.5.2 - Soaked CBR
c7e2f01d-42bb-5bdd-9fd5-714022f95480 | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
83e3a001-3d3d-514f-9f34-63fb738bdf55 | note | Acceptance / Conformance Criteria - ≥ 60%
0d29adce-b152-50e7-afdb-641350392408 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
75d4f7d2-5801-55c4-a473-5dabe0060293 | note | Verifying Document - IANZ Accredited Report
aec3f8ae-fb87-5c72-9cbe-5c0c82a2e235 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
6adbab04-e7e7-5f17-a334-1196189ed69d | note | ○ Results to Engineer 2 wks before importing
bdbc63d9-44ea-5d56-be39-fe3a88959820 | note | Verification Activity: Activity - HP
7e4dcc56-d732-517d-b124-a4e54fe92bd9 | note | Verification Activity: By - ENG
21362b24-5eae-5d82-bf51-7063bc20fcbc | signoff | AUTHORITY HOLDPOINT
e0ee8b37-5207-5a67-9235-4db5443a5a46 | checkpoint | 1.5.3 - Weathering Resistance
8c02c934-636c-57e8-bbb6-973ec9d7a377 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
c2e973a7-3bda-5f85-9d60-f9e95b1e7862 | note | Acceptance / Conformance Criteria - CA or better
0c4b66d6-35d4-5795-91e6-6045f195c57b | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
4eb7d36d-4d27-5c49-b85d-7d7a0fbd6e39 | note | Verifying Document - IANZ Accredited Report
30d2ea4c-645d-5804-b20b-1172403f2745 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
8555ae75-b9f5-593d-a1fc-651952af38f7 | note | ○ Results to Engineer 2 wks before importing
df1ece9c-2429-5b93-a84b-46e922d930b1 | note | Verification Activity: Activity - HP
13d242ef-1556-579d-bf11-fc690a5246e4 | note | Verification Activity: By - ENG
307eadad-dc3e-520c-bd11-926abfbdf1a6 | signoff | AUTHORITY HOLDPOINT
be766fdf-de48-5496-8902-95cb926372dc | checkpoint | 1.6.1 - Particle Size Distribution
afc63c1d-7a5e-5ade-ba57-33e6f233757c | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
42ec3bcf-c697-5020-ac2e-a6e2f46aca61 | note | Acceptance / Conformance Criteria -
11b3b027-6462-50c9-b4bc-268e3b733f9f | note | – – – – – – – – – – – – –
7d6b9c5c-35af-5282-bcb5-5a886ceca8b3 | note | Sieve Size ¦¦ % Passing
5629087b-b521-5fe2-97de-1268342789e0 | note | – – – – – – – – – – – – –
0395ea83-31db-5cd5-b2be-921663413061 | note | 63.0mm ¦¦ 100% passing
76a59ec4-eb15-5ff1-8dcc-0e78f1a210a9 | note | 37.5mm ¦¦ 55-85% passing
f068d9c3-e2f5-56f1-9cbb-7a6a378942d4 | note | 19.0mm ¦¦ 33-65% passing
21b236f8-30b0-5a42-aab5-eb103f884a91 | note | 9.5mm ¦¦ 20-50% passing
4b451d00-ac48-5830-a03a-96b1c05b7e64 | note | 4.75mm ¦¦ 10-36% passing
cca22675-3c65-5263-8404-5c3a9a51fbe9 | note | 2.36mm ¦¦ 5-27% passing
cddbeb4e-e884-5418-99ad-4f7cc0735485 | note | 1.18mm ¦¦ 2-20% passing
ef14642a-0be7-5e00-8bdb-7e9184cf4e8b | note | 0.425mm ¦¦ 1-13% passing
3ce79264-d0da-5fbd-a58b-c3dfb85bbd4b | note | 0.075mm ¦¦ 6% max passing
7bc702a5-474f-50d0-9a8d-04d2394b435e | note | – – – – – – – – – – – – –
8a1b8243-d16a-5934-ae82-7d28f937e38b | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
52f228bf-99e0-5c09-b21a-92fbcff47a29 | note | Verifying Document - IANZ Accredited Report
f1a0c1a1-e058-5ca7-977d-12a089b95097 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
8c2053ec-407b-5cc0-be91-b580953454b5 | note | ○ 0-400 - 2 tests
5d3a0052-cd19-56e6-9e90-899c953ca979 | note | ○ 400-1,500 - 3 tests
89ccf57c-e416-5b9f-84ce-d03a610ed645 | note | ○ 1,500-4,000 - 4 tests
4520b710-b4af-58bf-85fa-e5a120cf40d8 | note | ○ >4,000 - 1 test for each additional 1,000m3
67f70142-0878-5eea-9773-0ad3252ac566 | note | – Results to Engineer 2 wks before importing
36f75e96-1cd3-59bd-9fd2-99902b66b7ff | note | Verification Activity: Activity - HP
f4223ca7-1e0f-5ec2-b1c3-92c4e2e7ad6a | note | Verification Activity: By - ENG
55f6b97f-a0ef-5509-80e3-4cbba5b25836 | signoff | AUTHORITY HOLDPOINT
caaf95fd-2094-5bb8-8bec-67f91091c1d0 | checkpoint | 1.6.2 - Shape Control
072ab6ce-8c41-5daf-9b44-a2849e82cab9 | note | Detail - Tolerance allowed from approved grading curve (%)
02c2a873-5fc0-52e6-8a33-5a71636c1f69 | note | Acceptance / Conformance Criteria -
e199ebe5-7b71-5340-9d2b-407cb752b83f | note | – – – – – – – – – – – – –
14b7eba2-f6d1-511b-9be1-b7ad57a65204 | note | Sieve Size ¦¦ % Tolerance
a567df51-0446-5eae-8c34-17d89de23ed3 | note | – – – – – – – – – – – – –
2b931a6a-cb2e-5ddb-91bf-cb0f28d711ca | note | 37.5 – 9.5 ¦¦ 34-50%
6c446530-aae5-55e0-9408-8e11ff380f14 | note | 19.0 – 4.75 ¦¦ 18-40%
acba0edb-138f-5a17-ae06-50e22b297ddb | note | 9.5 – 2.36 ¦¦ 12-32%
ad1be66f-7aa5-51c3-8883-709e1258b9d1 | note | 4.75 – 1.18 ¦¦ 6-24%
ccf8fba8-e634-5ecd-81e7-4692492db16d | note | 2.36 – 0.6 ¦¦ 2-20%
6bef8454-4bea-5d39-838e-3194471d9c2f | note | 1.18 – 0.3 ¦¦ 0-15%
325124ed-f1ad-517a-a700-b18c2fe668e0 | note | 0.6 – 0.15 ¦¦ 0-12%
445280ea-7c7f-58d9-b79e-4dca086b82d5 | note | – – – – – – – – – – – – –
db26026a-1ed0-5962-8361-f5fb81cb6f01 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
1b8891b2-02bd-51d5-9d9f-16b878dc04da | note | Verifying Document - IANZ Accredited Report
69ed027e-c706-52b8-8cbd-6bb85407f7af | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
bb7398d3-0519-5ce1-a518-e93d6c143e28 | note | ○ 0-400 - 2 tests
b04b3f09-aea4-5295-9de1-c6f61b5f1524 | note | ○ 400-1,500 - 3 tests
42df31e6-a33b-5d1b-bc93-ea1ad69c7a1b | note | ○ 1,500-4,000 - 4 tests
da97a941-481e-5c38-81cb-3ba029faee0c | note | ○ >4,000 - 1 test for each additional 1,000m3
73468e33-5ed7-5e18-9492-707620ceaf89 | note | – Results to Engineer 2 wks before importing
e3f51ade-c2d4-5df5-aebd-167686e14dc6 | note | Verification Activity: Activity - HP
32d325e7-eef4-525f-ad8f-93f91502c71e | note | Verification Activity: By - ENG
6cff9c4a-facf-5300-bd4c-e1b20fd4bb30 | signoff | AUTHORITY HOLDPOINT
ed826021-51b3-5439-99ac-54c432e8af8f | checkpoint | 1.6.3 - Sand Equivalent
6b935366-f67e-515c-a5a3-716ca8a2ba3d | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
deb6986c-5b5f-5124-bbb1-c590aaaf4db0 | note | Acceptance / Conformance Criteria - ≥ 30
a8116b3b-0ed0-5bca-bc26-db27989c6294 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
180bbf1d-5f37-51f2-bfe9-32f9a8a9bf5b | note | Verifying Document - IANZ Accredited Report
6100e88f-e8fb-5f8d-a878-efffecbb87a1 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
1e24a64e-af4c-5175-b765-7311dcda9797 | note | ○ 0-400 - 2 tests
e8034803-9506-5300-baf0-3fb3b6cae353 | note | ○ 400-1,500 - 3 tests
9364c3fc-4d3f-533b-897e-91387d3ae7fa | note | ○ 1,500-4,000 - 4 tests
591d2da9-ec93-5fbf-8ae9-d8e6d078e4f1 | note | ○ >4,000 - 1 test for each additional 1,000m3
dff31db3-f635-5ad0-9a10-ea9664b04659 | note | – Results to Engineer 2 wks before importing
f8fc7d49-adf6-503c-a908-353080911e3f | note | Verification Activity: Activity - HP
182aaa08-edb4-5bd7-bf24-7e7928e9e1a2 | note | Verification Activity: By - ENG
6901966c-9669-50d5-b04b-3eb27016ca86 | signoff | AUTHORITY HOLDPOINT
c2630989-ebd4-59ac-9b00-da45e0ca90d7 | checkpoint | 1.6.4 - Cone Penetrometer Limit
45854cf4-a7cc-56b7-a35f-9e9a94dd9b18 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
b09f0cfc-7499-5964-be03-ac394212238c | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 25
fb978d9a-b5e5-5c3d-bbe1-d440726ecbdc | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
af048f81-5ab3-5d05-ba01-5669402fbf9c | note | Verifying Document - IANZ Accredited Report
84fe6473-678c-561e-a314-ebdd83e258d1 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
9c31e1a6-cc6b-54df-b083-469171a060d0 | note | ○ 0-400 - 2 tests
63f1651a-c0c7-59c9-bd3b-dbc8a6aeb6e9 | note | ○ 400-1,500 - 3 tests
f0d6d72d-f7b5-5cd5-9481-13f81b304b9d | note | ○ 1,500-4,000 - 4 tests
fe810a58-c474-5d4b-b602-1a1b5d80e188 | note | ○ >4,000 - 1 test for each additional 1,000m3
41bca39c-b3e3-5d2f-b5ef-91b4516adbd7 | note | – Results to Engineer 2 wks before importing
57c52052-205f-585d-b1bc-eb46f324eab5 | note | Verification Activity: Activity - HP
5f81fcd4-b178-55fa-9921-428e903821e0 | note | Verification Activity: By - ENG
4a85db6d-5756-5b33-847b-4c92a593ed52 | signoff | AUTHORITY HOLDPOINT
9b54ee39-e5f8-5b11-928b-a66ec127db33 | checkpoint | 1.6.5 - Plasticity Index
fb9a449a-1a4a-5df9-8249-26cf2be37b68 | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
2752871c-0019-5173-95cb-65d927587771 | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
5f027b7c-31bc-59b1-8231-3121eed86ae2 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
0c92e546-076c-527b-b38d-91e0f561202e | note | Verifying Document - IANZ Accredited Report
60e59c0a-05af-52af-915a-d6bed6ce69c0 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
ccb3c2b5-dfec-5d53-a744-f7a852c817dd | note | ○ 0-400 - 2 tests
ba507eb1-e82a-56fc-b70d-d11675ad30dd | note | ○ 400-1,500 - 3 tests
186dfb54-3c65-5a2e-bab5-eb9e89f59b18 | note | ○ 1,500-4,000 - 4 tests
1cc39e36-02ed-5c01-a2e8-be413be2b95d | note | ○ >4,000 - 1 test for each additional 1,000m3
438ac739-c2c2-502c-9d36-6550e6a92373 | note | – Results to Engineer 2 wks before importing
979107d4-e7f1-5aa8-bf6e-6f5dafcfa936 | note | Verification Activity: Activity - HP
a285c70f-0706-5fc5-a637-b7813541b9ac | note | Verification Activity: By - ENG
cbc9d276-320b-5638-9c2a-31281d96a6ba | signoff | AUTHORITY HOLDPOINT
dcab115c-9154-5fdd-a72f-f20bf343f4a3 | checkpoint | 1.6.6 - Accelerated Weathering
7b7bf50b-d26b-50d3-b58f-0ca514fe90bf | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
f6195fa8-f77d-5cbb-b6d7-2b3b297f9dc9 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
7b7add49-4589-5d15-a11f-f4479718ddc5 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
2a485930-59a1-56a1-a0ef-d611fe9974a5 | note | Verifying Document - IANZ Accredited Report
b4cbc3ca-8881-58a2-a256-622071605df2 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
cc32e1b4-bc25-547d-9357-875b53db9eff | note | ○ 0-400 - 2 tests
294d0c37-3745-5cc5-968d-e3d9f00aac15 | note | ○ 400-1,500 - 3 tests
21b5e54a-2d44-557c-b87b-f430fb85ddfa | note | ○ 1,500-4,000 - 4 tests
db1245eb-fd85-550f-87fe-483b9a7e5126 | note | ○ >4,000 - 1 test for each additional 1,000m3
184a9b66-ce16-5803-b3b9-1397eee2e571 | note | – Results to Engineer 2 wks before importing
0624afcd-70e1-5e22-bb1e-c140fd945959 | note | Verification Activity: Activity - HP
6535c7e0-2aa6-59aa-b040-02bc1c99aa03 | note | Verification Activity: By - ENG
6b9745a5-966c-5488-8ec3-e653d9f85eb5 | signoff | AUTHORITY HOLDPOINT
7a800fc0-1e63-543d-b3eb-9b78df73e3a7 | checkpoint | 1.6.7 - Maximum Dry Density and Optimum Water Content
8b8af90a-b043-580a-9706-0b0284cda8b5 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
90d0e7a4-33af-58b2-96ed-fb60c6c8bae3 | note | Acceptance / Conformance Criteria - Report Value Only
8f561e22-a37b-5b89-a9a4-8e52019697b5 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
243dcd90-b765-58c3-857c-3b75b4f3f35a | note | Verifying Document - IANZ Accredited Report
88569e98-785a-51b8-a81d-01ed2a58e76a | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
f263d608-a142-56ee-ada0-08b28834f794 | note | ○ Results to Engineer 2 wks before importing
424c78fd-7b32-5a9d-8c9c-3835c046f282 | note | Verification Activity: Activity - HP
fb972efb-64a1-5490-bb19-07834a778a5f | note | Verification Activity: By - ENG
be7f0025-4d03-5d0c-8da9-84b785a21758 | signoff | AUTHORITY HOLDPOINT
d7a6912e-9edc-5761-b53b-87858c42b973 | checkpoint | 1.7.1 - Cement Modified Maximum Dry Density and Optimum Water Content
ed4cf536-0221-54d7-81dc-d614b8827d21 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test using 5% cement
e292a394-6f92-545f-948f-132aaa47e5e3 | note | Acceptance / Conformance Criteria - Report Value Only
60a25b7d-173b-5776-b692-f77154f3e7e4 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
4c289582-16b7-524d-b1ba-367d474ba083 | note | Verifying Document - IANZ Accredited Report
41e753e2-5147-581b-a0b3-bc3a6ad2f01a | note | Testing Quantity Required (based from schedule qtys) - 1 Test at 5%
4e2c09ca-d123-561d-8649-5e53557c2147 | note | ○ Results to Engineer 2 wks before importing
525d7eb6-996d-5130-b208-8a8fc6a87dd0 | note | Verification Activity: Activity - HP
9bb77728-008c-5b3c-9889-d0b72a9e7364 | note | Verification Activity: By - ENG
27e8ec3c-36e4-540a-92b6-c2263eb72b72 | signoff | AUTHORITY HOLDPOINT
4c1005da-b170-5f17-acaf-a0b8efdfc978 | section | SECTION 2 – SUBSOIL DRAINS
3a9aa7b7-54e5-5092-9ef8-3e33a828f3f5 | checkpoint | 2.1.1 - Subsoil Drain inspection
7868e328-4d23-5691-8770-cae5b4d4f551 | note | Detail - Subsoils to be placed below kerb lines and inspected by Engineer
3bcb6d41-bae3-5deb-9491-2c7d228b1520 | note | Acceptance / Conformance Criteria - Engineers Approval
d57e16ed-6919-52c1-95f7-70fd58165787 | note | Standard / Specification - PS 17.6.3
c577da4a-72fa-5c18-b4c8-55b22115f979 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
93e1a397-b736-5c9a-8ebf-dc57911d4862 | note | Verification Activity: Activity - I
41dd316c-c3e0-5062-be0c-067fe9eea269 | note | Verification Activity: By - ENG
e56ae963-bc62-520f-b544-a42dcdae9917 | checkpoint | 2.1.1 - Excavation
cdb3458c-7630-5e66-b6cb-ca25937d57ce | note | Detail - Excavtion of Trench should be within tolerances.
40d99778-f0aa-5e21-a611-7908c054c452 | note | Acceptance / Conformance Criteria - 335mm deep x 300mm wide
5ab95e11-ee18-5b52-9137-a2541cb12f0f | note | Standard / Specification - Drawings
d6faa342-f2ae-5806-b119-ca7da8667f84 | note | Verifying Document - Checksheet
6d182f0b-404e-52bc-a7e2-244b7b2bd3a5 | note | Testing Quantity Required (based from schedule qtys) - While Construction
3a47aaea-d771-5ddf-8085-2e93554bcfd9 | note | Verification Activity: Activity - M
79b0301d-dd74-539a-a7c8-7e937d007611 | note | Verification Activity: By - SE
082565ed-d47c-553b-9b97-ad38d4e14da1 | checkpoint | 2.1.2 - Placement of Bidim
344b9e30-8f40-58cf-b76d-c1ca2bf7adf5 | note | Detail - A29 Bidim to be placed andd wrapped around Trench.
631b007d-bd15-5f77-a730-97ae04418b88 | note | Acceptance / Conformance Criteria - Minimum Width 300mm.
6beb958f-f379-5d02-a555-4ecda4642f8c | note | Standard / Specification - Drawings
4ef1ca6a-6fb4-55b4-bda0-c4a927c86648 | note | Verifying Document - Checksheet
803bc173-e3bc-52d1-9793-cdbc1bb2a959 | note | Testing Quantity Required (based from schedule qtys) - While Construction
0988b146-098d-536f-bc8e-a9fbca975f8a | note | Verification Activity: Activity - M
514da5a4-b747-5c78-afdc-210572ab4f06 | note | Verification Activity: By - SE
dde19193-4b1f-5c77-8127-b5518f3fbd5d | checkpoint | 2.1.3 - Cushion (Bedding)
b4cfd0b2-3b4c-58c8-90e2-e551dfb4f122 | note | Detail - Pipe must have 75mm of Cushion. Drainage 60:40 Material to be used.
c294d646-8459-5aea-8bc2-487924083423 | note | Acceptance / Conformance Criteria - Minimum 75mm
0744bd33-a98a-57f8-b154-902dc44dc06e | note | Standard / Specification - Drawings
64d5b4c2-6fed-5710-9436-b106a1b24db6 | note | Verifying Document - Checksheet
407e2e0f-286a-5aea-bb87-a68dd38c0d09 | note | Testing Quantity Required (based from schedule qtys) - While Construction
c14d4c54-57ad-5972-b6f5-2785b804d38d | note | Verification Activity: Activity - M
582f1401-3333-5ddf-a464-d26d70abc96f | note | Verification Activity: By - SE
70e501d2-021b-5208-8c4a-a75a34ef2fb5 | checkpoint | 2.1.4 - Placement of Pipe
a9ebf62b-949f-5767-9ece-c494ff7acb15 | note | Detail - 110mm Perforated Pipe to be laid Down
122428a3-f35c-5817-b700-62e537a55f99 | note | Acceptance / Conformance Criteria - As Per Drawings
5238ffd0-8d3c-5491-be3c-84e34eb7008f | note | Standard / Specification - Drawings
37de8b47-21c0-5782-962c-3a8134f02583 | note | Verifying Document - Checksheet
41d449b3-e63c-548e-94b9-a01f7c8176c2 | note | Testing Quantity Required (based from schedule qtys) - While Construction
b89b98b6-fe33-5794-9a08-989a50473c2e | note | Verification Activity: Activity - M
5a1b0ef7-6f45-5fa4-990e-0655251c80b6 | note | Verification Activity: By - SE
f1f568b8-4530-5632-a55b-175f9a06927b | checkpoint | 2.1.5 - Backfill
0acee75e-890f-5323-b025-f28d84e82fcc | note | Detail - Pipe Must have a 150mm cover from Bottom of Pavement. Drainage 60:40 Material to be used.
81530b6c-07f7-553f-9624-771066d2518b | note | Acceptance / Conformance Criteria - >150mm Cover
a443c08d-9a74-5bfb-ae0c-f94d513f8a21 | note | Standard / Specification - Drawings
a9674791-131e-5bba-a956-b2008e9bd8db | note | Verifying Document - Checksheet
28c038e7-6229-5510-a7ab-b847ddc50ff1 | note | Testing Quantity Required (based from schedule qtys) - While Construction
30b7238b-eb99-5a30-9d5b-fb624982f99f | note | Verification Activity: Activity - M
f74c140a-a34a-5cd9-8623-8632d710cae4 | note | Verification Activity: By - SE
8a9f9b68-09a7-55c6-8987-51db7b75daad | section | SECTION 3 – PLACEMENT OF GEOGRID AND GEOTEXTILE FABRIC
ccf9594e-d49f-5329-bf83-626fe37fa59f | checkpoint | 3.1.1 - Placement of Geotextile Fabric
415e5660-d373-530b-919a-5202818ba849 | note | Detail - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
2024858b-c0eb-5e8c-bd06-e789df837600 | note | Acceptance / Conformance Criteria - Visual inspection
cde3dff5-c040-532f-9565-be662c449405 | note | Standard / Specification - NTC0097
adb1d676-72e5-5de3-aec7-cdb1a68471f5 | note | Verification Activity: Activity - WP
e6b6b0a9-36bd-53f2-a597-d57f65f8d644 | note | Verification Activity: By - ENG
ac5f9cb4-cd40-5b3c-8bd5-624f64275a3b | checkpoint | 3.1.2 - Onsite Check by Engineer on Geogrid
4f5ebb76-0931-5c69-b304-957ecbe93037 | note | Detail - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
4b2f85c5-b2a2-59e0-8675-d17f58111be6 | note | Acceptance / Conformance Criteria - Visual inspection
c6fa8314-912c-547f-8d10-b9a954bdbdc6 | note | Standard / Specification - NTC0100
15e337d8-0423-5638-a916-94c470827d39 | note | Verification Activity: Activity - HP
93d51212-68bb-5070-9c33-12d1a099ac41 | note | Verification Activity: By - ENG
eb08b0ac-65e3-542c-979a-67945f78695a | signoff | AUTHORITY HOLDPOINT
030f9409-3014-523d-91b6-81f9b1a23f7e | checkpoint | 3.1.3 - Placement of Geogrid
166e9956-1924-5458-85f2-6719bbe4e5ce | note | Detail - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
f9c619ac-cb30-5417-9146-6cc67c38db53 | note | Acceptance / Conformance Criteria - Visual inspection
6ec490da-5f83-5d26-b01f-48becd32dace | note | Standard / Specification - NTC0100
77e52eaf-1927-5f7d-9ed9-501a797ccaa0 | note | Verification Activity: Activity - WP
e5830aea-f1d0-5c3a-9135-dbedab1df752 | note | Verification Activity: By - ENG
c85b9499-6bb3-50cc-bff6-dda40dbcab08 | section | SECTION 4 – SUBGRADE IMPROVEMENT LAYER TESTING (UNBOUND AP65)
fbb83861-2f3e-5f9e-b7aa-a3a6f3dddc54 | checkpoint | 4.1.1 - Plateau Density Test
c48daefa-a277-52ee-bba6-769b0ab0db6f | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
b5b4de30-5108-5a03-81cc-35530b3904fe | note | Acceptance / Conformance Criteria - Plateau Density Report
941c8fff-c4a4-534a-9b0a-7128f4cffd9a | note | Standard / Specification - NZTA B/02 7.5
deb94de3-9a57-5ffd-be75-78a102cf2c96 | note | Verifying Document - IANZ Accredited Report
e0fe0d02-b179-5f2e-8524-ac2e5806a203 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
fc9bf276-24bb-5b36-8897-c8e8a807af69 | note | Verification Activity: Activity - I
20c27d30-bfe4-5aa7-b9d7-f43375c665e3 | note | Verification Activity: By - SE
8978f6d9-9591-5dfb-be5a-ffb27e512bcf | checkpoint | 4.2.1 - 3m Straight Edge
088ac201-f650-57b1-b6bc-f73ae733637f | note | Detail - Formation check to ensure surface is smooth
4b2ae4f8-e2fd-55bb-8d15-850187cae87e | note | Acceptance / Conformance Criteria - +/- 10mm
7a7eb108-7af9-5f00-81d5-45280caae87f | note | Standard / Specification - TNZ B/2 7.7
d4bbf039-0622-5518-8cea-7e16a0b6460b | note | Verifying Document - Check Sheet
b748789f-5e3f-58ef-8c72-932d96d35498 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
9acae8a8-22e8-5d47-b432-47bb2acf0616 | note | Verification Activity: Activity - I
d0644fb8-e0ce-550d-a37c-ba0441023c2f | note | Verification Activity: By - SE
706bd440-6a52-559d-9175-cad4665e6d2c | checkpoint | 4.3.1 - Stringlines or equivalent
29d7b230-00ec-5e79-bbae-95ef785924e0 | note | Detail - Stringlines or equivalent to check finished height of surface
5d47af75-e454-5d22-be07-1bfa69a2c953 | note | Acceptance / Conformance Criteria - -25mm + 5mm
660b65e9-ac2b-510f-994a-42e76760fe5e | note | Standard / Specification - NZTA B/02 5.1
9021868d-dc91-5f0c-80ec-c887b901b5f0 | note | Verifying Document - Check Sheet
9eb68c1d-38bc-5318-8d7c-767cb0c507cf | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres, 1 set = 5 tests
5de7bb6e-ac69-54a3-a800-361f0cc08207 | note | Verification Activity: Activity - I
bb65ba39-4fad-5d33-acc7-ba525da961e9 | note | Verification Activity: By - SE
5fa3f95a-3bc5-594a-9cd0-86a23e986f7a | checkpoint | 4.4.1 - Compaction - NDM
b3e0a7c7-932d-5cdf-976c-9887a8a4b92a | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
51c3766d-56c5-5c8e-a7db-7eec9003e34a | note | Acceptance / Conformance Criteria - Ave >95% of MDD
6815098c-c50c-59ae-b4a3-91930674c259 | note | ○ Min >92% of MDD
2a847921-bc4c-55ee-ba71-f9fe7cfbd5aa | note | Standard / Specification - NZTA B/02 7.6
82fcedde-721f-53bb-b393-a4703ea904a2 | note | Verifying Document - IANZ Accredited Report
098882bb-07d1-5c67-9f2a-6f34c3e36ea5 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
1dec6fc1-0382-5cbe-8b6f-a1cc7e3fdb1d | note | Verification Activity: Activity - I
1e3dea94-7f3d-5b12-b985-918274ad160c | note | Verification Activity: By - SE
11f5f52e-5681-4508-8566-1ff68828d2c1 | checkpoint | 4.4.2 - Benkelmen Beam
25cd01df-96b7-5a7d-bd58-daf5a95e75db | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane. Unbound layer.
6554958c-26b0-5c81-91a6-31b28f5488a0 | note | Acceptance / Conformance Criteria - 90th Percetile: 2.43mm
d6be88d7-21e4-56d1-bd8b-2151dfae5e48 | note | ○ Maximum: 2.9mm
d493d0bc-b68e-580b-aa69-5c13f24e9c3d | note | Standard / Specification - PS 20.14.5, NTC0160
1871db32-e221-5f53-8c6c-755b8593c002 | note | Verifying Document - IANZ Accredited Report
3e912a8a-f7e5-5ebb-ae88-fabe6a67c1c5 | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
a857019d-9340-5c08-9daf-1792e70d307b | note | Verification Activity: Activity - HP
dbba3f50-f2fc-58e3-97e7-18e16a948bee | note | Verification Activity: By - ENG
b00d6f4a-d5b5-42ad-be81-c0f9188e3db7 | signoff | AUTHORITY HOLDPOINT
7f714426-2f7b-568b-bd6a-870227ac8b5a | section | SECTION 5 – CEMENT STABILISED SUBBASE LAYER CONSTRUCTION
f23d3bcf-da57-5faa-8a63-954c685b2a11 | checkpoint | 5.1.1 - Plateau Density Test
cc5f710f-c4ed-5c9b-a3be-990e22dfa28f | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
bf533fd2-ad71-5e44-9c36-a61901c633a6 | note | Acceptance / Conformance Criteria - Plateau Density Report
2fce7f8d-8a25-52b9-b95f-e0f6009718de | note | Standard / Specification - NZTA B/06 7.6
46f34ce2-7eab-5e4e-9b00-7899202a71eb | note | Verifying Document - IANZ Accredited Report
12413265-7538-57d2-9e63-9a00e79dce81 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
3af0906a-5adf-5b4d-a703-94ce4401a938 | note | Verification Activity: Activity - I
dd208442-5db2-5e6f-b924-5361162f923a | note | Verification Activity: By - SE
519755ef-020c-5639-a123-8278fec8211a | checkpoint | 5.2.1 - Mat Test
3af287c4-0c7b-586e-a188-04e717f43c63 | note | Detail - 1m2 Canvas - used to check the 24kg (as per Lab Report) of cement being used per m2
15827eea-b40a-53f9-8d61-1dc6fbcc0bf9 | note | Acceptance / Conformance Criteria - Visual inspection, check sheet
3b271596-991e-50f5-adac-4db47c83bc17 | note | Standard / Specification - NZTA B/06 7.3
021e202a-7448-56a9-832d-5154ae51f643 | note | Verifying Document - Stabilisation Check Sheet
1299122d-27ff-5fc0-9414-bd10351d8c12 | note | Testing Quantity Required (based from schedule qtys) - Every 400m2
1ae9d442-98d0-5a35-811f-6e73fd734ab1 | note | Verification Activity: Activity - I
66a8b26d-f02d-5534-82ae-2069436fc603 | note | Verification Activity: By - SE
216475f9-90fc-539b-a7f1-2cbd864aa2f9 | checkpoint | 5.3.1 - 3m Straight Edge
2799ccef-e235-5fef-acb3-02f0188c0289 | note | Detail - Formation check to ensure surface is smooth
e663fc4b-5283-54b5-baa3-8def825e970d | note | Acceptance / Conformance Criteria - +/- 10mm
4355a172-055c-56ae-b53a-eec1d136258b | note | Standard / Specification - TNZ B/2 7.7
5f278734-eb6f-5a9c-a5dd-7d6b03cdc8ea | note | Verifying Document - Check Sheet
a17d7473-6bc7-5453-b39d-c60b35032160 | note | Testing Quantity Required (based from schedule qtys) - Every 20m Centres, 1 each lane
13a51fcf-8054-552f-bb6c-05308400b6b0 | note | Verification Activity: Activity - I
342a1c0a-fc4e-5caf-b169-bd55eb9de0b7 | note | Verification Activity: By - SE
bae58215-8e95-53f1-a9bb-6b791787c1cb | checkpoint | 5.4.1 - Stringlines or equivalent
44d49f23-c3f2-58b5-b0d0-821852551e99 | note | Detail - Stringlines or equivalent to check finished height of surface
ce5b35be-82e1-5799-8ac9-d045425e8399 | note | Acceptance / Conformance Criteria - -15mm + 0mm
e248cf33-c919-5c6b-9dc4-29eb13a53c94 | note | Standard / Specification - NZTA B/06 8.2.2
970703c8-ef3c-5d54-8639-053c64ddeb76 | note | Verifying Document - Check Sheet
082f348d-cbc0-55ae-949e-0258d86692e7 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres, 1 set = 5 tests
27f78099-aac1-563c-a55e-9e8172fdee3c | note | Verification Activity: Activity - I
1e03d02a-991e-549b-a9f7-8e740b9b36ee | note | Verification Activity: By - SE
f640c8ea-d18b-5d5e-b3e4-62ed7ea38a47 | checkpoint | 5.5.1 - Compaction - NDM
b5c1649b-be4b-5e88-9bd7-a9b789892514 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
35590d4f-df2c-5301-8a1c-333294b4fe3f | note | Acceptance / Conformance Criteria - Ave >95% of MDD
3be65a71-19ee-5288-aeb9-d3e145807af7 | note | ○ Min >92% of MDD
29e0cac3-6215-5876-9ee9-729d7a1541a9 | note | Standard / Specification - NZTA B/06 8.1
1b527a3e-999d-5791-bfeb-2d7d1ee56548 | note | Verifying Document - IANZ Accredited Report
15699b62-4a02-5811-a39c-2dba1a235dab | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
df5faff6-3ef6-5c5d-a445-64da9f246d62 | note | Verification Activity: Activity - I
c55b1a8c-9950-5b09-b5da-294eebac1360 | note | Verification Activity: By - SE
63167d57-bcbc-581f-8f9c-e3d4369162fb | checkpoint | 5.6.1 - Curing of Stabilised Surface
5fbe1084-a0c0-584a-b744-289e95a14bc0 | note | Detail - No traffic allowed on stabilised surface for 7 days unless approved by Engineer
4bb833fe-c737-50ea-aade-317352e5de71 | note | Acceptance / Conformance Criteria - Stabilisation Check Sheet
66749a5e-75d2-5be7-a277-4e7c57ed56a5 | note | Standard / Specification - NZTA B/06 7.8
5fb8d73b-2c34-5068-bc56-b9c2b4d6b5e2 | note | Verifying Document - Stabilisation Check Sheet
82c9d842-3f9f-524e-9214-e457c7b4eb2d | note | Testing Quantity Required (based from schedule qtys) - Upon Completion of 7 day period
fbdf4a58-a344-562c-9f10-5ed969d8bfd0 | note | Verification Activity: Activity - I
3c4a46cc-cdac-55f1-b0a5-994f7af0dfe3 | note | Verification Activity: By - SE
19525c46-c718-58f4-85f9-e34ae46fdf46 | checkpoint | 5.7.1 - Benkelmen Beam
98786ce2-9ffe-55bf-88e6-8d370dff77d5 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
948c2021-2367-5312-96ec-6df9102a7a29 | note | ○ Unbound layer.
95b04bd6-2c3a-5290-99c3-7ce0ca1fe8dd | note | ○ Cemeneted Layer.
17bf2a14-2bb1-59bd-a0f2-015eabcdfd64 | note | Acceptance / Conformance Criteria - 90th Percentile: 1.03mm
04e51b7d-2d03-52eb-b179-1ca4f280d344 | note | ○ Maximum: 1.19mm
f52601d8-0668-549f-a046-fce27556bf31 | note | Standard / Specification - PS 20.14.5, NTC0160
972b4f4e-816c-5b56-b816-0455d7fa1036 | note | Verifying Document - Test Report
c603ed99-a2cf-5b91-b478-1f9022478da4 | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
7e0782e8-31b9-5c50-94d1-65083b32ce10 | note | Verification Activity: Activity - HP
bba8f27a-aaf8-5ac6-954b-6be5ef86e47d | note | Verification Activity: By - ENG
975a7f97-1e87-4e17-84ed-4b306dfa317b | signoff | AUTHORITY HOLDPOINT
f9cf37be-9207-5ed8-87eb-d126d9905e66 | checkpoint | 5.8.1 - Unconfined Compressive Strength with 5% cement
2ca3865f-8469-5707-9ac3-df7f8170c999 | note | Detail - NZS4402:1986, Test 6.3.1 - Unconfined Compressive Strength
b584ecb8-11fc-5350-9880-582a1f815d27 | note | Acceptance / Conformance Criteria - >5mPa
1032ea49-9f3b-5d9d-8541-1590f0406afa | note | Standard / Specification - PS 20.14.5
c6dc379a-a6fc-53d4-a0e4-5c24e738d37a | note | Verifying Document - IANZ Accredited Report
618dfbf3-99cd-50cb-aaa4-6029b352452a | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval - no less than 5 working days prior to placement of cement bound material
03b03acf-437b-562c-b9d2-d6d14956b206 | note | Verification Activity: Activity - HP
27ac9251-a399-5b62-b34f-b404ad43b2be | note | Verification Activity: By - ENG
7d5b7306-3909-57dd-b7b6-4ed4e8a45f24 | signoff | AUTHORITY HOLDPOINT
9bb2814f-26a1-4222-a180-801ad64fc39f | checkpoint | 5.8.2 - Mixed material testing (ITS)
fad6d81c-060c-5ed7-bc95-c11f5bab3fe0 | note | Detail - During mixing, the contractor shall take a pair of representative samples behind the mixing plant per lot or at a minimum of 2 pairs of representative samples per day. These samples shall be placed in a sealed plastic bag and cured for 1 hour before compacting into a mould and testing the indirect tensile strength (ITS) of the mixed material according to NZTA T/19
a754223d-8a59-55a1-84a7-37539205418f | note | Acceptance / Conformance Criteria - Report Value Only
ca1b4ece-b51c-587c-9a86-b1930426b06e | note | Standard / Specification - TNZ B6 7.5
d6148c98-e436-5b68-94ba-486f4ad8be09 | note | Verifying Document - IANZ Report
27e9dba3-171e-5cb7-9b71-fff9415fd15e | note | Testing Quantity Required (based from schedule qtys) - While Construction
7a5b71f3-6362-557b-a320-a57ac9f29391 | note | Verification Activity: Activity - HP
f99f322d-bb1c-5ae3-9070-ecf56985cf31 | note | Verification Activity: By - ENG
e7ec50d1-43ff-4bee-8b3d-2ee1bb7076c8 | signoff | AUTHORITY HOLDPOINT
1086364d-de9f-4ac8-a4fc-f3741dd8925e | checkpoint | 5.8.3 - Pre-cracking
bd277821-4e60-534a-af56-4b6079e0afdc | note | Detail - Pre-cracking of the cement-bound sub-base layer, shall be done between 24 and 48 hours after stabilisation is completed.
1a7abf99-2426-57e0-942a-84537035eaa7 | note | Acceptance / Conformance Criteria - shall be done between 24 and 48 hours after stabilisation is completed.
1d91d225-6df6-5cfe-8092-e69de92fc94e | note | Standard / Specification - TNZ B6 - 7.7
d44b88ae-c9a9-516d-8857-cc5ee87d7bad | note | Verifying Document - Visual Inspection
6f825cef-a40d-54ae-9386-2b0099444af3 | note | Testing Quantity Required (based from schedule qtys) - Across Cemented Bound Area
9b573b27-11d6-5326-b057-797c6ad8c08b | note | Verification Activity: Activity - I
b185f731-2159-5a96-ab43-89585b076ff3 | note | Verification Activity: By - SE
4f8a2be1-d186-573d-bbb7-0edff722e943 | checkpoint | 5.9.1 - QA Submission
c7436c11-9247-58a0-bac8-909fc8ff6be8 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
c4d0bcd4-7fa6-574e-874f-1f829aa06ed3 | note | Acceptance / Conformance Criteria - Engineers Approval
f367719d-e9d2-5282-9348-90f09ad25558 | note | Standard / Specification - Appendix V
2985bb19-e111-50ef-a961-2171be9903d1 | note | Verifying Document - All test reports
94ac8523-73aa-5f65-9057-2ced3838246b | note | ○ Material Test Results
6d34ef49-8448-5167-8d0f-06abff7e5028 | note | ○ Laboratory MDD
6d4206ec-6b89-52f1-b760-425c0526f5ac | note | ○ NDM results
f70053d0-1d53-564f-a20d-c339b393d893 | note | ○ Proof Roll
f2b7406e-53c6-5be4-9d24-5b6dbdb8fba7 | note | Verification Activity: Activity - HP
149cacc9-267e-5394-844d-7935b6f0b5b9 | note | Verification Activity: By - ENG
ea68ee32-4883-5055-b88e-cf365d2c5f26 | signoff | AUTHORITY HOLDPOINT
40980c22-697d-5bb0-a7ce-88d236624533 | section | SECTION 6 – KERB & CHANNEL PREPARATION
971e81ae-83b7-5da5-9a8c-d1c45890d09c | checkpoint | 6.1.1 - Stringlines or equivalent
e434b038-c141-5b69-aebd-40202139aab9 | note | Detail - Stringlines or equivalent to check height of surface prep
22c94c73-b0a3-5538-aef5-c2fe4f083604 | note | Acceptance / Conformance Criteria - +/-5mm
146ad516-7797-53a1-800b-9347e3983730 | note | Standard / Specification - PS 21.7.6
a7a88b91-5951-56fe-950e-4a564ada05d3 | note | Verifying Document - Check Sheet
59d095d5-2a76-58e1-862f-b96dbc923f35 | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
e46f6082-5b25-5281-aa3c-4b7798fc5f3f | note | Verification Activity: Activity - I
c9cef1eb-dbb6-52c4-8bf7-10608beb25c4 | note | Verification Activity: By - SE
36a35987-56f2-51a2-91ba-2c48bca739e3 | checkpoint | 6.2.1 - Compaction - Clegg Hammer
2da0abb8-7532-5883-8118-c393b6210192 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
f9c39ecb-88f6-5212-80c8-d7e740978c92 | note | Acceptance / Conformance Criteria - Min 25 CIV
6a9ce316-74c2-53b2-8ab9-7f765fa20e5a | note | Verifying Document - Clegg Hammer Report
df84fd3c-b7b7-5cfa-8d83-2f99a08c0767 | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
e9f96654-48b4-5451-8db0-3f0bc5ed9838 | note | Verification Activity: Activity - I
d387a782-cdb6-5763-bcce-033e6da78dc6 | note | Verification Activity: By - SE
36d029d6-34c9-5e91-93ce-791ffd26d7f9 | section | SECTION 7 – AS-BUILTS / REDPEN MARKUPS
baf9c479-b65c-5f5e-8f66-06d9120fccaa | checkpoint | 7.1 - As-Builts/ Red pen markup
aa35aae9-176d-573f-b665-da8ffde9a384 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
5eebddc1-bf5c-5f87-86af-aef3f1c4277b | note | Standard / Specification - PS 16.7.6
2be5ae1b-3798-55e6-968d-a05a7b72df3c | note | Verifying Document - Red pen markups
9eb681da-1c5a-530c-9e7c-d2d2f2b0f1e4 | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
4cde1caf-95ab-56e6-99dc-e56d010d1a4c | note | Verification Activity: Activity - D
c9f0b89c-0c96-5411-b2c7-e49674f8054a | note | Verification Activity: By - SV
48312c0b-12e8-475f-baaf-3e3a6966058e | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
de6a491f-cde9-5c0a-bbb5-ddc66b5c7d95 | textbox | Contractor's Rep Name:
3e19eb86-f2c5-5e8e-8950-02c84fbe801d | textbox | Engineer's Rep. Name:
4342eb16-d77a-5109-a6c5-cd6f688b255a | date | Date:
a78d5e74-8a28-4923-9a07-3a7b3e770186 | signoff | Add Signature
7e3ede23-cd72-5fbc-a371-d16341a3fc56 | checklist | DN1210-007 ITP Stormwater Rev 0 | itp | DN1210-007 ITP Stormwater Rev 0
9dbf9507-d5c1-5f76-b0e9-632a875b7d7c | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
61faafb8-e067-5299-84f0-3fd60960e68e | checkpoint | 1.1.1 - Extent of Line Setout
8c6ec2f9-39bd-56e6-af44-d2517ac396f2 | note | Detail - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Stormwater drawings. Identify any clashes before construction.
7d6a7e91-0e37-5917-8fba-1a8a1eefae57 | note | Acceptance / Conformance Criteria - Engineers Approval
e5fee9e3-7922-574d-92a5-7ffc18141aab | note | Standard / Specification - Design Drawings
44187e60-7257-5c43-8598-469a199c8f58 | note | Verifying Document - ITP Sign Off
1f14d97f-faf6-5369-b434-80379019109a | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
8b6e67aa-6aa6-5b21-9bfd-9a3eb29a45ee | note | Verification Activity: Activity - M
a97d5839-1e49-59fa-b864-a3a67cc79564 | note | Verification Activity: By - PE
58d8e667-bb88-509f-83a3-6a1f01d0e239 | checkpoint | 1.1.2 - Existing Stormwater system
49e460ff-036a-53b2-b79f-9c99f6652733 | note | Detail - Confirmation of existing stormwater network.
42c9dd57-cc47-5267-b8e0-a6a8918f72a0 | note | Acceptance / Conformance Criteria - Survey Informations
7a99dc1c-fb5a-5edd-876e-c469c1399ebf | note | Standard / Specification - Appendix V
741ac5b0-1750-5d08-89d8-999292956bf0 | note | Verifying Document - Survey data
39a0f032-457e-5f57-abda-8c2115ba5d0c | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
3651724b-6601-57d2-9532-88e9342cce24 | note | Verification Activity: Activity - HP
1684a043-6be9-57cd-a4e1-b987c3933cc0 | note | Verification Activity: By - ENG
439eb8b4-e232-503c-ae3b-29d0c5635540 | signoff | AUTHORITY HOLDPOINT
b2505ca3-943c-534d-afb7-23e310ef1e65 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
7b779b30-3202-5976-a674-5a18e46af7e0 | checkpoint | 2.1.1 - Material grading: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
1f334567-e26c-5615-a6c5-437f663ff8bd | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
24d05b84-18e6-5631-89c4-8498e20aed26 | note | Acceptance / Conformance Criteria - Stockpile size 1500 to 4000m3. PS- Table 21.2 for GAP/AP20 PS- Table 20.3 for Overlay and Embedment Zone Material NZTA F/6 for Drainage Aggregate- Grading section 2.2
5c9ddec3-cfba-5a3a-924a-5cd74196e283 | note | Standard / Specification - PS-21.7.2
a3371f70-425c-5a18-9783-f9204e2236fa | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
0cbe2752-5826-50eb-837c-fe29a51d166f | note | Testing Quantity Required (based from schedule qtys) - 4 Test 1 Test for each additional 1000m3
f33c1220-9cf8-5e0f-b2f5-9a13930a12cb | note | Verification Activity: Activity - HP
daa93a5e-c9ac-5db2-a1d1-769932c9e987 | note | Verification Activity: By - ENG
d9a47fe7-92b9-5d7e-ba3b-89916ba64f50 | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
4aeddbe8-5560-52d8-adc7-e338b59829ce | signoff | AUTHORITY HOLDPOINT
8d324d50-cc82-585e-af30-1900442f0418 | checkpoint | 2.1.2 - Weathering index: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
3e9433c2-8416-541a-9b8e-f94896d44afd | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
02556238-6038-5fd8-b6ca-daae3b6dab89 | note | Acceptance / Conformance Criteria - Engineers Approval AA to CA
aaddeb8c-95ff-56d6-9a6f-3409bffb689d | note | Standard / Specification - PS-21.7.2
189140fd-eb19-5a38-9198-6caffd786c65 | note | Verifying Document - Lab Test Report NZS 4407.3.11
da98e593-24a7-5f5a-8ce9-7c74c81324f7 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
792e2727-8b39-5b9a-b169-fd5e24df259b | note | Verification Activity: Activity - HP
cd225301-feb2-5a18-90ba-b565d40136e9 | note | Verification Activity: By - ENG
b934f0f0-a41c-5df1-9909-a98c6e8a0321 | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
a2fc101a-90b9-54e1-89a9-1383075ee775 | signoff | AUTHORITY HOLDPOINT
5c6967dd-7748-5877-a08e-26c0fca616fa | checkpoint | 2.1.3 - Crushing Resistance: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
42790e68-27b0-5257-b87e-1982f42796e2 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
984bb7bc-4f10-5043-80f2-d40e640bf675 | note | Acceptance / Conformance Criteria - Engineers Approval >100kN
e3bb4083-971b-55a2-9772-0a0a21cf7749 | note | Standard / Specification - PS-21.7.2
0a7679d5-39c2-5de1-b95d-39ec647eab43 | note | Verifying Document - Lab Test Report NZS 4407.3.10
7b856239-6bd6-5372-9166-20d22ad5dee5 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
8585d6ff-4e91-5a30-8302-655099e0e606 | note | Verification Activity: Activity - HP
2648d9d0-a0ed-5b83-8385-c18a55813457 | note | Verification Activity: By - ENG
65121ca3-b1e1-5e4a-a887-0a084d4ac8bf | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
cbd04506-6cf4-5b18-9ff7-c44dfcd7f02d | signoff | AUTHORITY HOLDPOINT
7191560b-5e9b-500b-8294-b06ed11c768b | checkpoint | 2.1.4 - Geotextile/Geogrid
6edffe58-5601-5dee-9731-a95829301d91 | note | Detail - Minimum Strength Class C & Filter Class 1 or TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
3a4e22eb-c194-507d-ad79-45831776f912 | note | Acceptance / Conformance Criteria - Engineers Site Representative to inspect trench.
ea038197-1b00-5782-8df6-03b39f7859d3 | note | Standard / Specification - PS-16.5.7
45a7f083-9498-53f2-b122-3e13010cc7d0 | note | Verifying Document - Certification
0f9de01c-864c-5a5d-9a87-6273d2f836c7 | note | Testing Quantity Required (based from schedule qtys) - 1 time
7bd65c91-8676-53ea-80aa-104dd809277c | note | Verification Activity: Activity - HP
70bcf854-abb5-5221-9218-490224e68a4a | note | Verification Activity: By - ENG
b25b3fba-56ef-5a01-97a4-28b869a99641 | signoff | AUTHORITY HOLDPOINT
d353cea1-760b-54fc-ba9d-3f6628ef5bc6 | checkpoint | 2.2.1 - Riprap test Criteria
d286ec9a-b058-5a28-8a8f-00cf21213193 | note | Detail - Weathering Index of Coarse Aggregate.
b4077272-8d75-5913-bca2-1bfc527d262e | note | Acceptance / Conformance Criteria - Engineers Approval AA to CA
4831fecc-6eb9-5f1b-81f3-d46c6f6c69d7 | note | Standard / Specification - PS-21.7.4
68a6c4d8-cf61-50c7-9b19-fe178bdd7042 | note | Verifying Document - Lab Test Report NZS4407.3.11
a816cfe2-2037-516c-975a-ca474f1f903b | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
8657b15f-6259-5bf9-ae34-67f8613f7f29 | note | Verification Activity: Activity - HP
ad7dd6dd-66e5-55cd-bffa-63ca75e31be6 | note | Verification Activity: By - ENG
c2623d1f-bd3a-5637-bac9-0bae411ac607 | signoff | AUTHORITY HOLDPOINT
37c23bd2-a3fb-5b1c-be0c-98555e939a1c | checkpoint | 2.2.2 - Riprap test Criteria
1f2b2ecb-2e9e-536c-b013-fa147e18aea2 | note | Detail - Crushing Resistance of Course Aggregate.
9f617669-633c-5613-b494-287a0eaa94a0 | note | Acceptance / Conformance Criteria - Engineers Approval > 150kN
9238c7ab-8930-54a1-9a16-5efa91586e06 | note | Standard / Specification - PS-21.7.4
c6746b54-5e95-5509-bcff-cf78f24161d7 | note | Verifying Document - Lab Test Report NZS4407.3.10
8b24e29e-64a0-5fbb-a080-7de232bfbf75 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
fc644247-06a4-507e-a5ac-029409aa04df | note | Verification Activity: Activity - HP
498ea4f1-b4e1-51d9-a137-bfa5469497d6 | note | Verification Activity: By - ENG
1ac63ecd-b84e-5578-bb6f-a120cffbdda3 | signoff | AUTHORITY HOLDPOINT
b0917513-6283-539a-acb3-a2b3aa920522 | checkpoint | 2.2.3 - Riprap test Criteria
d628b4fa-a5af-504b-a446-56451c012aa7 | note | Detail - Solid Density of Aggregate.
dfdbff3b-306e-5700-8fe9-fd39b874d80c | note | Acceptance / Conformance Criteria - Engineers Approval ≥ 2.65 tonnes per m3
a4334eca-ba29-5bde-8260-79e987fe1d3b | note | Standard / Specification - PS-21.7.4
25932fa2-7703-56ba-83e1-059a9132add0 | note | Verifying Document - Lab Test Report NZS4407.3.7.1
2187692d-ece8-5d53-8ef4-159ba70b2333 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
7bfc33aa-87c5-5816-965d-d04b52316581 | note | Verification Activity: Activity - HP
df1af21a-0031-5b1e-bf94-ec72f87e1906 | note | Verification Activity: By - ENG
a590b01d-a0ea-50ef-b3d0-57465bb74403 | signoff | AUTHORITY HOLDPOINT
5317a3a0-6700-5834-a89f-bd6ef24b9bf5 | checkpoint | 2.2.4 - Riprap test Criteria
12f0ae57-b248-5298-9aef-21cb5140cd53 | note | Detail - Grading of the material.
73ec9ed6-31a3-5759-9d8e-af6d74715b93 | note | Acceptance / Conformance Criteria - D=50 150mm Riprap Grading Aperture Size- 230mm Aperture Size- 150mm Aperture Size- 95mm
002fa807-2c30-50a7-8e68-c20a54016e80 | note | Standard / Specification - PS-21.7.4 PS-21.5.14 Table 21.3
09758b78-075b-5f15-baa0-097393ff974e | note | Verifying Document - Lab Test Report NZS4407.3.8.2
11292c02-362a-584d-a56b-3f927be37292 | note | Testing Quantity Required (based from schedule qtys) - Percentage passing- 85 Percentage passing- 50 Percentage passing- 15
d31ca261-8d16-5930-bafd-7c13e256dbb1 | note | Verification Activity: Activity - HP
588d5b23-fad5-5711-97aa-fb690e88338a | note | Verification Activity: By - ENG
947ebb05-cb3d-5cbb-9402-8ca942d558c0 | signoff | AUTHORITY HOLDPOINT
98285b74-1d71-57f6-9977-ee088beb181f | checkpoint | 2.2.5 - Riprap test Criteria
255e8990-7914-5fa5-b163-eeb7f68c9963 | note | Detail - Point Load Strength.
2d7082ac-318b-59a1-8cce-77a95e658c7d | note | Acceptance / Conformance Criteria - Engineers Approval >1.5 Mpa
15ba3521-b680-5a07-b9aa-b31840006f30 | note | Standard / Specification - PS-21.7.4
f033c320-d8d9-55fe-821c-b40d10e4aa59 | note | Verifying Document - Lab Test Report ASTM D5731
619db733-dd8a-59a0-a845-0888aa125eba | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
3d026438-f16a-5d68-af72-5e85aeb86337 | note | Verification Activity: Activity - HP
87a4d598-27dc-5715-b148-458db0082944 | note | Verification Activity: By - ENG
0063bf6f-94a0-5293-8cea-55db2d898e31 | signoff | AUTHORITY HOLDPOINT
c58e1f7b-cdec-556d-b433-f2dbfce36ed4 | checkpoint | 2.2.6 - Riprap test Criteria
e4203914-0330-590b-a5e6-017784aba336 | note | Detail - UCS Rock
bde3dda1-6f3b-5ec4-a027-5d616f175f23 | note | Acceptance / Conformance Criteria - Engineers Approval >30 Mpa
2f9f77e7-86b8-5c19-b6fd-8c5a2a960825 | note | Standard / Specification - PS-21.7.4
8ef95ebd-fef6-5403-acc8-27880f47e268 | note | Verifying Document - Lab Test Report AS4133.4.2.1
ea339cdb-416c-5b18-8a8b-d996a77051ce | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
0e0d3efd-5dd0-5a5f-ad8c-7c6c66e92c9b | note | Verification Activity: Activity - HP
351f00b1-ec78-5d7f-add6-76cb4b6e545a | note | Verification Activity: By - ENG
ebf02735-8f7e-512d-8e6c-9d466034bd52 | signoff | AUTHORITY HOLDPOINT
7685f2ef-c62e-5fb7-a70f-d353bd416788 | checkpoint | 2.3.1 - Pipe and fittings. (uPVC SN16, PVC, PP, PE and Concrete pipe).
b01a1fdd-980f-57b1-be0a-974d4f3bb258 | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
4c191b62-9e9e-5c94-be52-070246d48b7a | note | Acceptance / Conformance Criteria - Site Engineer Approval
8d5cf5a8-4e17-5231-a5b6-ca8dd8ec696a | note | Standard / Specification - PS- 21.5.1 PS- 21.5.2 PS- 21.5.3
75775828-4804-5f60-a3df-9a82d162ad6b | note | Verifying Document - Delivery Dockets
751b8bc4-6897-5063-a6d7-87d47ec7c076 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
7e8d13c8-1979-5990-aacf-08b73505fda9 | note | Verification Activity: Activity - H
4006c96a-bc64-5e43-9917-9020fd14008d | note | Verification Activity: By - SE
a5d92bcd-6b64-564d-acc9-23954f1e76ee | checkpoint | 2.3.2 - Stormwater- Structure (SWMH, SDMH, GMH, CP, DCP, CPMH, MP, HW)
950e6069-be5d-58e8-906f-75c387756cac | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the Structure are correct and in good condition.
7249efd0-13a8-5579-bfe8-c850866e2857 | note | Acceptance / Conformance Criteria - Site Engineer Approval
b50f929a-38af-527f-a81a-e53528cbf432 | note | Standard / Specification - PS- 21.5.4 NZS 3109:1997
e6a2b17a-e105-5c3c-9310-968bf24eddd4 | note | Verifying Document - Delivery Dockets
63930cae-a21d-5047-ac1e-9857f8ff5e7b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d41b08a3-eeac-54e7-8f15-e394c8e93b03 | note | Verification Activity: Activity - H
e9e75178-846a-5eef-b1b1-8521d4d46882 | note | Verification Activity: By - SE
cbed7aea-7be8-51e8-bfaa-a2df8eb77a1f | checkpoint | 2.3.3 - Granular Material (GAP20/AP20, GAP65/AP65/LRAP65/Riprap and Drainage aggregate)
407ef78e-50cd-57c8-8824-f9d8e8852c18 | note | Detail - Confirm Specification and material in good condition.
1136a1e3-699e-58c3-9d0c-aa15898cd5f4 | note | Acceptance / Conformance Criteria - Site Engineer Approval
b8087df2-d012-5974-9df1-eba90d28bbbf | note | Standard / Specification - PS-21.7.2
cdc5971a-6269-5354-b5c8-8f9475803eae | note | Verifying Document - Delivery Dockets
9d088f1f-9f2a-5ca3-bb59-e6e1b2142f5a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5a3f4e82-12f6-5d82-8f50-0afdd218756f | note | Verification Activity: Activity - H
077a5639-66fb-5771-88cc-8c3b6cf276b6 | note | Verification Activity: By - SE
c71f9062-d24e-5bf6-a7c7-105d5eef56fd | checkpoint | 2.3.4 - Geotextile/Geogrid
7bcf08b7-ff3d-545e-84c3-04e1e82f1589 | note | Detail - Minimum Strength Class C, Filtration Class 1.
e1ab34a5-a3f2-5e9c-927f-ff3d58e9cc8b | note | Acceptance / Conformance Criteria - Site Engineer Approval
ae9fbf32-cb1a-5c09-97d0-ef9c77c01924 | note | Standard / Specification - PS-21.7.3
3c978ce7-deea-5c28-a3fb-87c317f1a200 | note | Verifying Document - Delivery Dockets
2666c2e2-715b-5082-910b-8fbf5a733244 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
95b961d6-569a-5cba-9d93-b4a540fa1ba6 | note | Verification Activity: Activity - H
e11c4279-6af9-5f37-8469-0635e4d97c4f | note | Verification Activity: By - SE
9cc06a11-17ee-5f49-ac50-31c36fc22fcb | section | SECTION 3 – CONSTRUCTION ACTIVITY
6060b861-66f7-50a6-931b-1a3e09522cab | checkpoint | 3.1.1 - Foundation Compliance
7536601b-5795-54c4-9390-a7bed0019a30 | note | Detail - On Granular or Cohesive Material
724edf15-3e3a-5915-9121-84578bd157f8 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
f830645a-2aab-58bb-906c-27c71c18a48c | note | Standard / Specification - PS- 21.7.2 Appendix V
8c31040c-a189-533b-825a-9de443fb9ff9 | note | Verifying Document - Scala test result
8740789d-55d4-5feb-971a-45877bdd7d1a | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
c84c9e22-44a5-5f1d-affd-04e3960ef8b3 | note | Verification Activity: Activity - W
6ecf1e8f-3477-5567-837f-fa8625d3e6b8 | note | Verification Activity: By - SE
c1c96344-d442-58de-82ed-d9085e766b87 | checkpoint | 3.1.2 - Undercut approval
00595da2-b0ec-5ba3-b6df-33932dcee49a | note | Detail - On Subgrade
7af00c8c-0774-501e-ba30-da67c0745a5c | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
25a1d52f-7fda-5426-b137-dd447b2e82ad | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
baaf7fca-54a1-5394-b84d-d1811e3fb804 | note | Verifying Document - Lab Test Report
8ea61e8d-88b8-50d8-acc4-310275e23e59 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
1d831097-2f81-5314-aeb1-6393177b78c0 | note | Verification Activity: Activity - H
92fe9a12-d005-54bf-bb3d-bfeeeb2adab5 | note | Verification Activity: By - SE
1a41ffdc-e630-5238-b3c6-b7ddb238f1d2 | checkpoint | 3.1.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
6479ab9c-b45b-5e98-ace7-2a2eb58883e8 | note | Detail - On Granular Material
6aa210aa-94f1-5f44-9779-2cb46f254d92 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
1da33ee3-ae6d-5b44-beeb-d48a29e36b20 | note | Standard / Specification - PS- 16.5.12
55ff37d4-947c-5ac3-a0dc-9a1ac4e5af92 | note | Verifying Document - Lab Test Report
b9c7f2b9-a88f-5b50-9010-a5d3751a4a1a | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
3195e80f-8f03-5d16-af20-4cc0d10e4085 | note | Verification Activity: Activity - H
bea0a486-f7a1-590a-9672-73554f189ccd | note | Verification Activity: By - SE
122c791d-c0bb-5292-b890-be01180cb1f8 | checkpoint | 3.1.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
eb402eea-cbce-5dd1-a273-ee269f7ccd3d | note | Detail - On Granular Material
83dc2d43-8184-51d7-94cd-24ed704f194a | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
d64474e8-d06b-51eb-b3e4-359d201a1552 | note | Standard / Specification - PS- 16.5.12
830684fd-21d1-565f-bd8f-b354a2dfb8f4 | note | Verifying Document - Lab Test Report
5ef9c053-d06b-5ce9-ac02-98995c5ebb54 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
1bc17671-cf1c-5423-ba88-09bfa3f56f0b | note | Verification Activity: Activity - H
454bf4fe-bd23-55ed-b3e8-9e1c8817b574 | note | Verification Activity: By - SE
6f02a627-0efa-5c52-bfc6-1db0fde3e838 | checkpoint | 3.1.5 - Pre-Backfill Inspection
e77f1704-9e25-5c33-82d2-09c9dbcbaf60 | note | Detail - Inspection of Structure
f951ec8b-dc9a-5405-91b7-0b06259a0bc3 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
f66efe11-8c35-5953-92b4-943ab3b55648 | note | Standard / Specification - PS- 21.6.11
64af34f4-5cfc-5680-ac8c-58a6c7f63728 | note | Verifying Document - Manhole/Catchpit Record
b27ddea0-6078-5c28-9201-42a353cbad85 | note | Testing Quantity Required (based from schedule qtys) - Continuous
bb2164bf-e8e5-5586-aea5-061af184642d | note | Verification Activity: Activity - I
e5f99403-c158-536d-bfe9-6880cebf1bf7 | note | Verification Activity: By - SE
c35a65d5-6eb2-5191-8c79-ec76f3f7c3b4 | checkpoint | 3.1.6 - Survey
1bf06fba-025e-505c-a887-754d08cdaa1d | note | Detail - Inspection of Structure
eef5d195-346e-560a-9c18-f7ae502040d2 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
3d297368-0aa2-5564-8d83-e1bfe2975029 | note | Standard / Specification - PS- 21.7.6
585535f5-494f-5bcf-901d-dbd9dc20572d | note | Verifying Document - Survey Data
ac82bd90-691d-5db6-a45e-46fcee96c120 | note | Testing Quantity Required (based from schedule qtys) - Continuous
623c6f9c-4701-599d-8589-c1f0211284ec | note | Verification Activity: Activity - H
57afac1e-90f7-56b1-bd39-70911dccf45b | note | Verification Activity: By - SV
e681d924-eb9d-5908-874f-e2a9cfead256 | checkpoint | 3.1.7 - Backfill Compaction Testing
2e8ec344-8cd3-50fa-ab02-e7785f1be849 | note | Detail - On Granular or Cohesive Material
c5251a47-746a-55b5-8328-90325b509eff | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
84724f52-fc63-5dd7-94a8-ed5a9141e72c | note | Standard / Specification - PS- 21.6.12 Appendix V
f06b0520-7e15-5235-8046-70af6152b0c3 | note | Verifying Document - Lab Test Report
001d7a06-1d2a-51f9-a625-fecf948e3e76 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
09b3371e-2d21-5aeb-8089-bc2b2d8f5770 | note | Verification Activity: Activity - H
00e72377-0f35-5af7-9afa-474c27318faf | note | Verification Activity: By - SE
8a67bad2-49a0-5b3e-9e07-3e95e06d76d3 | checkpoint | 3.2.1 - Foundation Compliance
6693aa39-d64e-5264-bf3b-3d30c6fa7822 | note | Detail - On Granular or Cohesive Material
e31f585c-fea8-5cfb-b089-a19c2db76d02 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
b276eb1f-1549-534b-a017-94d90077d154 | note | Standard / Specification - PS- 21.7.2 Appendix V
13cd0b61-a024-5d4e-98e4-6077201c68d9 | note | Verifying Document - Scala test result
ceef2f8c-5d86-5446-963d-a823469e910f | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
433d211f-33cc-5b63-8ae2-b545b77c9e46 | note | Verification Activity: Activity - W
81d04145-5426-5dea-860a-998a8a1ec3b7 | note | Verification Activity: By - SE
5c32e1a0-52b7-5c2e-8003-fdd7656ac09f | checkpoint | 3.2.2 - Undercut approval
ea278464-af9f-5fde-bd25-54d1ce0d139a | note | Detail - On Subgrade
80be3fd5-ac77-51c8-8656-679b043104cb | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
d035fdd2-0e37-5bf8-a24e-00f64ab6f4bd | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
b9dfc0b1-f7d0-5327-9c11-2df9f61ecda5 | note | Verifying Document - Lab Test Report
35c74bc4-0996-5b4f-b771-e9bfaeb3cf92 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
1c526564-e335-52bc-8daa-cd0f240e6fa8 | note | Verification Activity: Activity - H
4bd8b7ba-ea6f-5198-bb35-0097bea43aa0 | note | Verification Activity: By - SE
811e271f-f2a2-52ee-9167-0e158033e720 | checkpoint | 3.2.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
dcadc4d9-96fd-55ca-b0bd-89a8fff7a309 | note | Detail - On Granular Material
175eb5c8-e07a-5b6d-a58f-6695e40e86a8 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
def5d9ef-5cce-5477-9b47-c8546a5d1cb4 | note | Standard / Specification - PS- 16.5.12
7b3b0c16-3de9-53d5-8208-072297668bb8 | note | Verifying Document - Lab Test Report
10fb19b6-58bb-5b0c-ae29-e85d8d061777 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
30199c4e-14ec-592f-8548-0c6d5aded7b3 | note | Verification Activity: Activity - H
e9693bdf-97b2-570b-876d-3ccaed5e26a4 | note | Verification Activity: By - SE
77568fee-af21-5f9b-9f96-160b1a618b0b | checkpoint | 3.2.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
d3385acd-9e7e-55ff-ac08-aa28120b1ea3 | note | Detail - On Granular Material
6d9d584d-97c3-55a6-8e69-b1b64b687153 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
0adbe8b4-10a5-50d1-8637-12fd7870f94b | note | Standard / Specification - PS- 16.5.12
3d74ac21-d6ba-5b18-b993-94bb528d9d7c | note | Verifying Document - Lab Test Report
b1bb2dab-d898-5cd2-aad6-1e93c56ee60d | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
13a9894c-3b43-555f-8001-726e44a83bec | note | Verification Activity: Activity - H
54b0181f-8c7e-5a98-9b96-e51954539c7c | note | Verification Activity: By - SE
ff95eca0-5856-535c-b653-c34444e1d4db | checkpoint | 3.2.5 - Pre-Backfill Inspection
d610233e-42ab-5f87-a8d7-fca5762d01e1 | note | Detail - Inspection of Structure
4f3c5e54-c54a-5214-ac39-374f38f41675 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
02c38837-cfa7-5130-8f2c-4bfe01c5e835 | note | Standard / Specification - PS- 21.6.11
7ce2509c-5fbe-54f8-88f6-a2b46450e743 | note | Verifying Document - Manhole/Catchpit Record
cd972a7b-69e6-5e5f-8399-85ca4a4f4fd5 | note | Testing Quantity Required (based from schedule qtys) - Continuous
fced3349-4f6d-5430-82c9-db793cb555bd | note | Verification Activity: Activity - I
d4e5c9b9-6be9-5d50-8c4f-59798657d98c | note | Verification Activity: By - SE
8438b253-2cbd-5d5d-b5cf-63795fbb55c6 | checkpoint | 3.2.6 - Survey
7bdafb6a-9389-579e-b973-43343bcdadf2 | note | Detail - Inspection of Structure
e865e0af-739a-5375-b99d-123f9ad5c315 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
0e860317-0ff9-5357-afc2-06540e5ba10a | note | Standard / Specification - PS- 21.7.6
66f21632-48c8-54e7-b7ac-9151bd796787 | note | Verifying Document - Survey Data
a0dbbb05-8b70-547b-ba31-519ac1630378 | note | Testing Quantity Required (based from schedule qtys) - Continuous
8f5ce6b7-123f-53d3-9130-bb110ec1b3a1 | note | Verification Activity: Activity - H
c41e2a53-7736-569c-b991-9bd9148cb4be | note | Verification Activity: By - SV
b695541f-0861-5c72-a422-a5c37de96d6a | checkpoint | 3.2.7 - Backfill Compaction Testing
06f3bd12-4223-53d9-b29e-7d06a8343e5e | note | Detail - On Granular or Cohesive Material
8ef45800-36a7-57f2-91cf-a08f6e68c701 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
c253d9db-85d6-5395-99e5-ea5597604fdd | note | Standard / Specification - PS- 21.6.12 Appendix V
d72d5baa-fcce-5be2-833e-294e3bb480d5 | note | Verifying Document - Lab Test Report
f122f1b7-fa5f-58a5-b9ad-f7ca22b1bbea | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
46ee0a82-6c95-556e-8e14-55b3fe15e3f6 | note | Verification Activity: Activity - H
b4c34036-c8c4-53ac-99aa-ab67401f7bc3 | note | Verification Activity: By - SE
300b8fa1-28bb-53b2-8f55-761644c8d091 | checkpoint | 3.3.1 - Foundation Compliance
72b25472-d766-501a-831b-55c9f74ccb4f | note | Detail - On Granular or Cohesive Material
930b3a55-fefd-5113-b05d-16fd1c509667 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
d0feac88-eb37-517f-a9b7-520293a67e61 | note | Standard / Specification - PS- 21.7.2 Appendix V
a2b06bbd-6854-5815-880c-d7cf839fef59 | note | Verifying Document - Scala test result
6e33f9c1-30e4-5561-b3cf-a235a3921534 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
f1767cdd-3d25-53fc-a759-9694a9376d59 | note | Verification Activity: Activity - W
eb8d5159-f0aa-5677-8701-777298379968 | note | Verification Activity: By - SE
dff5ee8a-9019-5036-bebf-6f91dc5f062c | checkpoint | 3.3.2 - Undercut approval
62f7f656-3915-5fe1-999b-b1c784c58bb2 | note | Detail - On Subgrade
18aad1f8-a05d-569e-bd6f-f312c8237b7a | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
94915bbc-9276-53e4-ae92-1debd9c4e928 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
835a9559-1b67-550a-b55f-8e55eb2dfd68 | note | Verifying Document - Lab Test Report
79397d05-e464-55ed-adaa-ed48e7df704b | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
a845de8f-a05a-5d34-b04f-b007ea7876b8 | note | Verification Activity: Activity - H
b437dfd3-46d2-5a26-9ad5-98ccea8c7a11 | note | Verification Activity: By - SE
19146973-bab4-5555-ab24-77b09a0bbffe | checkpoint | 3.3.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
bf7449a2-e26c-52e5-a4e1-4804e01160c8 | note | Detail - On Granular Material
422260c0-3c73-5bec-9a50-24b474648e95 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
c4f86e78-aa99-59f3-96c8-0b5c9589c87b | note | Standard / Specification - PS- 16.5.12
0933885b-432e-5287-869b-39cee23cc6ce | note | Verifying Document - Lab Test Report
e9a47674-39d2-583b-8646-550672af1e8a | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
7f9eb0b6-750c-5889-a74a-664d89746c81 | note | Verification Activity: Activity - H
78779cd2-0f31-5357-b747-116add696165 | note | Verification Activity: By - SE
94a0623a-421b-55f6-bfcc-21a724ec9dfb | checkpoint | 3.3.4 - Bedding and Embedment Zone Compaction Testing (Polypropylene(civil boss)/Polyethylene Pipe).
5d6416a8-6629-59b5-8972-8054db23e34f | note | Detail - On Granular Material
b56a5fbf-25c2-5138-ae4c-a3a9acc94f41 | note | Acceptance / Conformance Criteria - Bedding Zone: 100mm(for DN300 & DN375) 150mm (for pipes greater than DN375) Embedment Zone: Pipe Dia ≤450 - 150mm GAP20/AP20 - Overlay Pipe Dia 450< D ≤900 - 150mm GAP20/AP20 - Overlay Pipe Dia 900< D ≤4000 - 150mm GAP20/AP20 - Overlay Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
b6dc7386-bcd0-5a96-b0db-e9b815586e18 | note | Standard / Specification - PS- Table 21.7 PS- Table 21.12 AS/NZS 2566.2/2002
98cbd37d-a6ae-5726-b7a6-b8c811e85d8e | note | Verifying Document - Lab Test Report
c9022001-0066-5752-9f30-29dec6664249 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
eb703980-b343-5b35-b4e9-ae266e81c5a2 | note | Verification Activity: Activity - H
08b1c655-664d-5fad-ba55-b191d3419185 | note | Verification Activity: By - SE
d2e13628-b927-50fd-ad8e-db3f761f1f7d | checkpoint | 3.3.5 - Survey
4f14edc7-e9a4-52f1-86c5-798205a9be33 | note | Detail - Surveyor to Setout
9aaf4ffb-8a34-55c0-9b8f-534553d3a398 | note | Acceptance / Conformance Criteria - Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance
5f46781b-fac3-5535-b0f7-4236485214f6 | note | Standard / Specification - PS- 21.7.6 Table 21.15
29691daf-2cec-5dbc-9554-fd4dd5340e7a | note | Verifying Document - Survey Data
aa9af37a-13a7-5b98-8ca2-93763c070541 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
7ca755d6-9e4e-5c08-b7bf-60dfcec72b9b | note | Verification Activity: Activity - H
bb14b4d7-ca9b-55e5-93d4-c48df3421efe | note | Verification Activity: By - SV
652c96e1-768e-5161-abb8-33857043d37c | checkpoint | 3.3.6 - Backfill Compaction Testing
47ca7528-0d20-5fce-992c-8c0031ca4e99 | note | Detail - On Granular or Cohesive Material
32176970-0811-5c42-91cb-991b95a0281d | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
9842a3cd-5db2-54d5-865d-b6f862a0a05c | note | Standard / Specification - PS- 21.6.12 Appendix V
a5d78d5b-202b-5f3c-a550-fd62b25bd144 | note | Verifying Document - Lab Test Report
e7439544-899e-5b79-8ee2-d2bb641a8f06 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
1aae88bf-61ef-5403-97bf-80a113807d94 | note | Verification Activity: Activity - H
43b502f6-f5ba-5206-a0fc-688b56775d8c | note | Verification Activity: By - SE
276798c2-34e6-5e87-bb66-a7f7df9fa38c | checkpoint | 3.3.7 - Pipe Inspection
a06df628-6013-57d7-a7ac-1babe6b7f651 | note | Detail - Inspection of Drainage line
ec6eb0af-4baf-5fab-9b74-5626aa4d40db | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
19d27f5f-351b-5aeb-9ea9-d95200a9b1fc | note | Standard / Specification - PS- 21.7.6
e1c1c3c9-58ca-56b4-85d0-e418d334d0b5 | note | Verifying Document - Drainage line record
5aa69d23-1991-58b1-9a59-332e16116508 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
c091935b-68ff-51ce-98cb-936e9c5d13fa | note | Verification Activity: Activity - I
73b2bb90-7fd3-5df0-b0d5-4a0cbfb04bb8 | note | Verification Activity: By - SE
23e48d28-c984-5a1a-adf0-687888856fce | checkpoint | 3.4.1 - Foundation Compliance
b1f82680-2f23-507d-87ef-07e955ead30f | note | Detail - On Granular or Cohesive Material
1b93c683-9a16-58d4-ac1b-397eeb6713a0 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
294224ec-429c-56f6-b1f4-926c48f6aedf | note | Standard / Specification - PS- 21.7.2 Appendix V
d9e02b9a-d672-52e5-a7bf-b568f7a18e0a | note | Verifying Document - Scala test result
5e9520af-5a32-5a5c-9585-f45b773a33cd | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
2499b3ea-793c-5c4b-8fa9-3064a06065b4 | note | Verification Activity: Activity - W
2a5383b3-1ae7-58cb-9ef3-97ba0f35a866 | note | Verification Activity: By - SE
2e297fed-b0b9-5c9a-82c6-da43f519fdc6 | checkpoint | 3.4.2 - Undercut approval
545f6878-eea1-53de-b124-115e4bea2d50 | note | Detail - On Subgrade
10340e4e-6257-5290-b88f-6e40d6a7a12f | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
edb7d806-2d41-5542-98c4-eb52582f365d | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
093f5f9a-3816-5de1-ac1c-6e9fcd02705d | note | Verifying Document - Lab Test Report
80a49d8c-ebb7-5b16-9ca8-d1dcf9e87a49 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
bd67af40-cd47-5271-84e1-b2da193705be | note | Verification Activity: Activity - H
f625d731-0e13-5d69-948e-c653bdc205df | note | Verification Activity: By - SE
34f0d9ca-7f76-56e1-a2e3-84ec7ac51186 | checkpoint | 3.4.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
1cde9d5b-6e5b-51b0-96b1-89b50215cdf0 | note | Detail - On Granular Material
ecfefb9b-e1e0-5eab-90d9-373d1bcda7be | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
53de2b2f-1021-5d68-a804-5faae55e6841 | note | Standard / Specification - PS- 16.5.12
7e978c77-060f-54fb-ae26-91a16b8ef59b | note | Verifying Document - Lab Test Report
2cdd3332-b236-51b5-8327-796aa39199f1 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
6162c2a1-63a8-57fb-bb0b-7622e1405e38 | note | Verification Activity: Activity - H
173f5d3c-1b2b-5dcc-a2ac-58c7bfbe497c | note | Verification Activity: By - SE
5d768dd2-9cd0-5756-bb3c-505106479de8 | checkpoint | 3.4.4 - Bedding Compaction Testing
e0d9eb16-66df-5645-8e1f-d4e3c38dda8b | note | Detail - On Granular Material
99b11551-54e4-54cd-a53d-cad405368fc6 | note | Acceptance / Conformance Criteria - HS2- 0.3xD (outer dia of the pipe) Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
b2a1e921-a6a9-5310-bcf0-49ace4543ca2 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
98f34698-29eb-5684-b946-231b0b1fdad6 | note | Verifying Document - Lab Test Report
1a08ef5d-a3eb-55f8-a583-415abebb5504 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
9aa15384-64ca-56a3-a1a5-704acaf63829 | note | Verification Activity: Activity - H
19ee0ce2-d1ad-586f-81ea-517090fdf8fa | note | Verification Activity: By - SE
4bfe46f7-744f-55e6-8523-2ea18484410b | checkpoint | 3.4.5 - Haunch Zone Compaction Testing
224e6c9d-bdd6-531f-9a04-548031bde3a1 | note | Detail - On Granular Material
75f3cb6e-0698-5a92-8841-e0e9a35055a8 | note | Acceptance / Conformance Criteria - HS2- 100mm if D≤1500 (or) 150mm if D≥1500 Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
ed49a71e-fcd5-53e6-9ca9-d990f1cff0d2 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
cf4d2da9-bd55-5f3f-9c41-662eaa888790 | note | Verifying Document - Lab Test Report
f0be1216-6c9e-51d9-9af2-b2e776e44c86 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
9efd0274-a60a-57ba-b9ef-ccb4abbf1e5c | note | Verification Activity: Activity - H
e36eb1a9-5762-5ddc-ab87-3a11d36356ff | note | Verification Activity: By - SE
4844df56-a700-5e51-ab74-6839a6589fc8 | checkpoint | 3.4.6 - Side Zone Compaction Testing
045cfc2d-e067-5c0d-b7ee-3de5ee0a51c0 | note | Detail - On Granular Material
902bb784-8f80-55d7-a628-ba068f696b5a | note | Acceptance / Conformance Criteria - HS2- 100mm if D≤1500 (or) 150mm if D≥1500 Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
197bfed8-4df7-5d6b-896c-bc9e643a3fe5 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
22a9f67b-954c-5a70-a4be-1ea07b3eec27 | note | Verifying Document - Lab Test Report
bd0aa8a8-2d6a-56f4-9da3-955b0d0bec8e | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
02a51015-539b-5496-a1d6-cca46e19783f | note | Verification Activity: Activity - H
c0f448f2-ef13-57ec-b25e-67d5360e370b | note | Verification Activity: By - SE
43578e81-672f-5d7a-9d20-9ac1e812a489 | checkpoint | 3.4.7 - Survey
f110438e-dbb1-5f27-b476-ad22c584065f | note | Detail - Surveyor to Setout
d13b1de4-0a4a-55fc-ba7f-1bcf383fe023 | note | Acceptance / Conformance Criteria - Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance
a7bf3aa8-13db-5519-a403-e2e43b483e2f | note | Standard / Specification - PS- 21.7.6 Table 21.15
551d7c42-81f9-5cef-aaec-1839171717f6 | note | Verifying Document - Survey Data
6c9ae2f8-ce02-5e92-82d0-2782494c2f06 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
02243be4-0538-547e-8fa3-672b12b7beb2 | note | Verification Activity: Activity - H
3a82526b-f26f-58bf-8e47-1f813a1487b8 | note | Verification Activity: By - SV
b1c5561f-735f-5ab9-80a5-52eccf1118e5 | checkpoint | 3.4.8 - Overlay Zone Compaction Testing
21620ddf-4f86-5dfe-932a-8b6316603fe3 | note | Detail - On Granular Material
dfcd6cd6-66e2-538b-8a8c-67d72e089686 | note | Acceptance / Conformance Criteria - Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
33243dda-43bd-581c-8039-3e52aeb08f27 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
f8e50a62-3f10-5546-a417-21c635152588 | note | Verifying Document - Lab Test Report
431e22ce-c629-529b-b9ad-fb11b917760c | note | Testing Quantity Required (based from schedule qtys) - One test per 30m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 1 Tests 0m-50m: 3 Tests 0m-100m: 5 Test
d6b81813-19b0-5eb9-ab7d-2e630aa5a232 | note | Verification Activity: Activity - H
fa87cd6f-f03c-5fd2-866d-130718e89598 | note | Verification Activity: By - SE
1b1ebc88-e4b8-502f-a958-3dcc4a007de4 | checkpoint | 3.4.9 - Backfill Compaction Testing
6a094b79-1e76-5958-8703-4e9310286b05 | note | Detail - On Granular or Cohesive Material
11097803-d3b1-5322-8840-d9c50d0ca5dc | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
cc1b8541-1fae-502d-a986-042fb92fef01 | note | Standard / Specification - PS- 21.6.12 Appendix V
7398fa83-6c42-5e52-9853-413853c200c4 | note | Verifying Document - Lab Test Report
8e68f238-4b88-503f-a35e-a4968b197090 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
1fe264f1-fced-5c9e-92b3-e784ab8ea9c3 | note | Verification Activity: Activity - H
4616e0ce-8c25-596f-a21b-a6bea2533fe2 | note | Verification Activity: By - SE
b758dbb4-248e-55bb-94cc-12a4cac84109 | checkpoint | 3.4.10 - Pipe Inspection
8d62a9ca-2cb4-51ee-8612-9cfdecb7cd6d | note | Detail - Inspection of Drainage line
7390c541-2715-5937-a0fc-79281c4f4290 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
c70214f0-30f1-5268-ad19-c6148d2aae66 | note | Standard / Specification - PS- 21.7.6
ae3d6d27-9844-5c17-ba83-d851b62db0a8 | note | Verifying Document - Drainage line record
cc65bc02-bfd1-54ff-a5a1-a937d0a7af29 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
85044673-0283-5e56-bae4-211e54ff9e8a | note | Verification Activity: Activity - I
5d0e0b52-3d6f-54c9-b7b1-24e898dd5b39 | note | Verification Activity: By - SE
a76d1aac-996b-561a-bc2b-69470a3fa996 | checkpoint | 3.5.1 - Headwall and Wingwall Foundation Compliance
f78edb06-81df-5055-a7c6-22d019d7c9d4 | note | Detail - On Granular or Cohesive Material
97596680-55f9-5a46-8ce9-b8b1984f656d | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
161eaefd-8b47-59b9-b777-387959290641 | note | Standard / Specification - PS- 21.7.2 Appendix V
7b8e1d0e-bdaf-5c20-8b28-cafdadd6986c | note | Verifying Document - Scala test result
e03bdc2e-8294-534f-a613-5a33f65f7bd0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Structure
2040fe92-1fb9-507d-b744-8496efceebd4 | note | Verification Activity: Activity - HP
b7f8addb-ca48-546f-a551-113c91e28417 | note | Verification Activity: By - ENG
70cd1be4-24ef-5063-abbf-f9dd93200e27 | signoff | AUTHORITY HOLDPOINT
f0688442-75bc-5d76-8177-3a9f6ee2134e | checkpoint | 3.5.2 - Undercut approval
ef0cd571-aeb0-54e9-9e9e-19dd57cc235e | note | Detail - On Subgrade
bb14ca25-4957-5fc9-8545-89ff1c784f8a | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
655ae977-f498-5805-a035-bc4288e7a720 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
05a01e9c-c880-52f5-94aa-0b63f931fedb | note | Verifying Document - Lab Test Report
a9411a00-5910-5970-aa31-7e3d6790cf9c | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
b06f7107-af61-5bfb-bf17-3763ded23ba6 | note | Verification Activity: Activity - H
95be9e29-2675-5975-90ba-ec47a2d96f0e | note | Verification Activity: By - SE
2478973b-6f47-5310-9ffd-14c721927804 | checkpoint | 3.5.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
5042d307-9abd-5707-9605-d866128daf16 | note | Detail - On Granular Material
fa542ca6-6552-5098-94cd-791e525997ec | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
b9cbfc1c-82d8-5684-822f-dad934367fa1 | note | Standard / Specification - PS- 16.5.12
23883edc-8bb5-5cf2-ba08-227d467d0ee7 | note | Verifying Document - Lab Test Report
bdb4fb1d-8f73-5155-b396-f6c9d5bfd867 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
94f59778-160b-5167-ab93-15cf962ff3fd | note | Verification Activity: Activity - H
24812b13-38e5-58c8-91de-caf926e6101b | note | Verification Activity: By - SE
4ba0a161-7530-58d1-afea-40100c2ddf2a | checkpoint | 3.5.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
aa4eae94-8e84-57e9-bc40-c0b6b8009d56 | note | Detail - On Granular Material
eba0b638-dba3-5c2a-ab67-2e5b677eedea | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
c6897a67-2e80-5b1d-8f91-4aed91d56933 | note | Standard / Specification - PS- 16.5.12
bb90d2cb-a8b6-530d-b551-b981361468b1 | note | Verifying Document - Lab Test Report
71ae2f59-a3e0-51c5-a2e9-f2c0861accbe | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Structure
c0bf7afb-a77e-5085-943d-ab34d9e6b8ef | note | Verification Activity: Activity - H
16e83c92-8258-53c7-be6e-bd8f2bc5bf7b | note | Verification Activity: By - SE
67a6cf71-f8c4-51e4-a8e6-ca7a915ab61e | checkpoint | 3.5.5 - Pre-Backfill Inspection
c9139488-9c15-5b76-a7ac-fe17a6e366e7 | note | Detail - Inspection of Structure
83687d12-36a9-5e3d-92c8-897dcf39c5fc | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
734c6fe9-b6e4-52ea-8756-b95c074ba38f | note | Standard / Specification - PS- 21.6.11
8180e4c1-c5b4-5603-94e3-0a2f84fec26b | note | Verifying Document - Manhole/Catchpit Record
9e476b44-9580-5f7d-8534-13388d2f8daa | note | Testing Quantity Required (based from schedule qtys) - Continuous
8e9a0637-842a-5346-80d7-c99da18b9f0a | note | Verification Activity: Activity - I
4b91cc23-a269-5d77-b7ac-8accd37f2e43 | note | Verification Activity: By - SE
d18baf16-8975-5e0c-8261-32049d9f49aa | checkpoint | 3.5.6 - Survey
84f9a34c-796e-57ed-b114-985940468f9f | note | Detail - Inspection of Structure
5711b32e-0f22-5f39-a7c7-b4e77ea77a32 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
a48f22c0-7cdb-59b4-afec-1a8992a98a71 | note | Standard / Specification - PS- 21.7.6
e95723be-0632-52be-9f6d-f854b5b07e04 | note | Verifying Document - Survey Data
ff404fa2-d32e-5ed9-8635-b5305ae93854 | note | Testing Quantity Required (based from schedule qtys) - Continuous
29a1340b-6e42-5360-b910-b3b22a11e517 | note | Verification Activity: Activity - H
ce76f530-653d-59ae-8e7a-47f935139969 | note | Verification Activity: By - SV
dc025cac-6aca-58ae-b492-06adb07f8de3 | checkpoint | 3.5.7 - Backfill Compaction Testing
1346e21b-2fef-5562-85ac-4cea3a579f77 | note | Detail - On Granular or Cohesive Material
71051c6d-4c93-52d4-b996-5076b9fb16d6 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
3195505d-e3f2-5348-baf9-25ab49003165 | note | Standard / Specification - PS- 21.6.12 Appendix V
14bcfe6b-29c5-53b7-9ba1-74dbebc17739 | note | Verifying Document - Lab Test Report
3b096be4-1256-5002-a55a-71e8231fb4d7 | note | Testing Quantity Required (based from schedule qtys) - 1 test per layer at Quarter Points around the Structure.
4039098c-fb29-5e32-91ac-91c844648db6 | note | Verification Activity: Activity - H
81f698d1-a27d-5d65-bc46-6da8159ee841 | note | Verification Activity: By - SE
909aaa35-1436-5b32-b06b-9bd5efa45dfb | checkpoint | 3.6.1 - Riprap Foundation Compliance
8c982575-8f2c-59c1-977e-c25c39d64f25 | note | Detail - On Granular or Cohesive Material
2bb8285c-229b-54fb-97ec-f833ba6be8f1 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
dc955bbc-9a3d-593e-9962-9c82ee33751b | note | Standard / Specification - PS- 21.7.2 Appendix V
9add7a5a-96f2-581e-bc0c-7dcc547c8131 | note | Verifying Document - Scala test result
458d268d-c5ce-58a1-acdd-6a0e85e5b93b | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
4265f2e4-0470-5cd6-99c9-d0fbed85396e | note | Verification Activity: Activity - W
8e3ec2d6-cb8b-5d7a-82ad-f27f70273460 | note | Verification Activity: By - SE
c318d5a2-491c-50a3-a033-e6f98e6800b5 | checkpoint | 3.6.2 - Undercut approval
0e8c63a4-8c7b-5557-b780-b6bd4f412b40 | note | Detail - On Subgrade
d618f982-fedd-5c90-b8c8-6f337bd942df | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
f89839c8-0e55-5a32-849f-7799c50c9639 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
e53943a5-601a-5adb-aca0-5d36125067c9 | note | Verifying Document - Lab Test Report
7b1e4c0b-e56c-5662-88b8-11aaf8368b70 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
67d32ada-8318-541d-aff5-31b1a35b74fa | note | Verification Activity: Activity - H
5445342b-5422-5140-9aec-4eed0f9bebf4 | note | Verification Activity: By - SE
6a55d5f9-a096-5d22-bb1c-56e2e00cb6d1 | checkpoint | 3.6.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
4d27efe5-19d0-50e1-8ef6-50037e431090 | note | Detail - On Granular Material
1cc127d0-0a40-512c-8ee3-73acb8f02810 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
27b92731-ded7-54d5-9e34-9ba001b42097 | note | Standard / Specification - PS- 16.5.12
a2064463-78e9-5070-a08b-0d3b645233d1 | note | Verifying Document - Lab Test Report
930351f6-ec88-51bc-8c2d-be40d14ef1cb | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
673ded28-b7af-5da6-9048-05f86cacdd96 | note | Verification Activity: Activity - H
92b90047-732d-5e91-8a1b-0c821b01b370 | note | Verification Activity: By - SE
70aa118b-5499-55a2-88d1-6a112d0eb702 | checkpoint | 3.7.1 - CCTV Inspection
46c6bdc6-2aae-5108-affc-809fef37f6fd | note | Detail - CCTV stormwater pipes at completion of trench backfill but prior to final surfacing (pavements, etc.)
ccd8b0cc-b65c-5d2e-a6da-a6fe7b42fda4 | note | Acceptance / Conformance Criteria - Every stormwater pipeline 225mm diameter or greater.
162700d6-751b-549a-96a9-86215702274a | note | Standard / Specification - PS- 21.7.6 PS- 21.7.8
d89f7f1c-f83f-5c38-982b-be558f2eb986 | note | Verifying Document - CCTV Report
5bfeab30-8546-5182-ad77-d2a8f0024b72 | note | Testing Quantity Required (based from schedule qtys) - 1 per line
5a19d298-49c6-5d79-ab44-c505a060d77c | note | Verification Activity: Activity - S
3af3faf7-912c-5633-8f2a-a41081eb6280 | note | Verification Activity: By - PE
84c3283d-24bd-504e-b593-7adb2a662256 | section | SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
13049da8-dc5f-50e6-9653-61f13f53ec94 | checkpoint | 4.1.1 - Survey As-Builts
43405ff8-93a4-578f-8245-80b6a0ba30db | note | Detail - Quality Check on New Works based on the tolerances in RITS
75fa7eec-e69c-5510-a9fd-4d65f0dc461d | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
7e5788d2-50c9-52f4-bf02-4a7eda67d156 | note | Standard / Specification - PS-21.7.7
5fe67f93-427a-59b5-ae3e-31e8cfcf0324 | note | Verifying Document - Red pen markup only
91e56975-23b2-52d3-a796-4e4e6b9d9e16 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
7b449813-211a-5938-b86c-3592cb4fb49a | note | Verification Activity: Activity - H
84f4cb19-b321-5af5-81b4-05813f1cc00d | note | Verification Activity: By - SE
cb6ba0b2-0793-4a89-a8bd-eb5bb3818a9f | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
23a52ea0-c0a3-58f6-a912-c89c733a0219 | textbox | Contractor's Rep Name:
e566d123-07cf-5568-93a5-76ca2c9dd9fc | textbox | Engineer's Rep. Name:
95981a3f-70e7-52bc-bd38-a2aa23047133 | date | Date:
d6eef712-edbd-4cd5-8ca8-0e8534f86864 | signoff | Add Signature
ff1dd30e-f24a-4b4b-9eac-bf686c0f70de | checklist | DN1210-008 ITP Noisewall 1 Rev 1 | itp | DN1210-008 ITP Noisewall 1 Rev 1
dc439d04-ad5e-5573-818f-c5c286b26df4 | section | SECTION 1 – PRE-CONSTRUCTION - MATERIAL, PERSONNEL & THIRD PARTY APPROVALS
5ba25caa-7a71-5139-8d6d-82357c289e49 | checkpoint | 1.1.1 - All metalwork to be approved by the engineer after fabrication
87bdd074-adec-58fd-a63c-e6d5e028f17e | note | Detail - Hot dip galvanised to standard hdg 900
98c69e01-29f3-53f2-8d6f-dd8f1cafe8dc | note | Acceptance / Conformance Criteria - Engineers Approval
b0b5c028-b263-5d86-8468-bed9858bf891 | note | Standard / Specification - PS 18.6.3
c6975e6d-cf42-58a9-96dc-90bbede7ad84 | note | Verifying Document - Visual inspection
071be570-ee9f-5a57-8e93-4b073c8c9c16 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
9bee1edf-40d8-5d3f-9a5d-4906f515415f | note | Verification Activity: Activity - HP
79f83faf-d5c7-5db3-9443-d9741f98c18e | note | Verification Activity: By - ENG
068dedb1-7fbd-5e00-a102-f41752de9010 | signoff | AUTHORITY HOLDPOINT
5b77c275-c7aa-5684-bd40-ba54d126d5bf | checkpoint | 1.1.2 - Hot rolled steel plates
2c47a6e9-a08e-5739-8f29-c7e8d3d02837 | note | Detail - All hot rolled steel sections shall be grade 300 complying with AS/NZS 3679: part 1
0dabdb54-74a7-54dd-ae40-de3ad20818e8 | note | Acceptance / Conformance Criteria - Grade 300 - AS/NZS 3679 Part 1
c76b6bca-e6f4-56fa-b7bb-d1453d9508b2 | note | Standard / Specification - PS 18.6.3
a46f0673-50f2-5848-9a66-351ee8402005 | note | Verifying Document - Supplier data sheet/ Mill certs
f71ae4d5-a759-5b64-b484-b80fad78b13a | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
80d4a903-5755-56af-b710-67b364d9d378 | note | Verification Activity: Activity - WP
b76c6864-d65d-5d6e-ba9b-54b00ad6a871 | note | Verification Activity: By - SE
993a2c97-80d3-5c56-8bb5-3a0cd3e51097 | checkpoint | 1.1.3 - Cold formed steel plates
d229f0f2-364a-5210-8086-72c1ce3bc2bc | note | Detail - All cold formed steel sections shall be grade 350lo complying with AS/NZS 1163
ba4d8304-9bcc-5de9-bb60-487d32752774 | note | Acceptance / Conformance Criteria - Grade 350 lo - AS/NZS 1163
c8b7045d-4e65-5004-b178-2faf397810e7 | note | Standard / Specification - PS 18.6.3
d30d11e5-c982-50e0-8b24-1c3de7152c7d | note | Verifying Document - Supplier data sheet / Mill certs
88a15989-7ae8-53ff-bf84-0175e84754d0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
7c299bb9-c2f8-54d8-a453-63e52980a80f | note | Verification Activity: Activity - WP
27df037d-7969-5882-879b-edce791de7c5 | note | Verification Activity: By - SE
db79d8f7-33e2-5c0e-862f-cefa1df6e8e5 | checkpoint | 1.1.4 - Mild Steel plates
a32c4834-9a78-539c-a5d5-7389c11d1b7d | note | Detail - All mild steel plate shall be hot rolled grade 350 complying with AS/NZS3678 (AS/NZS 3678-350)
7cd9c1c7-b21f-5d70-88cb-fbbfeaa4afd6 | note | Acceptance / Conformance Criteria - Grade 350 - AS/NZS 3678 (AS/NZS 3678-350)
d88a1b24-e1db-52f5-8aaa-7b85b0ae3e0f | note | Standard / Specification - PS 18.6.3
46e7120f-018f-5703-8219-bb5e63b2883d | note | Verifying Document - Supplier data sheet / Mill certs
a914bf70-1c36-5e5c-897c-04a8c79f8ab1 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
5f2399dc-817f-55ed-a292-855b1c106f85 | note | Verification Activity: Activity - WP
c77476e6-0463-533c-a9c8-eac096afef73 | note | Verification Activity: By - SE
4efd7e12-8765-507c-8da0-599a589078b5 | checkpoint | 1.1.5 - Round bar/rod
d5ef4756-3498-5ae0-9a8b-684db7d96f7f | note | Detail - To be grade 300 to AS/NZS 4671
fbc5f7fb-ae65-5167-953f-1701743687a8 | note | Acceptance / Conformance Criteria - Grade 300 - AS/NZS 4671
b4cd69d2-a6ba-5f3c-9b24-fa0050b144d7 | note | Standard / Specification - PS 18.6.3
c4b46c52-20a5-5af5-ac60-51251bebc3eb | note | Verifying Document - Supplier data sheet / Mill certs
e6e6c9c9-4a44-573d-9963-66dcef45d4e0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
4d58bc98-af07-5c06-b891-53233ccb29c2 | note | Verification Activity: Activity - WP
56ab8d87-e873-54cf-a6c1-e57300c7fd8d | note | Verification Activity: By - SE
1e999714-ded7-5714-ab23-b5f574a633d9 | checkpoint | 1.1.6 - Bolts and treaded rods
1e50e369-0191-5760-bd17-89eba5bce932 | note | Detail - All bolts and threaded rods shall be category 4.6/s to AS 1252
2d982ca6-dcd0-5c16-b12e-41a1e5c8cdf4 | note | Acceptance / Conformance Criteria - Category 4.6/s to AS 1252
844e284f-14e5-5b7f-be6d-cb835df0005b | note | Standard / Specification - PS 18.6.3
29b0a3f2-dd61-5e2b-97cc-688a22af3ac7 | note | Verifying Document - Supplier data sheet / Mill certs
791a825e-9754-565d-9548-7fc700f2c145 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
d3c70cf8-f765-5516-bc1b-8e0a2780853b | note | Verification Activity: Activity - WP
bfc76215-8b62-5cc8-8738-8c55a68ce26c | note | Verification Activity: By - SE
d47b70c7-d4f7-50b0-a088-bbd13a0577a5 | checkpoint | 1.1.7 - Rough or sharp edges
8239cc44-df77-5242-9d2a-53a51beb9e26 | note | Detail - All rough or sharp edges or protrusions to be buffed smooth
17f0a785-ff6a-5f0f-9d31-ed21bf94dabd | note | Acceptance / Conformance Criteria - All rough or sharp edges or protrusions to be buffed smooth
b5b71663-219b-5d9f-b957-16d39207e4cc | note | Standard / Specification - PS 18.6.3
cc58fa48-e238-53d1-85fc-bf562f0e3f01 | note | Verifying Document - Visual inspection
59159e4c-59a9-5256-99c1-d369a80f0b82 | note | Testing Quantity Required (based from schedule qtys) - During construction
14acb6ad-ba1b-5e05-8b3c-2c7e58085328 | note | Verification Activity: Activity - WP
730fa375-2c73-551a-be83-c3d2fc2ee5c9 | note | Verification Activity: By - SE
704a29d7-c4e9-5cfa-84e8-252fd7bf2eb1 | checkpoint | 1.1.8 - Epoxy Coating to the Steel column
da36ea66-3e4c-5373-8400-500b2eeccdc8 | note | Detail - High build epoxy paint all round the UC column concrete interface
4f50d82f-af3a-5dee-a5b8-897551e5b9f3 | note | Acceptance / Conformance Criteria - all columns must be coted with epoxy at steel and concrete interface
3831f71a-b15d-5fee-a9a9-57072adab45d | note | Standard / Specification - WSP-DR-STR-0306
3b331bb3-c95a-5cb7-93b2-40083c5e8e22 | note | Verifying Document - Visual inspection
c71ecc60-3158-574f-b678-6bc87e3f42be | note | Testing Quantity Required (based from schedule qtys) - During construction
e57e7e2d-40fe-5f23-b707-093f89a44736 | note | Verification Activity: Activity - WP
7b63766e-38d0-5caa-954f-4697e765b776 | note | Verification Activity: By - ENG
95a62a2d-dc41-5729-8c34-772c79c3554e | checkpoint | 1.1.9 - Butynol sheeting - membrane
5a887d98-a2d4-54ae-a390-0257dd636dcd | note | Detail - Butynol or any similar approved shall be used between timber and steel
2ca757a4-cbc8-566c-a551-e5db903dcfc1 | note | Acceptance / Conformance Criteria - Membrane seal
b6b16dcb-822a-55ae-88cc-938242b76771 | note | Standard / Specification - PS18.6.3
ef5fb293-1a54-57d4-96f0-4323475e14ee | note | Verifying Document - Supplier data sheet and Engineers approval
82673ede-b43f-50e3-bcde-fc08d9726de8 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
2a6cfa88-e388-5cd9-ac3a-21a9ef606b81 | note | Verification Activity: Activity - HP
345840de-24e7-571d-b77f-bf487038ee5b | note | Verification Activity: By - ENG
ba2ef6ed-92a6-53c7-bfe9-b134dba90eb7 | signoff | AUTHORITY HOLDPOINT
e6bb1c37-103d-54be-bbb4-bf36c50c5f77 | checkpoint | 1.2.1 - Timber
54251110-fb04-5634-804a-92c22b624288 | note | Detail - Timber shall be VS8 grade radiate pine complyng with NZS 3603 and graded to NZS 3631
fcd03198-8f9c-5850-84d0-b493cd0ba8d4 | note | Acceptance / Conformance Criteria - VS8 Grade radiate pine with a Timber strength - 11.7MPa
5e992fc1-b3d7-5182-9932-816b8f7679e4 | note | Standard / Specification - PS 18.6.3
c4f87a52-0519-5ae8-b336-5759aea2f92c | note | Verifying Document - Supplier data sheet
fa6a83af-5c9d-580d-a86b-e5a78110f7e3 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
a50d4d7b-7c36-5752-a447-950f2b4e1fb5 | note | Verification Activity: Activity - I
e1de97ba-ae1c-5ab1-918a-6404fe0c2bb2 | note | Verification Activity: By - SE
30369b36-252b-59e5-8453-1ef6cc725793 | checkpoint | 1.2.2 - Timber - in contact with the ground
5152ee6b-48c1-5452-b7f7-665c012b4671 | note | Detail - Round or rough sawn piles in contact with the ground to be H5
c3eeb317-ac30-5f95-9d7e-3101991d8efb | note | Acceptance / Conformance Criteria - H5
75f7dbe8-72b9-5f1a-b8f7-15826c932b2d | note | Standard / Specification - PS 18.6.3
bf956d8b-9861-5579-80f7-03b4bee0420a | note | Verifying Document - Supplier data sheet
23055f9c-ecab-5a59-a7fb-780233919e42 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6e964ee1-46bb-52ad-b717-a5218a6e0fdd | note | Verification Activity: Activity - I
f380da60-80b7-5056-9f3a-2277ffcf4687 | note | Verification Activity: By - SE
94a81899-257a-5ffe-8a11-73f210325de7 | checkpoint | 1.2.3 - Timber - not in contact wth the ground
43baedb1-f8dd-5799-ac13-68a41cd4a8ae | note | Detail - Rough sawn timber not in contact with the ground to be H3.2
cc284ec9-df83-5816-ad1e-e548ef3fd65a | note | Acceptance / Conformance Criteria - H3.2
8995acd9-333c-570a-aec6-e20765ea8fac | note | Standard / Specification - PS 18.6.3
7cc07edd-fd8c-54ae-9d41-96ce81f43ac9 | note | Verifying Document - Supplier data sheet
7544f38c-33b7-522c-846e-628837afbd0f | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
91921caa-8caf-5c2e-9d1c-53429a51783a | note | Verification Activity: Activity - I
51024bff-9929-505d-af6d-acbf42b96537 | note | Verification Activity: By - SE
ee29378b-32d7-5f42-aa47-1090de8ff24e | checkpoint | 1.2.4 - All timber components of noise wall
c2944171-e8da-5bd4-8444-bbb67bfefd09 | note | Detail - Timber treatment shall comply with requirements of the NZ Timber Preservation Council incorporating - MP 3640. All timber shall be branded to NZS3640:2003 and must be treated not less than 2 months prior to use.
6448cf6e-b977-5414-adad-2b8f783fe839 | note | Acceptance / Conformance Criteria - MP 3640 NZS3640:2003
00a5bf57-9093-5222-a8de-7d7dded3457f | note | Standard / Specification - PS 18.6.3
1e318461-45a4-58c1-8ed2-c2bcf92458f5 | note | Verifying Document - Supplier data sheet
8c1efafa-2b61-531e-8f1f-39397d4d62b1 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
a0d72391-9573-5058-a0eb-84b413e05e9b | note | Verification Activity: Activity - I
3f823901-11f9-5b7a-981a-3f0f4aac3691 | note | Verification Activity: By - SE
f9d62092-ddd4-595b-9974-ca2ed9af18d3 | checkpoint | 1.2.5 - All timber components of noise wall
0efa02f3-da79-5b77-bdd5-a4d5f22e1971 | note | Detail - Timber shall have a moisture content less than 18% at time of installation to avoid excessive shrinkage effects.
20c0394f-4abc-5d3b-8f4d-edef79533980 | note | Acceptance / Conformance Criteria - Timber shall have a moisture content less than 18% at time of installation to avoid excessive shrinkage effects.
2d87e160-dae4-5e64-b3a7-76c6a9977cb4 | note | Standard / Specification - PS 18.6.3
94f6326b-2489-5eb6-be61-4aa3bd13487b | note | Verifying Document - Supplier data sheet
307a1a62-bac2-522c-a99c-4cf8b742b1ba | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6a315b29-999f-5814-ba87-a57841b3c4c0 | note | Verification Activity: Activity - I
bc525129-b4b8-5d43-885b-04861ce2640c | note | Verification Activity: By - SE
3272a837-e1fc-58a0-bc7d-7379bc60c516 | checkpoint | 1.2.6 - All timber components of noise wall
544ad440-b824-5da8-aee9-8bd16b5721e5 | note | Detail - Treat all cut surfaces with clear zinc naphthenate preservative and in accordance with NZ 3602.
f76dc74f-24e1-549f-88e4-1abf6be9aa7f | note | Acceptance / Conformance Criteria - Treat all cut surfaces with clear zinc naphthenate preservative and in accordance with NZ 3602.
37588d10-c423-59ed-961c-c956f7444c29 | note | Standard / Specification - PS 18.6.3
64c3846b-da7a-5d28-afc5-0c21935d4daf | note | Verifying Document - Supplier data sheet
d518a1e3-9870-5cfd-a733-66bea55e6cfc | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
eaf54b00-742e-551f-b9ec-5f73e8687585 | note | Verification Activity: Activity - I
911327c4-79d1-5baa-bb99-d9fb85bf6469 | note | Verification Activity: By - SE
f9dfbf52-7921-564c-a925-33cba059da58 | checkpoint | 1.2.7 - Galvanised bolts
2440ec0a-26dc-5d22-924a-c6e698d6f007 | note | Detail - All galvanised bolts in contact with H5 treated timber shall be protected using CP grease in pre-greased holes
855e0003-4cf5-5e72-8e20-f8b1614cf3e2 | note | Acceptance / Conformance Criteria - All galvanised bolts in contact with H5 treated timber shall be protected using CP grease in pre-greased holes
42f7b2c3-d6c9-51a6-8261-8b52eb60acaa | note | Standard / Specification - PS 18.6.3
e0a8034f-f8a9-5a0b-b2ba-c642ba4a4544 | note | Verifying Document - Supplier data sheet
3c2a2849-e465-5a3c-9b68-b756239e59e9 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
f4e95223-4a6a-5b04-8f80-6bfc0009a868 | note | Verification Activity: Activity - I
d4334259-f555-5639-a09f-63f567035a45 | note | Verification Activity: By - SE
e1936029-7894-51a0-a7be-3a1a2e755a8a | checkpoint | 1.3.1 - FH Nails
28d68371-a3d5-511d-b574-81b8c7782309 | note | Detail - General structural use 75mm x 3.15mm FH nails . All nails shall be flat headed, unless otherwise shown, hot dip galvanised and fully driven
db628c59-bf96-53a3-807a-f39fd18dcc9b | note | Acceptance / Conformance Criteria - 75mm x 3.15mm FH Nails
4a24bfb7-c4b1-5ca4-98da-eb87499c26ca | note | Standard / Specification - PS 18.6.3
05837ee9-a67a-5272-9bcb-f7894e309c17 | note | Verifying Document - Delivery dockets and supplier data sheet
fa89e629-1bca-55aa-aec2-dbd87af7df2f | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
82240e18-b2c3-525e-a2bd-727bb0d0d38b | note | Verification Activity: Activity - I
d179c9ba-17a7-5947-bae0-079338a7cc4e | note | Verification Activity: By - SE
92dc6277-2665-5d70-9e48-177822abec7e | checkpoint | 1.3.2 - Bolts
6fd1fc27-2e0a-5602-b948-507ecdba4eab | note | Detail - Bolts shall be M12 hot dip galvanised engineers bolts fitted with 50x50x5 galvanised square washers both ends. Washers for coach screws shall be provided in accordance with NZS 3604
672ea647-fc9d-597d-a6f1-13f399bfe296 | note | Acceptance / Conformance Criteria - M12 hot dipped, 50x50x5 galvanised square washers
f0c14c3d-8f7f-5a83-bc6c-760c84878fa1 | note | Standard / Specification - PS 18.6.3
aa565e89-d839-522b-9d92-689160284664 | note | Verifying Document - Delivery dockets and supplier data sheet
9ecbbaa8-0958-51a5-9143-d165d1ec9f6c | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
42240d1d-3fb6-54ad-979c-dcceb7e9c33c | note | Verification Activity: Activity - I
d49b33e6-b909-5d28-a95a-0e9dd644da3e | note | Verification Activity: By - SE
f6166390-0424-550a-b578-335017e863af | checkpoint | 1.3.3 - Bolts within 100mm of ground
ef0a452e-c447-559d-b720-ec3894f29512 | note | Detail - Bolts within 100mm of ground to be stainless steel.
910e16b5-6385-5c14-b82a-1a3eddeba3a0 | note | Acceptance / Conformance Criteria - Stainless steel bolts
aad17169-f7e8-5347-b07f-98395edf6661 | note | Standard / Specification - PS 18.6.3
126723f5-ecf6-5a58-a83c-f5b39d7d2534 | note | Verifying Document - Delivery dockets and supplier data sheet
4c1ffdfc-2a94-538b-909e-c3a8044cabe0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
413b49f0-dcc7-5238-8eab-d5a8b84ec194 | note | Verification Activity: Activity - I
3581952e-8803-5645-a554-6a585406dae6 | note | Verification Activity: By - SE
52dad3df-5c5f-542a-9707-5e4361323e21 | checkpoint | 1.3.4 - Coach screws
057507f2-4ca3-53ed-b8f0-f91c2e0da906 | note | Detail - All screws shall be hot dip galvanised and screw fixings shall be pre-bored.
1172649a-ca70-5d69-8e0d-9831d8152c9f | note | Acceptance / Conformance Criteria - Hot dip galvanised
43aeca2a-3829-5bf7-9322-fe2d86805984 | note | Standard / Specification - PS 18.6.3
a00ac75c-241f-517d-b981-d91e3044bfad | note | Verifying Document - Delivery dockets and supplier data sheet
7d2e118d-6fb3-5f8f-a6c3-dfbb5789eab7 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
df201f03-523a-5c04-b873-1de4e77e82bc | note | Verification Activity: Activity - I
96482dff-afec-5c12-b89f-0f524336fc05 | note | Verification Activity: By - SE
868e15d2-a829-5664-9f4e-1c730798c2ea | section | SECTION 2 – CONSTRUCTION ACTIVITY
8abc6212-3111-540b-9738-78a20e86ed40 | checkpoint | 2.1.1 - Setting out of Noise wall 1 all Posts
db9796ec-3de3-5f3e-a2b1-b371b55d636e | note | Detail - Setting out to follow design coordinates and levels within tolerance as specified in PS 18.5.7 section (e).
53c8d121-406a-5754-9665-84e5ce60fddc | note | Acceptance / Conformance Criteria - Engineers Approval
1ac7c545-fb56-5f43-9e9d-71200baa4099 | note | Standard / Specification - PS 18.6.1
49eefdea-60f2-5a7e-9485-4e81f54dee3d | note | Verifying Document - Visual inspection
9b22254b-b8c5-5fe2-abd2-fa7d667abe0e | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
d1b4e7ef-1486-5850-8c93-780e3ff27f28 | note | Verification Activity: Activity - WP
d5b62a0e-ab48-51a2-a5ca-bac0bff62f81 | note | Verification Activity: By - ENG
ac86be99-18f9-57a8-bf7c-14f69d596955 | checkpoint | 2.1.2 - Geo Technical investigation on each post holes
45032e44-c37a-598f-82f4-efe6d77a54e1 | note | Detail - Holes are to be 400mm dia and 2.8m deep. Shear vane testing to be completed to a strength of 60kpa
89cde49d-cbed-5656-8b76-5995c7d79101 | note | Acceptance / Conformance Criteria - Shear vane strength of 60kpa
815a6b13-4eda-5a1c-a9bb-3617264cd253 | note | Standard / Specification - PS 18.6.2
754362a4-9655-5c9c-92cb-f40197172609 | note | Verifying Document - Shear vane test report/Visual inspection
f9620d0c-b2c0-56cb-bd18-a6a4a167c6e9 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
c233521d-d38f-54bc-a9e0-72be1d3f9899 | note | Verification Activity: Activity - HP
4209a781-2ab3-588f-8d78-e9fa3287449d | note | Verification Activity: By - ENG
9e47e5c7-cb75-541e-a14f-4afa4b5d7a68 | signoff | AUTHORITY HOLDPOINT
2cdf9c15-2c63-5aac-9f2e-a940d4990caf | checkpoint | 2.1.3 - Noise wall footing concrete
139e9071-f02a-51c5-872c-60346393be5c | note | Detail - 17.5 MPA Concrete
9a2ac467-7a99-507c-88f3-8c9200f75b7b | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 17.5MPA
01f3b2d3-71df-5c0e-a557-cebe048096f7 | note | Standard / Specification - PS 18.6.2
a31d14e4-0d82-51e2-8601-61322fbf976b | note | Verifying Document - Concrete Delivery Docket
324e5e6c-bff7-5126-a664-7c0f7209f2b4 | note | Testing Quantity Required (based from schedule qtys) - During Construction
3216a620-a366-5d1a-8ff3-dfedb315054d | note | Verification Activity: Activity - I
2d5f18ab-85ce-56a2-b39b-83bbed73787d | note | Verification Activity: By - SE
b0af36a8-2e1e-5d8c-8d3d-b3d850c71730 | checkpoint | 2.1.4 - Installing Wooden Railings
207f27c0-a0e6-587f-8899-c5cad0ebc6df | note | Detail - with sufficient embeddment of nails and connecting details as per drawings
b8c45349-31a7-5ed8-9b83-67be91a22764 | note | Acceptance / Conformance Criteria - Skew nails shall be installed as shown:
6543a4e4-ab92-5a54-b0b3-4b3930c38246 | note | Standard / Specification - PS 18.6.3
6487da79-9484-5263-a42b-99a80c9b5613 | note | Verifying Document - Noise wall Checksheet
5ef90dfc-9ed5-55fb-8406-0f069a808cc3 | note | Testing Quantity Required (based from schedule qtys) - During Construction
89875b75-8f03-53ee-8339-893c9791911f | note | Verification Activity: Activity - I
a98fea2e-6479-5811-8272-80c2c4a34be4 | note | Verification Activity: By - SE
47886ec3-63d6-5e34-814f-8a266d50043d | section | SECTION 3 – POST CONSTRUCTION (HANDOVER)
49e56452-d262-55bb-8e2e-45db3938f81d | checkpoint | 3.1 - As-builts
790edb2b-229c-5e7c-980d-fe019c0d306d | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
4915cc5a-a225-518b-a3da-ffe8886dca97 | note | Acceptance / Conformance Criteria - All changes to design need to be captured on the noise wall drawing set
71b63e81-f275-5591-812b-c0601b22bae6 | note | Standard / Specification -
f046623b-db5a-53f8-bd6b-d4e4b89d9e10 | note | Verifying Document - Redpen Markup
9cd59d86-5195-5dd3-a4f3-42f6def3fa28 | note | Testing Quantity Required (based from schedule qtys) - During construction and after finishing
ffc5e08f-200b-5cd0-ab09-336f592f225b | note | Verification Activity: Activity - WP
a1abcf24-c909-5eb5-a2d0-6730301d1972 | note | Verification Activity: By - SE
e5125254-ffa1-40a7-8898-657a0b543ade | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
5b316864-b58a-55a0-8416-0635f30f4dea | textbox | Contractor's Rep Name:
17ce483e-e328-5e7a-a60e-0fd11ed74c75 | textbox | Engineer's Rep. Name:
32adacd4-f54c-55af-8dc0-0fabac71ba31 | date | Date:
e325a840-3071-4552-9013-4b3bb5e9bd70 | signoff | Add Signature
8c66c8f7-6bc4-445f-9130-ad10c40b11b7 | checklist | DN1210-009 ITP Underpass Rev 0 | itp | DN1210-009 ITP Underpass Rev 0
9cbb510e-fd5d-4219-af3d-5f436531ae9e | section | SECTION 1 – EARTHWORKS SUBGRADE
4b8442c9-d337-4db5-bde4-ea2c0d5abaed | checkpoint | 1.1.1 - Cut Subgrade Inspection
a0cd40f0-6ab6-5c48-add2-ed14c5397384 | note | Detail - Engineer to inspect all foundation surface inspections
56d04848-e1a7-5446-98e4-0807d8202465 | note | Acceptance / Conformance Criteria - Engineers Approval
dcb61ee7-d946-5ae2-9ced-7f1232dee7c8 | note | Standard / Specification - Appendix V
f8ca2430-1672-59d8-ad0b-e1ef73b9dc37 | note | Verifying Document - Visual Observation
00b32753-c725-5f62-8254-8d76c67a0b4b | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
eb77ce94-f291-5f30-908c-de65ca7cafa3 | note | Verification Activity: Activity - HP
c68a4b1e-7c0e-5ccc-80b5-058d3f24f57a | note | Verification Activity: By - ENG
393a82f7-b3c7-4080-85fb-ffdc930f746a | signoff | AUTHORITY HOLDPOINT
fe906f2c-8564-45d4-b12a-24e38a51b667 | checkpoint | 1.2.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
be2404ff-fd22-511b-b3c0-b5d7a4fd1024 | note | Detail - This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
8d54c44f-b86c-5d57-a64b-bcbf5bf3abf4 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
fe06a3a4-0846-5222-a3a0-edd8a6fb88c0 | note | ○ Single Test Min SU: >50kPa
aa0752af-6a98-5d2a-ad94-e08764c7d8b7 | note | Standard / Specification - Appendix XVIII
10ae48b3-fc36-53eb-8b6c-a690e9910492 | note | Verifying Document - Shear Vane Report
693dc52b-b004-517b-9639-b6e5c7dec805 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
65e1976c-483d-5485-bccd-9162b55ed8ef | note | Verification Activity: Activity - I
debc24a2-16c1-5050-9e31-7890bf0629a9 | note | Verification Activity: By - SE
e52b86a5-b667-471a-b63f-e45d88af79e8 | checkpoint | 1.3.1 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
4869fba6-e378-5d3e-a433-53b2a5b7d6c4 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
bb41ccfb-e9d6-5e81-b6d3-d777072128ee | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
cb72e9a4-eb8f-5c81-bcb4-c753560d01e2 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
c6f25b73-2fc1-5a47-9227-1eb1b10e4308 | note | Standard / Specification - Appendix XVIII
f8e82909-0414-58c2-b20c-8ff47b597494 | note | Verifying Document - Scala Report
1c1239f6-e846-57a7-968c-ece61f59413e | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
ab485686-7a4d-500c-9b95-08e2b73ee3dc | note | Verification Activity: Activity - I
f1b63378-316d-526a-874b-6337508b9bb9 | note | Verification Activity: By - SE
34f35990-312e-4551-ac9c-b683685967e2 | checkpoint | 1.4.1 - Undercut Surface Inspection
3455ad10-4902-5b88-bbc5-24f8bcfd63d7 | note | Detail - Engineer to inspect undercut surface and determine undercut requirements.
0568c8dd-fb95-5072-a6f8-038c12c96935 | note | Acceptance / Conformance Criteria - Engineers Approval
f21f8e30-459a-569b-b9e2-d80120fecb88 | note | Standard / Specification - Appendix V
cf29355c-d20e-5bfc-af1b-667d39dadc50 | note | Verifying Document - Engineers Approval
2ffa16c2-ba28-5f7c-bde9-6cb10a3911bf | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
c404a650-32c9-5fbc-8d11-12557dd3053c | note | Verification Activity: Activity - WP
8f692dc3-bc9c-5729-a9b7-e88689700cc3 | note | Verification Activity: By - ENG
e13da792-0d1e-4e73-8b23-6fb9cdad2ed7 | checkpoint | 1.4.2 - Placement of Geotextile on Undercut
ff42db0e-2d67-5894-ae0f-fd07af6dbfb8 | note | Detail - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
e2ab5f07-bcc4-5382-9338-c1f66e789a76 | note | Acceptance / Conformance Criteria - Engineers Approval
038eb8a9-66e4-5a21-9b3f-c4e5745f4241 | note | Standard / Specification - PS 16.6.4, TNZ F/7: 2003 8.3
8eab2ff8-a0b1-5974-a0dc-7de5168d9650 | note | Verifying Document - Visual Inspection
8e0a2ffe-d77f-5819-9b4a-aaa3aa1cf5bf | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
5a73b327-2ec0-59db-9a95-33b1419c270c | note | Verification Activity: Activity - WP
d4defb56-fadd-595f-93a3-3aa564d245d7 | note | Verification Activity: By - ENG
05bf4ffa-fdd0-4c21-8138-feaf4e0eb7ef | checkpoint | 1.4.3 - Backfill undercut
095c2041-8e00-5ca2-8df7-954b56ff9d42 | note | Detail - Backfill undercut with AP100 and lightly compact.
d1e87609-4f3c-5327-8303-6e4099783099 | note | Acceptance / Conformance Criteria - Engineers Approval
c889b3ab-5893-5352-8ba6-81f5f065de84 | note | Standard / Specification - In Eight ref: DN1210-WSP-NTC-0207
fceb0599-f45e-5daf-b736-49b9537d253f | note | Verifying Document - Visual Inspection
46a0f26a-f8b7-5b57-9c99-a939af10d9aa | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
06095ac4-9afa-5ef1-8b34-b21ee75c6eac | note | Verification Activity: Activity - I
4739a17c-b638-576e-ad7a-4b102099a57f | note | Verification Activity: By - SE
9fbc893c-6858-4254-a22e-1619e2055582 | checkpoint | 1.5.1 - Foundation Compliance
af159101-811b-525d-b715-dfa8a00b310e | note | Detail - On Granular or Cohesive Material
f7d29786-abb3-581c-87fe-958e09b0baaa | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
3ae2950a-5c95-5c22-b09d-ea9c027c45a8 | note | ○ Cohesive Material: Shear vane Strength 70kPa
715bdcf2-fe84-554f-83d5-5e216502b802 | note | Standard / Specification - PS- 21.7.2, Appendix V
002f0a75-0eaf-5dfe-8d46-844fdd4ff0ba | note | Verifying Document - Scala test result or Shear vane result
15a94ab6-1330-5869-82a8-fa738139e2ba | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
ab67b06f-33ce-55aa-bc40-5d7922e22376 | note | ○ 0-5m: 1 Tests
6592e4e6-d65e-5971-b859-c7ed132017e1 | note | ○ 0m-10m: 1 Tests
06d0b956-7e20-5dda-8f11-462811cdcb4d | note | ○ 0m-20m: 2 Tests
8270c8c9-0c3b-5ef0-9622-52fe305a1634 | note | ○ 0m-50m: 4 Tests
ffef4716-d092-5218-963e-90386cab37df | note | ○ 0m-100m: 6 Test
65050099-fa93-5d77-9a83-42dfb50bdbb9 | note | Verification Activity: Activity - W
3ed704c2-162e-5324-9c7e-411d440f4555 | note | Verification Activity: By - SE
e1095b8c-8ca4-4b3a-91a6-279bb38a48e2 | checkpoint | 1.5.2 - Undercut approval
1e9b6bf3-a2ae-5c69-85a2-a0d2288a9661 | note | Detail - On Subgrade
b8a979cb-284c-53df-87cc-9682ee4fb002 | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
7c9e669a-f46c-505f-8095-ed4d6ec3501a | note | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
ec1b08ad-fbac-502d-9619-727f500868c1 | note | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
a2d365fc-f241-5c0a-85fb-f723f4e45c4d | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11, AS/NZS 2566.2/2002
a6a599cc-7453-5fce-b0e4-5f5f582b90d1 | note | Verifying Document - Lab Test Report
6f307141-ff67-5a1b-b326-3cfb57d12570 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
e2677a2d-b7c9-5070-a4bc-9498788edbb7 | note | Verification Activity: Activity - H
9fbbf2a3-f31e-533d-be3c-a88504ca5168 | note | Verification Activity: By - SE
d824467f-f395-4d60-bb18-39202da292cb | checkpoint | 1.5.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
456117ec-526a-5acb-9c04-04505c7ed8bf | note | Detail - On Granular Material
71cbaeb2-f85d-51f8-805e-ef348fcd5b56 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
f6bff517-46ea-5b0f-91bf-63dcebe58bb9 | note | Standard / Specification - PS- 16.5.12
d0fe12d2-e82b-5c89-b16e-49dfdb76b0cf | note | Verifying Document - Lab Test Report
9a11e13b-0711-5f63-8bc9-7885945b841c | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
c41ccd72-3ab2-5de7-901f-6c716816cd48 | note | ○ 0-5m: 1 Tests
a69a76a3-ce97-5598-a58e-4ba970efe853 | note | ○ 0m-10m: 1 Tests
247a0ed3-c3dc-535c-93f7-a4491d7ae496 | note | ○ 0m-20m: 2 Tests
bc6a4c42-e2c3-5bea-ac1a-29daa8f3d3c3 | note | ○ 0m-50m: 4 Tests
3ae612af-6f82-501c-9486-3e08129d6f21 | note | ○ 0m-100m: 6 Test
14acd621-7ff5-582f-8fa0-75a4abd4cdbb | note | Verification Activity: Activity - H
a65a9578-faf0-51a5-9896-623c654b80b0 | note | Verification Activity: By - SE
9718a80a-5001-4764-a31d-45120910a2a0 | checkpoint | 1.5.4 - Bedding and Embedment Zone Compaction Testing (Polypropylene(civil boss)/Polyethylene Pipe).
8e941255-4a30-5dd6-bfde-8a74e8033298 | note | Detail - On Granular Material
a543fc8d-e18d-5ccf-874d-ce86b7f22b36 | note | Acceptance / Conformance Criteria - Bedding Zone:
0e40f8ef-b50a-592b-a63c-81ce89f360ad | note | ○ 100mm(for DN300 & DN375)
ad0f9091-69ee-52dc-a18b-59c1444a560a | note | ○ 150mm (for pipes greater than DN375)
c7a91e8a-b12f-518b-a823-9d80b8c8e88f | note | Embedment Zone:
fb1dc8aa-33f9-5671-b8ba-ec5b2e18f640 | note | ○ Pipe Dia ≤450 - 150mm GAP20/AP20 - Overlay
5644ec67-4fab-5cf3-9422-5df2cad58949 | note | ○ Pipe Dia 450< D ≤900 - 150mm GAP20/AP20 - Overlay
e14f2639-7490-5c8b-90c4-5da88a772183 | note | ○ Pipe Dia 900< D ≤4000 - 150mm GAP20/AP20 - Overlay
8c4b3f37-a138-5cfc-b419-9fa0b898f6fd | note | Minimum Compaction - Trafficable and Non-Trafficable 95% MDD on metal.
7c645d58-3fbd-5a4d-848f-6173f65da55c | note | Standard / Specification - PS- Table 21.7. PS- Table 21.12, AS/NZS 2566.2/2002
1e0a314c-d559-5b45-be17-16935aacf9ec | note | Verifying Document - Lab Test Report
8318e27d-7abb-52f0-aa95-784b8c93cb57 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole.
42c0682b-f1de-51f2-96af-1e7f0d9f103c | note | ○ 0-5m: 1 Tests
cbad12a8-c336-56ca-8dba-a090b934cfad | note | ○ 0m-10m: 1 Tests
47648d79-369a-5ba8-be0b-49c4d485e448 | note | ○ 0m-20m: 2 Tests
9ead80b9-8aa5-5113-9974-900a39812bf5 | note | ○ 0m-50m: 4 Tests
a4761450-d00c-53ae-87f4-d836fb515cab | note | ○ 0m-100m: 6 Test
ae313561-afb6-5e12-8501-8433f6064499 | note | Verification Activity: Activity - H
0585439d-af8d-50e8-9e75-31cc6ceefe2e | note | Verification Activity: By - SE
6a6d5cce-9102-4e60-91b5-48841b4a7a69 | checkpoint | 1.5.5 - Survey
1cd870a1-06d7-51b9-8817-3e63f8e2feb3 | note | Detail - Surveyor to Setout
70eafa9f-a639-5bcc-b430-9d599c1f23c4 | note | Acceptance / Conformance Criteria - Vertical design Setout:
c578fbc5-444d-5e06-9039-12f38ebd486f | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
38804002-e67d-50a0-8737-96bf122f1c32 | note | ○ Pipes > 1% grade: +/- 20mm variance
bd1a64ba-8351-5616-945c-bc6e55542f00 | note | Horizontal design Setout:
0a052d36-449d-51b0-84a3-cc396a21d5c6 | note | ○ +/-30mm variance
d59e00d5-46bc-54ba-9a29-3c635ef741e3 | note | Standard / Specification - PS- 21.7.6, Table 21.15
62c334ce-67a3-5223-be11-181fb4168741 | note | Verifying Document - Survey Data
dec7f80b-48b9-54f0-9896-988efa80ed3d | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
f4c53f68-ef8a-5991-9a1f-16e5fa089977 | note | Verification Activity: Activity - H
499691a4-cf9a-5b6d-93fb-e9d5d8efb2cb | note | Verification Activity: By - SV
beda0927-ed15-49f2-aad4-5a49fce0cc44 | checkpoint | 1.5.6 - Backfill Compaction Testing
0ece060a-c6a6-550f-ae6f-b0ca429237bd | note | Detail - On Granular or Cohesive Material
2cf4dae0-67a3-5511-b1be-74811fd560c3 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65
de437d89-1753-535d-914f-03849b7e2a94 | note | ○ Backfill Compacted in 200mm layers.
4ad80bc2-d7a9-5242-a2cc-572db4ff3764 | note | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
9a95282c-66cf-5ea2-9f74-fe077afdb482 | note | Standard / Specification - PS- 21.6.12, Appendix V
353489ea-d367-5283-a791-c8af10e28a8b | note | Verifying Document - Lab Test Report
0307a37c-ef56-53e6-bf8e-cca9a94c6eda | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole.
563d0b46-9651-55d1-abdb-50c20b52981a | note | ○ 0-5m: 1 Tests
76f0f0d6-5f0a-5d15-a1c4-cef9e9eaa12b | note | ○ 0m-10m: 1 Tests
fac98e3c-2d3f-5540-a0d9-c5ac68dbc872 | note | ○ 0m-20m: 2 Tests
009ae553-4784-513c-91d7-9c29c0aad035 | note | ○ 0m-50m: 4 Tests
2cea7500-b836-5cf6-bea0-df701b086a03 | note | ○ 0m-100m: 6 Test
7665f11e-0068-5e53-976a-60ac8f841a07 | note | Verification Activity: Activity - H
e4c705da-8fe0-5401-b7a2-395db72c9b30 | note | Verification Activity: By - SE
4a82f6f0-5fd6-41f7-ab5a-086e05d6066e | checkpoint | 1.5.7 - Pipe Inspection
adeefd12-12e8-5344-8556-02775b23de3d | note | Detail - Inspection of Drainage line
c4bdce43-e672-5aa7-b4e6-a2d0de74d584 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place.
a3ca49b5-61f6-55d6-9a65-9dfb76aad7c0 | note | ○ Check for gaps and/or defects and check pipe alignment for straightness
9870d81d-f277-5496-9f35-954c12d10209 | note | Standard / Specification - PS- 21.7.6
7de63379-c512-5bf2-81f5-e3c3c8d751f2 | note | Verifying Document - Drainage line record
60c2159e-17a8-5257-8af3-f28cd8717275 | note | Testing Quantity Required (based from schedule qtys) - Continuous, 1 per Line
215585ac-84e5-551f-8eec-d2bceadf1ea5 | note | Verification Activity: Activity - I
b6e5e62d-bf4b-5c54-9896-450424d69290 | note | Verification Activity: By - SE
5098333f-b1f2-4fb2-bdbd-bd6705741763 | checkpoint | 1.6.1 - Settlement Monitoring
9ab273f2-d0c2-5c59-860d-63096aa807fd | note | Detail - Settlement monitoring with installing the settlement plate at underpass foundation level and as described in PS 18.5.4 during the construction at various levels.
32c593fd-f4fd-5e6f-81cd-b31bc9b3df54 | note | Acceptance / Conformance Criteria - Settlement monitoring done regularly after completion of foundation, on completion of precast installation, on completion of cover fill, on completion of finish structure.
11147817-30a5-59fc-91a7-fef472bd7b5a | note | Standard / Specification - PS 18.5.4
83c0c449-1483-55a5-a279-c4236a036770 | note | Verifying Document - Installation of Settlement plates/Visual Inspection
05202b70-f054-52f5-9d36-293e902fd939 | note | Testing Quantity Required (based from schedule qtys) - as per construction sequence per PS 18.5.4
7554c2d7-e688-5be8-88e9-d7614ebfa08f | note | Verification Activity: Activity - I
52af0cfb-d5ad-5709-9658-e2ac78c8114f | note | Verification Activity: By - SE
7e7b0425-1cea-4d85-a51e-47aec741c801 | checkpoint | 1.6.2 - Placement of Geotextile
00e294f0-252b-5803-93cf-3ce1d395f81a | note | Detail - A layer of Class C Geotextile Fabric to be placed between cut surface and imported A1 Structural Fill with 500mm overlaps
6b4af9bc-7516-507d-9fb8-c7b0daa72025 | note | Acceptance / Conformance Criteria - Visual Inspection
297f8f30-128f-5fc3-8ee8-3d814f9f97ae | note | Standard / Specification - NTC084
708d07a7-f47b-54e2-a7c8-d95569d42957 | note | Verifying Document - Visual Observation
48a2b78c-544f-5da9-ab49-f5c001d04237 | note | Testing Quantity Required (based from schedule qtys) - As Required
0259cc79-c61e-5dc1-ac97-abe31230e87e | note | Verification Activity: Activity - I
6eb1bc75-4ca6-5812-9408-8f3ac7750361 | note | Verification Activity: By - SE
753bb261-4be3-45aa-ba40-5836cc15e71f | checkpoint | 1.6.3 - Compaction - Clegg Hammer for GAP65 & AP40
3407b06f-b7ec-5ce3-9ccb-91d68c726119 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
77f69b77-c171-54f6-ae71-1aef17c735bd | note | Acceptance / Conformance Criteria - Structural Fill
20fc8612-5f23-548a-88c5-c882ca737028 | note | ○ Min CIV 18
e2864c38-4608-5f29-aedc-9f2cc4ff0c87 | note | ○ Ave CIV 20
a6e77705-22a6-5bdf-bd5c-587b902deebf | note | Standard / Specification - Appendix XVIII
0f725119-6faf-54c5-8a94-d1ebc129d963 | note | Verifying Document - Clegg Hammer Report
6df0a4a4-1028-5927-9ff8-e58ecb7a594e | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
0675c4e1-b656-55b1-8444-235b03960aa4 | note | Verification Activity: Activity - I
7645cbe0-c842-5197-beb8-d6660992e759 | note | Verification Activity: By - SE
e88f547e-3776-4d3d-8204-cebbc1b5d70d | checkpoint | 1.6.4 - Placement of Geogrid
b2975911-af36-523e-a6a7-74596419e05d | note | Detail - The Durargid X 40/40 Geogrid shall be placed on top of the GAP65 layer and the first AP40 layer.
ed04be36-abf8-5259-9aec-3aa7bfef814d | note | Acceptance / Conformance Criteria - Visual inspection
be12496c-5d4d-53eb-921d-539f36ccfd78 | note | Standard / Specification - STR Drawings Sheet 203
2c563733-746e-567e-b267-921c59469b30 | note | Verifying Document - Visual Inspection
a7dfc397-9a7a-5291-a89d-b900c00cb754 | note | Testing Quantity Required (based from schedule qtys) - Across gravel raft
8bb6db61-b6a3-5e2e-909f-52f128bae1eb | note | Verification Activity: Activity - WP
5ba5a8c8-b230-5aa2-b560-7b00a3c0e34c | note | Verification Activity: By - ENG
09af1979-c0eb-4464-a1c5-d490d3ebf876 | checkpoint | 1.6.5 - Compaction - NDM on top AP40 layer
86eb0b4d-46c4-5cc0-a2dc-1761af70f049 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
4f119d60-fe61-5d87-94cd-8182a0e7a991 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
45701040-3a75-57e0-baf1-4a9542cbcee5 | note | ○ Min >92% of MDD
97a78d24-612c-5f07-bde2-59ab67752b28 | note | ○ Non Granular Material
08c34fad-8ea0-5087-88e2-ad9c21554a32 | note | ○ Max Air Voids 8%
7d3a2816-5482-52fd-9feb-c17a3a655e91 | note | Standard / Specification - Appendix XVIII
6a814472-c8cc-5cec-9b85-ef0d80e4b3c7 | note | Verifying Document - IANZ Accredited Report
06dd1acf-4757-5203-8cf6-0f3b5628701d | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) on last lift of AP40
4790c63b-148c-5515-8989-9053dcef6dff | note | Verification Activity: Activity - I
5be44172-93e4-502b-a97c-6a9ab138002d | note | Verification Activity: By - SE
d00539b7-a37e-4a54-86fc-99c174064fa8 | section | SECTION 2 – PRE-CONSTRUCTION - MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
98ac3291-8fcb-4b79-a303-a5f78034f153 | checkpoint | 2.1 - Reinforcing steel and Strands
6ee5e622-1e47-5aec-bfe1-908d6e21d166 | note | Detail - All Reinforcement bars and strands used in structural concrete to be approved by the engineer prior to construction.
8b079b6e-8507-579d-8bf2-a755f268ba16 | note | ○ Post tensioning strand to be high tension ASTM galvanized and complying with AS/NZ standard
2d69da43-7f09-5cb3-9809-1b421c23b305 | note | Acceptance / Conformance Criteria - Test certificates shall be obtained from the manufacturer for all strand, cable and bar to be used in the work and copies shall be forwarded to the Engineer at least one week before the programmed commencement of any work incorporating these materials. Test certificates shall be traceable to the batch of material supplied to the work.
8a2fd099-fe8f-53bf-b44a-d1695de6e219 | note | ○ High yield steel, Grade 500E, Seismic MA.
df4c4f93-d326-5469-8deb-23163b32cf3f | note | ○ Post tensioning strand to be high tension ASTM galvanized and complying with AS/NZ standard
b787fca1-167a-5db8-8f82-e7b44e5e96a7 | note | Standard / Specification - PS 18.3.3, 18.5.7 and 19.13.1
c1195fa5-e62a-53c1-b80b-cd2bb33668fc | note | Verifying Document - Supplier data sheet/ Mill certs
cad8bb9a-6298-5693-884b-728e8dab0575 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
7be52d19-6068-5b4e-a8d0-b5413a876870 | note | Verification Activity: Activity - HP
54577b7f-abee-52aa-adc7-6c4444ac6907 | note | Verification Activity: By - ENG
c930413a-f551-4011-841c-9e75a2884b0e | signoff | AUTHORITY HOLDPOINT
054664b9-4677-4549-87cc-8f7f88ea4038 | checkpoint | 2.2 - Concrete Spacer Blocks
40a291eb-2760-5b32-89f2-8f062ef5089f | note | Detail - Reinforcement cover spacer blocks shall be either made from concrete with a specified strength at least 10mPa stronger than the surrounding concrete; or Plastic spacer blocks.
7ae311f7-9c11-5f7a-aba3-46a0058cbd84 | note | Acceptance / Conformance Criteria - Concrete cover spacing blocks = at least 10mPa stronger than surrounding concrete.
f4292a3a-786b-5597-bfa3-539575c39e76 | note | Standard / Specification - PS 19.3.2
3d49c541-bff7-539f-9bcb-bbd73b622bde | note | Verifying Document - Supplier data sheet
f2270a73-7eed-5078-be2a-1d5d4ee78d91 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
0ead33a5-aae0-51f4-84b3-af4bf0dd8aab | note | Verification Activity: Activity - I
3a47b668-a67f-51d3-9820-75ea5b3f990c | note | Verification Activity: By - SE
6d19217b-ae81-4598-a21a-0d06112e60fd | checkpoint | 2.3 - Concrete mix design
2d9b1435-2e86-5496-8db4-81786a1c97ef | note | Detail - Approved mix design - Concrete shall be of the class as defined by NZS 3104 have a minimum 28 days compression strength as specified for various members: for underpass apron pour: 40mpa
c155e949-e408-5442-869a-fa6076b7a67d | note | Acceptance / Conformance Criteria - 28 Day concrete requirements: UNDERPASS APRON POUR: 40MPA
19e29b6d-60e4-55a5-93e7-93a0129dbd29 | note | Standard / Specification - PS 19.3.3
c3fd48a1-0ea1-59e2-bd1f-2c2b4b3a124f | note | Verifying Document - Approved Mix design
1776dea2-fe02-550f-b7af-acfebaec49f9 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
d4ecf044-8714-5243-a147-86e522207e77 | note | Verification Activity: Activity - HP
e6c009fc-538e-5bbd-8257-8dde660e675c | note | Verification Activity: By - ENG
af78300d-bc80-4bef-bd3c-eb3daf8d766a | signoff | AUTHORITY HOLDPOINT
112d5e6f-6a38-4b93-98c7-8fa5aa205502 | checkpoint | 2.4 - Shop Drawing Approval
28134cf2-3f94-5607-ae04-8972ca7e5f0a | note | Detail - Shop drawing review and approval from Engineer and Production QA Records to be submitted
5dd2acf6-c9fb-5aa6-adfb-3964a0af4d64 | note | Acceptance / Conformance Criteria - Send shop drawings to the Engineer for review, at least 14 days prior to manufacture. Any variations between the Drawings and shop drawings shall be clearly identified and brought to the attention of the Engineer.
52276d51-53b3-58c9-bff0-7c06447b4b0b | note | Standard / Specification - PS 19.12.6
c911f45f-e747-5235-ba32-499fc2340fe8 | note | Verifying Document - Shop Drawing Approval, QA records
ccacee30-b42f-59cf-bd71-a4b54e5ac82d | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
4c51dc64-cc6b-5e60-96a5-ff9166dfe6f3 | note | Verification Activity: Activity - HP
1e401908-a478-54cc-bf78-1437b6d84622 | note | Verification Activity: By - ENG
2f239c55-e127-40bb-983f-51ea9acb6428 | signoff | AUTHORITY HOLDPOINT
347fc3f6-5078-4d12-9b92-c160e23445f6 | checkpoint | 2.5 - Anti-graffiti products
c210295e-c36f-5044-a9a7-804652249d5c | note | Detail - Permanent (not sacrificial) anti-graffiti coatings shall be applied to the exposed faces of all concrete surfaces including wingwalls. The coatings shall have a design life of not less than 10 years. The Contractor shall submit the proposed extent of application for authorisation by the Engineer.
e8a85e98-fb32-5a55-8764-1bec862cb1be | note | Acceptance / Conformance Criteria - Permanent (not sacrificial) anti-graffiti coatings shall be applied to the exposed faces of all concrete surfaces including wingwalls. The coatings shall have a design life of not less than 10 years. The Contractor shall submit the proposed extent of application for authorisation by the Engineer.
65cbfd85-113d-5c05-a89e-696679902480 | note | Standard / Specification - PS 14.7.1
14a8414a-1f36-593f-95ca-4b2630562be2 | note | Verifying Document - Details of pre qualified product
9e4acfb1-9e70-5118-a277-4955791080a5 | note | Testing Quantity Required (based from schedule qtys) - Prior to Application - Engineers Approval
dee39587-1844-5b4d-b54b-e0ae387782ac | note | Verification Activity: Activity - HP
aa3b591e-5d75-5d97-be98-253a708bd6c2 | note | Verification Activity: By - ENG
eddb478f-fd43-45e0-bd2a-0ab7a4df6900 | signoff | AUTHORITY HOLDPOINT
de1219a8-7346-4686-86a3-93830b04b437 | checkpoint | 2.6 - Joint Sealing and Waterproofing Sealant
3b3406a4-fe7c-552b-a12b-0bb9029efe32 | note | Detail - Pre approved joint sealant meeting the specification requirements
babdf75a-97d4-50ad-b6c3-dc60194d4a02 | note | Acceptance / Conformance Criteria - Joints are to be sealed using a fuel resistant, multi-component polysulphide sealant designed for horizontal and vertical joints in concrete and is joint sealant pourable or gunning grade as appropriate.
5e7e3c69-0ce5-5fb4-8bdb-f976a5d88e98 | note | Standard / Specification - PS 19.12.6
da0d4644-d3e1-5f65-94aa-eef6020bd4b6 | note | Verifying Document - Delivery dockets and supplier data sheet
aaa11a3e-e381-5e2b-90d5-dd0215db4fca | note | Testing Quantity Required (based from schedule qtys) - Prior to construction - Engineers approval
b3201498-86d2-5b0f-a925-af184133c362 | note | Verification Activity: Activity - HP
0efdf45a-058d-5193-bf43-506ab8082958 | note | Verification Activity: By - ENG
2dd7e97d-5551-4ebc-94a6-150f91f7c794 | signoff | AUTHORITY HOLDPOINT
3a6fea7d-6e89-4f82-90e7-5898dd0f59c8 | checkpoint | 2.7 - Compressible filler board
cd6241a8-a7bc-50db-82c4-8911efbd19ce | note | Detail - Compressible filler board specification to meet the project requirements.
93f534c0-5787-5cef-9c3c-9eb4e653eb26 | note | Acceptance / Conformance Criteria - Details of the compressible filler board proposed to be used as a construction joint shall meet specification requirements.
d55176a6-0b21-55b5-ba57-50ccce15cd7e | note | Standard / Specification - PS 19.12.6
0b18717e-65d9-5900-b9e2-2b03041de7e9 | note | Verifying Document - Delivery dockets and supplier data sheet
768a2b11-128d-5af9-babb-c4d2a1b63b76 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6550a22e-67ad-59b0-8d52-c00f68d041c1 | note | Verification Activity: Activity - I
7d266dc1-f48e-507e-905e-e70b4299ec11 | note | Verification Activity: By - SE
2697b654-750c-4ff8-aa49-4f6626ff73ba | checkpoint | 2.8 - Application of Non-Slip Coating - Sikafloor 91 or Sikafloor150
28b71e12-8a73-5ee8-81c0-43e983b63249 | note | Detail - Proposed product to be approved by Engineer
741009c7-be12-59a0-9e15-2d8fe1278e3f | note | Acceptance / Conformance Criteria - The top of the underpass floor slab and bottom chamfers will have Sikafloor 91 or Sikafloor 150 applied after the installation of the box culvert segments. The thickness of this is to be between 3 and 5mm. The application of the product must be done in accordance with the manufacturer’s specifications.
9adbff8c-ab5b-53b5-8ced-b217bc2e5317 | note | Standard / Specification - PS 19.2.4
a0406e4f-e678-5eb4-aba9-e485a35f3307 | note | Verifying Document - Product data sheet
ed52e13a-496a-573e-9c0b-0dd3604a6802 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
3f6448ae-b28a-5a5c-aa54-daf731b65f13 | note | Verification Activity: Activity - HP
8fa51e85-e480-5fd4-91a9-b0c57e94ba14 | note | Verification Activity: By - ENG
cb56397e-bbd9-4f9a-a88f-e2763b64fda0 | signoff | AUTHORITY HOLDPOINT
ef3bd09a-5ad5-491b-b32b-eafa8dea5b3f | section | SECTION 3 – CONSTRUCTION ACTIVITIES - BLINDING AND PRE-CAST POUR
743821ff-023a-4216-96c8-0465bcf4c605 | checkpoint | 3.1.1 - Setting out of Underpass Blinding level with 1% fall towards Northern end
da107dbd-ebc6-548e-bdce-ab234bbbba1c | note | Detail - Setting out boxing and complete site checks as concrete is poured to ensure flat surface for placing precast units
8991ec2a-175c-573b-9022-788568cb84ea | note | Acceptance / Conformance Criteria - Site supervisor verification
f4d5ef9a-b56c-59f3-b19d-8957e8abf1e4 | note | Standard / Specification - PS 18.5.3
601aab22-e044-5f64-967c-750de51dbfe0 | note | Verifying Document - Visual inspection
b3fdecdd-20fc-5492-a180-5accd09136c1 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
7a07d5f2-753f-524c-a259-c02af50dfdad | note | Verification Activity: Activity - I
972f6d69-24d8-507b-aa62-0a0486ab05cc | note | Verification Activity: By - ENG
bb27ef25-7e0a-4f33-aa0b-5b3fa71eb456 | checkpoint | 3.1.2 - Blinding Concrete
566e16dd-4b63-5501-9555-df90b7526c52 | note | Detail - Concrete Compressive Strength on 28 days to gain min of 10MPa
07aa5203-90f3-5bb0-a29a-eb347cc827ab | note | Acceptance / Conformance Criteria - Blinding concrete shall have a minimum 28 days compressive strength of 10 Mpa and comply with the requirements for prescribed mix concrete specified by NZS 3104
c1ff74e2-1afb-5816-8cc4-e001cd452b7e | note | Standard / Specification - PS 19.3.3
62fa7ccf-e9fd-5a0e-80be-9b8ad7c1cc74 | note | Verifying Document - Concrete Delivery Docket
31fda7e1-0ba5-5e3b-b01f-c93a69a86fac | note | Testing Quantity Required (based from schedule qtys) - During construction
4fbac7e9-eed8-5404-b5f8-fbe847e41803 | note | Verification Activity: Activity - I
f49fd7d8-a07a-572f-94db-1b2498e04b1d | note | Verification Activity: By - SE
c04c514d-9fb7-4444-aaa0-39ad4a3daad1 | checkpoint | 3.1.3 - Setting out of positions of the Underpass units
8b2bb112-121b-5c1a-aaed-64fe529a0e91 | note | Detail - Setting out to follow design coordinates and levels within tolerance as specified in PS 18.5.3 by approved licensed surveyor to certify the Set-Out positions.
aca4d159-3362-5644-a4bb-b21523482828 | note | Acceptance / Conformance Criteria - Engineers Approval
102cfe0d-fa65-5311-98b0-51bcdd33df81 | note | Standard / Specification - PS 18.5.3
ef75cc33-167a-5733-9f52-997c0a792375 | note | Verifying Document - Visual inspection
51bc48ac-bf65-5b39-a90f-a06b5e0b1603 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
6902b5a7-357a-5b04-88e4-540c8c52884b | note | Verification Activity: Activity - I
5fd546ca-d84b-572e-8d8f-e5b3aec6abba | note | Verification Activity: By - ENG
7d8cdb34-b9f8-4d3d-8620-0ff7caad10b2 | checkpoint | 3.2.1 - Forms and Moulds
11c8e98b-9a53-5ecf-aea6-9f7da49169ce | note | Detail - Tolerance on the placement of internal forms and moulds shall be +-5mm
33073ce1-2331-590f-be72-877f30a53e4e | note | Acceptance / Conformance Criteria - Moulds shall be rigid accurately formed and of sufficient strength and stiffness to prevent distortion under vibration.
0d4cebc9-9b7e-5516-b4d6-0064d688071d | note | Standard / Specification - PS 19.12.5
705f1538-5abe-52d9-9225-b9fe46afc3f3 | note | Verifying Document - Manufacturer QA records
e467ac5f-ffd3-56db-8620-e8243e0e7467 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
a71aed16-8a76-55c5-92f5-0079d755e766 | note | Verification Activity: Activity - I
e3b9a82d-6972-5407-b7c7-546b8661f899 | note | Verification Activity: By - SE
76d2c678-26cd-4103-95c6-7d5639b68f38 | checkpoint | 3.2.2 - Pre Pour Inspection
a4c4b271-3bd6-5fe1-86ac-129b80d950ce | note | Detail - Pre Pour inspection to check:
409e4cea-c55e-55e4-a987-ca3c28794195 | note | – Reinforcing
bbfe4b89-b369-5465-8852-89885a2c4ef9 | note | – Moulds
ec274a89-ad2d-5507-83ca-56a47c0b3562 | note | – Cover Spacer Blocks
16efd87b-5b2c-5d7e-97cf-89f1276abd2f | note | Acceptance / Conformance Criteria - The Engineer shall be informed 8 hours prior to the casting of any unit, to allow the Engineer to attend the pre-casting plant to inspect before and during production of the units.
46f51f83-86de-5e90-a2e4-8d2858148dfc | note | ○ Reinforcing shall be pre assembled wherever possible into rigid cages using a template or jig. Reinforcing shall be tied together with wire unless otherwise accepted by the Engineer
380ea89e-831d-52b9-a9a1-57563c7799c9 | note | ○ Confirm correct type and location of cover block is used.
8bae5121-0038-54a0-b70e-67dd06e95772 | note | Standard / Specification - PS 19.3.2, 19.4.3 & 19.12.3
51162623-9a26-5e86-bfe9-db9eba5940e3 | note | Verifying Document - Pre pour inspection checklist, Manufacturer QA records
d0417c94-c97b-50c6-a501-32e74feda823 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
4b1a5982-bc2f-5763-a1ed-32bf66e7c059 | note | Verification Activity: Activity - HP
e64ca039-8c89-50c9-886b-4d8a567911fe | note | Verification Activity: By - ENG
fb5b8559-ed9a-4c02-bfbd-b666f62c1ac9 | signoff | AUTHORITY HOLDPOINT
f542d24b-d3ea-4c94-b99a-05c42215516f | checkpoint | 3.2.3 - Concrete sampling and testing
36aaa947-c97c-593a-a4fc-2e27217c206a | note | Detail - Pre cast Methodology from Pre co to submit to Engineer and Compression Test Report
469273a4-dee2-5800-82ed-7314a28f71ec | note | Acceptance / Conformance Criteria - For pours under 150m³: three standard cylinders shall be made for each 50m³ of concrete placed, or part thereof, for testing of 28 days compressive strength in an approved laboratory.
091e3fab-a089-58f7-b22b-8d814723378f | note | ○ For repetitive precast underpass units with 6.42m3 each pours undertaken on a regular basis, three standard cylinders shall be made for each of the first five pours of any one type, and thereafter three standard cylinders shall be made for every fifth pour of that type for testing of 28 days compressive strength in an approved laboratory.
62f7f6c2-a59a-526c-b063-c6b862cb46e0 | note | Standard / Specification - PS 19.4.3
6f46bbda-91f6-5ef1-be30-0d715d7e3d07 | note | Verifying Document - Slump Test/ Compressive strength test Report at 28 days/Pre pour inspection checklist
89bc52a1-495e-5f19-a18f-93453754ecc9 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
9f958ada-543d-53f1-879f-98808994175d | note | Verification Activity: Activity - HP
657f490e-85d8-5b07-8eb6-f0557b0595aa | note | Verification Activity: By - ENG
c700d85c-6232-4e9b-8bc1-19ede21ec0c5 | signoff | AUTHORITY HOLDPOINT
b2aea290-4700-4434-9e95-80fba8abc8e9 | checkpoint | 3.2.4 - Surface Finish of pre cast concrete Units
8f8b150d-e826-5d52-a573-8f5ffccb08ee | note | Detail - Surface finish to comply the requirements for pre cast concrete units.
0cf1de62-1c3e-571f-b892-4879defbcdbc | note | Acceptance / Conformance Criteria - For all precast concrete units all surfaces except those against which concrete will be subsequently placed, shall have a concrete surface finish complying with the requirements of NZS 3114, F4 finish for formed surfaces and U3 finish for unformed surfaces.
8efac5ed-e8c8-5945-b78b-64ce498b476d | note | Standard / Specification - PS 19.7.1
02eccc6f-a59d-5c63-a6bc-90aee7aa8b43 | note | Verifying Document - Visual Inspection
51237cd1-2d26-532b-84d9-33326dae53b8 | note | Testing Quantity Required (based from schedule qtys) - Each Item
f028b363-a603-57c0-bdc8-d7c998cbc8e5 | note | Verification Activity: Activity - I
49da067e-58f9-541e-9684-761267356be6 | note | Verification Activity: By - SE
ef9a936b-49b4-4283-8526-0d5b481d9ee1 | checkpoint | 3.3.1 - Post Pour inspections
3af22d0c-fd8d-5794-b861-a20191bc0a06 | note | Detail - Post Pour inspection
80ee11aa-abbd-5a5c-9974-033520bc6bc8 | note | Acceptance / Conformance Criteria - Following the concrete pour and stripping out form works: the concrete shall be inspected for Size, Shape, Features, inserts, reliefs, and Finish against the drawings.
a55727af-a0f2-513f-954f-996dfb62bf79 | note | Standard / Specification - PS 19.3.1
205d056b-583b-591e-b215-6ed717f32959 | note | Verifying Document - Visual Inspection/Post pour checklist
6c865795-6974-52e0-a1e4-5e6859f79a4a | note | Testing Quantity Required (based from schedule qtys) - Each Pour
2ab43b02-f61b-5091-a8dc-c50b224e8a65 | note | Verification Activity: Activity - HP
8fadb844-0327-5704-919d-831f77c37a11 | note | Verification Activity: By - ENG
26a55d1e-79d5-4d2a-875c-f0aa45d141f1 | signoff | AUTHORITY HOLDPOINT
ab880dad-4e87-48d0-bb94-48b3dc48b874 | checkpoint | 3.3.2 - Defective Concrete Finishes
901f00d6-f99d-5fd4-a30f-278c0de647fd | note | Detail - Repair of defective concrete finish other than that due to minor porosity of the surface shall be carried out only when approved by the Engineer.
88d8dfd8-67b4-5d27-b087-5af5dd2280a9 | note | Acceptance / Conformance Criteria - Repair of defective concrete finish other than that due to minor porosity of the surface shall be carried out only when approved by the Engineer.
7d93d3eb-172e-52c5-ad9f-ac0d075a138c | note | Standard / Specification - PS 19.3.1
abe0ce5a-6fbb-5e6d-9fd0-7573c58cc427 | note | Verifying Document - Visual Inspection/ Post pour checklist
64938b64-e8a3-5194-a13a-5bd373df6903 | note | Testing Quantity Required (based from schedule qtys) - All Concrete Elements
a0f6c396-5a1d-5488-9f5b-ebd7f5ed45fe | note | Verification Activity: Activity - HP
f6ec05d6-5373-5bcc-9aff-16259a71f1ff | note | Verification Activity: By - ENG
a7f61ff1-9c2e-4b05-bede-ee9a714b2a42 | signoff | AUTHORITY HOLDPOINT
8c5eb30a-6314-46c5-9c85-1f6bfc4d2bed | checkpoint | 3.3.3 - Joint Sealing of Pre cast members
1aefbf62-b47a-50cc-b9f8-0edcfa1cbda8 | note | Detail - Joint sealing of pre cast members
76b3906f-be09-57bf-a11c-9d910a743cd5 | note | Acceptance / Conformance Criteria - Joints are to be sealed using a fuel resistant, multi-component polysulphide sealant designed for horizontal and vertical joints in concrete and is joint sealant pourable or gunning grade as appropriate.
bc6ad653-9b56-5a4f-a3f5-b8cdbb5a4c1e | note | Standard / Specification - PS 19.12.6
ec666cfd-8d31-545f-887d-32cd7d8fb27d | note | Verifying Document - Post installation inspection check list
57bec8fa-b74c-5853-a2db-1fa4e5f13504 | note | Testing Quantity Required (based from schedule qtys) - After placing pre-cast units
c92aa63b-aeec-5dd6-9861-b58db6f729a7 | note | Verification Activity: Activity - I
a5f3a0ed-35b7-55c9-8b40-17275e59ee88 | note | Verification Activity: By - SE
c547d492-7791-4678-b19a-9c2e897d1999 | section | SECTION 4– CONSTRUCTION ACTIVITY- POST TENSIONING OF UNDERPASS UNITS
4b3e96cc-b7cd-4059-b926-e9de5444999f | checkpoint | 4.1.1 - Detail methodology for Post Tensioning of Stage 1 of underpass units to develop and send to designer for approval
b6532d1f-31ac-5f80-8b27-5c02ec716b46 | note | Detail - Detail method of stressing
31c8e749-af8d-51b2-bd20-9ef4cbd19dd4 | note | Acceptance / Conformance Criteria - 1*15.2 Galvanized, greased and sheathed strand per corner (Ungrouted) to be inserted in each corner for stage 1, 16 units of underpass.
72be10b5-b9f6-58a9-9e25-d0968ba269f6 | note | ○ Both ends will have a 40mm rebate for grouting.
ff81736b-92f6-50f5-ab2f-77d338b7daa9 | note | ○ And those strands will be tensioned to meet the project specification.
3e3855a8-973f-58b4-9f9c-bf406378fd6a | note | Standard / Specification - PS 19.14.1
6120e120-c076-5557-8c98-263e865ec928 | note | Verifying Document - Method Statement
50856ec0-211d-56c9-beb7-ff56ab87eb75 | note | Testing Quantity Required (based from schedule qtys) - Before installing units
d1450bba-53c3-556a-9b73-a98abdbf4940 | note | Verification Activity: Activity - HP
340e5539-766a-5640-a815-200e433c4221 | note | Verification Activity: By - SE
99af2022-6107-4b9b-93e2-882ac41c9512 | signoff | AUTHORITY HOLDPOINT
91e514be-2f6d-40d1-8952-ad778e899a4a | checkpoint | 4.1.2 - Detensioning of stage1 underpass units for Stage 2 construction
27868745-3f1f-5854-b3cb-d77d03b4b1ef | note | Detail - Detail method of stressing
a75d5579-b6f2-55e8-8d0e-fdebfcd046a5 | note | Acceptance / Conformance Criteria - Detensioning will be done on one corner at a time, remove wedges via special pocket pull new strand and tension.
e11626ae-7955-55b5-9cc0-80430dc8bb71 | note | ○ This will ensure at least 3 corners remain under tension at any given time.
ddc48088-4995-5eb6-90ac-53f6d8f77fc5 | note | Standard / Specification - PS 19.14.1
85900feb-bcec-5a7d-a8de-495a8aa820e1 | note | Verifying Document - Method Statement
05db36fc-1143-5d4a-ba92-32eca6df128b | note | Testing Quantity Required (based from schedule qtys) - Before landing stage 2 units
953591ce-2dfb-598c-bfec-c1ec9c6569c6 | note | Verification Activity: Activity - HP
fef0c05c-f23a-545c-b2b5-23d090154eee | note | Verification Activity: By - SE
f071a83d-4bae-4420-99b8-adf4912bdf6c | signoff | AUTHORITY HOLDPOINT
c9acdfb6-da11-480c-9718-28d50b055f41 | checkpoint | 4.1.3 - Stressing Operation
bab6b2c6-7a6e-5b0b-97d2-a0d1519bc99e | note | Detail - Post tensioning of strand to be done not to exceed 80% of maximum ultimate breaking strength. Post tensioning strands to be stressed simultaneously or following the sequence of stressing as noted on shop drawings.
788e0d38-a00e-5b00-ae34-687325d9db78 | note | Acceptance / Conformance Criteria - Stressing forces shall be as per NZS 3101 section 19 for maximum permissible levels of force within a strand during and after stressing. In no case shall a strand be stressed to greater than 80% of its ultimate breaking strength.
9643bbce-20aa-5e48-9b31-343803549e3a | note | Standard / Specification - NZS3101 Section 19 PS 19.14.1
210d969f-8019-5d03-877e-d947873ca451 | note | Verifying Document - Method Statement
1fbfe15a-19d5-52d2-980e-a17d1bb48aaf | note | Testing Quantity Required (based from schedule qtys) - All units for tensioning
cf72f6d7-17ba-56fd-8f0d-6dbe62890225 | note | Verification Activity: Activity - HP
678bf252-cb56-5a1a-952a-81efd10ab685 | note | Verification Activity: By - SE
602d350f-6d14-4cfa-be7c-4f7a01a7fb0b | signoff | AUTHORITY HOLDPOINT
391cc4d0-27f2-4f28-80be-93b70840dea9 | checkpoint | 4.1.4 - Concrete Strength at time of stressing
49e1119f-0cb0-54f1-9ae5-457c104dd442 | note | Detail - Samples taken during construction of concrete member to be tested for compressive strength and the results shall be used to determine the acceptability of the structural member for stressing.
b6ce2c3a-a12d-56f0-8a6b-13eb92b1da43 | note | Acceptance / Conformance Criteria - The minimum compressive strength required before stressing shall be 30MPa unless noted otherwise on the drawings.
8400ef00-3c23-5fad-9eb0-e2a34536470f | note | Standard / Specification - PS 19.14.1
bba88764-998c-532e-a36a-84317772f629 | note | Verifying Document - Concrete Test Reports
dd934fd1-adcf-5c02-8401-5176969b7f8b | note | Testing Quantity Required (based from schedule qtys) - as per test report in section 2.2.2
159f1885-3efe-51bf-9277-de4b54028d92 | note | Verification Activity: Activity - HP
6a4331a0-8f57-5276-94f0-feb9bdc73488 | note | Verification Activity: By - SE
c4240516-9180-4a35-af5b-5548fb73fb21 | signoff | AUTHORITY HOLDPOINT
271c0361-0225-4204-9952-09fef53e8b3f | checkpoint | 4.1.5 - Stressing Calculations
ec01499d-cbd5-5a4e-97eb-f7783c83b0b4 | note | Detail - Calculation done will form the basis of comparison to the actual stressing results recorded as an indication that the appropriate levels of stressing are being achieved in each strand.
8af9c0ec-8220-5041-9ce7-c183c533ae8a | note | Acceptance / Conformance Criteria - Theoretical calculations for each strand size and profile to determine theoretical jacking forces and corresponding theoretical elongations.
9b9a6c76-d37c-5dbe-8bd4-05dbb108bd04 | note | ○ These calculations shall be based on the assumed property of strand and forwarded to the Engineer for review and approval at least 7 working days prior to the stressing operations commencing.
bbf19dbf-e342-5604-9cf9-49de8ce94589 | note | Standard / Specification - PS 19.14.1
03208da9-adc2-5af1-a505-80cc95d7a659 | note | Verifying Document - Calculation data sheet
29d15933-8fb1-51e6-92c3-28db7df794d1 | note | Testing Quantity Required (based from schedule qtys) - All units for tensioning
63883fdd-295b-598f-876d-427dc85f8fc7 | note | Verification Activity: Activity - HP
9712cb12-53a1-5803-8144-2966f82f403d | note | Verification Activity: By - SE
53e183f5-5ceb-486d-916f-dcbf44e8ca36 | signoff | AUTHORITY HOLDPOINT
e4504edc-9c9f-4828-9cd0-f0e3852bf700 | checkpoint | 4.1.6 - Protection of Strands
a08f0595-5198-5794-9aa4-1756acd2d54e | note | Detail - Post tensioning strands shall be cut flush with the end faces of the pre cast unit (including any recess) unless noted otherwise on the drawings. Gas cutting of Strand is not permitted.
6f5745eb-927a-5143-9467-fe01acb6c4bd | note | Acceptance / Conformance Criteria - Cut ends of the strand sealed and protected with minimum of 5mm of epoxy mortar or a coat of high build epoxy paint.
b3e238f2-1dd7-5583-9333-cf58fdc9837e | note | Standard / Specification - PS 19.14.1
51ae7e2b-59c8-5496-ab86-dc73312001a9 | note | Verifying Document - Visual Inspection
eeb1c7b1-4010-5db5-ae5d-d520150e3bbd | note | Testing Quantity Required (based from schedule qtys) - All units with Strands
08b3f00f-6069-5ad6-8465-0a95a619aff5 | note | Verification Activity: Activity - I
1127bf7c-48a2-5c53-9252-c469717f64f5 | note | Verification Activity: By - SE
05f94978-8045-42cc-8184-b35f662547dc | checkpoint | 4.1.7 - Stressing Records
46da9cc4-f658-5e81-b422-9cda4c00f056 | note | Detail - Record of stressing shall be taken and reported to designer.
b7f1efc3-22de-5a5b-90c8-5a333ce51ba9 | note | Acceptance / Conformance Criteria - Stressing record as per PS 19.14.1 section IV, subsection I
baa29a25-c972-531f-9951-dab01df2ced6 | note | Standard / Specification - PS 19.14.1
fae6a2f1-b6fe-5199-b072-886c99a8d8ce | note | Verifying Document - Stressing records
c92109ae-44cf-5377-a5d5-cb32e2f87e36 | note | Testing Quantity Required (based from schedule qtys) - All units with Strands
3391ef56-9f28-5847-a914-200fbc8a9495 | note | Verification Activity: Activity - I
6717b9df-aaf7-5864-8142-29783163d0db | note | Verification Activity: By - SE
0c20247a-43fe-4d64-b29d-159a375fb0f8 | section | SECTION 5 – CONSTRUCTION ACTIVITY- UNDERPASS WINGWALL, DUCTING AND BACKFILL
2d8dbf3a-79ed-472c-bc86-6e0bdea01edc | checkpoint | 5.1.1 - Position Monitoring
9d4d376f-5792-591e-b049-dd2fea75b27b | note | Detail - Surveying to be done on the primary structural elements as their construction is completed, location of base slab, strip footing, roof of slab, top of wing walls
850ce3ff-078b-5249-a668-450b4fbd0b60 | note | Acceptance / Conformance Criteria - Surveying done as per PS 18.5.4 on various stages of the construction of underpass. Position of underpass as built and recorded
56ad3c4f-d78d-51a9-b723-ebfdcff2f3e0 | note | Standard / Specification - PS 18.5.4
e2498386-238d-5033-998e-2c72b1e4d2de | note | Verifying Document - Survey recording of position to the required tolerances
83cbee7f-e309-5f3f-81b4-51162fda9eda | note | Testing Quantity Required (based from schedule qtys) - When each construction step finishes
5049c4c8-db9a-57ff-978f-bf4b5ad223da | note | Verification Activity: Activity - I
345e81f4-4809-5ec6-a67c-92d0b3d1ca4a | note | Verification Activity: By - SE
d117ffb8-9fe4-4428-8b13-db3b74ec10ec | checkpoint | 5.1.2 - Placement of Geotextile on Cut Surface
4f4e44ed-e792-593e-9326-d974ef4e3f00 | note | Detail - Geotextile to be placed up the sides of the cut surface, with joints overlapped by 500mm minimum
9ace3f27-f864-55c4-9bb9-5773e6220ec5 | note | Acceptance / Conformance Criteria - Engineers Approval
4c17289c-f0cb-5897-a32d-e8b4c3ab3e74 | note | Standard / Specification - PS 16.6.4, TNZ F/7: 2003 8.3
d4f496bb-12a3-5c84-8414-7375ca46fbb9 | note | Verifying Document - Visual Inspection
21346a48-1f98-5ae7-9583-2cdb6faea446 | note | Testing Quantity Required (based from schedule qtys) - Across undercut area
428515bc-0aa7-50f3-807b-b2df2144e9ca | note | Verification Activity: Activity - WP
8c52ebfc-5481-5105-a10f-133ceb95be38 | note | Verification Activity: By - ENG
4720299d-b74f-4bb7-95b6-92251043ffcf | checkpoint | 5.2.1 - Trench Excavation
12c458e6-5f63-56ac-98bd-1ea4a381545e | note | Detail - To be excavated to within a tolerance.
d6b0c441-49d1-5e49-a668-1015283d1965 | note | ○ Not more than 100 metres of trench associated with each site shall remain open at one time.
48798956-ffbe-5d4d-aa81-9596837d4532 | note | Acceptance / Conformance Criteria - +/- 100 mm of the planned horizontal.
da97c883-6c14-5db0-8a47-d2b5436b9cdd | note | ○ The maximum deviation shall be 1 in 20 in both the horizontal and vertical planes.
46eba14b-2c80-5fa0-a95b-2d9ba3e13370 | note | ○ Less than 100m
2839ef16-3858-5a27-b09e-cab445652ccf | note | Standard / Specification - PS 25.13.2 (Ai)
144f0dd6-6007-5621-bf4c-120d7625af77 | note | Verifying Document - Survey
cec979cd-1ae7-5d59-8fc9-4695e685adf0 | note | Testing Quantity Required (based from schedule qtys) - Every time
5098021c-e984-5930-be44-86e807c87eaf | note | Verification Activity: Activity - M
dc15560d-331e-5ed7-8d8e-514c95d54a5f | note | Verification Activity: By - SE
e315953f-7b5d-4c1c-ab61-383fa6dbff35 | checkpoint | 5.2.2 - Unsuitable Materials
4f96230f-e13e-5d8f-b920-f9da3b18fa02 | note | Detail - All confirmed unsuitable material shall be excavated down to suitable materials.
05b52d11-98e8-52a4-a694-738665227dec | note | Acceptance / Conformance Criteria - Dig Down to Get Suitable Materials or get Engineers Approval.
91175973-14d5-579d-9d61-9e9ceaa8ce2f | note | Standard / Specification - PS 25.13.2 (Bii)
b6f70c2a-efd9-5860-8f00-1206353078f2 | note | Verifying Document - Visual
5564928f-982e-571a-9529-57a92c686cfc | note | Testing Quantity Required (based from schedule qtys) - Every time
8487ae28-63f0-5cf1-9879-edd30a057da3 | note | Verification Activity: Activity - M
cd25888b-2dc8-5171-be25-266080ac2099 | note | Verification Activity: By - SE
81842a5e-f487-4f07-ba95-6be359c05238 | checkpoint | 5.2.3 - Foundation Compliance
edda29b8-b2fc-57a6-8a85-bf43e36d6bdd | note | Detail - It shall be de-watered prior to installation of bedding material.
e9866990-8b9a-56d1-9080-b4230571bf71 | note | ○ If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
8a7d25f8-d8cf-5df3-a483-13a8400420fc | note | Acceptance / Conformance Criteria - Witness.
6bc9084e-9654-5865-bec9-c2ed77b57959 | note | ○ 50mm granular layer shall be laid and compacted before the bedding layer is laid.
95045a1e-ef57-5048-8910-689600548db5 | note | Standard / Specification - PS 25.13.2 (G)
6d9996d7-c96c-5252-a985-e280837b74b0 | note | Verifying Document - Visual Inspection
fc91a45d-7439-566b-abc8-b7cdbb339770 | note | Testing Quantity Required (based from schedule qtys) - Every time
366c7612-dbb3-55ac-b6fd-3b12bb9eff54 | note | Verification Activity: Activity - M
ab4d3980-6849-530e-9e98-9529ceed4b4a | note | Verification Activity: By - SE
953f1403-f2fd-4a09-973f-d623ad462f96 | checkpoint | 5.2.4 - Bedding
00c1cc82-a2bc-52e9-977a-59995f5aa69a | note | Detail - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
3939bf03-a99f-5063-aff7-28d7d4e872ae | note | Acceptance / Conformance Criteria - Mixed Dust to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
d3ef4cba-c403-56ee-b225-e728640456c9 | note | Standard / Specification - PS 25.13.2 (g) Modified by Engineer WSP
e2d5321b-3d6d-59b9-947e-e9f30be4599b | note | Verifying Document - Visual Inspection
47601345-8dfc-5f03-800e-570381e2cadd | note | Testing Quantity Required (based from schedule qtys) - Every time
7d9fd81b-a996-524d-93b7-ac725a72123d | note | Verification Activity: Activity - M
88ea430f-d416-510e-be3a-45bd0d7bb64d | note | Verification Activity: By - SE
19d03263-3bc6-45fa-9bea-c7009d7e74d6 | checkpoint | 5.2.5 - Bedding (Enchased in concrete)
0125ab28-16bb-566a-a07f-135b7caf881e | note | Detail - Concrete Bedding to be placed. Compressive strength of concrete used no less than 20MPa
f291dfaa-02fe-57d1-b9f3-90657629f6ed | note | Acceptance / Conformance Criteria - 50mm
9663a4f8-540c-5f8b-99bb-4ee1aacc7e65 | note | Standard / Specification - PS 25.13.7 c)
893a2c45-af46-5d29-9f9b-98ee86d2d055 | note | Verifying Document - Visual Inspection
af8fc72c-6d1b-5c7f-b8d3-f3e35bdd8cc7 | note | Testing Quantity Required (based from schedule qtys) - Every time
f0fbc2ab-acdd-51c4-b6b8-29a2adb85cb4 | note | Verification Activity: Activity - M
0071623d-f263-5101-a102-7ad9d8aa7532 | note | Verification Activity: By - SE
3510d5a0-994b-482a-b4c3-19150811d7a7 | checkpoint | 5.2.6 - Installation of Ducts
bdf1b4ec-5a9a-524f-aa87-7a101a7f9071 | note | Detail - If more than 2 ducts are being placed.
0252a6ca-25cf-5998-800c-4443e38d6b26 | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
9aaa6cf3-e61f-5847-bd32-afb89c900ee8 | note | Standard / Specification - PS 25.13.7 (B3)
c405d751-c1d6-5a5c-b6d8-85f14c167dcf | note | Verifying Document - Visual Inspection
913055fb-8e2e-5e4b-9ed7-1316c4bd589c | note | Testing Quantity Required (based from schedule qtys) - Every time
3ce5d948-1fae-5973-949a-5a71a7116ce9 | note | Verification Activity: Activity - M
8e3fa9e1-c440-5fca-ab81-50fd398d4638 | note | Verification Activity: By - SE
3ada663c-3179-4e56-bc4f-996a8d82e034 | checkpoint | 5.2.7 - Warning Tape
eed58be1-4b6a-535b-a9f2-32954920a2c3 | note | Detail - Warning tape to be placed above services.
a4c5f7ac-68e1-5cd9-bd7c-62bccc87981d | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the duct
e07291d4-b2f8-5f84-9da7-620a5a54ae39 | note | Standard / Specification - PS 25.13.7 b) iii & f)
23094f91-2eb3-51c8-93ee-c14e4f6cecb7 | note | Verifying Document - Visual Inspection
e1b8a1f0-a497-590d-9885-cecced8fe883 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
ff8defd8-884c-5ed2-8609-c48585e6c5bd | note | Verification Activity: Activity - M
12ceb7d7-2e54-5700-9c83-f07a69aef06c | note | Verification Activity: By - SE
f288613d-4b12-46cb-8a24-c1837ca78f76 | checkpoint | 5.2.8 - Overlay
1bedc859-16e1-5bd3-95ab-6cbe43269280 | note | Detail - Mixed Dust to be placed and compacted
79496bd8-0294-55ca-86b6-50dc7493355d | note | Acceptance / Conformance Criteria - 100mm thick mixed dust
29f9711e-18d1-5b57-b0e8-4a3f2cecc027 | note | Standard / Specification - PS 25.13.7 b) ii
9f798b8b-12a0-5124-a113-bed897b37ca4 | note | Verifying Document - Visual Inspection
8e79d3f1-4758-5c46-b187-250aeea61086 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
1ed5eca0-4f6f-5614-9aa2-153018048ec0 | note | Verification Activity: Activity - M
4ed9dd4e-0cf2-5019-9d79-9c6cdde58724 | note | Verification Activity: By - SE
b27003d0-9dfd-4db5-8003-7bc92329dd88 | checkpoint | 5.2.9 - Overlay (Concrete Enchased Ducts)
ad6d068f-e680-51db-9136-5865a855f484 | note | Detail - Overlay and surroundings to be placed with concrete.
45715326-d292-56ca-9b7d-f5246353e57c | note | Acceptance / Conformance Criteria - 100mm thick on top of Ducts
ec8c7066-a58c-5f84-aeec-b4b7145d3a51 | note | ○ 50mm thick side of the Ducts
2041a20c-b033-55f8-bf4b-d800ecfc3d96 | note | Standard / Specification - PS 25.13.7 c)
35c8b8c9-7b39-5a63-b066-ce65f93a83a2 | note | Verifying Document - Visual Inspection
68895aca-e2f0-51d7-a50a-4bf3e244f188 | note | Testing Quantity Required (based from schedule qtys) - Every time
ef1bbfdf-7471-5f3d-bfae-8007e793d205 | note | Verification Activity: Activity - M
2d4d9d29-e5d3-5e14-83bf-40cc7bf0cd2b | note | Verification Activity: By - SE
e624363c-a7f3-4200-a908-a5b14169eacd | checkpoint | 5.2.10 - Overlay Testing (Concrete Enchased)
8d88067b-4374-578d-8395-03ed663a20a6 | note | Detail - Placed Concrete needs to meet the strength Criteria
b927d677-4629-5641-8ca0-79e8c7c017c9 | note | Acceptance / Conformance Criteria - >20 MPA
6798d431-cd48-5667-80a3-b73f6bd42773 | note | Standard / Specification - PS 25.13.7 c)
1f17467d-a0da-5b95-af8b-8ad9bdb443ae | note | Verifying Document - Concrete Dockets
f1eb4010-1385-502a-bd4b-73969c04cee3 | note | Testing Quantity Required (based from schedule qtys) - Every time
55953956-15ee-5394-a217-22b1fe1e3848 | note | Verification Activity: Activity - H
2d660eb5-0e08-5e2c-a959-c7556381edf2 | note | Verification Activity: By - SE
64805427-a955-44ec-9a77-7a6dc956a887 | checkpoint | 5.2.11 - Backfill
35b4f383-981a-5baa-83f3-13b250ed4318 | note | Detail - GAP20 to be used if site material is not approved.
ea9adb7c-a127-5983-8734-0239bf2fab3c | note | ○ NDM Testing to be carried out.
55944cb5-0e24-593f-96c8-0365910ff710 | note | Acceptance / Conformance Criteria - 100 to 250mm thick compacted material.
9dc423a4-c2e2-5e81-8302-d6c9364543c7 | note | ○ Min 92% compaction and Average of 95%.
ea6fc683-4426-5153-b766-50899414f681 | note | Standard / Specification -
135e3174-5d3e-527b-abfd-e2ae985b4f6e | note | Verifying Document - Lab report.
05fc38b2-f8d2-5de5-b16f-4079127ae001 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
b860155e-326e-57e1-835a-b0107d384955 | note | Verification Activity: Activity - H
db5dc94a-43b2-5fc0-b7e6-254220f27db1 | note | Verification Activity: By - SE
6532af4f-afed-4f67-8d27-3de12a41f404 | checkpoint | 5.2.12 - After Completion of Ducts
8239b708-733b-51bc-aa24-9cd0cc89ed57 | note | Detail - The Contractor shall pull the pig through the ducts to ensure there are no blockages between access points and no foreign material remains in the duct.
1767dcc3-b3e9-5631-be44-fa112e2e6729 | note | Acceptance / Conformance Criteria - The diameter of the pig used for proving the duct or pipe shall be at least 90% of the actual internal diameter of the pipe or duct being proofed.
845d1ce5-7c97-5fc2-990c-6b3743696db8 | note | ○ No blockage inside the pipe
259f0715-9e54-5a8e-b0b4-4a8c3ec73616 | note | Standard / Specification - SP 25.13.7 E(1)
7c37438a-31e0-5688-8c6d-ceb6c3192878 | note | Verifying Document - Visual Inspection
dc8dc9c9-13e9-564e-a0dd-9c2adb9ad114 | note | Testing Quantity Required (based from schedule qtys) - Every time
84af8afa-fa91-5b24-b5df-30f46092f196 | note | Verification Activity: Activity - M
e913a630-16ea-5b53-bca3-ff110b3b2943 | note | Verification Activity: By - SE
0ab1d969-52e7-4609-8ba5-59874021d1d7 | checkpoint | 5.2.13 - Caps
a197ce51-f9fa-5bcb-a6f8-97892e79ddd7 | note | Detail - All duct ends shall be capped
e8277531-4066-5eb4-9142-c076f1b20a62 | note | Acceptance / Conformance Criteria - Capped ducts
fc0a637d-fa90-532d-85f0-99268ca4ab61 | note | Standard / Specification - PS 25.13.7 (EV)
63b634fc-8ce0-53c4-a992-5fef4566d9a9 | note | Verifying Document - Visual Inspection
f23c1148-dd8e-5a0c-9580-dbbdb7d02448 | note | Testing Quantity Required (based from schedule qtys) - Every time
40cb83ce-da21-5375-8812-0bcc2c84c620 | note | Verification Activity: Activity - M
a96d5487-5e3b-58d5-be11-d1f6da9ca088 | note | Verification Activity: By - SE
0ea2403f-f487-47a1-98ea-bd1d451f097f | checkpoint | 5.2.14 - Survey As Built
0f97076e-f9b9-5ee5-af67-4915753127d9 | note | Detail - As Built every ducts joint before backfill
7a18a043-5908-5c70-a8d2-1d166882148f | note | Acceptance / Conformance Criteria - Completed as per drawings
d3b8f093-79ef-5a2e-a626-66c0d31ef19f | note | Standard / Specification - Standard Practise
1e7b502a-3e65-5177-ac0c-ae473a925309 | note | Verifying Document - Survey
8eb9a18f-a4ab-5826-b695-f46b49b67cd3 | note | Testing Quantity Required (based from schedule qtys) - on going
f42a3d97-dbdd-5a0f-af35-38176c6ddf6b | note | Verification Activity: Activity - H
f2a8847e-fb7d-5c71-8636-56a4f1913943 | note | Verification Activity: By - PE
88fef857-c750-4c83-a42e-8117326904ec | checkpoint | 5.2.15 - Compaction - Clegg Hammer
7a0bbcce-3e13-502e-bd40-7ad881131259 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
610eeec0-e29b-56ac-9dcd-b8e0977cd69f | note | Acceptance / Conformance Criteria - Structural Fill
f3a115bc-08bd-51aa-bdd2-13ca761c3cac | note | – Min CIV 18
25b78a8c-387c-52b4-94a1-0a6c09fffe68 | note | – Ave CIV 20
ccaf93f5-693a-534f-a88d-9d87c2b2973f | note | ○ Non-Structural Fill
67292336-2707-5ca4-bcf6-ef183c9f4c88 | note | – Min CIV 10
b991e857-bca8-5e5e-ba50-672c207f6387 | note | – Max CIV 12
9e0d0391-ffcb-5c9a-8729-f3e6b6291828 | note | Standard / Specification - Appendix XVIII
f89bd28b-6969-5cbb-b7e9-1dd4d39a753b | note | Verifying Document - Clegg Hammer Report
8c526c58-5498-5708-a465-ebc0a6193112 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
cb1f0f94-3b42-5e49-82e7-d39b298f7b27 | note | Verification Activity: Activity - I
a5b69548-1b4b-535c-8021-712703182a68 | note | Verification Activity: By - SE
b62e7030-7e52-49f7-802b-cbc0d327f889 | checkpoint | 5.2.16 - Compaction - NDM
9b629f71-cead-58ba-a66a-fe19f088a88b | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
0f2df5b9-2703-5e36-814b-7b0c2d9401d4 | note | Acceptance / Conformance Criteria - Ave >95% of MDD
eeaf73ce-25c8-56ef-9ee3-6b2a6480baa0 | note | ○ Min >92% of MDD
b1c2136a-ad22-505b-b360-8ae9aa54d2f6 | note | ○ Non Granular Material
357e89a6-ac37-50d6-8d9a-5733063903c6 | note | ○ Max Air Voids 8%
6c12459e-b0e7-5299-893c-e157fc1e4371 | note | Standard / Specification - Appendix XVIII
1fc5c8e4-504b-57b7-987f-7b61070a775d | note | Verifying Document - IANZ Accredited Report
8a930f07-36b4-5e34-bf77-71059fb8294b | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
978a88bc-73b1-53bb-ae92-752db5453d06 | note | Verification Activity: Activity - I
66cab62a-ec6b-5f99-988d-26aeea676605 | note | Verification Activity: By - SE
bd3ed90e-e6c3-499f-a3e7-0701800a596f | checkpoint | 5.3.1 - Subsoil Drain inspection
698c917c-c9f9-55b8-b7d9-02920c8761a5 | note | Detail - Subsoils to be placed adjacent to the underpass and inspected by Engineer
053828d7-155b-5199-8545-6e376e3fb2ee | note | Acceptance / Conformance Criteria - Engineers Approval
8bad0038-c7ac-5541-b53d-3f1ba532cab9 | note | Standard / Specification - PS 17.6.3
ee14da95-e29e-5632-bf79-81bd249a3b6c | note | Verifying Document - Visual Inspection
fb8186ab-bc8c-524e-95ca-409f71b03b1a | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
4ca194fc-5360-5a54-9477-9ef71171d09e | note | Verification Activity: Activity - I
120d1428-1bb4-5fe7-8985-01b8505b28d9 | note | Verification Activity: By - ENG
cddc7fe7-2b45-4a26-b614-75577cec6684 | checkpoint | 5.3.2 - Excavation
f48ffdd4-1097-5135-ac9d-36a5a775a974 | note | Detail - Excavation of Trench should be within tolerances.
1f15e36b-91ce-5a67-ade8-e4665fc6cf40 | note | Acceptance / Conformance Criteria - 335mm deep x 300mm wide
f18d3b34-7c13-519c-8ca1-372251fcf7c8 | note | Standard / Specification - Drawings
b6429cb3-bbf5-5ec4-9969-5fa745f2d824 | note | Verifying Document - Checksheet
23f0d1fd-38ef-5c51-801a-150a8b96d50d | note | Testing Quantity Required (based from schedule qtys) - During Construction
872f847b-8b6a-5a06-bd10-be6168908453 | note | Verification Activity: Activity - M
20ee4664-1e9f-5213-b8d0-a3e6836b992c | note | Verification Activity: By - SE
84b345e8-bc11-4931-94f8-b2b718b5d4e9 | checkpoint | 5.3.3 - Placement of Bidim
1b0bd37d-5e46-560b-b0a4-0fb6657694ae | note | Detail - A29 Bidim to be placed and wrapped around Trench.
7d8766ba-095a-5f94-9cc2-a17ca23d8b0c | note | Acceptance / Conformance Criteria - Minimum Width 300mm.
0445d078-84c9-572e-b83e-6c2d9913e148 | note | Standard / Specification - Drawings
6640dd3a-f7cb-59c4-841f-0837c303f463 | note | Verifying Document - Checksheet
8b8f6d93-79c4-5fae-8de3-cda69955dcc4 | note | Testing Quantity Required (based from schedule qtys) - During Construction
41b1306a-94bf-57be-9eb3-b97ee9fb52e5 | note | Verification Activity: Activity - M
8f53af20-66fd-558c-b15f-511b1dd42af1 | note | Verification Activity: By - SE
78c559b1-e0ee-4ab4-a5b5-cb63ec996f1a | checkpoint | 5.3.4 - Cushion (Bedding)
9d0f8e41-7690-551a-b37e-59bd50a2a506 | note | Detail - Pipe must have 75mm of Cushion. Drainage 60:40 Material to be used.
356da31f-468c-5b7c-8e73-bf548fb32ab9 | note | Acceptance / Conformance Criteria - Minimum 75mm
d0c8a570-c1cf-5636-a36e-dc2bf7ee2732 | note | Standard / Specification - Drawings
6cc9e6dc-6955-5905-978c-0cbd947e7fd4 | note | Verifying Document - Checksheet
2adb462e-b4dd-5c5c-8aa6-60aa96356953 | note | Testing Quantity Required (based from schedule qtys) - During Construction
32c0a2c2-1b9e-5628-90eb-c8aef0845edc | note | Verification Activity: Activity - M
dff824f7-a40d-5bd2-93c0-965af79b5272 | note | Verification Activity: By - SE
756440af-c1b3-49ad-8171-8f327a5f9483 | checkpoint | 5.3.5 - Placement of Pipe
291eb7fa-db53-51d8-be16-61855b343c27 | note | Detail - 110mm Perforated Pipe to be laid Down
b51c189f-970e-5e7d-9509-4f121d87a5da | note | Acceptance / Conformance Criteria - As Per Drawings
c2edbed1-3b8c-58f8-bed0-a436539e539f | note | Standard / Specification - Drawings
7ac00807-fd4c-5cdb-a222-0c9b543bf9c0 | note | Verifying Document - Checksheet
e1cbdfda-5425-5d62-8067-ea047dd95dd6 | note | Testing Quantity Required (based from schedule qtys) - During Construction
a244f73f-f9a5-5d1c-8ba0-713a885b9a65 | note | Verification Activity: Activity - M
4ecfc7d8-c3ed-508c-afe1-6cad3ae29e82 | note | Verification Activity: By - SE
e1c00396-cf67-4abd-add1-58e9014e29a6 | checkpoint | 5.3.6 - Backfill
0b95e677-217f-5dbf-a5d3-eb5fa570dd41 | note | Detail - Pipe Must have a 150mm cover from Bottom of Pavement.
2b59aedd-ac8f-5c66-9960-480e273dae21 | note | ○ Drainage 20:40 Material to be used.
18c57cc4-d906-5fa0-af9b-f996a2999e67 | note | Acceptance / Conformance Criteria - >150mm Cover
c13b938b-e6d5-56e0-af03-a9c5378d147a | note | Standard / Specification - Drawings
7a5dcb1e-26d1-5c80-9d2b-49ee2efb0a90 | note | Verifying Document - Checksheet
52b1f0af-3a5c-5cb1-9e37-6c8559d96573 | note | Testing Quantity Required (based from schedule qtys) - During Construction
025dd61a-b677-52b0-b981-90e0ded7096d | note | Verification Activity: Activity - M
58be6f5a-f280-507d-8b04-3de278a3dc5d | note | Verification Activity: By - SE
097a0d9d-145e-4f9a-9831-32ab2556840c | section | SECTION 6 - UNDERPASS GRATED TRENCH DRAIN
6b02624f-a62d-41ce-a371-baafc433125c | checkpoint | 6.1 - Installation of Channel Drain
fd3bcfde-68eb-50de-9757-abf188950a47 | note | Detail - 300mm wide grated trench drain with WAVE HEELSAFE grate to be located at end of underpass apron. Trench drain to connect to SWMH2.1.5 via dn150 pvc-u sn16 pipe. Grated trench drain to have min. loading class C.
4350ab82-c826-5d8f-b5ed-f5feaf2c456e | note | Acceptance / Conformance Criteria - Installed as per manufactures instructions
736f585b-cebf-536c-9341-c6e49dd10ebe | note | Standard / Specification - 21.5.8
60afc622-a7f9-54c6-9359-210f594a11bc | note | Verifying Document - Inspection and record
050ec89a-3938-517a-8508-b0ca2667366f | note | Testing Quantity Required (based from schedule qtys) - During Construction
ca284089-bb5d-565a-8825-9f21355766bd | note | Verification Activity: Activity - WP
f4886b0c-d361-5478-82da-d6d0f4743363 | note | Verification Activity: By - ENG
52fda9e0-b946-4406-a739-88a4a74e8e3a | section | SECTION 7 - AS-BUILTS/ REDPEN MARKUPS
ffcb0ed9-f730-461a-8a14-6d1552b2e891 | checkpoint | 7.1 - As-Builts/ Red pen markup
c32deded-47ce-574f-9586-a7c1a494984c | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
992cae27-87bb-559e-a203-0ec564f395cc | note | Acceptance / Conformance Criteria - As built drawing red pen markups
5344aad5-2565-5cde-893b-8a953d2fc3b0 | note | Standard / Specification - PS 16.7.6
9090d8ab-0867-5037-8956-891f95f06a0e | note | Verifying Document - Red pen markups
459397cb-9589-5e70-82f4-d45dd115ab97 | note | Testing Quantity Required (based from schedule qtys) - During construction
eb857af8-8fd8-5a85-befe-b287607784ff | note | Verification Activity: Activity - D
66f09670-03d3-5c08-913b-62664b64b9d6 | note | Verification Activity: By - SE
ea42ec14-fba5-4b05-a6ca-93a37285cf37 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
1e8467bf-0481-5a1f-a8e8-87c82681a6d7 | textbox | Contractor's Rep Name:
20cadb38-f718-5861-ba34-4ffd25245641 | textbox | Engineer's Rep. Name:
aa2a294b-6827-5870-8ffd-d1e2b17a7102 | date | Date:
721787b5-0541-414d-acab-197ff67345b7 | signoff | Add Signature
c8d1e418-0de5-47c8-8d7a-6d870334a545 | checklist | DN1210-011 ITP Wastewater Open Cut Rev 0 | itp | DN1210-011 ITP Wastewater Open Cut
0f588adc-77f9-48e7-9aad-54c4b1da8537 | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
299075c4-5c9d-4274-973a-04447a19d1b8 | checkpoint | 1.1.1 - Pipe Laying
69307b7e-c0c1-532e-b07d-ba0b52a3d24b | note | Detail / Activity - Method statement
1c27c28d-8dd3-545f-87b0-10d8f63a1dda | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
09bd9dab-b8eb-5a15-8f9f-9bae701fd467 | note | Standard / Specification - PS- 22.3 Appendix V
a7f808e5-1c36-5f4f-b03c-4d8a45f3bb52 | note | Verifying Document - Wastewater Construction Work Pack - Open Cut Sign off
d7bf0fb2-e732-5759-960e-6467e9db3b44 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
aaed5e31-bb50-51db-8467-12838ffa24d7 | note | Verification Activity: Activity - HP
309c64ae-b0ae-5dd1-b980-56720c0b08a3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
27bcd6d2-5684-5c86-8637-274294e91b11 | note | Verification Activity: By - ENG
b9581f36-1f1b-4052-8a86-a417d7d54eff | signoff | AUTHORITY HOLDPOINT
a204e3aa-26b3-4be8-b9e5-4f604ebb02f9 | checkpoint | 1.1.2 - Butt-Fusion Welding
38d11196-8824-51c6-b260-1f028c74a6d1 | note | Detail / Activity - Method statement
d84e6b16-1a37-5441-95ab-af41a20d866e | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
a0ff76dd-5abc-5506-84b3-af4540100af6 | note | Standard / Specification - PS- 22.9.4
78ddb59f-3f95-5b8b-b4bb-fde293cf7279 | note | Verifying Document - Wastewater Butt-Fusion Welding Work Pack Sign off
788ae0c5-622a-5b17-9509-2e8ec3f716af | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
15d86717-51f6-59af-a3f0-6edd9326e50f | note | Verification Activity: Activity - HP
1706e69c-85a4-51bf-bdc4-03af7cea8fe0 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6f2f14af-92b2-5eab-8696-5671639fd783 | note | Verification Activity: By - ENG
6ffa504c-8ddb-43e1-8c30-c916a0ceab9b | signoff | AUTHORITY HOLDPOINT
3388db01-c23a-4674-ae24-d92ca51bf4e7 | checkpoint | 1.1.3 - Electrofusion (EF) Welding
1b3b6d42-9999-57f8-b7ec-0c6988804de1 | note | Detail / Activity - Method statement
b7ab8378-4ef3-584e-8114-dcfad7e36d01 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
e1dbcab1-f463-5905-a6e7-2948db64ff74 | note | Standard / Specification - PS- 22.9.5
2fcddb95-7437-53e4-8246-c5f350a9ed13 | note | Verifying Document - Wastewater Electrofusion (EF) Welding Work Pack Sign off
325cb855-dd93-5844-ad44-67fa255c45c8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
c0547089-3351-52f1-809c-d6f0b162bb65 | note | Verification Activity: Activity - HP
3710d36e-b605-5a3e-b8eb-af7e5ba043f3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a17f6ab0-aaea-511c-82b1-1c47ac6d477c | note | Verification Activity: By - ENG
adb5dd0f-a3c9-4723-80a0-44d248faa341 | signoff | AUTHORITY HOLDPOINT
0122b533-1e35-4e7c-9cb9-b0f2b272cafa | checkpoint | 1.1.4 - Pipeline Pressure Testing
426a1ab0-f2ff-5859-ab7f-a5370fd8fbe8 | note | Detail / Activity - Method statement
66c5521d-e8f1-5603-9cdc-f70eb7db7a92 | note | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
3f5c0943-dddb-5597-bc56-21d3367636b2 | note | Standard / Specification - PS- 22.3 Appendix V
69e09f37-166f-51d6-a427-30b47b42e94e | note | Verifying Document - Wastewater Pipeline Pressure Testing Work Pack Sign off
a7d78aba-f5f6-5ea6-bd3c-286fff9a683c | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
9c68304e-bb32-52f4-ac97-d0e2a515e1e3 | note | Verification Activity: Activity - HP
01fd9b37-e70d-5373-955f-2f173071be6b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
36fa88a2-4cb1-53c5-ae12-af67abd81b5e | note | Verification Activity: By - ENG
5a233e3d-8bda-4ac7-b265-1412daf6457c | signoff | AUTHORITY HOLDPOINT
e69e77f6-387a-4b57-9631-ebba6768fc5d | checkpoint | 1.1.5 - Extent of Line Setout
0c00b8ef-6558-58b6-944c-d122bb37eb8c | note | Detail / Activity - Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings.
4a7f6042-a3d1-59d6-8c63-2800645d12fb | note | ○ Identify any clashes before construction.
4c7f3cb0-7025-5868-8044-909048992288 | note | ○ LOT - markup
6270c23e-106d-544a-97a5-df33f0725b6a | note | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
4daa92a8-8234-57be-b970-bd996363bee6 | note | Standard / Specification - Design Drawings
3cb386ef-f18c-5f7c-8579-75864761b59e | note | Verifying Document - ITP Sign Off / Mark-up
31ff7e7f-e83e-51e1-a283-27d1cef67edc | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
813a6e92-8aaf-5a00-99c7-57d7655dd186 | note | Verification Activity: Activity - HP
7b5b46f0-f72f-5c7f-9e79-cf709c01a3e3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
461ef13c-8efb-5564-ab87-86790b676801 | note | Verification Activity: By - ENG
abe7f8a1-8a1a-449a-83eb-70b5c4b1fc72 | signoff | AUTHORITY HOLDPOINT
047d7115-2e03-4997-b839-b2b091c2fb1f | checkpoint | 1.1.6 - Existing Wastewater system (If any)
e7900500-da4e-51f7-9a04-02ed56a13279 | note | Detail / Activity - Confirmation of existing Wastewater network.
328ec7f9-2c75-5301-a372-8b709db28c8f | note | Acceptance / Conformance Criteria - Survey Informations
30cb13f6-65d2-573d-93b3-443452b5b830 | note | Standard / Specification - Appendix V
1ef3df51-82a4-5912-9a9f-57f96b6b8241 | note | Verifying Document - Survey data
d8c04ed5-5bda-54e6-b83a-650b388522bd | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
f2c60e7d-6ef1-5983-a3a8-bebe9fa57c9d | note | Verification Activity: Activity - HP
86e9c52e-f167-5ca2-b750-66debd0f65e3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a1c70f5e-abc1-591b-8ed5-eb4c76056786 | note | Verification Activity: By - ENG
f09f7f93-7fb4-4eac-9c5a-886160cae258 | signoff | AUTHORITY HOLDPOINT
9362e772-38cd-4fcb-b8a4-25e0f0559541 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
6b8aecea-823b-404b-8911-253aa1e50b6c | checkpoint | 2.1.1 - Material grading: Materials (Imported sand and AP20) MDD
63d4c020-79c7-560c-b789-6d9a7d69490c | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone compliance.
36cc880a-e1aa-58b6-bad8-d307d941db01 | note | Acceptance / Conformance Criteria - Embedment Zone Material accordance with AS/NZS 2566.2
eb81b2d8-3cb6-5df1-8988-6892d510a53c | note | Standard / Specification - PS 22.13.1
0512002a-a118-5651-b204-bba9216a3c7c | note | Verifying Document - Lab Test Report, NZS 4407.3.8.1
e3b7513e-0a3f-5c87-8899-173fb36b6587 | note | Testing Quantity Required (based from schedule qtys) - 1 Test for each additional 1000m3
513142f5-d2f2-5cdf-a1ba-cd20c625d26a | note | Verification Activity: Activity - HP
03843f2a-1790-5568-af5a-0db07eb1f79a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b5ab0006-723d-565d-8022-272889787130 | note | Verification Activity: By - ENG
97779da6-9fce-442e-9e80-8116c3bb3a15 | signoff | AUTHORITY HOLDPOINT
b685762c-c35b-49a8-8cec-eb2498c8b94b | checkpoint | 2.1.2 - Material grading: Materials (Imported sand and AP20) PSD
15c81c65-b31f-5550-b001-d139322edadd | note | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone compliance.
a1e1037f-48cf-5297-9ae7-bc24869f4602 | note | Acceptance / Conformance Criteria - Embedment Zone Material accordance with AS/NZS 2566.2
f141b141-5b4c-5f71-9c73-663f10907516 | note | Standard / Specification - PS 22.13.1
d08756c2-edfb-58ed-baef-2c3b66787b33 | note | Verifying Document - Lab Test Report, NZS 4407.3.8.1
5c96fff6-e38e-5ba9-9a22-20e0f1f52f3e | note | Testing Quantity Required (based from schedule qtys) - 1 Test for each additional 1000m3
f80c6562-4556-557d-b558-f8b6549c44c2 | note | Verification Activity: Activity - HP
3df68d53-30d9-5639-8ae9-6f2b73e556c7 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
91f5846d-d38b-50f8-b37d-a5a16def689a | note | Verification Activity: By - ENG
8f5d7486-3a29-4f8c-a0dc-7ed9f990943d | signoff | AUTHORITY HOLDPOINT
f1faa230-8b06-4059-882e-bd84ebbbf52c | checkpoint | 2.2.1 - Material grading: Materials (Excavated Pumice GAP65/AP65) MDD
0e190bb8-14c4-5edd-9122-45c3e9e6fb8b | note | Detail / Activity - Trench Fill and undercut material compliance.
2d123c17-f0d4-59ef-b5b0-21aff1d6636b | note | Acceptance / Conformance Criteria - Trench fill - TNZ F1
6223bab8-f7b0-5547-a339-b5f7197dd0e3 | note | ○ IFC Drawing WST-0320
ca5d7a67-8001-54ed-b682-30ad53629c9c | note | ○ PS - Stormwater Specification
d9003dea-90c0-56fd-a99c-838a60064715 | note | Standard / Specification - PS 21.7.2
0b15375b-7038-5338-a5b9-26a72f72d751 | note | Verifying Document - Lab Test Report, NZS 4407.3.8.1
cbcedeec-0df5-5d3d-aa49-b3a152bf14d0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test for each additional 1000m3
7b1649bb-9a73-5df0-9e41-042f900b7086 | note | Verification Activity: Activity - HP
f39a9b25-8abb-5c15-9d13-a00dc9690a81 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
247f11f7-a363-5eab-b231-4a51c12309ca | note | Verification Activity: By - ENG
5113fb71-e3ae-4429-963e-7af11ccd5812 | signoff | AUTHORITY HOLDPOINT
6a97fe5f-e4b5-45e9-a021-d0e0f255be9c | checkpoint | 2.2.2 - Material grading: Materials (Excavated Pumice GAP65/AP65) PSD
01d79828-56bd-5f3d-9340-dbb50cbf4dae | note | Detail / Activity - Trench Fill and undercut material compliance.
2899101d-b38c-5aa5-9ea0-48f49cd5fc92 | note | Acceptance / Conformance Criteria - Trench fill - TNZ F1
db53130e-b7f7-592a-a190-f16a18f66915 | note | ○ IFC Drawing WST-0320
71aad77c-4990-55f5-bcac-659f1db527a8 | note | ○ PS - Stormwater Specification
965b0172-b85b-5eba-9037-05cce18670fa | note | Standard / Specification - PS 21.7.2
fcd82aff-11b7-5aa6-9c44-b2c57080303b | note | Verifying Document - Lab Test Report, NZS 4407.3.8.1
4c4072a1-86a3-5f79-ab1e-7c61837b1a20 | note | Testing Quantity Required (based from schedule qtys) - 1 Test for each additional 1000m3
f6a9eb63-b5ec-5768-8712-ad2d13d6ec1e | note | Verification Activity: Activity - HP
52bd6ddf-7f62-5a56-b0c4-32400cc78faa | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1a11dd84-38ca-5f47-97a5-332750f44593 | note | Verification Activity: By - ENG
9e7b18bc-8dcf-4a4f-a358-78e04953a19b | signoff | AUTHORITY HOLDPOINT
65e8758a-c5c9-4834-bf5e-9d488418cf02 | checkpoint | 2.2.3 - Weathering index: Materials (Excavated Pumice GAP65/AP65)
b36db8d6-98ee-5e98-a38b-189c444f5ce2 | note | Detail / Activity - Trench Fill and undercut material compliance.
b9a1a652-9d0a-557c-a003-49adbf5e4605 | note | Acceptance / Conformance Criteria - Trench fill - TNZ F1
72d796cd-d390-552b-848f-82d308b58548 | note | ○ IFC Drawing WST-0320
1a6351da-53ca-560a-a7e3-ee372b5f9e8a | note | ○ PS - Stormwater Specification
1c59e22e-c7bf-587e-98ff-f1eb866217f0 | note | Standard / Specification - PS 21.7.2
fa624fa9-1b4d-55b2-bcc6-eb8db18d3f3f | note | Verifying Document - Lab Test Report, NZS 4407.3.11
c24c3816-5e1d-54be-8138-c591dd38a5b4 | note | Testing Quantity Required (based from schedule qtys) - 1 test per source
f55be268-5e98-5898-b33d-8dc582090939 | note | Verification Activity: Activity - HP
261a3799-7012-54a2-9446-b2a01a63a65b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
122b264d-df0c-5fdf-ac0e-9f9ade9469ca | note | Verification Activity: By - ENG
564b4e3d-5d5f-4cf5-a357-55d6f16f706a | signoff | AUTHORITY HOLDPOINT
e2ab8314-be9d-4c97-a2e1-56cd93b83481 | checkpoint | 2.2.4 - Crushing Resistance: Materials (Excavated Pumice GAP65/AP65)
853bf6b1-8a33-5dc1-8a77-d840829fb027 | note | Detail / Activity - Trench Fill and undercut material compliance.
f0421502-cfc8-5633-b82b-d9d7bf31869e | note | Acceptance / Conformance Criteria - Trench fill - TNZ F1
c7020bc6-3654-5b5c-950d-34a1e692aa11 | note | ○ IFC Drawing WST-0320
c71d053a-28f0-511d-9767-de9773228300 | note | ○ PS - Stormwater Specification
b1a3a047-c1e0-5a63-a890-5d2f40f58ea3 | note | Standard / Specification - PS 21.7.2
478fccf4-1894-5a8d-b5c2-a666eaca3ec8 | note | Verifying Document - Lab Test Report, NZS 4407.3.10
375d8d45-e020-5db7-a3ad-b40dbfd48b8b | note | Testing Quantity Required (based from schedule qtys) - 1 test per source
7ee4ad42-aa73-51fb-9b6c-b8d78aae0f0b | note | Verification Activity: Activity - HP
a556b06d-e568-5e0f-8e7e-229e01cbcc9f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
e0bbdf21-3ace-54f7-b38c-ba3395741ba5 | note | Verification Activity: By - ENG
d0dbf79d-af56-4147-a26d-3d8b43a8b9f9 | signoff | AUTHORITY HOLDPOINT
445cdfe8-afc3-4a64-88cc-3055af15d31b | checkpoint | 2.3.1 - Pipes (PE/ Sleeve)
cd6e0332-f215-5e0c-b2a8-0e226e9b33e9 | note | Detail / Activity - Manufacturer's record and location of extrusion plants.
dbe223f5-9518-59c8-a75b-cf1d7e16ed28 | note | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
674e8b82-da68-5a9a-8612-8f94c4c74d87 | note | ○ Full Traceability information and certification of analysis for the resin batch.
058d1801-6abc-5f4c-842c-27cad6fe7b96 | note | Acceptance / Conformance Criteria - Engineer approval
c8a7e04e-bd39-55e9-9bfc-76d0afe33f91 | note | Standard / Specification - PS-22.4.1 (d)
83f9ba81-b91d-5e17-8abb-8095755b5422 | note | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets.
eafcb51c-e3d4-511a-97be-64517a9dffa4 | note | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
f970312d-0329-5825-9b48-00423a7603d1 | note | Verification Activity: Activity - HP
217c5d85-a00d-53ed-b3ec-3fde857780a8 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a3932c0e-2e38-5095-b626-4244fc48308d | note | Verification Activity: By - ENG
cb03afa8-3358-4292-8019-c79b8a47ae84 | signoff | AUTHORITY HOLDPOINT
6119b3a3-89a6-403a-9807-a95bb1cb56e9 | checkpoint | 2.3.2 - Green Dome Odour Filter
efd93454-9472-5b63-bda2-d06770be5323 | note | Detail / Activity - A Green Dome Odour Filter (Model GDOF36) complete with DN150 ducting.
720abfc3-4f05-5fb1-ab92-c95e59d733d6 | note | Acceptance / Conformance Criteria - IFC Drawing 0323-1
ae57b777-ec38-532b-bc37-69c89d5734f8 | note | Standard / Specification - Model GDOF36
4bf0d5b9-1c37-5f29-9c7e-8eab9c86f2e4 | note | Verifying Document - Delivery Dockets
ed1b9603-b8dd-5e3c-93d2-05eafed2ab3c | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
b9fe6ff9-b83b-5780-b0cd-126bb4671201 | note | Verification Activity: Activity - H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
b490a747-4277-5fe8-a975-89ea65b8fc0c | note | Verification Activity: By - SE
67466b53-61fd-429d-b080-0d2439709835 | checkpoint | 2.3.3 - Valves, Adaptors, Flanges and Fittings
a36e4d36-ebed-5524-915f-ac9a90406a88 | note | Detail / Activity - Have a pressure rating no less than the designed pressure.
044d2234-e989-5155-855e-f60ae4b45d8f | note | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
0d53f2ef-e118-5b2f-83f8-d1e499b0958f | note | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
9713a556-ba0d-50f9-a9a9-a901d927ff34 | note | Acceptance / Conformance Criteria - Engineer approval, AS/NZS 4129
d9325437-abae-5c0e-8c19-9bbe6b1cff05 | note | Standard / Specification - PS-22.4.2
64834250-5f3b-58cd-9eca-d8c7356ad9c4 | note | Verifying Document - Delivery Dockets
1623f670-4401-5d52-9e94-33509000b72f | note | Testing Quantity Required (based from schedule qtys) - Prior to Procurement
17dc9f7a-a0fe-5b3b-a4d6-d5205f522821 | note | Verification Activity: Activity - HP
46795a2c-c679-5bdc-b4d0-c5c70664a67b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ca9c20d9-8d0f-5664-86d8-634cb0f9c595 | note | Verification Activity: By - ENG
18c104a6-8a20-4051-b425-828ef538ba69 | signoff | AUTHORITY HOLDPOINT
0b7ade51-07f2-4b67-9b00-ed63b60b05e8 | checkpoint | 2.4.1 - Pipe and fittings. (PE100- DN200 PN10, DN180 PN10, DN400 PN16, DN500 PN16).
db646308-549a-5feb-bc5f-705d0fee2823 | note | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
c43ff3b8-17a3-5b54-a02f-cff46382c972 | note | Acceptance / Conformance Criteria - As Per Drawings
34e3c333-4fe6-5449-810b-37a2cd07740f | note | Standard / Specification - Design Drawings
5cc7180c-91a5-580b-8563-fb9d4c03702a | note | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
4c8c600b-f2db-50cb-9c51-98b533b40049 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
e612cc4a-6169-5ad5-92fb-20a03451c1cb | note | Verification Activity: Activity - H
56d235bc-1c94-5e90-896d-1e0d3d7a696f | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
07ce395b-016e-5ac9-82aa-ae0f846a9e34 | note | Verification Activity: By - SE
33d64e49-b6de-46a9-b5c5-184274781ff4 | checkpoint | 2.4.2 - Valves, Adaptors, Flanges and Fittings
2abae2e3-eb07-5552-8434-d882dd681a5c | note | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
abe61d51-99f0-53ee-a4d2-83a6969a0b7d | note | Acceptance / Conformance Criteria - As Per Drawings
f58d87d3-7844-5cb4-9854-64efb4d1ad88 | note | Standard / Specification - PS-22.4.2
5131af6d-79bb-56ab-bd3a-5a4ae3a07b6a | note | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
89bbb1a0-422a-5686-8b8f-d4252f26e0be | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
f8e0b079-2702-52da-99e9-a5b7b73be253 | note | Verification Activity: Activity - H
4607d824-47b9-5108-a578-e945d1f3da23 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
87b143cd-e0f6-5e7f-bcf4-cfbe9b0edc01 | note | Verification Activity: By - SE
369e361e-4918-4ef4-b481-3ee248ec9670 | checkpoint | 2.4.3 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
99f42f5c-420b-5ac4-85f8-b6807ab262f0 | note | Detail / Activity - Confirm Specification and material in good condition.
f8c61ea5-3563-5ec9-8d98-f942a265f3f2 | note | Acceptance / Conformance Criteria - Site Engineer Approval
45ab8368-5356-51bb-a6cf-a1d92ccfa025 | note | Standard / Specification - PS-22.4.1
19106153-823f-5506-9b49-f50829ba1867 | note | Verifying Document - Delivery Dockets
3add0376-a722-5a5f-9dcd-e9db946b7575 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
4deeac4a-32c1-517e-99ab-ced5f706ae72 | note | Verification Activity: Activity - H
9a507282-b7a5-5796-b8d9-4dc5c4da826b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8e0824c5-08c9-5ef3-b817-aac21582cffe | note | Verification Activity: By - SE
cac7fbdf-6df4-4818-8a59-3791c6ee356c | checkpoint | 2.4.4 - Bidim/Geogrid
fd836e45-9367-5541-be45-1aacf57f7aa6 | note | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
3ca5aaf9-f46d-53f6-b9d6-599aaa6ca5cc | note | Acceptance / Conformance Criteria - Site Engineer Approval
ed0095a2-f6a5-5690-8a61-44bb366498a6 | note | Standard / Specification - PS-22.4.1
2ee600c4-3cdc-5cf2-b147-ffdb5d2c60fe | note | Verifying Document - Delivery Dockets
efe23815-05bb-5216-9c66-2013a1fa8027 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
12a28ac8-39f2-5e24-b680-37311fc02b45 | note | Verification Activity: Activity - H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
27acb9bd-c281-5272-92a9-23f1701d9398 | note | Verification Activity: By - SE
10bd6aca-7fc3-4fb4-b0ec-872d5596ccf5 | section | SECTION 3 – CONSTRUCTION ACTIVITY
3642cfb5-a232-495f-a3e9-b353ac249617 | checkpoint | 3.1.1 - Foundation Compliance
5b9ecbc0-3a66-5230-9d9e-21ccbb2d8151 | note | Detail / Activity - On Granular or Cohesive Material
276c50a1-6b35-5d08-881e-e934c36a3228 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
291b0c66-d4d5-5354-a277-0570736cc2ae | note | (Or)
a0a0e25a-3c01-57eb-bd49-7e9cb43d7aae | note | ○ Cohesive Material: Vane Shear Strength 70kPa
12adaa71-3a1b-549f-80cc-137ee12cc373 | note | Standard / Specification - Appendix V
da7fe8d9-c4ff-548f-9914-df92ec53cc3d | note | Verifying Document - Scala/Shear test result
f6dff767-dcc5-5c8a-9a2f-f2fc04aa1b6c | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
f3df22b4-835d-5c25-ad86-fd08b76ee3a0 | note | Verification Activity: Activity - W
cc4b79a4-46b0-53fa-94a3-030a818a1313 | note | ○ Review of text reports/records or other evidence of compliance
8d631a94-a6a5-58a8-bee5-688cd4b4dd95 | note | Verification Activity: By - SE
0c78897e-586f-4338-affc-79675371ad5e | checkpoint | 3.1.2 - Undercut approval
8ee6f765-88ae-5687-ad7c-1a7f43d57b80 | note | Detail / Activity - Trench Foundation
96c69c00-ba57-5367-b2eb-f71768d425c0 | note | Acceptance / Conformance Criteria - 300mm Max cut
54da3093-3972-5338-8f7f-5dfa7dbde26f | note | ○ IFC Drawing Sheet 320
c1828a75-275b-54e3-b65d-790e80a4a147 | note | (Or)
8100c88b-bf9c-510e-bb66-169a27f8691a | note | ○ Engineers approval
a45504ce-a4bd-5b2c-ba00-94f36fbb4788 | note | Standard / Specification - IFC Drawing WST 0320. AS/NZS 2566.2/2002
1814587f-523b-578f-8940-d34f7c242338 | note | Verifying Document - Lab Test Report / Wastewater line record
158f7eef-4014-5ff5-93e9-a42f6d401a46 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
027078c9-fd13-5f44-9929-6ef3b0beeb11 | note | Verification Activity: Activity - H
c01f7e4d-f088-55f9-8065-9c44cf4209e3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0502a114-cb87-5a2f-9913-e346638f4256 | note | Verification Activity: By - SE
0270bad1-a6bb-4561-a980-0fb3c4bdb887 | checkpoint | 3.1.3 - Undercut Backfill Compliance (PAP5)
34ec93f5-a982-5d40-9c3f-96ff40f37ea2 | note | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
94c94f44-aba0-520e-bb38-43fccc076285 | note | Acceptance / Conformance Criteria - Visiual Inspection
cc8b006e-5deb-5ad3-91ad-a7f984e48993 | note | Standard / Specification - IFC Drawing WST 0320
6ccacff5-aa4b-5dc0-b147-b6a776045d90 | note | Verifying Document - Lab Test Report / Wastewater line record
9c9c62ff-ad3b-5f16-86e0-ec8f2429a074 | note | Testing Quantity Required (based from schedule qtys) - Every Undercut
cfac9e27-1487-55da-a2ba-7ad80b76dd69 | note | Verification Activity: Activity - H
09f9fe2b-2c85-596b-af1e-53006f14b691 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
c2fc6cdc-2e59-5624-b243-51a2500ee140 | note | Verification Activity: By - SE
125b5a66-97e2-4b8e-b83b-cd3d1b096ad2 | checkpoint | 3.1.4 - Bedding Zone Compaction Testing (PE Pipe)
c2b95ca8-0431-5095-bb35-88043de97b95 | note | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand or GAP20)
15fb79c9-7045-5196-b00f-76c8c962afe5 | note | Acceptance / Conformance Criteria - Bedding Zone:
510faa0f-1204-5d6d-ba1b-766e8698f5bb | note | ○ 100mm minimum thickness (compacted) over the bottom of the trench.
6ba336f5-9422-5575-b058-6a11ea12abc6 | note | ○ Minimum Compaction - Trafficable 95% MDD and Non-Trafficable 85% MDD
f201301c-2a6f-5666-ad05-49d2a7c3abfa | note | Standard / Specification - IFC Drawing 0320-1, AS/NZS 2566.2/2002
2ee42e88-f276-59f2-8e0f-553d41023b8a | note | Verifying Document - Lab Test Report
d9185c1d-b149-57ac-9752-c6d0034c8282 | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 20m evenly spaced intervals.
e98a47eb-c7af-5c75-8a5c-2540f09c454d | note | Verification Activity: Activity - H
3001de09-4099-565c-9688-542be5c5d059 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5e982e1d-78fc-5cfb-835b-3b020430ae68 | note | Verification Activity: By - SE
ead767a0-d2a0-4add-ab99-134e777d80bf | checkpoint | 3.1.5 - Laying of Pipes
78cee73a-55dd-5716-82d7-b14a1428add9 | note | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
f034a005-c4f0-5ea9-8286-f81f79eec0fd | note | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
568842f1-d6d3-561b-8f8b-d27e379105d0 | note | Acceptance / Conformance Criteria - As Per Drawings. Facing upwards.
73b71578-5c34-500b-ae1c-826c0eb0ebbc | note | Standard / Specification - PS22.7.1 C
4f8a32c0-6c1e-5d96-9506-b5656ccf6645 | note | Verifying Document - Visual Inspection / Wastewater line record
2dcb6974-87c4-5bb3-873a-ead9dafdfeb0 | note | Testing Quantity Required (based from schedule qtys) - Every Line
6e0609a0-ce1d-5c01-9d97-d3315f85f337 | note | Verification Activity: Activity - H
b3384957-e2af-5499-962e-f9175e266a6c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
0ca41f10-ea1e-5310-b021-5e7d1be42c1b | note | Verification Activity: By - SE
2ad4f35d-a568-4ab4-be8f-9a72c06e9c65 | checkpoint | 3.1.6 - Pipe Installation on Curved Alignments
993176c7-1da7-506b-98fb-7fe03b8c77a4 | note | Detail / Activity - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
8a75ea21-ddab-5c9c-a13a-1efcd7106369 | note | Acceptance / Conformance Criteria - AS Per POP 202
bd6fbfd8-ef63-5e6a-bc8a-16fe25b3b378 | note | Standard / Specification - PS 22.7.1 D
71db1f3f-210e-591d-ab77-5297f18f115b | note | Verifying Document - Visual Inspection / Wastewater line record
5c5802d9-7d97-52a5-8680-f5dd16637424 | note | Testing Quantity Required (based from schedule qtys) - Every Line
a58d9027-ea8e-51c9-9970-5e07a8d9eda2 | note | Verification Activity: Activity - M
9ff1be09-61aa-50c3-84fa-ab31e3d9d1f4 | note | ○ Monitor on Random Basis
58e93ded-44de-5997-b523-edcadad09714 | note | Verification Activity: By - SE
87887334-82ca-4a3e-84ae-d36b69672b4d | checkpoint | 3.2.1 - Flanges
2058549d-f52c-5e6d-99c4-a049dc776a42 | note | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
d3a5169c-01ad-583d-822f-5dc5ab6c63d4 | note | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
b31d2664-7542-50d9-9a9b-e37c7978d99a | note | Standard / Specification - PS 22.7.5
51c24cc4-9674-570c-b24d-7d2fbb256649 | note | Verifying Document - Visual Inspection
4af85927-d398-52e0-9ee7-872007d7be67 | note | Testing Quantity Required (based from schedule qtys) - First flanged joint
daf7aa0b-928f-5196-947f-72cb32757c1e | note | Verification Activity: Activity - HP
362f27aa-d758-5e61-b6b9-d744255eb91a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3b6625d2-f611-559a-b309-a2409fd66d6c | note | Verification Activity: By - ENG
1a183f05-a77f-44ba-8daa-e94233dce801 | signoff | AUTHORITY HOLDPOINT
0ea35940-b246-41f1-a252-d517907e54b2 | checkpoint | 3.2.2 - Bends
c6fa6617-fc1a-5cbd-aad2-5536b4b9ff59 | note | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
5ac2732d-583f-54d6-b330-0de6d8bf7466 | note | ○ Fitting must meets the same PN rating as the adjacent PE 100.
bfbe51cd-36d2-5af6-9529-532b507fc68b | note | ○ Fittings must be suitable for producing the joints shown on the Drawings.
2ceabf2c-696e-5029-9dcb-a784314dc8c8 | note | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
b0bcdcef-f827-5282-ba0e-ac562c6ffbf8 | note | Standard / Specification - PS 22.4.2
3335dd70-9b76-5973-bfee-f94ca631a20e | note | Verifying Document - Visual Inspection
fa9d1ab7-b406-5646-b0cf-73d3d354d6e8 | note | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
86c8107d-0527-552a-8601-1b2468691344 | note | Verification Activity: Activity - H
96c01fdc-7f4b-55e1-9254-89455b34f9db | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
8e18b3c5-5d5e-578f-89d1-925546834eba | note | Verification Activity: By - SE
c68fba1d-f1d3-4f3c-a4ba-02ac5f7726ce | checkpoint | 3.3.1 - Butt-Fusion pre construction weld test
4d51a74a-cabe-5053-affb-a7f2e1baa5cb | note | Detail / Activity - One weld on the most common size of pipes used for the project.
195b8545-0b54-57f6-9706-fbc548df36cb | note | ○ One weld on the thickest wall (highest PN) pipe
fed9789a-ff88-56ba-a967-20bd7ad6d505 | note | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode.
0288af2f-fdd2-5675-bb6e-ce4a89b23885 | note | ○ WMS Report.
2d5fc79c-fe0f-5054-bcac-ad55c3f7a31c | note | Standard / Specification - PS 22.9.6 (a)
c81c34bb-a2d2-5643-b91d-e03c1ac1018d | note | Verifying Document - Visual Inspection
1921a9e1-5c13-501e-ad8d-bdf74bad170a | note | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
a7877d4c-01f3-52ed-bd39-b29101c9e102 | note | Verification Activity: Activity - HP
f7f1558f-8ba6-5005-9fbe-15e4e0f89429 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
3557f036-7e80-5f45-92f7-d07603b39fd2 | note | Verification Activity: By - ENG
c9d6f711-dacc-4e34-a676-d21f6f073cc9 | signoff | AUTHORITY HOLDPOINT
5264fb45-157a-49be-89eb-f5e9f6961051 | checkpoint | 3.3.2 - Butt-Fusion Welding
b7a659ab-9c7c-5bf9-8b0c-d918f3225a0d | note | Detail / Activity - Use only semi-automatic or automatic welding machines.
8cf98727-671d-508e-a8a3-73d7ae22aa15 | note | ○ Maintain a site record for all butt-fusion welds.
b74784b1-47fa-56a9-b1ae-d2a7f5e1ad15 | note | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
258dfff0-d8e4-5354-b2cc-eb3ba182a71f | note | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
f49d3776-049b-5142-831f-9e921b0d0ebf | note | ○ WMS Report
98256989-230f-5f33-8b17-eda107315d9a | note | Standard / Specification - Appendix 22. PS 22.9.4 C
537ab3b7-428c-5a49-b5d1-7a746e890d1b | note | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report.
f0fcebc1-c43e-531a-9d43-03e2284d7e32 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
cccf4169-14da-5e9d-a968-8e62a4a6a03f | note | Verification Activity: Activity - HP
415662c7-616c-558d-930d-d6e3497616ef | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4894d2f5-d762-5c62-9189-b93568a48916 | note | Verification Activity: By - ENG
ee57b4c6-3c6c-49ee-922f-a95fd370ec86 | signoff | AUTHORITY HOLDPOINT
fe66110d-ee83-49e2-be8e-bc4a6be64b37 | checkpoint | 3.3.3 - Butt-Fusion Construction weld test
541feffc-b020-5760-8b3a-468ab865051c | note | Detail / Activity - Test at least two welds from the first 50 welds.
76395f63-4315-5ff1-a4a5-d020abdaf477 | note | ○ One of the welds to be selected by the Engineer for satisfactory result.
2ca1a5bd-e4cd-5035-bc33-30ea41a3f3c4 | note | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
368f5aaf-3cd8-5dec-a7af-9cde2a5d025b | note | Standard / Specification - PS- 22.9.6 (a) (iv)
2276f622-9cea-5230-9b95-15d457aace41 | note | Verifying Document - Test report
aa63c14d-68a4-51d4-90c6-0a230b402348 | note | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
f556a726-7489-5205-b726-4798527dd2cb | note | Verification Activity: Activity - HP
1861fa86-ba8e-5eb4-b182-b85c8e45ab8c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
4753d60f-37a3-5e1d-9d94-a84fb7c0afb9 | note | Verification Activity: By - ENG
7bee8cbf-f7b8-4886-a030-90b960565c26 | signoff | AUTHORITY HOLDPOINT
c4d8da74-1fc8-4702-8e71-1c53025c2c50 | checkpoint | 3.3.4 - Survey
cd3ba98d-4bfd-5ce1-aa76-36b925b77b74 | note | Detail / Activity - Inspection of Pipeline Inverts
f130e06c-a9eb-5a49-9402-083e24f7ba8e | note | Acceptance / Conformance Criteria - Vertical design Setout:
feb6d12c-8944-5af3-bc5f-1a19559cf856 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
6e76ab56-4d04-590e-862e-43fcfd83407c | note | ○ Pipes > 1% grade: +/- 20mm variance
54e7cbe3-ff52-51bf-be32-7420243ebb05 | note | ○ Horizontal design Setout: +/-30mm variance
4777a216-e684-5199-a46a-295d35b50e2d | note | Standard / Specification - PS- 21.7.6 Table 21.15
3afa0fc7-aca0-530e-ab82-a1886e0fefb5 | note | Verifying Document - Survey Data / As-built record
8269c385-f3cb-59aa-825f-45edceac9fb6 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
294697b7-8b99-5b11-8f36-8ff5bcf15c92 | note | Verification Activity: Activity - H
2dc1b142-adaf-5b18-9c8b-3483353c27a3 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
1b1e5c46-dfad-5063-ae1e-55f33e68aa23 | note | Verification Activity: By - SE
e4f764a9-ef79-42c3-a310-d80950739a4f | checkpoint | 3.4.1 - Electrofusion (EF) pre construction weld test
9e111d95-1649-5c7e-8e26-119f78624879 | note | Detail / Activity - Use the designated welding equipment and the approved WMS.
17f4a785-b02b-5180-8fd6-30aa690be4ff | note | ○ On the largest size of PE pipe used in this Contract
ccd41dbd-c0bd-5237-808d-a19fa57b57c4 | note | Acceptance / Conformance Criteria - ISO 21751 (strip-Bend test) or ISO 13954 (Peel-decohesion test)
2f5ea580-5481-5c20-9ebe-49dadd4c9c62 | note | ○ WMS Report
ba205a52-7296-545b-b1d6-0ba2499ab426 | note | Standard / Specification - PS 22.9.6 (b)
5da68782-101d-5d3e-8c57-3a734545f325 | note | Verifying Document - Visual Inspection
d2173e55-9ce8-5a76-bf79-34377bbd38c4 | note | Testing Quantity Required (based from schedule qtys) - One test welds per operative(Welder)
35ab3c8c-67ce-5050-af9c-d0074f19b334 | note | Verification Activity: Activity - HP
45d765c2-8ea4-59ed-bd01-8f0471ff3c2c | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
087a71c7-0a48-502d-99c7-eaa8fdec5f1f | note | Verification Activity: By - ENG
78eeed18-5051-4d13-ada8-feac99f0fa07 | signoff | AUTHORITY HOLDPOINT
f2a7c31e-763f-4797-8b56-291c50f1b99f | checkpoint | 3.4.2 - Electrofusion (EF) Welding
7ef18837-afb1-5bb5-98ea-02e4b9258868 | note | Detail / Activity - Required if Butt fusion welding cannot be perform.
c575f147-8be5-51ac-991a-5fadd4d99ead | note | ○ EF Jointing in accordance with PIPA POP 001.
4d683b36-2d76-5b2c-acb7-7b9d224bfe22 | note | ○ The lead welder or welding supervisor must verify on the site record form.
25f2e7d4-f504-5d32-b6ad-7704fbdfef14 | note | Acceptance / Conformance Criteria - WMS Report
73312eec-00b0-53c5-a2a8-734a0fbdbc7d | note | ○ Checklist (refer to CWP).
fcf8ffbd-ed47-59ac-ba60-e9589fe67f68 | note | Standard / Specification - PS 22.9.5 Appendix 22
e9d55126-8211-56ec-8048-d9fb56e81ecf | note | Verifying Document - Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report.
c996f5a7-e604-56eb-a874-eb791236cc14 | note | Testing Quantity Required (based from schedule qtys) - Every Welding Point
03c7f04f-3946-555f-9c4c-fef0d57eedd1 | note | Verification Activity: Activity - H
f4372999-1ddd-5540-b826-0360d5a2e769 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
6066519b-4270-53b4-94c7-3971a249911d | note | Verification Activity: By - SE
b57e0824-0cb7-4236-b824-615ad984578d | checkpoint | 3.4.3 - Electrofusion (EF) construction weld test
ef201a59-5c53-5c12-b117-857ca02577f1 | note | Detail / Activity - EF weld quality to be maintained.
2a13bbb9-12ae-5d9d-9f96-2d9e8adc1b6a | note | Acceptance / Conformance Criteria - EF coupler and EF saddle testing
08b6bd64-0230-56be-9baf-00e2d4f6785d | note | Standard / Specification - PS- 22.9.6 (b) (iv)
49827065-f3ac-572b-85b9-1ec98aedbd37 | note | Verifying Document - Test report
4fa03908-433a-52d1-b293-e6b5570f2d57 | note | Testing Quantity Required (based from schedule qtys) - 1 in 10 test
31e9b334-5e58-5cea-9fa0-5abe14392368 | note | Verification Activity: Activity - HP
5f0520eb-10e7-5ee2-a79f-3d880df50c36 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5f00cf91-b246-568b-9c88-891b34220701 | note | Verification Activity: By - ENG
439d0609-9a8f-42c7-9e76-ef273d9cb957 | signoff | AUTHORITY HOLDPOINT
b5b8cbb8-fc94-4c45-a8fa-db26b5dd9e0e | checkpoint | 3.4.4 - Survey
add1188d-af85-5248-9ae1-b65b9110ec62 | note | Detail / Activity - Inspection of Pipeline Inverts
f996d8cb-d17a-5946-b4bb-add205bbeb4b | note | Acceptance / Conformance Criteria - Vertical design Setout:
0a6d7885-7c1d-5d17-93bc-7c3d117b1c77 | note | ○ Pipes ≤ 1% grade: +/- 10mm variance
321d1360-b495-56fa-89af-9b7cd62eec0e | note | ○ Pipes > 1% grade: +/- 20mm variance
7097dacd-57a5-5e80-8405-03ab7dbfb06a | note | ○ Horizontal design Setout: +/-30mm variance
87e48dc4-cc9e-52fa-878b-f1ba6df07379 | note | Standard / Specification - PS- 21.7.6 Table 21.15
72a2f83d-f131-5054-b0e3-36ba1a9bffe6 | note | Verifying Document - Survey Data / As-built record
9f479144-df2e-5447-95e8-a1ba2d069560 | note | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
33a3e236-e43d-57d2-a151-578f980f3328 | note | Verification Activity: Activity - H
f0e56d6e-0a7f-5581-b72c-78e933f4817a | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a9abaadc-ecc1-59ed-9b3a-c2d55c9ee9f0 | note | Verification Activity: By - SE
c87e0e3a-5762-4ece-925d-2f2117c3581b | checkpoint | 3.5.1 - Emebment Zone - (Side Haunch Overlay)
2198a488-6d6b-56c9-aee6-f8cd55e68d13 | note | Detail / Activity - Granular Sand backfill Compacted in 200mm Layers.
dee0f174-d44f-5a02-afe4-cd148ab9171a | note | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays.
e859cedf-169f-5d82-86e6-98a7a68d1332 | note | ○ NDM BS to be Carried Out
134871c5-ef49-5bf5-bec5-c47033534939 | note | Acceptance / Conformance Criteria - in 200mm layers.
1a7c4421-2104-56e8-b17c-9604815be328 | note | ○ More than 85% of MDD.
908f7557-81a9-5027-b12b-45666d4378f6 | note | Or
06feef18-6412-5370-81ce-fa9da06b5034 | note | ○ Minimum Compaction- Trafficable 95% MDD and Non-Trafficable 85% MDD
53c3c5b4-ef68-5fea-8fa7-5260daf95eae | note | Standard / Specification - IFC Drawing 0320-1
46a5759e-2443-5aa4-b637-5ccb11958401 | note | Verifying Document - Lab Report / Wastewater line record
fdc03492-962a-57c7-b62d-7b7487fb28a4 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals. 200mm lift.
f786b390-4ff6-5904-b23f-da6f7ab3f81e | note | Verification Activity: Activity - H
b6fdc62c-e07c-51f7-a33d-a2e9ac1ca401 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5548e626-85fb-5f04-90f7-f9906fc78461 | note | Verification Activity: By - SE
91f4d083-a60d-4c93-9311-e407d256dd95 | checkpoint | 3.5.2 - Pipe Markers
8521c1fb-9b3a-5f50-9dcd-63b2dadddbce | note | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
32e02472-0aa7-5212-8115-71faf3cedc24 | note | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
192e7d1f-cb05-536a-acb8-a17f9ac927a7 | note | Acceptance / Conformance Criteria - AS Per Drawings.
f9adb7ac-16e7-54fd-ac8a-fe453a212b9a | note | Standard / Specification - PS 22.7.3 a
8b2c8f1c-0a31-582f-9873-5dfd09242372 | note | Verifying Document - Visual Inspection / Wastewater line record
bc8e769e-49d5-52fc-84f9-0f3278af8e56 | note | Testing Quantity Required (based from schedule qtys) - Every Line
2e026beb-e2bd-523b-a424-f240121cc1a5 | note | Verification Activity: Activity - H
0854144f-fa8b-5c83-bcf2-0fa684aea2b1 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
f338c095-6574-552c-9152-d237f2e22187 | note | Verification Activity: By - SE
0e38e2f9-1a38-426b-8291-96534cf2c17d | checkpoint | 3.5.3 - Backfill Compaction Testing
dd68ea1f-e65f-5081-b95e-8256a1f9f71b | note | Detail / Activity - GAP65/AP65/LRAP65 Backfill Compacted in 200mm Layers.
602e875e-181d-51ea-9136-5d87a973f7fc | note | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
91f2e973-5b9d-5ed7-a9ef-c398add0a106 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers.
3a81fedf-b846-5b8d-9fee-ea6cf9f8d4b1 | note | ○ Testing to be completed on maximum 200mm lifts of backfill.
8fed19d1-ada4-5f12-aeb2-dec5771f3f5b | note | ○ LRAP65 - achive 90% NDM on Grassed Area and 95% NDM on Shared and Carriageway.
307b1a4e-3f0e-5087-8454-45f556580c1d | note | Standard / Specification - PS- 22.13.5 NDM Standard 25832, NZS 4402 Test 4.1.3
239303ba-114c-53c0-89f7-77a979a03d5b | note | Verifying Document - Lab Report / Wastewater line record
fa4a4a8b-e937-55e7-99f2-23b8abe02c5e | note | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 20m evenly spaced intervals..
d746177d-f176-545c-9064-521ba7f52021 | note | Verification Activity: Activity - H
faedee6d-52b1-5e9b-b838-6dc9e2c43389 | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
5f4258be-f723-5604-8840-e92913c39bf3 | note | Verification Activity: By - SE
0e459007-a1a8-428f-bfdb-73f074b5711d | checkpoint | 3.6.1 - Pipe Inspection
dfbee3a6-1a37-56ed-97e3-dbac83579952 | note | Detail / Activity - Inspection of Drainage line
f485c883-e273-5e6a-8277-1e19f3cbd222 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
fb4629ff-4e8f-5def-b2c5-8ecacef1f38a | note | Standard / Specification - Internal
d924abfb-6a1d-53f0-9d52-528e77c06fa5 | note | Verifying Document - Wastewater line record
09cef8a5-5d23-5a5d-a638-343e834ca6f4 | note | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
1f0c034a-4d52-516e-a951-b087af1ccfbd | note | Verification Activity: Activity - I
77635919-f6a5-5f3f-a3af-7f1136e67a19 | note | ○ Formal inspection activity to be undertaken and recorded.
55486e2f-2fb3-5faf-89e8-7b5bfe372762 | note | Verification Activity: By - SE
30d7eee6-33ae-48f8-b39c-438bc320d529 | checkpoint | 3.7.1 - Pressure Acceptance Testing
3b06cb80-94a1-5055-b67d-e0f897f48c7d | note | Detail / Activity - Backfill/cover with embedment before testing
591c2940-1220-5107-a948-25f9747265f4 | note | ○ End caps in place, provision for filling the pipeline and bleeding air.
34e10bf0-4906-50a1-8c2c-6fe80250f0d8 | note | Acceptance / Conformance Criteria - Wastewater Rising Main Pipelines – 800kPa
c65f5295-0eb2-57c1-a3a1-9142a519a1c3 | note | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
7969fbf6-135c-5bef-8294-b5866b5463e1 | note | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
c2f42f87-2fe8-5610-a68c-bff41cb5752e | note | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
3175f7a9-619c-5df8-bead-79743478a0de | note | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
95276c5d-4fb7-5e79-95ed-a2eb7ec57f47 | note | Verification Activity: Activity - HP
575f9f87-1162-525c-a5b7-6555b7140a0b | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
a6117092-aade-5896-a2c7-94295a8d889d | note | Verification Activity: By - ENG
45e79789-15df-4382-b27e-07fd8b2df1bd | signoff | AUTHORITY HOLDPOINT
a69d486f-b42e-4d22-aaaf-49b6fa324777 | section | SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
20078e99-75b4-4ec6-88b6-27e902fe3139 | checkpoint | 4.1.1 - Survey As-Builts
ad780205-4068-5d54-9d65-482824118cf1 | note | Detail / Activity - Quality Check on Nee pipeline and structure based on the tolerances in RITS
4ff1db64-9b94-55b1-83fe-0a0e70545fc6 | note | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
11bb7a13-6d62-597d-ae32-1f4b7b5b1f52 | note | Standard / Specification - Project Specifications
4bbb8d57-ab12-5ad5-8927-76c2da7568c9 | note | Verifying Document - Red pen markup only
8be1b147-8e24-5f65-bea2-ad83f2e64732 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
4f9cc613-942d-5804-ad3c-6082f9de8b62 | note | Verification Activity: Activity - H
ea2fae57-d1a3-55e9-a7e8-4eff479349af | note | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
ff85eaf6-0b21-5580-b910-b7926f346902 | note | Verification Activity: By - SE
73f818c1-121d-439a-b7c9-d754294a6c57 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
321f5209-28e1-533c-8039-e64de6236244 | textbox | Contractor's Rep Name:
dae81756-a607-5b4c-a60c-4c1e72f2e99b | textbox | Engineer's Rep. Name:
c2520112-335c-50b4-96ed-303b8d315493 | date | Date:
92377e05-430d-46ee-be23-996d57fa68f6 | signoff | Add Signature
f53db032-4ab8-40bc-bc97-c7cfbbbc69dc | checklist | DN1210-012 ITP Utilities Rev 1 | itp | DN1210-012 ITP Utilities Rev 1
8e916c0c-5850-4ca0-aad3-d295c9619403 | section | 1. PRE-CONSTRUCTION (P&G / ESTABLISHMENT) - 1.1 GENERAL
4a66bb89-4063-48d7-ba64-2c8f3122a315 | checkpoint | 1.1.1 - Trench Profile
0bcb6d66-7e1e-522d-ba87-be9b0db6f981 | note | Detail - Tolerance of +/- 100 mm of the planned horizontal alignment and the maximum deviation shall be 1 in 20 in both the horizontal and vertical planes.
67dc9f3e-9171-50cf-b1b6-87fec1d0c3a6 | note | Acceptance / Conformance Criteria - Survey Set out
dd78f3e2-e03d-5227-a645-a1acee11c522 | note | Standard / Specification - PS 25.13.2 a (1)
40ba78fc-9e73-52b2-a54a-f9029e66caf3 | note | Verifying Document - Survey Data
20d912dd-83fb-52e2-b2fc-f85bf0271bb6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
9abec1dd-c417-52ff-a7dd-f5c2e029111e | note | Verification Activity - H
f2dfcbc7-c870-5849-aeca-006cd2d2d0c7 | note | By - ENG
d7f561a4-3e32-4b1a-9982-23753a93830f | signoff | AUTHORITY HOLDPOINT
25425128-8231-4e6d-aa60-7136a71593a6 | checkpoint | 1.1.2 - Underground Services
283dd870-0601-52e4-855c-ca1a319e14fe | note | Detail - Pothole all services within traffic management prior to commencement of trenching. Accurately record the location and reduced level of each service and forward Engineer.
e9093ccf-6692-5b86-aa60-478a2d8764e6 | note | Acceptance / Conformance Criteria - Survey Data/Existing utilities Drawings
c178e828-e156-5366-98fb-7c2b3ee5879b | note | Standard / Specification - Appendix V
afa0302e-7ad5-5f89-980f-717933ab154f | note | Verifying Document - Survey Data
999d0726-1342-5992-bf08-3221e0b8ecb8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
5195c12a-66bf-5ab3-be01-01228c27e530 | note | Verification Activity - H
917c7757-35c5-53a4-b610-1d5f602e77cd | note | By - PE/SE
af7a8933-9e5a-48a0-a05a-129fd15c5cc9 | signoff | AUTHORITY HOLDPOINT
39a6b05e-30a2-4740-ac86-41f6215e698b | section | 2. MATERIAL, PERSONNEL & THIRD PARTY APPROVAL - 2.1 MATERIAL TESTING
486cc648-29a7-46e8-87c0-82a4976fb1ca | checkpoint | 2.1.1 - Bedding and Overlay Material: Clean Imported Sand or SAP 7
4c6a5b85-12dc-57af-9f84-eb844b1a72b4 | note | Detail - Material grading:PSD
81d99318-3953-50b0-87a3-553626258b67 | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
842b2c18-b12a-55f1-ac5d-21652cdca29f | note | Standard / Specification - PS 25.13.2 g) & h)
110948ae-0e2c-51af-a67d-1197efab1263 | note | Verifying Document - Delivery Dockets/Material Certification
6d35a092-9e71-53f3-8366-f69dd71548b1 | note | Testing Quantity Required (based from schedule qtys) - NA
5b73eeea-f3c1-562c-addc-9e13da30056b | note | Verification Activity - HP
9a700353-5f28-57db-a746-62af3930586e | note | By - ENG
b1e0dc8e-de0b-4e74-a9aa-38a5ebc23b8a | signoff | AUTHORITY HOLDPOINT
44d83bac-76f3-42c4-8c5e-39b2257c0cec | checkpoint | 2.1.2 - Materials: GAP65-Backfill Material
23b3c69e-61c3-5c8d-b7c9-27e3a083e564 | note | Detail - Material grading:PSD
69982c10-640a-5c1d-b2c2-6349b69f27c9 | note | Acceptance / Conformance Criteria - Stockpile size over 4000m3 PS- 16.5.11 for GAP65
0d2e1224-6bdf-544e-8baa-647e3abc8c29 | note | Standard / Specification - PS-21.7.2 Table 21.9
89926f4d-431c-5a36-a4e7-5be287cc0f9a | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
538f58d9-8e96-5832-bd96-e69312922f9f | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 1000m3
582b6634-6b50-520c-8e89-1d5f35c4e7b7 | note | Verification Activity - HP
9569ed76-8c8e-598b-ac62-26995c7de055 | note | By - ENG
63d81330-269f-4298-9075-db67765b857e | signoff | AUTHORITY HOLDPOINT
0b6e92e6-b517-4dab-b57d-d9abacf69d0b | checkpoint | 2.1.3 - Materials: GAP65-Backfill Material
dead2c3d-8425-5ced-9f1d-c49fef0cedf6 | note | Detail - Weathering index:
10ac7968-b8ea-5b19-8b95-0f9febb656a2 | note | Acceptance / Conformance Criteria - AA to CA
f554ac44-d467-5ccc-847c-8f1390459f01 | note | Standard / Specification - PS-21.7.2 Table 21.9
987d8f4e-3f75-5e58-83e8-8420be2644fd | note | Verifying Document - Lab Test Report NZS 4407.3.11
8b7fa9c2-a910-5cc0-bdd6-f7af3e21259d | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
89b237ec-4d43-5544-857e-dccdc5cffbda | note | Verification Activity - HP
5eaf02df-d9ca-5f5a-8fa5-c343b8ec9cfc | note | By - ENG
464c66bc-6468-4260-b978-70b3310b1037 | signoff | AUTHORITY HOLDPOINT
09ef89c4-2afa-4d83-9697-447334c2113f | checkpoint | 2.1.4 - Materials: GAP65-Backfill Material
67aaf769-fcec-552c-9ed7-bf1a39112466 | note | Detail - Crushing Resistance
ffc49956-2e6a-5dd3-a304-40ece59ef931 | note | Acceptance / Conformance Criteria - >100KN
f76a0622-fd6e-5455-847e-d508fcacedbc | note | Standard / Specification - PS-21.7.2 Table 21.9
1a5aa289-6eaf-59a0-9437-a111b759d478 | note | Verifying Document - Lab Test Report NZS 4407.3.10
92ed5aba-43ea-56b8-a774-1a2293235f5c | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
b14c597e-8b01-5272-8ddb-301b10feb6bb | note | Verification Activity - HP
b5d26f2d-714e-521b-9a61-469d0abb98d8 | note | By - ENG
006c000e-da74-49b5-97af-9a1160001773 | signoff | AUTHORITY HOLDPOINT
0e80def9-0026-4998-a4ca-cde2b81a47e9 | checkpoint | 2.1.5 - Materials Approvals
a56af989-ca4e-5c53-a433-cd450e47f5e5 | note | Detail - All works and materials are to comply with the National Code of Practice for Utilities Operators' Access to Transport Corridors, and Individual Utility Providers Requirements
8895bb7e-c427-5901-a5aa-07751a808d3a | note | Acceptance / Conformance Criteria - Prior to Commencement and throughout construction
fdbe7567-dbbc-519b-80f5-59a9d0d58c39 | note | Standard / Specification - Project Specifications
5c389606-b39f-5d8e-8d26-163bf0f5146f | note | Verifying Document - Utilities Providers Approval/Material Certification /Delivery Dockets
3ddf2253-d8cc-5de2-81a4-28ced242fc94 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
ef51aec0-3acf-5b8c-814d-5627875e5648 | note | Verification Activity - H
1af29b68-624c-5b9b-b62a-c702c9fce0fe | note | By - SE
4ece6099-0f01-4b16-bde4-65c5945709fa | signoff | AUTHORITY HOLDPOINT
83f97cbe-b43e-4cbc-bc3b-729ae9f6c33e | section | 2.2 MATERIAL DELIVERY
ee48925a-b035-46ef-97b4-087f4ef5eabb | checkpoint | 2.2.1 - Pipe and fittings. Ducts
7db8345a-ba3e-58a1-ae6b-4d5f1a4d4028 | note | Detail - Duct Pipes shall be of the size, material and class nominated in Drawings. Ducts shall be high impact uPVC or High-Density Polyethylene (HDPE). Duct colours shall be to local authorities requirements. Duct colours for the different Utility Structures must be in accordance with the guidelines.
333fbb3f-f90e-5faa-ae0e-3ca9b54ed4ef | note | Acceptance / Conformance Criteria - Comply with Project Specifications
625baae0-854c-5ffd-9828-2611affb4ecb | note | Standard / Specification - PS 25.13.6 b)
51f875eb-7058-5199-9123-ccc9ee657e66 | note | Verifying Document - Delivery Dockets/Material Certification
497e2f66-3f6d-5599-b0d5-be28065d2a77 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5aa16fdc-5187-5a70-a7e8-62d24fd18fa9 | note | Verification Activity - H
78bc25dd-85bf-5421-be72-73f158f43e7c | note | By - SE
f97a8dfd-6853-5b80-b674-22bd03bdd93b | note | Comments / Closeout Details - Duct details will be instructed by service providers.
30b72118-4b36-4dd5-91c9-00414bc65ae7 | signoff | AUTHORITY HOLDPOINT
95fc4281-439d-4b9a-bfa7-e0f188d3b25a | checkpoint | 2.2.2 - Bedding material
349f055c-40d5-51ac-b330-812b78a35726 | note | Detail - Clean Imported Sand or SAP 7
52d5971e-85d0-5bd6-a4bf-6ae513e08feb | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
ac7553e4-090f-598d-93fd-a88a790432ad | note | Standard / Specification - PS 25.13.2 g) & h) & 25.13.7 b) ii
c7246019-cc11-595a-a5c5-ed534863d820 | note | Verifying Document - Delivery Dockets/Material Certification
da3558cd-d367-5395-806d-f6d08fba0c9f | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
13520fea-8f9a-58bd-94f0-b9d17b4cee98 | note | Verification Activity - H
bd332cbf-5d6b-5170-a45e-98515475dc80 | note | By - SE
e29ceea3-5f67-41be-9f64-7ba1ea194895 | signoff | AUTHORITY HOLDPOINT
d5398cc0-f040-422b-8e23-1339dfa1e2a1 | checkpoint | 2.2.3 - Backfill Material
775a8ca9-30b0-5457-92f9-21908aa5712d | note | Detail - Under roads, driveways and footpath - refer to pavement section for appropriate materials and layer thickness. Under berm or grass areas - site Won materials to be approved by Engineer or GAP65 to be used if site material does not meet Specs
b2e368c6-bc23-5da4-a48d-978978955761 | note | Acceptance / Conformance Criteria - Comply with Project Specifications
dc270cb9-cd17-59bd-803a-59e13c5cd7f6 | note | Standard / Specification - PS 25.13.2 h) i to iii & 25.13.4 a)
05583998-e4ea-505c-906c-b3681ae0bfd5 | note | Verifying Document - Delivery Dockets/Lab Test reports
b3465e16-1c11-5103-b922-723dc70f41a1 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
1524ee9f-d13e-5e50-87c6-a5e81f8459d0 | note | Verification Activity - H
9ba41559-439e-5d84-8fd8-cd22bd752862 | note | By - SE
7245ad1a-3400-43c7-aa67-5b628124c14c | signoff | AUTHORITY HOLDPOINT
a4d7cdb7-b059-4497-a17f-f892ba5d8756 | checkpoint | 2.2.4 - Pits Covers
b54dfeb9-8272-5c6a-9c91-dbe596f03cfd | note | Detail - Jointing and pulling pits shall have slip resistant surfaces.
6e129f47-6b34-5471-a0c8-52ff04f7831c | note | Acceptance / Conformance Criteria - Class A-10Kn. Class B- 80Kn. Class C- 150Kn. Class D-120KN.
f10b6ad6-3c89-5058-ba2a-5ab374cde17a | note | Standard / Specification - PS 25.13.6 c) AS/NZS 3661-1- 1993.
febba2d3-986d-5831-b1b0-a89896aa2976 | note | Verifying Document - Material Certifications. Delivery Dockets
8632adbf-8bac-5027-840e-de9d33e4f89b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
b523dd59-d9ee-5824-bcb7-d9730aa34ecf | note | Verification Activity - H
3c22d34c-297b-55df-9dc8-1e84a24caef9 | note | By - SE
12320b3f-a7f1-48e9-acfe-43a50c1746ea | signoff | AUTHORITY HOLDPOINT
2e80cf9e-cce2-4de5-a526-19b5f0b1c990 | section | 3. CONSTRUCTION ACTIVITY - 3.1
4473bcd7-a7bd-4e0a-b8c6-5007ed250edc | checkpoint | 3.1.1 - Trench Excavation
881014cb-a527-53b7-bee5-f8672fe67d26 | note | Detail - To be excavated to within a tolerance. Not more than 100 metres of trench associated with each site shall remain open at one time.
3e77300b-24e3-57d9-8d0c-54d09709df76 | note | Acceptance / Conformance Criteria - #ERROR!
12365ca8-56e6-5f1a-acee-ef8499fd5229 | note | Standard / Specification - PS 25.13.2 a) i
e5d1fb7e-67ac-59a5-9234-fe1d48f36ff3 | note | Verifying Document - Survey
39daa345-e591-50a6-9823-ea6a4c1e5c31 | note | Testing Quantity Required (based from schedule qtys) - Every time
6b035129-a403-50e6-a124-eafc4b6f86b9 | note | Verification Activity - M
b8e83467-db66-5745-9ff7-de536dd190a8 | note | By - SE
c560f64e-3631-49b4-b19d-a3becd6f68a3 | checkpoint | 3.1.2 - Unsuitable Materials
788da501-45e1-5204-b133-312faf493b0b | note | Detail - All confirmed unsuitable material shall be excavated down to suitable materials.
3b5a9fdc-7571-5cb9-8c38-a2295f4015fa | note | Acceptance / Conformance Criteria - Dig Down to Get Suitable Materials or get Engineers Approval.
8d8e26ee-a00d-5e92-ad99-5ebf580c87e6 | note | Standard / Specification - PS 25.13.2 b) ii
a32f42d3-0de8-5a1a-a4e0-0f297dd3fd71 | note | Verifying Document - Visual
eacc48f2-a624-5251-8847-87e6cddcb3cb | note | Testing Quantity Required (based from schedule qtys) - Every time
9d2893a1-8ed0-54ea-a3ad-ea1451cc7677 | note | Verification Activity - M
50c89cc8-28e1-5b9a-8865-40337e15e174 | note | By - SE
4a681e24-b46a-4441-9bd6-7e42252ebb01 | checkpoint | 3.1.3 - Foundation Compliance
9f3f9957-5265-56a7-8e28-baf2e6f1f334 | note | Detail - It shall be de-watered prior to installation of bedding material. If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
b4f5bf4b-5651-5370-9694-0525360b32f1 | note | Acceptance / Conformance Criteria - 50mm granular layer shall be laid and compacted before the bedding layer is laid.
70967d19-82ff-5029-93ac-e78b1e927194 | note | Standard / Specification - PS 25.13.2 c) and g)
bb29f6e5-6443-5910-892c-ab0fdd680881 | note | Verifying Document - Visual Inspection
d7b30555-ed23-54f5-971d-8f7663e42d70 | note | Testing Quantity Required (based from schedule qtys) - Every time
7f197952-ec14-51dd-a602-b43e97854998 | note | Verification Activity - M
f2e6e66d-882f-50c4-8a0e-428f0e065146 | note | By - SE
49179d62-20cd-451d-9cc5-4bdc9f49dc68 | checkpoint | 3.1.4 - Bedding
8614c5cc-5665-5fa3-ab79-3f8940785aa5 | note | Detail - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
0736aece-5d03-503d-8bd2-dc15e71dfe33 | note | Acceptance / Conformance Criteria - Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
119d2e5e-a84d-5440-9563-82cc8c9de3ac | note | Standard / Specification - PS 25.13.2 g)
f566dbf0-0c84-5db8-aa23-db97f0e0357e | note | Verifying Document - Visual Inspection
95c8247d-bef3-517d-afe5-71c62c023bcb | note | Testing Quantity Required (based from schedule qtys) - Every time
cf88f922-c00b-5c77-94ae-58ea7117c49b | note | Verification Activity - M
7af9af8b-6269-5b6b-9749-5e37f31ca339 | note | By - SE
78830cf9-10a2-4c5e-8550-200be233c777 | checkpoint | 3.1.5 - Bedding (Encased in concrete)
e2a882fc-91f0-5b73-ac67-4727ea84b5b1 | note | Detail - Concrete Bedding to be placed. Compressive strength of concrete used no less than 20MPa
e92735c5-112e-5f6a-ab41-56137c2c3ed8 | note | Acceptance / Conformance Criteria - 50mm
c925fb4c-df71-59d9-8612-f84c6aee1fad | note | Standard / Specification - PS 25.13.7 c)
aa502856-7f55-501a-8b7a-1cc391135779 | note | Verifying Document - Visual Inspection
15aa5f42-8a9c-5efd-8d93-0ae20c77a890 | note | Testing Quantity Required (based from schedule qtys) - Every time
99a33773-5ba8-5074-9c2e-001402773f08 | note | Verification Activity - M
b3c964ab-9694-5169-83b2-96437b72a933 | note | By - SE
dfc31b15-66cf-447e-b61f-2a1b0891b1c2 | checkpoint | 3.1.6 - Installation of Ducts
5b79e591-f8e5-5827-adaa-be34a18a3b89 | note | Detail - If more than 2 ducts are being placed.
a223bcd1-0b1c-5e32-beba-bb2d6eb87ff5 | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
deeb4f1c-8275-5660-ad84-a68effb8da42 | note | Standard / Specification - PS 25.13.7 b) iii
d86431aa-c70a-50be-a1cf-a63445223e1f | note | Verifying Document - Visual Inspection
24b5f92a-0d49-5a68-85cd-e4c7a023a435 | note | Testing Quantity Required (based from schedule qtys) - Everytime
4d7275e2-defa-5308-9cdc-0c13ffff8e33 | note | Verification Activity - M
4c27abcb-e832-5ed4-8489-e71afe910f15 | note | By - SE
a05dd518-a7e7-4a26-9f83-a8f2a44879cd | checkpoint | 3.1.7 - Draw Wires
5edb7e75-29a5-5246-b153-3b8dadcbedb7 | note | Detail - A draw wire shall be installed in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting.
9d659fb7-8cb7-5a1b-be14-7d781f814ada | note | Acceptance / Conformance Criteria - Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load. ≥20 years design life. The ends of draw wires shall be made fast within the pits and be secured to the duct plugs.
5c218fd5-e8d2-540a-9a00-2af658da7a07 | note | Standard / Specification - PS 25.13.7 e) ii to iv
f066a145-aaea-5c8d-a3ab-5f5869ec9dda | note | Verifying Document - Visual Inspection
8f57c5b6-de05-5c56-a867-4cffa95efeb7 | note | Testing Quantity Required (based from schedule qtys) - Every time
752d02da-2b6f-5438-b36b-7effcef8df65 | note | Verification Activity - M
d77a631e-2c4a-503f-aae3-306c4c26277e | note | By - SE
9d07cbba-54d9-488f-aaaa-b8959d513f76 | checkpoint | 3.1.8 - Caps
1bfdfd82-7fe6-5e68-9de7-b048819822ff | note | Detail - All duct ends shall be capped
ae5add1e-5d83-53f5-8d27-724134035025 | note | Acceptance / Conformance Criteria - Capped ducts
a3d7f628-012e-5ea4-b7c4-6f7f0f8c09e4 | note | Standard / Specification - PS 25.13.7 e) v
1b0dc8a4-1927-5f71-b1f5-72771fe7de73 | note | Verifying Document - Visual Inspection
387d27f1-087e-5ca4-aeaf-1624f5a7c315 | note | Testing Quantity Required (based from schedule qtys) - Every time
393cf3ed-7340-5bb4-9068-e6e079e4f5c2 | note | Verification Activity - M
57c7c6ec-efd8-5ea6-bda5-8e472b70ed9f | note | By - SE
b17ea8f5-9cdb-4403-a4d8-4c5f65d3300c | checkpoint | 3.1.9 - Warning Tape
fffcaef5-8628-5f0b-974b-849c726c921d | note | Detail - Warning tape to be placed above services.
51439d3b-16f0-5217-8a6f-2a24ba22fa89 | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the duct
e9c43411-659c-5c77-b569-388644d1a8ed | note | Standard / Specification - PS 25.13.7 b) iii & f)
fe08ade8-e822-5587-8394-f5dcc7688f8f | note | Verifying Document - Visual Inspection
00f192cc-e9dd-52d7-a66c-f6a410d5c154 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
66839ed7-44f6-50fe-a63f-4fcd43402bea | note | Verification Activity - M
5924d14b-7652-5653-ab92-1041568205ed | note | By - SE
e306fc1c-d395-46d7-a477-4d04ef77d232 | checkpoint | 3.1.10 - Overlay
c96c786d-a3ac-538f-bd2f-f7a7a9396209 | note | Detail - Clean Imported Sand or SAP 7 to be placed and compacted
bc7ad0de-793b-56a0-b539-d517e3b9bc52 | note | Acceptance / Conformance Criteria - 100mm thick Clean Imported Sand or SAP 7
a891bdad-70a0-52b3-aacc-ffe42aceab7b | note | Standard / Specification - PS 25.13.7 b) ii
1dd21f08-8d27-5bfb-b9e8-6a9f25e00417 | note | Verifying Document - Visual Inspection
127845bd-db3a-5def-b2b7-0a3acf4b4686 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
d556104c-2e88-5f64-9ae2-9701f3e1b8a3 | note | Verification Activity - M
b9d5c2fd-2a2a-5863-8989-b22e6624b3e7 | note | By - SE
3f3429b5-7132-4adb-b746-c9a7683a7539 | checkpoint | 3.1.11 - Overlay (Concrete Encased Ducts)
1f4429d8-f8a2-5bac-a86d-0813b9fde853 | note | Detail - Overlay and surroundings to be placed with concrete.
0b70a8f8-2690-5c27-8c4c-3c4c4fd010c2 | note | Acceptance / Conformance Criteria - 100mm thick on top of Ducts 50mm thick side of the Ducts
f9675d8c-79e1-56da-a27d-b43646e236b3 | note | Standard / Specification - PS 25.13.7 c)
010b256a-1588-58ba-9c39-62df9f4f7179 | note | Verifying Document - Visual Inspection
b34dbc84-d497-5c86-b2ce-8799a8d0f168 | note | Testing Quantity Required (based from schedule qtys) - Every time
d597156a-ed6b-5674-85c6-119be7aa2d64 | note | Verification Activity - M
236de8df-23be-5469-b74e-c361c55f82d8 | note | By - SE
0bae926a-9ce6-4858-9d51-9b2f9caa194c | checkpoint | 3.1.12 - Overlay Testing (Concrete Encased)
35e54c37-e0b1-598a-be0e-b1e2bb10136f | note | Detail - Placed Concrete needs to meet the strength Criteria
b074a358-5034-527a-bf77-2f7fbd297b7a | note | Acceptance / Conformance Criteria - >20 MPA
fa29de66-7375-50c6-8352-5c130ce9b7b3 | note | Standard / Specification - PS 25.13.7 c)
b0012925-f4cc-5a23-b915-ab5034f37dbe | note | Verifying Document - Concrete Dockets
91ed986f-a827-54fe-9a6b-7600723d8aa7 | note | Testing Quantity Required (based from schedule qtys) - Every time
9aacd20f-1f0f-508c-b1b7-468d26f1adbc | note | Verification Activity - H
90a5508c-f605-5494-9626-9395b1c0b5a6 | note | By - SE
0491c173-2aab-4592-86c2-67fcbec243f9 | signoff | AUTHORITY HOLDPOINT
5b6c2158-a99a-4448-ab3e-92552e8438d9 | checkpoint | 3.1.13 - Backfill
5bf88ea3-a40c-5c85-9bc5-bd9bc4a1e4e6 | note | Detail - GAP65 to be used if site material is not approved. NDM Testing to be carried out.
d007f31b-e980-5f51-b330-b26ba3ad43ae | note | Acceptance / Conformance Criteria - NDM Test every 250mm compacted layer Min 92% compaction rate and Average of 95%.
d72fe4f3-f5d8-5c87-ba13-19390696dae7 | note | Standard / Specification - PS 25.13.10 a) modified
b5333357-30a1-5679-9e39-f6a426589629 | note | Verifying Document - Lab report.
053515aa-9b3b-50c0-bfb4-56f808ca9c52 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
682f58e3-a6cd-56d3-ae35-8208fb6bbe45 | note | Verification Activity - H
3e64b478-e791-5aab-9131-020ba8bddd83 | note | By - SE
f4cf8649-25a9-4847-814e-28f6d264bf5b | signoff | AUTHORITY HOLDPOINT
aee89273-de10-42e4-89e7-889fa4ef10d3 | checkpoint | 3.1.14 - Pit Installation Location
78c4648b-49e0-5f28-8583-31e1f07bcca5 | note | Detail - Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid .
bfb37dbb-602a-54ce-865a-5f9bc9a9edc0 | note | Acceptance / Conformance Criteria - Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas. When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side. When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side.
1835a7c4-faa8-5498-b21a-52a635aa2845 | note | Standard / Specification - PS 25.13.8 a)
0708013d-51a8-535c-bd10-3d6f229329d2 | note | Verifying Document - Visual Inspection
950eab39-7f6f-598c-b4bc-b438a93cd9a9 | note | Testing Quantity Required (based from schedule qtys) - Every time
7c294134-4f12-5c05-a658-a9c7c627ad90 | note | Verification Activity - H
3f51bcd6-f532-5373-99ff-edace48712db | note | By - SE
b17ed789-fce9-5f0b-af6a-f65804704759 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
b30154a2-27cf-4399-9ebd-8961bb518b47 | signoff | AUTHORITY HOLDPOINT
4fede5a1-b426-4107-93fe-fbd3a4824ffd | checkpoint | 3.1.15 - Pit Installation Bedding
4ba50b52-7982-5304-a05b-b5ece97d1dda | note | Detail - Bedding with 150mm compacted GAP20 covered with 20mm compacted sand
f714ef28-6d1a-5fe8-b6e0-c8594a9f683b | note | Acceptance / Conformance Criteria - 150mm GAP20 covered with 20mm Sand
88a7d06c-e1cd-5f91-b95c-78a49a4d9b81 | note | Standard / Specification - PS 25.13.8 d)
f3588442-3583-5377-886f-1334bf1a0099 | note | Verifying Document - Visual Inspection
4a69ed86-2acf-5fb1-ba3b-a28f9a65b3be | note | Testing Quantity Required (based from schedule qtys) - Every time
9f492a93-7b7f-5b2c-bb98-924386c86df8 | note | Verification Activity - H
a4bd4db7-0e1e-51c1-b511-0cf4fb01e48f | note | By - SE
cdd9bd87-4c5e-595c-bae4-1b37f5494cab | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
0bd6e6a0-05f2-41ed-8cf5-802339320a6a | signoff | AUTHORITY HOLDPOINT
fe4a52eb-50ec-46b2-829a-261874d7888e | checkpoint | 3.1.16 - Pit Installation Backfilling
7d489dc7-5bbc-5fb4-9b31-a0f8163f708e | note | Detail - Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts.
500e8173-6802-5b17-a562-f5da50056f90 | note | Acceptance / Conformance Criteria - Min 92% compaction rate and Average of 95%.
ef7d94e5-4ee1-5d47-89e9-4f90d2138b3b | note | Standard / Specification - PS 25.13.10 a) modified
3e39b019-1e19-5ace-9f61-521efd6d31db | note | Verifying Document - Visual Inspection
72261735-3e57-5fe8-98e5-1f9fe9c01b44 | note | Testing Quantity Required (based from schedule qtys) - Every time
b747e77b-8f12-5546-96fd-5bdbf812d01f | note | Verification Activity - H
301bcfe1-402b-5b92-bc23-86c8a3fb4796 | note | By - SE
effe1658-db19-571c-b1eb-3597f1a6ecb6 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
81bc6170-8c9c-45f0-b620-12e1089e96ca | signoff | AUTHORITY HOLDPOINT
a1333581-120a-45d8-9b00-bb9c191658e9 | checkpoint | 3.1.17 - Pit Installation Clean up
cea66dc3-485e-5822-8e9f-c030703f0300 | note | Detail - Clean out all pit after completion of the work
ba3186df-c924-5b82-ac04-b2f5eae40ea4 | note | Acceptance / Conformance Criteria - Pit are free of dirty, mud,water and foreign materials
4a67d1d0-2cf3-5de9-aca4-16a4e0882ed1 | note | Standard / Specification - PS 25.13.8 e)
42dd3885-0376-5ec5-9b6d-c0db556cf49d | note | Verifying Document - Visual Inspection
bcdb6a29-93e7-5635-ac42-4cf1cfdf82ef | note | Testing Quantity Required (based from schedule qtys) - Every time
01606bd5-cb4b-5683-ba2d-65dbe816a496 | note | Verification Activity - M
c7db4af7-46f8-560c-8b92-e1d42d0b4448 | note | By - SE
4b3f379c-f817-5f86-b89e-9105a8b52a80 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator will clean the pit.
c508a466-171c-4f79-875c-c23e6a410c2f | checkpoint | 3.1.18 - Survey As Built
f986c5ac-7748-5e6b-b32b-c2a181dade03 | note | Detail - As Built every ducts joint before backfill
f9fbcc29-98d5-562e-84e9-57d1f7357dcf | note | Acceptance / Conformance Criteria - Completed as per drawings
108777ac-97dd-5670-b2fd-aa1ebb5ff775 | note | Standard / Specification - Standard Practise
c091fbf0-ef67-52e4-a28d-f14313c9f7ef | note | Verifying Document - Survey
449f69b7-8db5-5180-9127-5cd276569e69 | note | Testing Quantity Required (based from schedule qtys) - on going
0542d6c1-82c9-55fd-9307-73923cbeb027 | note | By - PE
8684bf06-73a7-4869-a78a-feab8acbd2f0 | section | 4. POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - 4.1 AS-BUILTS
2af294bc-bf87-484b-989f-db926cf70510 | checkpoint | 4.1.1 - Survey As-Builts
53cf4a25-16e2-5051-b5db-eb5ec3759817 | note | Detail - Quality Check on New Works based on the tolerances in RITS
83de8240-0fb0-5adb-8cdb-1750f0103661 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
b9ffad88-9cb4-57f8-b1b9-5dedfdde3f02 | note | Standard / Specification - PS-21.7.7
bbed9c01-fa35-530b-ab40-200efdd164d8 | note | Verifying Document - Red pen markup only
313a5680-5efb-513d-9f2e-dcdbdfe71f03 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
e4c858d1-5129-5530-baed-d20d31d20be2 | note | Verification Activity - H
9394f156-0b56-5a84-8b84-7ffc7787352e | note | By - SE
a072cf05-9802-47ac-9772-7070c5ba6526 | signoff | AUTHORITY HOLDPOINT
883bc83d-ede3-411c-818e-9c174952ad4f | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
1ca370eb-b058-595e-a9ed-d66f689435ee | textbox | Contractor's Rep Name:
5fe4ef1b-aeca-5f08-b1dd-a92b48753f25 | textbox | Engineer's Rep. Name:
db1422ec-6c03-598b-96e0-d0dfa9ae47fc | date | Date:
e3308bb4-14be-4adf-9e64-6431ddef9d3f | signoff | Add Signature
1f3c3fcb-78d1-4127-bc4a-8df8f2c3f654 | checklist | DN1210-013 ITP Surfacing EME Rev 0 | itp | DN1210-013 ITP Surfacing EME
90555150-c218-440f-9a27-547fcc3b4fad | section | 1.0. Pre-Commencement Activities
53e3d4cf-8e68-4ea5-bff5-ad16396d733d | checkpoint | 1.1 - Approved JMF for EME2 Base Course
d8726d28-6023-53e0-9607-f412c132e329 | note | Detail of Activity / Test - EME2 Whitehall V1 T24/3436
a0259e27-b134-5882-9a53-68930d4fa0cb | note | Action (Hold, Monitor, Witness) - H
2ddf311a-e1f1-52c2-815c-6c556231d46a | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
5acaf4cd-ddcb-5f41-96b0-68f3395c516d | note | Inspection / Test method - Confirm requirements are followed
544c89c1-772a-5b69-b023-20c65501354e | note | Acceptance Criteria - JMF Validated in accordance with NZTA M/32:2021
ae77f756-071f-5416-9d9c-d7596e9f02b2 | note | Record documents (QCP - Quality Control Portal) - Mix Design Report
562604a4-f3d1-5581-8f62-83f7c0aa26c3 | note | Responsibility - Paving Contractor
6d74af2c-9a14-58f4-8982-8ef88301a8aa | note | Designer - A
a1bdfa76-99c4-5dc0-9716-3e334b8f4909 | note | Eng. Rep / NZTA - I
425a57f8-d813-5944-8473-bc9bd40b4b63 | note | Contractor - R
7196002d-9f9a-430e-bc8a-1bda014ca31b | signoff | AUTHORITY HOLDPOINT
0a04a84d-8a66-4722-a8a6-bb4082803d33 | checkpoint | 1.2 - Approved Quality Plan/Renewal Quality Plan
d5128a0d-150d-58f6-9663-c0e32aed106c | note | Detail of Activity / Test - Prepare and Submit RQP
07d8607a-4c7f-5196-8bed-d1fc77850ee2 | note | Action (Hold, Monitor, Witness) - H
25fb6bf9-6f25-5de6-9049-2b161bf6aace | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
dacac2b1-9c2f-578b-8d6a-1571fb03b6ea | note | Inspection / Test method - Review /Acceptance by Engineer
ab1a1b04-199a-58c9-9736-ee8b4cdd2680 | note | Record documents (QCP - Quality Control Portal) - RQP
4f5278cd-2ec7-5efa-977b-6ce4762d1ada | note | Responsibility - Paving Contractor
633b2f25-8074-5441-b655-b8730c110531 | note | Designer - I
9a77d6ce-b865-5f49-b7a0-c4a88b51461b | note | Eng. Rep / NZTA - A
5dbd0480-aa40-5985-94fb-09b356baba83 | note | Contractor - R
3307b532-7d4f-4682-9932-e0cde264a8f4 | signoff | AUTHORITY HOLDPOINT
f3a79375-a4a1-48a6-a4eb-e524007283f8 | checkpoint | 1.3 - TMP Approval
9e8e04fc-9405-5e49-a04f-5abb4d65d006 | note | Detail of Activity / Test - Prepare and Submit TMP
74d84884-4964-5b23-9165-54eb1f1417db | note | Action (Hold, Monitor, Witness) - H
610d656e-daa7-5618-98e5-1cecb82dc5b6 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
e7d85e54-0c02-50ac-9df1-558f86322cf2 | note | Inspection / Test method - Review /Acceptance by TMC
8577cd9e-4bf0-5abc-8ed0-d463e88b84a2 | note | Record documents (QCP - Quality Control Portal) - TMP
bfa74ea0-3264-540a-a5d1-5d049e618ba0 | note | Responsibility - Paving Contractor
999b831d-1594-5567-bdd6-b3c9d1bbd2a8 | note | Designer - I
ef5e26a3-5a6a-5fdf-a491-db952d02813b | note | Eng. Rep / NZTA - A
3d9a3cd5-a53f-5f56-9c5f-f041455079e6 | note | Contractor - R
c13a1c7b-0774-4b60-b96c-b9130733e9f7 | signoff | AUTHORITY HOLDPOINT
071a64dc-464e-44c1-9d94-d9c110e1f0f2 | checkpoint | 1.4 - Public Notification
feb77416-6de7-5657-a0c9-8bb12c989748 | note | Detail of Activity / Test - Communication with affected parties
bae40a06-a77f-5feb-aecb-a65e4bd645dd | note | Action (Hold, Monitor, Witness) - H
699ccbff-67de-5f1b-b010-1cc261b0f771 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
c27368d6-c7a6-54cc-ad99-e9071d6f909d | note | Inspection / Test method - Media/Letter Drops/TREIS
3cd38d19-3da1-58e8-8f2b-250192c5aef3 | note | Acceptance Criteria - Letter drop to local residents/ Greater consultation as required
b9ed9752-5f30-5d18-8a90-3947bd32e4bf | note | Record documents (QCP - Quality Control Portal) - Letter
b07b45b7-8e69-5dc9-84bc-92b52fb6c462 | note | Responsibility - Paving Contractor
98d970c8-6d88-5b5b-b494-7c4c38918a85 | note | Eng. Rep / NZTA - A
a75c477a-c8e3-5737-aaf2-c62a276a6ad5 | note | Contractor - R
b5f63704-1ea8-456e-8692-417435fb8258 | signoff | AUTHORITY HOLDPOINT
fbe6a576-7bfc-4561-9f23-f24f64707716 | checkpoint | 1.5 - Crew Briefing Plan
f575b5ea-0176-55e0-93df-04066de84291 | note | Detail of Activity / Test - Prepare and submit CBP and VMP
dd77976d-5ead-52d0-bdf9-10c103fbcfa2 | note | Action (Hold, Monitor, Witness) - H
6924bb72-289e-5a14-88e8-712a3aefc2ee | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
ab0e6db3-b377-530d-937f-fd17db523e17 | note | Inspection / Test method - Written Plan
f336549c-98ee-5d8f-bad2-b5ddbbfbcfb3 | note | Acceptance Criteria - Approved by Responsible Manager
4c53c8bc-e59f-5381-b879-d021903fb88a | note | Record documents (QCP - Quality Control Portal) - CBP
c9554978-185e-50bb-9a0e-82c91b13a6b3 | note | Responsibility - Paving Contractor
d2fffa30-52a6-5165-8171-ca14a3225364 | note | Eng. Rep / NZTA - I
02d7c548-8dc8-5984-be17-6192172b73a3 | note | Contractor - A
77aee04a-1439-47a8-8e1b-8d62b9a0e092 | signoff | AUTHORITY HOLDPOINT
3e312c5b-8185-45e0-9e95-af333d2045b7 | checkpoint | 1.6 - Site Conditions
d02bb5aa-88df-54ce-b1b7-f2f5d6c73415 | note | Detail of Activity / Test - Weather suitable, Site extents marked, surface suitable for paving (Depths/milling/cleanup complete etc), Environmental Controls in place
f2dc5bf7-8254-5abf-9cbf-e3ab21d1ca63 | note | Action (Hold, Monitor, Witness) - H
3a1f252f-fc45-5c9f-b989-6b68a889abb8 | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
ffcb4af1-cac0-51f1-8c2d-4a05054850b8 | note | Inspection / Test method - Confirm requirements are followed
9a4303f1-0b84-5153-8e35-2b7e89a59afe | note | Acceptance Criteria - Weather conditions and Site is suitable for paving
29fe3c73-89d5-5a81-9ced-310c6b190447 | note | Record documents (QCP - Quality Control Portal) - Site Diary/String Sheets
0269ac2a-6262-5f47-a364-5d03fc1c1d80 | note | Responsibility - Paving Contractor
b42129e5-73d4-5c69-a916-0e22308feafc | note | Eng. Rep / NZTA - I
7e7c7d70-c348-5f2e-a55c-b6c80525113c | note | Contractor - R
8ff84887-8f93-42f3-bb2c-056076ffd1bd | signoff | AUTHORITY HOLDPOINT
f23cdff8-3aa3-4588-9730-e53dda40ff35 | checkpoint | 1.7 - Traffic Loops
b38ba871-9610-563a-880b-6f3c1fcf3570 | note | Detail of Activity / Test - Communication with affected parties
cbaf637f-98f5-587b-bac2-a58e538dc7c8 | note | Action (Hold, Monitor, Witness) - H
f84478e9-4a8b-5064-9a96-04889435d858 | note | Minimum Test Frequency (Lot = 1 day’s production) - Minimum of 7 days Before Works commence
a5789dc4-203a-5c86-9aa4-18ebd00a8d0d | note | Inspection / Test method - Visual
f2f97555-fc28-50fe-8412-01fef6bf0fe1 | note | Acceptance Criteria - Notify RC at least 7 days before surfacing is programmed
91a9260f-5123-50fd-bac1-1196d154ff32 | note | Record documents (QCP - Quality Control Portal) - Communication
f991f379-2d7e-5b62-8e1a-88af229e5c6b | note | Responsibility - Paving Contractor
36f37b9b-88b1-5bcd-a1aa-69ac3c8f1518 | note | Eng. Rep / NZTA - A
6c2b6964-f14c-5e7c-b4d3-17dde35f6e27 | note | Contractor - R
749c3c97-2a7d-4d8f-9902-ecf5b1fc6a9e | signoff | AUTHORITY HOLDPOINT
ec493d14-6768-4494-ac98-49d871cf8473 | checkpoint | 1.8 - Paving Plan
2c13cb21-0ef4-5342-82a0-c606375ea05e | note | Detail of Activity / Test - Paving Plan to be completed
8963f05b-4476-553d-9cd7-034253e82f72 | note | Action (Hold, Monitor, Witness) - H
eee9a839-2ef2-52e5-93cc-00dc90bbcaec | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
cb5ab1f2-8f1e-5872-a0d1-b268943e9fbc | note | Inspection / Test method - NZTA M/32:2021 Clause 9.5.1
c7bfff1c-2019-5e53-aa89-98a217b40375 | note | Acceptance Criteria - Paving Plan to be completed for each shift
423ab632-a605-5599-afc1-63949239bce0 | note | Record documents (QCP - Quality Control Portal) - Paving Plan
fabf057e-2960-5991-b2df-74453edf1351 | note | Responsibility - Paving Contractor
f8f0cb95-09eb-542d-8438-e44940aca017 | note | Eng. Rep / NZTA - I
028ec8dc-f97b-578e-b1f4-7ef8655e44d1 | note | Contractor - R
6a4cdb7b-3b77-4c3a-a943-251ee6933f52 | signoff | AUTHORITY HOLDPOINT
b6294803-740b-45be-902e-c30277a3a8ba | section | 2.0. MANUFACTURE OF ASPHALT
4eb7f6ed-4ae4-4a2e-b76a-ef73d952d804 | checkpoint | 2.1 - Temperatures
2615c758-329f-5e9d-8da3-47858c2be2e0 | note | Detail of Activity / Test - Mixing of aggregates and bitumen
dec099e4-2609-5edc-968f-48e03254bcc0 | note | Action (Hold, Monitor, Witness) - M
81232165-a0c6-536b-9032-6fb6da91bacb | note | Minimum Test Frequency (Lot = 1 day’s production) - Constant monitoring of temperature by calibrated euipment
4fc82854-f43e-5411-a9b6-763e9e678e84 | note | Inspection / Test method - Plant temperature probes
1a7a48fb-fd93-5792-9767-18f7b1325de0 | note | Acceptance Criteria - EME2 binder Mixing range 180 - 190°C
8ceee789-1d67-51ec-b564-67478fe46303 | note | ○ NZTA M/32:2021 states max. 190 deg.C
7f9c795a-9b86-572c-8e55-986e9ba4cc5f | note | Record documents (QCP - Quality Control Portal) - Plant site diary
81dacd1e-489b-5840-89f1-9aea0d36f2e7 | note | Responsibility - Asphalt Manufacturer
53fd666d-24ca-5d90-ab9b-9ed6f5a21df7 | note | Designer - I
9742246a-6389-54a5-882d-833b49f5c033 | note | Eng. Rep / NZTA - I
f33fe83c-3f5c-5938-815b-c3207daf1b02 | note | Contractor - R
c89eab6d-c269-49f5-8337-82e7c3162d8b | checkpoint | 2.2 - Production Asphalt
7213158e-ccdb-57c8-a32f-5dafe28f56bb | note | Detail of Activity / Test - Particle Size Distribution
5c18c652-91d1-5f60-a021-342c761cbc51 | note | Action (Hold, Monitor, Witness) - M
abccd3fe-60e4-5855-9245-9cb6b6ab1ef0 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
eba2d8ba-6aaf-504c-8057-0c7ae67c1b6a | note | Inspection / Test method - NZS 4407, Test 3.8.1
f623c518-d095-5ce7-b099-a113afa392aa | note | Acceptance Criteria - NZTA M/32:2021, Refer to Table 5.3
784b01b4-2ace-5518-83cc-994242418a66 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
24c6a835-3500-5f2b-9fdb-6964857010b7 | note | Responsibility - Asphalt Manufacturer
3c71d6fc-0041-5d58-adc4-14bdc2787eb1 | note | Designer - I
c0d361dd-62d5-5089-b4c0-e0e8d44551ec | note | Eng. Rep / NZTA - I
ac8bf286-f064-522b-969e-d29376d8a280 | note | Contractor - R
4f32417f-0be0-4c07-bf13-0f210274d929 | checkpoint | 2.3 - Production Asphalt
48e69e8f-81f2-52d3-84d5-2d17d790c844 | note | Detail of Activity / Test - Binder Content
ece8d70f-acf0-59d7-983f-7657cca9a471 | note | Action (Hold, Monitor, Witness) - M
3aadaa53-0c9e-5f07-92c7-4ae86dd23ce4 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 200t at asphalt plant
26c487a6-7d41-56a7-8dc9-7ebf74bb0675 | note | Acceptance Criteria - NZTA M/32:2021
353decd0-c16d-551b-bf90-be728a266a43 | note | ○ Individual Test Result: ± 0.5
1fa7fe09-9048-5050-a112-31f9c0d3c536 | note | ○ Mean of Three Test Results: ± 0.3
566da329-5c4e-5d55-ab9d-0ecc0ce9153e | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
b2e7ffd1-c6cf-5169-a96e-26df8a345ee9 | note | Responsibility - Asphalt Manufacturer
00cc3439-d13e-579d-b90a-82b86691e1df | note | Designer - I
dac685a3-58d7-597f-b247-2c584dfda06f | note | Eng. Rep / NZTA - I
426f4831-e6c8-50f5-953e-6e530d8ae5d3 | note | Contractor - R
9ba7a860-d5d0-42ad-bf3a-5f8c26ab497b | checkpoint | 2.4 - Production Asphalt
3cff7c88-507f-5f27-bece-3144a88a5814 | note | Detail of Activity / Test - Max. Specific Gravity (MSG) of mix
e79b0f8d-c5c5-5c68-864c-e7c4e6145d7d | note | Action (Hold, Monitor, Witness) - M
814ae9ee-5162-56d4-a19c-0435b73ef700 | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
418f2633-1ca1-56cb-b0c1-193a764f0493 | note | Acceptance Criteria - Report
ea2a54f5-0df7-5c07-97ca-f04300a0e505 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
7e793629-01b3-5dd7-bfa5-e59c24246f45 | note | Responsibility - Asphalt Manufacturer
932ddc02-092a-5d77-8ec9-0744e99fba77 | note | Designer - I
ec683fa5-c9f0-5063-a211-5d376f50b48a | note | Eng. Rep / NZTA - I
41f1f310-729e-54bd-9f76-c0fa3e4f2e1d | note | Contractor - R
cb3fd138-6ec2-41ce-97e6-2d6459b2c682 | checkpoint | 2.5 - Production Asphalt
6959e388-4cf4-5ad4-aee0-b76996954a6c | note | Detail of Activity / Test - Air Voids at lab design compaction
9562c194-24eb-58af-8815-b04467bfd31e | note | Action (Hold, Monitor, Witness) - M
f41cc873-6542-5f9c-a00c-839f8deb49ef | note | Minimum Test Frequency (Lot = 1 day’s production) - 1 per 600t at asphalt plant
74d924c6-7421-50e1-9809-cda1324648ff | note | Acceptance Criteria - NZTA M/32:2021
c1a23c1b-9995-5b8b-b95f-2c54489d7700 | note | ○ Individual Test Results: +2.0, -1.0
282cae58-b8d9-5700-a049-220d26f2ba4e | note | ○ Mean of Three Test Results: +1.2, -0.6
ac0af13b-c183-599b-8c92-9a2fd9b997e0 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert
1f25d7a9-451d-54ac-b07f-7b73c0888e62 | note | Responsibility - Asphalt Manufacturer
033007df-8594-5a93-bfdc-f422cf3e05f2 | note | Designer - I
d2e87fc6-921f-5181-ac63-d3aafd2ffaf6 | note | Eng. Rep / NZTA - I
e3063d3b-abb0-57f7-8a66-7d58af286aee | note | Contractor - R
f020b356-945b-4863-9941-b5cdbe4e3f4c | section | 3.0. PLACING AND FINISHING
0afe85dd-be12-4a4d-b2ad-58b77a355f5e | checkpoint | 3.1 - Milling
4a843451-f2c1-5050-8cbf-1d5652740212 | note | Detail of Activity / Test - Surface strung to ensure milling Depth is achieved
73661ce7-c6b9-5dc4-a673-0beb864e9dcb | note | Action (Hold, Monitor, Witness) - H
1e433a86-846d-5625-a542-d523828e544a | note | Minimum Test Frequency (Lot = 1 day’s production) - Before Works commence
3622c83a-5895-5b51-aa2f-b7aed56070f6 | note | Inspection / Test method - Confirm requirements are followed
2e1c0a9d-11e8-51fb-8902-89328e10a621 | note | Acceptance Criteria - Site is suitable for paving
1fb4e4d0-cf1e-5234-b3bf-5ecf47281e79 | note | Record documents (QCP - Quality Control Portal) - String Sheet
7a3f744d-1da0-500c-8cae-34b988f46b17 | note | Responsibility - Paving Contractor
639ed026-157a-53c1-85f4-c995ef265b82 | note | Eng. Rep / NZTA - I
fc4a27b2-8df3-5bdb-abf7-3526bc74bb23 | note | Contractor - R
6289d73f-2996-493e-aa7d-0f5e5c68c5e2 | signoff | AUTHORITY HOLDPOINT
78ac0994-cb3d-431e-80c5-a8dd1a27e59a | checkpoint | 3.2 - Tack Coat, OR
562f3869-e372-543a-a52e-62f124c3c6ab | note | Detail of Activity / Test - Application of Tack Coat
ab3330e8-20f1-520b-9f48-1afee9dc728e | note | Action (Hold, Monitor, Witness) - M
cd069770-0343-5dac-bd2a-5f6d92580c3e | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
8bd2bb74-3053-5de4-811d-26fd1d12c06c | note | Inspection / Test method - Dip bitumen emulsion tank before and after
fa9f5c51-0a8e-5c23-8bf0-608204749aef | note | Acceptance Criteria - Target Between 0.2l/m2 - 0.6l/m2 +/- 0.1l/m2 From Target Application Rate
7b33274a-0fb8-537d-82a0-684875c0fc99 | note | Record documents (QCP - Quality Control Portal) - Site Diary
94f3e780-6eec-55f1-96d2-c7535ece5e06 | note | Responsibility - Paving Contractor
d9c20d1b-6a46-52e1-ba63-906a4c9322da | note | Designer - I
1814b80a-c02c-5d18-896e-c708389ffae5 | note | Eng. Rep / NZTA - I
17f0fca5-1439-5be4-99b6-a4cba8d529ef | note | Contractor - R
8abc4c66-6b64-46b4-b244-ba873bc2d80d | checkpoint | 3.3 - Membrane Seal
25ae3c5b-71b9-5a7d-9510-91dd193b35b9 | note | Detail of Activity / Test - Application of Membrane Seal
7fcf3160-c877-52e4-9b20-1a794c967a0d | note | Action (Hold, Monitor, Witness) - M
8b7b1e3f-b358-5cd3-8e85-03f0059ef791 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Lot
27efe21c-2945-593c-a1ed-2d6864dd264e | note | Inspection / Test method - Sealing Records
1067d2ce-3d3f-5bd7-b3b2-30aebc7f26de | note | Acceptance Criteria - Application rate, chip type and binder as per membrane seal design
436208ba-a97a-5064-bf6e-d223837fe6ac | note | Record documents (QCP - Quality Control Portal) - Sealing Records
65f28276-8531-5be1-968b-84e152525b29 | note | Responsibility - Paving Contractor
f003cb72-fb68-5edd-bf78-8355b8b62fa1 | note | Designer - I
7de6f0d0-0475-5d95-934d-b83bec7b2717 | note | Eng. Rep / NZTA - I
a1891846-ccc0-52c4-a071-3eb33bac9ad5 | note | Contractor - R
c646669d-81d4-40a0-ac50-84f8a79db178 | checkpoint | 3.4 - Temperature
95217190-faf9-5a52-b9d8-3507bcd3522b | note | Detail of Activity / Test - Pavement Surface
fdd852ee-b2b6-5666-b891-a1869865172d | note | Action (Hold, Monitor, Witness) - M
e50fdfff-7d89-518e-bf1c-f9515de93926 | note | Minimum Test Frequency (Lot = 1 day’s production) - Start of shift and every 1 hour until temperature rising
8ee086a9-e072-5a08-8f79-b1c694138236 | note | Inspection / Test method - Infrared gauge
d25c6950-59ae-5a7e-915a-15c8f0d6cd60 | note | Acceptance Criteria - ≥ 5°C for Structural, or as otherwise agreed with NZTA
b890e363-85c6-59d5-a530-7d6ba36ff2d6 | note | Record documents (QCP - Quality Control Portal) - Site diary
5e35e01e-1ca8-5202-b48c-7d2d3ff7e548 | note | Responsibility - Paving Contractor
f5901305-3f2d-5dd0-bfc7-ceafa5aa1ca5 | note | Designer - I
5c3e0b1f-95d0-5671-9eeb-968fc997ea3e | note | Eng. Rep / NZTA - I
d41c0f98-d8d1-5495-9216-ca5dc554f87c | note | Contractor - R
334f6c8a-6448-4b27-b01f-97c063964dcb | checkpoint | 3.5 - Temperature
5e0a760f-6341-5f35-b21e-25505bac942f | note | Detail of Activity / Test - Asphalt Delivery temperature
d3d23e76-331f-5ff6-a467-c7984297d1fe | note | Action (Hold, Monitor, Witness) - M
f9d5119e-552a-585d-b06f-08be6c77663a | note | Minimum Test Frequency (Lot = 1 day’s production) - Every Load on delivery to the Paver Hopper
3dfe43d7-c8a0-5aa2-9d48-6b6283e3eef0 | note | Inspection / Test method - Temperature Probe/Infrared gauge
e5aa21a9-eb6c-56af-bde7-665a9ff46798 | note | Acceptance Criteria - Target ≥ 150 deg.C. in the Paver
a80e5b70-4c28-513e-8e3f-5df6a8203bc5 | note | ○ Min. ≥ 130 deg.C in the Paver
90670339-ce3b-50c0-b053-7b5518669539 | note | ○ <130°C to be Rejected
a765937c-8cab-52d2-ac51-2352b35613fa | note | Record documents (QCP - Quality Control Portal) - Site Diary
b12dc223-82ee-5f31-8c07-0b33e3710b5d | note | Responsibility - Paving Contractor
d3448472-3296-5f4e-a518-3cee0678a2e7 | note | Designer - I
ed7ad57b-8972-52ae-b865-eabc95e37b63 | note | Eng. Rep / NZTA - I
ec9a2c3f-a9de-50e4-88cd-177af2bfff47 | note | Contractor - R
3edaccc7-63ee-43b9-a6fc-880169ba8a38 | checkpoint | 3.6 - Temperature
e01bcff1-f481-5f48-a054-102f8dbbb9f8 | note | Detail of Activity / Test - Compaction Temperature
a415ee66-9fe4-5ebe-baa9-7dc3e04cfa62 | note | Action (Hold, Monitor, Witness) - M
75aee3b3-9b36-5c47-b31c-b7aba8fd5f4a | note | Minimum Test Frequency (Lot = 1 day’s production) - During compaction
b3c6899d-99c9-58b0-8ea8-4c17c1f53bf4 | note | Inspection / Test method - Temperature Probe/Infrared gauge
7b451404-c914-58ff-a689-2d05dc81efc2 | note | Acceptance Criteria - 130-150°C at commencement of compaction.
e7d528ee-47f8-5a49-bb6c-9c21be0df107 | note | ○ < 90°C - Stop Rolling
dbf54ac7-b2b8-591f-b53a-d0368cc762e7 | note | Record documents (QCP - Quality Control Portal) - Site diary
af9c8e07-7fdf-5068-90ed-0f5006490044 | note | Responsibility - Paving Contractor
16b31812-d4c7-5e6c-9c66-5c72b7d4fcd4 | note | Designer - I
f41eddbe-72ee-5a19-8576-828f3db44bbc | note | Eng. Rep / NZTA - I
09181dff-7910-50fd-ba8e-1df21bf2e825 | note | Contractor - R
2fd1da07-faba-4555-bdaa-f6d3b6b2cb40 | checkpoint | 3.7 - Mat
5fa5a44d-8332-5f42-8472-d35c237f4b85 | note | Detail of Activity / Test - Load Locate
c227a8ff-6cae-5e83-802c-363ece352dbd | note | Action (Hold, Monitor, Witness) - M
2597f3af-5a9f-518d-8e1c-f83b279147b1 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each load
bfad18f5-bb0d-52e5-9c17-7c3100b6a318 | note | Inspection / Test method - M/32
f5a5ad0e-50ec-5efa-80b1-3afedaee6083 | note | Acceptance Criteria - Each load can be indentified to a location using a diagram. Record includes:
39a2a416-e2f9-5f57-a5a0-43433fee394a | note | ○ Truck ID/Rego/Driver
b198248d-12dc-521b-8543-a3a22e2ab362 | note | ○ Depart Plant Time
1436610f-f7d8-58b3-86ff-93ff57ed7da4 | note | ○ Arrive Site Time
61558398-60ab-5daa-b456-ac8746ce7ea6 | note | ○ AC Temp on Arrival
9ef3832a-e6be-5009-a8cb-877e53823d25 | note | ○ Tonnage
9f269cc9-9f8e-552f-ae36-9b06ed956def | note | ○ Run Width
108e94ef-e52a-5e12-9db9-e351054aea64 | note | ○ Estimated Run Length
083d8d05-c288-50ae-984e-a6fe1064df6e | note | ○ Calculated Area
e77aa0ee-b4be-5e7f-92d0-861cb1013091 | note | ○ Calculated Average Depth
933d947a-46ec-5a4c-90ab-73b2880f851c | note | Record documents (QCP - Quality Control Portal) - Paving Run Sheet
a936bc0e-8774-51bb-83e8-5b41dfb8018e | note | Responsibility - Paving Contractor
e5b72081-a1a1-5484-9a2e-349a53a1d290 | note | Designer - I
788c66a7-8a3c-5fae-935f-6aed67e9495e | note | Eng. Rep / NZTA - I
e3b1a323-ae15-5086-ba11-ae38fc400124 | note | Contractor - R
968eaf1b-1e1c-47fe-acd8-6072e978fd18 | checkpoint | 3.8 - Mat
ae0b8880-f6d1-5aa8-9526-4f800644b3bc | note | Detail of Activity / Test - Thickness Monitoring
aafb4e7c-dd21-5579-bcea-1589ccaffb96 | note | Action (Hold, Monitor, Witness) - M
a506507f-177c-5afe-b953-da7be95dc084 | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
f72d5af8-242f-5b15-bd28-135466ffc7cd | note | Inspection / Test method - Dipping
5ad6dcee-b595-5353-8619-9c7c0a6dbac5 | note | Acceptance Criteria - Target Loose Thickness -0mm / +10mm
9d22e03d-a5a0-5ab2-babf-3ee861ac8856 | note | Responsibility - Paving Contractor
dbfd62d8-82d5-53d7-bf67-561460ff6f6f | note | Designer - I
021f212e-7748-598e-b952-2e4bf941fa29 | note | Eng. Rep / NZTA - I
1c66b3d7-dda3-56e1-be4d-68726ec7ade8 | note | Contractor - R
9a05ea4f-7391-4c53-b648-c8459c06288e | checkpoint | 3.9 - Mat
b942f4e8-9034-548c-ae30-32bf9427a5d1 | note | Detail of Activity / Test - Compaction - NDM
524874c4-550b-5daf-ae69-9a4ee999f4dc | note | Action (Hold, Monitor, Witness) - M
b85e6050-9eed-5ac2-a7f8-347fa49fc3c7 | note | Minimum Test Frequency (Lot = 1 day’s production) - Plateau to be completed on 1st run, thereafter monitor compaction/roller passes to achieve target density.
cbd3f529-997b-5f89-bfa9-a86b26ff994d | note | Inspection / Test method - Insitu density and air voids
1bd41b7f-7c7f-57a6-9d23-ed3ad7aa6797 | note | Acceptance Criteria - NZTA M/32:2021 - section 9.8
fe9702f1-5112-5aeb-8456-7415e01186a4 | note | Responsibility - Paving Contractor
9470f193-b554-522d-8cb9-4ba685626fea | note | Project Specific Notes / Instructions - Use a calibrated NDM with established core correlation. Locate and mark cores, record NDM Bulk density by core location (including any offset used).
d3c9c2dc-52a8-5faa-8375-57a4ed017432 | note | Designer - I
e9aa7c58-4e32-5fb5-bd72-6c2f4e236acc | note | Eng. Rep / NZTA - I
99d8c54f-6ed1-50a5-9985-662e030d12a6 | note | Contractor - R
71186777-be05-4610-a80e-d2611934f6a3 | checkpoint | 3.10 - Mat
e9e3a49d-8e30-5899-b797-7fbe01c7fe6b | note | Detail of Activity / Test - Compaction
788e20d7-2ea3-5935-bb8e-2bb35846d93e | note | Action (Hold, Monitor, Witness) - H
5610e79e-4963-509a-a96a-00d46647db75 | note | Minimum Test Frequency (Lot = 1 day’s production) - Mat: 1 per 300m2/min. 8 per Lot Joint: 1 per 100m/min. 3 per Lot, In the event of a day's production being > 30t but < 2400m2, then it will be permissable to reduce the number of cores to; Mat: 1 per 300m2 with a minimum of 4 per Lot, and Joint: 1/100m with a minimum of 3 per Lot
3fb6cd59-e57d-5e6e-9987-51106a3a0e3d | note | Inspection / Test method - Insitu density and air voids
90663f86-c55c-5dac-a21a-8e1d6be3b71b | note | Acceptance Criteria - NZTA M/32:2021 - section 9.8
bf08307a-6902-5f72-b43c-2c573cf19ea9 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
53a71814-2d56-586f-b8e6-98193e33a134 | note | Responsibility - Paving Contractor
5f889082-360d-5995-998e-4c930f7df187 | note | Project Specific Notes / Instructions - A pavement lot shall be an essentially homogeneous section of work completed within a shift of production.
8411a3ef-a1c4-5409-aa73-7d6ce3107d95 | note | ○ The lot shall be divided into an appropriate number of approximately equal sub-lots and a core shall be taken randomly within each sub-lot. The Engineer or their delegate shall use a random method for locating each core position, such as ASTM D5361 or a similar process.
25e01f4f-2acf-554b-b773-c3d9b9765310 | note | Designer - A
744c2672-c0ba-593d-98b2-c601f2c53bdb | note | Eng. Rep / NZTA - I
3376e5c2-b508-5cfd-8f60-af84b8ac3ce2 | note | Contractor - R
d078e82a-81f2-48cd-a222-ea5cd1c17010 | signoff | AUTHORITY HOLDPOINT
ddd9fa08-683e-4fe7-bffd-f2f486ce467f | checkpoint | 3.11 - Mat
0fb4a213-863f-5327-addd-c9a522da3177 | note | Detail of Activity / Test - Thickness
9bbb6de5-68e0-57bd-8ebe-f6187aedd9e7 | note | Action (Hold, Monitor, Witness) - H
ec4b03da-e81d-5101-9d19-fe49e741e3bb | note | Minimum Test Frequency (Lot = 1 day’s production) - Average of 4 measurements per core
ae585f97-b4f0-5642-beea-118c15d0c3d0 | note | Inspection / Test method - Measure Cores
ed060c9f-b306-57a7-8ebf-6c7ae3ac1a87 | note | Acceptance Criteria - LCV ≥ Specified Depth (Minimum)
9a3ee352-e735-5382-b656-28462fe19b7f | note | ○ NZTA M/32:2021 - section 9.7
80d401a2-4cb6-5da5-89fe-59f66d7a584b | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
9ef7fc52-636a-5c3d-b51a-ad67271f9e97 | note | Responsibility - Paving Contractor
2ea9fc12-cf61-50a2-8fdb-c6a2b98e0a8c | note | Designer - A
580472ba-675a-5914-a9cb-a3dcbcb3a47e | note | Eng. Rep / NZTA - I
6639c178-51da-50f7-b9a7-8c372708e8d8 | note | Contractor - R
5e21e4b6-4954-4d8d-81f6-fd7e0c9f9dd3 | signoff | AUTHORITY HOLDPOINT
7e9a9732-bf3c-4791-b186-3268f88f4c41 | checkpoint | 3.12 - Mat
ce1a2a68-0ac9-5288-9335-f9093ee4f369 | note | Detail of Activity / Test - Shape
acf06b8c-2de4-5ff2-817c-772dfe78c6cc | note | Action (Hold, Monitor, Witness) - M
43bc0e08-e8b7-5e7e-b69d-544c44b0df2a | note | Minimum Test Frequency (Lot = 1 day’s production) - Continuously
d7b19ead-f4d1-5f95-bfae-d6ee60c30454 | note | Inspection / Test method - 3m Straight edge
3cd9e014-6193-5ca6-aaa9-8a77885e898c | note | Acceptance Criteria - Where the length of the site or the geometry is such that a road roughness-measuring vehicle cannot be used then the straight edge can be used for checking the surface shape. Refer NZTA M/32:2021 - section 10.
c101c21a-5558-5dd0-b9b7-c59a0121ddf3 | note | ○ Not more than 5mm under a 3m Straight Edge.
4d48a6e1-94ac-5f80-8494-2293c727a1fe | note | Record documents (QCP - Quality Control Portal) - Straight Edge Record
89c90973-be41-5d27-bcaf-d9b1da193844 | note | Responsibility - Paving Contractor
1bffd564-6299-5c8a-b272-f9fb9be39169 | note | Designer - I
4684a047-d3b9-5c93-b442-1274d2a57ae1 | note | Eng. Rep / NZTA - I
252366b8-d479-5346-8b12-0ec89efbd64f | note | Contractor - R
3af14346-d6f4-4f35-95b0-c0d06fa395c6 | checkpoint | 3.13 - Paving Quality
895c3a22-7356-5fa3-adab-937e051fb827 | note | Detail of Activity / Test - Texture
2da5cbf3-22e6-525c-b839-94c5cb00720d | note | Action (Hold, Monitor, Witness) - M
d14557d1-208c-5b78-baec-5ed3b4c8e377 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site (If Required)
bcd42084-0a20-5d5e-be05-aceb5e5d5d16 | note | Inspection / Test method - Sand Circle or HSD
4cda6cb7-435b-535d-9304-6e655bc062c1 | note | Acceptance Criteria - NZTA T/10: 2013
a5e1e8d4-4852-5991-a96a-3414983343d5 | note | Record documents (QCP - Quality Control Portal) - IANZ accredited test cert.
3eef4fdb-8e29-5cc8-bfa2-5f95d23f5118 | note | Responsibility - Paving Contractor
cd0be239-07e6-5aef-a573-a7593786ca0c | note | Designer - I
8b3835d7-9c81-5717-8d4e-e228af1dff5b | note | Eng. Rep / NZTA - I
1b6599c5-d79c-5010-96fa-f4d11bc4a76b | note | Contractor - R
50989137-0893-40ae-a984-bd1f7cfafa9b | checkpoint | 3.14 - Paving Quality
a5c261e5-8775-566c-a5b8-89c0ede3ca19 | note | Detail of Activity / Test - Level
a9311866-dfc5-547d-b7dd-4c06ca07b2bd | note | Action (Hold, Monitor, Witness) - M
57d373fb-33ce-5f28-a8cb-6edfbd7aa58a | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site (If Required)
65849f2f-6f6e-5e68-8e88-00c11cdd9411 | note | Inspection / Test method - As Built Survey
d391c391-1eab-50e7-a229-537e3404e68d | note | Acceptance Criteria - -0 < +5mm from Specified Level
95d0ecd9-76e0-574e-8714-dc5eba73730a | note | ○ Where there is Kerb and Channel shall be flush with or no more than 5mm above the LOC.
aa803f4a-e0c5-56fc-a7bc-d913187c7dc0 | note | ○ NZTA M/32:2021 - section 10.1
846a1e3b-41d3-561b-89ed-45556b5c4813 | note | Record documents (QCP - Quality Control Portal) - Survey As builts
dc06e6d7-25fb-5307-9f7e-570c57946141 | note | Responsibility - Paving Contractor
dddf07a1-9aec-5463-b100-21f02f705bec | note | Designer - I
e6a281af-80be-5224-9986-ca28c7c2eb07 | note | Eng. Rep / NZTA - I
995f947a-d740-5e35-bca7-e5eb78946bf4 | note | Contractor - R
251453e0-7425-46d9-83c8-df97a3dd1a07 | checkpoint | 3.15 - Paving Quality
70256339-1da5-5c1b-9a7f-8b483f230de7 | note | Detail of Activity / Test - Alignment
62fe077d-2eb3-5783-a070-7210031a2e4e | note | Action (Hold, Monitor, Witness) - M
5050a288-d3ef-50d9-86a6-9747e5c12108 | note | Minimum Test Frequency (Lot = 1 day’s production) - Per Site (If Required)
283f952a-65b7-5c4d-8255-09f2137337d2 | note | Inspection / Test method - As Built Survey
643aa2cf-a1ad-57f2-847a-7c440352db01 | note | Acceptance Criteria - ±50 mm from drawings
b367acd9-220f-59c8-936f-a11b54a69b77 | note | ○ NZTA M/32:2021 - section 10.2
053e446d-67ab-502d-b980-2fcf4d12f05a | note | Record documents (QCP - Quality Control Portal) - Survey As builts
6ab5e81c-e066-5c72-be31-6cc7faa83574 | note | Responsibility - Paving Contractor
3cd52e42-2b70-52ef-a457-f22820fa6ae8 | note | Designer - I
688eaf10-35c4-5098-8ac2-05cfc62f188c | note | Eng. Rep / NZTA - I
9cfc1d29-0243-509b-bc1c-fd162c255ff4 | note | Contractor - R
537f248b-da6f-4dc6-b37b-284a6d357fec | checkpoint | 3.16 - Post Paving Completion Checks
042da5e3-28c0-541e-aaa0-04618547924d | note | Detail of Activity / Test - Site clear and cleanup
b304495a-c5de-5eb8-933f-fdcc7181957f | note | Action (Hold, Monitor, Witness) - W
86a8da67-30a1-5882-9f4d-bc6ed8839708 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
86eab0ef-ace2-5917-b4c4-1ea5cef304e3 | note | Inspection / Test method - Visual
32f39019-2580-5ecc-9cc5-0fb6696d98c0 | note | Acceptance Criteria - Site is cleared of plant (or parked in safe location) cleanup of all waste mix, paper and detritus is complete
05390f60-7c7e-5697-a61e-aa9b85fdfb7c | note | Record documents (QCP - Quality Control Portal) - Site Diary
e6d8fe28-1af5-5c2c-b9eb-1a39846b829c | note | Responsibility - Paving Contractor
1459f1d0-86fb-5a81-9bfe-af73910bc25c | note | Eng. Rep / NZTA - I
32fedf5c-adb4-5d37-946b-60644bfec5f9 | note | Contractor - R
e3930173-2a65-4451-9a09-2361ac0d84a9 | checkpoint | 3.17 - Post Paving Completion Checks
c0b4fbba-0df2-5d6d-ba6a-5cb5a7d5cdfb | note | Detail of Activity / Test - Pavement Marking
5a29dbda-1c60-5ce5-a07f-9de7668c5f00 | note | Action (Hold, Monitor, Witness) - W
14a8a08c-07f0-5532-8a12-67d42785d6d7 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
b95b260b-0b61-5eff-8a81-fdf3a445cc46 | note | Inspection / Test method - Visual
515ae211-1e31-5fb9-8957-08e7ba1ac816 | note | Acceptance Criteria - Roadmarking is complete
8ad7ae51-da02-502d-9f5d-a860e61586cb | note | Record documents (QCP - Quality Control Portal) - Site Diary
c542e157-eafc-5607-875a-33d72a621b7e | note | Responsibility - Paving Contractor
52a96869-fd8b-57d3-986a-4674932d09fc | note | Eng. Rep / NZTA - I
016eac2e-4387-5852-97e8-a30144b48fbd | note | Contractor - R
7a92ee2b-bd21-4bf3-87bc-d08de8a1c631 | checkpoint | 3.18 - Post Paving Completion Checks
ffbd31dd-4e6b-5761-ba4e-5d530021b892 | note | Detail of Activity / Test - Cold Joint Bandaging
ae708ba8-fe18-5587-95b7-12484191e1c3 | note | Action (Hold, Monitor, Witness) - W
a8319801-bb6b-5be9-be3e-2e6ef27eae51 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
30a509ec-69fa-529f-9f65-5294afcb2332 | note | Inspection / Test method - Visual
ed81bfc8-524a-57c0-a16d-12537f920d78 | note | Acceptance Criteria - Cold joint bandaging is complete
61efc8a1-5e69-5f42-a5ba-1efdb1fb9aff | note | Record documents (QCP - Quality Control Portal) - Site Diary
af5d2538-c49a-5de4-adc5-81e7a09a21a9 | note | Responsibility - Paving Contractor
f1a960de-7f78-50a4-9f81-32e1d26e6da1 | note | Eng. Rep / NZTA - I
b621d845-0b87-5ab3-b603-c7e1416adef4 | note | Contractor - R
aadcba3c-f82c-4fe8-85d2-77dd75b55ae6 | checkpoint | 3.19 - Post Paving Completion Checks
bd9e7b65-205b-544e-a111-ca6b653232fa | note | Detail of Activity / Test - Service Covers Checked
52ce8fe1-ba20-5c2c-a305-e51e4cbd2c78 | note | Action (Hold, Monitor, Witness) - W
37ad8222-eb9a-557a-a921-2591f95aa199 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
792d3c74-0106-565c-a8cc-38c781db5b16 | note | Inspection / Test method - Visual
cc862365-e62a-560a-8df9-935c192a7adf | note | Acceptance Criteria - Check that service covers are cleared and level with the pavement
83d78c26-9efb-58d7-ac13-b9e91831e61d | note | Record documents (QCP - Quality Control Portal) - Site Diary
817aa501-e367-546b-bfd2-c2b0e3004469 | note | Responsibility - Paving Contractor
4a9f71d3-7cd3-5bda-8496-089441ca77c3 | note | Eng. Rep / NZTA - I
5b8a1daa-7f25-508c-978b-c6eeb58463e8 | note | Contractor - R
1e2a6d01-db5e-4076-9c49-803c07882d2d | checkpoint | 3.2 - Post Paving Completion Checks
c557cfde-65f1-54da-ab10-61a4b4f60694 | note | Detail of Activity / Test - Traffic Loops Reinstated
91521bb2-932e-572a-9146-72b696128607 | note | Action (Hold, Monitor, Witness) - W
6d9039ad-9c41-55f8-afe3-94cd74d36ba9 | note | Minimum Test Frequency (Lot = 1 day’s production) - Each Site/Shift
dbc28b38-5c24-5cd1-bd12-537791789fab | note | Inspection / Test method - Visual
9e1ad543-650e-5dc7-8d9b-f3099e1c8b4c | note | Acceptance Criteria - Check that affected traffic loops have been reinstated
9ccb657a-704e-574c-bdc9-89b84d386188 | note | Record documents (QCP - Quality Control Portal) - Communication
43e29b9b-ad25-52a1-8b2b-2e029f0c566a | note | Responsibility - Paving Contractor
321cc5d0-6cf5-5fd2-b1f1-6979759b7f1e | note | Eng. Rep / NZTA - I
6f499201-c4d4-5405-8ed9-3ae8f87e90c4 | note | Contractor - R
1f1679b8-ff49-4d99-a587-1efcc9033d98 | section | 4.0. As Built Records
41dc27e2-9451-4a1d-bad9-c2f98cb145a3 | checkpoint | 4.1 - Assessment of all test results for conformity
748f5b46-8a82-52ac-a58e-d93856f234cf | note | Detail of Activity / Test - Review against ITP Requirements
89869b31-6ed2-541b-b1bb-ac77131e5a56 | note | Action (Hold, Monitor, Witness) - H
1db243b5-96cf-582e-8161-b5528478219a | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
0f6407bc-efa0-5797-9a10-e159d1dc62cb | note | Inspection / Test method - Review
71b2ef9c-f331-57fb-8a12-023c36f77429 | note | Acceptance Criteria - Reporting of any non-conforming results to Engineer via NCR
18b11731-1403-5816-afa0-82b6e503e701 | note | Record documents (QCP - Quality Control Portal) - NCR
d8c6a656-9566-5113-ad53-daaf784f0890 | note | Responsibility - Paving Contractor
481ea603-83e3-5077-ab93-a0b55d5ebfdc | note | Designer - I
d59daba7-0939-5345-bae1-bd1530e87121 | note | Eng. Rep / NZTA - A
6b08a26d-ff21-5bf2-ad8b-c05a473e8e12 | note | Contractor - R
5f7356e3-3ce9-40b8-9a34-8855188e9d7d | signoff | AUTHORITY HOLDPOINT
834ed3c1-bd73-4d68-844e-4ae54eb083d9 | checkpoint | 4.2 - RAMM pavement and surface records
ab1f1148-f782-59ca-b710-410a7298ba70 | note | Detail of Activity / Test - RAMM surfacing pavement data spreadsheet updated
c3c55026-bac4-5ae4-a3e4-183c8fdd2cf8 | note | Action (Hold, Monitor, Witness) - W
b928a0a8-e3b6-56b7-94f5-b119d8fc948f | note | Minimum Test Frequency (Lot = 1 day’s production) - For each site on the project
21fbd7e8-50f7-5ab9-b7bc-39cf5554df8e | note | Inspection / Test method - Prepare Data
2fd6c45d-f0a0-5357-8039-72eb217c1d55 | note | Acceptance Criteria - Over milled and Deep lift extents recorded and verified by Contract Engineer / QA
e7f9a797-6de8-5abf-b494-5b4bb2150ceb | note | ○ Spray sheets for membrane area received by Contract Engineer from Sealing Team.
be46345b-1f2c-5919-8f14-6227d799a9b4 | note | ○ Surfacing layer extents recorded and verified by Contract Engineer.
9f1fcc2e-75b5-568d-bb3a-9d2d013c4fd7 | note | Record documents (QCP - Quality Control Portal) - RAMM Spreadsheet
da93a5b2-6d5b-506d-8ae7-de0e0d28bdba | note | Responsibility - Paving Contractor
539cc33a-333c-5816-9a0a-db300df41fcc | note | Designer - I
bcb61852-f5c4-5785-8fd7-cf782773ca46 | note | Eng. Rep / NZTA - A
0e9dd0fb-dd5a-5f15-a316-5ed5d7d949a0 | note | Contractor - R
ae6761fc-bd00-41ef-984c-c35f643b458d | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
dff2d346-1ad5-54db-8f8d-5238422640fa | textbox | Contractor's Rep Name:
1146c89c-cb0a-51a4-9b90-095d0d16b2d0 | textbox | Engineer's Rep. Name:
c10f1875-23b2-5ba4-bbd9-1d9ed9f388c1 | date | Date:
4b465f45-987d-418c-92b6-767bab679cb2 | signoff | Add Signature
8693f360-eada-47f3-9a1d-f3381cf3ace3 | checklist | DN1210-016 ITP Fencing Rev 1 | itp | DN1210-016 ITP Fencing Rev 1
9dbf9507-d5c1-5f76-b0e9-632a875b7d7c | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
61faafb8-e067-5299-84f0-3fd60960e68e | checkpoint | 1.1.1 - Extent of Line Setout
2d49439a-3db5-5e85-9b0b-ca24f4b79ac2 | note | Detail - Ensure line and level of Fences has been marked out and agreed with Engineer in accordance with fence drawings.
29900d8c-108b-5bcb-ba90-3d2400fb1787 | note | Acceptance / Conformance Criteria - Engineers Approval
06e46e56-df76-5bec-90a5-c8ab5053aedd | note | Standard / Specification - Design Drawings
6e8489e2-fb2d-58f0-bf97-b57361fa463e | note | Verifying Document - ITP Sign Off
c1e300dc-eedd-5142-9f9a-1031ebfcf3b6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
9867705c-34a8-5fa4-ac89-8b325319a281 | note | Verification Activity: Activity - M
2597987d-ecc6-5af2-a423-671d0723a0f9 | note | Verification Activity: By - ENG
e9e8c2cd-2e34-5f02-8879-699288a9aa24 | checkpoint | 1.1.2 - Existing Fences system
f32c2d60-9006-5930-9f6b-c2059a7b2aec | note | Detail - Confirmation of existing Fence network.
8e482f4a-68fc-5545-8c52-941d9c8393af | note | Acceptance / Conformance Criteria - Survey Information's
15423d91-33c1-5772-b194-ca935acfe13d | note | Standard / Specification - Appendix V
a22b1324-349d-5388-b8f2-7cd6deed0be7 | note | Verifying Document - Survey data
06f131f8-2b9c-517c-8bf1-a86163db0679 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
2c553a08-9c29-57a0-b028-7b823682dc6c | note | Verification Activity: Activity - HP
455af034-9038-5f48-af09-f4980792f812 | note | Verification Activity: By - ENG
a071cef9-3b84-5a44-b239-8ada30897af8 | signoff | AUTHORITY HOLDPOINT
b2505ca3-943c-534d-afb7-23e310ef1e65 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
5032c6c8-1674-507b-9e9e-9ec0d09378eb | checkpoint | 2.1.1 - Timber (Rails/palings/battens) Posts
a81013da-d335-5038-9c3a-bf1ada791a78 | note | Detail - Treatment
c29adedd-6d0a-5c3c-af84-2548b36de425 | note | Acceptance / Conformance Criteria - H4
641c8d13-92c6-5734-a9f9-7a827bc2e863 | note | ○ H5 if touching ground otherwise H4
a8116ba3-05fb-5a11-a829-3fc17a982a24 | note | Standard / Specification - PS 27.5.5, NZS3607:1989
dc71efa7-cd41-5d29-a76d-db43d735b4d7 | note | Verifying Document - Delivery docket
d54ebcd7-a415-52f4-bb63-b53fb1780186 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
6dea0fbd-834c-5396-b585-29f6c8f5d8ef | note | Verification Activity: Activity - M
2cadf66d-84f1-567f-8b9d-b6ad000b32e5 | note | Verification Activity: By - SE
ff5686ac-35c4-536d-8305-ab342ed5957e | checkpoint | 2.1.2 - Steel (Wire/Metal fence)
471c13c3-334c-56e2-8a0b-e96c7e97c797 | note | Detail - Standard galvanised high tensile steel wire
75e50762-15d6-5b4a-9e79-d2ada755fd73 | note | Acceptance / Conformance Criteria - 2.4mm 12 gauge
6106274f-2944-5117-b75f-6a67e37f4337 | note | Standard / Specification - PS 27.5.1, PS 22.5.6
18e4522f-9002-5550-a9f3-e815c15dabdf | note | Verifying Document - Delivery Docket
55eefcb1-cdb8-56ea-b5ca-83b50390d83a | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
6da8dfdd-3e94-51cf-aa9a-d50d3657a29f | note | Verification Activity: Activity - M
1e6d896a-d77b-50fe-b701-9fa92a840bfc | note | Verification Activity: By - SE
489029af-ef0a-5f3a-b8fe-c98f2f8d59cc | checkpoint | 2.1.3 - Chain Link Net
fb315c75-5831-5ae8-838a-9490cc84d931 | note | Detail - Standard galvanised high tensile steel wire
75edb50b-7a66-5053-b343-dd5aaa97a314 | note | Acceptance / Conformance Criteria - 50*50 Max grid size
cb612150-a942-5284-9355-afa86e7fd150 | note | ○ Powder coated black finish
05b033fb-a4e9-593a-972f-af3ab8aeda25 | note | Standard / Specification - PS 14.6.1
b4ef8562-d5f3-5c66-94d7-614093dae351 | note | Verifying Document - Delivery Docket
dc0041d3-2301-51ce-bc4f-c9f15e7f8fb2 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
4e760af3-a526-5d2c-80d1-e5eb00863b05 | note | Verification Activity: Activity - M
8d4e7b06-7ee1-5d0f-95b9-b572a860eb13 | note | Verification Activity: By - SE
591f8625-e14e-5db2-9fa4-b5d19a067cc5 | checkpoint | 2.1.4 - Material (Fixings/fasteners/hinges/chains)
28e911e2-5198-5b13-a9be-af191a00da8e | note | Detail - Jointing
822cc2ce-04e1-5a67-b3e5-2148ab5ae88d | note | Acceptance / Conformance Criteria - Hot dip galvanised
01f9a961-8407-559f-a4b0-288c00dca841 | note | Standard / Specification - PS 27.5.1
f639d918-6f43-5577-84ff-6b2799ba0d07 | note | Verifying Document - Delivery Docket
3d59af60-6986-50ea-811a-cda0111e73f6 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
7806c0f5-e56b-58dc-93cc-ac50fd55c2ed | note | Verification Activity: Activity - M
e2935100-6616-5c08-9fbe-19fcfe7e7cca | note | Verification Activity: By - SE
9cc06a11-17ee-5f49-ac50-31c36fc22fcb | section | SECTION 3 – CONSTRUCTION ACTIVITY
4f3a473f-e466-5291-a795-4d0c92b1a2b3 | checkpoint | 3.1.1 - Wetlands Fence
f866857b-ce13-59f6-8fca-ccf773564bd7 | note | Detail - Install around the wetland
16be6173-c6ec-598a-80a0-bc506f5d4028 | note | ○ Black powder coated finish
02f97957-1b4c-5ba0-913e-2c6a46c4d6a9 | note | Acceptance / Conformance Criteria - 1.5M high
7878d232-a1da-53e7-8b56-551687b16305 | note | ○ Hot dip Galvanised
49455d3b-ce8d-5a0b-bb1d-4ee2f0059392 | note | Standard / Specification - PS 2-32735.02-WSP-DR-UDL-0407, PS 27.5.1, PS 27.5.2
b3e15b83-25bd-53c8-8724-0afc06f86748 | note | Verifying Document - Delivery docket
db100ae5-c88c-5953-bdac-afd6169ee08f | note | Testing Quantity Required (based from schedule qtys) - During installation
b54fff12-3021-50a1-a528-9d5e4e6811d0 | note | Verification Activity: Activity - M
8b1cfc15-3b30-5ee6-a294-a4d0f16103c9 | note | Verification Activity: By - SE
42ecb55c-639f-5bdc-a60c-8778e8f586be | checkpoint | 3.2.1 - Timber fence
d4316e81-867b-58ab-9596-b44287b1f3cf | note | Detail - Preserve timber exposed faces
5d5e9a2d-6a4d-58bc-9093-8643504d18fd | note | ○ Post imbedded in ground
8e9338f9-e7a9-5b7d-9ca3-3aa80ff61f31 | note | Acceptance / Conformance Criteria - 1.8m high
9508edf4-88d7-55ba-9ac8-e6968cf7b96b | note | ○ Exposed timber faces neatly protected with 2 coats of timber preservative (Metalex)
9623e987-c6f2-5d55-81fc-5622cb550839 | note | ○ 1800mm in ground with 17.5MPa concrete
4e0aa3d2-8b75-5ddd-8631-9598808c35b4 | note | ○ Minimum 100mm extend around the post
a685488e-d7f7-514d-942c-d745412a8f69 | note | Standard / Specification - PS 27.5.5
f6d7f996-c09b-5457-82a7-f73078527bb4 | note | Verifying Document - Delivery docket
7faebad8-8d34-5361-b428-2cbb50372b40 | note | Testing Quantity Required (based from schedule qtys) - During installation
4cc86542-9a5b-5660-882a-2b059e971f0b | note | Verification Activity: Activity - M
26b50076-ae91-5c35-8a91-c9991469d4f5 | note | Verification Activity: By - SE
0925a98a-cb05-53ed-bbcf-af284fac16fe | checkpoint | 3.3.1 - Post and Wire Farm Fence
a99eecce-1bd6-5757-ab09-4a0d680142a2 | note | Detail - 8 Steel wire
7db0eb80-7ddd-573a-9253-9f0367c508c9 | note | ○ Timber post located at max 5m centre and securely rammed
94b5ab92-09fd-549a-bbef-470b80a3ded6 | note | ○ Battens affixed to wire and timber evenly spaces
468bcdd9-c010-5727-bb03-23297570b593 | note | Acceptance / Conformance Criteria - Wire and ground distance < 125mm
a81f057d-2c0a-5b49-913d-da98849be607 | note | ○ Top wire to > 1m from ground
a6e655e0-1d7a-5e59-bdce-49e96ca95c86 | note | ○ Top of post > 50mm top wire
4fe274a8-f56a-5649-9772-9f3c0ea9eca6 | note | ○ Wires not attached on road side
79fcb05f-b14c-593e-9310-936c029d8ec0 | note | ○ First 3 wire separation 125mm
3819f83b-c1d0-5a7b-93fa-b09ec9bce062 | note | ○ Min 3 battens between posts
042662cf-7c8a-5cba-9f10-e32e166877c2 | note | Standard / Specification - PS- 27.5.6, NZS 2566
3418000d-3d38-57bb-9402-e322950b9a0a | note | Verifying Document - Visual inspection
ef05d5b9-bd63-5ba9-97f5-67cb63132ce0 | note | Testing Quantity Required (based from schedule qtys) - During Construction
cb8ceb04-16f5-57d6-9011-32b47bb8254a | note | Verification Activity: Activity - M
750bf047-2bb0-5ba5-b919-f85ad174c439 | note | Verification Activity: By - SE
94bb45d6-7c4a-5d34-9c38-ef50db464e25 | checkpoint | 3.3.2 - Strainer Posts
5eaa510d-3abf-564d-91e0-0687d7761430 | note | Detail - At new and existing fence terminations
51b392b8-abab-5567-87a5-77726bb2042c | note | ○ At each corner distance between corner and/or termination strainer exceeds 200m
d6c56c89-dfe6-5340-8dba-2e813b7fd5f7 | note | Acceptance / Conformance Criteria - Double footing and tight wire secured to the post using 4mm wire
b0a26b89-41ad-5167-af76-f10b58d3241c | note | Standard / Specification - PS 22.5.6.b
6ddd964e-1636-56b0-96f6-13d333cc1fd6 | note | Verifying Document - Visual inspection
5bf4e9fe-de84-5ef6-b6e3-19665fa1c039 | note | Testing Quantity Required (based from schedule qtys) - During Construction
9fd2937e-3755-58d7-ac9e-22f0494e473d | note | Verification Activity: Activity - M
d0bf2e5e-cac4-54d8-a3ed-5919040b7a75 | note | Verification Activity: By - SE
4067999f-5728-5587-8d89-7544a2a9c8b2 | checkpoint | 3.4.1 - Chain Link fence
49ccd8f6-152c-5be0-86c8-0816a13e7e1b | note | Detail - As per drawings
cf7d3ade-8d42-5a14-a50f-070e5a74f692 | note | ○ Headwall and Wingwall fencing
bb2211d5-3200-58fd-ab7a-1eb31f32ef4a | note | ○ Secured with posts and top rails
08ca82e7-f3c2-5580-985a-2e7f1364c65b | note | ○ Spacing between two post must be equal
66f2a5bf-d6be-5cb9-9bbd-d73b88e04d37 | note | Acceptance / Conformance Criteria - Tie wire on every second diamond
742f6d38-b923-5d12-b795-864bced588b5 | note | ○ Spacing < 2400mm
eb901cff-cee9-5f5c-97bd-5755a3be111b | note | Standard / Specification - PS 2-32735.02-WSP-DR-UDL-0407
cfbb4d20-0a62-51e2-83f7-f7e6f4f19055 | note | Verifying Document - Visual inspection
016b0d32-bd62-5a8b-8694-80f46c88f8c5 | note | Testing Quantity Required (based from schedule qtys) - During Construction
929a7432-3580-52b6-949b-87077a10bcf3 | note | Verification Activity: Activity - M
359818d8-98d8-5a2b-8d59-d3bb6f1a10b4 | note | Verification Activity: By - SE
801f7ada-618c-5ced-9ef5-1d9f7eae2d38 | section | SECTION 4 – HANDOVER
13049da8-dc5f-50e6-9653-61f13f53ec94 | checkpoint | 4.1.1 - Survey As-Builts
80835152-ec3b-5e5a-b659-35b7e243d274 | note | Detail - Quality Check on New Works based on the tolerances in RITS
6137f7ba-ad1a-5fce-8331-3e570fa5c5e8 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
5afaec36-5ff3-5d6c-8432-40d0ad8dea64 | note | Standard / Specification - PS-21.7.7
a9994d3c-d6bb-548a-a6b8-094cae2a1a95 | note | Verifying Document - Red pen markup only
02da7ac2-5c09-551f-b3e2-139dc087d778 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
44d84a42-1183-5ed1-aa30-431c32e958db | note | Verification Activity: Activity - H
9dd801c2-36c1-54bb-89d4-b13fc7e94d3a | note | Verification Activity: By - ENG/PE
9a1e2b98-f0f3-450f-8a5c-ba9bb3e1c1ba | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
8b5e7450-04e4-5aa3-bcc3-3784c4ee089a | textbox | Contractor's Rep Name:
70d8edb1-97bf-5c80-909b-6d716e3b5c77 | textbox | Engineer's Rep. Name:
1ab2ebb3-2c35-5f8a-bf3b-b6cfd57b39c2 | date | Date:
290d4bbd-090a-435c-b416-27d5ccad8496 | signoff | Add Signature
073b10ce-c426-4196-b2a0-264fdc283285 | checklist | DN1210-026 ITP Pavements Type 1A Rev 1 | itp | DN1210-026 ITP Pavements Type 1A
9423c4d7-5e91-4454-a4fb-e0b52df0008c | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS (MATERIAL & THIRD PARTY APPROVALS)
31899494-833c-499a-9e66-2e51a2c3d529 | checkpoint | 1.1.1 - Geogrid
ded6c325-2294-5443-9c32-71b1ad231a93 | note | Detail - The Contractor shall submit the full details of the geogrid they propose to use to the Engineer for approval prior to installation.
735b1237-751e-5cc3-8a79-74a60dda6111 | note | Acceptance / Conformance Criteria - Engineers Approval
58e5b285-e7b9-57b6-a94e-e2b2fa07b8fe | note | Standard / Specification - PS 20.5.2, PS 16.5.13
c25bf4ff-a01a-5f1a-a28b-bb0457a7c6b6 | note | Verifying Document - Data Sheets and Approval
e0079757-f159-518e-9320-092d690f6881 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
34fb81af-2717-597b-bf9a-76cbeb0196c8 | note | Verification Activity: Activity - HP
fb6becc4-e1b0-5bc5-96ad-dc7f79311b67 | note | Verification Activity: By - ENG
b959828d-0294-406a-ae8f-fe1020601e16 | signoff | AUTHORITY HOLDPOINT
db5b4f51-e280-40d9-85c7-dc9c1ba1b465 | checkpoint | 1.1.2 - Geotextile Fabric
843c99ea-a3dd-552d-8c0b-95bb59f3d87a | note | Detail - The Contractor shall submit the full details of the geotextile fabric they propose to use to the Engineer for approval prior to installation.
3576f768-9e51-5ed7-be1a-9127cca15254 | note | Acceptance / Conformance Criteria - Engineers Approval
afea997f-891d-5185-b066-9728e85b5105 | note | Standard / Specification - PS 20.5.2, PS 16.5.14
b418ec99-492b-572e-93b1-8d734906e40f | note | Verifying Document - Data Sheets and Approval
19a4308c-fc7a-58ff-b6bc-1e6639f5eb84 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
5858b1d7-19a1-555a-8213-169cdbce71d0 | note | Verification Activity: Activity - HP
e8990a0c-20b3-5238-a169-f3329d2ecccf | note | Verification Activity: By - ENG
7e0034ec-ff5d-4174-8b0d-90f2c7d3b601 | signoff | AUTHORITY HOLDPOINT
0acfebc3-02f0-4f37-89b3-0297d827a514 | checkpoint | 1.2.1 - Crushing Resistance
cd846756-c97c-59bc-83bc-4c99bdd580aa | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
1a870996-30fb-59f6-87ea-f617456a3b0d | note | Acceptance / Conformance Criteria - >100KN
dff4a9f2-b2dc-59e0-ac17-0e0b20080baa | note | Standard / Specification - Appendix XVIII
38df10d6-451b-59df-b16c-0d42c9b101a4 | note | Verifying Document - IANZ Accredited Report
8341cbcd-c356-54a3-8092-e83e3a7ef8a4 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
a565fa9d-668d-5011-bb2b-4545e1cf0135 | note | ○ Results to Engineer 2 wks before importing
2f4c4742-87ab-5f3a-b888-512f26f5a438 | note | Verification Activity: Activity - HP
ab1ebaaa-592c-5646-9c24-2771faab8fbf | note | Verification Activity: By - ENG
ad91d7af-3d94-400b-af06-6d8a432dec06 | signoff | AUTHORITY HOLDPOINT
c3f22bfa-d315-4da1-9bbc-409895ebd19f | checkpoint | 1.2.2 - Particle Size Distribution
87af45bd-a393-5e94-b4af-e08d3e519557 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
fc66d116-2471-5d0b-bff1-ded67868bcdb | note | Acceptance / Conformance Criteria - Max Particle Size 53mm
c5eb30ae-24e4-5a8e-addb-2b34a15d44eb | note | ○ Max 10% passing 13.2mm sieve
842ccf6a-af8b-5a15-9c18-e6805c513d33 | note | Standard / Specification - Appendix XVIII
2564b50c-921d-5fdb-87f8-c1b947469520 | note | Verifying Document - IANZ Accredited Report
fafe5ffd-9db7-5853-824a-caebec7113eb | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3
15cfafdc-27f1-5655-90d1-c009c7c9fe20 | note | ○ Results to Engineer 2wks before importing
d9a89a56-b410-5c8d-98e4-9569d16d07e2 | note | Verification Activity: Activity - HP
6ff47114-ce91-5c58-ade0-5aae80f2877f | note | Verification Activity: By - ENG
e1e4b2ec-9f97-4d7f-bf36-278feba5717b | signoff | AUTHORITY HOLDPOINT
98d842e5-af51-4d61-94c7-ec48faeb3a4a | checkpoint | 1.2.3 - Weathering Resistance
a6a9f7ea-fc27-5723-b693-53ca25b298ca | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
54a2fba2-5d76-5de2-a38e-adaa3ea203cd | note | Acceptance / Conformance Criteria - CA or better
daa24e72-6091-57f4-9678-c891ea216a8f | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
4b412552-7da3-5f8f-b56f-9995e676c9cb | note | Verifying Document - IANZ Accredited Report
6bdb912b-b0e9-5fae-9760-fe8f7a6e77f8 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
cc9480f7-e180-5182-a601-2012a6d95cd2 | note | ○ Results to Engineer 2 wks before importing
26177c3d-1a08-53ea-bd24-0109386535df | note | Verification Activity: Activity - HP
d8999b98-9e21-5c35-815e-8aaafb52cede | note | Verification Activity: By - ENG
75836ba6-f9c0-4aea-b425-8709f2e3a2fe | signoff | AUTHORITY HOLDPOINT
501f8326-f9a3-41b0-898c-e5f5e213e13b | checkpoint | 1.3.1 - Crushing Resistance
d0e7b228-20e1-59e0-8814-628e1656b682 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
6ebd5384-676e-5118-9d5f-860839f20479 | note | Acceptance / Conformance Criteria - >100KN
44061de5-5b0b-5d45-bab8-4df81027368d | note | Standard / Specification - NZS4407:2015 Test 3.10
89a1b701-1ec6-52a4-9bef-33aad0b59c35 | note | Verifying Document - IANZ Accredited Report
4a370797-1287-5d14-b617-9296a1c399b0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
3d105fe9-c9ff-5554-87b9-d67f2a6c2077 | note | ○ Results to Engineer 2 wks before importing
de348323-9ab0-5d18-a86b-3021169b48f7 | note | Verification Activity: Activity - HP
fb660106-a94d-533a-ad90-e7adb513256e | note | Verification Activity: By - ENG
998124dc-c242-4c0c-ad03-0f3c68e21358 | signoff | AUTHORITY HOLDPOINT
35f33a25-0906-49d9-a9e5-4f4bec4954c5 | checkpoint | 1.3.2 - Soaked CBR
10820a39-af1d-552f-a08e-af2c196a535e | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
7d495b1d-a91d-5e30-a230-d5763bc03465 | note | Acceptance / Conformance Criteria - >60%
4211831e-d23b-5e97-894d-c458f88d8a0b | note | Standard / Specification - NZS4407:2015 Test 3.15
0a9f7dc8-b024-5bf1-9ddf-7e852dc33574 | note | Verifying Document - IANZ Accredited Report
dc48b22b-314e-580e-b143-1295c43d7acc | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
b15bfe46-837a-553c-aae8-d04fa0e1f13f | note | ○ Results to Engineer 2 wks before importing
3c32e5c4-5175-56d0-9088-d124ca970a64 | note | Verification Activity: Activity - HP
4874f395-b7fb-5608-9e67-0908ff86cec4 | note | Verification Activity: By - ENG
0b1ba297-373c-4c6e-be73-ed6584192583 | signoff | AUTHORITY HOLDPOINT
daa3ba95-18bb-414d-a8f3-23a474eb0d74 | checkpoint | 1.3.3 - Weathering Resistance
9f35029a-0f44-55cb-8b71-eedafec63145 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
f92d2c71-b4b8-5fd7-8e0a-21744b2ca99e | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
05ac6d7c-369f-5850-bc89-8574c6d4be21 | note | Standard / Specification - NZS4407:2015 Test 3.11
4e87f8dd-a799-5cf4-84b8-937d409bf65f | note | Verifying Document - IANZ Accredited Report
b68312e4-559b-5e3e-88b6-1b1fbad1d99b | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
449033d8-7276-50cb-83da-8323643dc8ae | note | ○ Results to Engineer 2 wks before importing
0c91779d-f8da-55a1-8da5-7cb8a3dc7dde | note | Verification Activity: Activity - HP
174804d4-cc54-5fc6-b23a-8cc790a83f26 | note | Verification Activity: By - ENG
4f160e28-3252-42be-ad19-6481cdc9434a | signoff | AUTHORITY HOLDPOINT
9c6814ac-05e2-439a-90e7-68cb0a3d0552 | checkpoint | 1.4.1 - Particle Size Distribution
22ef05de-8fe1-55ae-92c4-62b33cabb926 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
d3e01e1a-6bda-51fb-b1e2-fae0595ac2eb | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
1d95b49c-57a7-5089-ad79-4051bd5e9e05 | note | 63.0mm ¦¦ 100% passing
491a1c30-4a92-5379-a781-3bf7d6f04f9d | note | 37.5mm ¦¦ 68-90% passing
9824003d-c186-50b5-9663-28d935979ee4 | note | 19.0mm ¦¦ 42-76% passing
bb8a749d-7c03-5d75-8b28-fcd68178e4dc | note | 9.5mm ¦¦ 26-58% passing
ef0c3a15-df4f-51ab-a978-b792c776da13 | note | 4.75mm ¦¦ 16-44% passing
d20b3017-9cf8-54e0-8341-e0d7c529e36e | note | 2.36mm ¦¦ 10-33% passing
08ea3c8f-ee2e-59f0-ab39-7d466ddeddda | note | 1.18mm ¦¦ 6-24% passing
d5efc050-0a90-54ca-86a7-b0aa9c062b8e | note | 0.425mm ¦¦ 3-14% passing
04bf9098-77e5-5913-a568-f18d07582849 | note | 0.075mm ¦¦ 1-6% passing
87eada81-2263-5e85-94a7-7d678d0e059d | note | Standard / Specification - NZS4407:2015 Test 3.8.1
ec7e0857-d147-5bb2-ae3f-9faee0ce3bc1 | note | Verifying Document - IANZ Accredited Report
65ff0ea8-87a7-5bf1-8a93-3e1ff6c81367 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
7dec627e-bd20-563a-a3d3-825aa107276d | note | ○ 0-400 - 2 tests
dbc6e8ed-3758-56c5-9cec-a0b4d63ca4ab | note | ○ 400-1,500 - 3 tests
b14e88b4-3098-514a-bb90-d13c2aed7e81 | note | ○ 1,500-4,000 - 4 tests
4a991e70-9dc2-5ac4-b6bd-b4e4219f00a3 | note | ○ >4,000 - 1 test for each additional 1,000m3
24452072-c00e-5749-986e-40eed674c36b | note | – Results to Engineer 2 wks before importing
c517d451-5841-55cd-8481-98733ef3da86 | note | Verification Activity: Activity - HP
807fb9de-a3ec-50f4-b23e-428e04fbf8e7 | note | Verification Activity: By - ENG
726ec3b4-b49b-4ebf-9214-23aafe32e47e | signoff | AUTHORITY HOLDPOINT
18767c54-986d-47cf-82ee-669cd53203f3 | checkpoint | 1.4.2 - Sand Equivalent
3bd18539-0f91-54e1-9694-a1e7227d7997 | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
a136de90-608c-5763-be13-f8eb395d376d | note | Acceptance / Conformance Criteria - ≥ 25
a78bbb31-3f45-5543-acde-16e3d0c7224e | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
c233776c-5dfd-524e-b284-dc3b0e01569c | note | Verifying Document - IANZ Accredited Report
48ae8898-00a8-5a57-87c2-9e9be4560b6b | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
a05b7ba6-7b67-50ff-b651-15a0ad6e8b18 | note | ○ 0-400 - 2 tests
f61d6566-0018-523f-b94d-c8fb879527b9 | note | ○ 400-1,500 - 3 tests
961252a8-55ee-542b-9948-3b3cc86ae754 | note | ○ 1,500-4,000 - 4 tests
6026bd10-09d5-56ae-8211-bf7308e4e275 | note | ○ >4,000 - 1 test for each additional 1,000m3
fde6525e-cfcc-5963-922b-36a50bf874ab | note | – Results to Engineer 2 wks before importing
18777131-6d23-5b08-8936-e893a3821a56 | note | Verification Activity: Activity - HP
475aafbe-613b-5eba-af68-a058490e9a57 | note | Verification Activity: By - ENG
4299503a-616b-4ff8-be1e-8b79f22558d3 | signoff | AUTHORITY HOLDPOINT
7ad9c416-17d0-46c8-9257-ca4804133b13 | checkpoint | 1.4.3 - Maximum Dry Density and Optimum Water Content
6ab93145-cf9c-5671-89e7-fbc59debbafb | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
26429510-4069-52e9-8327-24314b54219c | note | Acceptance / Conformance Criteria - Report Value Only
4aea692a-ea8e-53aa-8b76-10456c19e9f7 | note | Standard / Specification - NZS4402:1986 Test 4.1.2
d5ddaae6-d286-5ffd-9fae-d1493db86ae0 | note | Verifying Document - IANZ Accredited Report
2b739195-56d7-51cc-9ecd-190a6a5d061f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
4c6aa23f-cadd-5c3d-8ccd-0364ac600238 | note | ○ Results to Engineer 2 wks before importing
d90a5713-5369-5e31-af17-aa9a730edcf4 | note | Verification Activity: Activity - HP
b02136a4-dfb3-57f0-939e-6bbed172532d | note | Verification Activity: By - ENG
47bfbabb-4409-4a70-b28a-33c6e8858d13 | signoff | AUTHORITY HOLDPOINT
6ce595d4-24f5-41de-8631-549951d08907 | checkpoint | 1.5.1 - Crushing Resistance
2f5c97f9-e61b-56a2-aa5e-712c4d142422 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
21fa532e-a380-5b78-a213-6f676f360fb3 | note | Acceptance / Conformance Criteria - < 10% fines passing 2.36mm under a load of 130kN
5f5296f2-c965-51b6-9713-b4ecbda358bf | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
59732cff-e5ab-5ed6-8b0c-4148ecd5ec02 | note | Verifying Document - IANZ Accredited Report
df6c20a7-927e-53c8-a293-3cb8ea188560 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
019b1669-7b1e-5fc1-8c51-968320b132ba | note | ○ Results to Engineer 2 wks before importing
a742e342-70e7-5327-93b3-873f59938850 | note | Verification Activity: Activity - HP
81b20f15-0347-55d4-a88b-49108c3fecdf | note | Verification Activity: By - ENG
00b5475b-2bc6-4cee-9bde-169b44e962b7 | signoff | AUTHORITY HOLDPOINT
57ffac27-2515-4376-a9ab-690cc094a5ce | checkpoint | 1.5.2 - Soaked CBR
fd3a4d97-16b7-5111-899b-aa24ca340f0c | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
8143c1f2-16ba-5e94-aed7-8524ed3c4d43 | note | Acceptance / Conformance Criteria - ≥ 60%
c3fb71f3-678e-5c3a-be8c-e7e8521ae832 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
de1bf16e-241e-5a54-91e0-e2bbae475ba6 | note | Verifying Document - IANZ Accredited Report
03ed405d-ada8-5d5e-9365-43212d062929 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
ffd42fb2-6d1f-5fe5-9438-6db3e4fb0d30 | note | ○ Results to Engineer 2 wks before importing
11197fe7-8bea-5ba7-9861-c598c88eb6bb | note | Verification Activity: Activity - HP
bb3ec055-4aea-543e-b22b-468bc16e8746 | note | Verification Activity: By - ENG
27adf4c9-d477-4ae1-9a6e-8a2cf3d73235 | signoff | AUTHORITY HOLDPOINT
b0e646b4-849d-4ee6-8f9c-e81803555daf | checkpoint | 1.5.3 - Weathering Resistance
8b015982-eff8-552d-b435-7a6e84af5a69 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
d5826536-29b0-59d5-a855-997aa524492f | note | Acceptance / Conformance Criteria - CA or better
2fee8da2-4cd7-5c43-bc8e-d6555e5d0562 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.1
76479d2f-f684-56b5-99b3-32acffcb422f | note | Verifying Document - IANZ Accredited Report
06309d18-34be-5ae3-9d31-a7767407e4e4 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source every 10,000m3
285c4865-7b1a-5b6c-989f-84af103c4335 | note | ○ Results to Engineer 2 wks before importing
c896e17f-8bbc-5908-b379-44eae06e8369 | note | Verification Activity: Activity - HP
d4ae2fa0-85cb-5fe4-ab4e-59c1c422522a | note | Verification Activity: By - ENG
6aa6cf9c-63a5-421f-b3ea-581381f517e8 | signoff | AUTHORITY HOLDPOINT
fded66f6-b112-4887-bbd3-66430d1f5ac4 | checkpoint | 1.6.1 - Particle Size Distribution
acb572d6-1968-5c91-8f63-d20b89c539d7 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
d3dda28a-5286-51c5-aea2-fac01bfb9dee | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
2b9f1bb2-f9f9-5291-81f5-ed641622b0db | note | 63.0mm ¦¦ 100% passing
61ec1f11-4e23-582a-ba59-32c7f6b95739 | note | 37.5mm ¦¦ 55-85% passing
50c30b7c-2ddc-5246-8405-534c0b6549e0 | note | 19.0mm ¦¦ 33-65% passing
6c76e1a5-7825-5667-aedd-f18d543d91ca | note | 9.5mm ¦¦ 20-50% passing
71f87ecd-8ac7-5ab1-8bf6-5330a2f4d633 | note | 4.75mm ¦¦ 10-36% passing
fea8a055-6333-5469-9436-678a22a713c8 | note | 2.36mm ¦¦ 5-27% passing
53ad37f6-4504-5391-8ae1-6b53ee891c76 | note | 1.18mm ¦¦ 2-20% passing
2f70f343-586d-5a6b-b049-65fe4ff75921 | note | 0.425mm ¦¦ 1-13% passing
a25b79e2-242f-5228-aa9b-39d52c42f375 | note | 0.075mm ¦¦ 6% max passing
be27b6f0-72b5-5aad-aec8-87038e9991d5 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
60243f69-84f3-5a25-bd57-09440d06ba2d | note | Verifying Document - IANZ Accredited Report
7c336808-e982-5e8d-9bdc-513ec75ccc44 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
327f9bcb-fb75-5c7e-b412-a6b0498c082a | note | ○ 0-400 - 2 tests
beaef7ca-311b-531e-b818-db0bf0008f0c | note | ○ 400-1,500 - 3 tests
8c9392e4-9c01-559d-ba41-085666e170bc | note | ○ 1,500-4,000 - 4 tests
0141e8e2-ae0b-5170-adec-a005e628527c | note | ○ >4,000 - 1 test for each additional 1,000m3
6115f220-9cf0-590d-bbf8-d163c364237a | note | – Results to Engineer 2 wks before importing
203f2751-d6c1-5dad-938a-c3720ec24231 | note | Verification Activity: Activity - HP
6df4f987-9c3a-5c7d-9219-4bff2c5ff131 | note | Verification Activity: By - ENG
d9fad559-30af-4748-8dd5-d6ee8c90ab4b | signoff | AUTHORITY HOLDPOINT
e4f45488-db64-4900-9961-2aba6b945c3d | checkpoint | 1.6.2 - Shape Control
8f3dd964-179b-54ee-979b-2677917141be | note | Detail - Tolerance allowed from approved grading curve (%)
f74c73a9-333c-5384-8fc5-664f4e942dd1 | note | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Tolerance
9dab7c3a-8338-5d76-9c17-d1b3afe9577a | note | 37.5 – 9.5 ¦¦ 34-50%
7d888140-8815-5fa3-b0ce-d592530e4e71 | note | 19.0 – 4.75 ¦¦ 18-40%
0c4e86c5-c57f-5f20-931e-6b18db5787f2 | note | 9.5 – 2.36 ¦¦ 12-32%
865da25e-4b48-5eb2-956a-560a6b542cea | note | 4.75 – 1.18 ¦¦ 6-24%
3595dbc6-49aa-508d-8fc0-b101414ea547 | note | 2.36 – 0.6 ¦¦ 2-20%
d2faacb2-5a42-5b9c-8e16-aa2645ee4b4f | note | 1.18 – 0.3 ¦¦ 0-15%
af435bff-b935-5365-8581-f013288dbc18 | note | 0.6 – 0.15 ¦¦ 0-12%
2ed25dd8-dd19-5deb-8994-fba0bba91a42 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
bb6d1f68-9da6-53dc-98dc-6b7aee1e059f | note | Verifying Document - IANZ Accredited Report
ca41b2fe-cf46-57ac-9825-c4f0d666cc92 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
f3b29147-b73a-5f1f-a03e-27009b11deea | note | ○ 0-400 - 2 tests
9bc69d86-59e1-5148-a57a-226e115429b7 | note | ○ 400-1,500 - 3 tests
dc21575e-f061-52ef-997d-51fcd5c67a75 | note | ○ 1,500-4,000 - 4 tests
6ac96ba3-6d54-5d79-94d4-2985f619c85c | note | ○ >4,000 - 1 test for each additional 1,000m3
4c3a4d22-88ea-56ca-a81c-522051ec71c9 | note | – Results to Engineer 2 wks before importing
7cd55c7c-36ca-5c6d-8cec-350a6ce06f68 | note | Verification Activity: Activity - HP
d4786860-4e8c-5b4c-b8a4-561699b35082 | note | Verification Activity: By - ENG
28955505-62c9-454a-b205-792c6f14b0b1 | signoff | AUTHORITY HOLDPOINT
35161628-0315-4014-83b5-141c4f57ee5e | checkpoint | 1.6.3 - Sand Equivalent
d292bbb5-95fe-5be8-9420-62455f453fdb | note | Detail - NZS4407:2015, Test 3.6 Sand Equivalent
da183d42-e710-5f6d-86f6-b2557f92871d | note | Acceptance / Conformance Criteria - ≥ 30
d966c876-928f-5b97-8a4d-b8ff2fe89b82 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
e9a08cd8-e0d3-5f4d-a962-5071d0fbde76 | note | Verifying Document - IANZ Accredited Report
75b1e418-5040-540e-bdca-534512f5ff24 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
f7a1b7d8-23b8-59b3-9be6-6fe1ae1f150e | note | ○ 0-400 - 2 tests
52e6d77b-6415-5ff1-843b-ce5906112b29 | note | ○ 400-1,500 - 3 tests
efcd6bfb-fec0-5778-a8f7-c9ec4bcdfc06 | note | ○ 1,500-4,000 - 4 tests
127aee68-748a-5b6b-aa90-b69f4f6405e6 | note | ○ >4,000 - 1 test for each additional 1,000m3
c49e3845-8b22-5aa0-9df4-f7b2f9e1b43b | note | – Results to Engineer 2 wks before importing
7afd9db4-a896-514b-aed8-2129f8175936 | note | Verification Activity: Activity - HP
f4d7778d-f21b-5b1d-b61e-0456b0c8271f | note | Verification Activity: By - ENG
5b0dd7e1-2e53-4597-b2ed-62a35c4a788d | signoff | AUTHORITY HOLDPOINT
1245373b-8c14-49aa-9aa9-e39a3c2690e0 | checkpoint | 1.6.4 - Cone Penetrometer Limit
aa99ebef-7e4c-5ccb-a734-3ddcb34b3ab2 | note | Detail - NZS4407:2015, Test 3.2 Cone Penetration
6a960e67-6a93-5b74-8c8d-34be2372aec6 | note | Acceptance / Conformance Criteria - Cone Penetrometer ≤ 25
5d7f54ca-de96-5606-a16f-0e74dd037bda | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
770cb8fb-be6b-5bf4-b285-aa5685d73e97 | note | Verifying Document - IANZ Accredited Report
95f92f5c-e435-548d-80ee-0953e9a06712 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
1c5bcd3f-d495-5456-ac9e-7026b205d614 | note | ○ 0-400 - 2 tests
8389b67d-6e81-5770-af56-6502b00a89c5 | note | ○ 400-1,500 - 3 tests
f23c8f4f-ec26-562d-98c9-53aedcaee6a8 | note | ○ 1,500-4,000 - 4 tests
87256890-4bfa-5b42-874e-16f32d34bb69 | note | ○ >4,000 - 1 test for each additional 1,000m3
7873f697-d04c-5a49-b228-1264e818eb7c | note | – Results to Engineer 2 wks before importing
21df9621-98e9-5652-88c9-84862adeb8b8 | note | Verification Activity: Activity - HP
0bdf335a-9d61-5bf4-ad89-92de6b43bca6 | note | Verification Activity: By - ENG
f41ddc94-dbc1-4c3a-a3af-707df3298de9 | signoff | AUTHORITY HOLDPOINT
66e6a11f-1391-4671-bed9-e4a169ae5e1c | checkpoint | 1.6.5 - Plasticity Index
afb454e9-2605-5346-8210-967d9408ac7e | note | Detail - NZS4407:2015, Test 3.4 Plasticity Index
91eb8072-583d-5fb7-9851-e2532386adea | note | Acceptance / Conformance Criteria - Plasticity Index ≤ 8
c5b73234-c77f-56b8-9ae7-5958c88ac396 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
eb053cfc-dab7-573d-8cca-45e45ee204a8 | note | Verifying Document - IANZ Accredited Report
0e96ab00-fd63-53b4-9a59-460ed1d5baff | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
4fe85226-0903-5604-855f-83374d2e42a4 | note | ○ 0-400 - 2 tests
3c891fdf-8d61-56cf-91c6-0bdaf545a501 | note | ○ 400-1,500 - 3 tests
be053d42-f2e0-56a5-8bd6-9039a88798a7 | note | ○ 1,500-4,000 - 4 tests
70829659-bb62-52ff-95ae-2d62f4dbfd83 | note | ○ >4,000 - 1 test for each additional 1,000m3
eb5ec36c-87af-55ef-8c77-5601a0f10d1f | note | – Results to Engineer 2 wks before importing
9dab3aaa-13d2-50f9-8d4e-85c8dee3de2f | note | Verification Activity: Activity - HP
e0f9e6ce-7881-5975-bb4d-bae8f1f4850d | note | Verification Activity: By - ENG
dae8bf9f-c8f7-48ad-a225-658aa90a852e | signoff | AUTHORITY HOLDPOINT
7f2f26c6-e87d-4bd0-998c-c36b5bb09ece | checkpoint | 1.6.6 - Accelerated Weathering
6e90061a-8b40-52bb-8b8d-86fed545a863 | note | Detail - NZTA T/20 Ethylene Glycol Accelerated Weathering Test
cf34ac93-421d-5f5f-b07b-f02f3e0f7045 | note | Acceptance / Conformance Criteria - ≤ 30% increase in fines
ff4e36fd-7594-5b3d-a010-9984fb6c2813 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
0589cbe9-e464-5f6b-8671-6918f67e5f8e | note | Verifying Document - IANZ Accredited Report
0d48fdde-cc3b-5ae6-b422-ff5efaad14cb | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required Stockpile Size (m3):
ddb398bb-a8c3-5ce7-a810-4cbf8d430def | note | ○ 0-400 - 2 tests
bc1ac96c-3f63-5aac-9171-9cb207556db5 | note | ○ 400-1,500 - 3 tests
89250bb8-adfd-57c2-8b12-4d6afb3bcffe | note | ○ 1,500-4,000 - 4 tests
f720ddc8-f62c-57ba-abca-fe66c2588121 | note | ○ >4,000 - 1 test for each additional 1,000m3
31fa3ae2-0d5f-51e2-85a9-e668afc85151 | note | – Results to Engineer 2 wks before importing
68d274c2-0389-5a9f-9340-0127ae9e4694 | note | Verification Activity: Activity - HP
7d90a44a-44c2-5c1b-9cd3-41306fcdf6f1 | note | Verification Activity: By - ENG
df813c86-ab3c-4f55-b0d4-86f7e9ac03c1 | signoff | AUTHORITY HOLDPOINT
101909de-fa2a-46b4-bb42-4529af2109fe | checkpoint | 1.6.7 - Maximum Dry Density and Optimum Water Content
1497bd29-46a7-57d0-9cb6-a226a23d3823 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
4a32f38d-65bb-56ff-a894-4f678752764b | note | Acceptance / Conformance Criteria - Report Value Only
694e0aec-67b1-5586-b72e-0f9b1930f3a7 | note | Standard / Specification - PS 20.7.1, TCC-IDC IT-4.7.2
c4129a88-5707-51ef-95e7-9200ace85e89 | note | Verifying Document - IANZ Accredited Report
49406ced-0fa8-565d-a35e-9bb49d573fba | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
67cbb732-cca2-5763-871b-5e8d9782b8f5 | note | ○ Results to Engineer 2 wks before importing
0d577e2c-5924-51f1-a35f-250bc51fd0b0 | note | Verification Activity: Activity - HP
92502d25-e1ce-5843-be22-7f2394019665 | note | Verification Activity: By - ENG
f682b319-bef7-4004-834b-f6143e5421d9 | signoff | AUTHORITY HOLDPOINT
780209b1-3381-499d-aa8d-440077a1bbcc | section | SECTION 2 – CONSTRUCTION - SUBSOIL DRAINS
c9a0f44d-bbbe-4658-996c-d3e6ce7a04d7 | checkpoint | 2.1.1 - Subsoil Drain inspection
0f03e87a-4ce5-5006-beb7-b2c7197df617 | note | Detail - Subsoils to be placed below kerb lines and inspected by Engineer
f0b15acc-cecf-5945-9904-788938a3504e | note | Acceptance / Conformance Criteria - Engineers Approval
c0211aa7-fb02-566d-8776-49f0885a3c13 | note | Standard / Specification - PS 17.6.3
c6cd9127-3730-530b-b691-47cf1f61a206 | note | Verifying Document - Release of hold point
bd994b9b-ab3e-5496-b86c-61ddf3d46115 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
34075fb3-d281-5f91-a8e0-b49e9b2ecde8 | note | Verification Activity: Activity - I
602319d9-51b5-5f91-bcbb-8a158fa9c746 | note | Verification Activity: By - ENG
18fff7d2-e88b-4e4c-ab5f-7aaec5ad4aee | checkpoint | 2.1.1 - Excavation
e0596ef8-e6bc-525b-86c7-10e1051579bf | note | Detail - Excavtion of Trench should be within tolerances.
01c4e9c6-9fa2-56b2-bf71-f935ff6c5798 | note | Acceptance / Conformance Criteria - 335mm deep x 300mm wide
f01b08d2-d0d1-5070-8312-f97b6798ead9 | note | Standard / Specification - Drawings
14096404-c34c-5aa5-8eae-29f4cef9e6dc | note | Verifying Document - Subsoil Checksheet
1e721651-bad3-5b53-8218-3aff30f1d6ed | note | Testing Quantity Required (based from schedule qtys) - During Construction
1e71cb5a-cd1d-5a5f-b81e-5eaf8ed25616 | note | Verification Activity: Activity - M
19a975a3-ceba-5ac2-9fa5-e8068a22d5e6 | note | Verification Activity: By - SE
cd630c77-4f2a-42c3-8ea1-1ae60dc34070 | checkpoint | 2.1.2 - Placement of Bidim
94c9ddb9-6dc5-5512-b21e-208a16a44a72 | note | Detail - A29 Bidim to be placed andd wrapped around Trench.
6c878745-84f3-51b4-8e02-e5d5b256e925 | note | Acceptance / Conformance Criteria - Minimum Width 300mm.
4628c80d-36c1-5aaf-9df9-bab54a0c81dc | note | Standard / Specification - Drawings
95257eea-5bb9-5ccc-a538-4261e613d173 | note | Verifying Document - Subsoil Checksheet
2f746bb9-06fc-500a-8dc8-8960c1811550 | note | Testing Quantity Required (based from schedule qtys) - During Construction
de3c0783-edef-51eb-883d-6493299d6502 | note | Verification Activity: Activity - M
dfb7c90c-c81b-5699-9907-e139fe6eac2c | note | Verification Activity: By - SE
4dacafe2-6213-4b59-aa22-f9adf31c08a6 | checkpoint | 2.1.3 - Cushion (Bedding)
b1c65d51-c6cd-5cca-acf8-517573d911d1 | note | Detail - Pipe must have 75mm of Cushion. Drainage 20:40 Material to be used.
558cf078-1664-537a-bb52-5e2bbe3aeb47 | note | Acceptance / Conformance Criteria - Minimum 75mm
e009158d-0192-52c8-b801-1dad981d7cd7 | note | Standard / Specification - Drawings
5cb1b3bd-e626-54da-88c7-30589059ec97 | note | Verifying Document - Subsoil Checksheet
05f61b71-6706-5c9d-8dbe-516c98bc7078 | note | Testing Quantity Required (based from schedule qtys) - During Construction
932f058d-d32c-58ff-8869-7db8518c2da6 | note | Verification Activity: Activity - M
10233c1d-f7f4-5ccb-83a0-9a5af93e75e7 | note | Verification Activity: By - SE
4ef045cd-8899-498d-b411-10d7bb038397 | checkpoint | 2.1.4 - Placement of Pipe
95c275ea-dda0-5b97-9fd0-7c4992b5894f | note | Detail - 110mm Perforated Pipe to be laid Down
21236585-cf9b-5d4e-b9f5-b465a0a8d258 | note | Acceptance / Conformance Criteria - As Per Drawings
37587856-e947-5a89-9ab2-78a84a1d25af | note | Standard / Specification - Drawings
53a05ca3-14c2-5dea-b708-2ac490bb29d6 | note | Verifying Document - Subsoil Checksheet
59743d09-80d9-5757-b9f2-84b8ddad9dc6 | note | Testing Quantity Required (based from schedule qtys) - During Construction
81a2f73e-1a2d-51be-8b4f-1851b582dab9 | note | Verification Activity: Activity - M
cf02a88b-a773-575a-b5b9-6551a62cdcac | note | Verification Activity: By - SE
a7abf62b-adfe-49c6-9b35-3778c10196d4 | checkpoint | 2.1.5 - Backfill
6851d909-e696-57c7-8f96-e8e8ac62c83a | note | Detail - Pipe Must have a 150mm cover from Bottom of Pavement.
e6111ff7-1a06-564a-bedf-2e734e83d4d7 | note | ○ Drainage 20:40 Material to be used.
fa995c9a-936e-56ea-a6da-7cf861d3d795 | note | Acceptance / Conformance Criteria - >150mm Cover
a6083ea5-b17b-51a6-ac29-067d28b4a1c1 | note | Standard / Specification - Drawings
732bde75-7050-5385-bd99-cdb140b15580 | note | Verifying Document - Subsoil Checksheet
11323b96-df18-511b-9b2f-9c6007d28dec | note | Testing Quantity Required (based from schedule qtys) - During Construction
c809d460-2eee-5d9f-b4a8-e4cce32c5fee | note | Verification Activity: Activity - M
1f2f20e0-4412-598b-9d84-37c8951b9acd | note | Verification Activity: By - SE
508a3d7d-c8bf-41c1-8eef-c75b6a2e2536 | section | SECTION 3 – CONSTRUCTIN - PLACEMENT OF GEOGRID AND GEOTEXTILE FABRIC
0732ff46-0f8e-4d78-8d68-4746707e341d | checkpoint | 3.1.1 - Placement of Geotextile Fabric
c66e4071-e591-5122-b996-6ee241d0ce3e | note | Detail - Place Geotextile Fabric Strength Class B across pavement area, with 500mm overlaps
186b53b9-2e05-5c21-87ef-da772d1d7ca2 | note | Acceptance / Conformance Criteria - Visual inspection
f33c2fcc-965d-519a-b236-1add7f5ebfeb | note | Standard / Specification - NTC0097
7163238f-bb09-5afe-b3c4-2ed2e843063b | note | Verifying Document - Visual inspection
84a43778-2257-5475-b88b-85c9a9965bfc | note | Testing Quantity Required (based from schedule qtys) - During Construction
d85dd530-711a-5d5e-85db-f30828ae2579 | note | Verification Activity: Activity - WP
09bd55a4-d788-52d1-885d-c29af9dbaeb1 | note | Verification Activity: By - ENG
338c6efd-e82a-4f78-9c2b-7c61229059e6 | checkpoint | 3.1.2 - Onsite Check by Engineer on Geogrid
f175aafa-ff75-5530-bff0-b1b29e410842 | note | Detail - Installation of Geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied.
ee3f5e08-ae98-5477-9f94-56515cd76db8 | note | Acceptance / Conformance Criteria - Visual inspection
e15cce84-4569-5ce6-b0bc-42974134ec8e | note | Standard / Specification - NTC0100
8bb1afa1-98c4-576d-85a2-7f5b55878970 | note | Verifying Document - Release of hold point
8a8e3eb0-7550-547d-b9ea-f80ad85d7cb8 | note | Testing Quantity Required (based from schedule qtys) - During Construction
f188a9ad-9203-57f2-9d4e-f068cf2dd6ed | note | Verification Activity: Activity - HP
ee8c54a6-cfe4-5402-a6ea-d934289b2cb5 | note | Verification Activity: By - ENG
ebca47be-adf2-42cb-b0e8-1d79226d4e89 | signoff | AUTHORITY HOLDPOINT
c71f9c33-c3bb-4a16-9c09-576dc5c93a6d | checkpoint | 3.1.3 - Placement of Geogrid
14c883c2-6149-57dd-b9c6-fef5343dee17 | note | Detail - The Duragrid X 30/30 Geogrid shall be placed on top of the Geotextile Fabric, and overlap areas of structural fill by a minimum of 2m, or as directed by the Engineer on site where the layer depth of structural fill is insufficient to limit deflections from the subgrade.
ecd73193-6ed2-5356-a5c7-bc99d432fe3d | note | Acceptance / Conformance Criteria - Visual inspection
f172ec27-ef2c-563a-8454-2ad283febd0c | note | Standard / Specification - NTC0100
4cfb6987-4676-509f-b9c0-6ce88b7949ce | note | Verifying Document - Visual inspection
cc829193-e4dd-5054-a211-f594b6bb7488 | note | Testing Quantity Required (based from schedule qtys) - During Construction
0ce068f0-90d2-5737-85b7-1c0c5afc5f97 | note | Verification Activity: Activity - WP
3a8f6cb4-dd80-5562-99b5-6a9e6d825953 | note | Verification Activity: By - ENG
fbcbf2b1-81f7-4986-8cd1-26a9f961891f | section | SECTION 4 – CONSTRUCTION - SUBGRADE IMPROVEMENT LAYER TESTING
1704f5f3-813a-451b-8350-6539109f8764 | checkpoint | 4.1.1 - Plateau Density Test
d20b8454-0a71-5b5d-9de6-a8bc0783abc8 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
1906fb20-dfd8-5164-8055-a601639d0293 | note | Acceptance / Conformance Criteria - Plateau Density Report
3899a4e8-dbed-58bd-a5c4-c06bdd7c599b | note | Standard / Specification - NZTA B/02 7.5
7dee8da4-3abd-5333-b01e-ca920e02aac2 | note | Verifying Document - IANZ Accredited Report
49c7d788-8bdb-5ba4-aa55-f4e91ee23a83 | note | Testing Quantity Required (based from schedule qtys) - 1 Test
11bd93fd-033a-5aba-88b0-007a807fbdd3 | note | Verification Activity: Activity - I
90266214-703b-59a4-98e3-ec252004b543 | note | Verification Activity: By - SE
4b261cdf-29bb-4ba6-8410-636087589e2d | checkpoint | 4.2.1 - Stringlines or equivalent
acd4d31d-35cf-5476-802b-26d4e9ab0061 | note | Detail - Stringlines or equivalent to check finished height of surface
1390d1aa-dd4e-5791-bc2b-86202a05902a | note | Acceptance / Conformance Criteria - -25mm + 5mm
222be1c3-0989-585f-b36d-8e91fa834747 | note | Standard / Specification - NZTA B/02 5.1
026430b0-f816-5c71-8d42-dad78643623c | note | Verifying Document - Check Sheet
9e4f3e48-0eed-5a1e-82e7-acb2695d94ca | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
3106f911-17ec-5914-a2f7-5f0d4121ac93 | note | ○ 1 set = 5 tests
abac6be7-1b1b-5b26-b889-78975326050e | note | Verification Activity: Activity - I
f683f145-337e-538b-8790-cd36b0a0815a | note | Verification Activity: By - SE
557190b8-78ed-4a1b-848c-9aae1f23200c | checkpoint | 4.2.2 - 3m Straight Edge
30ab32ee-126f-5e5f-ac4f-d04babf3b550 | note | Detail - Formation to ensure Surface is Smooth
cb8b92dd-33e8-57de-bd35-363f38337111 | note | Acceptance / Conformance Criteria - 10mm (-/+)
6b757d8b-cc88-5c54-83de-fca6fdca3f88 | note | Standard / Specification - TNZ B/2 7.7
2f23cf18-39af-562e-b235-3c32687466cd | note | Verifying Document - Checksheet
0ffbd940-f8af-5f60-b80d-fb802e616a33 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
f3ebe210-1b2a-5f61-b8f2-c295a9089e58 | note | ○ 1 set = 5 tests
2e14658f-0dc5-5925-9921-977da8f356f7 | note | Verification Activity: Activity - I
f25bcbcd-404d-50c2-8753-e2ccf470adc8 | note | Verification Activity: By - SE
8be63174-fd88-450a-95c3-4dac90f9fd6b | checkpoint | 4.3.1 - Compaction - NDM
717a34f7-6bee-5e34-9696-e96e9862abd2 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
43809d09-f875-5aca-8a76-06c43f717d9f | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
54197f0c-5f9c-5ddc-a409-2a0cdf749d6d | note | Standard / Specification - NZTA B/02 7.6
09c94633-54d1-558a-8c0c-0ae5721a2af2 | note | Verifying Document - IANZ Accredited Report
3764b5a7-c79d-5993-8dcb-8c23b881457f | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
789f8aed-98b1-5e2c-8f38-c55a6b10c38d | note | Verification Activity: Activity - I
875c8ad1-936f-58e2-8c1e-071a7ce15554 | note | Verification Activity: By - SE
a19a27c7-a9ef-4277-b0a7-692c153fc285 | checkpoint | 4.3.2 - Benkelmen Beam
3294d61a-787c-55d1-a25d-0bbd6ca63eb1 | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
d6beeffd-da45-5ec7-a03f-f0080a10ce7f | note | Acceptance / Conformance Criteria - Engineers Approval
ccec9286-6f1e-5a9a-b1cd-503c58bce4a8 | note | Standard / Specification - NTC0160
10858f74-8d79-5369-bd4c-bed2c91f1154 | note | Verifying Document - IANZ Accredited Report
2d697e00-3da5-5e21-81ff-f49da10ed5dd | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
7f81cd92-dd78-5e67-85c5-8864953fe165 | note | Verification Activity: Activity - I
13638ca2-63e4-572d-8f0c-d21f90c66d82 | note | Verification Activity: By - SE
9738961a-32d5-48e4-8dce-4600f1cc52fc | section | SECTION 5 – CONSTRUCTION - SUBBASE LAYER CONSTRUCTION
63bd97ee-d1aa-4e34-b364-c47f2e0d3a74 | checkpoint | 5.1.1 - Plateau Density Test
4c14623e-087a-5003-b580-83605dd345a0 | note | Detail - Using a 14T Roller carry out plateau density test to determine optimum rolling pattern using static and vibratory passes
9e13c42f-712f-590e-af6d-afde073c31c2 | note | Acceptance / Conformance Criteria - Plateau Density Report
b413c405-6334-5b84-b7f8-757eb970bccf | note | Standard / Specification - NZTA B/06 7.6
aaa98e93-236c-52c3-afc7-ea42fc8a6969 | note | Verifying Document - IANZ Accredited Report
dcc00793-da02-5953-bc0d-8095bd646f4a | note | Testing Quantity Required (based from schedule qtys) - 1 Test
3e7445c1-f9a9-501f-bbd3-713df8c3de3f | note | Verification Activity: Activity - I
cbf471ca-fd30-5ced-9480-1ea3fda7b378 | note | Verification Activity: By - SE
e5de0bc4-6402-439f-b2b2-d70d4f4dff91 | checkpoint | 5.1.2 - 3m Straight Edge
e0062508-838a-55ac-a444-2d7b2b12a864 | note | Detail - Formation to ensure Surface is Smooth
adc187d7-3ac4-559a-a33a-560d596a78f3 | note | Acceptance / Conformance Criteria - 10mm (-/+)
b5bc08ea-9248-5f27-a41e-191aa2f302f9 | note | Standard / Specification - TNZ B/2 7.7
f0cab3b9-cb57-592e-9eb2-542b3ae44641 | note | Verifying Document - Checksheet
b481e96a-6596-5012-91ff-fe122552dec1 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
b69d0fa3-b75c-5777-bb56-72d36b99f810 | note | ○ 1 set = 5 tests
ea758b56-768c-5ae4-8db6-708bac46ad42 | note | Verification Activity: Activity - I
523e7a28-255b-53a2-9e1d-4b6de3df4239 | note | Verification Activity: By - SE
699bb454-a9af-40da-b774-cf979b2de58b | checkpoint | 5.2.1 - Stringlines or equivalent
4dcfed96-99c9-56ee-b967-194e1481bf56 | note | Detail - Stringlines or equivalent to check finished height of surface
f768d0a3-9501-5099-a153-c2edd7b7482b | note | Acceptance / Conformance Criteria - -25mm + 5mm
a2afbe27-e29b-5c9b-8a8a-389f6a93359d | note | Standard / Specification - NZTA B/02 5.1
7e84b04e-ec1a-5622-81da-a3ffff5d294d | note | Verifying Document - Check Sheet
4288ed40-e6d3-52e5-bd37-35ab5e9f9de7 | note | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
ffd61f7e-7a81-5216-8f48-bf2cc6c86d0d | note | ○ 1 set = 5 tests
8022486e-46ab-535e-bb9f-204837cc058e | note | Verification Activity: Activity - I
6e076803-dc5b-5e56-957a-c5348ba3f75b | note | Verification Activity: By - SE
5ead6841-8b6e-4765-b03f-e66a46bd9b64 | checkpoint | 5.3.1 - Compaction - NDM
9883deee-6625-5220-b4a4-8f8fed8a9a8c | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
40418678-dc6f-5c87-941a-16d35afbdc54 | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
7aef05f9-7877-5335-9f51-cdb62c94aece | note | Standard / Specification - NZTA B/02 7.6
3d5b493d-0b87-56f4-a9aa-b5cb1b965587 | note | Verifying Document - IANZ Accredited Report
b4c7bafa-4a35-5bc6-ab63-18b6c74caa26 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) 1000m2
2144d8b0-692e-50da-bd0d-19b640e6f682 | note | Verification Activity: Activity - I
28c9a76f-0dbb-5ee7-b2c8-c55846dbdb02 | note | Verification Activity: By - SE
742d5d2d-bcbc-4c61-b8d8-9c21cae16026 | checkpoint | 5.4.1 - Benkelmen Beam
99e0bd81-202c-56ae-8928-5d60a134559d | note | Detail - As directed by Engineer 15m staggered by wheel path for each lane.
585fb1f6-7545-595f-9644-04fdcbaf6ee1 | note | Acceptance / Conformance Criteria - 90th Percentile: 1.65mm
459bdca6-9fe4-55b4-b320-d07e54e0cb4a | note | ○ Maximum: 1.82mm
a5a3e3f4-c218-5e64-bccf-8d1d839b47ee | note | Standard / Specification - PS 20.14.5, NTC0160
6016dbba-230b-5b61-8b52-0645f3f92644 | note | Verifying Document - Test Report
828d0f2a-f3dc-5334-8f1d-65e7eac400fb | note | Testing Quantity Required (based from schedule qtys) - As directed by Engineer
da3bd737-4b0f-5728-ae44-5c4539220c2e | note | Verification Activity: Activity - HP
456c958b-1442-5619-9e54-341c65e634db | note | Verification Activity: By - ENG
6404f98d-2b4e-42f6-abfa-e0616be5a8e4 | signoff | AUTHORITY HOLDPOINT
9c66bbe8-e2dc-4215-a2cc-f8febe1ac75a | checkpoint | 5.5.1 - QA Submission
09edb72e-e3f5-578a-8698-3cf344255300 | note | Detail - Submit all Subbase QA before proceeding with next pavement layer
b57d9c15-f27c-5941-a209-dfbb77a4eb52 | note | Acceptance / Conformance Criteria - Engineers Approval
2e19410d-6613-5a01-95b6-65c191d2f435 | note | Standard / Specification - Appendix V
ce10e081-cb19-5203-a909-f4ab6e1a88bc | note | Verifying Document - All test reports
7cf858a4-53a5-57f8-97ab-43b7f58dbb33 | note | ○ Material Test Results
10af2f79-b9e2-5f4d-9f67-c1f0942f1567 | note | ○ Laboratory MDD
13882438-a99f-5834-a88f-e9657b0604f8 | note | ○ NDM results
e94205f5-053e-52e4-a4fd-b7c941a83ec7 | note | ○ Proof Roll - hold point release
bbe0949e-dd4b-52f0-9f06-611216241e4f | note | Testing Quantity Required (based from schedule qtys) - Once
077a59ca-7715-55d2-8546-c08060cfaa2a | note | Verification Activity: Activity - HP
9072c04d-ff29-5a1d-bafc-74a05664e877 | note | Verification Activity: By - ENG
9ec6aac2-84e6-481b-a785-a4280d55de09 | signoff | AUTHORITY HOLDPOINT
cf4fcf3a-db8a-46f3-8d15-a01e45a57941 | section | SECTION 6 – KERB & CHANNEL PREPARATION
899b90e0-68ad-4db5-afe2-ab3565534027 | checkpoint | 6.1.1 - Stringlines or equivalent
1023fa29-0365-5640-a125-4b9194fda1af | note | Detail - Stringlines or equivalent to check height of surface prep
09836910-0b50-565e-b7c4-7c6d7294dd18 | note | Acceptance / Conformance Criteria - +/-5mm
ff906209-dc1d-5eec-ac42-ca17aba1b273 | note | Standard / Specification - PS 21.7.6
2df1ed5f-7510-5e59-8fdc-d0b88ab03ac0 | note | Verifying Document - Check Sheet
03ba536b-388d-5815-a7aa-9046fe85c9ee | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
adca65cb-4597-59d3-a134-190229d2b318 | note | Verification Activity: Activity - I
22f45d27-0a35-51e9-a8b5-650f4b954a32 | note | Verification Activity: By - SE
56062c06-c70f-4339-9c2a-9f50d3e46d4e | checkpoint | 6.2.1 - Compaction - Clegg Hammer
593dd740-efe5-5ca1-a813-9a0ac77a8f7d | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
c686f1a3-ff3f-5c5c-8364-7e157e3bd27c | note | Acceptance / Conformance Criteria - Min 25 CIV
3adf654a-51e1-5788-924e-c63c8dc7dd63 | note | Standard / Specification -
0a712ddd-b43d-5a7a-b9e9-6210807354db | note | Verifying Document - Clegg Hammer Report
c8a23c6e-0465-5d8f-94f4-dc94b617e42d | note | Testing Quantity Required (based from schedule qtys) - 1 Test along kerb line @ 20m centres
120b7062-749b-595b-a801-fdb79ce0ec77 | note | Verification Activity: Activity - I
94ef0de0-2e6e-51c8-b163-2f386f98d2fa | note | Verification Activity: By - SE
34d44896-ab9f-4e6d-8198-14c0b0ff4f7e | section | SECTION 7 – AS-BUILTS / REDPEN MARKUPS
4426daa7-0945-4c5b-b2d2-a9e07780d211 | checkpoint | 7.1 - As-Builts/ Red pen markup
e497ebc3-4169-51d7-8384-c2936a11240c | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
f018c892-11c1-564f-b62a-498f545fe7d9 | note | Acceptance / Conformance Criteria - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
bc21b89a-3b01-5d23-9d50-8461234324a3 | note | Standard / Specification - PS 16.7.6
f3ac0088-aa92-54af-be63-f134c925a8bd | note | Verifying Document - Red pen markups
7ea5d3fe-3c3a-5225-9a9d-0c262c9f8c4e | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
f02dda16-b68a-5242-b10b-93792cc26ec2 | note | Verification Activity: Activity - D
f7524803-8c31-53aa-98a4-663b27aabb3e | note | Verification Activity: By - SV
f51cc6b0-67e6-4391-8af4-ec53016ad791 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
a35e0753-1be5-5fb5-b671-f795abe98c53 | textbox | Contractor's Rep Name:
21ac8f41-6f1c-53d1-8199-539e5db86886 | textbox | Engineer's Rep. Name:
663b7691-31f8-5c72-b576-0f8d31f79366 | date | Date:
f72d9537-a070-4711-97d7-ea25994662b5 | signoff | Add Signature
7ae85e6d-e36b-474b-9708-3aa234363a58 | checklist | DN1210-SP2-003 ITP Northern Access & Carpark Earthworks Rev 2 | itp | DN1210-SP2-003 ITP Northern Access & Carpark Earthworks Rev 2
63a52af8-1190-4aa1-aa8a-3e2aac889874 | section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS
c99d133e-a9d8-4077-8b7c-ab05ed2243e9 | checkpoint | 3.1.1 - Earthworks Construction Pack
10167ebf-16d3-5965-a2a7-a9efdb8611e4 | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points on Ineight for review and approval prior to works.
200adc43-adea-5a43-b827-5e6b62b4f172 | note | Acceptance / Conformance Criteria - Engineers Approval
0658ea2d-5070-58b1-b576-b23f140df0db | note | Standard / Specification - Appendix V
7cdb9548-1353-588c-a295-a0c02a5c71eb | note | Verifying Document - Approved Methodology
5aa44755-771d-5682-8997-5495a129dfd9 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
a4c78a33-c13f-5b55-a94a-09b95164990d | note | Verification Activity: Activity - HP
8dcb9355-345c-5dcc-ab62-c4c3a03c3d61 | note | Verification Activity: By - ENG
99b40231-0dff-4397-94bc-a4acf99978c5 | signoff | AUTHORITY HOLDPOINT
d8878d0b-2b26-4ab7-8850-f3be976859fd | checkpoint | 3.1.2 - Ecology Sign Off
913f5562-3c13-5b0c-9628-8014969cb2ea | note | Detail - Confirmation from Ecology that earthworks can proceed
3c301350-739a-5b41-bec1-2c868cc3765d | note | Acceptance / Conformance Criteria - Email
c215de2b-e4a6-5ffc-b565-14a1ae8df301 | note | Standard / Specification - Internal Hold Point
082cd810-4b83-5ffb-917d-2cd1fb764d72 | note | Verifying Document - Email from Ecology NZ
1bdf8d5c-9ae7-5db5-8d82-2bbf2e05a1c5 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
ec630dd6-6b4a-5fdf-b256-32e74bc0739d | note | Verification Activity: Activity - H
077477e0-1e7a-55f1-aa16-cf058c9d80b1 | note | Verification Activity: By - SE
1038659f-f4d5-4d45-9cb8-05e6cd4f28e2 | checkpoint | 3.1.3 - Erosion & Sedimentation Controls
c4ca9a21-81d1-5891-945f-dc303805393c | note | Detail - Confirm that Erosion and Sedimentation Controls are in place prior to earthworks proceeding
be8591e6-572a-5608-ad25-1c1bcb578f58 | note | Acceptance / Conformance Criteria - As-built Completed
83980992-ea22-54da-ab28-6427baef82d1 | note | Standard / Specification - Internal Hold Point
a6ce45af-19db-5de2-9da9-bd6e3859bbbd | note | Verifying Document - ESC As-built
be2b67ed-1f4c-5930-bda8-99c463df4ae7 | note | Testing Quantity Required (based from schedule qtys) - Prior to Earthworks
2fad6462-4077-546b-bb09-acf3a329b3f9 | note | Verification Activity: Activity - H
52f429d8-ce41-5f83-9e9c-7572ed5a48da | note | Verification Activity: By - SE
d1caa6b3-2cd9-4f0a-aa38-f485771f9026 | section | SECTION 4 – MATERIAL, PERSONNEL, TESTING & THIRD PARTY APPROVAL
cf78bce4-1633-4c87-a313-89cbe60a7332 | checkpoint | 4.1.1 - Weathering Resistance
3a920aec-b935-5fc6-8bd8-5f41282c49c0 | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
627d90c5-613a-552b-ade2-7b442624d8b3 | note | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
f3391f72-c68b-5e01-b381-a9f51ad6081e | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
39c28b24-7d46-53d4-b84a-a4132fa7209c | note | Verifying Document - IANZ Accredited Report
d118443c-ee4f-5756-8aca-aa297378b25e | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
0e4b5027-674d-595b-9da2-ef3394e9a89e | note | Verification Activity: Activity - HP
49b04c1d-aca3-5324-a3c3-cfb09161aaed | note | Verification Activity: By - ENG
0145895a-37e4-4da5-8850-d292cf76dc8e | signoff | AUTHORITY HOLDPOINT
4fd16fda-09de-4762-a4d9-9815568f3d46 | checkpoint | 4.1.2 - Los Angeles Abrasion Test
e22fc0b0-1fe4-5858-bc47-5b3ff217f4a8 | note | Detail - NZS4407:2015, Test 3.12 - The Abrasion Resistance of Aggregate by use of the Los Angeles Machine
50c342e7-22bb-569b-822b-feddde72af4a | note | Acceptance / Conformance Criteria - 0.5
cfbf9a98-62eb-5a4e-9d0a-45bdd783dc5d | note | Standard / Specification - PS 16.5.5, Appendix V
e5cc0792-c4e7-58d3-b3fd-41a55a5c14f5 | note | Verifying Document - IANZ Accredited Report
20729fbb-b14d-51a4-8878-d870e39c4f93 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Required, Results to Engineer 2 wks before importing
f580c960-8790-57da-8a62-f2c3420dd472 | note | Verification Activity: Activity - HP
570710bd-1770-5ff6-872d-8908f0ef1242 | note | Verification Activity: By - ENG
2437aa78-a47c-4a38-8286-76b7e7dce074 | signoff | AUTHORITY HOLDPOINT
33b89a7b-955c-4638-9a39-8c4820593104 | checkpoint | 4.1.3 - Particle Size Distribution
faa1f97f-664c-56bc-94a4-6e9f06a60d13 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
aaaea570-aad9-5c94-8b24-eff6e7e571ff | note | Acceptance / Conformance Criteria - No Particles >200mm, Maximum fines 10% passing 75micron sieve
a929653b-5434-544e-93a4-2b9754dbb0bb | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
7d36b436-36de-5dd8-b926-3166d46e6028 | note | Verifying Document - IANZ Accredited Report
8bbf289f-876c-572d-8b87-50dbc570c688 | note | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
0283661b-6c56-5c5e-9792-3b218459dd81 | note | ○ 0-400 - 2 tests
cf939ca3-0b76-581c-9d20-a8795c9d143b | note | ○ 400-1,500 - 3 tests
9ae37699-97c1-5df8-b4b4-056e497e79c9 | note | ○ 1,500-4,000 - 4 tests
2aed5e33-1540-52d2-8e8a-80f74dac988b | note | ○ >4,000 - 1 test for each additional 1,000m3
d4c771ce-6e90-5721-8a76-391a504ee647 | note | – Results to Engineer 2 wks before importing
8e56868f-f5a4-54f1-9853-e073298224d2 | note | Verification Activity: Activity - HP
259475d6-1cfc-5b02-b135-bc4836cbe2f6 | note | Verification Activity: By - ENG
883b7dd6-99fe-4244-927e-0ce085e8feb6 | signoff | AUTHORITY HOLDPOINT
c34accc8-8fc6-4860-a9c1-faa4c7169acf | checkpoint | 4.1.4 - Maximum Dry Density and Optimum Water Content
d15fbba4-bb1b-5b28-a702-c8bd03fe4171 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
ac5af58a-8bee-5a08-b540-ede06f1557e6 | note | Acceptance / Conformance Criteria - Report Value Only
5edeb382-bf16-562e-b8ab-e9af8d6ab527 | note | Standard / Specification - Appendix XVIII, Appendix V
977abc37-1c4e-506d-a7f4-3f41d5fc0a59 | note | Verifying Document - IANZ Accredited Report
075372c8-4abf-55e7-886a-4e4d3689fa0f | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
a8bf1862-dc96-56a8-9211-4ec7715a433c | note | Verification Activity: Activity - HP
af8d7bc5-3165-5994-b7df-db161a39cb20 | note | Verification Activity: By - ENG
104656f9-73d3-4dfd-a1f4-1b0d3b55cf2a | signoff | AUTHORITY HOLDPOINT
84f16312-2375-4212-b3c7-0dcabc83c774 | checkpoint | 4.1.5 - Soaked CBR
3c415a71-daac-5975-9e6e-c73480ebdffe | note | Detail - NZS4407:2015, Test 3.15 The California Bearing Ratio (CBR)
9dfbc3ea-9b61-5fe4-81f7-3c94444858eb | note | Acceptance / Conformance Criteria - >25%
6cea0c44-3ace-59ce-84da-1314d6aee017 | note | Standard / Specification - PS 16.5.5, Appendix V
bf6cfeae-8d62-57ef-8722-c2d031491f52 | note | Verifying Document - IANZ Accredited Report
b4243790-51c3-598a-9cda-441a5e5af11d | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
a42c6419-12a5-507a-b618-49b14ae305d5 | note | Verification Activity: Activity - HP
587e0594-37c3-5e04-9d2c-aaf9282de255 | note | Verification Activity: By - ENG
4eac297b-c7f0-4d88-a3b6-1668845f81ac | signoff | AUTHORITY HOLDPOINT
920a3a52-130e-446a-9b64-457339e355f9 | checkpoint | 4.1.6 - Solid Density
dc9fa64b-1a9e-515e-bca0-1b809ce455d2 | note | Detail - NZS4407:2015, Test 3.7.1 - The Solid Density of Aggregate Particles
78856b6a-cd0e-52fb-b629-39a706b68276 | note | Acceptance / Conformance Criteria - Report Value Only
43f7b384-7963-5002-bd48-638c752db4d5 | note | Standard / Specification - Appendix XVIII, Appendix V
aba97eca-50bf-5de5-82be-86fee321e4c1 | note | Verifying Document - IANZ Accredited Report
594a4307-2a90-555e-b686-0a2959d4f3fb | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
1561d058-0399-5b8c-a919-4a87ac4ef96e | note | Verification Activity: Activity - HP
befe9656-72cb-5f45-8c15-780e4c11d84f | note | Verification Activity: By - ENG
1ef74505-c3b2-452c-97e1-0bab2365544e | signoff | AUTHORITY HOLDPOINT
882c9caf-ed08-44e4-8abe-de8e2d035ff1 | checkpoint | 4.1.7 - Crushing Resistance
8c884f04-30e7-5549-a730-b98b6b752bd1 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
9e43aec0-7f60-5ab6-9907-ecc3f7d45795 | note | Acceptance / Conformance Criteria - >100KN
1643e209-1fff-5b05-93a3-febf9ec2a53e | note | Standard / Specification - Appendix XVIII, Appendix V
d7960ff3-df73-52d3-bfe8-641a9dc9a487 | note | Verifying Document - IANZ Accredited Report
57a8d27b-1f64-5cea-9fa8-c09500b9d1f9 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
d910ed61-95ee-56d3-aedc-289f6efed97b | note | Verification Activity: Activity - HP
e69588bf-90dc-51f3-bfcc-635ece6ad6a5 | note | Verification Activity: By - ENG
64770687-0665-4822-8819-9d9e92ebbd3d | signoff | AUTHORITY HOLDPOINT
1ddda134-484e-4247-810c-cc1119235bf9 | checkpoint | 4.2.1 - Particle Size Distribution
9fc9fc49-fd65-50a4-9ceb-a8a174fe08be | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
ee8ff0d1-0700-5d3f-8f63-2c46c1c8d16b | note | Acceptance / Conformance Criteria - Report Value Only
504358a7-a60e-52b2-a706-c0ef575f3259 | note | Standard / Specification - PS 16.5.12
408c47c2-e85d-51e6-bda4-cd9aa94e6db3 | note | Verifying Document - IANZ Accredited Report
754ede11-d472-5541-bb71-5fb036f3bb97 | note | Testing Quantity Required (based from schedule qtys) - Number of Tests Required?
971d1fbd-8e5c-534f-a32e-9d3b86d4d66e | note | Stockpile size:
f2436c38-9fb7-5574-8320-7b3c4053c0e8 | note | ○ 0 to 400m3 – 2 tests
7c9d7a85-7f91-5889-b0a2-516b73940b45 | note | ○ 400 to 1500m3 – 3 tests
fff24328-ddf9-598c-bdc0-c8624cf47269 | note | ○ 1500 to 4000m3 – 4 tests
238ddab0-6a0b-5cc6-938c-754eaa1cd482 | note | ○ >4000m3 – 1 test for each additional 1,000m3
d5a186fe-6df0-5a60-9ad3-11656d0b8ad6 | note | – Results to Engineer 2wks before importing
872f81fc-22a0-5053-8a6a-f7cc28cfa732 | note | Verification Activity: Activity - HP
c4b82f3a-84fd-5050-946b-2737c424ad3c | note | Verification Activity: By - ENG
ab4b0173-461d-47d4-a957-46202cd78726 | signoff | AUTHORITY HOLDPOINT
43cc80bc-ece2-449a-a479-3ec1ee22cf5f | checkpoint | 4.2.2 - Maximum Dry Density and Optimum Water Content
21481602-b958-51b7-b1e6-f09d9db142f4 | note | Detail - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
6bbca740-a859-521b-9816-faa9d4656ad4 | note | Acceptance / Conformance Criteria - Report Value Only
fd93416f-22ed-50fd-b07c-9e2e431491c1 | note | Standard / Specification - PS 16.5.12
ef7d2497-3a0e-5368-9991-bb51ae96b815 | note | Verifying Document - IANZ Accredited Report
0879c2df-d090-566a-a994-8adf3f57b775 | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
53caa342-4777-54cf-bd25-d2543d38d462 | note | Verification Activity: Activity - HP
9d2dc668-53da-55b6-9ba8-d87bf4acb6f1 | note | Verification Activity: By - ENG
e7cc0a21-52ed-4ca0-9c2d-00452bf0e59c | signoff | AUTHORITY HOLDPOINT
2ea9ad43-096d-4006-8088-157471bfdd56 | checkpoint | 4.3.1 - Crushing Resistance
74bcea60-b38d-534b-b9b1-4cd481b19751 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
bcaadb54-e756-598d-b848-fd18a815e53c | note | Acceptance / Conformance Criteria - >100KN
051bad98-0e58-56a8-9976-22cbd0afe837 | note | Standard / Specification - Appendix XVIII
416e8571-ce24-55be-9672-10667c8b993d | note | Verifying Document - IANZ Accredited Report
f1c8e9d8-a4d6-531f-985f-c2d1c5a1afb6 | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
3ece5057-1a32-5c4e-b2cd-211ecb421171 | note | Verification Activity: Activity - HP
dc9563ad-9efe-5be4-aae4-f4233dde90bf | note | Verification Activity: By - ENG
91b0bdcd-ca84-4eb6-8543-0abdcedeeef4 | signoff | AUTHORITY HOLDPOINT
6501b0f3-6305-451e-833d-e2c704fa3e16 | checkpoint | 4.3.2 - Particle Size Distribution
a0c4eac5-8d73-5191-8d92-ecdc11fd6abc | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
be3a2de6-8804-50a9-976c-306a61943087 | note | Acceptance / Conformance Criteria - Max Particle Size 53mm
5e50098f-5357-5711-bd05-c175b7d20344 | note | ○ Max 10% passing 13.2mm sieve
f57b3101-33ac-5b87-9d97-f5ef90832701 | note | Standard / Specification - Appendix XVIII
d77b25c3-26a7-539c-9b74-e5e99d4e892d | note | Verifying Document - IANZ Accredited Report
8493d7ca-321b-5a00-a624-603e80481e67 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 100m3, Results to Engineer 2wks before importing
f47399f0-6185-5a5a-b510-87549ef986c5 | note | Verification Activity: Activity - HP
39f36664-0921-53e8-b3b5-cb2dcbd4dbaa | note | Verification Activity: By - ENG
f4b31f1d-c419-4a7b-ab46-cfdbbcd01bab | signoff | AUTHORITY HOLDPOINT
18d98917-5913-4e05-ae6d-6e3ddcfd731e | checkpoint | 4.3.3 - Weathering Resistance
b6bd5b3a-31d9-56cc-bc07-b82824279d4c | note | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
3a25ff9a-0f2b-5d41-836c-9b277c52cd5c | note | Acceptance / Conformance Criteria - CA or better
bec8936b-0cf3-57e9-8375-89779aa4ca3f | note | Standard / Specification - Appendix XVIII, PS 16.5.5, Appendix V
b3df6dd6-59d2-5588-b69c-0ee1a0b8da76 | note | Verifying Document - IANZ Accredited Report
e544816c-5b44-521a-97ed-4b02e63f729c | note | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source, Results to Engineer 2 wks before importing
c65a06a2-b3fd-511c-8f40-1c1215c307ed | note | Verification Activity: Activity - HP
b320dc08-a1b0-5f70-a477-236d2d6c3a8b | note | Verification Activity: By - ENG
2b883239-2884-4602-a1e0-48020171cbc7 | signoff | AUTHORITY HOLDPOINT
d79df45f-9160-4f0a-a1be-1ae1f2906bc0 | checkpoint | 4.4.1 - Geotextile
28283dee-4865-551f-a430-691a0144acb4 | note | Detail - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval prior to installation.
e8d090a2-f35a-5e74-b8fb-cead6aa100ce | note | Acceptance / Conformance Criteria - Engineers Approval
786ca4e1-67da-584d-8bac-04368df96589 | note | Standard / Specification - PS 16.5.7, Appendix V
7d0e5257-179b-5774-b372-1fdd03c14d01 | note | Verifying Document - Delivery Docket/Material certificate
4f96f9e0-1281-5701-a0ec-7aa48b55b52b | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
aae3c485-94e4-5688-8f44-32a7e9380398 | note | Verification Activity: Activity - HP
7959b4c9-e3c1-5002-b5a0-498ee47290b8 | note | Verification Activity: By - ENG
bb082231-2fb1-41ac-997c-2b319b671b9c | signoff | AUTHORITY HOLDPOINT
ff5c68c7-efe3-4689-a40c-0abf9d43c3b9 | checkpoint | 4.4.2 - Geogrid
aa440346-d8aa-52f2-ae5d-9c32c8176590 | note | Detail - All uniaxial, biaxial and triaxial geogrid shall be manufactured in accordance with a management system that complies with BS EN ISO 9001 and BS 14001 and shall submit to the Engineer for approval.
f157f831-aff3-5b3c-81dd-e591d74e730f | note | Acceptance / Conformance Criteria - Engineers Approval
54297783-3595-5f7e-b03b-f7063d2340e8 | note | Standard / Specification - PS 16.6.5, BS EN ISO 9001:2000, Appendix V
74201647-bc89-5064-96d7-dc3f531333f5 | note | Verifying Document - Delivery Docket/Material certificate
ce76eafa-eb0b-5e90-979e-8be7e17d58b3 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
faef31c0-88eb-5cd3-97e3-28c7c24fac3e | note | Verification Activity: Activity - HP
19ed23e7-3836-511f-9788-52ea5598bb77 | note | Verification Activity: By - ENG
8c8c90b3-36fe-4353-93b4-b03191ca5b2a | signoff | AUTHORITY HOLDPOINT
cff04487-cf30-4917-af0e-0d37456176b1 | checkpoint | 4.5.1 - Laboratory Testing for Soil Suitability
11d2c865-cb90-5ea6-8aab-4b314e348841 | note | Detail - Soil Test Results from Hill Laboratories to confirm that topsoil suitable to for reuse Soil Reaction
a58df18d-48e2-5a2d-b065-774c85d88442 | note | ○ Electrical Conductivity
d94e7b64-5b58-582c-b37b-39f9e428437a | note | ○ Mechanical Analysis (texture)
5a1ec5ad-e143-51cc-b26e-2514a84b2555 | note | ○ Stone Content
bd32f399-9eb6-5802-9457-e19381c7ce8a | note | ○ Nutrient Levels of nitrogen, available phosphorus, available potassium and available magnesium
f57884db-8128-5ebb-b0a6-10fad5247479 | note | ○ Organic Matter Content
81eb07e9-17d9-50e4-a40c-e19005edaf7f | note | ○ Check for Toxic or Hazardous substances
768cc8f0-ed50-5d8a-a8cb-caf006ff1203 | note | Acceptance / Conformance Criteria - Engineers Approval
64c33bf3-a63f-5229-a9b3-f4588d846ce1 | note | Standard / Specification - NZTA P39:2013 3.1
ebe8106c-b706-57ac-bc2e-9502b2a10c0f | note | Verifying Document - Hill Laboratories Test Report
9f220b6b-699e-5885-bf8e-045064a6e63d | note | Testing Quantity Required (based from schedule qtys) - 10 equal samples taken from site, mixed together, then 1kg of soil sealed into a plastic bag and sent to lab for sampling
af757549-701f-5ec5-a456-bc30ebc3218c | note | Verification Activity: Activity - I
67708aaa-3e79-5031-9765-2505462e11a7 | note | Verification Activity: By - SE
8d2f7f28-9383-45d1-9f1f-677283936a57 | checkpoint | 4.6.1 - Crushing Resistance
7127ac6d-1699-5657-a806-6e38ad36e445 | note | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
24c8e50b-948e-5cda-b092-5085d93bd653 | note | Acceptance / Conformance Criteria - >100KN
2fe45093-e78b-5f0a-9e96-a7f2e1d535fd | note | Standard / Specification - PS 16.5.15
db647343-6a32-50d8-97ad-b1089b670f39 | note | Verifying Document - IANZ Accredited Report
46b98987-6231-5143-810b-b004ae4e5feb | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
89a77fa7-c55c-5f83-964f-7b3d040eef2f | note | Verification Activity: Activity - HP
394ff6ac-5235-5006-8e46-cdd9b0b67a27 | note | Verification Activity: By - ENG
0a7472d2-7c0b-4dd4-86e7-886605947e29 | signoff | AUTHORITY HOLDPOINT
25ceaf3e-a8d9-44fd-8fae-a8428feaa7d1 | checkpoint | 4.6.2 - Particle Size Distribution
50798836-e42d-5cba-ac5a-2988bce9fb41 | note | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
f89e8adc-3caa-5502-96a2-101286521281 | note | Acceptance / Conformance Criteria - Max Particle Size 130mm, Max 5% passing 19mm sieve
ac62921d-59dd-5d5a-b065-c0d2e5f14baa | note | Grading:
c6ad294a-e4ac-5152-b9e3-99adc546ee05 | note | Sieve Size ¦¦ % Passing
2ece2c6a-d34c-5168-b51e-00ac91207e9b | note | 130mm ¦¦ 100
a7b74c18-be2f-5192-9e1c-408f2e98fbd3 | note | 100mm ¦¦ 70-80
b806526a-4b19-58ed-a0e6-1f4ff51bffe4 | note | 63mm ¦¦ 40-50
8fd6533d-e7af-5ad8-bad4-033e6502359d | note | 37.5mm ¦¦ 20-25
06fa4641-87ae-5f5f-a7f1-ad8e7610d8aa | note | 19mm ¦¦ 0-5
ef91176a-8e03-5385-aec6-83f168b95c84 | note | Standard / Specification - PS16.5.15
097d27fc-3e2a-5413-8d77-e20f65e74381 | note | Verifying Document - IANZ Accredited Report
ba5af504-3836-5f5e-88d0-eeeeb2672e5d | note | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source, Results to Engineer 2 wks before importing
cac7277c-5672-5681-8032-fdb2d169a4f9 | note | Verification Activity: Activity - HP
ba90e3ba-c441-5f93-ae91-28d1aefdd5bd | note | Verification Activity: By - ENG
5244dfca-6304-4859-8657-cf713071285b | signoff | AUTHORITY HOLDPOINT
be483645-c21f-4675-b4e6-62b8696f1903 | section | SECTION 5 – CUT SUBGRADE TESTING
dfc0978b-38b8-4b8d-81d1-44e40f83afca | checkpoint | 5.1.1 - Proof Roll
098a4dfc-dfb0-5a2c-8ec4-ad9db56d9f66 | note | Detail - Visual Inspection of Proof Roll
d08e3ab3-5d57-5f3d-8246-8eeccd5ec8a7 | note | Acceptance / Conformance Criteria - Displacement <15mm
d136410d-c24c-58de-ace6-5363edcb13e9 | note | Standard / Specification - Appendix XVIII
5d797d84-3e15-54af-bc88-20a78fbc1d21 | note | Verifying Document - Visual Observation
0b78dac1-fb93-5477-9295-79682b2adc77 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
ffc402ce-0c33-5438-a154-610b3dc23646 | note | Verification Activity: Activity - HP
497b7d19-aa07-5e67-bbba-77bad0f89c45 | note | Verification Activity: By - ENG
89ac51aa-9619-4d63-bde0-f03f672a4173 | signoff | AUTHORITY HOLDPOINT
b51917db-1f28-470a-9806-d857f775ba73 | checkpoint | 5.1.2 - Cut Subgrade Inspection
51bb84cb-b6e8-5a69-95e5-626ab7e46970 | note | Detail - Engineer to inspect all foundation surface inspections
d79755e6-34af-5e2b-8d1e-93ba2ca86e10 | note | Acceptance / Conformance Criteria - Engineers Approval
ebaa6c50-d055-5444-b433-ea6c9bc37de7 | note | Standard / Specification - Appendix V
791e8dc0-2308-5ea4-84c0-08a1fa129e5e | note | Verifying Document - Visual Observation
b10d2496-eb16-5d58-8761-afb4f804a97c | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
e739f339-3f77-5620-bc1d-151267ce68c8 | note | Verification Activity: Activity - HP
0ffc3abf-f81b-5aae-9387-983c2772393a | note | Verification Activity: By - ENG
fe71315d-d86c-4ac2-8d13-90a2a270ed75 | signoff | AUTHORITY HOLDPOINT
f568b83a-74a1-43ba-b0f6-1fe2131c604e | checkpoint | 5.2.1 - Cut Subgrade Testing - Cohesive Soil Shear Vane
d1bdfe48-979b-5de1-9ff1-3a84a7e9f657 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
9e2ad0be-5bd3-5940-84cc-4d36d58abef0 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
2ef57dfb-4d5d-56b0-9b37-45b2be16f941 | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
eb3c9ee2-7ba1-52dd-b0ec-bfce8092b595 | note | ○ Single Test Min SU: >50kPa, 2-3m deep
e3a57475-597c-5c47-ac56-f484936f8739 | note | Standard / Specification - Appendix XVIII
9bece1b8-e49b-5d52-844c-582d31917804 | note | Verifying Document - Shear Vane Report
e3952059-d267-59f4-a947-ff1ae1904035 | note | Testing Quantity Required (based from schedule qtys) - 0.5m interval, 4 test per 400M2
ab7e2dec-9301-5f14-895f-0b9107098bb6 | note | Verification Activity: Activity - I
eb223c11-ede7-5c2f-96d5-c9140d94dd9a | note | Verification Activity: By - SE
8b04bba0-3e53-4c7a-a6ce-8e6b89b7ede8 | checkpoint | 5.2.2 - Cut Subgrade Testing - Cohesive Soil Scala Penetrometer
0acf793e-d137-570c-9925-f4026b1e4930 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
efbd34b5-d40f-56b2-a973-96f4000ebf5a | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
d361eed9-c00a-50fa-976e-d1e8d1ec793c | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
89476ac3-6e9e-5a24-bbec-bd97a011393f | note | Standard / Specification - Appendix XVIII
9c1be8ba-1563-5d74-917d-b5e07ce6cb43 | note | Verifying Document - Scala Report
28b14fde-5db8-5d0f-9ade-614649931d75 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
e4ae1aa2-af42-51ff-9c1f-1e965de3a3b9 | note | Verification Activity: Activity - I
61c1477a-0d84-56f9-a0f7-5f93faf95339 | note | Verification Activity: By - SE
dbf6344d-29bd-4591-8fa4-d0420808f0ed | checkpoint | 5.3.1 - Cut Subgrade Testing - Granular Soil Scala Penetrometer
b8446bc3-e5ef-5ae7-8d1c-8e6c62a77849 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
c5af1f06-7744-554a-bcc0-305fcf3b6fcc | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
40aaeb85-2db9-59ea-bc62-0eb01c3f5294 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration, 2m deep
57c24a30-6044-5bdd-96e9-8811abdbbcd3 | note | Standard / Specification - Appendix XVIII, PS - 16.6.5
ca971eb5-06c9-57b2-a591-bc6d9f953eb0 | note | Verifying Document - Scala Report
3ff8e003-8f9e-5f9d-8ad5-37ce3eb92753 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
6a4b7cc2-dd21-547a-9e0a-0f2eb6170540 | note | Verification Activity: Activity - I
00fc9fdb-4279-54e7-aff0-7928e3bd3dc3 | note | Verification Activity: By - SE
35c58996-e979-4edd-ab81-95cf3292a042 | checkpoint | 5.4.1 - Release of Hold Point
ae80a22f-bb21-5913-808d-eb2b3c8bb618 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
f0454278-57b3-57b8-99e7-c5fe6815bf1d | note | Acceptance / Conformance Criteria - Engineers Approval
07df8add-1601-5ef6-a8d3-3e5b35efa1d4 | note | Standard / Specification - PS 16.9.3
a10fd2c9-cce7-5992-b11f-86216c277950 | note | Verifying Document - CONQA Approval
0888c961-40ae-5682-ba6a-a1b791ec9e0f | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
8d437422-039f-5b46-a41f-bc524882f7e2 | note | Verification Activity: Activity - HP
9140f5a1-dfc8-55f1-8ab7-93bf60b9194f | note | Verification Activity: By - ENG
08a66dd7-101a-4de4-804e-2d1241183392 | signoff | AUTHORITY HOLDPOINT
84b73365-bef8-46ab-b379-0e77985630cb | checkpoint | 5.5.1 - Subgrade Level Confirmation
978866de-77f6-5342-823e-f636fe33fc19 | note | Detail - Confirm subgrade is 735mm from finished height
8a22d0d9-2c5e-5265-bf43-1953dcf354c1 | note | Acceptance / Conformance Criteria - String lines - or equivalent are 735mm +0mm/-30mm
b2872315-e3e0-52c8-a93c-8045c42622c0 | note | Standard / Specification - PS 20.14.5
4f173124-a627-5ac7-bef5-408cd8953a98 | note | Verifying Document - Survey as-builts
e17bb15e-0e57-56f5-be02-9172dbc289ec | note | Testing Quantity Required (based from schedule qtys) - Every 20m chainage
237ed36d-3b50-5a5f-bbb9-540dbe738241 | note | Verification Activity: Activity - I
7dbced6f-5bcc-5e48-ac45-7ec869714a02 | note | Verification Activity: By - SE
6efa6117-2285-4e55-9090-577bdf42996b | checkpoint | 5.5.2 - Subgrade CBR Testing
7e0b6f12-df06-5a43-b1b4-fbfb4c1e3548 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
84d5b86a-4d52-51b8-88e0-720b103ff87f | note | ○ Testing of the Subgrade where no Structural Fill has been placed, Scala's to be carried out. This test shall be undertaken on the cut surface to a depth of not less than 1m
cb3e2e99-7599-5da0-a276-d4f07e6dc83f | note | Acceptance / Conformance Criteria - Pavement Type 1
5b72eb2d-08fb-5a92-8114-8a2e7d8f7cb4 | note | ○ CBR >6
5a517362-2140-500a-a281-7375a68e64f9 | note | ○ Min 3 blows / 100mm
3db91f7d-6715-5c6e-ba40-b8193970f36a | note | – Pavement Type 2, 6, 7
6fde8757-b4d9-5d5d-8352-0d957d8e4d8a | note | ○ CBR >2.5
9801f996-a34b-5ce4-a61d-5be1a0d3d1db | note | ○ Min 2 blows / 100mm
41238e87-7765-591d-9585-aa1ca0080c40 | note | – Pavement Type 3, 4, 5, 8
2cbc3cbf-97b8-5269-a8f2-4169cfdac5a9 | note | ○ CBR >3
2bc56818-f4c2-595f-bcd3-2aecf29d09a9 | note | ○ Min 2 blows / 100mm
9e07dfdb-c580-5ad5-8776-21223f830f3f | note | Standard / Specification - PS 20.4.1
4265bbf5-dc54-58cd-a99f-46ed1fc9ab16 | note | Verifying Document - Scala Report
caf15e9d-4393-54f7-b32d-e5cc60ffcf09 | note | Testing Quantity Required (based from schedule qtys) - 1 test per 100M2
1d0e3c60-79f8-5539-9489-3f7ad1db14f4 | note | Verification Activity: Activity - I
2b1a036d-1b4e-53c0-94cc-65b87411f4a3 | note | Verification Activity: By - SE
914c6b79-0ff0-4745-b2d9-1c3edc76d5af | checkpoint | 5.5.3 - Release of Hold Point
66fad841-4980-55e6-a7e4-30a79e0cb2a1 | note | Detail - To release the subgrade hold point and be able to start placing pavement layers, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
111e6026-9a21-5c35-8fae-082cfd42a485 | note | Acceptance / Conformance Criteria - Engineers Approval
705e553b-66c8-56bb-89f1-5507a9686269 | note | Standard / Specification - PS 16.9.3
2b62974a-60e7-5a0e-b744-aaddd091076d | note | Verifying Document - CONQA Approval
72bcf30e-1a4f-5b63-a5ca-21bb3c66df1f | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
e44537c4-93a7-5159-9110-a0502f5e6e5b | note | Verification Activity: Activity - HP
492dd4d6-8c56-5755-9aae-2b8dcc41bb04 | note | Verification Activity: By - ENG
65d37d78-1c8e-400b-81ef-ea4e1062c492 | signoff | AUTHORITY HOLDPOINT
8117beef-b5fd-4fb2-8198-6009aa3fa232 | section | SECTION 6 – CUT SLOPE INSPECTIONS
c414198a-45f6-49bd-94cd-b22c6710e237 | checkpoint | 6.1.1 - Cut Side Slope Inspection
023cc0a1-3b0c-5773-bcf5-90033e4e93ac | note | Detail - Inspection records to include photographs, logged soils (to NZ Geotechnical Guidelines) and shear vane testing
c878c9fc-3ce4-5272-8b0e-5d24c6ebf88a | note | Acceptance / Conformance Criteria - Engineers Approval
1f32848a-b8b7-5bf9-9cc9-5ce588adf0f5 | note | Standard / Specification - PS 16.6.4
bf760bd5-ea12-56c1-88e5-233d940b0a25 | note | Verifying Document - Site Records
e706dd8c-74b9-528e-86c6-8a3604c3734f | note | Testing Quantity Required (based from schedule qtys) - As per Engineer
d77c3907-969d-5f0a-9089-1439ce1373b8 | note | Verification Activity: Activity - W
c5b7aa59-06be-51e8-87d0-0966e3444976 | note | Verification Activity: By - ENG
cde568f3-5661-4e69-b3b2-5697e1054ed7 | checkpoint | 6.1.2 - Cut Slope - Soil Log
27870974-295c-5425-94b3-1e9f3c4578d1 | note | Detail - Soils to be logged to NZ Geotechnical Guidelines
939bf334-b6de-5aba-a943-ac2857810fd5 | note | Acceptance / Conformance Criteria -
b66e0e22-abc0-5f22-811d-560908c79b9c | note | Standard / Specification - PS 16.6.4
199098c1-f77b-501b-9b27-b666aed7a876 | note | Verifying Document - Soil Log
18f8a3cd-3cd6-5fd9-b232-34b1261c334d | note | Testing Quantity Required (based from schedule qtys) -
412d41e7-d6b6-57e0-baad-9d9ed27ae4e4 | note | Verification Activity: Activity - I
c8f9430d-3bc2-523b-951a-f31dbcb0e896 | note | Verification Activity: By - SE
ed167d0e-9ff7-411b-9248-10134dbf89a7 | checkpoint | 6.1.3 - Cut Slope - Shear Vane Test
33c23fc1-7919-507d-9d3a-64e60770f4e4 | note | Detail - NZ Geotechncial Society 2001 - Guideline for Hand Held Shear Vane Test
60b7245d-6b54-5b28-992c-55dc80367291 | note | ○ This test shall be undertaken at the design subgrade level to a depth of 2-3m below the design subgrade level
95b22c56-8cff-5776-a05e-e25af27e646d | note | Acceptance / Conformance Criteria - Average Minimum SU: > 60kPa
4a2e678a-9ccf-56e7-a030-404b0935b5da | note | ○ Single Test Min SU: >50kPa
8f3177b2-94d4-5007-99d0-e56e2b73c7ca | note | Standard / Specification - PS 16.6.4
5926a7d4-5d92-5d2b-b9b3-c57b34a666ff | note | Verifying Document - Shear Vane Report
9d8d8541-aabc-521e-8eaa-c5e2f1dd6e72 | note | Testing Quantity Required (based from schedule qtys) -
485a8a00-fb49-5fa2-a596-34315ed34954 | note | Verification Activity: Activity - I
b782b88e-0f32-5920-a9ce-fba1ddcf3ad7 | note | Verification Activity: By - SE
6a091508-c937-4d61-987b-c573fa12ab2a | checkpoint | 6.1.4 - Drainage Measures if Seepage Encountered
8e495619-13ca-5471-8aea-e65ac29b08af | note | Detail - Borehole Drains or ballasting may be required, to be directed by Engineer
bdc330da-377a-5006-ade2-cad242dc30f9 | note | Acceptance / Conformance Criteria - Engineers Approval
7af9ad0a-e2cc-5781-bf17-ccecd0231a94 | note | Standard / Specification - PS 16.6.4
1cc6b52f-8473-56c2-9fb1-fbeca9963383 | note | Verifying Document - Engineer approval
f7f18a75-5005-5d13-837c-2d6ff84f15ab | note | Testing Quantity Required (based from schedule qtys) - As per Engineer
e1b9f004-2d9f-5b58-a4ca-ce0a1c933e05 | note | Verification Activity: Activity - I
ae95c875-6383-556e-9761-5937be172749 | note | Verification Activity: By - ENG
86433569-6812-4fdb-ad45-2c7c43b6f31d | checkpoint | 6.1.5 - Design and Grade Check
8a966e6d-9dc1-5a7d-8c1c-9ba75da3373c | note | Detail - Confirm cut slopes have been correctly excavated to design and grade
44227bbf-1a2b-5c38-a3b5-4eaf0d88768a | note | Acceptance / Conformance Criteria -
1f58862d-9c02-57e2-a51b-aded16165714 | note | Standard / Specification - PS 16.7.1
f5e54251-aa95-5f00-aa2d-6094deb42a3b | note | Verifying Document - Survey Records
2003e1ee-aacc-53db-b029-3fc43a786722 | note | Testing Quantity Required (based from schedule qtys) -
a44e031c-385a-5c34-a5f2-5120eb53211d | note | Verification Activity: Activity - D
80d39d8f-4d94-58ab-b4ca-034de57fdba8 | note | Verification Activity: By - SV
4f51f1df-4238-4069-a0c0-73ce67212fea | checkpoint | 6.1.6 - Stabilisation of Cut Slope Surface
3066f967-fd59-5182-a02f-dfdee1c59a33 | note | Detail - Cut slope surfaces to be topsoiled and grass seeded or planted as soon as possible
3ec0573f-ec3c-5e34-b9c0-d25ed2421dc7 | note | Acceptance / Conformance Criteria -
be41bfc5-3cc9-5d2f-bb32-af47a5695fba | note | Standard / Specification - PS 16.6.4
826e8dab-e9c0-5729-ade5-1df922b33f6b | note | Verifying Document - Site Records
7256d485-d934-51c8-80f5-42992b56d72e | note | Testing Quantity Required (based from schedule qtys) -
05ec052b-80d3-51ac-8f29-a26119629df2 | note | Verification Activity: Activity - C
1ad7b84e-6f78-578c-b4b3-1cc724c3cfb4 | note | Verification Activity: By - SE
fb81c9be-f31b-432c-8b2b-81bf42c9ea3b | checkpoint | 6.2.1 - Release of Hold Point
bda6d2a7-7005-53e3-ab65-25237f8d05a7 | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
a5ab3bf3-f328-5c77-863f-0e789d098000 | note | Acceptance / Conformance Criteria - Engineers Approval
914afdce-e4c9-5221-91a9-be0a3ca2684d | note | Standard / Specification - PS 16.9.3
59ce497a-dafa-598d-abfe-5e42b0a2ddd9 | note | Verifying Document - CONQA Approval
da195f72-c14d-58c0-9445-5e2c9864e65b | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
559fd59f-c709-5190-ad72-55a7ecb5b61b | note | Verification Activity: Activity - HP
56ed7567-e0b1-566f-aa82-f37a4a15a5eb | note | Verification Activity: By - ENG
3fcaf40a-91bf-4d8f-a9a7-b2f41cb0c4ee | signoff | AUTHORITY HOLDPOINT
8ea0e304-a00d-43c6-8739-d448383c1db0 | section | SECTION 7 – UNDERCUT TO WASTE & BACKFILL
0781a768-0a32-4344-8e4e-20c171df31e1 | checkpoint | 7.1.1 - Undercut Surface Inspection
a29bab05-38fb-5558-af6a-320ec1d90314 | note | Detail - Engineer to inspect undercut surface
31ec49b8-ff03-5920-9239-0e445d371c3d | note | Acceptance / Conformance Criteria - Engineers Approval
5bbcaeba-fa6f-51ca-9abc-027243b05d91 | note | Standard / Specification - Appendix V
01f13bac-9a3d-5b4e-baec-255c566e54f4 | note | Verifying Document - Engineers Approval
f4c2bcd0-0b9f-5974-9ad7-185755be0c28 | note | Testing Quantity Required (based from schedule qtys) - Across stripped area
5ba65619-c883-5591-96d0-48e121cefa4f | note | Verification Activity: Activity - W
b329a92e-8214-5377-8fd9-c08226f5829a | note | Verification Activity: By - ENG
23e7b460-cfb3-4485-ad1a-0a68d0d5b989 | checkpoint | 7.1.2 - Placement of Geotextile on Undercut
fd838f5b-ced6-52c6-b28e-645755a28c92 | note | Detail - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
d23ba909-7c66-5a8e-ad1e-9be452db6058 | note | Acceptance / Conformance Criteria - Engineers Approval
8800b7a7-68d2-5e71-bd48-d23fde36dcdf | note | Standard / Specification - PS 16.6.4, TNZ F/7: 2003 8.3
8c75fcad-8bc6-5cb7-a3b4-c321045191cb | note | Verifying Document -
3c9c5b77-635e-59fe-9289-2c82645ec2cb | note | Testing Quantity Required (based from schedule qtys) -
38cb6bb1-2f25-56de-82f4-df646133cdd4 | note | Verification Activity: Activity - W
2656f423-4985-5fc1-9a38-93b111921f1e | note | Verification Activity: By - ENG
16dd6fb6-dfda-408a-9922-3e1b9fbdfcac | checkpoint | 7.1.3 - Subsoil Drain inspection
806c2bc9-4497-5c04-9ef8-d1c46328db37 | note | Detail - Subsoils to be placed at base of cuts where directed by the Engineer
101697f6-9e6f-515d-b23b-6d1bc0c4105b | note | Acceptance / Conformance Criteria - Engineers Approval
d47f5355-1c23-52f1-b54f-5abae6f1f70d | note | Standard / Specification - PS 16.6.4
28a21e02-b605-5d32-bc48-1e8f3ec93013 | note | Verifying Document -
6cf509b3-9276-5bd1-acc4-611b323e79b8 | note | Testing Quantity Required (based from schedule qtys) - No less than 24 hours prior to placement of backfill
0986ac29-45f8-58b6-9098-35917f9e9ba6 | note | Verification Activity: Activity - W
5d6095bb-f45a-5d54-bad7-7f72c1b46cee | note | Verification Activity: By - ENG
ab30b7bd-91f4-4d6a-80fa-f096d21b2fed | checkpoint | 7.2.1 - Release of Hold Point
37a22d96-95db-5957-8792-2bb00c74ef9c | note | Detail - To release the subgrade hold point and be able to start placing fill, the Contractor shall provide written certification that all insepcted and tested subgrade comlies with the requirements in PS 16.6
01a90689-ca23-5e5f-9844-496754f6af8f | note | Acceptance / Conformance Criteria - Engineers Approval
d9fe0936-444d-56ca-82ed-6c81a0c2fddc | note | Standard / Specification - PS 16.9.3
3ab7afd8-28ce-5784-bec9-96f70c27a185 | note | Verifying Document - CONQA Approval
917560fa-3f1d-5b37-8d02-dba9751bad27 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
e08b9c95-b2d9-5e8c-b580-7190856fbb2a | note | Verification Activity: Activity - HP
63fa45f9-6267-5731-83c4-e346e2689f6f | note | Verification Activity: By - ENG
194c22bd-619b-45e4-a92a-52e5707fc0d3 | signoff | AUTHORITY HOLDPOINT
ce8741bd-d7a3-4497-b02f-5e353e91fdec | section | SECTION 8 – COMPACTION OF IMPORTED FILL
28314c46-79c9-459a-8246-5826afaf703b | checkpoint | 8.1.1 - Placement of Geotextile
f572abba-0bf1-5184-8f3c-ec292bc02c5a | note | Detail - A layer of Class B Geotextile Fabric to be placed between cut surface and imported A1 Structural Fill with 500mm overlaps
dd350f9e-1e85-5afe-8b76-35f68c0aa1fd | note | Acceptance / Conformance Criteria - Visual Inspection
532419ca-3317-5872-b054-de36a2c504bf | note | Standard / Specification - NTC084
76aa943f-4bfc-574b-b681-9f9037f9a2d0 | note | Verifying Document - Visual Observation
70992602-9c24-5c69-83d1-bb86c2a7acc7 | note | Testing Quantity Required (based from schedule qtys) - As Required
53bf64e8-36df-5932-8a42-585016361800 | note | Verification Activity: Activity - I
7e60f3df-0351-5b13-872a-0888d788253c | note | Verification Activity: By - SE
0563f76a-bf92-4fdd-a6c3-32429085a8cc | checkpoint | 8.2.1 - Compaction - Clegg Hammer
964a5260-a265-5db2-b07b-5935f95e33c1 | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
3b781eaf-7c37-5d2f-a76d-6853b5a22201 | note | Acceptance / Conformance Criteria - Structural Fill: Min CIV 18, Ave CIV 20
089305e5-5cce-57f1-b13f-add1522a51d5 | note | ○ Non-Structural Fill: Min CIV 10, Max CIV 12
d7025ec6-0ca3-54b2-805e-19701f9db974 | note | Standard / Specification - Appendix XVIII
e406e0ea-13e6-5acb-96b7-ad46018bf8ef | note | Verifying Document - Clegg Hammer Report
a9846bae-f7cc-50ac-84f0-2d125ab61b20 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
fba95479-95a0-5506-af9b-fd4e5b43eed3 | note | Verification Activity: Activity - I
9c506d3d-94c0-5769-8b8b-0e85bcf87640 | note | Verification Activity: By - SE
d85da4d3-cc2e-4bf2-bcb5-a8a388b0df3f | checkpoint | 8.2.2 - Compaction - NDM
0ecfc4fa-96bb-5cc7-80fa-3ac7ca394bb9 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
7bfe2a6f-c917-59ca-9244-7a547cd11d39 | note | Acceptance / Conformance Criteria - Ave >95% of MDD, Min >92% of MDD
e4d59f85-ba3a-5845-af20-553e9aa70653 | note | ○ Non Granular Material: Max Air Voids 8%
0dea1e1d-773b-584a-818b-634b7d024e69 | note | Standard / Specification - Appendix XVIII
eace9fa6-2137-51cd-8e22-aff30120f6aa | note | Verifying Document - IANZ Accredited Report
c1081b72-650c-54ae-abd7-e14a3addcff0 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
759cfe41-9c2f-5d6e-87e1-22e49b6c9e2b | note | Verification Activity: Activity - I
c7f20b94-4b29-5d58-8874-df31453b7b98 | note | Verification Activity: By - SE
71a294cb-c8ed-4981-8a3a-600d0c351ec0 | checkpoint | 8.2.3 - Compaction Trials
e2ff21cd-6177-596d-8472-9da03051c4c1 | note | Detail - The Contractor shall carry out compaction trials of the various soil types and combinations on site, and any imported fill materials, using different layer thicknesses, types of rollers and conditioning plant (ie construction discs and scarifiers). The trials shall be conducted over the duration of the earthworks operation with the objective of determining the most suitable and efficient techniques to meet the compaction requirements. The trial details, test data and conclusions shall be reported and copied to the Engineer within five days of completion of each trial.
2dbd85d6-5e84-55a3-8bb8-9861623f39e5 | note | Acceptance / Conformance Criteria - Engineers Approval
549db573-c8bb-5d4c-83d5-83a09597dddb | note | Standard / Specification - PS 16.6.5
bb764a26-c943-5f74-a858-36c596278bf3 | note | Verifying Document - Trial Results
3fcb3cdf-7687-57d4-8b14-bc6646de5626 | note | Testing Quantity Required (based from schedule qtys) -
9cd21e41-3310-5562-b124-22d0cddc035b | note | Verification Activity: Activity - R
445d8a25-6b11-5b5a-a2b3-2b9905e44f32 | note | Verification Activity: By - ENG
da386258-58d2-4b0c-8c0b-9b672d953b10 | checkpoint | 8.3.1 - Compaction - Structural Fill Scala Penetrometer
f1624108-4588-5aec-ad30-a69b3bbf61b1 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
5b0905fd-fd35-598d-8f68-37e402e98936 | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
efaa4208-2fed-5e97-b627-89f6588ff9c4 | note | Acceptance / Conformance Criteria - Minimum 5 blows per 100mm penetration
c694dd7b-e74c-50da-b871-b2e7f1f99311 | note | Standard / Specification - PS 16.5.12
abb91d08-aaaa-5819-a29c-8f7d61c8ab86 | note | Verifying Document - Scala Report
4776851e-1e4c-584d-a0ed-cee58cdeb60c | note | Testing Quantity Required (based from schedule qtys) - Minimum 1 test per 500m3 of filling evenly distributed over the extent and depth of the filling. A minimum of 1 test per 500mm lift or part thereof to be completed through the full lift thickness.
a5bdcbee-0715-5dd2-bd76-007b8663fbe1 | note | Verification Activity: Activity - I
9b7e8b3e-ce0a-50f7-ad87-71cddf2309ab | note | Verification Activity: By - SE
fcdff1e5-23bd-4954-9140-ed5e2efcd1d5 | checkpoint | 8.3.2 - Compaction - Structural Fill NDM
ddf0fbc4-6a80-5be6-907a-d823a94353b2 | note | Detail - NZS4407:2015, Test 4.3 Nuclear Moisture Density Gauge (Backscatter Mode)
70348de7-3521-52db-a5e7-1cae1275b84c | note | Acceptance / Conformance Criteria - Ave >95% of MDD
a8828faf-8762-5d94-8516-88640ab1f1a7 | note | ○ Min >92% of MDD
369edca3-8e60-5ad8-871a-f061e53adbaa | note | Standard / Specification - PS 16.5.12
94190a09-43b0-5e25-91ee-a00d385b5c3f | note | Verifying Document - IANZ Accredited Report
c4bfc1cf-4b82-5e78-adbf-3168c0c4aa6f | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests) per 400mm lift (every 2nd lift) of fill per 1000m2 of placed
0d381acc-e496-5978-84e9-fb46f4932e28 | note | Verification Activity: Activity - I
7cba9401-43ff-5df8-bd1e-3823f63a620e | note | Verification Activity: By - SE
f8a243ea-a509-416b-96ae-0969f339194c | checkpoint | 8.3.3 - Pumice Sand Fill
61a882eb-aab5-5648-b726-162fbe9a3c65 | note | Detail - Pumice Sand Material shall be contained with an outer layer of fill with a minimum thickness of 600mm. Must be Hardfill and/or imported Type A1 material and/or Type A2 material and/or Type A3 material
b0bc56b6-67b3-557f-b878-b249cf94f47e | note | Acceptance / Conformance Criteria -
f8fba99b-3f3d-5e0c-84c3-eb06fadce78d | note | Standard / Specification - PS 16.5.12
05af8a9f-73ae-5967-9b16-3ba158babe42 | note | Verifying Document - Site Records
ce0119a9-b26c-5a43-841a-2d5c2c3df3bd | note | Testing Quantity Required (based from schedule qtys) -
f3599b30-cf72-5e38-9bc8-b9846f61529f | note | Verification Activity: Activity - H
ca72cada-0754-5ea7-920b-252fc980ebc1 | note | Verification Activity: By - SE
5967f1b6-16f5-4bfa-8818-f55adf617aaf | checkpoint | 8.4.1 - Cut to fill
1e7d98f0-cc16-57f7-9cd5-8beae0bcf00e | note | Detail - Cut from classic building and use as a fill material
febc238d-8b89-5f1b-bfc2-1d3cd0f6494c | note | Acceptance / Conformance Criteria - Engineers Approval
f94dff61-0699-5791-b5b9-572d607f988b | note | Standard / Specification - PS 16.5.5 (b)
59575344-cc13-5019-854a-20b0f3475bfe | note | Verifying Document - Visual Observation
32fbfd2b-3b6c-5158-bb2e-02726787190e | note | Testing Quantity Required (based from schedule qtys) - If there is change in colour or after every 1000m2 of placed
371bcc6c-47c7-5fc8-a3c3-729d493d9c2a | note | Verification Activity: Activity - HP
2fe6dd9a-2f22-5d4d-8994-3b2916a95d0f | note | Verification Activity: By - ENG
6aa1a7a9-90be-4fc0-b37a-3e4110ace36b | signoff | AUTHORITY HOLDPOINT
a494e477-6f88-484e-a333-319228ca6545 | checkpoint | 8.4.2 - Compaction - Structural Fill Scala Penetrometer
e88b20ca-ec46-538b-b2a4-f01e414bb2fb | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
98d74863-26bb-514d-afb5-15b6c16e506e | note | ○ Scala penetrometer testing to be undertaken
3b68cdbb-3b67-5f98-b618-9dfb6664da05 | note | Acceptance / Conformance Criteria - Minimum 4 blows per 100mm penetration
9b2269b5-84d9-50ad-a3fe-55b6fc2cdfcc | note | Standard / Specification - PS: XVIII
73b312da-bd43-5275-9541-79c313a2a954 | note | Verifying Document - Scala Report
b0ecff54-ebb8-5a2d-91ba-ad1a38e33f86 | note | Testing Quantity Required (based from schedule qtys) - Minimum 1 set(5test) per 100m3 of filling evenly distributed over the extent and depth of the filling. A minimum of 400mm lift required.
acae5698-471a-55e7-b659-f30299858969 | note | Verification Activity: Activity - I
ac60b448-47d2-5db0-843a-eef7d4f69cf9 | note | Verification Activity: By - SE
e509cf73-7398-4005-b9bc-be775e63b128 | section | SECTION 9 – TOPSOIL PLACEMENT
c2cab1aa-65e6-4d2f-bc65-320687eca21f | checkpoint | 9.1.1 - Topsoil Placement on cut and fill embankments
d09b8fb8-2aa6-5ed4-9d38-5d2826813abf | note | Detail - Confirmation of thickness and material suitability
1022d2c7-74c0-5aca-a140-27cd1dfc2072 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
51f6394d-e159-5603-a284-e6f13e2e9a9a | note | Standard / Specification - PS 16.6.3 b)
11aa633a-1880-5351-9bf9-78df7b6e151f | note | Verifying Document - Visual Observation
e129084a-77a5-59af-a735-67e8f15e6404 | note | Testing Quantity Required (based from schedule qtys) - Once per lot after topsoil re-spread
622ccf0c-850a-52a4-9c54-07c8253dafab | note | Verification Activity: Activity - H
88cb1a66-2b9c-579c-a89a-98f16d4a6097 | note | Verification Activity: By - SE
e8229b09-d6fd-4e54-92d9-c62459ab74f3 | section | SECTION 10 – SETTLEMENT INSTALLATION & MONITORING
58be23bf-4688-4e30-b0b2-b6b63a7357ba | checkpoint | 10.1.1 - Instrument Reading Notice
9013008a-1bbc-5afe-93f2-5815006cfddd | note | Detail - The Contractor shall inform the Engineer two days in advance of planned instrument readings so that the Engineer may observe the work.
4cf9f484-599a-5a1a-92d1-f842aa9700a2 | note | Acceptance / Conformance Criteria - 2 days notice to Eng
14972fff-789f-5eb5-b768-2716392c64c4 | note | Standard / Specification - PS 16.8.2
927cfcce-64ed-5e0d-a6a1-767df4a2d19a | note | Verifying Document - Site Records
e3bf3ff9-7446-52e1-9691-e7db9dcc158b | note | Testing Quantity Required (based from schedule qtys) - Every Time
f4b5baa9-c32e-5c53-bfbc-80ac2316d794 | note | Verification Activity: Activity - H
9896fdbb-83c1-5d98-b01b-d15b55ce2d2e | note | Verification Activity: By - SE
26a94fa6-6bbf-416f-90cf-5e9e95d5e04c | checkpoint | 10.1.2 - Results Submitted to Engineer
d8525a80-1b19-517b-baf8-3d266e0a3134 | note | Detail - Results will be submitted to the Engineer within 1 day of reading the instruments
2bf5e40a-5d2c-5192-9709-12ece7fb2881 | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
0fb8386d-01a2-5f56-941e-4e5fa6c80c68 | note | Standard / Specification - PS 16.8.2
155a4973-cd4d-50c2-b8b5-7868a8c43d61 | note | Verifying Document - Site Records
05813563-805b-568b-9eb3-57a9539b17fd | note | Testing Quantity Required (based from schedule qtys) - Every Time
f01c0039-3b93-5c60-b9f7-e45061a296cc | note | Verification Activity: Activity - H
417f66b3-6342-53ec-b170-fed1a106cdfc | note | Verification Activity: By - SE
90b8ebf5-99a2-4fbd-9102-f172d3a0400b | checkpoint | 10.1.3 - Baseline Readings
0c152c63-7513-5a8b-9783-b06dfa808be7 | note | Detail - The Contractor shall take 3 sets of baselines readings from all instruments at 2 day intervals
bb96dc01-ab8e-57c7-91e2-1d1ec46ea28a | note | Acceptance / Conformance Criteria - Engineers Approval
da720b12-9a72-5ce7-8d72-8ff6c6aa3de0 | note | Standard / Specification - PS 16.8.2
71e0cdc8-3eb9-5a32-b833-55f8298a29d0 | note | Verifying Document - Site Records
2755e0f4-0dca-504e-a4d5-f19ee3b05343 | note | Testing Quantity Required (based from schedule qtys) - Every 2 days
6eeae8a2-6193-52aa-a3a6-c23e064de208 | note | Verification Activity: Activity - H
18c7965d-4bd9-5aec-a48c-f2adc455a2ff | note | Verification Activity: By - SE
0cbbce5b-3444-47d8-a57e-e12e058129cc | checkpoint | 10.1.4 - Readings During Active Fill Placement
4197cef7-d738-5556-b253-1545b28c8a62 | note | Detail - During active fill placement, the Contractor shall read all monitoring plates twice a week or every 1 metre of fill whichever is more frequent
db84ea5a-e268-5946-998b-18850c51d04c | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
9eca1f22-45d5-531e-bf9e-61ccfa5b84e4 | note | Standard / Specification - PS 16.8.2
5e7f206d-a75b-57c0-b499-2aef9f3d5e35 | note | Verifying Document - Site Records
4e3a2db6-9a55-5c97-8358-88b1435c7b92 | note | Testing Quantity Required (based from schedule qtys) - Twice a week
75f44174-7e1d-5cba-8660-8066fa3819f1 | note | Verification Activity: Activity - R
a045c7ac-9280-59f4-940d-46b5fe77607b | note | Verification Activity: By - SV
c934e3a6-8d4e-427a-84ae-4023bcecf911 | checkpoint | 10.1.5 - Readings During No Active Earthworks in Area
6fb21a42-c624-5660-9916-402a978f7cd0 | note | Detail - The Contractor shall read all monitoring plates weekly if there is no active earthworks taking place in the area
5c2145e6-39c3-5d7d-bb58-7b442a6c8e3a | note | Acceptance / Conformance Criteria - To Engineer within 1 day of Reading
ec69199c-8728-5949-ac73-99a35badc6f8 | note | Standard / Specification - PS 16.8.2
3d410bcc-215a-5931-aa23-a54a79e11990 | note | Verifying Document - Site Records
2795fa80-cd50-5ea7-9fb6-8b6bb8a60bce | note | Testing Quantity Required (based from schedule qtys) - Weekly
ffd719cc-d7c3-5e6e-b572-29f82aa3fe16 | note | Verification Activity: Activity - R
77dbba5c-7689-5482-b9c0-957ec7e8dce3 | note | Verification Activity: By - SV
e110b10a-f3f4-408f-ae33-65c4c1d3d958 | checkpoint | 10.1.6 - Settlement Monitoring Termination
780a6751-c986-51fa-9550-2ade040b1d3e | note | Detail - The criteria for terminating the embankment preload are either: Three consecutive measurements indicating the t90 settlement value has been achieved, A rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed. The settlement readings shall be evaluated by the Engineer to assess the need to extend the monitoring.
d6d8be6e-969e-581e-ba89-3965fcfe93e5 | note | Acceptance / Conformance Criteria - Either:
f8aed0bf-4a71-5d16-a811-6409ccddc2c8 | note | ○ 3 Consecutive Measurements showing T90 settlement value achieved
1c278dbe-dd7a-5b3b-89ef-28ff3eb72ecf | note | Or
3cb40c75-75cf-5cb1-a7ba-cee3b2811e31 | note | ○ Rate of settlement less than 10% of the maximum rate measured immediately after the fill was completed
55b1f356-5628-5166-8bc3-0ec5b75bc340 | note | Standard / Specification - PS 16.8.5
edcc3231-271c-570d-8511-110efa0f5000 | note | Verifying Document - Site Records
cf103fa0-97ac-55af-9741-8daa9dd3a34b | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
c518c396-d5a1-5d3b-a3f1-867ed7d60d3b | note | Verification Activity: Activity - HP
06f0858c-8c5c-5623-b7c7-7ee08b1dd8c3 | note | Verification Activity: By - ENG
69dd92b3-df53-4990-a6f7-7426016b08eb | signoff | AUTHORITY HOLDPOINT
cf645024-fa01-4361-8fcc-6ffc48edeae4 | section | SECTION 11 – AS-BUILTS
6b6ee8e5-bffc-4685-b200-07529d88117c | checkpoint | 11.1 - As-Builts
cb5ddbd4-8b3f-5603-94d9-82f17700d657 | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
d25443ea-366e-5df3-a9d7-57ca49b1eeab | note | Acceptance / Conformance Criteria - As-build record
aecac2b9-9f9d-5ed6-babc-e8e89e1ad75a | note | Standard / Specification - PS 16.7.6
8b7fb3b1-5706-58e9-92e9-76b26f384385 | note | Verifying Document - Survey Records/redpen markups
1722e594-0f26-544b-841f-646f99f95d1d | note | Testing Quantity Required (based from schedule qtys) - During Earthworks
883f666e-15ca-55c3-9490-1089d15cad50 | note | Verification Activity: Activity - D
047410e9-1559-5ea5-b9eb-bfa9072acf4b | note | Verification Activity: By - SV
92f5b9bc-fb99-4286-8260-5508499e3c20 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
0a533e5f-f9ae-5ae3-9fce-85af0750349d | textbox | Contractor's Rep Name:
5ee7cbe6-5df5-5a26-b69e-cfb72eda4898 | textbox | Engineer's Rep. Name:
38028213-2a86-5e72-b9b1-c50b3c2fbd2e | date | Date:
f555597d-3e8e-4492-ace5-f06d34450f5f | signoff | Add Signature
fcfd5d08-3f3b-4b4b-8470-ccc187cfacbc | checklist | DN1210-SP2-003 ITP Temp works - Removal of Traffic islands and swale backfill Rev 0 | itp | DN1210-SP2-003 ITP Temp works - Removal of Traffic islands and swale backfill
53d1e63d-ba83-46fd-a672-8c7a20436e3e | section | SECTION 1 – PRE-CONSTRUCTION HOLD POINTS
183650fc-395a-4c82-97ee-e0d68a3ce422 | checkpoint | 1.1.1 - Methodology
871daec1-bf5c-506c-b1e8-9e229b5190bb | note | Detail - The Contractor shall submit the construction and QA methodology, for each element of Earthworks, incl construction, Site Access, dewatering, wet weather, testing, inspection and hold points for review and approval prior to works.
b343a29e-8e8e-506b-979e-4429875e2ae1 | note | Acceptance / Conformance Criteria - Engineers Approval
87791dda-ff77-50e0-b4bb-bdbc840226da | note | Standard / Specification - Appendix V
a0dad9c5-c910-53d4-ba98-9f3643ef4b6d | note | Verifying Document - Approved Methodology
5ca5e53b-c4c8-5915-ae9f-2b75d2065a89 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
4694ee63-248a-5a26-b77c-b8137dbdbd2b | note | Verification Activity: Activity - HP
74882bde-0f42-526d-a2e3-040e1f1e0d07 | note | Verification Activity: By - ENG
34b52e0e-9679-4939-8d9c-4179600f59b0 | signoff | AUTHORITY HOLDPOINT
6aea78be-4f3c-4685-b1f7-b0bbae58a3df | checkpoint | 1.1.3 - Erosion & Sedimentation Controls
d42d5416-01fb-5eb4-9668-fb10c6770c1d | note | Detail - Confirm that the weather and environment will be suitable for works with the Environmental advisor.
84e42fe2-c5a4-5ff5-bbda-d8c9b4a29ab5 | note | Acceptance / Conformance Criteria - As-built Completed
be2e3663-9bcf-5259-8e11-f3d6cc4ea52f | note | Standard / Specification - Internal Hold Point
9dd8ca8d-72c3-5d3e-94bf-a974e82d1e90 | note | Verifying Document - ESC As-built
e6a9909c-6653-5f8a-85b4-6dcb949e037c | note | Testing Quantity Required (based from schedule qtys) - Prior to works commence
b07e535d-a8a4-557b-ac3a-6cd4347858fd | note | Verification Activity: Activity - H
59490025-55a8-5a29-a58b-6ee7949071d3 | note | Verification Activity: By - QM
434dfae4-9534-4a15-a03d-001c01f62846 | checkpoint | 1.2.1 - Geotextile
909ed18d-2112-5bf2-a926-d2f3f21ba29a | note | Detail - The Contractor shall submit the full details of the geotextile they propose to use to the Engineer for approval prior to installation.
a1d4b849-6698-5e3a-8f70-35b8b7a3e8d0 | note | Acceptance / Conformance Criteria - Engineers Approval
d638d01b-264e-56a0-b17e-81452b9149eb | note | Standard / Specification - PS 16.5.7, Appendix V
3b6e995c-05a2-52df-86a0-1e6450752aa4 | note | Verifying Document - Data Sheets
15bdd476-2b14-5f53-9416-5f900a79f401 | note | Testing Quantity Required (based from schedule qtys) - Results to Engineer for Approval
e0ef2bba-e4fc-5dde-b918-abf444a50101 | note | Verification Activity: Activity - HP
ea21f3bf-4b6d-5dcc-930f-4bb42f1584c1 | note | Verification Activity: By - ENG
8a23fa3f-033b-48b9-a79e-a4a856fc2acd | signoff | AUTHORITY HOLDPOINT
59922969-035d-4da2-9ef2-e08497f3de7e | checkpoint | 1.3.1 - Source data
06ba33e7-df67-56d6-a236-dcc44de120f9 | note | Detail - NZS4407:2015, Test 3.11 - Weathering Quality Index
530cdcee-59c0-57d1-84bd-580163c7eaaf | note | ○ NZS4402:1988, Test 4.2.1 - Standard Compaction Result
0e8757bd-07c4-5f6f-b2aa-1379e073be84 | note | ○ NZS4407:1991, Test 3.12 - Los Angeles Abrasion Test Result
b6d9e160-5e98-5292-814d-aaf708682beb | note | Acceptance / Conformance Criteria - As per specified criteria
9704fc8b-3485-548f-b1f1-56d4bc07772a | note | Standard / Specification - PS 16.5.5
69b2eb06-2689-5b8a-93be-2b4e1edf5fc6 | note | Verifying Document - IANZ Accredited Report
4cd83dea-24c6-5ff6-81bb-992a5b734edc | note | Testing Quantity Required (based from schedule qtys) - 2 Test per Source
3dc2c8eb-3f81-5dcc-8573-bd773e4b35b2 | note | Verification Activity: Activity - HP
96a5d8eb-d8d5-5f63-a182-a0498418a690 | note | Verification Activity: By - ENG
70bb1424-38b7-48f6-b6a2-26fc3a5b8156 | signoff | AUTHORITY HOLDPOINT
541c128a-50ce-49c0-86ae-fd445fd66bb2 | checkpoint | 1.4.1 - Dense Graded Asphalt
04d330f5-2eb6-5fa9-8fa1-452e4ca8f0de | note | Detail - Conforming sieve size and Mix designation refer to clause 3.3.1 and Table 3.5
6044fdb8-ce10-56bf-97f3-9436a672b392 | note | Acceptance / Conformance Criteria -
50b9af76-1d2d-54b2-bcd3-ab29fd0b190c | note | – – – – – – – – – – – – –
8afffc12-cbb0-5be3-affd-11495a17c3a1 | note | Sieve Size (mm) ¦¦ Mix Designation: DG7 ¦¦ Mix Designation: DG ¦¦ Mix Designation: DG14
2ba3db7a-bc64-5d24-9103-a761b810d949 | note | Percentage Passing Sieve Size (By Mass)
e4e621ca-27a0-5900-8a53-6a4ea2c7e7e9 | note | – – – – – – – – – – – – –
d6e2067c-cb76-59bc-b448-98d27ff95057 | note | 19.0 ¦¦ – ¦¦ – ¦¦ 100
b6b87316-637a-5cc9-992c-ad8245b4e9dc | note | 13.2 ¦¦ – ¦¦ 100 ¦¦ 83 – 100
d08557d4-42a6-5fbd-b476-cd4de0a2a9f5 | note | 9.5 ¦¦ 100 ¦¦ 79 – 100 ¦¦ 68 – 90
fb66f1e4-ebdb-5567-bb43-c5dd33d2293a | note | 6.7 ¦¦ 80 – 100 ¦¦ 63 – 90 ¦¦ 54 – 79
ef4c790d-f63f-5f6a-b7bd-b27fd6d0695b | note | 4.75 ¦¦ 66 – 90 ¦¦ 50 – 79 ¦¦ 43 – 70
3bd9394f-1619-557c-b6ca-c243c9c562ba | note | 2.36 ¦¦ 44- 75 ¦¦ 32 – 61 ¦¦ 28 – 55
e4bb4ce4-4990-50a4-840a-4da3b06ceabf | note | 1.18 ¦¦ 29 – 60 ¦¦ 22 – 48 ¦¦ 19 – 43
d4f2c482-11b0-5b4d-a262-a5150303a52d | note | 0.600 ¦¦ 19 – 47 ¦¦ 15 – 36 ¦¦ 13 – 32
6afdd9cf-afdf-532e-9a13-e03a001327f7 | note | 0.300 ¦¦ 12 – 33 ¦¦ 10 – 26 ¦¦ 9 – 23
66cbc57b-b145-54b7-80ba-05bd90d12329 | note | 0.150 ¦¦ 8- 22 ¦¦ 6 – 17 ¦¦ 6 – 16
9ead9df4-e8e9-5a11-9b32-5444783b3bc8 | note | 0.075 ¦¦ 5 – 12 ¦¦ 4 – 11 ¦¦ 4 – 10
0e18938e-49cf-5ea8-b725-0fe681779027 | note | – – – – – – – – – – – – –
2d940bbb-0f63-59a7-b205-f219826d89fd | note | Minimum Layer Thickness (mm) ¦¦ 25 ¦¦ 35 ¦¦ 50
92121793-6597-56af-9591-45b5ec02b163 | note | Binder Content ¦¦ 5.0 – 7.0 ¦¦ 4.5 – 6.5 ¦¦ 4.3 – 6.3
35ca611c-ae38-522a-8e25-24cd09a164bc | note | – – – – – – – – – – – – –
a6d9598d-21cd-5981-86f8-15ff49ed02b7 | note | Standard / Specification - NZTA M10: 2020 / PS 20.12
c5a562db-4153-581b-b1dc-118727172676 | note | Verifying Document - IANZ Accredited Report
8d79dfe9-871d-5736-bdde-02a194455e10 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction and during construction
e949c1e1-fba7-5129-b267-05b94672af5b | note | Verification Activity: Activity - H
49a0a5de-3b89-5f47-9af5-40d2dd03cc90 | note | Verification Activity: By - SUP
ea6220da-4c98-4bf0-a2a6-66f72f4a434d | checkpoint | 1.5.1 - Subsoil Pipes
274529b2-fff2-5b79-afca-87bf1f241eba | note | Detail - Drainage pipes used in subsoil drainage shall be smooth bore perforated Landflow 100mm diameter complying with NZTA F5 unless otherwise stated on the drawings. Pipes shall not have a geofabric filter sock unless requested by the Engineer.
70f779f2-1281-5509-aa93-746212566faa | note | Acceptance / Conformance Criteria - NZTA F5
e4ce6dc7-93b8-5a66-8850-28a98ff8581a | note | Verifying Document - Verifying document to be copy of delivery dockets, photos of pipes onsite with tag showing class
38a3131f-81d9-547a-bb7f-53e1a7544a54 | note | Testing Quantity Required (based from schedule qtys) - During Installation
723bc1e9-d4c0-561d-8260-bb39260dc6d7 | note | Verification Activity: Activity - I
2b0211d6-6d18-575f-be8a-7e75f048d9c1 | note | Verification Activity: By - SE
2178114d-9de7-4294-9fc9-e58f479ba78e | checkpoint | 1.5.2 - Catchpit
de14068c-2a46-5e41-939e-2ca8bfb3f022 | note | Detail - Catchpits are proposed to be precast concrete chambers with grate and frames shall be cycle-friendly Hynds Hydro Stormwater Grate and Frame or approved equivalent for all local roads and the state highway
1e985340-c406-562a-a217-a6827b2527ba | note | Standard / Specification - PS 21.5.4, PS 21.6.12
ed79978f-1b0a-5a2a-94ee-d02f1f4721cc | note | Verifying Document - Site Photo / Checksheet
a8b74203-ae81-53ab-a4fa-f5d1cd0b51fb | note | Testing Quantity Required (based from schedule qtys) - During Installation
090aa7c6-b9e8-5601-b21e-9e9d82c7c927 | note | Verification Activity: Activity - I
9a3f1b34-fda6-58ab-a227-02ec023ea8dc | note | Verification Activity: By - SE
e7f10a24-7f58-4c17-9c55-358659d949f1 | section | SECTION 2 – TEMPORARY CONSTRUCTION - EARTHWORKS
4ceb2292-4e9c-476c-81d6-5cc8de855785 | checkpoint | 2.1.1 - Cut Subgrade Testing - Cohesive Soil Scala Penetrometer
de086e42-0d54-5b7a-8da2-d393e47f5cf9 | note | Detail - NZS4402:1988, Test 6.5.2 - Dynamic Cone Penetrometer
b0a13e6d-ac70-5612-a267-92a442116454 | note | ○ Scala penetrometer testing to be undertaken instead of shear vane tests where shear vane is unable to penetrate subgrade material
4d8e20d7-5c7d-5fc2-a9ee-5a1e26de2315 | note | Acceptance / Conformance Criteria - Minimum 3 blows per 100mm penetration
729aa5e4-60d6-53bf-99e2-4cdd873a7bfd | note | Standard / Specification - Appendix XVIII
ce08cad8-13c2-5549-be60-ce5598350eac | note | Verifying Document - Scala Report
3f087b76-8a50-599f-8b9c-7612255a7cb9 | note | Testing Quantity Required (based from schedule qtys) - 4 test per 400M2
3a4220cb-9d39-5b71-8be6-8a0be3bbbd5a | note | Verification Activity: Activity - I
f34ab335-ab1d-5764-ae67-0780172b9e23 | note | Verification Activity: By - SE
065e6f73-ac5b-45c4-b0b1-2fcd47b9c343 | checkpoint | 2.1.2 - Proof Roll
94fd5a28-9d58-52c0-9b91-e93b474ece94 | note | Detail - Visual Inspection of Proof Roll an d undercut surface
e037022e-2515-5a26-886d-137ae2396c00 | note | Acceptance / Conformance Criteria - Visual Inspection
93ea7a20-8df7-532c-ae33-e49db0b86f41 | note | Standard / Specification - Appendix XVIII
0aa4b4ba-4ea5-5984-92f4-3b4d958aa56b | note | Verifying Document - Visual Site Record
4fcae931-91e8-58c0-8054-803e9bf384e2 | note | Testing Quantity Required (based from schedule qtys) - Across Finished Area
10035b01-d93c-56e1-866b-2af53df54c86 | note | Verification Activity: Activity - I
fe735711-1de5-54a5-a10e-2881c1cf95ed | note | Verification Activity: By - SE
b404eef9-ea3d-4386-8c39-8dbec1300748 | section | SECTION 3 – COMPACTION OF IMPORTED FILL
054753db-cca2-4bbd-ac76-d6ad0d696f7b | checkpoint | 3.1.1 - Placement of Geotextile
2bc709f3-e2de-5063-9748-f970e0608557 | note | Detail - A layer of Class B Geotextile Fabric is to be placed between the cut surface and imported GAP65 Fill with minimum overlap 400mm between adjacent geotextile strips.
00b4ed1c-65de-5a06-b6ab-8a9072a01a57 | note | Acceptance / Conformance Criteria - Geotextile to be placed across the undercut base and up the sides, with joints overlapped by 500mm minimum
3bf1f8c1-e5d3-5668-9a60-524709998556 | note | Standard / Specification - Engineers Approval
0607936b-5794-5c25-a57b-9b3044c54ab9 | note | Verifying Document - PS 16.6.4, TNZ F/7: 2003 8.3
760871b2-de5d-576f-a99b-7f801276e992 | note | Testing Quantity Required (based from schedule qtys) - As Required
ad1ac9a4-d6de-5f16-9043-3b36669d8d82 | note | Verification Activity: Activity - I
d0ffa18c-dfa5-56bd-b722-d06d585442a0 | note | Verification Activity: By - SE
2ca6c86f-5d41-4a86-8c9a-40a268cccd51 | checkpoint | 3.1.2 - Subsoil Drain inspection
ebc8eb7d-2085-582e-b64c-23d034db425b | note | Detail - Subsoils to be placed at base of cleaned-out swale to falls required to drain to existing road crossing drainage
134a64d0-8cd5-5c64-94c3-4d1f4d335424 | note | Acceptance / Conformance Criteria - Visual inspection
11c437e3-1960-5a2d-81f7-ba05bbf1a222 | note | Verification Activity: Activity - I
787ded38-8143-5b32-90b9-679becd4b77c | note | Verification Activity: By - SE
e535c3db-e835-4f06-abfe-9605a50c1984 | checkpoint | 3.3.1 - Backfill Installation
0dab4155-9287-5e68-86ff-4f9fcf420d68 | note | Detail - All backfill is to be installed in 250mm lifts and compacted to the following standards.
94cbf07b-7e89-51af-8ff1-70cac812c5e2 | note | Acceptance / Conformance Criteria - Visual Inspection
18d0b3d6-9ccc-53cf-92fa-878e99c7d01e | note | Standard / Specification - Appendix XVIII
ad99ce20-52d5-5d48-b062-6f3c5e4ce303 | note | Verifying Document - Photo
fd639c1c-51dc-54d3-af8e-2ac09a49f782 | note | Testing Quantity Required (based from schedule qtys) - Each Layer
876f27ef-d962-5c30-8b2c-493fef588687 | note | Verification Activity: Activity - I
752e2378-a643-5636-8857-836647115373 | note | Verification Activity: By - SE
8f2c1d1d-230e-48f3-9dda-afa9ef584bb4 | checkpoint | 3.3.2 - Compaction - Clegg Hammer
0d575b74-7a86-500f-a99f-ee1fb300d03b | note | Detail - ASTM D5874-16:2016 Clegg Hammer Testing
f72c9dff-1d42-5e18-8d32-f6473b9f92e8 | note | Acceptance / Conformance Criteria - Structural Fill
884f1458-45a0-501b-a08c-c0d003b57912 | note | – Min CIV 18
d4d9a7ab-e2b2-53dd-a65a-b522cab76baf | note | – Ave CIV 20
1ee97c69-3a61-5262-af92-ebfc03c198ec | note | ○ Non-Structural Fill
cb1aca23-5a38-5c4d-af95-d41b8ab16215 | note | – Min CIV 10
685b1d7c-55fc-5447-9806-0a30de0d78bc | note | – Max CIV 12
b8ecc57e-0750-525d-a74d-5c80ee14b730 | note | Standard / Specification - Appendix XVIII
bf92fd5a-2b8c-5b40-8cca-37b9126d573b | note | Verifying Document - Clegg Hammer Report
43ce03af-0531-5bb0-a217-996a67d50099 | note | Testing Quantity Required (based from schedule qtys) - 1 set (5 tests per 5x5m grid) per 1000m2 of placed per area worked each day, per lift
7c21f5ed-66b7-5579-99a0-8d8361f5d62b | note | Verification Activity: Activity - I
674ca043-7c15-5d0b-a073-a5e3628bdd7f | note | Verification Activity: By - SE
e19829af-d77f-41fa-8f0d-a7cab600b594 | section | SECTION 4 – SURFACING
83f1f40c-2c87-42ff-9f3b-3dbb1878c39e | checkpoint | 4.1.1 - DG10 Asphalt
996b6b68-5904-5e5e-af77-ffd9bfe7ff52 | note | Detail - Layer thickness to be min. 40mm or approved by Engineer
4e7f6814-f05f-5362-b3b2-37d5f27c217c | note | Acceptance / Conformance Criteria - Visual Inspection
b918bb4e-ca80-554c-b704-a137e9e4adc5 | note | Standard / Specification - NZTA M10: 2020 / PS 20.12
80a44eed-3023-54cd-b83f-21f2825a8eae | note | Verifying Document - Prior to Paving
f746a21b-fad5-5e98-a6b3-69c4c6ff19d7 | note | Testing Quantity Required (based from schedule qtys) - During construction
dddfb60b-8707-56c8-9fad-a6aa725c8eea | note | Verification Activity: Activity - I
e233fc4d-76e5-5b69-ba51-4e7b2c6937f7 | note | Verification Activity: By - SE
eacf6503-0788-475a-a241-99a991259e8c | section | SECTION 5 – AS-BUILTS
535991ae-488e-4945-80d7-2c5e51fa8f21 | checkpoint | 5.1.1 - As-Builts
80072cf2-4d98-528e-b971-defb3b1a2eb6 | note | Detail - As-Built records and drawings shall accurately record the layout and extent of all the work and locations of subsurface drainage systems and their outlets.
e00ea4d4-cf7a-5dc3-9888-e305600d3710 | note | Standard / Specification - PS 16.7.6
738a6ffa-73be-5a98-ad1a-190736096ccd | note | Verifying Document - Survey Records
83154674-a7a1-564c-bf82-18d03e3b9439 | note | Testing Quantity Required (based from schedule qtys) - Post Construction
874cc4b8-9414-5123-a60d-748a610fe08a | note | Verification Activity: Activity - D
b3937cc1-4fce-55dc-b9f8-77ae2281a726 | note | Verification Activity: By - SV
36dc5489-9969-404c-bf55-0431d994ef94 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
ad404e68-0b2a-5337-b0f6-a2dae4118ac0 | textbox | Contractor's Rep Name:
65fe3d6b-1341-5134-8da0-99624d67bdc3 | textbox | Engineer's Rep. Name:
e0658281-fc66-5a34-bd92-5a4dff3f6047 | date | Date:
6e18cc9f-808b-4961-87bb-11354f7fe25d | signoff | Add Signature
93d3506a-a15e-4039-8a9e-c44cf8b60cb8 | checklist | SYS - 73 |  | 73
b2dceae1-6f3c-431f-831e-6b41e00eeeff | checkpoint-no-value | Received Instruction
e4f2777a-7f04-50de-9745-2958c8a5f7c0 | textbox | Reference/SI Number
65b6d5f6-7f80-577f-bcf6-70ffa15492b8 | date | Date Instructed
9f6df03a-9879-5224-900b-760dab7f436a | textbox | Client
23c0b2aa-79e1-54c5-95fa-1603cc37dd53 | textbox | Scope of work
2bf62a9a-13fa-5a6f-9829-91da02b98aea | textbox | Agreed value
899bcdee-7434-47b3-89d9-9543876b8cb1 | signoff | Approval
05a186f2-1bb1-49b6-b698-a0075cec0e13 | checkpoint | Job Complete
ed6455d7-5e8a-52bf-8b9e-11a3372735e5 | date | Date Complete
22759515-1c8e-5c8a-bdf8-fc349711cb11 | textbox | Details of work
40537615-018e-59a6-9c8d-62638c7abeba | labour-materials | Labour and Materials
a1f6db10-ec9b-4e21-99e3-ce665914bbd2 | signoff | Attach Signature
54448d7b-622a-4c5a-9284-0dd6f6064094 | checkpoint-no-value | Values
8bc11931-2076-562b-8733-9481cc5af9c0 | number | Labour value
91d0d905-5143-55a8-b499-3bb811a6bc68 | number | Materials value
0162cfe6-2eb5-5a66-9d0b-672250d2e67a | textbox | Other items
87cc2e94-2852-5e3f-8f1b-d8b46bb36442 | number | Total value
453dec8d-3ba2-448a-b765-0fee0b726515 | checklist | Ω (DEPRECATED) DN1210-007 ITP Stormwater Rev 0 | itp | DN1210-007 ITP Stormwater Rev 0
9dbf9507-d5c1-5f76-b0e9-632a875b7d7c | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
61faafb8-e067-5299-84f0-3fd60960e68e | checkpoint | 1.1.1 - Extent of Line Setout
8c6ec2f9-39bd-56e6-af44-d2517ac396f2 | note | Detail - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Stormwater drawings. Identify any clashes before construction.
7d6a7e91-0e37-5917-8fba-1a8a1eefae57 | note | Acceptance / Conformance Criteria - Engineers Approval
e5fee9e3-7922-574d-92a5-7ffc18141aab | note | Standard / Specification - Design Drawings
44187e60-7257-5c43-8598-469a199c8f58 | note | Verifying Document - ITP Sign Off
1f14d97f-faf6-5369-b434-80379019109a | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
8b6e67aa-6aa6-5b21-9bfd-9a3eb29a45ee | note | Verification Activity: Activity - M
a97d5839-1e49-59fa-b864-a3a67cc79564 | note | Verification Activity: By - PE
58d8e667-bb88-509f-83a3-6a1f01d0e239 | checkpoint | 1.1.2 - Existing Stormwater system
49e460ff-036a-53b2-b79f-9c99f6652733 | note | Detail - Confirmation of existing stormwater network.
42c9dd57-cc47-5267-b8e0-a6a8918f72a0 | note | Acceptance / Conformance Criteria - Survey Informations
7a99dc1c-fb5a-5edd-876e-c469c1399ebf | note | Standard / Specification - Appendix V
741ac5b0-1750-5d08-89d8-999292956bf0 | note | Verifying Document - Survey data
39a0f032-457e-5f57-abda-8c2115ba5d0c | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
3651724b-6601-57d2-9532-88e9342cce24 | note | Verification Activity: Activity - HP
1684a043-6be9-57cd-a4e1-b987c3933cc0 | note | Verification Activity: By - ENG
439eb8b4-e232-503c-ae3b-29d0c5635540 | signoff | AUTHORITY HOLDPOINT
b2505ca3-943c-534d-afb7-23e310ef1e65 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
7b779b30-3202-5976-a674-5a18e46af7e0 | checkpoint | 2.1.1 - Material grading: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
1f334567-e26c-5615-a6c5-437f663ff8bd | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
24d05b84-18e6-5631-89c4-8498e20aed26 | note | Acceptance / Conformance Criteria - Stockpile size 1500 to 4000m3. PS- Table 21.2 for GAP/AP20 PS- Table 20.3 for Overlay and Embedment Zone Material NZTA F/6 for Drainage Aggregate- Grading section 2.2
5c9ddec3-cfba-5a3a-924a-5cd74196e283 | note | Standard / Specification - PS-21.7.2
a3371f70-425c-5a18-9783-f9204e2236fa | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
0cbe2752-5826-50eb-837c-fe29a51d166f | note | Testing Quantity Required (based from schedule qtys) - 4 Test 1 Test for each additional 1000m3
f33c1220-9cf8-5e0f-b2f5-9a13930a12cb | note | Verification Activity: Activity - HP
daa93a5e-c9ac-5db2-a1d1-769932c9e987 | note | Verification Activity: By - ENG
d9a47fe7-92b9-5d7e-ba3b-89916ba64f50 | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
4aeddbe8-5560-52d8-adc7-e338b59829ce | signoff | AUTHORITY HOLDPOINT
8d324d50-cc82-585e-af30-1900442f0418 | checkpoint | 2.1.2 - Weathering index: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
3e9433c2-8416-541a-9b8e-f94896d44afd | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
02556238-6038-5fd8-b6ca-daae3b6dab89 | note | Acceptance / Conformance Criteria - Engineers Approval AA to CA
aaddeb8c-95ff-56d6-9a6f-3409bffb689d | note | Standard / Specification - PS-21.7.2
189140fd-eb19-5a38-9198-6caffd786c65 | note | Verifying Document - Lab Test Report NZS 4407.3.11
da98e593-24a7-5f5a-8ce9-7c74c81324f7 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
792e2727-8b39-5b9a-b169-fd5e24df259b | note | Verification Activity: Activity - HP
cd225301-feb2-5a18-90ba-b565d40136e9 | note | Verification Activity: By - ENG
b934f0f0-a41c-5df1-9909-a98c6e8a0321 | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
a2fc101a-90b9-54e1-89a9-1383075ee775 | signoff | AUTHORITY HOLDPOINT
5c6967dd-7748-5877-a08e-26c0fca616fa | checkpoint | 2.1.3 - Crushing Resistance: Materials (GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate)
42790e68-27b0-5257-b87e-1982f42796e2 | note | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone/Pavement subsoil drainage aggregate and undercut material compliance.
984bb7bc-4f10-5043-80f2-d40e640bf675 | note | Acceptance / Conformance Criteria - Engineers Approval >100kN
e3bb4083-971b-55a2-9772-0a0a21cf7749 | note | Standard / Specification - PS-21.7.2
0a7679d5-39c2-5de1-b95d-39ec647eab43 | note | Verifying Document - Lab Test Report NZS 4407.3.10
7b856239-6bd6-5372-9166-20d22ad5dee5 | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
8585d6ff-4e91-5a30-8302-655099e0e606 | note | Verification Activity: Activity - HP
2648d9d0-a0ed-5b83-8385-c18a55813457 | note | Verification Activity: By - ENG
65121ca3-b1e1-5e4a-a887-0a084d4ac8bf | note | Comments / Closeout Details - The grading limits on the Stevensons quarry materials provided are acceptable to use (LRAP65 and GAP20)
cbd04506-6cf4-5b18-9ff7-c44dfcd7f02d | signoff | AUTHORITY HOLDPOINT
7191560b-5e9b-500b-8294-b06ed11c768b | checkpoint | 2.1.4 - Geotextile/Geogrid
6edffe58-5601-5dee-9731-a95829301d91 | note | Detail - Minimum Strength Class C & Filter Class 1 or TNZ F/7geotextile is to be used in Trench Backfill of Drainage pipe in Wet conditions.
3a4e22eb-c194-507d-ad79-45831776f912 | note | Acceptance / Conformance Criteria - Engineers Site Representative to inspect trench.
ea038197-1b00-5782-8df6-03b39f7859d3 | note | Standard / Specification - PS-16.5.7
45a7f083-9498-53f2-b122-3e13010cc7d0 | note | Verifying Document - Certification
0f9de01c-864c-5a5d-9a87-6273d2f836c7 | note | Testing Quantity Required (based from schedule qtys) - 1 time
7bd65c91-8676-53ea-80aa-104dd809277c | note | Verification Activity: Activity - HP
70bcf854-abb5-5221-9218-490224e68a4a | note | Verification Activity: By - ENG
b25b3fba-56ef-5a01-97a4-28b869a99641 | signoff | AUTHORITY HOLDPOINT
d353cea1-760b-54fc-ba9d-3f6628ef5bc6 | checkpoint | 2.2.1 - Riprap test Criteria
d286ec9a-b058-5a28-8a8f-00cf21213193 | note | Detail - Weathering Index of Coarse Aggregate.
b4077272-8d75-5913-bca2-1bfc527d262e | note | Acceptance / Conformance Criteria - Engineers Approval AA to CA
4831fecc-6eb9-5f1b-81f3-d46c6f6c69d7 | note | Standard / Specification - PS-21.7.4
68a6c4d8-cf61-50c7-9b19-fe178bdd7042 | note | Verifying Document - Lab Test Report NZS4407.3.11
a816cfe2-2037-516c-975a-ca474f1f903b | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
8657b15f-6259-5bf9-ae34-67f8613f7f29 | note | Verification Activity: Activity - HP
ad7dd6dd-66e5-55cd-bffa-63ca75e31be6 | note | Verification Activity: By - ENG
c2623d1f-bd3a-5637-bac9-0bae411ac607 | signoff | AUTHORITY HOLDPOINT
37c23bd2-a3fb-5b1c-be0c-98555e939a1c | checkpoint | 2.2.2 - Riprap test Criteria
1f2b2ecb-2e9e-536c-b013-fa147e18aea2 | note | Detail - Crushing Resistance of Course Aggregate.
9f617669-633c-5613-b494-287a0eaa94a0 | note | Acceptance / Conformance Criteria - Engineers Approval > 150kN
9238c7ab-8930-54a1-9a16-5efa91586e06 | note | Standard / Specification - PS-21.7.4
c6746b54-5e95-5509-bcff-cf78f24161d7 | note | Verifying Document - Lab Test Report NZS4407.3.10
8b24e29e-64a0-5fbb-a080-7de232bfbf75 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
fc644247-06a4-507e-a5ac-029409aa04df | note | Verification Activity: Activity - HP
498ea4f1-b4e1-51d9-a137-bfa5469497d6 | note | Verification Activity: By - ENG
1ac63ecd-b84e-5578-bb6f-a120cffbdda3 | signoff | AUTHORITY HOLDPOINT
b0917513-6283-539a-acb3-a2b3aa920522 | checkpoint | 2.2.3 - Riprap test Criteria
d628b4fa-a5af-504b-a446-56451c012aa7 | note | Detail - Solid Density of Aggregate.
dfdbff3b-306e-5700-8fe9-fd39b874d80c | note | Acceptance / Conformance Criteria - Engineers Approval ≥ 2.65 tonnes per m3
a4334eca-ba29-5bde-8260-79e987fe1d3b | note | Standard / Specification - PS-21.7.4
25932fa2-7703-56ba-83e1-059a9132add0 | note | Verifying Document - Lab Test Report NZS4407.3.7.1
2187692d-ece8-5d53-8ef4-159ba70b2333 | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
7bfc33aa-87c5-5816-965d-d04b52316581 | note | Verification Activity: Activity - HP
df1af21a-0031-5b1e-bf94-ec72f87e1906 | note | Verification Activity: By - ENG
a590b01d-a0ea-50ef-b3d0-57465bb74403 | signoff | AUTHORITY HOLDPOINT
5317a3a0-6700-5834-a89f-bd6ef24b9bf5 | checkpoint | 2.2.4 - Riprap test Criteria
12f0ae57-b248-5298-9aef-21cb5140cd53 | note | Detail - Grading of the material.
73ec9ed6-31a3-5759-9d8e-af6d74715b93 | note | Acceptance / Conformance Criteria - D=50 150mm Riprap Grading Aperture Size- 230mm Aperture Size- 150mm Aperture Size- 95mm
002fa807-2c30-50a7-8e68-c20a54016e80 | note | Standard / Specification - PS-21.7.4 PS-21.5.14 Table 21.3
09758b78-075b-5f15-baa0-097393ff974e | note | Verifying Document - Lab Test Report NZS4407.3.8.2
11292c02-362a-584d-a56b-3f927be37292 | note | Testing Quantity Required (based from schedule qtys) - Percentage passing- 85 Percentage passing- 50 Percentage passing- 15
d31ca261-8d16-5930-bafd-7c13e256dbb1 | note | Verification Activity: Activity - HP
588d5b23-fad5-5711-97aa-fb690e88338a | note | Verification Activity: By - ENG
947ebb05-cb3d-5cbb-9402-8ca942d558c0 | signoff | AUTHORITY HOLDPOINT
98285b74-1d71-57f6-9977-ee088beb181f | checkpoint | 2.2.5 - Riprap test Criteria
255e8990-7914-5fa5-b163-eeb7f68c9963 | note | Detail - Point Load Strength.
2d7082ac-318b-59a1-8cce-77a95e658c7d | note | Acceptance / Conformance Criteria - Engineers Approval >1.5 Mpa
15ba3521-b680-5a07-b9aa-b31840006f30 | note | Standard / Specification - PS-21.7.4
f033c320-d8d9-55fe-821c-b40d10e4aa59 | note | Verifying Document - Lab Test Report ASTM D5731
619db733-dd8a-59a0-a845-0888aa125eba | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
3d026438-f16a-5d68-af72-5e85aeb86337 | note | Verification Activity: Activity - HP
87a4d598-27dc-5715-b148-458db0082944 | note | Verification Activity: By - ENG
0063bf6f-94a0-5293-8cea-55db2d898e31 | signoff | AUTHORITY HOLDPOINT
c58e1f7b-cdec-556d-b433-f2dbfce36ed4 | checkpoint | 2.2.6 - Riprap test Criteria
e4203914-0330-590b-a5e6-017784aba336 | note | Detail - UCS Rock
bde3dda1-6f3b-5ec4-a027-5d616f175f23 | note | Acceptance / Conformance Criteria - Engineers Approval >30 Mpa
2f9f77e7-86b8-5c19-b6fd-8c5a2a960825 | note | Standard / Specification - PS-21.7.4
8ef95ebd-fef6-5403-acc8-27880f47e268 | note | Verifying Document - Lab Test Report AS4133.4.2.1
ea339cdb-416c-5b18-8a8b-d996a77051ce | note | Testing Quantity Required (based from schedule qtys) - 1 per 1000m3
0e0d3efd-5dd0-5a5f-ad8c-7c6c66e92c9b | note | Verification Activity: Activity - HP
351f00b1-ec78-5d7f-add6-76cb4b6e545a | note | Verification Activity: By - ENG
ebf02735-8f7e-512d-8e6c-9d466034bd52 | signoff | AUTHORITY HOLDPOINT
7685f2ef-c62e-5fb7-a70f-d353bd416788 | checkpoint | 2.3.1 - Pipe and fittings. (uPVC SN16, PVC, PP, PE and Concrete pipe).
b01a1fdd-980f-57b1-be0a-974d4f3bb258 | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
4c191b62-9e9e-5c94-be52-070246d48b7a | note | Acceptance / Conformance Criteria - Site Engineer Approval
8d5cf5a8-4e17-5231-a5b6-ca8dd8ec696a | note | Standard / Specification - PS- 21.5.1 PS- 21.5.2 PS- 21.5.3
75775828-4804-5f60-a3df-9a82d162ad6b | note | Verifying Document - Delivery Dockets
751b8bc4-6897-5063-a6d7-87d47ec7c076 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
7e8d13c8-1979-5990-aacf-08b73505fda9 | note | Verification Activity: Activity - H
4006c96a-bc64-5e43-9917-9020fd14008d | note | Verification Activity: By - SE
a5d92bcd-6b64-564d-acc9-23954f1e76ee | checkpoint | 2.3.2 - Stormwater- Structure (SWMH, SDMH, GMH, CP, DCP, CPMH, MP, HW)
950e6069-be5d-58e8-906f-75c387756cac | note | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the Structure are correct and in good condition.
7249efd0-13a8-5579-bfe8-c850866e2857 | note | Acceptance / Conformance Criteria - Site Engineer Approval
b50f929a-38af-527f-a81a-e53528cbf432 | note | Standard / Specification - PS- 21.5.4 NZS 3109:1997
e6a2b17a-e105-5c3c-9310-968bf24eddd4 | note | Verifying Document - Delivery Dockets
63930cae-a21d-5047-ac1e-9857f8ff5e7b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
d41b08a3-eeac-54e7-8f15-e394c8e93b03 | note | Verification Activity: Activity - H
e9e75178-846a-5eef-b1b1-8521d4d46882 | note | Verification Activity: By - SE
cbed7aea-7be8-51e8-bfaa-a2df8eb77a1f | checkpoint | 2.3.3 - Granular Material (GAP20/AP20, GAP65/AP65/LRAP65/Riprap and Drainage aggregate)
407ef78e-50cd-57c8-8824-f9d8e8852c18 | note | Detail - Confirm Specification and material in good condition.
1136a1e3-699e-58c3-9d0c-aa15898cd5f4 | note | Acceptance / Conformance Criteria - Site Engineer Approval
b8087df2-d012-5974-9df1-eba90d28bbbf | note | Standard / Specification - PS-21.7.2
cdc5971a-6269-5354-b5c8-8f9475803eae | note | Verifying Document - Delivery Dockets
9d088f1f-9f2a-5ca3-bb59-e6e1b2142f5a | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5a3f4e82-12f6-5d82-8f50-0afdd218756f | note | Verification Activity: Activity - H
077a5639-66fb-5771-88cc-8c3b6cf276b6 | note | Verification Activity: By - SE
c71f9062-d24e-5bf6-a7c7-105d5eef56fd | checkpoint | 2.3.4 - Geotextile/Geogrid
7bcf08b7-ff3d-545e-84c3-04e1e82f1589 | note | Detail - Minimum Strength Class C, Filtration Class 1.
e1ab34a5-a3f2-5e9c-927f-ff3d58e9cc8b | note | Acceptance / Conformance Criteria - Site Engineer Approval
ae9fbf32-cb1a-5c09-97d0-ef9c77c01924 | note | Standard / Specification - PS-21.7.3
3c978ce7-deea-5c28-a3fb-87c317f1a200 | note | Verifying Document - Delivery Dockets
2666c2e2-715b-5082-910b-8fbf5a733244 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
95b961d6-569a-5cba-9d93-b4a540fa1ba6 | note | Verification Activity: Activity - H
e11c4279-6af9-5f37-8469-0635e4d97c4f | note | Verification Activity: By - SE
9cc06a11-17ee-5f49-ac50-31c36fc22fcb | section | SECTION 3 – CONSTRUCTION ACTIVITY
6060b861-66f7-50a6-931b-1a3e09522cab | checkpoint | 3.1.1 - Foundation Compliance
7536601b-5795-54c4-9390-a7bed0019a30 | note | Detail - On Granular or Cohesive Material
724edf15-3e3a-5915-9121-84578bd157f8 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
f830645a-2aab-58bb-906c-27c71c18a48c | note | Standard / Specification - PS- 21.7.2 Appendix V
8c31040c-a189-533b-825a-9de443fb9ff9 | note | Verifying Document - Scala test result
8740789d-55d4-5feb-971a-45877bdd7d1a | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
c84c9e22-44a5-5f1d-affd-04e3960ef8b3 | note | Verification Activity: Activity - W
6ecf1e8f-3477-5567-837f-fa8625d3e6b8 | note | Verification Activity: By - SE
c1c96344-d442-58de-82ed-d9085e766b87 | checkpoint | 3.1.2 - Undercut approval
00595da2-b0ec-5ba3-b6df-33932dcee49a | note | Detail - On Subgrade
7af00c8c-0774-501e-ba30-da67c0745a5c | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
25a1d52f-7fda-5426-b137-dd447b2e82ad | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
baaf7fca-54a1-5394-b84d-d1811e3fb804 | note | Verifying Document - Lab Test Report
8ea61e8d-88b8-50d8-acc4-310275e23e59 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
1d831097-2f81-5314-aeb1-6393177b78c0 | note | Verification Activity: Activity - H
92fe9a12-d005-54bf-bb3d-bfeeeb2adab5 | note | Verification Activity: By - SE
1a41ffdc-e630-5238-b3c6-b7ddb238f1d2 | checkpoint | 3.1.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
6479ab9c-b45b-5e98-ace7-2a2eb58883e8 | note | Detail - On Granular Material
6aa210aa-94f1-5f44-9779-2cb46f254d92 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
1da33ee3-ae6d-5b44-beeb-d48a29e36b20 | note | Standard / Specification - PS- 16.5.12
55ff37d4-947c-5ac3-a0dc-9a1ac4e5af92 | note | Verifying Document - Lab Test Report
b9c7f2b9-a88f-5b50-9010-a5d3751a4a1a | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
3195e80f-8f03-5d16-af20-4cc0d10e4085 | note | Verification Activity: Activity - H
bea0a486-f7a1-590a-9672-73554f189ccd | note | Verification Activity: By - SE
122c791d-c0bb-5292-b890-be01180cb1f8 | checkpoint | 3.1.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
eb402eea-cbce-5dd1-a273-ee269f7ccd3d | note | Detail - On Granular Material
83dc2d43-8184-51d7-94cd-24ed704f194a | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
d64474e8-d06b-51eb-b3e4-359d201a1552 | note | Standard / Specification - PS- 16.5.12
830684fd-21d1-565f-bd8f-b354a2dfb8f4 | note | Verifying Document - Lab Test Report
5ef9c053-d06b-5ce9-ac02-98995c5ebb54 | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
1bc17671-cf1c-5423-ba88-09bfa3f56f0b | note | Verification Activity: Activity - H
454bf4fe-bd23-55ed-b3e8-9e1c8817b574 | note | Verification Activity: By - SE
6f02a627-0efa-5c52-bfc6-1db0fde3e838 | checkpoint | 3.1.5 - Pre-Backfill Inspection
e77f1704-9e25-5c33-82d2-09c9dbcbaf60 | note | Detail - Inspection of Structure
f951ec8b-dc9a-5405-91b7-0b06259a0bc3 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
f66efe11-8c35-5953-92b4-943ab3b55648 | note | Standard / Specification - PS- 21.6.11
64af34f4-5cfc-5680-ac8c-58a6c7f63728 | note | Verifying Document - Manhole/Catchpit Record
b27ddea0-6078-5c28-9201-42a353cbad85 | note | Testing Quantity Required (based from schedule qtys) - Continuous
bb2164bf-e8e5-5586-aea5-061af184642d | note | Verification Activity: Activity - I
e5f99403-c158-536d-bfe9-6880cebf1bf7 | note | Verification Activity: By - SE
c35a65d5-6eb2-5191-8c79-ec76f3f7c3b4 | checkpoint | 3.1.6 - Survey
1bf06fba-025e-505c-a887-754d08cdaa1d | note | Detail - Inspection of Structure
eef5d195-346e-560a-9c18-f7ae502040d2 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
3d297368-0aa2-5564-8d83-e1bfe2975029 | note | Standard / Specification - PS- 21.7.6
585535f5-494f-5bcf-901d-dbd9dc20572d | note | Verifying Document - Survey Data
ac82bd90-691d-5db6-a45e-46fcee96c120 | note | Testing Quantity Required (based from schedule qtys) - Continuous
623c6f9c-4701-599d-8589-c1f0211284ec | note | Verification Activity: Activity - H
57afac1e-90f7-56b1-bd39-70911dccf45b | note | Verification Activity: By - SV
e681d924-eb9d-5908-874f-e2a9cfead256 | checkpoint | 3.1.7 - Backfill Compaction Testing
2e8ec344-8cd3-50fa-ab02-e7785f1be849 | note | Detail - On Granular or Cohesive Material
c5251a47-746a-55b5-8328-90325b509eff | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
84724f52-fc63-5dd7-94a8-ed5a9141e72c | note | Standard / Specification - PS- 21.6.12 Appendix V
f06b0520-7e15-5235-8046-70af6152b0c3 | note | Verifying Document - Lab Test Report
001d7a06-1d2a-51f9-a625-fecf948e3e76 | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
09b3371e-2d21-5aeb-8089-bc2b2d8f5770 | note | Verification Activity: Activity - H
00e72377-0f35-5af7-9afa-474c27318faf | note | Verification Activity: By - SE
8a67bad2-49a0-5b3e-9e07-3e95e06d76d3 | checkpoint | 3.2.1 - Foundation Compliance
6693aa39-d64e-5264-bf3b-3d30c6fa7822 | note | Detail - On Granular or Cohesive Material
e31f585c-fea8-5cfb-b089-a19c2db76d02 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
b276eb1f-1549-534b-a017-94d90077d154 | note | Standard / Specification - PS- 21.7.2 Appendix V
13cd0b61-a024-5d4e-98e4-6077201c68d9 | note | Verifying Document - Scala test result
ceef2f8c-5d86-5446-963d-a823469e910f | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
433d211f-33cc-5b63-8ae2-b545b77c9e46 | note | Verification Activity: Activity - W
81d04145-5426-5dea-860a-998a8a1ec3b7 | note | Verification Activity: By - SE
5c32e1a0-52b7-5c2e-8003-fdd7656ac09f | checkpoint | 3.2.2 - Undercut approval
ea278464-af9f-5fde-bd25-54d1ce0d139a | note | Detail - On Subgrade
80be3fd5-ac77-51c8-8656-679b043104cb | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
d035fdd2-0e37-5bf8-a24e-00f64ab6f4bd | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
b9dfc0b1-f7d0-5327-9c11-2df9f61ecda5 | note | Verifying Document - Lab Test Report
35c74bc4-0996-5b4f-b771-e9bfaeb3cf92 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
1c526564-e335-52bc-8daa-cd0f240e6fa8 | note | Verification Activity: Activity - H
4bd8b7ba-ea6f-5198-bb35-0097bea43aa0 | note | Verification Activity: By - SE
811e271f-f2a2-52ee-9167-0e158033e720 | checkpoint | 3.2.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
dcadc4d9-96fd-55ca-b0bd-89a8fff7a309 | note | Detail - On Granular Material
175eb5c8-e07a-5b6d-a58f-6695e40e86a8 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
def5d9ef-5cce-5477-9b47-c8546a5d1cb4 | note | Standard / Specification - PS- 16.5.12
7b3b0c16-3de9-53d5-8208-072297668bb8 | note | Verifying Document - Lab Test Report
10fb19b6-58bb-5b0c-ae29-e85d8d061777 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
30199c4e-14ec-592f-8548-0c6d5aded7b3 | note | Verification Activity: Activity - H
e9693bdf-97b2-570b-876d-3ccaed5e26a4 | note | Verification Activity: By - SE
77568fee-af21-5f9b-9f96-160b1a618b0b | checkpoint | 3.2.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
d3385acd-9e7e-55ff-ac08-aa28120b1ea3 | note | Detail - On Granular Material
6d9d584d-97c3-55a6-8e69-b1b64b687153 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
0adbe8b4-10a5-50d1-8637-12fd7870f94b | note | Standard / Specification - PS- 16.5.12
3d74ac21-d6ba-5b18-b993-94bb528d9d7c | note | Verifying Document - Lab Test Report
b1bb2dab-d898-5cd2-aad6-1e93c56ee60d | note | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
13a9894c-3b43-555f-8001-726e44a83bec | note | Verification Activity: Activity - H
54b0181f-8c7e-5a98-9b96-e51954539c7c | note | Verification Activity: By - SE
ff95eca0-5856-535c-b653-c34444e1d4db | checkpoint | 3.2.5 - Pre-Backfill Inspection
d610233e-42ab-5f87-a8d7-fca5762d01e1 | note | Detail - Inspection of Structure
4f3c5e54-c54a-5214-ac39-374f38f41675 | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
02c38837-cfa7-5130-8f2c-4bfe01c5e835 | note | Standard / Specification - PS- 21.6.11
7ce2509c-5fbe-54f8-88f6-a2b46450e743 | note | Verifying Document - Manhole/Catchpit Record
cd972a7b-69e6-5e5f-8399-85ca4a4f4fd5 | note | Testing Quantity Required (based from schedule qtys) - Continuous
fced3349-4f6d-5430-82c9-db793cb555bd | note | Verification Activity: Activity - I
d4e5c9b9-6be9-5d50-8c4f-59798657d98c | note | Verification Activity: By - SE
8438b253-2cbd-5d5d-b5cf-63795fbb55c6 | checkpoint | 3.2.6 - Survey
7bdafb6a-9389-579e-b973-43343bcdadf2 | note | Detail - Inspection of Structure
e865e0af-739a-5375-b99d-123f9ad5c315 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
0e860317-0ff9-5357-afc2-06540e5ba10a | note | Standard / Specification - PS- 21.7.6
66f21632-48c8-54e7-b7ac-9151bd796787 | note | Verifying Document - Survey Data
a0dbbb05-8b70-547b-ba31-519ac1630378 | note | Testing Quantity Required (based from schedule qtys) - Continuous
8f5ce6b7-123f-53d3-9130-bb110ec1b3a1 | note | Verification Activity: Activity - H
c41e2a53-7736-569c-b991-9bd9148cb4be | note | Verification Activity: By - SV
b695541f-0861-5c72-a422-a5c37de96d6a | checkpoint | 3.2.7 - Backfill Compaction Testing
06f3bd12-4223-53d9-b29e-7d06a8343e5e | note | Detail - On Granular or Cohesive Material
8ef45800-36a7-57f2-91cf-a08f6e68c701 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
c253d9db-85d6-5395-99e5-ea5597604fdd | note | Standard / Specification - PS- 21.6.12 Appendix V
d72d5baa-fcce-5be2-833e-294e3bb480d5 | note | Verifying Document - Lab Test Report
f122f1b7-fa5f-58a5-b9ad-f7ca22b1bbea | note | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
46ee0a82-6c95-556e-8e14-55b3fe15e3f6 | note | Verification Activity: Activity - H
b4c34036-c8c4-53ac-99aa-ab67401f7bc3 | note | Verification Activity: By - SE
300b8fa1-28bb-53b2-8f55-761644c8d091 | checkpoint | 3.3.1 - Foundation Compliance
72b25472-d766-501a-831b-55c9f74ccb4f | note | Detail - On Granular or Cohesive Material
930b3a55-fefd-5113-b05d-16fd1c509667 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
d0feac88-eb37-517f-a9b7-520293a67e61 | note | Standard / Specification - PS- 21.7.2 Appendix V
a2b06bbd-6854-5815-880c-d7cf839fef59 | note | Verifying Document - Scala test result
6e33f9c1-30e4-5561-b3cf-a235a3921534 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
f1767cdd-3d25-53fc-a759-9694a9376d59 | note | Verification Activity: Activity - W
eb8d5159-f0aa-5677-8701-777298379968 | note | Verification Activity: By - SE
dff5ee8a-9019-5036-bebf-6f91dc5f062c | checkpoint | 3.3.2 - Undercut approval
62f7f656-3915-5fe1-999b-b1c784c58bb2 | note | Detail - On Subgrade
18aad1f8-a05d-569e-bd6f-f312c8237b7a | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
94915bbc-9276-53e4-ae92-1debd9c4e928 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
835a9559-1b67-550a-b55f-8e55eb2dfd68 | note | Verifying Document - Lab Test Report
79397d05-e464-55ed-adaa-ed48e7df704b | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
a845de8f-a05a-5d34-b04f-b007ea7876b8 | note | Verification Activity: Activity - H
b437dfd3-46d2-5a26-9ad5-98ccea8c7a11 | note | Verification Activity: By - SE
19146973-bab4-5555-ab24-77b09a0bbffe | checkpoint | 3.3.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
bf7449a2-e26c-52e5-a4e1-4804e01160c8 | note | Detail - On Granular Material
422260c0-3c73-5bec-9a50-24b474648e95 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
c4f86e78-aa99-59f3-96c8-0b5c9589c87b | note | Standard / Specification - PS- 16.5.12
0933885b-432e-5287-869b-39cee23cc6ce | note | Verifying Document - Lab Test Report
e9a47674-39d2-583b-8646-550672af1e8a | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
7f9eb0b6-750c-5889-a74a-664d89746c81 | note | Verification Activity: Activity - H
78779cd2-0f31-5357-b747-116add696165 | note | Verification Activity: By - SE
94a0623a-421b-55f6-bfcc-21a724ec9dfb | checkpoint | 3.3.4 - Bedding and Embedment Zone Compaction Testing (Polypropylene(civil boss)/Polyethylene Pipe).
5d6416a8-6629-59b5-8972-8054db23e34f | note | Detail - On Granular Material
b56a5fbf-25c2-5138-ae4c-a3a9acc94f41 | note | Acceptance / Conformance Criteria - Bedding Zone: 100mm(for DN300 & DN375) 150mm (for pipes greater than DN375) Embedment Zone: Pipe Dia ≤450 - 150mm GAP20/AP20 - Overlay Pipe Dia 450< D ≤900 - 150mm GAP20/AP20 - Overlay Pipe Dia 900< D ≤4000 - 150mm GAP20/AP20 - Overlay Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
b6dc7386-bcd0-5a96-b0db-e9b815586e18 | note | Standard / Specification - PS- Table 21.7 PS- Table 21.12 AS/NZS 2566.2/2002
98cbd37d-a6ae-5726-b7a6-b8c811e85d8e | note | Verifying Document - Lab Test Report
c9022001-0066-5752-9f30-29dec6664249 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
eb703980-b343-5b35-b4e9-ae266e81c5a2 | note | Verification Activity: Activity - H
08b1c655-664d-5fad-ba55-b191d3419185 | note | Verification Activity: By - SE
d2e13628-b927-50fd-ad8e-db3f761f1f7d | checkpoint | 3.3.5 - Survey
4f14edc7-e9a4-52f1-86c5-798205a9be33 | note | Detail - Surveyor to Setout
9aaf4ffb-8a34-55c0-9b8f-534553d3a398 | note | Acceptance / Conformance Criteria - Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance
5f46781b-fac3-5535-b0f7-4236485214f6 | note | Standard / Specification - PS- 21.7.6 Table 21.15
29691daf-2cec-5dbc-9554-fd4dd5340e7a | note | Verifying Document - Survey Data
aa9af37a-13a7-5b98-8ca2-93763c070541 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
7ca755d6-9e4e-5c08-b7bf-60dfcec72b9b | note | Verification Activity: Activity - H
bb14b4d7-ca9b-55e5-93d4-c48df3421efe | note | Verification Activity: By - SV
652c96e1-768e-5161-abb8-33857043d37c | checkpoint | 3.3.6 - Backfill Compaction Testing
47ca7528-0d20-5fce-992c-8c0031ca4e99 | note | Detail - On Granular or Cohesive Material
32176970-0811-5c42-91cb-991b95a0281d | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
9842a3cd-5db2-54d5-865d-b6f862a0a05c | note | Standard / Specification - PS- 21.6.12 Appendix V
a5d78d5b-202b-5f3c-a550-fd62b25bd144 | note | Verifying Document - Lab Test Report
e7439544-899e-5b79-8ee2-d2bb641a8f06 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
1aae88bf-61ef-5403-97bf-80a113807d94 | note | Verification Activity: Activity - H
43b502f6-f5ba-5206-a0fc-688b56775d8c | note | Verification Activity: By - SE
276798c2-34e6-5e87-bb66-a7f7df9fa38c | checkpoint | 3.3.7 - Pipe Inspection
a06df628-6013-57d7-a7ac-1babe6b7f651 | note | Detail - Inspection of Drainage line
ec6eb0af-4baf-5fab-9b74-5626aa4d40db | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
19d27f5f-351b-5aeb-9ea9-d95200a9b1fc | note | Standard / Specification - PS- 21.7.6
e1c1c3c9-58ca-56b4-85d0-e418d334d0b5 | note | Verifying Document - Drainage line record
5aa69d23-1991-58b1-9a59-332e16116508 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
c091935b-68ff-51ce-98cb-936e9c5d13fa | note | Verification Activity: Activity - I
73b2bb90-7fd3-5df0-b0d5-4a0cbfb04bb8 | note | Verification Activity: By - SE
23e48d28-c984-5a1a-adf0-687888856fce | checkpoint | 3.4.1 - Foundation Compliance
b1f82680-2f23-507d-87ef-07e955ead30f | note | Detail - On Granular or Cohesive Material
1b93c683-9a16-58d4-ac1b-397eeb6713a0 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
294224ec-429c-56f6-b1f4-926c48f6aedf | note | Standard / Specification - PS- 21.7.2 Appendix V
d9e02b9a-d672-52e5-a7bf-b568f7a18e0a | note | Verifying Document - Scala test result
5e9520af-5a32-5a5c-9585-f45b773a33cd | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
2499b3ea-793c-5c4b-8fa9-3064a06065b4 | note | Verification Activity: Activity - W
2a5383b3-1ae7-58cb-9ef3-97ba0f35a866 | note | Verification Activity: By - SE
2e297fed-b0b9-5c9a-82c6-da43f519fdc6 | checkpoint | 3.4.2 - Undercut approval
545f6878-eea1-53de-b124-115e4bea2d50 | note | Detail - On Subgrade
10340e4e-6257-5290-b88f-6e40d6a7a12f | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
edb7d806-2d41-5542-98c4-eb52582f365d | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
093f5f9a-3816-5de1-ac1c-6e9fcd02705d | note | Verifying Document - Lab Test Report
80a49d8c-ebb7-5b16-9ca8-d1dcf9e87a49 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
bd67af40-cd47-5271-84e1-b2da193705be | note | Verification Activity: Activity - H
f625d731-0e13-5d69-948e-c653bdc205df | note | Verification Activity: By - SE
34f0d9ca-7f76-56e1-a2e3-84ec7ac51186 | checkpoint | 3.4.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
1cde9d5b-6e5b-51b0-96b1-89b50215cdf0 | note | Detail - On Granular Material
ecfefb9b-e1e0-5eab-90d9-373d1bcda7be | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
53de2b2f-1021-5d68-a804-5faae55e6841 | note | Standard / Specification - PS- 16.5.12
7e978c77-060f-54fb-ae26-91a16b8ef59b | note | Verifying Document - Lab Test Report
2cdd3332-b236-51b5-8327-796aa39199f1 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
6162c2a1-63a8-57fb-bb0b-7622e1405e38 | note | Verification Activity: Activity - H
173f5d3c-1b2b-5dcc-a2ac-58c7bfbe497c | note | Verification Activity: By - SE
5d768dd2-9cd0-5756-bb3c-505106479de8 | checkpoint | 3.4.4 - Bedding Compaction Testing
e0d9eb16-66df-5645-8e1f-d4e3c38dda8b | note | Detail - On Granular Material
99b11551-54e4-54cd-a53d-cad405368fc6 | note | Acceptance / Conformance Criteria - HS2- 0.3xD (outer dia of the pipe) Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
b2a1e921-a6a9-5310-bcf0-49ace4543ca2 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
98f34698-29eb-5684-b946-231b0b1fdad6 | note | Verifying Document - Lab Test Report
1a08ef5d-a3eb-55f8-a583-415abebb5504 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
9aa15384-64ca-56a3-a1a5-704acaf63829 | note | Verification Activity: Activity - H
19ee0ce2-d1ad-586f-81ea-517090fdf8fa | note | Verification Activity: By - SE
4bfe46f7-744f-55e6-8523-2ea18484410b | checkpoint | 3.4.5 - Haunch Zone Compaction Testing
224e6c9d-bdd6-531f-9a04-548031bde3a1 | note | Detail - On Granular Material
75f3cb6e-0698-5a92-8841-e0e9a35055a8 | note | Acceptance / Conformance Criteria - HS2- 100mm if D≤1500 (or) 150mm if D≥1500 Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
ed49a71e-fcd5-53e6-9ca9-d990f1cff0d2 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
cf4d2da9-bd55-5f3f-9c41-662eaa888790 | note | Verifying Document - Lab Test Report
f0be1216-6c9e-51d9-9af2-b2e776e44c86 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
9efd0274-a60a-57ba-b9ef-ccb4abbf1e5c | note | Verification Activity: Activity - H
e36eb1a9-5762-5ddc-ab87-3a11d36356ff | note | Verification Activity: By - SE
4844df56-a700-5e51-ab74-6839a6589fc8 | checkpoint | 3.4.6 - Side Zone Compaction Testing
045cfc2d-e067-5c0d-b7ee-3de5ee0a51c0 | note | Detail - On Granular Material
902bb784-8f80-55d7-a628-ba068f696b5a | note | Acceptance / Conformance Criteria - HS2- 100mm if D≤1500 (or) 150mm if D≥1500 Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
197bfed8-4df7-5d6b-896c-bc9e643a3fe5 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
22a9f67b-954c-5a70-a4be-1ea07b3eec27 | note | Verifying Document - Lab Test Report
bd0aa8a8-2d6a-56f4-9da3-955b0d0bec8e | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
02a51015-539b-5496-a1d6-cca46e19783f | note | Verification Activity: Activity - H
c0f448f2-ef13-57ec-b25e-67d5360e370b | note | Verification Activity: By - SE
43578e81-672f-5d7a-9d20-9ac1e812a489 | checkpoint | 3.4.7 - Survey
f110438e-dbb1-5f27-b476-ad22c584065f | note | Detail - Surveyor to Setout
d13b1de4-0a4a-55fc-ba7f-1bcf383fe023 | note | Acceptance / Conformance Criteria - Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance
a7bf3aa8-13db-5519-a403-e2e43b483e2f | note | Standard / Specification - PS- 21.7.6 Table 21.15
551d7c42-81f9-5cef-aaec-1839171717f6 | note | Verifying Document - Survey Data
6c9ae2f8-ce02-5e92-82d0-2782494c2f06 | note | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
02243be4-0538-547e-8fa3-672b12b7beb2 | note | Verification Activity: Activity - H
3a82526b-f26f-58bf-8e47-1f813a1487b8 | note | Verification Activity: By - SV
b1c5561f-735f-5ab9-80a5-52eccf1118e5 | checkpoint | 3.4.8 - Overlay Zone Compaction Testing
21620ddf-4f86-5dfe-932a-8b6316603fe3 | note | Detail - On Granular Material
dfcd6cd6-66e2-538b-8a8c-67d72e089686 | note | Acceptance / Conformance Criteria - Minimum Compaction- Trafficable and Non-Trafficable 95% MDD on metal.
33243dda-43bd-581c-8039-3e52aeb08f27 | note | Standard / Specification - PS- Table 21.6 PS- Table 21.12 AS/NZS 2566.2/2002
f8e50a62-3f10-5546-a417-21c635152588 | note | Verifying Document - Lab Test Report
431e22ce-c629-529b-b9ad-fb11b917760c | note | Testing Quantity Required (based from schedule qtys) - One test per 30m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 1 Tests 0m-50m: 3 Tests 0m-100m: 5 Test
d6b81813-19b0-5eb9-ab7d-2e630aa5a232 | note | Verification Activity: Activity - H
fa87cd6f-f03c-5fd2-866d-130718e89598 | note | Verification Activity: By - SE
1b1ebc88-e4b8-502f-a958-3dcc4a007de4 | checkpoint | 3.4.9 - Backfill Compaction Testing
6a094b79-1e76-5958-8703-4e9310286b05 | note | Detail - On Granular or Cohesive Material
11097803-d3b1-5322-8840-d9c50d0ca5dc | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
cc1b8541-1fae-502d-a986-042fb92fef01 | note | Standard / Specification - PS- 21.6.12 Appendix V
7398fa83-6c42-5e52-9853-413853c200c4 | note | Verifying Document - Lab Test Report
8e68f238-4b88-503f-a35e-a4968b197090 | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipeline with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
1fe264f1-fced-5c9e-92b3-e784ab8ea9c3 | note | Verification Activity: Activity - H
4616e0ce-8c25-596f-a21b-a6bea2533fe2 | note | Verification Activity: By - SE
b758dbb4-248e-55bb-94cc-12a4cac84109 | checkpoint | 3.4.10 - Pipe Inspection
8d62a9ca-2cb4-51ee-8612-9cfdecb7cd6d | note | Detail - Inspection of Drainage line
7390c541-2715-5937-a0fc-79281c4f4290 | note | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
c70214f0-30f1-5268-ad19-c6148d2aae66 | note | Standard / Specification - PS- 21.7.6
ae3d6d27-9844-5c17-ba83-d851b62db0a8 | note | Verifying Document - Drainage line record
cc65bc02-bfd1-54ff-a5a1-a937d0a7af29 | note | Testing Quantity Required (based from schedule qtys) - Continuous 1 per Line
85044673-0283-5e56-bae4-211e54ff9e8a | note | Verification Activity: Activity - I
5d0e0b52-3d6f-54c9-b7b1-24e898dd5b39 | note | Verification Activity: By - SE
a76d1aac-996b-561a-bc2b-69470a3fa996 | checkpoint | 3.5.1 - Headwall and Wingwall Foundation Compliance
f78edb06-81df-5055-a7c6-22d019d7c9d4 | note | Detail - On Granular or Cohesive Material
97596680-55f9-5a46-8ce9-b8b1984f656d | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
161eaefd-8b47-59b9-b777-387959290641 | note | Standard / Specification - PS- 21.7.2 Appendix V
7b8e1d0e-bdaf-5c20-8b28-cafdadd6986c | note | Verifying Document - Scala test result
e03bdc2e-8294-534f-a613-5a33f65f7bd0 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Structure
2040fe92-1fb9-507d-b744-8496efceebd4 | note | Verification Activity: Activity - HP
b7f8addb-ca48-546f-a551-113c91e28417 | note | Verification Activity: By - ENG
70cd1be4-24ef-5063-abbf-f9dd93200e27 | signoff | AUTHORITY HOLDPOINT
f0688442-75bc-5d76-8177-3a9f6ee2134e | checkpoint | 3.5.2 - Undercut approval
ef0cd571-aeb0-54e9-9e9e-19dd57cc235e | note | Detail - On Subgrade
bb14ca25-4957-5fc9-8545-89ff1c784f8a | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
655ae977-f498-5805-a035-bc4288e7a720 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
05a01e9c-c880-52f5-94aa-0b63f931fedb | note | Verifying Document - Lab Test Report
a9411a00-5910-5970-aa31-7e3d6790cf9c | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
b06f7107-af61-5bfb-bf17-3763ded23ba6 | note | Verification Activity: Activity - H
95be9e29-2675-5975-90ba-ec47a2d96f0e | note | Verification Activity: By - SE
2478973b-6f47-5310-9ffd-14c721927804 | checkpoint | 3.5.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
5042d307-9abd-5707-9605-d866128daf16 | note | Detail - On Granular Material
fa542ca6-6552-5098-94cd-791e525997ec | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
b9cbfc1c-82d8-5684-822f-dad934367fa1 | note | Standard / Specification - PS- 16.5.12
23883edc-8bb5-5cf2-ba08-227d467d0ee7 | note | Verifying Document - Lab Test Report
bdb4fb1d-8f73-5155-b396-f6c9d5bfd867 | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
94f59778-160b-5167-ab93-15cf962ff3fd | note | Verification Activity: Activity - H
24812b13-38e5-58c8-91de-caf926e6101b | note | Verification Activity: By - SE
4ba0a161-7530-58d1-afea-40100c2ddf2a | checkpoint | 3.5.4 - Bedding Compaction Testing (GAP65/AP65/LRAP65)
aa4eae94-8e84-57e9-bc40-c0b6b8009d56 | note | Detail - On Granular Material
eba0b638-dba3-5c2a-ab67-2e5b677eedea | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
c6897a67-2e80-5b1d-8f91-4aed91d56933 | note | Standard / Specification - PS- 16.5.12
bb90d2cb-a8b6-530d-b551-b981361468b1 | note | Verifying Document - Lab Test Report
71ae2f59-a3e0-51c5-a2e9-f2c0861accbe | note | Testing Quantity Required (based from schedule qtys) - 1 Test per Structure
c0bf7afb-a77e-5085-943d-ab34d9e6b8ef | note | Verification Activity: Activity - H
16e83c92-8258-53c7-be6e-bd8f2bc5bf7b | note | Verification Activity: By - SE
67a6cf71-f8c4-51e4-a8e6-ca7a915ab61e | checkpoint | 3.5.5 - Pre-Backfill Inspection
c9139488-9c15-5b76-a7ac-fe17a6e366e7 | note | Detail - Inspection of Structure
83687d12-36a9-5e3d-92c8-897dcf39c5fc | note | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
734c6fe9-b6e4-52ea-8756-b95c074ba38f | note | Standard / Specification - PS- 21.6.11
8180e4c1-c5b4-5603-94e3-0a2f84fec26b | note | Verifying Document - Manhole/Catchpit Record
9e476b44-9580-5f7d-8534-13388d2f8daa | note | Testing Quantity Required (based from schedule qtys) - Continuous
8e9a0637-842a-5346-80d7-c99da18b9f0a | note | Verification Activity: Activity - I
4b91cc23-a269-5d77-b7ac-8accd37f2e43 | note | Verification Activity: By - SE
d18baf16-8975-5e0c-8261-32049d9f49aa | checkpoint | 3.5.6 - Survey
84f9a34c-796e-57ed-b114-985940468f9f | note | Detail - Inspection of Structure
5711b32e-0f22-5f39-a7c7-b4e77ea77a32 | note | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
a48f22c0-7cdb-59b4-afec-1a8992a98a71 | note | Standard / Specification - PS- 21.7.6
e95723be-0632-52be-9f6d-f854b5b07e04 | note | Verifying Document - Survey Data
ff404fa2-d32e-5ed9-8635-b5305ae93854 | note | Testing Quantity Required (based from schedule qtys) - Continuous
29a1340b-6e42-5360-b910-b3b22a11e517 | note | Verification Activity: Activity - H
ce76f530-653d-59ae-8e7a-47f935139969 | note | Verification Activity: By - SV
dc025cac-6aca-58ae-b492-06adb07f8de3 | checkpoint | 3.5.7 - Backfill Compaction Testing
1346e21b-2fef-5562-85ac-4cea3a579f77 | note | Detail - On Granular or Cohesive Material
71051c6d-4c93-52d4-b996-5076b9fb16d6 | note | Acceptance / Conformance Criteria - GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
3195505d-e3f2-5348-baf9-25ab49003165 | note | Standard / Specification - PS- 21.6.12 Appendix V
14bcfe6b-29c5-53b7-9ba1-74dbebc17739 | note | Verifying Document - Lab Test Report
3b096be4-1256-5002-a55a-71e8231fb4d7 | note | Testing Quantity Required (based from schedule qtys) - 1 test per layer at Quarter Points around the Structure.
4039098c-fb29-5e32-91ac-91c844648db6 | note | Verification Activity: Activity - H
81f698d1-a27d-5d65-bc46-6da8159ee841 | note | Verification Activity: By - SE
909aaa35-1436-5b32-b06b-9bd5efa45dfb | checkpoint | 3.6.1 - Riprap Foundation Compliance
8c982575-8f2c-59c1-977e-c25c39d64f25 | note | Detail - On Granular or Cohesive Material
2bb8285c-229b-54fb-97ec-f833ba6be8f1 | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
dc955bbc-9a3d-593e-9962-9c82ee33751b | note | Standard / Specification - PS- 21.7.2 Appendix V
9add7a5a-96f2-581e-bc0c-7dcc547c8131 | note | Verifying Document - Scala test result
458d268d-c5ce-58a1-acdd-6a0e85e5b93b | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
4265f2e4-0470-5cd6-99c9-d0fbed85396e | note | Verification Activity: Activity - W
8e3ec2d6-cb8b-5d7a-82ad-f27f70273460 | note | Verification Activity: By - SE
c318d5a2-491c-50a3-a033-e6f98e6800b5 | checkpoint | 3.6.2 - Undercut approval
0e8c63a4-8c7b-5557-b780-b6bd4f412b40 | note | Detail - On Subgrade
d618f982-fedd-5c90-b8c8-6f337bd942df | note | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
f89839c8-0e55-5a32-849f-7799c50c9639 | note | Standard / Specification - Table 1 Sheet STW 0405. PS- 21.6.11 AS/NZS 2566.2/2002
e53943a5-601a-5adb-aca0-5d36125067c9 | note | Verifying Document - Lab Test Report
7b1e4c0b-e56c-5662-88b8-11aaf8368b70 | note | Testing Quantity Required (based from schedule qtys) - If Undercut required
67d32ada-8318-541d-aff5-31b1a35b74fa | note | Verification Activity: Activity - H
5445342b-5422-5140-9aec-4eed0f9bebf4 | note | Verification Activity: By - SE
6a55d5f9-a096-5d22-bb1c-56e2e00cb6d1 | checkpoint | 3.6.3 - Undercut Backfill Compliance (GAP65/AP65/LRAP65)
4d27efe5-19d0-50e1-8ef6-50037e431090 | note | Detail - On Granular Material
1cc127d0-0a40-512c-8ee3-73acb8f02810 | note | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
27b92731-ded7-54d5-9e34-9ba001b42097 | note | Standard / Specification - PS- 16.5.12
a2064463-78e9-5070-a08b-0d3b645233d1 | note | Verifying Document - Lab Test Report
930351f6-ec88-51bc-8c2d-be40d14ef1cb | note | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. 0-5m: 1 Tests 0m-10m: 1 Tests 0m-20m: 2 Tests 0m-50m: 4 Tests 0m-100m: 6 Test
673ded28-b7af-5da6-9048-05f86cacdd96 | note | Verification Activity: Activity - H
92b90047-732d-5e91-8a1b-0c821b01b370 | note | Verification Activity: By - SE
70aa118b-5499-55a2-88d1-6a112d0eb702 | checkpoint | 3.7.1 - CCTV Inspection
46c6bdc6-2aae-5108-affc-809fef37f6fd | note | Detail - CCTV stormwater pipes at completion of trench backfill but prior to final surfacing (pavements, etc.)
ccd8b0cc-b65c-5d2e-a6da-a6fe7b42fda4 | note | Acceptance / Conformance Criteria - Every stormwater pipeline 225mm diameter or greater.
162700d6-751b-549a-96a9-86215702274a | note | Standard / Specification - PS- 21.7.6 PS- 21.7.8
d89f7f1c-f83f-5c38-982b-be558f2eb986 | note | Verifying Document - CCTV Report
5bfeab30-8546-5182-ad77-d2a8f0024b72 | note | Testing Quantity Required (based from schedule qtys) - 1 per line
5a19d298-49c6-5d79-ab44-c505a060d77c | note | Verification Activity: Activity - S
3af3faf7-912c-5633-8f2a-a41081eb6280 | note | Verification Activity: By - PE
84c3283d-24bd-504e-b593-7adb2a662256 | section | SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
13049da8-dc5f-50e6-9653-61f13f53ec94 | checkpoint | 4.1.1 - Survey As-Builts
43405ff8-93a4-578f-8245-80b6a0ba30db | note | Detail - Quality Check on New Works based on the tolerances in RITS
75fa7eec-e69c-5510-a9fd-4d65f0dc461d | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
7e5788d2-50c9-52f4-bf02-4a7eda67d156 | note | Standard / Specification - PS-21.7.7
5fe67f93-427a-59b5-ae3e-31e8cfcf0324 | note | Verifying Document - Red pen markup only
91e56975-23b2-52d3-a796-4e4e6b9d9e16 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
7b449813-211a-5938-b86c-3592cb4fb49a | note | Verification Activity: Activity - H
84f4cb19-b321-5af5-81b4-05813f1cc00d | note | Verification Activity: By - SE
963d04ed-09a1-5cc8-8265-74053e53279a | checklist | Ω (DEPRECATED) DN1210-008 ITP Noisewall 1 Rev 1 | itp | DN1210-008 ITP Noisewall 1 Rev 1
dc439d04-ad5e-5573-818f-c5c286b26df4 | section | SECTION 1 – PRE-CONSTRUCTION - MATERIAL, PERSONNEL & THIRD PARTY APPROVALS
5ba25caa-7a71-5139-8d6d-82357c289e49 | checkpoint | 1.1.1 - All metalwork to be approved by the engineer after fabrication
87bdd074-adec-58fd-a63c-e6d5e028f17e | note | Detail - Hot dip galvanised to standard hdg 900
98c69e01-29f3-53f2-8d6f-dd8f1cafe8dc | note | Acceptance / Conformance Criteria - Engineers Approval
b0b5c028-b263-5d86-8468-bed9858bf891 | note | Standard / Specification - PS 18.6.3
c6975e6d-cf42-58a9-96dc-90bbede7ad84 | note | Verifying Document - Visual inspection
071be570-ee9f-5a57-8e93-4b073c8c9c16 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
9bee1edf-40d8-5d3f-9a5d-4906f515415f | note | Verification Activity: Activity - HP
79f83faf-d5c7-5db3-9443-d9741f98c18e | note | Verification Activity: By - ENG
068dedb1-7fbd-5e00-a102-f41752de9010 | signoff | AUTHORITY HOLDPOINT
5b77c275-c7aa-5684-bd40-ba54d126d5bf | checkpoint | 1.1.2 - Hot rolled steel plates
2c47a6e9-a08e-5739-8f29-c7e8d3d02837 | note | Detail - All hot rolled steel sections shall be grade 300 complying with AS/NZS 3679: part 1
0dabdb54-74a7-54dd-ae40-de3ad20818e8 | note | Acceptance / Conformance Criteria - Grade 300 - AS/NZS 3679 Part 1
c76b6bca-e6f4-56fa-b7bb-d1453d9508b2 | note | Standard / Specification - PS 18.6.3
a46f0673-50f2-5848-9a66-351ee8402005 | note | Verifying Document - Supplier data sheet/ Mill certs
f71ae4d5-a759-5b64-b484-b80fad78b13a | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
80d4a903-5755-56af-b710-67b364d9d378 | note | Verification Activity: Activity - WP
b76c6864-d65d-5d6e-ba9b-54b00ad6a871 | note | Verification Activity: By - SE
993a2c97-80d3-5c56-8bb5-3a0cd3e51097 | checkpoint | 1.1.3 - Cold formed steel plates
d229f0f2-364a-5210-8086-72c1ce3bc2bc | note | Detail - All cold formed steel sections shall be grade 350lo complying with AS/NZS 1163
ba4d8304-9bcc-5de9-bb60-487d32752774 | note | Acceptance / Conformance Criteria - Grade 350 lo - AS/NZS 1163
c8b7045d-4e65-5004-b178-2faf397810e7 | note | Standard / Specification - PS 18.6.3
d30d11e5-c982-50e0-8b24-1c3de7152c7d | note | Verifying Document - Supplier data sheet / Mill certs
88a15989-7ae8-53ff-bf84-0175e84754d0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
7c299bb9-c2f8-54d8-a453-63e52980a80f | note | Verification Activity: Activity - WP
27df037d-7969-5882-879b-edce791de7c5 | note | Verification Activity: By - SE
db79d8f7-33e2-5c0e-862f-cefa1df6e8e5 | checkpoint | 1.1.4 - Mild Steel plates
a32c4834-9a78-539c-a5d5-7389c11d1b7d | note | Detail - All mild steel plate shall be hot rolled grade 350 complying with AS/NZS3678 (AS/NZS 3678-350)
7cd9c1c7-b21f-5d70-88cb-fbbfeaa4afd6 | note | Acceptance / Conformance Criteria - Grade 350 - AS/NZS 3678 (AS/NZS 3678-350)
d88a1b24-e1db-52f5-8aaa-7b85b0ae3e0f | note | Standard / Specification - PS 18.6.3
46e7120f-018f-5703-8219-bb5e63b2883d | note | Verifying Document - Supplier data sheet / Mill certs
a914bf70-1c36-5e5c-897c-04a8c79f8ab1 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
5f2399dc-817f-55ed-a292-855b1c106f85 | note | Verification Activity: Activity - WP
c77476e6-0463-533c-a9c8-eac096afef73 | note | Verification Activity: By - SE
4efd7e12-8765-507c-8da0-599a589078b5 | checkpoint | 1.1.5 - Round bar/rod
d5ef4756-3498-5ae0-9a8b-684db7d96f7f | note | Detail - To be grade 300 to AS/NZS 4671
fbc5f7fb-ae65-5167-953f-1701743687a8 | note | Acceptance / Conformance Criteria - Grade 300 - AS/NZS 4671
b4cd69d2-a6ba-5f3c-9b24-fa0050b144d7 | note | Standard / Specification - PS 18.6.3
c4b46c52-20a5-5af5-ac60-51251bebc3eb | note | Verifying Document - Supplier data sheet / Mill certs
e6e6c9c9-4a44-573d-9963-66dcef45d4e0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
4d58bc98-af07-5c06-b891-53233ccb29c2 | note | Verification Activity: Activity - WP
56ab8d87-e873-54cf-a6c1-e57300c7fd8d | note | Verification Activity: By - SE
1e999714-ded7-5714-ab23-b5f574a633d9 | checkpoint | 1.1.6 - Bolts and treaded rods
1e50e369-0191-5760-bd17-89eba5bce932 | note | Detail - All bolts and threaded rods shall be category 4.6/s to AS 1252
2d982ca6-dcd0-5c16-b12e-41a1e5c8cdf4 | note | Acceptance / Conformance Criteria - Category 4.6/s to AS 1252
844e284f-14e5-5b7f-be6d-cb835df0005b | note | Standard / Specification - PS 18.6.3
29b0a3f2-dd61-5e2b-97cc-688a22af3ac7 | note | Verifying Document - Supplier data sheet / Mill certs
791a825e-9754-565d-9548-7fc700f2c145 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
d3c70cf8-f765-5516-bc1b-8e0a2780853b | note | Verification Activity: Activity - WP
bfc76215-8b62-5cc8-8738-8c55a68ce26c | note | Verification Activity: By - SE
d47b70c7-d4f7-50b0-a088-bbd13a0577a5 | checkpoint | 1.1.7 - Rough or sharp edges
8239cc44-df77-5242-9d2a-53a51beb9e26 | note | Detail - All rough or sharp edges or protrusions to be buffed smooth
17f0a785-ff6a-5f0f-9d31-ed21bf94dabd | note | Acceptance / Conformance Criteria - All rough or sharp edges or protrusions to be buffed smooth
b5b71663-219b-5d9f-b957-16d39207e4cc | note | Standard / Specification - PS 18.6.3
cc58fa48-e238-53d1-85fc-bf562f0e3f01 | note | Verifying Document - Visual inspection
59159e4c-59a9-5256-99c1-d369a80f0b82 | note | Testing Quantity Required (based from schedule qtys) - During construction
14acb6ad-ba1b-5e05-8b3c-2c7e58085328 | note | Verification Activity: Activity - WP
730fa375-2c73-551a-be83-c3d2fc2ee5c9 | note | Verification Activity: By - SE
704a29d7-c4e9-5cfa-84e8-252fd7bf2eb1 | checkpoint | 1.1.8 - Epoxy Coating to the Steel column
da36ea66-3e4c-5373-8400-500b2eeccdc8 | note | Detail - High build epoxy paint all round the UC column concrete interface
4f50d82f-af3a-5dee-a5b8-897551e5b9f3 | note | Acceptance / Conformance Criteria - all columns must be coted with epoxy at steel and concrete interface
3831f71a-b15d-5fee-a9a9-57072adab45d | note | Standard / Specification - WSP-DR-STR-0306
3b331bb3-c95a-5cb7-93b2-40083c5e8e22 | note | Verifying Document - Visual inspection
c71ecc60-3158-574f-b678-6bc87e3f42be | note | Testing Quantity Required (based from schedule qtys) - During construction
e57e7e2d-40fe-5f23-b707-093f89a44736 | note | Verification Activity: Activity - WP
7b63766e-38d0-5caa-954f-4697e765b776 | note | Verification Activity: By - ENG
95a62a2d-dc41-5729-8c34-772c79c3554e | checkpoint | 1.1.9 - Butynol sheeting - membrane
5a887d98-a2d4-54ae-a390-0257dd636dcd | note | Detail - Butynol or any similar approved shall be used between timber and steel
2ca757a4-cbc8-566c-a551-e5db903dcfc1 | note | Acceptance / Conformance Criteria - Membrane seal
b6b16dcb-822a-55ae-88cc-938242b76771 | note | Standard / Specification - PS18.6.3
ef5fb293-1a54-57d4-96f0-4323475e14ee | note | Verifying Document - Supplier data sheet and Engineers approval
82673ede-b43f-50e3-bcde-fc08d9726de8 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
2a6cfa88-e388-5cd9-ac3a-21a9ef606b81 | note | Verification Activity: Activity - HP
345840de-24e7-571d-b77f-bf487038ee5b | note | Verification Activity: By - ENG
ba2ef6ed-92a6-53c7-bfe9-b134dba90eb7 | signoff | AUTHORITY HOLDPOINT
e6bb1c37-103d-54be-bbb4-bf36c50c5f77 | checkpoint | 1.2.1 - Timber
54251110-fb04-5634-804a-92c22b624288 | note | Detail - Timber shall be VS8 grade radiate pine complyng with NZS 3603 and graded to NZS 3631
fcd03198-8f9c-5850-84d0-b493cd0ba8d4 | note | Acceptance / Conformance Criteria - VS8 Grade radiate pine with a Timber strength - 11.7MPa
5e992fc1-b3d7-5182-9932-816b8f7679e4 | note | Standard / Specification - PS 18.6.3
c4f87a52-0519-5ae8-b336-5759aea2f92c | note | Verifying Document - Supplier data sheet
fa6a83af-5c9d-580d-a86b-e5a78110f7e3 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
a50d4d7b-7c36-5752-a447-950f2b4e1fb5 | note | Verification Activity: Activity - I
e1de97ba-ae1c-5ab1-918a-6404fe0c2bb2 | note | Verification Activity: By - SE
30369b36-252b-59e5-8453-1ef6cc725793 | checkpoint | 1.2.2 - Timber - in contact with the ground
5152ee6b-48c1-5452-b7f7-665c012b4671 | note | Detail - Round or rough sawn piles in contact with the ground to be H5
c3eeb317-ac30-5f95-9d7e-3101991d8efb | note | Acceptance / Conformance Criteria - H5
75f7dbe8-72b9-5f1a-b8f7-15826c932b2d | note | Standard / Specification - PS 18.6.3
bf956d8b-9861-5579-80f7-03b4bee0420a | note | Verifying Document - Supplier data sheet
23055f9c-ecab-5a59-a7fb-780233919e42 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6e964ee1-46bb-52ad-b717-a5218a6e0fdd | note | Verification Activity: Activity - I
f380da60-80b7-5056-9f3a-2277ffcf4687 | note | Verification Activity: By - SE
94a81899-257a-5ffe-8a11-73f210325de7 | checkpoint | 1.2.3 - Timber - not in contact wth the ground
43baedb1-f8dd-5799-ac13-68a41cd4a8ae | note | Detail - Rough sawn timber not in contact with the ground to be H3.2
cc284ec9-df83-5816-ad1e-e548ef3fd65a | note | Acceptance / Conformance Criteria - H3.2
8995acd9-333c-570a-aec6-e20765ea8fac | note | Standard / Specification - PS 18.6.3
7cc07edd-fd8c-54ae-9d41-96ce81f43ac9 | note | Verifying Document - Supplier data sheet
7544f38c-33b7-522c-846e-628837afbd0f | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
91921caa-8caf-5c2e-9d1c-53429a51783a | note | Verification Activity: Activity - I
51024bff-9929-505d-af6d-acbf42b96537 | note | Verification Activity: By - SE
ee29378b-32d7-5f42-aa47-1090de8ff24e | checkpoint | 1.2.4 - All timber components of noise wall
c2944171-e8da-5bd4-8444-bbb67bfefd09 | note | Detail - Timber treatment shall comply with requirements of the NZ Timber Preservation Council incorporating - MP 3640. All timber shall be branded to NZS3640:2003 and must be treated not less than 2 months prior to use.
6448cf6e-b977-5414-adad-2b8f783fe839 | note | Acceptance / Conformance Criteria - MP 3640 NZS3640:2003
00a5bf57-9093-5222-a8de-7d7dded3457f | note | Standard / Specification - PS 18.6.3
1e318461-45a4-58c1-8ed2-c2bcf92458f5 | note | Verifying Document - Supplier data sheet
8c1efafa-2b61-531e-8f1f-39397d4d62b1 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
a0d72391-9573-5058-a0eb-84b413e05e9b | note | Verification Activity: Activity - I
3f823901-11f9-5b7a-981a-3f0f4aac3691 | note | Verification Activity: By - SE
f9d62092-ddd4-595b-9974-ca2ed9af18d3 | checkpoint | 1.2.5 - All timber components of noise wall
0efa02f3-da79-5b77-bdd5-a4d5f22e1971 | note | Detail - Timber shall have a moisture content less than 18% at time of installation to avoid excessive shrinkage effects.
20c0394f-4abc-5d3b-8f4d-edef79533980 | note | Acceptance / Conformance Criteria - Timber shall have a moisture content less than 18% at time of installation to avoid excessive shrinkage effects.
2d87e160-dae4-5e64-b3a7-76c6a9977cb4 | note | Standard / Specification - PS 18.6.3
94f6326b-2489-5eb6-be61-4aa3bd13487b | note | Verifying Document - Supplier data sheet
307a1a62-bac2-522c-a99c-4cf8b742b1ba | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
6a315b29-999f-5814-ba87-a57841b3c4c0 | note | Verification Activity: Activity - I
bc525129-b4b8-5d43-885b-04861ce2640c | note | Verification Activity: By - SE
3272a837-e1fc-58a0-bc7d-7379bc60c516 | checkpoint | 1.2.6 - All timber components of noise wall
544ad440-b824-5da8-aee9-8bd16b5721e5 | note | Detail - Treat all cut surfaces with clear zinc naphthenate preservative and in accordance with NZ 3602.
f76dc74f-24e1-549f-88e4-1abf6be9aa7f | note | Acceptance / Conformance Criteria - Treat all cut surfaces with clear zinc naphthenate preservative and in accordance with NZ 3602.
37588d10-c423-59ed-961c-c956f7444c29 | note | Standard / Specification - PS 18.6.3
64c3846b-da7a-5d28-afc5-0c21935d4daf | note | Verifying Document - Supplier data sheet
d518a1e3-9870-5cfd-a733-66bea55e6cfc | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
eaf54b00-742e-551f-b9ec-5f73e8687585 | note | Verification Activity: Activity - I
911327c4-79d1-5baa-bb99-d9fb85bf6469 | note | Verification Activity: By - SE
f9dfbf52-7921-564c-a925-33cba059da58 | checkpoint | 1.2.7 - Galvanised bolts
2440ec0a-26dc-5d22-924a-c6e698d6f007 | note | Detail - All galvanised bolts in contact with H5 treated timber shall be protected using CP grease in pre-greased holes
855e0003-4cf5-5e72-8e20-f8b1614cf3e2 | note | Acceptance / Conformance Criteria - All galvanised bolts in contact with H5 treated timber shall be protected using CP grease in pre-greased holes
42f7b2c3-d6c9-51a6-8261-8b52eb60acaa | note | Standard / Specification - PS 18.6.3
e0a8034f-f8a9-5a0b-b2ba-c642ba4a4544 | note | Verifying Document - Supplier data sheet
3c2a2849-e465-5a3c-9b68-b756239e59e9 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
f4e95223-4a6a-5b04-8f80-6bfc0009a868 | note | Verification Activity: Activity - I
d4334259-f555-5639-a09f-63f567035a45 | note | Verification Activity: By - SE
e1936029-7894-51a0-a7be-3a1a2e755a8a | checkpoint | 1.3.1 - FH Nails
28d68371-a3d5-511d-b574-81b8c7782309 | note | Detail - General structural use 75mm x 3.15mm FH nails . All nails shall be flat headed, unless otherwise shown, hot dip galvanised and fully driven
db628c59-bf96-53a3-807a-f39fd18dcc9b | note | Acceptance / Conformance Criteria - 75mm x 3.15mm FH Nails
4a24bfb7-c4b1-5ca4-98da-eb87499c26ca | note | Standard / Specification - PS 18.6.3
05837ee9-a67a-5272-9bcb-f7894e309c17 | note | Verifying Document - Delivery dockets and supplier data sheet
fa89e629-1bca-55aa-aec2-dbd87af7df2f | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
82240e18-b2c3-525e-a2bd-727bb0d0d38b | note | Verification Activity: Activity - I
d179c9ba-17a7-5947-bae0-079338a7cc4e | note | Verification Activity: By - SE
92dc6277-2665-5d70-9e48-177822abec7e | checkpoint | 1.3.2 - Bolts
6fd1fc27-2e0a-5602-b948-507ecdba4eab | note | Detail - Bolts shall be M12 hot dip galvanised engineers bolts fitted with 50x50x5 galvanised square washers both ends. Washers for coach screws shall be provided in accordance with NZS 3604
672ea647-fc9d-597d-a6f1-13f399bfe296 | note | Acceptance / Conformance Criteria - M12 hot dipped, 50x50x5 galvanised square washers
f0c14c3d-8f7f-5a83-bc6c-760c84878fa1 | note | Standard / Specification - PS 18.6.3
aa565e89-d839-522b-9d92-689160284664 | note | Verifying Document - Delivery dockets and supplier data sheet
9ecbbaa8-0958-51a5-9143-d165d1ec9f6c | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
42240d1d-3fb6-54ad-979c-dcceb7e9c33c | note | Verification Activity: Activity - I
d49b33e6-b909-5d28-a95a-0e9dd644da3e | note | Verification Activity: By - SE
f6166390-0424-550a-b578-335017e863af | checkpoint | 1.3.3 - Bolts within 100mm of ground
ef0a452e-c447-559d-b720-ec3894f29512 | note | Detail - Bolts within 100mm of ground to be stainless steel.
910e16b5-6385-5c14-b82a-1a3eddeba3a0 | note | Acceptance / Conformance Criteria - Stainless steel bolts
aad17169-f7e8-5347-b07f-98395edf6661 | note | Standard / Specification - PS 18.6.3
126723f5-ecf6-5a58-a83c-f5b39d7d2534 | note | Verifying Document - Delivery dockets and supplier data sheet
4c1ffdfc-2a94-538b-909e-c3a8044cabe0 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
413b49f0-dcc7-5238-8eab-d5a8b84ec194 | note | Verification Activity: Activity - I
3581952e-8803-5645-a554-6a585406dae6 | note | Verification Activity: By - SE
52dad3df-5c5f-542a-9707-5e4361323e21 | checkpoint | 1.3.4 - Coach screws
057507f2-4ca3-53ed-b8f0-f91c2e0da906 | note | Detail - All screws shall be hot dip galvanised and screw fixings shall be pre-bored.
1172649a-ca70-5d69-8e0d-9831d8152c9f | note | Acceptance / Conformance Criteria - Hot dip galvanised
43aeca2a-3829-5bf7-9322-fe2d86805984 | note | Standard / Specification - PS 18.6.3
a00ac75c-241f-517d-b981-d91e3044bfad | note | Verifying Document - Delivery dockets and supplier data sheet
7d2e118d-6fb3-5f8f-a6c3-dfbb5789eab7 | note | Testing Quantity Required (based from schedule qtys) - Prior to construction
df201f03-523a-5c04-b873-1de4e77e82bc | note | Verification Activity: Activity - I
96482dff-afec-5c12-b89f-0f524336fc05 | note | Verification Activity: By - SE
868e15d2-a829-5664-9f4e-1c730798c2ea | section | SECTION 2 – CONSTRUCTION ACTIVITY
8abc6212-3111-540b-9738-78a20e86ed40 | checkpoint | 2.1.1 - Setting out of Noise wall 1 all Posts
db9796ec-3de3-5f3e-a2b1-b371b55d636e | note | Detail - Setting out to follow design coordinates and levels within tolerance as specified in PS 18.5.7 section (e).
53c8d121-406a-5754-9665-84e5ce60fddc | note | Acceptance / Conformance Criteria - Engineers Approval
1ac7c545-fb56-5f43-9e9d-71200baa4099 | note | Standard / Specification - PS 18.6.1
49eefdea-60f2-5a7e-9485-4e81f54dee3d | note | Verifying Document - Visual inspection
9b22254b-b8c5-5fe2-abd2-fa7d667abe0e | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
d1b4e7ef-1486-5850-8c93-780e3ff27f28 | note | Verification Activity: Activity - WP
d5b62a0e-ab48-51a2-a5ca-bac0bff62f81 | note | Verification Activity: By - ENG
ac86be99-18f9-57a8-bf7c-14f69d596955 | checkpoint | 2.1.2 - Geo Technical investigation on each post holes
45032e44-c37a-598f-82f4-efe6d77a54e1 | note | Detail - Holes are to be 400mm dia and 2.8m deep. Shear vane testing to be completed to a strength of 60kpa
89cde49d-cbed-5656-8b76-5995c7d79101 | note | Acceptance / Conformance Criteria - Shear vane strength of 60kpa
815a6b13-4eda-5a1c-a9bb-3617264cd253 | note | Standard / Specification - PS 18.6.2
754362a4-9655-5c9c-92cb-f40197172609 | note | Verifying Document - Shear vane test report/Visual inspection
f9620d0c-b2c0-56cb-bd18-a6a4a167c6e9 | note | Testing Quantity Required (based from schedule qtys) - Engineers Approval
c233521d-d38f-54bc-a9e0-72be1d3f9899 | note | Verification Activity: Activity - HP
4209a781-2ab3-588f-8d78-e9fa3287449d | note | Verification Activity: By - ENG
9e47e5c7-cb75-541e-a14f-4afa4b5d7a68 | signoff | AUTHORITY HOLDPOINT
2cdf9c15-2c63-5aac-9f2e-a940d4990caf | checkpoint | 2.1.3 - Noise wall footing concrete
139e9071-f02a-51c5-872c-60346393be5c | note | Detail - 17.5 MPA Concrete
9a2ac467-7a99-507c-88f3-8c9200f75b7b | note | Acceptance / Conformance Criteria - 28 days concrete strength test of 17.5MPA
01f3b2d3-71df-5c0e-a557-cebe048096f7 | note | Standard / Specification - PS 18.6.2
a31d14e4-0d82-51e2-8601-61322fbf976b | note | Verifying Document - Concrete Delivery Docket
324e5e6c-bff7-5126-a664-7c0f7209f2b4 | note | Testing Quantity Required (based from schedule qtys) - During Construction
3216a620-a366-5d1a-8ff3-dfedb315054d | note | Verification Activity: Activity - I
2d5f18ab-85ce-56a2-b39b-83bbed73787d | note | Verification Activity: By - SE
b0af36a8-2e1e-5d8c-8d3d-b3d850c71730 | checkpoint | 2.1.4 - Installing Wooden Railings
207f27c0-a0e6-587f-8899-c5cad0ebc6df | note | Detail - with sufficient embeddment of nails and connecting details as per drawings
b8c45349-31a7-5ed8-9b83-67be91a22764 | note | Acceptance / Conformance Criteria - Skew nails shall be installed as shown:
6543a4e4-ab92-5a54-b0b3-4b3930c38246 | note | Standard / Specification - PS 18.6.3
6487da79-9484-5263-a42b-99a80c9b5613 | note | Verifying Document - Noise wall Checksheet
5ef90dfc-9ed5-55fb-8406-0f069a808cc3 | note | Testing Quantity Required (based from schedule qtys) - During Construction
89875b75-8f03-53ee-8339-893c9791911f | note | Verification Activity: Activity - I
a98fea2e-6479-5811-8272-80c2c4a34be4 | note | Verification Activity: By - SE
47886ec3-63d6-5e34-814f-8a266d50043d | section | SECTION 3 – POST CONSTRUCTION (HANDOVER)
49e56452-d262-55bb-8e2e-45db3938f81d | checkpoint | 3.1 - As-builts
790edb2b-229c-5e7c-980d-fe019c0d306d | note | Detail - As-Built records and drawings shall accurately record the layout and extents of all the work including all of the cuts and fills, monitoring instrumentation, ground improvements, and locations of foundation / subsurface drainage systems and their outlets.
4915cc5a-a225-518b-a3da-ffe8886dca97 | note | Acceptance / Conformance Criteria - All changes to design need to be captured on the noise wall drawing set
71b63e81-f275-5591-812b-c0601b22bae6 | note | Standard / Specification -
f046623b-db5a-53f8-bd6b-d4e4b89d9e10 | note | Verifying Document - Redpen Markup
9cd59d86-5195-5dd3-a4f3-42f6def3fa28 | note | Testing Quantity Required (based from schedule qtys) - During construction and after finishing
ffc5e08f-200b-5cd0-ab09-336f592f225b | note | Verification Activity: Activity - WP
a1abcf24-c909-5eb5-a2d0-6730301d1972 | note | Verification Activity: By - SE
df22f407-2ccb-4a33-8ce5-c7f06a5f2987 | checklist | Ω (DEPRECATED) DN1210-012 ITP Utilities Rev 1 |  | DN1210-012 ITP Utilities Rev 1
8e916c0c-5850-4ca0-aad3-d295c9619403 | section | 1. PRE-CONSTRUCTION (P&G / ESTABLISHMENT) - 1.1 GENERAL
4a66bb89-4063-48d7-ba64-2c8f3122a315 | checkpoint | 1.1.1 - Trench Profile
0bcb6d66-7e1e-522d-ba87-be9b0db6f981 | note | Detail - Tolerance of +/- 100 mm of the planned horizontal alignment and the maximum deviation shall be 1 in 20 in both the horizontal and vertical planes.
67dc9f3e-9171-50cf-b1b6-87fec1d0c3a6 | note | Acceptance / Conformance Criteria - Survey Set out
dd78f3e2-e03d-5227-a645-a1acee11c522 | note | Standard / Specification - PS 25.13.2 a (1)
40ba78fc-9e73-52b2-a54a-f9029e66caf3 | note | Verifying Document - Survey Data
20d912dd-83fb-52e2-b2fc-f85bf0271bb6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
9abec1dd-c417-52ff-a7dd-f5c2e029111e | note | Verification Activity - H
f2dfcbc7-c870-5849-aeca-006cd2d2d0c7 | note | By - ENG
d7f561a4-3e32-4b1a-9982-23753a93830f | signoff | AUTHORITY HOLDPOINT
25425128-8231-4e6d-aa60-7136a71593a6 | checkpoint | 1.1.2 - Underground Services
283dd870-0601-52e4-855c-ca1a319e14fe | note | Detail - Pothole all services within traffic management prior to commencement of trenching. Accurately record the location and reduced level of each service and forward Engineer.
e9093ccf-6692-5b86-aa60-478a2d8764e6 | note | Acceptance / Conformance Criteria - Survey Data/Existing utilities Drawings
c178e828-e156-5366-98fb-7c2b3ee5879b | note | Standard / Specification - Appendix V
afa0302e-7ad5-5f89-980f-717933ab154f | note | Verifying Document - Survey Data
999d0726-1342-5992-bf08-3221e0b8ecb8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
5195c12a-66bf-5ab3-be01-01228c27e530 | note | Verification Activity - H
917c7757-35c5-53a4-b610-1d5f602e77cd | note | By - PE/SE
af7a8933-9e5a-48a0-a05a-129fd15c5cc9 | signoff | AUTHORITY HOLDPOINT
39a6b05e-30a2-4740-ac86-41f6215e698b | section | 2. MATERIAL, PERSONNEL & THIRD PARTY APPROVAL - 2.1 MATERIAL TESTING
486cc648-29a7-46e8-87c0-82a4976fb1ca | checkpoint | 2.1.1 - Bedding and Overlay Material: Clean Imported Sand or SAP 7
4c6a5b85-12dc-57af-9f84-eb844b1a72b4 | note | Detail - Material grading:PSD
81d99318-3953-50b0-87a3-553626258b67 | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
842b2c18-b12a-55f1-ac5d-21652cdca29f | note | Standard / Specification - PS 25.13.2 g) & h)
110948ae-0e2c-51af-a67d-1197efab1263 | note | Verifying Document - Delivery Dockets/Material Certification
6d35a092-9e71-53f3-8366-f69dd71548b1 | note | Testing Quantity Required (based from schedule qtys) - NA
5b73eeea-f3c1-562c-addc-9e13da30056b | note | Verification Activity - HP
9a700353-5f28-57db-a746-62af3930586e | note | By - ENG
b1e0dc8e-de0b-4e74-a9aa-38a5ebc23b8a | signoff | AUTHORITY HOLDPOINT
44d83bac-76f3-42c4-8c5e-39b2257c0cec | checkpoint | 2.1.2 - Materials: GAP65-Backfill Material
23b3c69e-61c3-5c8d-b7c9-27e3a083e564 | note | Detail - Material grading:PSD
69982c10-640a-5c1d-b2c2-6349b69f27c9 | note | Acceptance / Conformance Criteria - Stockpile size over 4000m3 PS- 16.5.11 for GAP65
0d2e1224-6bdf-544e-8baa-647e3abc8c29 | note | Standard / Specification - PS-21.7.2 Table 21.9
89926f4d-431c-5a36-a4e7-5be287cc0f9a | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
538f58d9-8e96-5832-bd96-e69312922f9f | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 1000m3
582b6634-6b50-520c-8e89-1d5f35c4e7b7 | note | Verification Activity - HP
9569ed76-8c8e-598b-ac62-26995c7de055 | note | By - ENG
63d81330-269f-4298-9075-db67765b857e | signoff | AUTHORITY HOLDPOINT
0b6e92e6-b517-4dab-b57d-d9abacf69d0b | checkpoint | 2.1.3 - Materials: GAP65-Backfill Material
dead2c3d-8425-5ced-9f1d-c49fef0cedf6 | note | Detail - Weathering index:
10ac7968-b8ea-5b19-8b95-0f9febb656a2 | note | Acceptance / Conformance Criteria - AA to CA
f554ac44-d467-5ccc-847c-8f1390459f01 | note | Standard / Specification - PS-21.7.2 Table 21.9
987d8f4e-3f75-5e58-83e8-8420be2644fd | note | Verifying Document - Lab Test Report NZS 4407.3.11
8b7fa9c2-a910-5cc0-bdd6-f7af3e21259d | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
89b237ec-4d43-5544-857e-dccdc5cffbda | note | Verification Activity - HP
5eaf02df-d9ca-5f5a-8fa5-c343b8ec9cfc | note | By - ENG
464c66bc-6468-4260-b978-70b3310b1037 | signoff | AUTHORITY HOLDPOINT
09ef89c4-2afa-4d83-9697-447334c2113f | checkpoint | 2.1.4 - Materials: GAP65-Backfill Material
67aaf769-fcec-552c-9ed7-bf1a39112466 | note | Detail - Crushing Resistance
ffc49956-2e6a-5dd3-a304-40ece59ef931 | note | Acceptance / Conformance Criteria - >100KN
f76a0622-fd6e-5455-847e-d508fcacedbc | note | Standard / Specification - PS-21.7.2 Table 21.9
1a5aa289-6eaf-59a0-9437-a111b759d478 | note | Verifying Document - Lab Test Report NZS 4407.3.10
92ed5aba-43ea-56b8-a774-1a2293235f5c | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
b14c597e-8b01-5272-8ddb-301b10feb6bb | note | Verification Activity - HP
b5d26f2d-714e-521b-9a61-469d0abb98d8 | note | By - ENG
006c000e-da74-49b5-97af-9a1160001773 | signoff | AUTHORITY HOLDPOINT
0e80def9-0026-4998-a4ca-cde2b81a47e9 | checkpoint | 2.1.5 - Materials Approvals
a56af989-ca4e-5c53-a433-cd450e47f5e5 | note | Detail - All works and materials are to comply with the National Code of Practice for Utilities Operators' Access to Transport Corridors, and Individual Utility Providers Requirements
8895bb7e-c427-5901-a5aa-07751a808d3a | note | Acceptance / Conformance Criteria - Prior to Commencement and throughout construction
fdbe7567-dbbc-519b-80f5-59a9d0d58c39 | note | Standard / Specification - Project Specifications
5c389606-b39f-5d8e-8d26-163bf0f5146f | note | Verifying Document - Utilities Providers Approval/Material Certification /Delivery Dockets
3ddf2253-d8cc-5de2-81a4-28ced242fc94 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
ef51aec0-3acf-5b8c-814d-5627875e5648 | note | Verification Activity - H
1af29b68-624c-5b9b-b62a-c702c9fce0fe | note | By - SE
4ece6099-0f01-4b16-bde4-65c5945709fa | signoff | AUTHORITY HOLDPOINT
83f97cbe-b43e-4cbc-bc3b-729ae9f6c33e | section | 2.2 MATERIAL DELIVERY
ee48925a-b035-46ef-97b4-087f4ef5eabb | checkpoint | 2.2.1 - Pipe and fittings. Ducts
7db8345a-ba3e-58a1-ae6b-4d5f1a4d4028 | note | Detail - Duct Pipes shall be of the size, material and class nominated in Drawings. Ducts shall be high impact uPVC or High-Density Polyethylene (HDPE). Duct colours shall be to local authorities requirements. Duct colours for the different Utility Structures must be in accordance with the guidelines.
333fbb3f-f90e-5faa-ae0e-3ca9b54ed4ef | note | Acceptance / Conformance Criteria - Comply with Project Specifications
625baae0-854c-5ffd-9828-2611affb4ecb | note | Standard / Specification - PS 25.13.6 b)
51f875eb-7058-5199-9123-ccc9ee657e66 | note | Verifying Document - Delivery Dockets/Material Certification
497e2f66-3f6d-5599-b0d5-be28065d2a77 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5aa16fdc-5187-5a70-a7e8-62d24fd18fa9 | note | Verification Activity - H
78bc25dd-85bf-5421-be72-73f158f43e7c | note | By - SE
f97a8dfd-6853-5b80-b674-22bd03bdd93b | note | Comments / Closeout Details - Duct details will be instructed by service providers.
30b72118-4b36-4dd5-91c9-00414bc65ae7 | signoff | AUTHORITY HOLDPOINT
95fc4281-439d-4b9a-bfa7-e0f188d3b25a | checkpoint | 2.2.2 - Bedding material
349f055c-40d5-51ac-b330-812b78a35726 | note | Detail - Clean Imported Sand or SAP 7
52d5971e-85d0-5bd6-a4bf-6ae513e08feb | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
ac7553e4-090f-598d-93fd-a88a790432ad | note | Standard / Specification - PS 25.13.2 g) & h) & 25.13.7 b) ii
c7246019-cc11-595a-a5c5-ed534863d820 | note | Verifying Document - Delivery Dockets/Material Certification
da3558cd-d367-5395-806d-f6d08fba0c9f | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
13520fea-8f9a-58bd-94f0-b9d17b4cee98 | note | Verification Activity - H
bd332cbf-5d6b-5170-a45e-98515475dc80 | note | By - SE
e29ceea3-5f67-41be-9f64-7ba1ea194895 | signoff | AUTHORITY HOLDPOINT
d5398cc0-f040-422b-8e23-1339dfa1e2a1 | checkpoint | 2.2.3 - Backfill Material
775a8ca9-30b0-5457-92f9-21908aa5712d | note | Detail - Under roads, driveways and footpath - refer to pavement section for appropriate materials and layer thickness. Under berm or grass areas - site Won materials to be approved by Engineer or GAP65 to be used if site material does not meet Specs
b2e368c6-bc23-5da4-a48d-978978955761 | note | Acceptance / Conformance Criteria - Comply with Project Specifications
dc270cb9-cd17-59bd-803a-59e13c5cd7f6 | note | Standard / Specification - PS 25.13.2 h) i to iii & 25.13.4 a)
05583998-e4ea-505c-906c-b3681ae0bfd5 | note | Verifying Document - Delivery Dockets/Lab Test reports
b3465e16-1c11-5103-b922-723dc70f41a1 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
1524ee9f-d13e-5e50-87c6-a5e81f8459d0 | note | Verification Activity - H
9ba41559-439e-5d84-8fd8-cd22bd752862 | note | By - SE
7245ad1a-3400-43c7-aa67-5b628124c14c | signoff | AUTHORITY HOLDPOINT
a4d7cdb7-b059-4497-a17f-f892ba5d8756 | checkpoint | 2.2.4 - Pits Covers
b54dfeb9-8272-5c6a-9c91-dbe596f03cfd | note | Detail - Jointing and pulling pits shall have slip resistant surfaces.
6e129f47-6b34-5471-a0c8-52ff04f7831c | note | Acceptance / Conformance Criteria - Class A-10Kn. Class B- 80Kn. Class C- 150Kn. Class D-120KN.
f10b6ad6-3c89-5058-ba2a-5ab374cde17a | note | Standard / Specification - PS 25.13.6 c) AS/NZS 3661-1- 1993.
febba2d3-986d-5831-b1b0-a89896aa2976 | note | Verifying Document - Material Certifications. Delivery Dockets
8632adbf-8bac-5027-840e-de9d33e4f89b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
b523dd59-d9ee-5824-bcb7-d9730aa34ecf | note | Verification Activity - H
3c22d34c-297b-55df-9dc8-1e84a24caef9 | note | By - SE
12320b3f-a7f1-48e9-acfe-43a50c1746ea | signoff | AUTHORITY HOLDPOINT
2e80cf9e-cce2-4de5-a526-19b5f0b1c990 | section | 3. CONSTRUCTION ACTIVITY - 3.1
4473bcd7-a7bd-4e0a-b8c6-5007ed250edc | checkpoint | 3.1.1 - Trench Excavation
881014cb-a527-53b7-bee5-f8672fe67d26 | note | Detail - To be excavated to within a tolerance. Not more than 100 metres of trench associated with each site shall remain open at one time.
3e77300b-24e3-57d9-8d0c-54d09709df76 | note | Acceptance / Conformance Criteria - #ERROR!
12365ca8-56e6-5f1a-acee-ef8499fd5229 | note | Standard / Specification - PS 25.13.2 a) i
e5d1fb7e-67ac-59a5-9234-fe1d48f36ff3 | note | Verifying Document - Survey
39daa345-e591-50a6-9823-ea6a4c1e5c31 | note | Testing Quantity Required (based from schedule qtys) - Every time
6b035129-a403-50e6-a124-eafc4b6f86b9 | note | Verification Activity - M
b8e83467-db66-5745-9ff7-de536dd190a8 | note | By - SE
c560f64e-3631-49b4-b19d-a3becd6f68a3 | checkpoint | 3.1.2 - Unsuitable Materials
788da501-45e1-5204-b133-312faf493b0b | note | Detail - All confirmed unsuitable material shall be excavated down to suitable materials.
3b5a9fdc-7571-5cb9-8c38-a2295f4015fa | note | Acceptance / Conformance Criteria - Dig Down to Get Suitable Materials or get Engineers Approval.
8d8e26ee-a00d-5e92-ad99-5ebf580c87e6 | note | Standard / Specification - PS 25.13.2 b) ii
a32f42d3-0de8-5a1a-a4e0-0f297dd3fd71 | note | Verifying Document - Visual
eacc48f2-a624-5251-8847-87e6cddcb3cb | note | Testing Quantity Required (based from schedule qtys) - Every time
9d2893a1-8ed0-54ea-a3ad-ea1451cc7677 | note | Verification Activity - M
50c89cc8-28e1-5b9a-8865-40337e15e174 | note | By - SE
4a681e24-b46a-4441-9bd6-7e42252ebb01 | checkpoint | 3.1.3 - Foundation Compliance
9f3f9957-5265-56a7-8e28-baf2e6f1f334 | note | Detail - It shall be de-watered prior to installation of bedding material. If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
b4f5bf4b-5651-5370-9694-0525360b32f1 | note | Acceptance / Conformance Criteria - 50mm granular layer shall be laid and compacted before the bedding layer is laid.
70967d19-82ff-5029-93ac-e78b1e927194 | note | Standard / Specification - PS 25.13.2 c) and g)
bb29f6e5-6443-5910-892c-ab0fdd680881 | note | Verifying Document - Visual Inspection
d7b30555-ed23-54f5-971d-8f7663e42d70 | note | Testing Quantity Required (based from schedule qtys) - Every time
7f197952-ec14-51dd-a602-b43e97854998 | note | Verification Activity - M
f2e6e66d-882f-50c4-8a0e-428f0e065146 | note | By - SE
49179d62-20cd-451d-9cc5-4bdc9f49dc68 | checkpoint | 3.1.4 - Bedding
8614c5cc-5665-5fa3-ab79-3f8940785aa5 | note | Detail - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
0736aece-5d03-503d-8bd2-dc15e71dfe33 | note | Acceptance / Conformance Criteria - Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
119d2e5e-a84d-5440-9563-82cc8c9de3ac | note | Standard / Specification - PS 25.13.2 g)
f566dbf0-0c84-5db8-aa23-db97f0e0357e | note | Verifying Document - Visual Inspection
95c8247d-bef3-517d-afe5-71c62c023bcb | note | Testing Quantity Required (based from schedule qtys) - Every time
cf88f922-c00b-5c77-94ae-58ea7117c49b | note | Verification Activity - M
7af9af8b-6269-5b6b-9749-5e37f31ca339 | note | By - SE
78830cf9-10a2-4c5e-8550-200be233c777 | checkpoint | 3.1.5 - Bedding (Encased in concrete)
e2a882fc-91f0-5b73-ac67-4727ea84b5b1 | note | Detail - Concrete Bedding to be placed. Compressive strength of concrete used no less than 20MPa
e92735c5-112e-5f6a-ab41-56137c2c3ed8 | note | Acceptance / Conformance Criteria - 50mm
c925fb4c-df71-59d9-8612-f84c6aee1fad | note | Standard / Specification - PS 25.13.7 c)
aa502856-7f55-501a-8b7a-1cc391135779 | note | Verifying Document - Visual Inspection
15aa5f42-8a9c-5efd-8d93-0ae20c77a890 | note | Testing Quantity Required (based from schedule qtys) - Every time
99a33773-5ba8-5074-9c2e-001402773f08 | note | Verification Activity - M
b3c964ab-9694-5169-83b2-96437b72a933 | note | By - SE
dfc31b15-66cf-447e-b61f-2a1b0891b1c2 | checkpoint | 3.1.6 - Installation of Ducts
5b79e591-f8e5-5827-adaa-be34a18a3b89 | note | Detail - If more than 2 ducts are being placed.
a223bcd1-0b1c-5e32-beba-bb2d6eb87ff5 | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
deeb4f1c-8275-5660-ad84-a68effb8da42 | note | Standard / Specification - PS 25.13.7 b) iii
d86431aa-c70a-50be-a1cf-a63445223e1f | note | Verifying Document - Visual Inspection
24b5f92a-0d49-5a68-85cd-e4c7a023a435 | note | Testing Quantity Required (based from schedule qtys) - Everytime
4d7275e2-defa-5308-9cdc-0c13ffff8e33 | note | Verification Activity - M
4c27abcb-e832-5ed4-8489-e71afe910f15 | note | By - SE
a05dd518-a7e7-4a26-9f83-a8f2a44879cd | checkpoint | 3.1.7 - Draw Wires
5edb7e75-29a5-5246-b153-3b8dadcbedb7 | note | Detail - A draw wire shall be installed in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting.
9d659fb7-8cb7-5a1b-be14-7d781f814ada | note | Acceptance / Conformance Criteria - Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load. ≥20 years design life. The ends of draw wires shall be made fast within the pits and be secured to the duct plugs.
5c218fd5-e8d2-540a-9a00-2af658da7a07 | note | Standard / Specification - PS 25.13.7 e) ii to iv
f066a145-aaea-5c8d-a3ab-5f5869ec9dda | note | Verifying Document - Visual Inspection
8f57c5b6-de05-5c56-a867-4cffa95efeb7 | note | Testing Quantity Required (based from schedule qtys) - Every time
752d02da-2b6f-5438-b36b-7effcef8df65 | note | Verification Activity - M
d77a631e-2c4a-503f-aae3-306c4c26277e | note | By - SE
9d07cbba-54d9-488f-aaaa-b8959d513f76 | checkpoint | 3.1.8 - Caps
1bfdfd82-7fe6-5e68-9de7-b048819822ff | note | Detail - All duct ends shall be capped
ae5add1e-5d83-53f5-8d27-724134035025 | note | Acceptance / Conformance Criteria - Capped ducts
a3d7f628-012e-5ea4-b7c4-6f7f0f8c09e4 | note | Standard / Specification - PS 25.13.7 e) v
1b0dc8a4-1927-5f71-b1f5-72771fe7de73 | note | Verifying Document - Visual Inspection
387d27f1-087e-5ca4-aeaf-1624f5a7c315 | note | Testing Quantity Required (based from schedule qtys) - Every time
393cf3ed-7340-5bb4-9068-e6e079e4f5c2 | note | Verification Activity - M
57c7c6ec-efd8-5ea6-bda5-8e472b70ed9f | note | By - SE
b17ea8f5-9cdb-4403-a4d8-4c5f65d3300c | checkpoint | 3.1.9 - Warning Tape
fffcaef5-8628-5f0b-974b-849c726c921d | note | Detail - Warning tape to be placed above services.
51439d3b-16f0-5217-8a6f-2a24ba22fa89 | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the duct
e9c43411-659c-5c77-b569-388644d1a8ed | note | Standard / Specification - PS 25.13.7 b) iii & f)
fe08ade8-e822-5587-8394-f5dcc7688f8f | note | Verifying Document - Visual Inspection
00f192cc-e9dd-52d7-a66c-f6a410d5c154 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
66839ed7-44f6-50fe-a63f-4fcd43402bea | note | Verification Activity - M
5924d14b-7652-5653-ab92-1041568205ed | note | By - SE
e306fc1c-d395-46d7-a477-4d04ef77d232 | checkpoint | 3.1.10 - Overlay
c96c786d-a3ac-538f-bd2f-f7a7a9396209 | note | Detail - Clean Imported Sand or SAP 7 to be placed and compacted
bc7ad0de-793b-56a0-b539-d517e3b9bc52 | note | Acceptance / Conformance Criteria - 100mm thick Clean Imported Sand or SAP 7
a891bdad-70a0-52b3-aacc-ffe42aceab7b | note | Standard / Specification - PS 25.13.7 b) ii
1dd21f08-8d27-5bfb-b9e8-6a9f25e00417 | note | Verifying Document - Visual Inspection
127845bd-db3a-5def-b2b7-0a3acf4b4686 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
d556104c-2e88-5f64-9ae2-9701f3e1b8a3 | note | Verification Activity - M
b9d5c2fd-2a2a-5863-8989-b22e6624b3e7 | note | By - SE
3f3429b5-7132-4adb-b746-c9a7683a7539 | checkpoint | 3.1.11 - Overlay (Concrete Encased Ducts)
1f4429d8-f8a2-5bac-a86d-0813b9fde853 | note | Detail - Overlay and surroundings to be placed with concrete.
0b70a8f8-2690-5c27-8c4c-3c4c4fd010c2 | note | Acceptance / Conformance Criteria - 100mm thick on top of Ducts 50mm thick side of the Ducts
f9675d8c-79e1-56da-a27d-b43646e236b3 | note | Standard / Specification - PS 25.13.7 c)
010b256a-1588-58ba-9c39-62df9f4f7179 | note | Verifying Document - Visual Inspection
b34dbc84-d497-5c86-b2ce-8799a8d0f168 | note | Testing Quantity Required (based from schedule qtys) - Every time
d597156a-ed6b-5674-85c6-119be7aa2d64 | note | Verification Activity - M
236de8df-23be-5469-b74e-c361c55f82d8 | note | By - SE
0bae926a-9ce6-4858-9d51-9b2f9caa194c | checkpoint | 3.1.12 - Overlay Testing (Concrete Encased)
35e54c37-e0b1-598a-be0e-b1e2bb10136f | note | Detail - Placed Concrete needs to meet the strength Criteria
b074a358-5034-527a-bf77-2f7fbd297b7a | note | Acceptance / Conformance Criteria - >20 MPA
fa29de66-7375-50c6-8352-5c130ce9b7b3 | note | Standard / Specification - PS 25.13.7 c)
b0012925-f4cc-5a23-b915-ab5034f37dbe | note | Verifying Document - Concrete Dockets
91ed986f-a827-54fe-9a6b-7600723d8aa7 | note | Testing Quantity Required (based from schedule qtys) - Every time
9aacd20f-1f0f-508c-b1b7-468d26f1adbc | note | Verification Activity - H
90a5508c-f605-5494-9626-9395b1c0b5a6 | note | By - SE
0491c173-2aab-4592-86c2-67fcbec243f9 | signoff | AUTHORITY HOLDPOINT
5b6c2158-a99a-4448-ab3e-92552e8438d9 | checkpoint | 3.1.13 - Backfill
5bf88ea3-a40c-5c85-9bc5-bd9bc4a1e4e6 | note | Detail - GAP65 to be used if site material is not approved. NDM Testing to be carried out.
d007f31b-e980-5f51-b330-b26ba3ad43ae | note | Acceptance / Conformance Criteria - NDM Test every 250mm compacted layer Min 92% compaction rate and Average of 95%.
d72fe4f3-f5d8-5c87-ba13-19390696dae7 | note | Standard / Specification - PS 25.13.10 a) modified
b5333357-30a1-5679-9e39-f6a426589629 | note | Verifying Document - Lab report.
053515aa-9b3b-50c0-bfb4-56f808ca9c52 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
682f58e3-a6cd-56d3-ae35-8208fb6bbe45 | note | Verification Activity - H
3e64b478-e791-5aab-9131-020ba8bddd83 | note | By - SE
f4cf8649-25a9-4847-814e-28f6d264bf5b | signoff | AUTHORITY HOLDPOINT
aee89273-de10-42e4-89e7-889fa4ef10d3 | checkpoint | 3.1.14 - Pit Installation Location
78c4648b-49e0-5f28-8583-31e1f07bcca5 | note | Detail - Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid .
bfb37dbb-602a-54ce-865a-5f9bc9a9edc0 | note | Acceptance / Conformance Criteria - Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas. When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side. When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side.
1835a7c4-faa8-5498-b21a-52a635aa2845 | note | Standard / Specification - PS 25.13.8 a)
0708013d-51a8-535c-bd10-3d6f229329d2 | note | Verifying Document - Visual Inspection
950eab39-7f6f-598c-b4bc-b438a93cd9a9 | note | Testing Quantity Required (based from schedule qtys) - Every time
7c294134-4f12-5c05-a658-a9c7c627ad90 | note | Verification Activity - H
3f51bcd6-f532-5373-99ff-edace48712db | note | By - SE
b17ed789-fce9-5f0b-af6a-f65804704759 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
b30154a2-27cf-4399-9ebd-8961bb518b47 | signoff | AUTHORITY HOLDPOINT
4fede5a1-b426-4107-93fe-fbd3a4824ffd | checkpoint | 3.1.15 - Pit Installation Bedding
4ba50b52-7982-5304-a05b-b5ece97d1dda | note | Detail - Bedding with 150mm compacted GAP20 covered with 20mm compacted sand
f714ef28-6d1a-5fe8-b6e0-c8594a9f683b | note | Acceptance / Conformance Criteria - 150mm GAP20 covered with 20mm Sand
88a7d06c-e1cd-5f91-b95c-78a49a4d9b81 | note | Standard / Specification - PS 25.13.8 d)
f3588442-3583-5377-886f-1334bf1a0099 | note | Verifying Document - Visual Inspection
4a69ed86-2acf-5fb1-ba3b-a28f9a65b3be | note | Testing Quantity Required (based from schedule qtys) - Every time
9f492a93-7b7f-5b2c-bb98-924386c86df8 | note | Verification Activity - H
a4bd4db7-0e1e-51c1-b511-0cf4fb01e48f | note | By - SE
cdd9bd87-4c5e-595c-bae4-1b37f5494cab | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
0bd6e6a0-05f2-41ed-8cf5-802339320a6a | signoff | AUTHORITY HOLDPOINT
fe4a52eb-50ec-46b2-829a-261874d7888e | checkpoint | 3.1.16 - Pit Installation Backfilling
7d489dc7-5bbc-5fb4-9b31-a0f8163f708e | note | Detail - Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts.
500e8173-6802-5b17-a562-f5da50056f90 | note | Acceptance / Conformance Criteria - Min 92% compaction rate and Average of 95%.
ef7d94e5-4ee1-5d47-89e9-4f90d2138b3b | note | Standard / Specification - PS 25.13.10 a) modified
3e39b019-1e19-5ace-9f61-521efd6d31db | note | Verifying Document - Visual Inspection
72261735-3e57-5fe8-98e5-1f9fe9c01b44 | note | Testing Quantity Required (based from schedule qtys) - Every time
b747e77b-8f12-5546-96fd-5bdbf812d01f | note | Verification Activity - H
301bcfe1-402b-5b92-bc23-86c8a3fb4796 | note | By - SE
effe1658-db19-571c-b1eb-3597f1a6ecb6 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
81bc6170-8c9c-45f0-b620-12e1089e96ca | signoff | AUTHORITY HOLDPOINT
a1333581-120a-45d8-9b00-bb9c191658e9 | checkpoint | 3.1.17 - Pit Installation Clean up
cea66dc3-485e-5822-8e9f-c030703f0300 | note | Detail - Clean out all pit after completion of the work
ba3186df-c924-5b82-ac04-b2f5eae40ea4 | note | Acceptance / Conformance Criteria - Pit are free of dirty, mud,water and foreign materials
4a67d1d0-2cf3-5de9-aca4-16a4e0882ed1 | note | Standard / Specification - PS 25.13.8 e)
42dd3885-0376-5ec5-9b6d-c0db556cf49d | note | Verifying Document - Visual Inspection
bcdb6a29-93e7-5635-ac42-4cf1cfdf82ef | note | Testing Quantity Required (based from schedule qtys) - Every time
01606bd5-cb4b-5683-ba2d-65dbe816a496 | note | Verification Activity - M
c7db4af7-46f8-560c-8b92-e1d42d0b4448 | note | By - SE
4b3f379c-f817-5f86-b89e-9105a8b52a80 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator will clean the pit.
c508a466-171c-4f79-875c-c23e6a410c2f | checkpoint | 3.1.18 - Survey As Built
f986c5ac-7748-5e6b-b32b-c2a181dade03 | note | Detail - As Built every ducts joint before backfill
f9fbcc29-98d5-562e-84e9-57d1f7357dcf | note | Acceptance / Conformance Criteria - Completed as per drawings
108777ac-97dd-5670-b2fd-aa1ebb5ff775 | note | Standard / Specification - Standard Practise
c091fbf0-ef67-52e4-a28d-f14313c9f7ef | note | Verifying Document - Survey
449f69b7-8db5-5180-9127-5cd276569e69 | note | Testing Quantity Required (based from schedule qtys) - on going
0542d6c1-82c9-55fd-9307-73923cbeb027 | note | By - PE
8684bf06-73a7-4869-a78a-feab8acbd2f0 | section | 4. POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - 4.1 AS-BUILTS
2af294bc-bf87-484b-989f-db926cf70510 | checkpoint | 4.1.1 - Survey As-Builts
53cf4a25-16e2-5051-b5db-eb5ec3759817 | note | Detail - Quality Check on New Works based on the tolerances in RITS
83de8240-0fb0-5adb-8cdb-1750f0103661 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
b9ffad88-9cb4-57f8-b1b9-5dedfdde3f02 | note | Standard / Specification - PS-21.7.7
bbed9c01-fa35-530b-ab40-200efdd164d8 | note | Verifying Document - Red pen markup only
313a5680-5efb-513d-9f2e-dcdbdfe71f03 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
e4c858d1-5129-5530-baed-d20d31d20be2 | note | Verification Activity - H
9394f156-0b56-5a84-8b84-7ffc7787352e | note | By - SE
a072cf05-9802-47ac-9772-7070c5ba6526 | signoff | AUTHORITY HOLDPOINT
2e511a95-c3d3-59b6-a074-0c7fb5c1986b | checklist | Ω (DEPRECATED) DN1210-016 ITP Fencing Rev 1 | itp | DN1210-016 ITP Fencing Rev 1
9dbf9507-d5c1-5f76-b0e9-632a875b7d7c | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
61faafb8-e067-5299-84f0-3fd60960e68e | checkpoint | 1.1.1 - Extent of Line Setout
2d49439a-3db5-5e85-9b0b-ca24f4b79ac2 | note | Detail - Ensure line and level of Fences has been marked out and agreed with Engineer in accordance with fence drawings.
29900d8c-108b-5bcb-ba90-3d2400fb1787 | note | Acceptance / Conformance Criteria - Engineers Approval
06e46e56-df76-5bec-90a5-c8ab5053aedd | note | Standard / Specification - Design Drawings
6e8489e2-fb2d-58f0-bf97-b57361fa463e | note | Verifying Document - ITP Sign Off
c1e300dc-eedd-5142-9f9a-1031ebfcf3b6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
9867705c-34a8-5fa4-ac89-8b325319a281 | note | Verification Activity: Activity - M
2597987d-ecc6-5af2-a423-671d0723a0f9 | note | Verification Activity: By - ENG
e9e8c2cd-2e34-5f02-8879-699288a9aa24 | checkpoint | 1.1.2 - Existing Fences system
f32c2d60-9006-5930-9f6b-c2059a7b2aec | note | Detail - Confirmation of existing Fence network.
8e482f4a-68fc-5545-8c52-941d9c8393af | note | Acceptance / Conformance Criteria - Survey Information's
15423d91-33c1-5772-b194-ca935acfe13d | note | Standard / Specification - Appendix V
a22b1324-349d-5388-b8f2-7cd6deed0be7 | note | Verifying Document - Survey data
06f131f8-2b9c-517c-8bf1-a86163db0679 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction
2c553a08-9c29-57a0-b028-7b823682dc6c | note | Verification Activity: Activity - HP
455af034-9038-5f48-af09-f4980792f812 | note | Verification Activity: By - ENG
a071cef9-3b84-5a44-b239-8ada30897af8 | signoff | AUTHORITY HOLDPOINT
b2505ca3-943c-534d-afb7-23e310ef1e65 | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
5032c6c8-1674-507b-9e9e-9ec0d09378eb | checkpoint | 2.1.1 - Timber (Rails/palings/battens) Posts
a81013da-d335-5038-9c3a-bf1ada791a78 | note | Detail - Treatment
c29adedd-6d0a-5c3c-af84-2548b36de425 | note | Acceptance / Conformance Criteria - H4
641c8d13-92c6-5734-a9f9-7a827bc2e863 | note | ○ H5 if touching ground otherwise H4
a8116ba3-05fb-5a11-a829-3fc17a982a24 | note | Standard / Specification - PS 27.5.5, NZS3607:1989
dc71efa7-cd41-5d29-a76d-db43d735b4d7 | note | Verifying Document - Delivery docket
d54ebcd7-a415-52f4-bb63-b53fb1780186 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
6dea0fbd-834c-5396-b585-29f6c8f5d8ef | note | Verification Activity: Activity - M
2cadf66d-84f1-567f-8b9d-b6ad000b32e5 | note | Verification Activity: By - SE
ff5686ac-35c4-536d-8305-ab342ed5957e | checkpoint | 2.1.2 - Steel (Wire/Metal fence)
471c13c3-334c-56e2-8a0b-e96c7e97c797 | note | Detail - Standard galvanised high tensile steel wire
75e50762-15d6-5b4a-9e79-d2ada755fd73 | note | Acceptance / Conformance Criteria - 2.4mm 12 gauge
6106274f-2944-5117-b75f-6a67e37f4337 | note | Standard / Specification - PS 27.5.1, PS 22.5.6
18e4522f-9002-5550-a9f3-e815c15dabdf | note | Verifying Document - Delivery Docket
55eefcb1-cdb8-56ea-b5ca-83b50390d83a | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
6da8dfdd-3e94-51cf-aa9a-d50d3657a29f | note | Verification Activity: Activity - M
1e6d896a-d77b-50fe-b701-9fa92a840bfc | note | Verification Activity: By - SE
489029af-ef0a-5f3a-b8fe-c98f2f8d59cc | checkpoint | 2.1.3 - Chain Link Net
fb315c75-5831-5ae8-838a-9490cc84d931 | note | Detail - Standard galvanised high tensile steel wire
75edb50b-7a66-5053-b343-dd5aaa97a314 | note | Acceptance / Conformance Criteria - 50*50 Max grid size
cb612150-a942-5284-9355-afa86e7fd150 | note | ○ Powder coated black finish
05b033fb-a4e9-593a-972f-af3ab8aeda25 | note | Standard / Specification - PS 14.6.1
b4ef8562-d5f3-5c66-94d7-614093dae351 | note | Verifying Document - Delivery Docket
dc0041d3-2301-51ce-bc4f-c9f15e7f8fb2 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
4e760af3-a526-5d2c-80d1-e5eb00863b05 | note | Verification Activity: Activity - M
8d4e7b06-7ee1-5d0f-95b9-b572a860eb13 | note | Verification Activity: By - SE
591f8625-e14e-5db2-9fa4-b5d19a067cc5 | checkpoint | 2.1.4 - Material (Fixings/fasteners/hinges/chains)
28e911e2-5198-5b13-a9be-af191a00da8e | note | Detail - Jointing
822cc2ce-04e1-5a67-b3e5-2148ab5ae88d | note | Acceptance / Conformance Criteria - Hot dip galvanised
01f9a961-8407-559f-a4b0-288c00dca841 | note | Standard / Specification - PS 27.5.1
f639d918-6f43-5577-84ff-6b2799ba0d07 | note | Verifying Document - Delivery Docket
3d59af60-6986-50ea-811a-cda0111e73f6 | note | Testing Quantity Required (based from schedule qtys) - Prior Construction
7806c0f5-e56b-58dc-93cc-ac50fd55c2ed | note | Verification Activity: Activity - M
e2935100-6616-5c08-9fbe-19fcfe7e7cca | note | Verification Activity: By - SE
9cc06a11-17ee-5f49-ac50-31c36fc22fcb | section | SECTION 3 – CONSTRUCTION ACTIVITY
4f3a473f-e466-5291-a795-4d0c92b1a2b3 | checkpoint | 3.1.1 - Wetlands Fence
f866857b-ce13-59f6-8fca-ccf773564bd7 | note | Detail - Install around the wetland
16be6173-c6ec-598a-80a0-bc506f5d4028 | note | ○ Black powder coated finish
02f97957-1b4c-5ba0-913e-2c6a46c4d6a9 | note | Acceptance / Conformance Criteria - 1.5M high
7878d232-a1da-53e7-8b56-551687b16305 | note | ○ Hot dip Galvanised
49455d3b-ce8d-5a0b-bb1d-4ee2f0059392 | note | Standard / Specification - PS 2-32735.02-WSP-DR-UDL-0407, PS 27.5.1, PS 27.5.2
b3e15b83-25bd-53c8-8724-0afc06f86748 | note | Verifying Document - Delivery docket
db100ae5-c88c-5953-bdac-afd6169ee08f | note | Testing Quantity Required (based from schedule qtys) - During installation
b54fff12-3021-50a1-a528-9d5e4e6811d0 | note | Verification Activity: Activity - M
8b1cfc15-3b30-5ee6-a294-a4d0f16103c9 | note | Verification Activity: By - SE
42ecb55c-639f-5bdc-a60c-8778e8f586be | checkpoint | 3.2.1 - Timber fence
d4316e81-867b-58ab-9596-b44287b1f3cf | note | Detail - Preserve timber exposed faces
5d5e9a2d-6a4d-58bc-9093-8643504d18fd | note | ○ Post imbedded in ground
8e9338f9-e7a9-5b7d-9ca3-3aa80ff61f31 | note | Acceptance / Conformance Criteria - 1.8m high
9508edf4-88d7-55ba-9ac8-e6968cf7b96b | note | ○ Exposed timber faces neatly protected with 2 coats of timber preservative (Metalex)
9623e987-c6f2-5d55-81fc-5622cb550839 | note | ○ 1800mm in ground with 17.5MPa concrete
4e0aa3d2-8b75-5ddd-8631-9598808c35b4 | note | ○ Minimum 100mm extend around the post
a685488e-d7f7-514d-942c-d745412a8f69 | note | Standard / Specification - PS 27.5.5
f6d7f996-c09b-5457-82a7-f73078527bb4 | note | Verifying Document - Delivery docket
7faebad8-8d34-5361-b428-2cbb50372b40 | note | Testing Quantity Required (based from schedule qtys) - During installation
4cc86542-9a5b-5660-882a-2b059e971f0b | note | Verification Activity: Activity - M
26b50076-ae91-5c35-8a91-c9991469d4f5 | note | Verification Activity: By - SE
0925a98a-cb05-53ed-bbcf-af284fac16fe | checkpoint | 3.3.1 - Post and Wire Farm Fence
a99eecce-1bd6-5757-ab09-4a0d680142a2 | note | Detail - 8 Steel wire
7db0eb80-7ddd-573a-9253-9f0367c508c9 | note | ○ Timber post located at max 5m centre and securely rammed
94b5ab92-09fd-549a-bbef-470b80a3ded6 | note | ○ Battens affixed to wire and timber evenly spaces
468bcdd9-c010-5727-bb03-23297570b593 | note | Acceptance / Conformance Criteria - Wire and ground distance < 125mm
a81f057d-2c0a-5b49-913d-da98849be607 | note | ○ Top wire to > 1m from ground
a6e655e0-1d7a-5e59-bdce-49e96ca95c86 | note | ○ Top of post > 50mm top wire
4fe274a8-f56a-5649-9772-9f3c0ea9eca6 | note | ○ Wires not attached on road side
79fcb05f-b14c-593e-9310-936c029d8ec0 | note | ○ First 3 wire separation 125mm
3819f83b-c1d0-5a7b-93fa-b09ec9bce062 | note | ○ Min 3 battens between posts
042662cf-7c8a-5cba-9f10-e32e166877c2 | note | Standard / Specification - PS- 27.5.6, NZS 2566
3418000d-3d38-57bb-9402-e322950b9a0a | note | Verifying Document - Visual inspection
ef05d5b9-bd63-5ba9-97f5-67cb63132ce0 | note | Testing Quantity Required (based from schedule qtys) - During Construction
cb8ceb04-16f5-57d6-9011-32b47bb8254a | note | Verification Activity: Activity - M
750bf047-2bb0-5ba5-b919-f85ad174c439 | note | Verification Activity: By - SE
94bb45d6-7c4a-5d34-9c38-ef50db464e25 | checkpoint | 3.3.2 - Strainer Posts
5eaa510d-3abf-564d-91e0-0687d7761430 | note | Detail - At new and existing fence terminations
51b392b8-abab-5567-87a5-77726bb2042c | note | ○ At each corner distance between corner and/or termination strainer exceeds 200m
d6c56c89-dfe6-5340-8dba-2e813b7fd5f7 | note | Acceptance / Conformance Criteria - Double footing and tight wire secured to the post using 4mm wire
b0a26b89-41ad-5167-af76-f10b58d3241c | note | Standard / Specification - PS 22.5.6.b
6ddd964e-1636-56b0-96f6-13d333cc1fd6 | note | Verifying Document - Visual inspection
5bf4e9fe-de84-5ef6-b6e3-19665fa1c039 | note | Testing Quantity Required (based from schedule qtys) - During Construction
9fd2937e-3755-58d7-ac9e-22f0494e473d | note | Verification Activity: Activity - M
d0bf2e5e-cac4-54d8-a3ed-5919040b7a75 | note | Verification Activity: By - SE
4067999f-5728-5587-8d89-7544a2a9c8b2 | checkpoint | 3.4.1 - Chain Link fence
49ccd8f6-152c-5be0-86c8-0816a13e7e1b | note | Detail - As per drawings
cf7d3ade-8d42-5a14-a50f-070e5a74f692 | note | ○ Headwall and Wingwall fencing
bb2211d5-3200-58fd-ab7a-1eb31f32ef4a | note | ○ Secured with posts and top rails
08ca82e7-f3c2-5580-985a-2e7f1364c65b | note | ○ Spacing between two post must be equal
66f2a5bf-d6be-5cb9-9bbd-d73b88e04d37 | note | Acceptance / Conformance Criteria - Tie wire on every second diamond
742f6d38-b923-5d12-b795-864bced588b5 | note | ○ Spacing < 2400mm
eb901cff-cee9-5f5c-97bd-5755a3be111b | note | Standard / Specification - PS 2-32735.02-WSP-DR-UDL-0407
cfbb4d20-0a62-51e2-83f7-f7e6f4f19055 | note | Verifying Document - Visual inspection
016b0d32-bd62-5a8b-8694-80f46c88f8c5 | note | Testing Quantity Required (based from schedule qtys) - During Construction
929a7432-3580-52b6-949b-87077a10bcf3 | note | Verification Activity: Activity - M
359818d8-98d8-5a2b-8d59-d3bb6f1a10b4 | note | Verification Activity: By - SE
801f7ada-618c-5ced-9ef5-1d9f7eae2d38 | section | SECTION 4 – HANDOVER
13049da8-dc5f-50e6-9653-61f13f53ec94 | checkpoint | 4.1.1 - Survey As-Builts
80835152-ec3b-5e5a-b659-35b7e243d274 | note | Detail - Quality Check on New Works based on the tolerances in RITS
6137f7ba-ad1a-5fce-8331-3e570fa5c5e8 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
5afaec36-5ff3-5d6c-8432-40d0ad8dea64 | note | Standard / Specification - PS-21.7.7
a9994d3c-d6bb-548a-a6b8-094cae2a1a95 | note | Verifying Document - Red pen markup only
02da7ac2-5c09-551f-b3e2-139dc087d778 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
44d84a42-1183-5ed1-aa30-431c32e958db | note | Verification Activity: Activity - H
9dd801c2-36c1-54bb-89d4-b13fc7e94d3a | note | Verification Activity: By - ENG/PE