## ITC Predrill
checklist | Pile Predrilling & Filling ITC
section | Location Details
checkpoint | Details
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
textbox | Row Number | Text Box
textbox | Table Number | Text Box
dropdown | Number of Piles | 8 Pile, 16 Pile, Other
textbox | If other, please specify
section | Drilling
checkpoint | Drilling
date | Date
dropdown | Drill Depth | 1.8m, Other
textbox | If other, please specify
dropdown | Drill Width | 300mm, Other
textbox | If other, please specify
checkpoint | North/South Verticality +/- 3deg
checkpoint | East/West Verticality +/- 3deg
section | Fill
checkpoint | Fill
dropdown | Predrill Fill Mix | 5% Stabilised Sand, Other
textbox | If other, please specify
section | Closeout
checkpoint | Non-Conformances Closed Out
note | P,F,Attachment
checkpoint | Works checked & completed
signoff | SIGN HERE

## ITC Piling
Piling ITC
| Location Details | Site Reference | Dropdown, 1,2,3,4,5,6,7,8,9,10,11,12,13,14
|  | Row Number | Text Box
|  | Table Number | Text Box
|  | Number of Piles | Checkbox, 8 Pile, 16 Pile, Other
Preconstruction
| Design | Issued For Construction Drawings: 01_Maungaturoto_FS2V-23*-12_DUO_EX 02_Maungaturoto_FS2V-23*-12_DUO_EX Schletter Electronic Design Data Schletter FS DUO - Fixed-tilt Installation Procedure | P,F,Attachment
Construction
| Pile Distribution to respective blocks | Survey Data Schletter pile location data Visual Inspection Piles distributed as per Schletter drawings, ie correct colour, code , dimensions and length | P,F,Attachment
| Pile Refusal | Drive piles to depth until they reach the point of refusal Record Pile location and mark on the drawing Record Actual Pile embedment Depth Pile refusal in accordance with pile refusal procedure Piles cut and holes drilled as per Schletter documentation Survey Record ITC Data Tracker Excel Pile Monitoring Sheet - Embedment Depth - Reveal Height Pile Test Result documentation | P,F,Attachment
| Pile Predrill to minimum embedment | For Each Pile Pile Predrill ITC Piles are minimum of 1.8m deep Predrill holes are minimum of 300mm dia Backfilled with approved mix as per Schletters Installation Procedure | P,F,Attachment
| Pile Installation | Schletter FS Duo Fixed-tilt Installation Procedure Install Pile on the correct location as per Schletter drawing Install pile within the design tolerances Piles should have no damage or deformation and in correct orientation North/South +/- 3° East/West +/- 3° Pile Twisting from axis +/- 5° Distance E/W +/- 100mm N/S +/- 50mm Reveal Height +/- 100mm Height difference foundation posts within one row +/- 50mm Piles have no damage deformation and in correct orientation | P,F,Attachment
| Cold Galvanising Repair, if required | Schletter FS Duo Fixed-tilt Installation Procedure Upper 30mm of the inside and outside of the pile is coated with a zinc rich primer | P,F,Attachment
Close-Out
| Non-Conformance-Reports | Non-Conformances Closed Out | P,F,Attachment
| Table Piling Completed | Table Piling Works checked & completed | HoldPoint, P,F,Attachment

## ITC Mechanical
Mechanical ITC
| Location Details | Site Reference | Dropdown, 1,2,3,4,5,6,7,8,9,10,11,12,13,14
|  | Row Number | Text Box
|  | Table Number | Text Box
Construction
| Mounting of Girders | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0 ITC Mechanical Installation Each M12x30 bolt passed through from the Girder and fixed on the Pile with a M12 Washer and M12 Flange Serrated Nut Torqued to value of +/- 5% of 53.2 - 58.8 Nm Each bolted connection shall be marked after torquing | P,F,Attachment
| Girder to Foundation Post Step Check | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0 ITC Mechanical Installation Angle of the Girder to the horizontal to be an angle of 23° +/- 1° | P,F,Attachment
| Purlin Connector Installation | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10 ITC Mechanical Installation Purlin Connector placed under purlin Screwed together with Four x M10x25 bolts for LC/LT Purlins Tightened to a torqued value of +/- 5% of 32Nm Each bolted connection shall be marked after torquing | P,F,Attachment
| Purlin Mounting Checks | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10 Purlin placed on top of the girder in correct direction FS Gen3 Girder Purlin connector bottom part attached FS Flex Claw Installed Purlin Connector Attached 3x Lengths as per IFC Design East/West 4320mm-5310mm-4320mm | P,F,Attachment
| Connection of Girder and Purlin | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10 ITC Mechanical Installation Girder FS Flex Claw M10x35 bolt and nut tightened to a torque of +/- 5% of 32Nm M21x30 bolt and nut tightened to a torque of +/- 5% of 56Nm | P,F,Attachment
Close-Out
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Table Mechanical Work Completed | Works completed for the table and checked | HoldPoint, P,F,Attachment

## ITC Panelling
Panel Installation ITC
| Location Details | Site Reference | Dropdown, 1,2,3,4,5,6,7,8,9,10,11,12,13,14
|  | Row Number | Text Box
|  | Table Number | Text Box
Construction
| Placing Module Clamps on Purlins | Schletter FS DUO - Fixed-tilt Installation Procedure ITC Panelling | P,F,Attachment
| Align Module and Tighten Clamps | Schletter FS DUO - Fixed-tilt Installation Procedure ITC Panelling | P,F,Attachment
| Align Module and gap between panels as per IFC Drawings | Schletter FS DUO - Fixed-tilt Installation Procedure ITC Panelling Top Panel to Bottom Panel: 5-10mm Panel with Module Clamps: 22mm | P,F,Attachment
| Ensure Panels are dry, clean of dust/mud and no visible damage | Schletter FS DUO - Fixed-tilt Installation Procedure ITC Panelling | P,F,Attachment
| Ensure Panels Start and Finish at even distances of the Purlin | 01_Maungaturoto_FS2V-23°-12_DUO_EX 02_Maungaturoto_FS2V-23°-12_DUO_EX ITC Panelling Panels shall be 50mm from the ends of the purlins | P,F,Attachment
| Ensure correct number of panels are installed for each table | Issued For Construction Drawings: 01_Maungaturoto_FS2V-23*-12_DUO_EX 02_Maungaturoto_FS2V-23*-12_DUO_EX Schletter Electronic Design Data ITC Panelling | P,F,Attachment
| Ensure Panels are properly secured | Schletter FS DUO - Fixed-tilt Installation Procedure ITC Panelling | P,F,Attachment
Close-Out
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Table Panel Installation Completed | Works completed for the table and checked | HoldPoint, P,F,Attachment