## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Pile Predrilling & Filling ITC | itp |  |  |  |  | C - 7051 ITC-ITR - Pile Predrilling & Filling ITC
section | Location Details
checkpoint | Details
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
textbox | Row Number
textbox | Table Number
dropdown | Number of Piles | 8 Pile,16 Pile,Other
textbox | If other, please specify
section | Drilling
checkpoint | Drilling
date | Date
dropdown | Drill Depth | 1.8m,Other
textbox | If other, please specify
dropdown | Drill Width | 300mm,Other
textbox | If other, please specify
checkpoint | North/South Verticality +/- 3deg
checkpoint | East/West Verticality +/- 3deg
section | Fill
checkpoint | Fill
dropdown | Predrill Fill Mix | 5% Stabilised Sand,Other
textbox | If other, please specify
section | Closeout
checkpoint | Non-Conformances Closed Out
label | P,F,Attachment
checkpoint | Works checked & completed
signoff | SIGN HERE
checklist | Piling ITC | itp |  |  |  |  | C - 7051 ITC-ITR - Piling ITC
section | Location Details
checkpoint | Details
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
textbox | Row Number
textbox | Table Number
label | Number of Piles
bool | 8 Pile
bool | 16 Pile
bool | Other
textbox | If other, please specify
section | Preconstruction
checkpoint | Design
label | Issued For Construction Drawings:
label | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ Schletter Electronic Design Data
label | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
section | Construction
checkpoint | Pile Distribution to respective blocks
label | Survey Data
label | ○ Schletter pile location data
label | Visual Inspection
label | ○ Piles distributed as per Schletter drawings, ie correct colour, code , dimensions and length
checkpoint | Pile Refusal
label | Drive piles to depth until they reach the point of refusal
label | Record Pile location and mark on the drawing
label | Record Actual Pile embedment Depth
label | Pile refusal in accordance with pile refusal procedure
label | Piles cut and holes drilled as per Schletter documentation
label | Survey Record
label | ITC Data Tracker Excel Pile Monitoring Sheet
label | – Embedment Depth
label | – Reveal Height
label | Pile Test Result documentation
checkpoint | Pile Predrill to minimum embedment
label | For Each Pile
label | Pile Predrill ITC
label | Piles are minimum of 1.8m deep
label | Predrill holes are minimum of 300mm dia
label | Backfilled with approved mix as per Schletters Installation Procedure
checkpoint | Pile Installation
label | Schletter FS Duo Fixed-tilt Installation Procedure
label | Install Pile on the correct location as per Schletter drawing
label | Install pile within the design tolerances
label | Piles should have no damage or deformation and in correct orientation
label | North/South +/- 3°
label | East/West +/- 3°
label | Pile Twisting from axis +/- 5°
label | Distance E/W +/- 100mm
label | N/S +/- 50mm
label | Reveal Height +/- 100mm
label | Height difference foundation posts within one row +/- 50mm
label | Piles have no damage deformation and in correct orientation
checkpoint | Cold Galvanising Repair, if required
label | Schletter FS Duo Fixed-tilt Installation Procedure
label | Upper 30mm of the inside and outside of the pile is coated with a zinc rich primer
section | Close-Out
checkpoint | Non-Conformance-Reports
label | Non-Conformances Closed Out
checkpoint | Table Piling Completed
label | Table Piling Works checked & completed
holdpoint | SIGN HERE
checklist | Mechanical ITC | itp |  |  |  |  | C - 7051 ITC-ITR - Mechanical ITC
section | Location Details
checkpoint | Details
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
textbox | Row Number
textbox | Table Number
section | Construction
checkpoint | Mounting of Girders
label | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0
label | ITC Mechanical Installation
label | Each M12x30 bolt passed through from the Girder and fixed on the Pile with a M12 Washer and M12 Flange Serrated Nut
label | Torqued to value of +/- 5% of 53.2 - 58.8 Nm
label | Each bolted connection shall be marked after torquing
checkpoint | Girder to Foundation Post Step Check
label | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0
label | ITC Mechanical Installation
label | Angle of the Girder to the horizontal to be an angle of 23° +/- 1°
checkpoint | Purlin Connector Installation
label | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
label | ITC Mechanical Installation
label | Purlin Connector placed under purlin
label | Screwed together with Four x M10x25 bolts for LC/LT Purlins
label | Tightened to a torqued value of +/- 5% of 32Nm
label | Each bolted connection shall be marked after torquing
checkpoint | Purlin Mounting Checks
label | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
label | Purlin placed on top of the girder in correct direction
label | FS Gen3 Girder Purlin connector bottom part attached
label | FS Flex Claw Installed
label | Purlin Connector Attached
label | 3x Lengths as per IFC Design
label | East/West 4320mm-5310mm-4320mm
checkpoint | Connection of Girder and Purlin
label | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
label | ITC Mechanical Installation
label | Girder
label | FS Flex Claw
label | M10x35 bolt and nut tightened to a torque of +/- 5% of 32Nm
label | M21x30 bolt and nut tightened to a torque of +/- 5% of 56Nm
section | Close-Out
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Table Mechanical Work Completed
label | Works completed for the table and checked
holdpoint | SIGN HERE
checklist | Panel Installation ITC | itp |  |  |  |  | C - 7051 ITC-ITR - Panel Installation ITC
section | Location Details
checkpoint | Details
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
textbox | Row Number
textbox | Table Number
section | Construction
checkpoint | Placing Module Clamps on Purlins
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | ITC Panelling
checkpoint | Align Module and Tighten Clamps
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | ITC Panelling
checkpoint | Align Module and gap between panels as per IFC Drawings
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | ITC Panelling
label | Top Panel to Bottom Panel: 5-10mm
label | Panel with Module Clamps: 22mm
checkpoint | Ensure Panels are dry, clean of dust/mud and no visible damage
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | ITC Panelling
checkpoint | Ensure Panels Start and Finish at even distances of the Purlin
label | 01_Maungaturoto_FS2V-23°-12_DUO_EX
label | 02_Maungaturoto_FS2V-23°-12_DUO_EX
label | ITC Panelling
label | Panels shall be 50mm from the ends of the purlins
checkpoint | Ensure correct number of panels are installed for each table
label | Issued For Construction Drawings:
label | 01_Maungaturoto_FS2V-23*-12_DUO_EX
label | 02_Maungaturoto_FS2V-23*-12_DUO_EX
label | Schletter Electronic Design Data
label | ITC Panelling
checkpoint | Ensure Panels are properly secured
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | ITC Panelling
section | Close-Out
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Table Panel Installation Completed
label | Works completed for the table and checked
holdpoint | SIGN HERE
checklist | Pile Predrilling & Filling ITP | itp |  |  |  |  | C - 7051 MSF Mech Piling ITP - Pile Predrilling & Filling ITP
section | Location Details
checkpoint | Details
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
textbox | Row Number
textbox | Table Number
dropdown | Number of Piles | 8 Pile,16 Pile,Other
textbox | If other, please specify
section | Drilling
checkpoint | Drilling
date | Date
dropdown | Drill Depth | 1.8m,Other
textbox | If other, please specify
dropdown | Drill Width | 300mm,Other
textbox | If other, please specify
checkpoint | North/South Verticality +/- 3deg
checkpoint | East/West Verticality +/- 3deg
section | Fill
checkpoint | Fill
dropdown | Predrill Fill Mix | 5% Stabilised Sand,Other
textbox | If other, please specify
section | Closeout
checkpoint | Non-Conformance-Reports
label | Non-Conformances Closed Out
checkpoint | Punch List
label | Development of Punchlist with PM/CM and or Supervisor Punch List closed out in a timely mannor
checkpoint | Handover
label | At completion of works QA/QC Pack is handed to client
label | Client Verifies Work has been completed correctly and all quality documents are in order
signoff | SIGN HERE
checklist | Piling ITP | itp |  |  |  |  | C - 7051 MSF Mech Piling ITP - Piling ITP
section | Location Details
checkpoint | Details
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
textbox | Row Number
textbox | Table Number
label | Number of Piles
bool | 8 Pile
bool | 16 Pile
bool | Other
textbox | If other, please specify
section | Preconstruction
checkpoint | Design
label | Issued For Construction Drawings:
label | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ Schletter Electronic Design Data
label | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
checkpoint | Survey & Setout
label | Schletter Electronic Design Data
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | Survey As Constructed Record
label | Pile Location Spreadsheet
checkpoint | Inspection Measuring and Test Equipment Registers (IMTE)
label | Supply of all calibration certificates
section | Construction
checkpoint | Pile Distribution to respective blocks
label | Survey Data
label | ○ Schletter pile location data
label | Visual Inspection
label | ○ Piles distributed as per Schletter drawings, ie correct colour, code , dimensions and length
checkpoint | Pile Refusal
label | Drive piles to depth until they reach the point of refusal
label | Record Pile location and mark on the drawing
label | Record Actual Pile embedment Depth
label | Pile refusal in accordance with pile refusal procedure
label | Piles cut and holes drilled as per Schletter documentation
label | Survey Record
label | ITC Data Tracker Excel Pile Monitoring Sheet
label | – Embedment Depth
label | – Reveal Height
label | Pile Test Result documentation
checkpoint | Pile Predrill to minimum embedment
label | For Each Pile
label | Pile Predrill ITC
label | Piles are minimum of 1.8m deep
label | Predrill holes are minimum of 300mm dia
label | Backfilled with approved mix as per Schletters Installation Procedure
checkpoint | Pile Installation
label | Schletter FS Duo Fixed-tilt Installation Procedure
label | Install Pile on the correct location as per Schletter drawing
label | Install pile within the design tolerances
label | Piles should have no damage or deformation and in correct orientation
label | North/South +/- 3°
label | East/West +/- 3°
label | Pile Twisting from axis +/- 5°
label | Distance E/W +/- 100mm
label | N/S +/- 50mm
label | Reveal Height +/- 100mm
label | Height difference foundation posts within one row +/- 50mm
label | Piles have no damage deformation and in correct orientation
checkpoint | Cold Galvanising Repair, if required
label | Schletter FS Duo Fixed-tilt Installation Procedure
label | Upper 30mm of the inside and outside of the pile is coated with a zinc rich primer
section | Close-Out
checkpoint | As Constructed - Redline Markup Drawings
label | At completion of the the piling for each area
label | Markup Redline Asbuilts if different from design and identify changes
checkpoint | Non-Conformance-Reports
label | Non-Conformances Closed Out
checkpoint | Punch List
label | Development of Punchlist with PM/CM and or Supervisor
label | Punch List closed out in a timely mannor
checkpoint | Handover
label | At completion of works QA/QC Pack is handed to client
label | Client Verifies Work has been completed correctly and all quality documents are in order
signoff | SIGN HERE
checklist | Mechanical ITP | itp |  |  |  |  | C - 7051 MSF Mech Piling ITP - Mechanical ITP
section | Location Details
checkpoint | Details
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
textbox | Row Number
textbox | Table Number
section | Preconstruction
checkpoint | Design
label | Issued For Construction Drawings:
label | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ Schletter Electronic Design Data
label | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
checkpoint | Inspection Measuring and Test Equipment Registers (IMTE)
label | Supply of all calibration certificates
section | Construction
checkpoint | Mounting of Girders
label | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0
label | ITC Mechanical Installation
label | Each M12x30 bolt passed through from the Girder and fixed on the Pile with a M12 Washer and M12 Flange Serrated Nut
label | Torqued to value of +/- 5% of 53.2 - 58.8 Nm
label | Each bolted connection shall be marked after torquing
checkpoint | Girder to Foundation Post Step Check
label | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0
label | ITC Mechanical Installation
label | Angle of the Girder to the horizontal to be an angle of 23° +/- 1°
checkpoint | Purlin Connector Installation
label | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
label | ITC Mechanical Installation
label | Purlin Connector placed under purlin
label | Screwed together with Four x M10x25 bolts for LC/LT Purlins
label | Tightened to a torqued value of +/- 5% of 32Nm
label | Each bolted connection shall be marked after torquing
checkpoint | Purlin Mounting Checks
label | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
label | Purlin placed on top of the girder in correct direction
label | FS Gen3 Girder Purlin connector bottom part attached
label | FS Flex Claw Installed
label | Purlin Connector Attached
label | 3x Lengths as per IFC Design
label | East/West 4320mm-5310mm-4320mm
checkpoint | Connection of Girder and Purlin
label | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
label | ITC Mechanical Installation
label | Girder
label | FS Flex Claw
label | M10x35 bolt and nut tightened to a torque of +/- 5% of 32Nm
label | M21x30 bolt and nut tightened to a torque of +/- 5% of 56Nm
section | Close-Out
checkpoint | As Constructed - Redline Markup Drawings
label | Red-line As-Built constructed records supplied
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Punch List
label | Development of Punchlist with PM/CM and or Supervisor
label | Punch List closed out in a timely mannor
checkpoint | Handover
label | At completion of works QA/QC Pack is handed to client
label | Client Verifies Work has been completed correctly and all quality documents are in order
signoff | SIGN HERE
checklist | Panel Installation ITP | itp |  |  |  |  | C - 7051 MSF Mech Piling ITP - Panel Installation ITP
section | Location Details
checkpoint | Details
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
textbox | Row Number
textbox | Table Number
section | Preconstruction
checkpoint | Design
label | Issued For Construction Drawings:
label | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ Schletter Electronic Design Data
label | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
checkpoint | Inspection Measuring and Test Equipment Registers (IMTE)
label | Supply of all calibration certificates
section | Construction
checkpoint | Placing Module Clamps on Purlins
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | ITC Panelling
checkpoint | Align Module and Tighten Clamps
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | ITC Panelling
checkpoint | Align Module and gap between panels as per IFC Drawings
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | ITC Panelling
label | Top Panel to Bottom Panel: 5-10mm
label | Panel with Module Clamps: 22mm
checkpoint | Ensure Panels are dry, clean of dust/mud and no visible damage
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | ITC Panelling
checkpoint | Ensure Panels Start and Finish at even distances of the Purlin
label | 01_Maungaturoto_FS2V-23°-12_DUO_EX
label | 02_Maungaturoto_FS2V-23°-12_DUO_EX
label | ITC Panelling
label | Panels shall be 50mm from the ends of the purlins
checkpoint | Ensure correct number of panels are installed for each table
label | Issued For Construction Drawings:
label | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ Schletter Electronic Design Data
label | ○ ITC Panelling
checkpoint | Ensure Panels are properly secured
label | Schletter FS DUO - Fixed-tilt Installation Procedure
label | ITC Panelling
section | Close-Out
checkpoint | As Constructed - Redline Markup Drawings
label | Red-line As-Built constructed records supplied
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Punch List
label | Development of Punchlist with PM/CM and or Supervisor
label | Punch List closed out in a timely mannor
checkpoint | Handover
label | At completion of works QA/QC Pack is handed to client
label | Client Verifies Work has been completed correctly and all quality documents are in order
signoff | SIGN HERE