## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1210-SP2-019-002 ITP Wetland 2 Stormwater Drainage Directional Drilling | itp |  |  |  |  | DN1210-SP2-019-002 ITP Wetland 2 Stormwater Drainage Directional Drilling Rev 0
section | SECTION 3 – PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
checkpoint | 3.1 - Extent of Line Setout
label | Detail - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Stormwater drawings.
label | ○ Identify any clashes before construction.
label | ○ Lot - Markup
label | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
label | Standard / Specification - Design Drawings
label | Verifying Document - ITP Sign Off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 3.2 - Material grading: Materials (Gap65/AP65)
label | Detail - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
label | Acceptance / Conformance Criteria - No Particles >200mm
label | ○ Maximum fines 10% passing 75micron sieve
label | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
label | ○ 0-400 - 2 tests
label | ○ 400-1,500 - 3 tests
label | ○ 1,500-4,000 - 4 tests
label | ○ >4,000 - 1 test for each additional 1,000m3
label | — Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Weathering index: Materials (Gap65/AP65)
label | Detail - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
label | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
label | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - Crushing Resistance: Materials (Gap65/AP65)
label | Detail - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
label | Acceptance / Conformance Criteria - >100KN
label | Standard / Specification - Appendix XVIII, Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - Material grading: Materials (Sand)
label | Detail - Bedding/Side Zone/ Overlay Zone/Embedment Zone
label | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
label | 19.0mm ¦¦ 85-100% passing
label | 9.5mm ¦¦ 25-55% passing
label | 4.75mm ¦¦ 0-10% passing
label | 2.36mm ¦¦ 0-5% passing
label | 0.075mm ¦¦ 0-2% passing
label | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
label | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
label | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
label | 400-1500m3 ¦¦ 3 Test
label | 1500-4000m3 ¦¦ 4 Test
label | >4000 ¦¦ 1 Test Additional 1000m3
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.6 - Pipes (PE)
label | Detail - Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
label | ○ Full Traceability information and certification of analysis for the resin batch.
label | Acceptance / Conformance Criteria - Full Traceability information and certification of Material
label | Standard / Specification - PS-22.4.1 (d) AS/NZS 1477
label | Verifying Document - Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.7 - Pipe and fittings.
label | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivery Dockets / Inspection Checksheet
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 3.8 - Granular Material (Sand, GAP65/AP65)
label | Detail - Confirm Specification and material in good condition.
label | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 3.9 - Bidim/Geogrid
label | Detail - BIDIM A29 Durogrid 30/30 or similar.
label | Acceptance / Conformance Criteria - Site Engineer Approval
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 3.10 - Tracer wire
label | Detail - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Acceptance / Conformance Criteria - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Standard / Specification - PS 22.7.3 a
label | Verifying Document - Docket
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 3.11 - Drilling Fluid mix
label | Detail - Fluid design to be submitted to engineer before start of works.
label | Acceptance / Conformance Criteria - Fluid design to be submitted to engineer before start of works.
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 3.12 - Reinforcing steel (Stilling Well)
label | Detail - Wetland 02 Stilling well detail (SDMH11.1.1)
label | Acceptance / Conformance Criteria - LAPS TO THE 16mm DIAMETER LONGITUDINAL
label | ○ BARS TO BE MIN. 825mm AS REQUIRED. REFER TO CONCRETE SPECIFICATION FOR FURTHER REQUIREMENTS AND HOLD POINTS.
label | ○ DRILL AND FIX 6 No. M30 HDG G8.8 THREADED ROD ANCHOR STUDS WITH NUT AND WASHER USING EPCON C8 EPOXY OR SIMILAR APPROVED.
label | ○ MIN. EMBEDMENT OF 210mm IN CONCRETE PAD. LENGTH TO SUIT MIN. EMBEDMENT AND THICKNESS OF MANHOLE FLANGE BASE.
label | ○ ANCHORS TO BE EQUALLY SPACED.
label | Standard / Specification - PS -IFC STW 0411
label | Verifying Document - Material docket
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 3.13 - Concrete
label | Detail - Wetland 02 Stilling well detail (SDMH11.1.1)
label | Acceptance / Conformance Criteria - Concrete should have 40MPA 28 day strength
label | Standard / Specification - PS -IFC STW 0411
label | Verifying Document - Material docket
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 3.14 - Stormwater - Structure (SWMH, SDMH)
label | Detail - Confirm diameter, class & jointing type as shown on the drawings, and that the Structure are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm diameter and size as shown on the drawings, and that the Structure are correct and in good condition.
label | Standard / Specification - PS- 21.5.4, NZS 3109:1997
label | Verifying Document - Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 4 – STORMWATER MANHOLE INSTALLATION
checkpoint | 4.1 - Foundation Compliance
label | Detail - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | ○ Cohesive Material: Vane Shear Strength 70kPa
label | Standard / Specification - Appendix V Table 21:11
label | Verifying Document - Shear vane or Scala test result
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - W
label | Verification Activity: By - SE
checkpoint | 4.2 - Undercut approval
label | Detail - On Subgrade
label | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
label | Standard / Specification - Table 21.5
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3 - Undercut Backfill Compliance AP65
label | Detail - On Granular Material
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | Standard / Specification - PS- 16.5.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.4 - Bedding Compaction Testing AP65
label | Detail - On Granular Material
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | Standard / Specification - PS- 16.5.12, PS- 21.6.11
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.5 - Stilling Well SDMH 11.1.1
label | Detail - Wetland 02 Stilling well detail (SDMH11.1.1)
label | Acceptance / Conformance Criteria - DN1800mm
label | ○ Sump depth > 750mm
label | ○ Concrete structure
label | ○ Concrete slab constructed
label | Standard / Specification - PS -IFC STW 0411
label | Verifying Document - Material docket
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.6 - Survey
label | Detail - Inspection of Structure
label | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
label | Standard / Specification - PS- 21.7.6
label | Verifying Document - Survey Data
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SV
checkpoint | 4.7 - Backfill Compaction Testing
label | Detail - From Overlay layer to the subgrade layer
label | Acceptance / Conformance Criteria - AP65 Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
label | ○ AP65 - Clegg 28% CIV
label | Standard / Specification - PS- 16.5.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.8 - Inspection
label | Detail - Inspection of Structure
label | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
label | Standard / Specification - PS- 21.6.11
label | Verifying Document - Manhole/Catchpit Record
label | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
section | SECTION 5 - STORMATER PE PIPELINE CONSTRUCTION
checkpoint | 5.1 - Survey
label | Detail - Surveyor to Setout
label | Acceptance / Conformance Criteria - Horizontal +-100mm
label | ○ Vertical +-200mm
label | Standard / Specification - PS-25.13.5
label | Verifying Document - Survey Data
label | Testing Quantity Required (based from schedule qtys) - Every 100m or at Chambers (whichever distance is the lesser)
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SV
section | SECTION 6 - STORMWATER PE PIPELINE (Butt-Fusion Welding)
checkpoint | 6.1 - Butt-Fusion Welding
label | Detail - Use only semi-automatic or automatic welding machines.
label | ○ Maintain a site record for all butt-fusion welds.
label | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
label | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
label | ○ WMS Report
label | Standard / Specification - Appendix 22. PS 22.9.4 C
label | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report.
label | Testing Quantity Required (based from schedule qtys) - Every Welding Point
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.2 - Survey
label | Detail - Inspection of Pipeline Inverts
label | Acceptance / Conformance Criteria - Horizontal +-100mm
label | ○ Vertical +-200mm
label | Standard / Specification - PS-25.13.5
label | Verifying Document - Survey Data / As-built record
label | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 7 - STORMWATER PIPELINE DIRECTIONAL DRILLING
checkpoint | 7.1 - Drilling level checks
label | Detail - Inspection of Pipeline Inverts
label | Acceptance / Conformance Criteria - Horizontal +-100mm
label | ○ Vertical +-200mm
label | Standard / Specification - PS-25.13.5
label | Verifying Document - Survey Data / As-built record
label | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.2 - Drilling Fluid Mix
label | Detail - Viscosity record
label | Acceptance / Conformance Criteria - Pump rate on eam 450L/min
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Viscosity record /checksheet
label | Testing Quantity Required (based from schedule qtys) - Every shot
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.3 - Correct Reamer used
label | Detail - Reamer size to confirm on site
label | Acceptance / Conformance Criteria - Reamer size to confirm on site
label | ○ Reamer must be >1000mm
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Checksheet
label | Testing Quantity Required (based from schedule qtys) - 1 per drill shot
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.4 - Pipe Damage
label | Detail - Damage <10% of wall thickness
label | Acceptance / Conformance Criteria - Damage <10% of wall thickness
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - Each pipe
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.5 - Tracer Wire
label | Detail - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Acceptance / Conformance Criteria - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Standard / Specification - PS 22.7.3 a
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.6 - Drill Report
label | Detail - Drill reportr to be submitted
label | Acceptance / Conformance Criteria - Drill reportr to be submitted which shows the all information of the drill works in one report
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Report
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.7 - Settlement monitoring and ground deformation (Baseline measurements)
label | Detail - Topo survey completed before and after drill shot
label | Acceptance / Conformance Criteria - Topo survey completed before and after drill shot
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Survey data
label | Testing Quantity Required (based from schedule qtys) - Every 6m
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 8 - CCTV
checkpoint | 8.1 - CCTV Inspection
label | Detail - CCTV stormwater pipes at completion of trench backfill but prior to final surfacing (pavements, etc.)
label | Acceptance / Conformance Criteria - Every stormwater pipeline 225mm diameter or greater.
label | Standard / Specification - PS- 21.7.6, PS- 21.7.8
label | Verifying Document - CCTV Report
label | Testing Quantity Required (based from schedule qtys) - 1 per line
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
section | SECTION 9 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
checkpoint | 9.1 - As-Builts / Redpen markups
label | Detail - Quality Check on New Works based on the tolerances in RITS
label | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
label | Standard / Specification - Project Specifications
label | Verifying Document - Red pen markup only
label | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature