## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Meter Panels (Pre-Energisation) | [5 empty] | Testing & Commissioning - Meter Panels (Pre-Energisation)
section | Physical Checks
checkpoint | Confirm panels dimensions are in accordance with approved shop drawings
checkpoint | Confirm correct circuit identification and labelling
checkpoint | Confirm correct size of earthing conductors
checkpoint | Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
section | Mechanical Checks
checkpoint | Confirm correct breaker ratings/settings
checkpoint | Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint | Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint | Repeat mounting and dismounting of power fuses for 1 time
checkpoint | Repeat mounting and dismounting of control fuses 1 time
checkpoint | Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards.
checkpoint | Conduct pull test for all cables connected to MCBs and Termination blocks
section | Preliminary Checks
checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint | 2. Confirm Main Breaker Closed
checkpoint | 3. Confirm Outgoing Breakers Closed
section | Earth Continuity Test
checkpoint | Earth Continuity
textbox | Resistance (Ω) - [Target: <0.5Ω]
signoff | Checked By (Heyday):
checklist | Meter Panels | [5 empty] | Quality - Meter Panels
checkpoint | Receipt of switchboard delivery to site
checkpoint | Correct panel built to shop drawings
checkpoint | Mounted correctly
checkpoint | Correct install location to set out drawings
checkpoint | Correct bracket and safe fixing
checkpoint | Correct labels and schedules installed
signoff | Signoff Required from Heyday
checkpoint | Photos of boards attached
checklist | Meter Panels (Energised) | [5 empty] | Testing & Commissioning - Meter Panels (Energised)
section | Phase Voltage Reading
checkpoint | Red - White
textbox | Voltage (V)
checkpoint | Red - Blue
textbox | Voltage (V)
checkpoint | White - Blue
textbox | Voltage (V)
checkpoint | Red - Neutral
textbox | Voltage (V)
checkpoint | White - Neutral
textbox | Voltage (V)
checkpoint | Blue - Neutral
textbox | Voltage (V)
checkpoint | Red - Earth
textbox | Voltage (V)
checkpoint | White - Earth
textbox | Voltage (V)
checkpoint | Blue - Earth
textbox | Voltage (V)
signoff | Checked By (Heyday):
section | Phase Rotation
checkpoint | Direction
button | Direction | Clockwise,Anti-Clockwise
signoff | Checked By (Heyday):
section | Meter Calibration Checks
checkpoint-no-status | METER CALIBRATION CHECKS
textbox | DB NUMBER:
label | Complete Verification checks with calibrated Multimeter –
label | Amps
label | Voltage
label | (Photo Evidence Required)
checkpoint | Multimeter reading (V=Volts & A=Amps) - Red Phase
textbox | Red Phase: Record V & A
checkpoint | Multimeter reading (V=Volts & A=Amps) - White Phase
textbox | White Phase: Record V & A
checkpoint | Multimeter reading (V=Volts & A=Amps) - Blue Phase
textbox | Blue Phase: Record V & A
checkpoint | DB Meter reading (V=Volts & A=Amps) - Red Phase
textbox | Red Phase: Record V & A
checkpoint | DB Meter reading (V=Volts & A=Amps) - White Phase
textbox | White Phase: Record V & A
checkpoint | DB Meter reading (V=Volts & A=Amps) - Blue Phase
textbox | Blue Phase: Record V & A
checkpoint | CHECK BY
signoff | Checked By (Heyday):