## Sheet1
Discipline / Equipment | Phase | Activity | Test/Inspection Description | Acceptance Criteria | Hold / Witness Point | Responsible Party
33kV HV Switchgear | Site Construction | Foundation & switch room inspection | Verify dimensions, cable ducts, earthing | As per civil drawing & spec | Witness | Civil Contractor / Horizon
|  | Panel skating & wiring | Align, connect inter-panel wiring | Panels aligned, wiring secure | Witness | Electrical Contractor
| T&C | Mechanical & visual checks | Inspect CBs, enclosures, interlocks | No damage; full functionality | Hold | Electrical Contractor / Horizon
|  | Contact resistance & IR test | Measure contact µΩ and insulation >5GΩ | µΩ ≤150, IR ≥5GΩ | Hold | Electrical Contractor
|  | Trip / opening test | Confirm operation and timing | Timing within manufacturer specs | Witness | Electrical Contractor
|  | CT & VT testing | Ratio, polarity, winding resistance | As per nameplate, ±1% error | Hold | Electrical Contractor
|  | Primary Injection, HIPOT, Relay tests | Full CT loop and HV withstand | As per OEM and IEC specs | Hold | Contractor / Horizon
|  | Sensitivity & Stability test | Relay sensitivity and stability checks | Pass/fail per relay logic | Witness | Electrical Contractor
|  | Line Differential Test | End-to-end comms & logic test | Confirm directional stability | Hold | Contractor / Horizon
|  | SCADA Testing | Point-to-point checks with EOC | Signal integrity and mapping OK | Witness | SCADA / Horizon
33/11kV Transformers | Site Construction | Foundation / room inspection | Verify location, plinth strength | As per drawings/spec | Witness | Civil Contractor
|  | Skating & fixing | Position transformer and anchor | Level, secured to base | Witness | Electrical Contractor
| T&C | Visual / Mechanical check | Inspect bushings, tank, cooling | No defects or leaks | Witness | Contractor / OEM
|  | IR & winding resistance | Measure insulation & resistance | IR ≥1GΩ, as per spec | Hold | Contractor
|  | Tap changer check | Electrical and manual operation | All taps functional | Witness | Contractor / OEM
|  | % Impedance test | Measure Z% via short test | Within spec vs FAT | Hold | Contractor
|  | Vector group test | Confirm winding vector | Matches nameplate (e.g. Dyn11) | Hold | Contractor
|  | Protection relay test | Secondary injection of relays | Matches settings and logic | Hold | Contractor
|  | Soak test | 24h soak after livening | No alarms, stable temps | Hold | Contractor / Horizon
33kV HV Cable | Site Construction | Cable pulling | Visual routing, bend radius, support | No damage, correct layout | Witness | Contractor
| T&C | IR test | ≥5GΩ per phase | Hold | Contractor
|  | VLF test | Apply test voltage per standard | As per IEC 60502 | Hold | Contractor
|  | HIPOT test | Withstand HV voltage | No breakdown | Hold | Contractor
General | Pre-commissioning | Pre-livening inspection | Check all systems ready | Visual confirmation & doc review | Hold | Commissioning Rep
|  | Ready for livening notice | Issued to all parties | Signed & approved | Hold | Commissioning Rep
| Post-commissioning | Final inspection & handover | All systems operational | Handover doc signed | Witness | Horizon / Contractor