## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 33kV HV Switchgear | itp |  |  |  |  | ITP - 33kV HV Switchgear
section | Site Construction
checkpoint | Foundation & switch room inspection
label | Test/Inspection Description - Verify dimensions, cable ducts, earthing
label | Acceptance Criteria - As per civil drawing & spec
label | Hold / Witness Point - Witness
label | Responsible Party - Civil Contractor / Horizon
checkpoint | Panel skating & wiring
label | Test/Inspection Description - Align, connect inter-panel wiring
label | Acceptance Criteria - Panels aligned, wiring secure
label | Hold / Witness Point - Witness
label | Responsible Party - Electrical Contractor
section | T&C
checkpoint | Mechanical & visual checks
label | Test/Inspection Description - Inspect CBs, enclosures, interlocks
label | Acceptance Criteria - No damage; full functionality
label | Hold / Witness Point - Hold
label | Responsible Party - Electrical Contractor / Horizon
holdpoint | HOLD POINT
checkpoint | Contact resistance & IR test
label | Test/Inspection Description - Measure contact µΩ and insulation >5GΩ
label | Acceptance Criteria - µΩ ≤150, IR ≥5GΩ
label | Hold / Witness Point - Hold
label | Responsible Party - Electrical Contractor
holdpoint | HOLD POINT
checkpoint | Trip / opening test
label | Test/Inspection Description - Confirm operation and timing
label | Acceptance Criteria - Timing within manufacturer specs
label | Hold / Witness Point - Witness
label | Responsible Party - Electrical Contractor
checkpoint | CT & VT testing
label | Test/Inspection Description - Ratio, polarity, winding resistance
label | Acceptance Criteria - As per nameplate, ±1% error
label | Hold / Witness Point - Hold
label | Responsible Party - Electrical Contractor
holdpoint | HOLD POINT
checkpoint | Primary Injection, HIPOT, Relay tests
label | Test/Inspection Description - Full CT loop and HV withstand
label | Acceptance Criteria - As per OEM and IEC specs
label | Hold / Witness Point - Hold
label | Responsible Party - Contractor / Horizon
holdpoint | HOLD POINT
checkpoint | Sensitivity & Stability test
label | Test/Inspection Description - Relay sensitivity and stability checks
label | Acceptance Criteria - Pass/fail per relay logic
label | Hold / Witness Point - Witness
label | Responsible Party - Electrical Contractor
checkpoint | Line Differential Test
label | Test/Inspection Description - End-to-end comms & logic test
label | Acceptance Criteria - Confirm directional stability
label | Hold / Witness Point - Hold
label | Responsible Party - Contractor / Horizon
holdpoint | HOLD POINT
checkpoint | SCADA Testing
label | Test/Inspection Description - Point-to-point checks with EOC
label | Acceptance Criteria - Signal integrity and mapping OK
label | Hold / Witness Point - Witness
label | Responsible Party - SCADA / Horizon
checklist | 33/11kV Transformers | itp |  |  |  |  | ITP - 33/11kV Transformers
section | Site Construction
checkpoint | Foundation / room inspection
label | Test/Inspection Description - Verify location, plinth strength
label | Acceptance Criteria - As per drawings/spec
label | Hold / Witness Point - Witness
label | Responsible Party - Civil Contractor
checkpoint | Skating & fixing
label | Test/Inspection Description - Position transformer and anchor
label | Acceptance Criteria - Level, secured to base
label | Hold / Witness Point - Witness
label | Responsible Party - Electrical Contractor
section | T&C
checkpoint | Visual / Mechanical check
label | Test/Inspection Description - Inspect bushings, tank, cooling
label | Acceptance Criteria - No defects or leaks
label | Hold / Witness Point - Witness
label | Responsible Party - Contractor / OEM
checkpoint | IR & winding resistance
label | Test/Inspection Description - Measure insulation & resistance
label | Acceptance Criteria - IR ≥1GΩ, as per spec
label | Hold / Witness Point - Hold
label | Responsible Party - Contractor
holdpoint | HOLD POINT
checkpoint | Tap changer check
label | Test/Inspection Description - Electrical and manual operation
label | Acceptance Criteria - All taps functional
label | Hold / Witness Point - Witness
label | Responsible Party - Contractor / OEM
checkpoint | % Impedance test
label | Test/Inspection Description - Measure Z% via short test
label | Acceptance Criteria - Within spec vs FAT
label | Hold / Witness Point - Hold
label | Responsible Party - Contractor
holdpoint | HOLD POINT
checkpoint | Vector group test
label | Test/Inspection Description - Confirm winding vector
label | Acceptance Criteria - Matches nameplate (e.g. Dyn11)
label | Hold / Witness Point - Hold
label | Responsible Party - Contractor
holdpoint | HOLD POINT
checkpoint | Protection relay test
label | Test/Inspection Description - Secondary injection of relays
label | Acceptance Criteria - Matches settings and logic
label | Hold / Witness Point - Hold
label | Responsible Party - Contractor
holdpoint | HOLD POINT
checkpoint | Soak test
label | Test/Inspection Description - 24h soak after livening
label | Acceptance Criteria - No alarms, stable temps
label | Hold / Witness Point - Hold
label | Responsible Party - Contractor / Horizon
holdpoint | HOLD POINT
checklist | 33kV HV Cable | itp |  |  |  |  | ITP - 33kV HV Cable
section | Site Construction
checkpoint | Cable pulling
label | Test/Inspection Description - Visual routing, bend radius, support
label | Acceptance Criteria - No damage, correct layout
label | Hold / Witness Point - Witness
label | Responsible Party - Contractor
section | T&C
checkpoint | IR test
label | Test/Inspection Description - ≥5GΩ per phase
label | Acceptance Criteria - Hold
label | Hold / Witness Point - Contractor
holdpoint | HOLD POINT
checkpoint | VLF test
label | Test/Inspection Description - Apply test voltage per standard
label | Acceptance Criteria - As per IEC 60502
label | Hold / Witness Point - Hold
label | Responsible Party - Contractor
holdpoint | HOLD POINT
checkpoint | HIPOT test
label | Test/Inspection Description - Withstand HV voltage
label | Acceptance Criteria - No breakdown
label | Hold / Witness Point - Hold
label | Responsible Party - Contractor
holdpoint | HOLD POINT
checklist | General | itp |  |  |  |  | ITP - General
section | Pre-commissioning
checkpoint | Pre-livening inspection
label | Test/Inspection Description - Check all systems ready
label | Acceptance Criteria - Visual confirmation & doc review
label | Hold / Witness Point - Hold
label | Responsible Party - Commissioning Rep
holdpoint | HOLD POINT
checkpoint | Ready for livening notice
label | Test/Inspection Description - Issued to all parties
label | Acceptance Criteria - Signed & approved
label | Hold / Witness Point - Hold
label | Responsible Party - Commissioning Rep
holdpoint | HOLD POINT
section | Post-commissioning
checkpoint | Final inspection & handover
label | Test/Inspection Description - All systems operational
label | Acceptance Criteria - Handover doc signed
label | Hold / Witness Point - Witness
label | Responsible Party - Horizon / Contractor