## Table 1
[5 empty] | Inspection and Test Plan - Control and Supervision of the Works | [12 empty] | Doc ID: FH-ZU2-QU-ITP053 REV: 0
Client: Melbourne Airport | [7 empty] | Contract No: CP14038-01 | [6 empty] | Prepared By: Jihad Barbar
Project: Taxiway Zulu | [12 empty] | Reviewed By: Jamal Khodr |  |  |  |  | Date: 11/12/2024
Construction Process: IWDI Pole Install | [12 empty] | Approved By: Marco Poggenberg |  |  |  |  | Date: 11/12/2024
Specifications: ZULU-BECA-001-SPC-00004
Structure / Component: AGL
Lot No: |  |  | Lot Details: |  |  | Lot size/Quantity: | [8 empty] | Date:
Item No. |  | Task/Activity Description |  | Inspection/Test | [10 empty] | HP/ WP/ AP/ IP TP/ SCP | Responsibility Project Engineer Principal’s Representative Surveyor Foreman | Checked by:
|  |  |  | Frequency |  |  | Acceptance Criteria |  | Reference Documents |  | Inspection/ Test Method |  | Record of conformity |  |  |  | Principal’s Rep. |  | FH | Date
1 |  | Preliminary Works
1.1 |  | Check for Correct Documentation |  | Prior to start |  |  | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings. - all drawings are the latest revision. |  | Drawings / Aconex Register |  | Verify |  | Drawings and drawing registers |  | HP* | Project Engineer / Site Engineer
1.2 |  | Implementation of all measures and controls |  | Prior to start |  |  | All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP |  | PSP, EMP, TMP, JSEA, SWMS, WP |  | Visual Inspection |  | This ITP signed |  | HP* | Project Engineer / Site Engineer
1.3 |  | Pre-lift preparation |  | Prior to start |  |  | Prior to Franna lift, the below shall be completed:  APAM Crane Permit  Mobile Crane Checklist  Lift Study (if required)  Certification of any lifting lugs/beams/spreaders (if required)  Pre lift checklist |  | PSP, EMP, TMP, JSEA, SWMS, WP |  | Verify |  | This ITP signed |  | HP* | Project Engineer / Site Engineer
1.4 |  | Material Submissions and Shop Drawings |  | Prior to start |  |  | Submission and approval of the following:  Pole Structure  Windsock (white)  Bird Spikes  LED Lamps  Isolating Switch  Surge Arrestor |  | Drawing 07503 |  | Verify |  | This ITP signed Aconex Reference |  | HP* | Project Engineer / Site Engineer
2 |  | Installation
2.1 |  | Pole Install |  | Each Lot |  |  | Pole installed level as per manufacturers specification and design drawings. Rag bolt nuts secured firmly and torqued as per manufacturers specification. |  | Manufactur ers spec Drawing 07503 |  | Visual Inspection |  | This ITP Signed Avionics Checklist |  | IP | Site Engineer / Foreman
2.2 |  | Cabling Works |  | Each Lot |  |  | Install cabling, isolating switch, surge arrestor, earthing and termination box |  | Drawing 07503 |  | Visual Inspection |  | This ITP Signed Avionics Checklist |  | IP | Site Engineer / Foreman
2.3 |  | Lighting |  | Each Lot |  |  | Install and connect LED lamps |  | Drawing 07503 |  | Visual Inspection |  | This ITP Signed Avionics Checklist |  | IP | Site Engineer / Foreman
2.4 |  | Windsock Barrel & Bird Spikes |  | Each Lot |  |  | Windsock & Barell installed and secured to pole, ensuring the windsock is installed 6500mm from the ground as per MOS139 Stainless steel bird spikes installed to floodlight mounting arms |  | Drawing 07503 MOS139 |  | Visual Inspection |  | This ITP signed |  | HP* | Site Engineer / Foreman
2.5 |  | Assembly |  | Each Lot |  |  | Demonstrate the lowering of pole and making sure the mast assembly isn't damaged when lowering. |  | Aconex BecaCPL- GCOR- 001356 |  | Visual Inspection |  | This ITP signed |  | IP | Site Engineer / Foreman
3 |  | Testing and Commissioning
3.1 |  | Energise IWDI |  | Each Lot |  |  | Perform relevant cable tests prior to energization (not limited to):  Polarity Check  Cable Loop Resistance (Ohms)  Insulation Resistance (Core-Core& Core to Earth) Confirm all test measurements are within AS3000 tolerances. |  | AS3000 |  | Verify |  | Certificate of Electrical Safety (Non- Prescribed) (CES) Avionics ITC |  | TP | Site Engineer / Foreman
3.2 |  | Testing – Lux Measurement Testing Grid |  | Each Lot |  |  | WITNESS POINT Provide 7 days notice to Principals Rep to attend IWDI shall be fully tested by continuous operation for not less than 24 hrs as a completed system prior to acceptance. The IWDI shall illuminate properly during each portion of the test. LED Lamps to be tested as per MOS139, with each reading between 100 to 600 lux within the testing grid. |  | ZULU- BECA-001- SPC-00003 cl. 4.6 MOS139 |  | Verify |  | This ITP signed Test Results Letter of Conformity Avionics ITC |  | TP WP | Site Engineer / Foreman
3.3 |  | Testing – Glare/Distraction to Pilots |  | Each Lot |  |  | From an observer’s standing position on ground that is level with the base of the pole there should be no glare at a range of 25 m or more. The assessment need only be made from those directions likely to be viewed from landing, taking-off or taxiing aircraft. Qualified individual includes an electrical engineer or a licensed electrician |  | ZULU- BECA-001- SPC-00003 cl. 4.6 MOS139 |  | Verify |  | This ITP Signed Avionics ITC |  | TP HP* | Site Engineer / Foreman
Final Inspection The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications. Print Name: Position: Signature: Date: / /
Legend:
| HP | Hold Point | Work shall not proceed past the HP until released by the Principal’s Representative | [6 empty] | IP |  | Inspection point |  | Formal Inspection to be done and recorded
| HP* | Fulton Hogan Hold Point | Work shall not proceed past the HP* until released by Fulton Hogan | [6 empty] | TP |  | Test Point |  | Product compliance test to be undertaken and recorded/reported
| WP | Witness Point | An inspection which must be witnessed by the Principal’s Representative | [6 empty] | SCP |  | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
| AP | Approval Point | Written or verbal approval given by the Principal’s Representative
Notes