## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP053 - IWDI Install & Commissioning | itp |  |  |  |  | FH-ZU2-QU-ITP053 - IWDI Install & Commissioning - Rev 0
section | 1.0 - Preliminary Works
checkpoint | 1.1 - Check for Correct Documentation
label | Frequency - Prior to start
label | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | – using the correct and complete set of drawings.
label | – all drawings are the latest revision.
label | Reference Documents - Drawings / Aconex Register
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings and drawing registers
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to start
label | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 1.3 - Pre-lift preparation
label | Frequency - Prior to start
label | Acceptance Criteria - Prior to Franna lift, the below shall be completed:
label | ○ APAM Crane Permit
label | ○ Mobile Crane Checklist
label | ○ Lift Study (if required)
label | ○ Certification of any lifting lugs/beams/spreaders (if required)
label | ○ Pre lift checklist
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 1.4 - Material Submissions and Shop Drawings
label | Frequency - Prior to start
label | Acceptance Criteria - Submission and approval of the following:
label | ○ Pole Structure
label | ○ Windsock (white)
label | ○ Bird Spikes
label | ○ LED Lamps
label | ○ Isolating Switch
label | ○ Surge Arrestor
label | Reference Documents - Drawing 07503
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed Aconex Reference
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
section | 2.0 - Installation
checkpoint | 2.1 - Pole Install
label | Frequency - Each Lot
label | Acceptance Criteria - Pole installed level as per manufacturers specification and design drawings.
label | ○ Rag bolt nuts secured firmly and torqued as per manufacturers specification.
label | Reference Documents - Manufacturers spec Drawing 07503
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Avionics Checklist
label | IP
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 2.2 - Cabling Works
label | Frequency - Each Lot
label | Acceptance Criteria - Install cabling, isolating switch, surge arrestor, earthing and termination box
label | Reference Documents - Drawing 07503
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Avionics Checklist
label | IP
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 2.3 - Lighting
label | Frequency - Each Lot
label | Acceptance Criteria - Install and connect LED lamps
label | Reference Documents - Drawing 07503
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Avionics Checklist
label | IP
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 2.4 - Windsock Barrel & Bird Spikes
label | Frequency - Each Lot
label | Acceptance Criteria - Windsock & Barell installed and secured to pole, ensuring the windsock is installed 6500mm from the ground as per MOS139
label | ○ Stainless steel bird spikes installed to floodlight mounting arms
label | Reference Documents - Drawing 07503, MOS139
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 2.5 - Assembly
label | Frequency - Each Lot
label | Acceptance Criteria - Demonstrate the lowering of pole and making sure the mast assembly isn't damaged when lowering.
label | Reference Documents - Aconex BecaCPL-GCOR- 001356
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
section | 3.0 - Testing and Commissioning
checkpoint | 3.1 - Energise IWDI
label | Frequency - Each Lot
label | Acceptance Criteria - Perform relevant cable tests prior to energization (not limited to):
label | – Polarity Check
label | – Cable Loop Resistance (Ohms)
label | – Insulation Resistance (Core-Core& Core to Earth)
label | ○ Confirm all test measurements are within AS3000 tolerances.
label | Reference Documents - AS3000
label | Inspection/Test Method - Verify
label | Record of conformity - Certificate of Electrical Safety (Non- Prescribed) (CES), Avionics ITC
label | TP
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 3.2 - Testing – Lux Measurement Testing Grid
label | Frequency - Each Lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Provide 7 days notice to Principals Rep to attend
label | ○ IWDI shall be fully tested by continuous operation for not less than 24 hrs as a completed system prior to acceptance. The IWDI shall illuminate properly during each portion of the test.
label | ○ LED Lamps to be tested as per MOS139, with each reading between 100 to 600 lux within the testing grid.
label | Reference Documents - ZULU-BECA-001-SPC-00003 cl. 4.6 MOS139
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed Test Results, Letter of Conformity Avionics ITC
label | TP WP
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 3.3 - Testing – Glare/Distraction to Pilots
label | Frequency - Each Lot
label | Acceptance Criteria - From an observer’s standing position on ground that is level with the base of the pole there should be no glare at a range of 25 m or more. The assessment need only be made from those directions likely to be viewed from landing, taking-off or taxiing aircraft.
label | ○ Qualified individual includes an electrical engineer or a licensed electrician
label | Reference Documents - ZULU-BECA-001-SPC-00003 cl. 4.6 MOS139
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Avionics ITC
label | TP, HP*
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: