## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
fd828da4-39dc-4ce3-85b3-ec3ef7efb398 | checklist | 561464-DOW-ITP-PC-001 Gravity Sewer | itp | 561464-DOW-ITP-PC-001 Gravity Sewer
1717eede-d860-4842-8c27-cf82e71aeee9 | section | SECTION 3 – RECEIVING INSPECTIONS
60387823-7ccb-45e8-8e5a-1931124dff29 | checkpoint | 3.1 - Material Delivery
13fa249c-4853-5892-a230-f2c42238b52e | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct size as per drawings and Specifications
68ef3256-67b4-56bd-983f-558a53bc8215 | note | Acceptance Criteria - Pipes shall be DN150 SN16 PVC-U rubber ring jointed
11b64ad0-7134-59e2-9c30-8e7c51e35810 | note | ○ Items are approved as per contract specification
aa31dae9-4ab4-520b-9c4f-0338e823c94a | note | ○ DCC approved
198f7523-10ae-5ca1-b737-91881887d232 | note | Verifying Document - Photos, delivery docket,
79bda257-7304-5157-a940-d49d2a6aa5f7 | note | Frequency - On Delivery
e615f043-6212-5f10-afb5-ff7c73447802 | note | Inspection Type (Visual, other) - Visual
825a2f03-516c-5baf-931b-79d1a026be29 | note | Inspection: Key - C
dc8d3efb-086b-5a26-b8b9-d37f4cac396c | note | Inspection: By - SP/QE
2da840bc-2ae8-4ef7-abf6-9efe20bd1c22 | checkpoint | 3.2 - Set out
8b9d43a6-4c33-5a0b-ac48-14ecfa53bc31 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
07b62d6d-1f3d-5599-bb3a-f0c46dab3870 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
7c1732eb-ebff-58b8-b602-c0f3e284e884 | note | Verifying Document - Survey marks, photos
f3ff83ff-5660-51f0-a2a8-eaf3b376a904 | note | Frequency - Prior to commencement of works
f7139f2e-8ede-5c12-a5b5-fdd9be8584bc | note | Inspection Type (Visual, other) - Survey
2a592127-5c71-5741-b8c0-973ab9add74b | note | Inspection: Key - H
40ce5f24-6c6c-540b-bd6f-57644e7c8366 | note | Inspection: By - SV/QE/PE/CR
9b16bf31-f684-4602-a872-07fc196f80bf | signoff | AUTHORITY HOLDPOINT
e14cd4f1-d699-4a97-b192-46ffa023a44d | section | SECTION 4 – IN-PROCESS INSPECTIONS
197d9920-990a-4aa1-b25a-98a5b63feb59 | checkpoint | 4.1 - Trench Excavation
f723b7ab-5f35-5da5-badd-e7f0f9990ee3 | note | Inspection Point: Quality Control Activity - excavate to achieve required depth to invert as per drawings
25d3bcc9-b965-5266-9365-9c8e74eaf0a6 | note | ○ Floor of trench to be even across width and length
f0547dc8-4045-5aca-8be4-c15232fcfcfb | note | Acceptance Criteria - Allow 100mm for bedding
8bb462d9-af52-5e39-be6b-76fba084100f | note | Verifying Document - Photos, measurement checks
de0cc256-3270-555c-8661-cda300c6b51c | note | Frequency - During Installation
35b5bfcd-105a-5c6d-ae6c-831974a6f2e4 | note | Inspection Type (Visual, other) - Visual
b12a7656-0311-5403-b45e-c2510b1c571f | note | Inspection: Key - C
314bb7e2-b596-5988-b7d8-e3eff66bf722 | note | Inspection: By - SP/QE/CM
83677bae-cf1c-48ff-a515-c50ba6af3635 | checkpoint | 4.2 - Foundation
d83822d9-0466-548c-80b3-84929b6b6872 | note | Inspection Point: Quality Control Activity - Trench Floor Foundation to be checked it is suitable to support loads
03357e67-cae2-5c6a-8101-527398e728c2 | note | Acceptance Criteria - Foundation should avoid very soft clay, saturated soil, or fragmented rock
0aa22ac3-e2ca-57f8-ae59-6b06e04fdb2a | note | Verifying Document - Photos
67d8755e-084e-50e3-b480-fc76077df1ce | note | Frequency - During Installation
a3224b55-f03a-5f4b-b125-d967bded5048 | note | Inspection Type (Visual, other) - Visual
72331b1c-ceaf-564b-993e-99456790f137 | note | Inspection: Key - H
7691bca3-eadb-5b1c-9353-75d44722e9fd | note | Inspection: By - SP/QE
4ee1a8cc-2629-4761-af98-d7eac12f6b46 | signoff | AUTHORITY HOLDPOINT
8fe7c4d8-a2c6-49c6-b80c-cdfaa470d9b3 | checkpoint | 4.3 - Install Pipe
ebb99398-aa0e-5928-9fe3-00a13d64480f | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per design drawings
41f72e9a-c9df-5828-b567-9c20355f53fc | note | Acceptance Criteria - Pipe not damaged during installation
ad212a17-baad-53c5-9bf3-ed94e582d223 | note | ○ Pipe installed to grade within tolerances
b5f3f83f-7184-5d95-ac56-129c97e67828 | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
4297c85e-66fe-50ce-8bed-9241ea8a0e78 | note | Frequency - During installation
2f1c564a-b3a2-5947-bd19-d336dcdb24ec | note | Inspection Type (Visual, other) - Visual, Survey
cb9ec0b6-1a12-5067-9e0b-604dcde45571 | note | Inspection: Key - C
09f3e668-e339-580e-8a0e-cfa9da2752d5 | note | Inspection: By - SP/QE
5ee1ff65-9a62-4be1-a948-856861e50e0a | checkpoint | 4.4 - Laterals connections and installation
4776f539-ea3d-5e73-86f9-a4a3e56912bd | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing
dfd94f2c-f0a4-5924-ae92-4ce25a90f3ba | note | Acceptance Criteria - Lateral connection as per drawing and DCC standard details
68e48312-d91c-54c0-87bc-39fd72da1685 | note | Verifying Document - Photos
7b660b0a-8c2e-53f9-8ba5-b8d3a378f6a6 | note | Frequency - Every Lateral
442e0dc2-910b-5aa0-8fdf-abe8c73287df | note | Inspection Type (Visual, other) - Visual, Survey
7c226bc5-091f-5e93-848f-3b06ba49b666 | note | Inspection: Key - C
fcd443f4-39b0-56ac-a467-6218c2b3af83 | note | Inspection: By - SP/QE
da075d86-1830-48df-8c0a-c4b545b73df6 | checkpoint | 4.5 - Embedment zone
91c54804-0fb9-5294-8dde-2a53928e4b3b | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
35a9dee9-5a72-5065-9a0e-9dbbe5c2d439 | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
360f94da-f75c-5603-bfb6-ad74f1042fe5 | note | Acceptance Criteria - min 100mm bedding
08e2952c-55f9-50da-93a6-398047ad4398 | note | ○ 100mm overlay
2ee46c6f-71be-54f1-a1e0-dccc52bb9253 | note | Verifying Document - Photos
57e78fc0-0ad6-5459-b037-36134667ed06 | note | Frequency - During Installation
9535d3ce-de85-5a24-9ee3-31ba84286fc0 | note | Inspection Type (Visual, other) - Visual
82969f38-22c2-5af4-ac41-f3415d12111d | note | Inspection: Key - C
708f48d0-d753-57bb-a2e1-cfed0ea8478d | note | Inspection: By - SP/QE
2fa848ad-110e-481a-944a-0cbf0e6af20a | checkpoint | 4.6 - Backfill and Compact
fe94dbc3-b40b-598f-81fd-8130b8da5143 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
6007de14-a277-5642-848f-d0861f54981d | note | ○ Compaction testing one test every two layers as required
0c7492df-6b33-5e5d-87b6-1f74d435ea0e | note | ○ Conductive signal strip to be laid at 300mm above pipe
f9ced9ea-5f4c-536b-b803-74d1e4450117 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
cc238824-3111-5de9-a38d-e1a7c9718d04 | note | Verifying Document - Photos, Compaction test results
834dea89-8728-532e-8de5-035ca4be29c4 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
022edbf2-3160-50db-b682-eac53360659f | note | Inspection Type (Visual, other) - Visual, On Site test
50a15cf0-72ed-59f2-831f-b92a73432c75 | note | Inspection: Key - H
9715ef8f-edc4-55da-a6aa-0ec4022832ae | note | Inspection: By - SP/QE/CM
20779dfc-7c43-42a3-99b5-c0efe8d5f12a | signoff | AUTHORITY HOLDPOINT
2a228ad4-430a-4539-a3f1-916b6d51b7b2 | checkpoint | 4.7 - Basecourse
560cde67-86af-5f38-a48f-675cefe0c02e | note | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
fea2d63c-a1c2-5f3c-93f2-4c4eac4a05f2 | note | Acceptance Criteria - 98% MDD in roads
c02a17d0-e1a0-58fc-952d-307e5ae83663 | note | Verifying Document - Photos, Compaction test results
795ceaba-4276-5f70-b69f-27f60b105966 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
f50c245a-6f2c-5b1c-84fe-02581c0c538a | note | Inspection Type (Visual, other) - Visual, On Site test
63dbc9cd-59b1-5f03-bda4-8ac1ead00e10 | note | Inspection: Key - H
9d9db31c-36bc-5a87-aaf9-a2bf82b11a9d | note | Inspection: By - SP/QE/CM
15680522-c441-4799-8b03-a8c873ef3c6a | signoff | AUTHORITY HOLDPOINT
da8d2c16-6f4a-4253-bd2e-8c2b7ab4c711 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
4db824c2-ca70-49bb-bd87-45663954693d | checkpoint | 5.1 - Leak Testing
61771cd4-54bd-5a24-bac9-649c4aa144de | note | Inspection Point: Quality Control Activity - Completed pipelines including laterals to be tested in the presence of the Engineer or their Representative in accordance with AS/NZS 2566.2 Section 6.4
837517f5-2fb1-532f-af05-dfc3ca849586 | note | Acceptance Criteria - Engineer Approval
e7bec4af-05e0-55d7-a18b-5bc168276d80 | note | Verifying Document - Test Records
1951db37-95ed-5976-81de-fbd93e5fc012 | note | Frequency - Every section of pipe completed
6b49c0bd-7166-5cde-a4f3-1ec738f09cec | note | Inspection Type (Visual, other) - On-Site Test
aeabb0da-a360-5acd-941e-0580a3b7b322 | note | Inspection: Key - H
7fde76d0-ea46-50c2-a3bb-f799bfa77527 | note | Inspection: By - SP/QE/CM/CR
e2459a1b-78a5-4d3a-a3dc-ee3018a98a21 | signoff | AUTHORITY HOLDPOINT
d08d2aeb-b711-4866-93e2-8de822f8e9e5 | checkpoint | 5.2 - CCTV
c51384c5-20d5-5665-843e-f7d39899c552 | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
f2fca48b-c018-5331-9d6f-6baa38a2b221 | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
66daaca9-9721-5c3e-955a-e98ce184bbec | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
55a9826f-a4fc-570e-a8e7-75b6508c2da9 | note | ○ Dips or ponding of water inside the pipe
39ac2eb6-cd93-5fd2-a1fd-8c96d2e696f4 | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
8c7b2cce-5242-5075-98d8-8a865a379b25 | note | Verifying Document - Test Records, CCTV footage
a8a4d4b3-ec20-5856-8ed8-863e20038c8b | note | Frequency - Every section of pipe completed
23e86508-9a24-51c1-9d7e-59a080273ade | note | Inspection Type (Visual, other) - On-Site Test
4e839d14-1624-5ec0-aa0d-a312c32e9af6 | note | Inspection: Key - H
e328ae5f-ac9b-5829-9ded-5d630ed3b6dc | note | Inspection: By - SP/QE/CM/CR
9e95830e-8cbb-41fc-9415-427549927941 | signoff | AUTHORITY HOLDPOINT