## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
f202a5d5-e25b-4565-b458-ee99a446b2b3 | checklist | 561464-DOW-ITP-PC-003 Watermain (Trenched) | itp | 561464-DOW-ITP-PC-003 Watermain (Trenched)
69a1f80a-7c54-4bda-a2b1-699d059788ea | section | SECTION 3 – RECEIVING INSPECTIONS
f8dfa879-834a-4797-85f3-7dd99a0dd365 | checkpoint | 3.1 - Material Delivery
e02f77f9-0dcd-5e48-b883-7d58d7e45135 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
d29b0bd8-f0d0-5d1b-a559-e1d0b6506d9c | note | Acceptance Criteria - Pipes shall be DN315 PE100 PN20
92ce6735-519a-54ef-baae-fcd56f3cbdaa | note | ○ Material and fittings are approved as per contract specification
fcec1e49-3243-5be1-b35d-f9cbc6ce8ad8 | note | Verifying Document - Photos,delivery docket
dcd68ea9-dae5-573e-b6a2-479423fe4794 | note | Frequency - On delivery
94db2bd9-d6b1-5a5a-b214-6aaca851bff4 | note | Inspection Type (Visual, other) - Visual
2e2d88d6-dad8-5572-ab4c-7d4d1b0acda2 | note | Inspection: Key - C
ad78f71b-d2cb-5967-87db-040c882de3c8 | note | Inspection: By - CR/IP
12746e36-d54e-4755-a7dc-8aa6e449e42d | checkpoint | 3.2 - Set out
5d18a616-28ec-5479-8ff4-c4163fd40582 | note | Inspection Point: Quality Control Activity - Allignment set out as per design or as agreed with Engineer
84867664-a47c-5ca0-aa2f-bd251b8f5873 | note | Acceptance Criteria - Set out matches drawings or as agreed with the Engineer
f951395c-a7f8-55a8-9a57-be14e1c6c2f6 | note | Verifying Document - Photos
5ea37322-9115-5b9b-b652-425d9436b913 | note | Frequency - Prior to commencement of works
74be6dc0-b454-5790-a5ab-041d006b94c4 | note | Inspection Type (Visual, other) - Visual
acadd416-2df3-5116-b408-ae518d12ae1a | note | Inspection: Key - C
98b71267-c3dc-5829-9b15-3d51bc556044 | note | Inspection: By - CR/IP
09d51630-7f1e-4237-8f24-6ea8e1f3dc29 | section | SECTION 4 – IN-PROCESS INSPECTIONS
4b794a28-0324-489f-b1e8-e4779ce1cb35 | checkpoint | 4.1 - Trench Excavation
b077f41e-6ca4-5755-9c8c-630a42a6ec07 | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawings
31b4cf5c-6a59-5d18-ad14-afed53ae1363 | note | ○ Floor of trench to be even across width and length.
75307ab5-5dde-5088-b8fe-5d6a3b71779e | note | Acceptance Criteria - Allow 100mm for bedding
c33cdb9a-4918-5076-bc8b-33ed7694b970 | note | ○ Allow for minimum cover of 750mm.
16991585-a709-56cc-aa2c-6d715b6baf4f | note | ○ As shown on Drawings
475b2a71-5df8-5621-bd16-7dc3e24b576d | note | Verifying Document - Photos
1a861ce9-e469-5b3a-8dbe-7fe9641bcc30 | note | Frequency - During Installation
20986d45-6f13-59ce-b468-ba8028142534 | note | Inspection Type (Visual, other) - Visual
f0879830-a4a1-53f1-84d4-5ebd17f8cb1d | note | Inspection: Key - V
6de8b566-01d8-57de-addf-88ec7acb5715 | note | Inspection: By - SP/CR
86343a17-df58-4f8b-8d79-2e74c752911a | checkpoint | 4.2 - Foundation
7a91f584-8474-50d2-8946-80bd3b1b668e | note | Inspection Point: Quality Control Activity - Material trench floor is inspected to ensure suitable
290a5ebe-1abd-5b3d-98d5-db075e2a41c1 | note | Acceptance Criteria - Able to support loads
775571a3-5516-5c04-9630-544ee92b834f | note | ○ Free of very soft material or irregular or fragmented rock
79678b45-c448-56ed-918a-0e2014986b5f | note | Verifying Document - Photos
f04dbbd3-1a94-5c7e-baec-8dfda044a67a | note | Frequency - During installation
965d801d-d9f6-5dc9-a97b-cb8bcbb73588 | note | Inspection Type (Visual, other) - Visual
e0cf15c1-a6f5-563d-a5f2-6c0c2e0b8490 | note | Inspection: Key - V
d5b649e9-8ffd-5ce3-8ebf-6dc8a3bef8ec | note | Inspection: By - SP/CR
4db330d2-2458-443d-8b4b-e3c6309374f9 | checkpoint | 4.3 - Pipe Installation
6e97bfe7-0fb2-5fd5-9921-5bc98ba6f4f2 | note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
cddf6db2-229d-5d63-835e-c18c34fbc428 | note | Acceptance Criteria - Pipe not damaged during installation
6cc09f2e-b6fc-585b-a08a-a849c08656d1 | note | ○ Pipe is centrally located within trench
26ae06c4-1eac-5660-a7f6-92e1372a5ec0 | note | ○ Pipe levels are within tolerance and according to the drawings
3013e2f9-5294-5eb5-bd06-0300ec9a03b2 | note | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
fa4e64bc-dbac-5a54-b93c-3ab93dbfa8e0 | note | Frequency - During installation
994cd95b-3ead-5a79-9601-6d306df1906c | note | Inspection Type (Visual, other) - Visual
a4d7ec1b-dc24-58ff-af9e-e977c3b503f5 | note | Inspection: Key - V
f26056cf-1385-5c85-ae23-fac46a29ba8f | note | Inspection: By - SP/CR
ab3ca1da-2c91-4d6b-a690-52beda6f57e5 | checkpoint | 4.4 - Embedment zone
acdb9b6f-5608-5105-9a83-8571225c1430 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
6ff23925-c002-54b9-9ed5-d6a5069ec54a | note | Acceptance Criteria - min 100mm bedding
0b5c5b53-43a4-5b7a-81a6-4fd10c2eee62 | note | ○ 150mm overlay
2b1e9d3e-915a-5286-a88f-b3bdc7522059 | note | Verifying Document - Photos
229aef6f-55e1-5845-9900-7dbbfda13926 | note | Frequency - During Installation
224e4f39-69b1-5bbc-9bcc-5774898a813c | note | Inspection Type (Visual, other) - Visual
8f42ceb7-76c0-5bbb-b196-fb02c85a9422 | note | Inspection: Key - V
2e73600c-4e9b-5ed4-b0a2-7d841c736fd7 | note | Inspection: By - SP/CR
2d495f8f-90d6-4d1d-9f6c-e49de671c741 | checkpoint | 4.5 - Backfill and Compact
e8729456-04c6-5809-9ce9-c699a588d31d | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
acef7be8-fe57-5e5d-b11a-1142e1bb8384 | note | ○ Compaction testing one test every two layers as required
026d5a5b-fe00-5637-af9f-93b6299b991b | note | ○ Conductive signal strip to be laid at 300mm above pipe
f4c234dd-a348-5f12-8485-4e43f8f52c1e | note | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
77f37144-0da8-58bd-bbb6-3201304b5ccd | note | Verifying Document - Photos, compaction test results
30429be8-897b-55c5-9ecb-b1d742765838 | note | Frequency - During Installation, compaction testing per 50m of pipeline
eb25e315-4f7f-52ae-a2bb-1a09fa285bf2 | note | Inspection Type (Visual, other) - Visual, On site test
46b04a3a-4290-56fd-a941-b4d160fd2413 | note | Inspection: Key - H
82737e9f-2be7-5e5d-bd25-67352c278db2 | note | Inspection: By - SP/CR/IR
97467c1b-6e79-4617-b71a-651223f586dd | signoff | AUTHORITY HOLDPOINT
12069458-99ca-43e2-8f64-bc19d9e21f07 | checkpoint | 4.6 - Basecourse
e3ad4b65-902a-524e-a5c4-823994beb1de | note | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
57dfbac0-ee0f-5d6f-b71d-44967f26341d | note | Acceptance Criteria - 98% MDD in roads
4d633dd4-85d4-5d7d-9750-4024ccb96c93 | note | Verifying Document - Photos, Compaction test results
2151298b-18fd-5f6c-ad9a-9cc785fdec90 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
32112cbe-49af-5345-855e-3d4cc017c6a7 | note | Inspection Type (Visual, other) - Visual, On Site test
07282b73-de52-5f55-a803-9540d77e2fa1 | note | Inspection: Key - H
103990b2-f2a3-52b1-a7d3-5148e82b2220 | note | Inspection: By - SP/QE/CM
59be1519-b0b5-40fa-9782-ad488bd32e81 | signoff | AUTHORITY HOLDPOINT
19c9cd76-1956-4e24-9163-17c308bc536f | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
53dff629-005f-48ed-925b-b3622bc90aed | checkpoint | 5.1 - Pressure Testing (PE pipeline)
c1cb0eb1-20ea-58b1-a2d0-b1d501e73701 | note | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
f2e52f54-6d94-5b66-b0a6-580101bfa773 | note | Acceptance Criteria - Specification Attachment C, clause 4.7.5
841e40ee-7776-531e-b5ab-065ea06885f3 | note | ○ No Thrust block failures, No visible leaks, Do not exceed make-up water limit
fa4f2894-91b9-5a93-be9e-cf3bd9b070ba | note | Verifying Document - Test Records
08ea1585-5179-5bc2-aeca-60a12fb136f5 | note | Frequency - Before commissioning
f4ee2994-2638-5e82-a4db-567f25778637 | note | Inspection Type (Visual, other) - On-Site Test
94362b4d-f210-54be-9b81-961ecaed0455 | note | Inspection: Key - H
01fbbde7-1716-54e6-afe6-475096a95855 | note | Inspection: By - CR/IP/DR
5401ee63-c9fb-4290-ac21-d91c3b640dbd | signoff | AUTHORITY HOLDPOINT
5b20c8f2-96a0-440c-b1ff-96de8c52cd55 | checkpoint | 5.2 - Disinfection
2fbf20a3-d7cb-54d5-90c9-20fdfd93a106 | note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
0be34b8f-8e6a-5391-833b-8f443e82641e | note | Acceptance Criteria - Specification Attachment C, clause 4.12
11212408-9d93-5669-a9bf-8412d41c01fd | note | Verifying Document - Test Records
9d4bd7d3-297d-5f3a-bf7d-d7c6028d6105 | note | Frequency - Before commissioning
67c1bbee-c018-5c52-b3bf-a33f218b4754 | note | Inspection Type (Visual, other) - On-Site Test
d7c80519-f018-5907-9a83-edde94fa4803 | note | Inspection: Key - H
ae9866ec-e1c1-560e-9a02-60032628cea6 | note | Inspection: By - CR/IP/DR
4fac940b-b088-47e5-8477-59134b94cb78 | signoff | AUTHORITY HOLDPOINT