## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
2c9bb35f-3db2-4721-a06b-327e0b2abb56 | checklist | 561464-DOW-ITP-PC-004 Butt Welding | itp | 561464-DOW-ITP-PC-004 Butt Welding
524ebca2-d23a-4419-b844-2c189c3621f4 | section | SECTION 3 – RECEIVING INSPECTIONS
6373221d-6c0e-4e17-92b8-64eae09237e4 | checkpoint | 3.1 - Material delivery
9de41165-89b0-58c3-8ea0-5c8720be75b0 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
8372476d-c1f5-5b2a-bd19-f58e6b564305 | note | Acceptance Criteria - Pipes shall be DN315 PE100 PN20
34001854-5ea7-5c29-ba62-b08428744852 | note | ○ Material and fittings are approved as per contract specification
6fc673f6-e53f-517b-ab33-e460686f011b | note | Verifying Document - Photo of pipe bundle(s) showing pipe classification.
5e8daa32-974e-56d2-80e1-f760b3364335 | note | ○ Delivery docket/packing slip
4aa30a0a-3f2b-5279-b5cf-e7ca5d38c6b1 | note | Frequency - On delivery
b468f30d-8a97-5f1c-8fd8-fd7f8618548a | note | Inspection Type (Visual, other) - Visual
882a580e-4d2c-5199-9441-b5eda6d882d1 | note | Inspection: Key - V
e60e514b-ef0f-59c2-b5cf-1c0e0671e9d7 | note | Inspection: By - CR, IP
1455057b-1938-4195-8153-dcf0e851ebeb | checkpoint | 3.2 - Certification of welding equipment
d781c839-96ae-5b20-ae9e-3fc8cf4d498e | note | Inspection Point: Quality Control Activity - Confirming just one butt welding machine in use during life of project.
76746b1b-963c-5d16-bac6-b53b7b441136 | note | Acceptance Criteria - Accepted by Client as suitable for use
717c18ab-b3de-5672-ba66-ac8aba46fbe8 | note | Verifying Document - Current calibration certificate/service record
2e19e464-2e92-5592-8a96-1fba91484f4b | note | Frequency - Prior to commencement of works
59547939-a150-5f0b-b631-123e6f968f4b | note | Inspection Type (Visual, other) - Hold point
747f08c4-43fb-5cf8-a9b9-e891df722c9b | note | Inspection: Key - H
f459c69a-12f6-53f0-afd4-78199e57571a | note | Inspection: By - IP
a5878b78-17b4-42f7-a534-9a6676630ab0 | signoff | AUTHORITY HOLDPOINT
7147b971-ef20-4a90-958c-e22ec8771754 | section | SECTION 4 – IN-PROCESS INSPECTIONS
5a76cfb7-f4df-4e65-ba29-27520fcd6ee2 | checkpoint | 4.1 - PE Welding – Operator and Equipment
8334d2cb-e04f-58de-aec7-41f6a98d4cfd | note | Inspection Point: Quality Control Activity - Competency certificate of welder and certificate of fitness for welding equipment
f963b942-25e2-534b-aaf4-7018ad16237c | note | Acceptance Criteria - Testing of weld samples carried out by an IANZ accredited laboratory.
cee431f8-da3e-5030-9fad-c0d9378b7e32 | note | Verifying Document - Current welding certificates of operatives
283e7fd3-83d9-557e-8747-24e26f1f4490 | note | ○ Current calibration record of welding Equipment
dda6ae0a-535d-5079-8d86-4716d5547e1b | note | ○ Tensile test results
d9f8ed19-116c-5245-a9c5-748f62ae7e4d | note | Frequency - During Installation
bc586208-aa61-5853-bc9f-fd5ad24bc5c9 | note | Inspection Type (Visual, other) - Inspection, Examine
8dd878f2-2798-5849-9bbe-58608e4e5c1f | note | Inspection: Key - I, E
8aeef420-cd2e-5a5e-8d39-a099d38b6722 | note | Inspection: By - CR, IR
dcdb788c-a80d-4202-ab79-39e0465b2753 | checkpoint | 4.2 - Test Sampling
67a75bd0-f110-5adb-b452-5e7cb9085cca | note | Inspection Point: Quality Control Activity - one pre-qualification per operator, one pilot weld per machine/per DN.
67410916-4f5f-50f6-ae01-26c2099fdfcd | note | ○ Test failures will require the previous weld and the following weld to be tested and passed.
9880cbc0-7b5e-5047-a38d-aa26b6d084a9 | note | Acceptance Criteria - Pass/Fail
4a69790b-4973-51c0-a22d-7cdd019a1308 | note | ○ ISO 21307
93e3a6bf-b00e-56a9-bb81-3fcc30e05560 | note | ○ ISO 13953 (Testing)
3cd394a6-f97b-5497-aece-919fc87d4202 | note | Verifying Document - Tensile test results from Kiwi Mechanical Ltd
1eaa4b71-932b-529d-9220-587cc14c62b1 | note | Frequency - Every 50 welds per operator (or as requested by Client).
170b36f0-744e-5e76-ac99-abf35ad33177 | note | ○ Test frequency to be reduced in response to consistent pass results, with Engineers approval.
738a1183-9f0d-50c6-bc15-bac89056dd87 | note | Inspection Type (Visual, other) - Operation
467c560c-5715-5e3d-821f-ec8119778a08 | note | Inspection: Key - O, R
085e5e4b-4a05-548a-8ddb-926ff6f5c3fe | note | Inspection: By - WS/CR, IR
3f3d676f-62df-48b7-97dd-086340d99ffc | checkpoint | 4.3 - Weld Completion
089a53fd-4dd2-5569-aeda-461b4ecc207b | note | Inspection Point: Quality Control Activity - Weld completed to required standard and specification
9753b4c4-5ee2-5517-abdb-b0391ec97194 | note | Acceptance Criteria - Pass/Fail
1c733ee4-3bdb-5c65-88e3-e20bf100f76a | note | ○ ISO 21307
2904c17c-f64a-5235-94ee-5138fc9ffd31 | note | Verifying Document - Power App or manual records
689175c4-6f21-5a61-b8a9-abc865882119 | note | ○ Data log from welding equipment
7df972d1-ec8d-57e0-8376-bf2a58b42853 | note | ○ Photo Log
b36646cd-0270-546f-b5c7-48fb740e8d3d | note | Frequency - Each weld
13626414-8bf0-5a8d-bbaa-5c3526156898 | note | Inspection Type (Visual, other) - Check, Dimension Inspection
89273140-9cc1-50e3-9968-9fea3ebf0f73 | note | Inspection: Key - C, D, R
d69ea8e1-1092-5dbc-9edf-898f3f25dc27 | note | Inspection: By - WS, CR, IR
6843d6b4-e73e-41b1-90f1-863373123581 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
2cf15509-641f-4874-a857-5d7f7472a53f | checkpoint | 5.1 - Completion of QA
6d3177ee-71a3-5ccf-ba0f-a0f1450b1dff | note | Inspection Point: Quality Control Activity - Ensure QA package complete.
a2a6710c-1092-543a-b9eb-a40a1325add1 | note | Acceptance Criteria - all necessary documents including HDPE welding compiled and handed over to ER in completeness.
de0f4719-f185-532a-9ee2-ca00c0f4c934 | note | Verifying Document - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment.
d2fff832-42cd-5ad6-a074-954573d77c7b | note | ○ EF controller printout for all EF joints
d6af8c34-6b89-5701-8f30-9c117b3544da | note | Frequency - Before practical completion
d834ee1d-f561-5dd1-a37a-accd0380b731 | note | Inspection Type (Visual, other) - Inspection, Monitor on Random Basis
be5b09d7-c938-55cd-80f6-ed3353e4a0d5 | note | Inspection: Key - I, M
3349086b-6c35-5c94-9759-bfce57495f84 | note | Inspection: By - CR, IP