## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 561464-DOW-ITP-PC-001 Gravity Sewer | itp
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct size as per drawings and Specifications
note | Acceptance Criteria - Pipes shall be DN150 SN16 PVC-U rubber ring jointed
note | ○ Items are approved as per contract specification
note | ○ DCC approved
note | Verifying Document - Photos, delivery docket,
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By - SP/QE
checkpoint | 3.2 - Set out
note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
note | Verifying Document - Survey marks, photos
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By - SV/QE/PE/CR
signoff | AUTHORITY HOLDPOINT
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
note | Inspection Point: Quality Control Activity - excavate to achieve required depth to invert as per drawings
note | ○ Floor of trench to be even across width and length
note | Acceptance Criteria - Allow 100mm for bedding
note | Verifying Document - Photos, measurement checks
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By - SP/QE/CM
checkpoint | 4.2 - Foundation
note | Inspection Point: Quality Control Activity - Trench Floor Foundation to be checked it is suitable to support loads
note | Acceptance Criteria - Foundation should avoid very soft clay, saturated soil, or fragmented rock
note | Verifying Document - Photos
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - H
note | Inspection: By - SP/QE
signoff | AUTHORITY HOLDPOINT
checkpoint | 4.3 - Install Pipe
note | Inspection Point: Quality Control Activity - Pipe installed to grade as per design drawings
note | Acceptance Criteria - Pipe not damaged during installation
note | ○ Pipe installed to grade within tolerances
note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
note | Frequency - During installation
note | Inspection Type (Visual, other) - Visual, Survey
note | Inspection: Key - C
note | Inspection: By - SP/QE
checkpoint | 4.4 - Laterals connections and installation
note | Inspection Point: Quality Control Activity - Lateral connection as per drawing
note | Acceptance Criteria - Lateral connection as per drawing and DCC standard details
note | Verifying Document - Photos
note | Frequency - Every Lateral
note | Inspection Type (Visual, other) - Visual, Survey
note | Inspection: Key - C
note | Inspection: By - SP/QE
checkpoint | 4.5 - Embedment zone
note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
note | Acceptance Criteria - min 100mm bedding
note | ○ 100mm overlay
note | Verifying Document - Photos
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By - SP/QE
checkpoint | 4.6 - Backfill and Compact
note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
note | ○ Compaction testing one test every two layers as required
note | ○ Conductive signal strip to be laid at 300mm above pipe
note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By - SP/QE/CM
signoff | AUTHORITY HOLDPOINT
checkpoint | 4.7 - Basecourse
note | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
note | Acceptance Criteria - 98% MDD in roads
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By - SP/QE/CM
signoff | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Leak Testing
note | Inspection Point: Quality Control Activity - Completed pipelines including laterals to be tested in the presence of the Engineer or their Representative in accordance with AS/NZS 2566.2 Section 6.4
note | Acceptance Criteria - Engineer Approval
note | Verifying Document - Test Records
note | Frequency - Every section of pipe completed
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By - SP/QE/CM/CR
signoff | AUTHORITY HOLDPOINT
checkpoint | 5.2 - CCTV
note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
note | ○ Dips or ponding of water inside the pipe
note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
note | Verifying Document - Test Records, CCTV footage
note | Frequency - Every section of pipe completed
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By - SP/QE/CM/CR
signoff | AUTHORITY HOLDPOINT
checklist | 561464-DOW-ITP-PC-002 Installation of Manhole | itp
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
note | Acceptance Criteria - Items are approved as per contract specification
note | ○ DCC approved
note | Verifying Document - Photos, delivery docket
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By - SP/QE
checkpoint | 3.2 - Set out
note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
note | Acceptance Criteria - - Allignment set out matches drawings or aggreed with the Engineer
note | Verifying Document - Survey marks, photos
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By - SV/SP/QE
signoff | AUTHORITY HOLDPOINT
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per drawings
note | ○ Floor of trench to be even across width and length
note | Acceptance Criteria - - Allow 100mm for bedding
note | Verifying Document - Photos, measurement checks
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By - SP/QE
checkpoint | 4.2 - Foundation
note | Inspection Point: Quality Control Activity - Trench Floor Foundation to be checked it is suitable to support loads
note | Acceptance Criteria - Foundation should avoid very soft clay, saturated soil, or fragmented rock
note | Verifying Document - Photos
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - H
note | Inspection: By - SP/QE
signoff | AUTHORITY HOLDPOINT
checkpoint | 4.3 - MH Installation
note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
note | Acceptance Criteria - -Final levels are in accordance with the drawings or within tolerance and agreed with the Engineer
note | Verifying Document - Photos, As-built
note | Frequency - During installation
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By - SP/QE
signoff | AUTHORITY HOLDPOINT
checkpoint | 4.4 - Benching
note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
note | ○ Benching shape to have smooth transitions at bends and junctions
note | Acceptance Criteria - - Benching built up to the specifications
note | Verifying Document - Photos
note | Frequency - During benching contruction
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - H
note | Inspection: By - SP/QE
signoff | AUTHORITY HOLDPOINT
checkpoint | 4.5 - Backfill and Compact
note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
note | ○ Compaction testing one test every two layers as required
note | Acceptance Criteria - - 95% MDD in roads, paths, and pavements
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By - SP/QE
signoff | AUTHORITY HOLDPOINT
checkpoint | 4.6 - Basecourse
note | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
note | Acceptance Criteria - 98% MDD in roads
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By - SP/QE/CM
signoff | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Leak Testing
note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
note | Verifying Document - Photos, test records
note | Frequency - For every manhole
note | Inspection Type (Visual, other) - Test, visual
note | Inspection: Key - H
note | Inspection: By - SP/QE/PE/CR
signoff | AUTHORITY HOLDPOINT
checklist | 561464-DOW-ITP-PC-003 Watermain (Trenched) | itp
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
note | Acceptance Criteria - Pipes shall be DN315 PE100 PN20
note | ○ Material and fittings are approved as per contract specification
note | Verifying Document - Photos,delivery docket
note | Frequency - On delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By - CR/IP
checkpoint | 3.2 - Set out
note | Inspection Point: Quality Control Activity - Allignment set out as per design or as agreed with Engineer
note | Acceptance Criteria - Set out matches drawings or as agreed with the Engineer
note | Verifying Document - Photos
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By - CR/IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawings
note | ○ Floor of trench to be even across width and length.
note | Acceptance Criteria - Allow 100mm for bedding
note | ○ Allow for minimum cover of 750mm.
note | ○ As shown on Drawings
note | Verifying Document - Photos
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By - SP/CR
checkpoint | 4.2 - Foundation
note | Inspection Point: Quality Control Activity - Material trench floor is inspected to ensure suitable
note | Acceptance Criteria - Able to support loads
note | ○ Free of very soft material or irregular or fragmented rock
note | Verifying Document - Photos
note | Frequency - During installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By - SP/CR
checkpoint | 4.3 - Pipe Installation
note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
note | Acceptance Criteria - Pipe not damaged during installation
note | ○ Pipe is centrally located within trench
note | ○ Pipe levels are within tolerance and according to the drawings
note | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
note | Frequency - During installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By - SP/CR
checkpoint | 4.4 - Embedment zone
note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
note | Acceptance Criteria - min 100mm bedding
note | ○ 150mm overlay
note | Verifying Document - Photos
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By - SP/CR
checkpoint | 4.5 - Backfill and Compact
note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
note | ○ Compaction testing one test every two layers as required
note | ○ Conductive signal strip to be laid at 300mm above pipe
note | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
note | Verifying Document - Photos, compaction test results
note | Frequency - During Installation, compaction testing per 50m of pipeline
note | Inspection Type (Visual, other) - Visual, On site test
note | Inspection: Key - H
note | Inspection: By - SP/CR/IR
signoff | AUTHORITY HOLDPOINT
checkpoint | 4.6 - Basecourse
note | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
note | Acceptance Criteria - 98% MDD in roads
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By - SP/QE/CM
signoff | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pressure Testing (PE pipeline)
note | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
note | Acceptance Criteria - Specification Attachment C, clause 4.7.5
note | ○ No Thrust block failures, No visible leaks, Do not exceed make-up water limit
note | Verifying Document - Test Records
note | Frequency - Before commissioning
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By - CR/IP/DR
signoff | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Disinfection
note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
note | Acceptance Criteria - Specification Attachment C, clause 4.12
note | Verifying Document - Test Records
note | Frequency - Before commissioning
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By - CR/IP/DR
signoff | AUTHORITY HOLDPOINT
checklist | 561464-DOW-ITP-PC-004 Butt Welding | itp
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
note | Acceptance Criteria - Pipes shall be DN315 PE100 PN20
note | ○ Material and fittings are approved as per contract specification
note | Verifying Document - Photo of pipe bundle(s) showing pipe classification.
note | ○ Delivery docket/packing slip
note | Frequency - On delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By - CR, IP
checkpoint | 3.2 - Certification of welding equipment
note | Inspection Point: Quality Control Activity - Confirming just one butt welding machine in use during life of project.
note | Acceptance Criteria - Accepted by Client as suitable for use
note | Verifying Document - Current calibration certificate/service record
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Hold point
note | Inspection: Key - H
note | Inspection: By - IP
signoff | AUTHORITY HOLDPOINT
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - PE Welding – Operator and Equipment
note | Inspection Point: Quality Control Activity - Competency certificate of welder and certificate of fitness for welding equipment
note | Acceptance Criteria - Testing of weld samples carried out by an IANZ accredited laboratory.
note | Verifying Document - Current welding certificates of operatives
note | ○ Current calibration record of welding Equipment
note | ○ Tensile test results
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Inspection, Examine
note | Inspection: Key - I, E
note | Inspection: By - CR, IR
checkpoint | 4.2 - Test Sampling
note | Inspection Point: Quality Control Activity - one pre-qualification per operator, one pilot weld per machine/per DN.
note | ○ Test failures will require the previous weld and the following weld to be tested and passed.
note | Acceptance Criteria - Pass/Fail
note | ○ ISO 21307
note | ○ ISO 13953 (Testing)
note | Verifying Document - Tensile test results from Kiwi Mechanical Ltd
note | Frequency - Every 50 welds per operator (or as requested by Client).
note | ○ Test frequency to be reduced in response to consistent pass results, with Engineers approval.
note | Inspection Type (Visual, other) - Operation
note | Inspection: Key - O, R
note | Inspection: By - WS/CR, IR
checkpoint | 4.3 - Weld Completion
note | Inspection Point: Quality Control Activity - Weld completed to required standard and specification
note | Acceptance Criteria - Pass/Fail
note | ○ ISO 21307
note | Verifying Document - Power App or manual records
note | ○ Data log from welding equipment
note | ○ Photo Log
note | Frequency - Each weld
note | Inspection Type (Visual, other) - Check, Dimension Inspection
note | Inspection: Key - C, D, R
note | Inspection: By - WS, CR, IR
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Completion of QA
note | Inspection Point: Quality Control Activity - Ensure QA package complete.
note | Acceptance Criteria - all necessary documents including HDPE welding compiled and handed over to ER in completeness.
note | Verifying Document - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment.
note | ○ EF controller printout for all EF joints
note | Frequency - Before practical completion
note | Inspection Type (Visual, other) - Inspection, Monitor on Random Basis
note | Inspection: Key - I, M
note | Inspection: By - CR, IP
checklist | 561464-DOW-ITP-PC-005 EF Welding | itp
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material delivery
note | Inspection Point: Quality Control Activity - Each pipe welding location check pipes to be welded
note | ○ Each EF fitting
note | ○ Check bags undamaged and sealed
note | Acceptance Criteria - Pipes shall be DN315 PE100 PN20
note | ○ EF fittings correct size, SDR, PE100 and pressure rating.
note | Verifying Document - Photo of markings and labels on pipe.
note | ○ Delivery docket/ packing slip
note | ○ Scan bar code on fitting
note | Frequency - On delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By - CR, IP
checkpoint | 3.2 - Certification of welding equipment
note | Inspection Point: Quality Control Activity - Confirming just one EF welding machine in use during life of project.
note | Acceptance Criteria - Accepted by Client as suitable for use
note | Verifying Document - Current calibration certificate/service record
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Hold point
note | Inspection: Key - H
note | Inspection: By - IP
signoff | AUTHORITY HOLDPOINT
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - PE Welding – Operator and Equipment
note | Inspection Point: Quality Control Activity - Competency certificate of welder and certificate of fitness for welding equipment
note | ○ Generator capacity adequate for the EF fittings.
note | Acceptance Criteria - Have peel decohesion test of weld samples carried out by an IANZ accredited laboratory.
note | Verifying Document - Current welding certificates of operatives
note | ○ Current calibration record of welding Equipment
note | ○ Peel decohesion test results
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Inspection, Examine
note | Inspection: Key - I, E
note | Inspection: By - CR, IP
checkpoint | 4.2 - Test Sampling
note | Inspection Point: Quality Control Activity - one pre-qualification per operator, one pilot weld per machine/per DN.
note | Acceptance Criteria - Pass/Fail
note | ○ ISO 13953 (Testing)
note | Verifying Document - Peel decohesion test results from Kiwi Mechanical Ltd
note | Frequency - Every 20 welds per operator (or as requested by Client).
note | ○ Test frequency to be reduced in response to consistent pass results, with Engineers approval.
note | Inspection Type (Visual, other) - Operation, Review
note | Inspection: Key - O, R
note | Inspection: By - WS/CR, IP
checkpoint | 4.3 - Weld Completion
note | Inspection Point: Quality Control Activity - Weld completed to required standard and specification.
note | ○ Only move strings after EF’s have cooled!
note | Acceptance Criteria - Pass/Fail
note | ○ PIPA POP001 version 8.1 2021 and POP014
note | ○ EF controller printout for all EF joints
note | Verifying Document - Power App or manual records
note | ○ Data log from welding equipment
note | ○ Photo Log
note | Frequency - Each weld
note | Inspection Type (Visual, other) - Check, Dimension Inspection
note | Inspection: Key - C, D, R
note | Inspection: By - WS/CR, IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Completion of QA
note | Inspection Point: Quality Control Activity - Ensure QA package complete.
note | Acceptance Criteria - all necessary documents including HDPE welding compiled and handed over to ER in completeness.
note | Verifying Document - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment.
note | Frequency - Before practical completion
note | Inspection Type (Visual, other) - Inspection, Monitor on Random Basis
note | Inspection: Key - I, M
note | Inspection: By - CR, IP
checklist | 561464-DOW-ITP-PC-006 Water Lateral Connections Checklist
section | Details Connection
checkpoint-no-value | Details Connection
date | Date
textbox | Installer Name
textbox | Property Address
checkpoint | Talbot nut tightened
checkpoint | Talbot open
checkpoint | Denso tape applied
checkpoint | Site photo attached
checkpoint | Install Accepted
section | Details Manifold
checkpoint-no-value | Details Manifold
date | Date
textbox | Installer Name
textbox | Approx distance from main (m)
checkpoint | Trace wire installed and visible in box
checkpoint | Box set up 250mm from boundary
checkpoint | Manifold 165mm below lid
checkpoint | Site photo attached
checkpoint | Install Accepted
checkpoint | Final Signoff
signoff | SIGNOFF / REQUEST SIGNOFF