## QA Mech set up example
QA Folder Structure |  | Date: 17/06/22 |  | checklists
Site QA
| Levels | Zone names
| Levels: Apron, Mezzanine, Level 1 & Roof | MELBOURNE AIRPORT
|  | APRON | Ductwork Installation, Pipework Installation, Mechanical Fit Off, Subcontractors | ALL
|  | MEZZANINE | Ductwork Installation, Pipework Installation, Mechanical Fit Off, Subcontractors | ALL
|  | LEVEL 1 | Ductwork Installation, Pipework Installation, Mechanical Fit Off, Subcontractors | ALL
|  | ROOF | Ductwork Installation, Pipework Installation, Mechanical Fit Off, Subcontractors | ALL
|  | Zone 7 | CHW Pipe work installation | ITC-007 Chilled water pipe
|  | Roof | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  | Fan installaion | ITC-003 Equipment Installation
|  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
|  |  | Plant room | ITC-004 Plant Room
|  |  | AHU Installation | ITC-003 Equipment Installation
|  |  | Pump installation | ITC-003 Equipment Installation
|  |  | FCU Installation | ITC-003 Equipment Installation
|  |  | Fan coil splits installation | ITC-003 Equipment Installation
INSTRUCTIONS - delete after reading
Use this sheet to set up your QA in Conqa.
You will need to determine how the site will be QA'd e.g. by floor and then rough in, fit off etc...
Also consider how you structure this to work with monthly claiming i.e. enable it to support the % you will claim as complete for the month.
Keep in mind, the Foreman/Supervisor/Leading hand completing the QA will use an app on their phone/tablet. They will be able to select and area and tap through the applicable zone/floor/apartment to get to the applicable ITC's. They will be able to upload photos, comments, drawings, send to builders for sign off,
In the example:
Column B - levels listed, this could be floors, buildings etc...
Column C - Zones/drawings/areas, the break up of the floor/level etc..
Column D - Installation type
Column E- Applicable ITC to quality review the work - ITC list is on the next tab
It's important to get the structure correct as this cannot be changed during QA.
To complete the sheet:
1. Overtype the information on this tab
2. Submit the entire worksheet to conqa Ben Murray ben@conqahq.com

## QA Folder Structure (hidden)
QA Folder Structure |  |  | Date: 17/06/22 |  | checklists
Site QA
Rough In
Level 1
|  |  | Woolworths | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | Ductwork Piece Factory | ITC-001 Floor Rough In
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | Fan installaion | ITC-003 Equipment Installation
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
|  |  |  | Plant room | ITC-004 Plant Room
|  |  |  | AHU Installation | ITC-003 Equipment Installation
|  |  |  | Pump installation | ITC-003 Equipment Installation
|  |  |  | FCU Installation | ITC-003 Equipment Installation
|  |  |  | Fan coil splits installation | ITC-003 Equipment Installation
Zone 3
|  |  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | Ductwork Piece Factory | ITC-001 Floor Rough In
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | Fan installaion | ITC-003 Equipment Installation
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
|  |  | Zone 4 | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | Ductwork Piece Factory | ITC-001 Floor Rough In
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  |  | FCU Installation | ITC-003 Equipment Installation
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | Fan installaion | ITC-003 Equipment Installation
|  |  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
|  |  | Zone 6 (Ambience) | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | Zone 7 (Ambience) | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
Level 2
|  |  | Zone 3 | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  |  | AHU Installation | ITC-003 Equipment Installation
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
|  |  | Zone 4 | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  |  | AHU Installation | ITC-003 Equipment Installation
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | Fan installation | ITC-003 Equipment Installation
|  |  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
|  |  | Zone 6 (Ambience) | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  | Zone 7 (Ambience) | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
Level 3
|  |  | Zone 3 | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | Fan installation | ITC-003 Equipment Installation
|  |  |  | AHU Installation | ITC-003 Equipment Installation
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | VAV installation | ITC-003 Equipment Installation
|  |  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
|  |  | Zone 4 | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | AHU Installation | ITC-003 Equipment Installation
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | VAV installation | ITC-003 Equipment Installation
|  |  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
Level 4
|  |  | Zone 3 | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | AHU Installation | ITC-003 Equipment Installation
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | VAV installation | ITC-003 Equipment Installation
|  |  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
|  |  | Zone 4 | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Ductwork insulation | ITC-006 Subcontractor Fit Off
|  |  |  | Grille Installation | ITC-002 Floor Fit Off
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | AHU Installation | ITC-003 Equipment Installation
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | VAV installation | ITC-003 Equipment Installation
|  |  |  | Fire Dampers & Fire Penetrations Register | ITC-012 Fire/smoke damper checklist
Roof
|  |  | Zone 3 | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | AHU Installation | ITC-003 Equipment Installation
|  |  |  | Fan installation | ITC-003 Equipment Installation
|  |  | Zone 4 | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | CHW Pipe work installation | ITC-007 Chilled water pipe
|  |  |  | HHW Pipe work installation | ITC-008 Heating water pipe
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
|  |  |  | AHU Installation | ITC-003 Equipment Installation
|  |  |  | Fan installation | ITC-003 Equipment Installation
Zone 6 (Ambience)
|  |  |  | Fan installation | ITC-003 Equipment Installation
|  |  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
Zone 7 (Ambience)
|  |  |  | Ductwork Installation | ITC-001 Floor Rough In
|  |  |  | Fan installation | ITC-003 Equipment Installation
|  |  |  | Mech elec installation | ITC-006 Subcontractor Fit Off
Level 2
|  |  | Zone 3 | Plant Room Checklist | ITC-004 Plant Room
|  |  | Zone 4 | Plant Room Checklist | ITC-004 Plant Room
Level 3
|  |  | Zone 3 | Plant Room Checklist | ITC-004 Plant Room
|  |  | Zone 4 | Plant Room Checklist | ITC-004 Plant Room
Level 4
|  |  | Zone 3 | Plant Room Checklist | ITC-004 Plant Room
Roof
|  |  | Zone 3 | Plant Room Checklist | ITC-004 Plant Room
INSTRUCTIONS - delete after reading
Use this sheet to set up your QA in Conqa.
You will need to determine how the site will be QA'd e.g. by floor and then rough in, fit off etc...
Follow the way it is written in different columns with each item stepped down a line.
Think of an app, the reason items are in separate columns, is each column represents an individual screen with a selection of options.
It's important to get the structure correct as this cannot be changed during QA.

## MECH ITCs
type | name | values
checklist | ITC-001 Floor Rough In
section | Pre-Start
checkpoint | Specification reference checked | Yes / No / N/A
text | Drawing number and revision | Yes / No / N/A
section | Ductwork
checkpoint | Supported to Entire standard (ENT-STD-3.1) | Yes / No / N/A
checkpoint | Duct flanges firmly bolted | Yes / No / N/A
checkpoint | Cleats installed | Yes / No / N/A
checkpoint | Installed to latest drawing | Yes / No / N/A
checkpoint | Correct rod lengths | Yes / No / N/A
checkpoint | Insulated as required | Yes / No / N/A
checkpoint | Damage free | Yes / No / N/A
checkpoint | Flex Supported to Entire standard (ENT-STD-1.1) | Yes / No / N/A
checkpoint | Seismic restraints installed as per Seismic design | Yes / No / N/A
checkpoint | Cushion Boxes Installed correctly | Yes / No / N/A
checkpoint | Fire dampers installed correctly | Yes / No / N/A
checkpoint | Volume control dampers installed correctly | Yes / No / N/A
checkpoint | Kitchen Exhaust duct sealed correctly | Yes / No / N/A
checkpoint | Hangers installed as per the design | Yes / No / N/A
checkpoint | Attenuators installed to the latest drawing | Yes / No / N/A
checkpoint | APAM STANDARD: Kitchen Exhaust Ductwork confirm fall, drainage, access doors (3m spacing), and signage per MAS-BLD-001. | Yes / No / N/A
checkpoint | APAM STANDARD: Confirm 1:200 grade slope and drain points at vertical risers | Yes / No / N/A
section | Pipework
checkpoint | Pipes correctly supported | Yes / No / N/A
checkpoint | Hydrostatically tested as per (ITC-010 & ITC-011) | Yes / No / N/A
checkpoint | Pipes insulated as required | Yes / No / N/A
checkpoint | Hangers installed as per the design | Yes / No / N/A
checkpoint | No other services suspended from pipe work | Yes / No / N/A
checkpoint | Installed to latest drawing | Yes / No / N/A
checkpoint | Welds checked | Yes / No / N/A
checkpoint | Seismic restraints installed as per Seismic design | Yes / No / N/A
checkpoint | Drains installed to standard & on correct grade | Yes / No / N/A
checkpoint | Refrigeration pressure test as per (ITC-013) | Yes / No / N/A
checkpoint | Springs correctly selected | Yes / No / N/A
checkpoint | Correct valves installed | Yes / No / N/A
checkpoint | Control valves installed correctly | Yes / No / N/A
checkpoint | APAM STANDARD: Verify pipe materials meet APAM and AS Standard (e.g., copper <100mm, steel >125mm) | Yes / No / N/A
checkpoint | APAM STANDARD: Ensure joint types comply (e.g., brazed for copper >50mm, welded only for LTHHW and HTHHW) | Yes / No / N/A
checkpoint | APAM STANDARD: Check installation of bellows and roller-type supports as per AS4041 | Yes / No / N/A
checkpoint | APAM STANDARD: Confirm compliance with design pressure/velocity requirements for CHW, LTHHW, HTHHW | Yes / No / N/A
checkpoint | APAM STANDARD: Verify dual isolation valves installed on HTHHW HEX branches, vents, and drains | Yes / No / N/A
checkpoint | APAM STANDARD: Thermal Engery Meter Verification: Meters installed per EN1434 Class 2 with 15min resolution and BMS interface | Yes / No / N/A
checkpoint | APAM STANDARD: Dosing System Setup: Closed/open loop systems include dosing, alarms, bleed valves | Yes / No / N/A
checkpoint | APAM STANDARD: Flushing and Passivation Records: QA documents for cleaning, flushing, passivation maintained | Yes / No / N/A
checklist | ITC-002 Floor Fit Off
section | Pre-Start
checkpoint | Specification reference checked | Yes / No / N/A
text | Drawing number and revision
section | Grilles
checkpoint | Installed to latest drawing | Yes / No / N/A
checkpoint | Dampers open | Yes / No / N/A
checkpoint | No Damage
checkpoint | APAM STANDARD: Provide photo evidence of support methodology | Yes / No / N/A
section | Filters
checkpoint | Installed to latest drawing | Yes / No / N/A
checkpoint | Accessible | Yes / No / N/A
section | Equipment
checkpoint | Access panels in correct location | Yes / No / N/A
checkpoint | Motorised control valves fitted | Yes / No / N/A
checkpoint | Equipment clearly labelled | Yes / No / N/A
checkpoint | Cassette face correctly fitted | Yes / No / N/A
checkpoint | APAM STANDARD: Damper & Fan Access: Ensure access to smoke spill fans, fire dampers is possible for inspection | Yes / No / N/A
section | Pipework
checkpoint | Pipes correctly supported | Yes / No / N/A
checkpoint | Hydrostatic test as per (ITC-010 & ITC-011) | Yes / No / N/A
checkpoint | Pipe insulated as required | Yes / No / N/A
checkpoint | No other services suspended from pipe work | Yes / No / N/A
checkpoint | Installed to latest drawing | Yes / No / N/A
checkpoint | Welds checked | Yes / No / N/A
checkpoint | DX indoor Unit correctly mounted | Yes / No / N/A
checkpoint | DX indoor unit drain connected | Yes / No / N/A
checkpoint | Refrigeration pressure test as per (ITC-013) | Yes / No / N/A
checkpoint | Pipework Clearly Labelled | Yes / No / N/A
checkpoint | Correct valves installed | Yes / No / N/A
checkpoint | Control valves installed correctly | Yes / No / N/A
section | Penetrations
checkpoint | Acoustic penetrations correctly sealed | Yes / No / N/A
checkpoint | Fire Penetrations correctly sealed | Yes / No / N/A
checkpoint | Fire Penetrations documented | Yes / No / N/A
checkpoint | Fire Dampers installed correctly | Yes / No / N/A
checkpoint | All fire dampers photo taken and issued to the project manager to include in fire damper schedule | Yes / No / N/A
checklist | ITC-003 Equipment Installation
section | Pre-Start
checkpoint | Specification reference checked | Yes / No / N/A
text | Drawing number and revision | Yes / No / N/A
section | Fans
checkpoint | Installed to latest drawing | Yes / No / N/A
checkpoint | Fan direction checked | Yes / No / N/A
checkpoint | Flexible connections installed | Yes / No / N/A
checkpoint | Vibration control correctly selected & installed | Yes / No / N/A
checkpoint | Seismic restraints Installed as per Seismic design | Yes / No / N/A
checkpoint | Acoustic treatment (if required) | Yes / No / N/A
checkpoint | APAM STANDARD: Labbelled with APAM Asett Number | Yes / No / N/A
checkpoint | VSD installed (if required) | Yes / No / N/A
checkpoint | APAM STANDARD: VSD specification compliance: confirm harmonic reduction, IP Rating, and DC choke built in | Yes / No / N/A
section | AHU / FCU / Cassettes
checkpoint | Installed to latest drawing | Yes / No / N/A
checkpoint | Seismic restraints Installed as per Seismic design | Yes / No / N/A
checkpoint | Pipe valve sets Installed correctly (ENT-STD-2.1) Pipe connections checked | Yes / No / N/A
checkpoint | Hydrostatic test as per (ITC-010 & ITC-011) | Yes / No / N/A
checkpoint | Drains installed to standard & correct fall | Yes / No / N/A
checkpoint | Unit clearly labelled | Yes / No / N/A
checkpoint | Viberation control correctly selected & installed | Yes / No / N/A
section | DX Split Systems
checkpoint | Indoor Unit installed as per the latest drawing | Yes / No / N/A
checkpoint | Outdoor unit installed as per the latest drawing | Yes / No / N/A
checkpoint | Installed in the correct positions and clearances | Yes / No / N/A
checkpoint | Pipe works installed to standards | Yes / No / N/A
checkpoint | Vibration control installed as required | Yes / No / N/A
checkpoint | Units clearly labelled | Yes / No / N/A
checkpoint | Refrigeration correctly lagged | Yes / No / N/A
checkpoint | Refrigeration pressure test as per (ITC-012) | Yes / No / N/A
checkpoint | Nitrogen used for purging during welding | Yes / No / N/A
section | Other Equipment
checkpoint | Dust extraction system installed as per drawing | Yes / No / N/A
checkpoint | Humidifier installed as per the latest drawing | Yes / No / N/A
checkpoint | Air compressors installed as per drawing | Yes / No / N/A
checkpoint | Equipment clearly labelled | Yes / No / N/A
checklist | ITC-004 Plant Room
section | Pre-Start
checkpoint | Specification reference checked | Yes / No / N/A
text | Drawing number and revision | Yes / No / N/A
section | Ductwork
checkpoint | Supported to Entire standard (ENT-STD-3.1) | Yes / No / N/A
checkpoint | Duct flanges firmly bolted | Yes / No / N/A
checkpoint | Cleats installed | Yes / No / N/A
checkpoint | Installed to latest drawing | Yes / No / N/A
checkpoint | Correct rod lengths | Yes / No / N/A
checkpoint | Insulated as required | Yes / No / N/A
checkpoint | Damage free | Yes / No / N/A
checkpoint | Seismic restraints installed as per seismic design | Yes / No / N/A
checkpoint | Attenuators installed to the latest drawing | Yes / No / N/A
checkpoint | VSD's installed correctly | Yes / No / N/A
checkpoint | Fire Dampers installed correctly | Yes / No / N/A
section | Pipework
checkpoint | Pipe fitings complete and pipes properly supported | Yes / No / N/A
checkpoint | Hydrostatic test as per (ITC-010 & ITC-011) | Yes / No / N/A
checkpoint | Pipes insulated as required | Yes / No / N/A
checkpoint | No other services suspended from pipe work | Yes / No / N/A
checkpoint | Installed to latest drawing | Yes / No / N/A
checkpoint | Welds checked | Yes / No / N/A
checkpoint | Seismic Restraints Installed as per Seismic design | Yes / No / N/A
checkpoint | Refrigeration pressure test as per (ITC-013) | Yes / No / N/A
checkpoint | Correct valves installed | Yes / No / N/A
checkpoint | Control valves installed correctly | Yes / No / N/A
checkpoint | Pipe work clearly labelled | Yes / No / N/A
section | Plant Room Equipment
checkpoint | Fans installed as per latest drawing | Yes / No / N/A
checkpoint | Quckfill installed as per latest drawing | Yes / No / N/A
checkpoint | Buffer tanks installed as per latest drawing | Yes / No / N/A
checkpoint | Chillers installed as per latest drawing | Yes / No / N/A
checkpoint | Pumps installed as per latest drawing | Yes / No / N/A
checkpoint | Expansion Tanks installed as per latest drawing | Yes / No / N/A
checkpoint | Water Treatment installed as per latest drawing | Yes / No / N/A
checkpoint | Air and dirt separtor installed as per latest drawing | Yes / No / N/A
checkpoint | Equipment Clealy Labelled | Yes / No / N/A
Yes / No / N/A
checklist | ITC-005 Subcontractor Rough In
section | Pre-Start
checkpoint | Specification reference checked | Yes / No / N/A
text | Drawing number and revision | Yes / No / N/A
section | Mechanical Electrical
checkpoint | Mech elec wires installed as per design | Yes / No / N/A
checkpoint | MSSB Installed as per design | Yes / No / N/A
checkpoint | Wall rough's complete (If required) | Yes / No / N/A
checkpoint | APAM STANDARD: MSSB Metering Compliance: MSSBs include Schneider iEM3250/PM5310 metering | Yes / No / N/A
checkpoint | APAM STANDARD: Verify MSSBs are IP rated | Yes / No / N/A
checkpoint | APAM STANDARD: Cable seperation: Ensure controls, power, and comms cables installed in dedicated containment. | Yes / No / N/A
checkpoint | APAM STANDARD: Fire/Mech matric updated and shutdowns witnessed prior to fire life safety witness testing | Yes / No / N/A
section | Controls
checkpoint | Control wire installed as per design | Yes / No / N/A
checkpoint | Control Panel Installed as per design | Yes / No / N/A
checkpoint | Wall rough in complete (If required) | Yes / No / N/A
checkpoint | APAM STANDARD: Verify BACnet or LonWorks connectivity and full BMS control readiness | Yes / No / N/A
checkpoint | APAM STANDARD: IP Rated Enclosures Controllers housed in IP51 (internal) or IP56 (external) rated enclosures with locks | Yes / No / N/A
checkpoint | APAM STANDARD: Sufficient clearance for inspection, removal, and serviceability confirmed | Yes / No / N/A
checkpoint | APAM STANDARD: 25% spare capacity or 1 spare controller included in each panel | Yes / No / N/A
checkpoint | APAM STANDARD: Field Device QA: Sensors, actuators and valves installed with correct orientation, protection and accessibility. | Yes / No / N/A
checkpoint | APAM STANDARD: Point to Point Testing: coordinate and oversee I/O and BMS Verification checks with commissioning techs
checkpoint | APAM STANDARD: Cable seperation: Ensure controls, power, and comms cables installed in dedicated containment. | Yes / No / N/A
checklist | ITC-006 Subcontractor Fit Off
section | Pre-Start
checkpoint | Specification reference checked | Yes / No / N/A
text | Drawing number and revision | Yes / No / N/A
section | Mechanical Electrical
checkpoint | Equipment wiring complete | Yes / No / N/A
checkpoint | Sensors installed (If required) | Yes / No / N/A
checkpoint | MSSB internal wiring complete | Yes / No / N/A
section | Controls
checkpoint | Equipment wiring complete | Yes / No / N/A
checkpoint | Controls installed as per design | Yes / No / N/A
checkpoint | Control Panel internal wiring complete | Yes / No / N/A
Yes / No / N/A
checklist | ITC-007 Chilled water pipe
section | Pre-Start
checkpoint | Test specifications met | Yes / No / N/A
text | Test period to be a minimum of 4 hours | Yes / No / N/A
label | Test pressure to be 900kPa (Exceeds AS4041-2006 Appendix U) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 15min for pipe ≤DN300 (For all other buildings) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 25min for pipe >DN300 (For CU building) | Yes / No / N/A
section | Test details
checkpoint | Test details | Yes / No / N/A
bool | Applies on this floor or level | Yes / No / N/A
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | 15/25 min reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete | Yes / No / N/A
checklist | ITC-008 Heating water pipe
section | Pre-Start
checkpoint | Test specifications met | Yes / No / N/A
text | Test period to be a minimum of 4 hours | Yes / No / N/A
label | Test pressure to be 700kPa (Exceeds AS4041-2006 Appendix U) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 15min for pipe ≤DN300 (For all other buildings) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 25min for pipe >DN300 (For CU building) | Yes / No / N/A
section | Test details
checkpoint | Test Details | Yes / No / N/A
bool | Applies on this floor or level | Yes / No / N/A
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | 15/25 min reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete | Yes / No / N/A
checklist | ITC-009 Condenser water pipe
section | Pre-Start
checkpoint | Test specifications met | Yes / No / N/A
text | Test period to be a minimum of 4 hours | Yes / No / N/A
label | Test pressure to be 700kPa (Exceeds AS4041-2006 Appendix U) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 15min for pipe ≤DN300 (For all other buildings) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 25min for pipe >DN300 (For CU building) | Yes / No / N/A
section | Test details
checkpoint | Test Details | Yes / No / N/A
bool | Applies on this floor or level | Yes / No / N/A
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | 15/25 min reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete | Yes / No / N/A
checklist | ITC-010 Refrigeration pipe
section | Pre-Start
checkpoint | Test specifications met | Yes / No / N/A
text | R410A Test Pressure to be 3000kPa, maintain for 24 hours
text | R32 Test Pressure to be 3000kPa, maintain for 24 hours
text | System reference
text | System test pressure
text | Refrigerant type
section | Test details
checkpoint | Test Details | Yes / No / N/A
bool | Applies on this floor or level | Yes / No / N/A
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | Final reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete | Yes / No / N/A
checklist | ITC-011 Natural Gas
section | Pre-Start
checkpoint | Test specifications met | Yes / No / N/A
text | R410A Test Pressure to be 3000kPa, maintain for 24 hours
text | R32 Test Pressure to be 3000kPa, maintain for 24 hours
text | System reference
text | System test pressure
text | Refrigerant type
section | Test details
checkpoint | Test Details | Yes / No / N/A
bool | Applies on this floor or level | Yes / No / N/A
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | Final reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete | Yes / No / N/A
checklist | ITC-012 Fire/smoke damper checklist
section | Pre-Start
checkpoint | Specification reference checked | Yes / No / N/A
text | Drawing numbers and revision
text | supplier
section | Fire/smoke dampers
checkpoint | Fire Smoke Damper Details
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
bool | Fire/smoke damper designation | Fire, Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable