## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Floor Rough In | [5 empty] | ITC-001 Floor Rough In
section | Pre-Start
checkpoint | Specification reference checked
text | Drawing number and revision
section | Ductwork
checkpoint | Supported to Entire standard (ENT-STD-3.1)
checkpoint | Duct flanges firmly bolted
checkpoint | Cleats installed
checkpoint | Installed to latest drawing
checkpoint | Correct rod lengths
checkpoint | Insulated as required
checkpoint | Damage free
checkpoint | Flex Supported to Entire standard (ENT-STD-1.1)
checkpoint | Seismic restraints installed as per Seismic design
checkpoint | Cushion Boxes Installed correctly
checkpoint | Fire dampers installed correctly
checkpoint | Volume control dampers installed correctly
checkpoint | Kitchen Exhaust duct sealed correctly
checkpoint | Hangers installed as per the design
checkpoint | Attenuators installed to the latest drawing
checkpoint | APAM STANDARD: Kitchen Exhaust Ductwork confirm fall, drainage, access doors (3m spacing), and signage per MAS-BLD-001.
checkpoint | APAM STANDARD: Confirm 1:200 grade slope and drain points at vertical risers
section | Pipework
checkpoint | Pipes correctly supported
checkpoint | Hydrostatically tested as per (ITC-010 & ITC-011)
checkpoint | Pipes insulated as required
checkpoint | Hangers installed as per the design
checkpoint | No other services suspended from pipe work
checkpoint | Installed to latest drawing
checkpoint | Welds checked
checkpoint | Seismic restraints installed as per Seismic design
checkpoint | Drains installed to standard & on correct grade
checkpoint | Refrigeration pressure test as per (ITC-013)
checkpoint | Springs correctly selected
checkpoint | Correct valves installed
checkpoint | Control valves installed correctly
checkpoint | APAM STANDARD: Verify pipe materials meet APAM and AS Standard (e.g., copper <100mm, steel >125mm)
checkpoint | APAM STANDARD: Ensure joint types comply (e.g., brazed for copper >50mm, welded only for LTHHW and HTHHW)
checkpoint | APAM STANDARD: Check installation of bellows and roller-type supports as per AS4041
checkpoint | APAM STANDARD: Confirm compliance with design pressure/velocity requirements for CHW, LTHHW, HTHHW
checkpoint | APAM STANDARD: Verify dual isolation valves installed on HTHHW HEX branches, vents, and drains
checkpoint | APAM STANDARD: Thermal Engery Meter Verification: Meters installed per EN1434 Class 2 with 15min resolution and BMS interface
checkpoint | APAM STANDARD: Dosing System Setup: Closed/open loop systems include dosing, alarms, bleed valves
checkpoint | APAM STANDARD: Flushing and Passivation Records: QA documents for cleaning, flushing, passivation maintained
checklist | Floor Fit Off | [5 empty] | ITC-002 Floor Fit Off
section | Pre-Start
checkpoint | Specification reference checked
text | Drawing number and revision
section | Grilles
checkpoint | Installed to latest drawing
checkpoint | Dampers open
checkpoint | No Damage
checkpoint | APAM STANDARD: Provide photo evidence of support methodology
section | Filters
checkpoint | Installed to latest drawing
checkpoint | Accessible
section | Equipment
checkpoint | Access panels in correct location
checkpoint | Motorised control valves fitted
checkpoint | Equipment clearly labelled
checkpoint | Cassette face correctly fitted
checkpoint | APAM STANDARD: Damper & Fan Access: Ensure access to smoke spill fans, fire dampers is possible for inspection
section | Pipework
checkpoint | Pipes correctly supported
checkpoint | Hydrostatic test as per (ITC-010 & ITC-011)
checkpoint | Pipe insulated as required
checkpoint | No other services suspended from pipe work
checkpoint | Installed to latest drawing
checkpoint | Welds checked
checkpoint | DX indoor Unit correctly mounted
checkpoint | DX indoor unit drain connected
checkpoint | Refrigeration pressure test as per (ITC-013)
checkpoint | Pipework Clearly Labelled
checkpoint | Correct valves installed
checkpoint | Control valves installed correctly
section | Penetrations
checkpoint | Acoustic penetrations correctly sealed
checkpoint | Fire Penetrations correctly sealed
checkpoint | Fire Penetrations documented
checkpoint | Fire Dampers installed correctly
checkpoint | All fire dampers photo taken and issued to the project manager to include in fire damper schedule
checklist | Equipment Installation | [5 empty] | ITC-003 Equipment Installation
section | Pre-Start
checkpoint | Specification reference checked
text | Drawing number and revision
section | Fans
checkpoint | Installed to latest drawing
checkpoint | Fan direction checked
checkpoint | Flexible connections installed
checkpoint | Vibration control correctly selected & installed
checkpoint | Seismic restraints Installed as per Seismic design
checkpoint | Acoustic treatment (if required)
checkpoint | APAM STANDARD: Labbelled with APAM Asett Number
checkpoint | VSD installed (if required)
checkpoint | APAM STANDARD: VSD specification compliance: confirm harmonic reduction, IP Rating, and DC choke built in
section | AHU / FCU / Cassettes
checkpoint | Installed to latest drawing
checkpoint | Seismic restraints Installed as per Seismic design
checkpoint | Pipe valve sets Installed correctly (ENT-STD-2.1) Pipe connections checked
checkpoint | Hydrostatic test as per (ITC-010 & ITC-011)
checkpoint | Drains installed to standard & correct fall
checkpoint | Unit clearly labelled
checkpoint | Viberation control correctly selected & installed
section | DX Split Systems
checkpoint | Indoor Unit installed as per the latest drawing
checkpoint | Outdoor unit installed as per the latest drawing
checkpoint | Installed in the correct positions and clearances
checkpoint | Pipe works installed to standards
checkpoint | Vibration control installed as required
checkpoint | Units clearly labelled
checkpoint | Refrigeration correctly lagged
checkpoint | Refrigeration pressure test as per (ITC-012)
checkpoint | Nitrogen used for purging during welding
section | Other Equipment
checkpoint | Dust extraction system installed as per drawing
checkpoint | Humidifier installed as per the latest drawing
checkpoint | Air compressors installed as per drawing
checkpoint | Equipment clearly labelled
checklist | Plant Room | [5 empty] | ITC-004 Plant Room
section | Pre-Start
checkpoint | Specification reference checked
text | Drawing number and revision
section | Ductwork
checkpoint | Supported to Entire standard (ENT-STD-3.1)
checkpoint | Duct flanges firmly bolted
checkpoint | Cleats installed
checkpoint | Installed to latest drawing
checkpoint | Correct rod lengths
checkpoint | Insulated as required
checkpoint | Damage free
checkpoint | Seismic restraints installed as per seismic design
checkpoint | Attenuators installed to the latest drawing
checkpoint | VSD's installed correctly
checkpoint | Fire Dampers installed correctly
section | Pipework
checkpoint | Pipe fitings complete and pipes properly supported
checkpoint | Hydrostatic test as per (ITC-010 & ITC-011)
checkpoint | Pipes insulated as required
checkpoint | No other services suspended from pipe work
checkpoint | Installed to latest drawing
checkpoint | Welds checked
checkpoint | Seismic Restraints Installed as per Seismic design
checkpoint | Refrigeration pressure test as per (ITC-013)
checkpoint | Correct valves installed
checkpoint | Control valves installed correctly
checkpoint | Pipe work clearly labelled
section | Plant Room Equipment
checkpoint | Fans installed as per latest drawing
checkpoint | Quckfill installed as per latest drawing
checkpoint | Buffer tanks installed as per latest drawing
checkpoint | Chillers installed as per latest drawing
checkpoint | Pumps installed as per latest drawing
checkpoint | Expansion Tanks installed as per latest drawing
checkpoint | Water Treatment installed as per latest drawing
checkpoint | Air and dirt separtor installed as per latest drawing
checkpoint | Equipment Clealy Labelled
Yes / No / N/A
checklist | Subcontractor Rough In | [5 empty] | ITC-005 Subcontractor Rough In
section | Pre-Start
checkpoint | Specification reference checked
text | Drawing number and revision
section | Mechanical Electrical
checkpoint | Mech elec wires installed as per design
checkpoint | MSSB Installed as per design
checkpoint | Wall rough's complete (If required)
checkpoint | APAM STANDARD: MSSB Metering Compliance: MSSBs include Schneider iEM3250/PM5310 metering
checkpoint | APAM STANDARD: Verify MSSBs are IP rated
checkpoint | APAM STANDARD: Cable seperation: Ensure controls, power, and comms cables installed in dedicated containment.
checkpoint | APAM STANDARD: Fire/Mech matric updated and shutdowns witnessed prior to fire life safety witness testing
section | Controls
checkpoint | Control wire installed as per design
checkpoint | Control Panel Installed as per design
checkpoint | Wall rough in complete (If required)
checkpoint | APAM STANDARD: Verify BACnet or LonWorks connectivity and full BMS control readiness
checkpoint | APAM STANDARD: IP Rated Enclosures Controllers housed in IP51 (internal) or IP56 (external) rated enclosures with locks
checkpoint | APAM STANDARD: Sufficient clearance for inspection, removal, and serviceability confirmed
checkpoint | APAM STANDARD: 25% spare capacity or 1 spare controller included in each panel
checkpoint | APAM STANDARD: Field Device QA: Sensors, actuators and valves installed with correct orientation, protection and accessibility.
checkpoint | APAM STANDARD: Point to Point Testing: coordinate and oversee I/O and BMS Verification checks with commissioning techs
checkpoint | APAM STANDARD: Cable seperation: Ensure controls, power, and comms cables installed in dedicated containment.
checklist | Subcontractor Fit Off | [5 empty] | ITC-006 Subcontractor Fit Off
section | Pre-Start
checkpoint | Specification reference checked
text | Drawing number and revision
section | Mechanical Electrical
checkpoint | Equipment wiring complete
checkpoint | Sensors installed (If required)
checkpoint | MSSB internal wiring complete
section | Controls
checkpoint | Equipment wiring complete
checkpoint | Controls installed as per design
checkpoint | Control Panel internal wiring complete
Yes / No / N/A
checklist | Chilled water pipe | [5 empty] | ITC-007 Chilled water pipe
section | Pre-Start
checkpoint | Test specifications met
text | Test period to be a minimum of 4 hours
label | Test pressure to be 900kPa (Exceeds AS4041-2006 Appendix U) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 15min for pipe ≤DN300 (For all other buildings) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 25min for pipe >DN300 (For CU building) | Yes / No / N/A
section | Test details
checkpoint | Test details
button | Applies on this floor or level | Yes,No,N/A
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | 15/25 min reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete
checklist | Heating water pipe | [5 empty] | ITC-008 Heating water pipe
section | Pre-Start
checkpoint | Test specifications met
text | Test period to be a minimum of 4 hours
label | Test pressure to be 700kPa (Exceeds AS4041-2006 Appendix U) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 15min for pipe ≤DN300 (For all other buildings) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 25min for pipe >DN300 (For CU building) | Yes / No / N/A
section | Test details
checkpoint | Test Details
button | Applies on this floor or level | Yes,No,N/A
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | 15/25 min reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete
checklist | Condenser water pipe | [5 empty] | ITC-009 Condenser water pipe
section | Pre-Start
checkpoint | Test specifications met
text | Test period to be a minimum of 4 hours
label | Test pressure to be 700kPa (Exceeds AS4041-2006 Appendix U) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 15min for pipe ≤DN300 (For all other buildings) | Yes / No / N/A
label | AS4041-2006 Table 6.7.3 Requires Test Time of 25min for pipe >DN300 (For CU building) | Yes / No / N/A
section | Test details
checkpoint | Test Details
button | Applies on this floor or level | Yes,No,N/A
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | 15/25 min reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete
checklist | Refrigeration pipe | [5 empty] | ITC-010 Refrigeration pipe
section | Pre-Start
checkpoint | Test specifications met
text | R410A Test Pressure to be 3000kPa, maintain for 24 hours
text | R32 Test Pressure to be 3000kPa, maintain for 24 hours
text | System reference
text | System test pressure
text | Refrigerant type
section | Test details
checkpoint | Test Details
button | Applies on this floor or level | Yes,No,N/A
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | Final reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete
checklist | Natural Gas | [5 empty] | ITC-011 Natural Gas
section | Pre-Start
checkpoint | Test specifications met
text | R410A Test Pressure to be 3000kPa, maintain for 24 hours
text | R32 Test Pressure to be 3000kPa, maintain for 24 hours
text | System reference
text | System test pressure
text | Refrigerant type
section | Test details
checkpoint | Test Details
button | Applies on this floor or level | Yes,No,N/A
text | Pipe system
text | area/section under
text | from
text | to
text | System working pressure
text | System test pressure
text | Initial reading - kPA, time, ambient temperature
text | Final reading - kPA, time, ambient temperature
section | Sign off
checkpoint | Sign off - attach signature below and pass once complete
checklist | Fire/smoke damper checklist | [5 empty] | ITC-012 Fire/smoke damper checklist
section | Pre-Start
checkpoint | Specification reference checked
text | Drawing numbers and revision
text | supplier
section | Fire/smoke dampers
checkpoint | Fire Smoke Damper Details
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
button | Fire/smoke damper designation | Fire,Smoke
text | Fire/smoke damper width x height
text | wall/slab thickness
text | position
checkpoint | Access panel in duct suitable for damper access
checkpoint | Fire/Smoke dampers labelled
checkpoint | Installed to manufacturers requirements
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable